04 - Southeast | 25S | Transfer | Group4_Fault_1032_P1 | 3 phase fault on NTXEAST4 (508561) 138 kV Bus a. Apply Fault at the NTXEAST4 (508561) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from NTXEAST4 (508561) 138 kV Bus to ESTGEN4 (508583) 138 kV Bus CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1033_P1 | 3 phase fault on OVERTON2 (509079) 69 kV Bus a. Apply Fault at the OVERTON2 (509079) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from OVERTON2 (509079) 69 kV Bus to TURNERT2 (509089) 69 kV Bus CKT 1 b. 2. Drop Load 1 at TURNERT2 (509089) 69 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1034_P1 | 3 phase fault on CARTHGT4 (509060) 138 kV Bus a. Apply Fault at the CARTHGT4 (509060) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from CARTHGT4 (509060) 138 kV Bus to MURVAULTP (509048) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1035_P1 | 3 phase fault on CARTHGT4 (509060) 138 kV Bus a. Apply Fault at the CARTHGT4 (509060) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from CARTHGT4 (509060) 138 kV Bus to LOGANSP4 (509071) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1036_P1 | 3 phase fault on ROKHILL2 (509082) 69 kV Bus a. Apply Fault at the ROKHILL2 (509082) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from ROKHILL2 (509082) 69 kV Bus to BECKVIL2 (509054) 69 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1037_P1 | 3 phase fault on ROKHILL2 (509082) 69 kV Bus a. Apply Fault at the ROKHILL2 (509082) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from ROKHILL2 (509082) 69 kV Bus to ROSBORO2 (509085) 69 kV Bus CKT 1 b. 2. Trip branch from ROSBORO2 (509085) 69 kV Bus to BLOCKRT2 (509055) 69 kV Bus CKT 1 b. 3. Drop Load 1 at ROSBORO2 (509085) 69 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1038_P1 | 3 phase fault on ROKHILL2 (509082) 69 kV Bus a. Apply Fault at the ROKHILL2 (509082) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from ROKHILL2 (509082) 69 kV Bus to CARTHAG2 (509056) 69 kV Bus CKT 1 b. 2. Trip branch from CARTHAG2 (509056) 69 kV Bus to LAPACIF2 (509068) 69 kV Bus CKT 1 b. 3. Drop Load 1 at CARTHAG2 (509056) 69 kV Bus b. 4. Drop Load 2 at CARTHAG2 (509056) 69 kV Bus b. 5. Drop Load 1 at LAPACIF2 (509068) 69 kV Bus b. 6. Drop Shunt 1 at CARTHAG2 (509056) 69 kV Bus1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1039_P1 | 3 phase fault on BIG3TAP2 (508539) 69 kV Bus a. Apply Fault at the BIG3TAP2 (508539) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from BIG3TAP2 (508539) 69 kV Bus to BIG 3 2 (508537) 69 kV Bus CKT 1 b. 2. Drop Load 1 at BIG 3 2 (508537) 69 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1040_P1 | 3 phase fault on BIG3TAP2 (508539) 69 kV Bus a. Apply Fault at the BIG3TAP2 (508539) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from BIG3TAP2 (508539) 69 kV Bus to LLAMOND2 (508551) 69 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1041_P1 | 3 phase fault on LETOURT2 (508549) 69 kV Bus a. Apply Fault at the LETOURT2 (508549) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from LETOURT2 (508549) 69 kV Bus to LETOURN2 (508581) 69 kV Bus CKT 1 b. 2. Trip branch from LETOURN2 (508581) 69 kV Bus to LETRNST2 (508536) 69 kV Bus CKT 1 b. 3. Drop Load 1 at LETOURN2 (508581) 69 kV Bus b. 4. Drop Load 1 at LETRNST2 (508536) 69 kV Bus b. 5. Drop Shunt 1 at LETOURN2 (508581) 69 kV Bus1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1042_P1 | 3 phase fault on EVENSID2 (509061) 69 kV Bus a. Apply Fault at the EVENSID2 (509061) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from EVENSID2 (509061) 69 kV Bus to FEARSCO2 (509086) 69 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1043_P1 | 3 phase fault on EVENSID2 (509061) 69 kV Bus a. Apply Fault at the EVENSID2 (509061) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from EVENSID2 (509061) 69 kV Bus to POYNTER2 (509081) 69 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1044_P1 | 3 phase fault on POYNTER2 (509081) 69 kV Bus a. Apply Fault at the POYNTER2 (509081) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from POYNTER2 (509081) 69 kV Bus to HNDRSNR2 (509065) 69 kV Bus CKT 1 b. 2. Trip branch from HNDRSNR2 (509065) 69 kV Bus to BEARCATTP 2 (509127) 69 kV Bus CKT 1 b. 3. Trip branch from BEARCATTP 2 (509127) 69 kV Bus to BECKVIL2 (509054) 69 kV Bus CKT 1 b. 4. Drop Load 1 at HNDRSNR2 (509065) 69 kV Bus b. 5. Drop Load 1 at BEARCATTP 2 (509127) 69 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1045_P1 | 3 phase fault on 4GRIMES% (334026) 138 kV Bus a. Apply Fault at the 4GRIMES% (334026) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from 4GRIMES% (334026) 138 kV Bus to 4COLSTTA% (334021) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1046_P1 | 3 phase fault on 4GRIMES% (334026) 138 kV Bus a. Apply Fault at the 4GRIMES% (334026) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from 4GRIMES% (334026) 138 kV Bus to 4MT.ZION (334060) 138 kV Bus CKT 1 b. 2. Trip branch from 4MT.ZION (334060) 138 kV Bus to 4L558T485 (334058) 138 kV Bus CKT 1 b. 3. Drop Load BZ at 4MT.ZION (334060) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1047_P1 | 3 phase fault on 4GRIMES% (334026) 138 kV Bus a. Apply Fault at the 4GRIMES% (334026) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from 4GRIMES% (334026) 138 kV Bus to 4MAG AND (334025) 138 kV Bus CKT 1 b. 2. Trip branch from 4MAG AND (334025) 138 kV Bus to 4SOTA 1 (334024) 138 kV Bus CKT 1 b. 3. Trip branch from 4SOTA 1 (334024) 138 kV Bus to 4NAVSSPLT! (334019) 138 kV Bus CKT 1 b. 4. Drop Load BZ at 4SOTA 1 (334024) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1048_P1 | 3 phase fault on 4GRIMES% (334026) 138 kV Bus a. Apply Fault at the 4GRIMES% (334026) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from 4GRIMES% (334026) 138 kV Bus to 4BENTWATER! (334039) 138 kV Bus CKT 1 b. 2. Trip branch from 4BENTWATER! (334039) 138 kV Bus to 4WALDEN (334040) 138 kV Bus CKT 1 b. 3. Trip branch from 4WALDEN (334040) 138 kV Bus to 4APRILTX (334041) 138 kV Bus CKT 1 b. 4. Trip branch from 4APRILTX (334041) 138 kV Bus to 4LFOREST (334042) 138 kV Bus CKT 1 b. 5. Trip branch from 4LFOREST (334042) 138 kV Bus to 4RABONCHAPEL (334049) 138 kV Bus CKT 1 b. 6. Trip branch from 4RABONCHAPEL (334049) 138 kV Bus to 4WDHAVN (334105) 138 kV Bus CKT 1 b. 7. Trip branch from 4WDHAVN (334105) 138 kV Bus to 4PONDEROSA% (334087) 138 kV Bus CKT 1 b. 8. Drop Load 1 at 4BENTWATER! (334039) 138 kV Bus b. 9. Drop Load 1 at 4WALDEN (334040) 138 kV Bus b. 10. Drop Load 1 at 4APRILTX (334041) 138 kV Bus b. 11. Drop Load BZ at 4LFOREST (334042) 138 kV Bus b. 12. Drop Load BZ at 4RABONCHAPEL (334049) 138 kV Bus b. 13. Drop Load BZ at 4WDHAVN (334105) 138 kV Bus b. 14. Drop Shunt 1 at 4BENTWATER! (334039) 138 kV Bus1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1049_P1 | 3 phase fault on 4PONDEROSA% (334087) 138 kV Bus a. Apply Fault at the 4PONDEROSA% (334087) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from 4PONDEROSA% (334087) 138 kV Bus to 4FISHCRK (334045) 138 kV Bus CKT 1 b. 2. Trip branch from 4FISHCRK (334045) 138 kV Bus to 4DEERLAKE (334048) 138 kV Bus CKT 1 b. 3. Trip branch from 4DEERLAKE (334048) 138 kV Bus to 4SPRINGBRNCH (334046) 138 kV Bus CKT 1 b. 4. Trip branch from 4SPRINGBRNCH (334046) 138 kV Bus to 4DOBBIN! (334044) 138 kV Bus CKT 1 b. 5. Trip branch from 4DOBBIN! (334044) 138 kV Bus to 4TUBULAR (334043) 138 kV Bus CKT 1 b. 6. Drop Load BZ at 4FISHCRK (334045) 138 kV Bus b. 7. Drop Load BZ at 4DEERLAKE (334048) 138 kV Bus b. 8. Drop Load BZ at 4SPRINGBRNCH (334046) 138 kV Bus b. 9. Drop Load 1 at 4DOBBIN! (334044) 138 kV Bus b. 10. Drop Load BZ at 4DOBBIN! (334044) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1050_P1 | 3 phase fault on 4PONDEROSA% (334087) 138 kV Bus a. Apply Fault at the 4PONDEROSA% (334087) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from 4PONDEROSA% (334087) 138 kV Bus to 4LONGMIR! (334075) 138 kV Bus CKT 1 b. 2. Trip branch from 4LONGMIR! (334075) 138 kV Bus to 4PANORAM (334074) 138 kV Bus CKT 1 b. 3. Trip branch from 4PANORAM (334074) 138 kV Bus to 4EGYPT (334073) 138 kV Bus CKT 1 b. 4. Trip branch from 4EGYPT (334073) 138 kV Bus to 4LEWIS% (334072) 138 kV Bus CKT 1 b. 5. Drop Load 1 at 4LONGMIR! (334075) 138 kV Bus b. 6. Drop Load 1 at 4PANORAM (334074) 138 kV Bus b. 7. Drop Load 1 at 4EGYPT (334073) 138 kV Bus b. 8. Drop Shunt 1 at 4LONGMIR! (334075) 138 kV Bus1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1051_P1 | 3 phase fault on 4PONDEROSA% (334087) 138 kV Bus a. Apply Fault at the 4PONDEROSA% (334087) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from 4PONDEROSA% (334087) 138 kV Bus to 4CONROE1! (334104) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1052_P1 | 3 phase fault on LLAMOND2 (508551) 69 kV Bus a. Apply Fault at the LLAMOND2 (508551) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from LLAMOND2 (508551) 69 kV Bus to GREGGTN2 (508542) 69 kV Bus CKT 1 b. 2. Trip branch from GREGGTN2 (508542) 69 kV Bus to NETTLTP2 (508559) 69 kV Bus CKT 1 b. 3. Drop Load 1 at GREGGTN2 (508542) 69 kV Bus b. 4. Drop Load 2 at GREGGTN2 (508542) 69 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1053_P1 | 3 phase fault on LLAMOND2 (508551) 69 kV Bus a. Apply Fault at the LLAMOND2 (508551) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from LLAMOND2 (508551) 69 kV Bus to AIRLINE2 (508538) 69 kV Bus CKT 1 b. 2. Trip branch from AIRLINE2 (508538) 69 kV Bus to LONGVHT2 (508553) 69 kV Bus CKT 1 b. 3. Drop Load 1 at AIRLINE2 (508538) 69 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1054_P4 | a. Apply single-phase fault on GRDA1 7 (512650) 345 kV Bus TO GREC TAP5 (512865) 345 kV Bus CKT 1 b. 1. Clear fault after 15 cycles: b. 2. Trip branch GRDA1 7 (512650) 345 kV Bus TO GREC TAP5 (512865) 345 kV Bus CKT 1 b. 3. Disconnect BUS 512821 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1055_P4 | a. Apply single-phase fault on 7SPORTSMAN (300740) 345 kV Bus TO GRDA1 7 (512650) 345 kV Bus CKT 1 b. 1. Clear fault after 15 cycles: b. 2. Trip branch 7SPORTSMAN (300740) 345 kV Bus TO GRDA1 7 (512650) 345 kV Bus CKT 1 b. 3. Disconnect BUS 512821 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1056_P4 | a. Apply single-phase fault on GRDA1 7 (512650) 345 kV Bus TO TONECE7 (512750) 345 kV Bus CKT 1 b. 1. Clear fault after 15 cycles: b. 2. Trip branch GRDA1 7 (512650) 345 kV Bus TO TONECE7 (512750) 345 kV Bus CKT 1 b. 3. Disconnect BUS 512821 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1060_P4 | a. Apply single-phase fault on T.NO.--7 (509852) 345 kV Bus TO IGLOOV 7 (513596) 345 kV Bus CKT 1 b. 1. Clear fault after 15 cycles: b. 2. Trip branch T.NO.--7 (509852) 345 kV Bus TO IGLOOV 7 (513596) 345 kV Bus CKT 1 b. 3. Disconnect BUS 513592 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1061_P4 | a. Apply single-phase fault on CLARMR 5 (512651) 161 kV Bus TO GRDA1 5 (512656) 161 kV Bus CKT 1 b. 1. Clear fault after 15 cycles: b. 2. Trip branch CLARMR 5 (512651) 161 kV Bus TO GRDA1 5 (512656) 161 kV Bus CKT 1 b. 3. Disconnect BUS 512700 b. 4. Disconnect BUS 512818 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1062_P4 | a. Apply single-phase fault on MAID 5 (512648) 161 kV Bus TO GRDA1 5 (512656) 161 kV Bus CKT 1 b. 1. Clear fault after 15 cycles: b. 2. Trip branch MAID 5 (512648) 161 kV Bus TO GRDA1 5 (512656) 161 kV Bus CKT 1 b. 3. Trip branch GRDA1 5 (512656) 161 kV Bus TO WMAIN ST5 (512742) 161 kV Bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1063_P4 | a. Apply single-phase fault at CLEVLND7 (512694) 345 kV Bus b. 1. Run for 15 cycles, Trip branch from T.NO.--7 (509852) 345 kV Bus TO CLEVLND7 (512694) 345 kV Bus CKT 1 b. 2. Clear fault at CLEVLND7 (512694) 345 kV Bus b. 3. Trip branch from CLEVLND7 (512694) 345 kV Bus TO G15-066T (560056) 345 kV Bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1064_P4 | a. Apply single-phase fault at CLEVLND7 (512694) 345 kV Bus b. 1. Run for 15 cycles, Trip branch from T.NO.--7 (509852) 345 kV Bus TO CLEVLND7 (512694) 345 kV Bus CKT 1 b. 2. Clear fault at CLEVLND7 (512694) 345 kV Bus b. 3. Disconnect bus CLEVLND1 (512817) 13.8 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1065_P4 | a. Apply single-phase fault at CLEVLND7 (512694) 345 kV Bus b. 1. Run for 15 cycles: b. 2. Trip branch from CLEVLND7 (512694) 345 kV Bus TO SOONER 7 (514803) 345 kV Bus CKT 1 b. 3. Trip three winding from CLEVLND7 (512694) 345 kV Bus TO CLEVLND 4 (512729) 138 kV Bus TO CLEVLND1 (512817) 13.8 kV CKT 1 b. 4. Clear fault at CLEVLND7 (512694) 345 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1066_P4 | a. Apply single-phase fault at MAID 5 (512648) 161 kV Bus b. 1. Run for 15 cycles, Trip branch from 5CHOTEAU1 (300069) 161 kV Bus TO MAID 5 (512648) 161 kV Bus CKT 1 b. 2. Clear fault at MAID 5 (512648) 161 kV Bus b. 3. Disconnect bus MAITER1 1 (512836) 13.2 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1067_P4 | a. Apply single-phase fault at MAID 5 (512648) 161 kV Bus b. 1. Run for 15 cycles, Trip branch from CATSAGR5 (512638) 161 kV Bus TO MAID 5 (512648) 161 kV Bus CKT 1 b. 2. Clear fault at MAID 5 (512648) 161 kV Bus b. 3. Disconnect bus MAITER1 1 (512836) 13.2 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1068_P4 | a. Apply single-phase fault at MAID 5 (512648) 161 kV Bus b. 1. Run for 15 cycles, Trip branch from DRYGULCH5 (512629) 161 kV Bus TO MAID 5 (512648) 161 kV Bus CKT 1 b. 2. Clear fault at MAID 5 (512648) 161 kV Bus b. 3. Disconnect bus MAITER1 1 (512836) 13.2 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1069_P4 | a. Apply single-phase fault at MAID 5 (512648) 161 kV Bus b. 1. Run for 15 cycles, Trip branch from KERR GR5 (512635) 161 kV Bus TO MAID 5 (512648) 161 kV Bus CKT 2 b. 2. Clear fault at MAID 5 (512648) 161 kV Bus b. 3. Disconnect bus MAITER1 1 (512836) 13.2 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1070_P4 | a. Apply single-phase fault at MAID 5 (512648) 161 kV Bus b. 1. Run for 15 cycles, Trip branch from MAID 5 (512648) 161 kV Bus TO GRDA1 5 (512656) 161 kV Bus CKT 1 b. 2. Clear fault at MAID 5 (512648) 161 kV Bus b. 3. Disconnect bus MAITER1 1 (512836) 13.2 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1071_P4 | a. Apply single-phase fault at MAID 5 (512648) 161 kV Bus b. 1. Run for 15 cycles, Trip branch from 5CHOTEAU1 (300069) 161 kV Bus TO MAID 5 (512648) 161 kV Bus CKT 1 b. 2. Clear fault at MAID 5 (512648) 161 kV Bus b. 3. Trip branch from MAID 5 (512648) 161 kV Bus TO GERALDGAY5 (512760) 161 kV Bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1072_P4 | a. Apply single-phase fault at MAID 5 (512648) 161 kV Bus b. 1. Run for 15 cycles, Trip branch from CATSAGR5 (512638) 161 kV Bus TO MAID 5 (512648) 161 kV Bus CKT 1 b. 2. Clear fault at MAID 5 (512648) 161 kV Bus b. 3. Trip branch from CATSAGR5 (512638) 161 kV Bus TO MAID 5 (512648) 161 kV Bus CKT 2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1073_P4 | a. Apply single-phase fault at MAID 5 (512648) 161 kV Bus b. 1. Run for 15 cycles, Trip branch from KERR GR5 (512635) 161 kV Bus TO MAID 5 (512648) 161 kV Bus CKT 1 b. 2. Clear fault at MAID 5 (512648) 161 kV Bus b. 3. KERR GR5 (512635) 161 kV Bus TO MAID 5 (512648) 161 kV Bus CKT 2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1074_P4 | a. Apply single-phase fault at MAID 5 (512648) 161 kV Bus b. 1. Run for 15 cycles, Trip branch from MAID 5 (512648) 161 kV Bus TO GRDA1 5 (512656) 161 kV Bus CKT 1 b. 2. Clear fault at MAID 5 (512648) 161 kV Bus b. 3. Trip branch from MAID 5 (512648) 161 kV Bus TO GRDA1 5 (512656) 161 kV Bus CKT 2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1076_P4 | a. Apply single-phase fault at KERR GR5 (512635) 161 kV Bus b. 1. Run for 15 cycles, Trip branch from KERR GR5 (512635) 161 kV Bus TO MAID 5 (512648) 161 kV Bus CKT 1 b. 2. Clear fault at KERR GR5 (512635) 161 kV Bus b. 3. Trip branch from KERR GR5 ( 512635 ) 161 kV Bus TO MAID 5 ( 512648 ) 161 kV Bus CKT 2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1078_P4 | a. Apply single-phase fault at KETCHUM5 (512669) 161 kV Bus b. 1. Run for 15 cycles, Disconnect Bus 512632 b. 2. Clear fault at KETCHUM5 (512669) 161 kV Bus b. 3. Trip branch from PENSA 5 (512654) 161 kV Bus TO KETCHUM5 (512669) 161 kV Bus CKT 1 b. 4. Drop Load 1 Bus 512669 b. 5. Disconnect Bus 512669 b. 6. Disconnect Bus 512845 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1079_P4 | a. Apply single-phase fault at PENSA 5 (512654) 161 kV Bus b. 1. Run for 15 cycles, Trip branch from DRYGULCH5 (512629) 161 kV Bus TO PENSA 5 (512654) 161 kV Bus CKT 1 b. 2. Clear fault at PENSA 5 (512654) 161 kV Bus b. 3. Disconnect bus PENSA 1 (512841) 13.8 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1080_P4 | a. Apply single-phase fault at PENSA 5 (512654) 161 kV Bus b. 1. Run for 15 cycles, Trip branch from KERR GR5 (512635) 161 kV Bus TO PENSA 5 (512654) 161 kV Bus CKT 1 b. 2. Clear fault at PENSA 5 (512654) 161 kV Bus b. 3. Disconnect bus PENSA 1 (512841) 13.8 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1081_P4 | a. Apply single-phase fault at PENSA 5 (512654) 161 kV Bus b. 1. Run for 15 cycles, Trip branch from DRYGULCH5 (512629) 161 kV Bus TO PENSA 5 (512654) 161 kV Bus CKT 1 b. 2. Clear fault at PENSA 5 (512654) 161 kV Bus b. 3. Trip branch from PENSA 5 (512654) 161 kV Bus TO KETCHUM5 (512669) 161 kV Bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1084_P4 | a. Apply single-phase fault at TONECE5 (512751) 161 kV Bus b. 1. Run for 15 cycles, Trip branch from SILMCTY5 (512643) 161 kV Bus TO TONECE5 (512751) 161 kV Bus CKT 1 b. 2. Clear fault at TONECE5 (512751) 161 kV Bus b. 3. Disconnect Bus 512754 b. 4. Drop Load 1 Bus 512745 b. 5. Drop Load 1 Bus 512746 b. 6. Disconnect Bus 512728 b. 7. Disconnect Bus 512745 b. 8. Disconnect Bus 512746 b. 9. Disconnect Bus 512747 b. 10. Disconnect Bus 512756 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 763002 [G18-064-GEN10.5500]
04 - Southeast | 25S | Transfer | Group4_Fault_1085_P4 | a. Apply single-phase fault at TONECE7 (512750) 345 kV Bus b. 1. Run for 15 cycles, Trip branch from FLINTCR7 (506935) 345 kV Bus TO TONECE7 (512750) 345 kV Bus CKT 1 b. 2. Clear fault at TONECE7 (512750) 345 kV Bus b. 3. Trip branch from GRDA1 7 (512650) 345 kV Bus TO TONECE7 (512750) 345 kV Bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1086_P4 | a. Apply single-phase fault at TONECE7 (512750) 345 kV Bus b. 1. Run for 15 cycles, Trip branch from GRDA1 7 (512650) 345 kV Bus TO TONECE7 (512750) 345 kV Bus CKT 1 b. 2. Clear fault at TONECE7 (512750) 345 kV Bus b. 3. Disconnect Bus 512752 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1087_P4 | a. Apply single-phase fault at BVRCNTY7 (515554) 345 kV Bus CB 307 Stuck b. Clear Fault after 16 cycles: b. 1. Trip branch from BVRCNTY7 (515554) 345 kV Bus TO BADGER 7 (515677) 345 kV Bus CKT 1 b. 2. Trip branch from BVRCNTY7 (515554) 345 kV Bus TO BADGER 7 (515677) 345 kV Bus CKT 2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1088_P4 | a. Apply single-phase fault at WINDFRM4 (515785) 138 kV Bus b. 1. Run for 16 cycles: b. 2. Trip branch from WINDFRM4 (515785) 138 kV Bus TO MOORLND4 (520999) 138 kV Bus CKT 1 b. 3. Trip branch from WOODWRD4 (514785) 138 kV Bus TO WINDFRM4 (515785) 138 kV Bus CKT 1 b. 4. Clear fault at WINDFRM4 (515785) 138 kV Bus b. 5. Drop Generator 1 Bus 515895 b. 6. Drop Load S1 Bus 515787 b. 7. Disconnect Bus 515785 b. 8. Disconnect Bus 515786 b. 9. Disconnect Bus 515787 b. 10. Disconnect Bus 515790 b. 11. Disconnect Bus 515895 b. 12. Disconnect Bus 515896 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1089_P4 | a. Apply single-phase fault at SUNNYSD7 (515136) 345 kV Bus b. 1. Run for 16 cycles: b. 2. Trip three winding transformer from SUNNYSD7 (515136) 345 kV Bus TO SUNNYSD4 (515135) 138 kV TO SUNYSD 1 (515405) 13.8 kV CKT 1 b. 3. Disconnect Bus SUNYSD 1 (515405) 13.8 kV CKT 1 b. 4. Trip branch from SUNNYSD7 (515136) 345 kV Bus TO G16-063-TAP (560088) 138 kV Bus CKT 1 b. 5. Clear fault at SUNNYSD7 (515136) 345 kV Bus b. 6. Drop Shunt 1 Bus SUNYSD 1 (515405) 13.8 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1090_P4 | a. Apply single-phase fault at DRAPER 4 (514933) 138 kV Bus b. 1. Run for 16 cycles: b. 2. Disconnect Bus 514946 b. 3. Trip branch from DRAPER 4 (514933) 138 kV Bus TO SOONRTP4 (514949) 138 kV Bus CKT 1 b. 4. Clear fault at DRAPER 4 (514933) 138 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1091_P4 | a. Apply single-phase fault at WAUKOTP4 (514711) 138 kV Bus b. 1. Run for 16 cycles: b. 2. Trip branch from WAUKOTP4 (514711) 138 kV Bus TO SO4TH 4 (514731) 138 kV Bus CKT 1 b. 3. Trip branch from WAUKOTP4 (514711) 138 kV Bus TO WOODRNG4 (514714) 138 kV Bus CKT 1 b. 4. Run for 10 cycles: b. 5. Trip branch from FRMNTAP4 (514709) 138 kV Bus TO FAIRMON4 (514712) 138 kV Bus CKT 1 b. 6. Trip branch from FRMNTAP4 (514709) 138 kV Bus TO WOODRNG4 (514714) 138 kV Bus CKT 1 b. 7. Trip branch from FRMNTAP4 (514709) 138 kV Bus TO SO4TH 4 (514731) 138 kV Bus CKT 1 b. 8. Clear fault at WAUKOTP4 (514711) 138 kV Bus b. 9. Disconnect Bus WAUKOTP4 (514711) 138 kV b. 10. Disconnect Bus FRMNTAP4 (514709) 138 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1092_P4 | a. Apply single-phase fault at JOHNCO 7 (514809) 345 kV Bus b. 1. Run for 16 cycles: b. 2. Trip branch from PITTSB-7 (510907) 345 kV Bus TO JOHNCO 7 (514809) 345 kV Bus CKT 1 b. 3. Trip branch from JOHNCO 7 (514809) 345 kV Bus TO SUNNYSD7 (515136) 345 kV Bus CKT 1 b. 4. Clear fault at JOHNCO 7 (514809) 345 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1093_P4 | a. Apply single-phase fault at GRACMNT7 (515800) 345 kV Bus b. 1. Run for 16 cycles: b. 2. Trip branch from G16-091-TAP (587744) 345 kV Bus TO GRACMNT7 (515800) 345 kV Bus CKT 1 b. 3. Trip branch from MINCO 7 (514801) 345 kV Bus TO GRACMNT7 (515800) 345 kV Bus CKT 1 b. 4. Clear fault at GRACMNT7 (515800) 345 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1095_P4 | a. Apply single-phase fault at PECANCK7 (515235) 345 kV Bus b. 1. Run for 16 cycles: b. 2. Trip branch from R.S.S.-7 (509782) 345 kV Bus TO PECANCK7 (515235) 345 kV Bus CKT 1 b. 3. Disconnect Bus PECANC21 (515759) 13.8 kV b. 4. Clear fault at PECANCK7 (515235) 345 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1097_P4 | a. Apply single-phase fault at REDBUD 7 (514909) 345 kV Bus b. 1. Run for 16 cycles: b. 2. Trip branch from ARCADIA7 (514908) 345 kV Bus TO REDBUD 7 (514909) 345 kV Bus CKT 2 b. 3. Trip branch from R.S.S.-7 (509782) 345 kV Bus TO REDBUD 7 (514909) 345 kV Bus CKT 1 b. 4. Clear fault at REDBUD 7 (514909) 345 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1098_P4 | a. Apply single-phase fault at FTSMITH8 (515305) 500 kV Bus b. 1. Run for 16 cycles: b. 2. Disconnect Bus FTSMTH31 (515727) 13.8 kV b. 3. Trip branch from 8ANO% (337909) 500 kV Bus TO FTSMITH8 (515305) 500 kV Bus CKT 1 b. 4. Clear fault at FTSMITH8 (515305) 500 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1099_P4 | a. Apply single-phase fault at SEMINOL7 (515045) 345 kV Bus b. 1. Run for 16 cycles: b. 2. Trip branch from PITTSB-7 (510907) 345 kV Bus TO SEMINOL7 (515045) 345 kV Bus CKT 1 b. 3. Disconnect Bus SEMINO21 (515757) 14.4 kV b. 4. Clear fault at SEMINOL7 (515045) 345 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1100_P4 | a. Apply single-phase fault at SOONER 7 (514803) 345 kV Bus b. 1. Run for 16 cycles: b. 2. Trip branch from G15-066T (560056) 345 kV Bus TO SOONER 7 (514803) 345 kV Bus CKT 1 b. 3. Disconnect Bus SOONER 1 (515760) 13.8 kV b. 4. Clear fault at SOONER 7 (514803) 345 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1101_P4 | a. Apply single-phase fault at WWDBORDT (755000) 345 kV Bus CB 384 Stuck b. Clear Fault after 16 cycles: b. 1. Trip branch from WWDBORDT (755000) 345 kV Bus TO BORDER 7 (515458) 345 kV Bus CKT 1 b. 2. Trip branch from BORDER 7 (515458) 345 kV Bus TO CRAWFISH_DR (560022) 345 kV Bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1102_P4 | a. Apply single-phase fault at VBI 5 (515339) 161 kV Bus b. 1. Run for 23.52 cycles, Trip branch from VAN BUR5 (505522) 161 kV Bus TO VBI 5 (515339) 161 kV Bus KT Z1 b. 2. Run for 2.1 cycles, Trip branch from OAKPARK5 (515315) 161 kV Bus TO GERBRTP5 (515326) 161 kV Bus CKT 1 b. 3. Run for 1.2 cycles, Trip branch from MASSARD5 (515343) 161 kV Bus TO WHITESD5 (515341) 161 kV Bus CKT 1 b. 4. Run for 1.5 cycles, Trip branch from HELBERG5 (515327) 161 kV Bus TO PUDDIN 5 (515346) 161 kV Bus CKT 1 b. 5. Run for 3.9 cycles, Trip branch from BRANCH 5 (515316) 161 kV Bus TO GRNDPRT5 (515524) 161 kV Bus CKT 1 b. 6. Run for 11.28 cycles, Trip branch from VAN BUR5 (505522) 161 kV Bus TO VBI 5 (515339) 161 kV Bus KT Z1 b. 7. Run for 2.1 cycles, Trip branch from OAKPARK5 (515315) 161 kV Bus TO GERBRTP5 (515326) 161 kV Bus CKT 1 b. 8. Run for 1.2 cycles, Trip branch from MASSARD5 (515343) 161 kV Bus TO WHITESD5 (515341) 161 kV Bus CKT 1 b. 9. Run for 1.5 cycles, Trip branch from HELBERG5 (515327) 161 kV Bus TO PUDDIN 5 (515346) 161 kV Bus CKT 1 b. 10. Run for 3.9 cycles, Trip branch from BRANCH 5 (515316) 161 kV Bus TO GRNDPRT5 (515524) 161 kV Bus CKT 1 b. 11. Run for 1.62 cycles, Trip branch from ROLANRD2 (515257) 69 kV Bus TO ROLANTP2 (515277) 69 kV Bus CKT 1 b. 12. Run for 9.18 cycles, Trip branch from TAHLQH 5 (512655) 161 kV Bus TO HWY59TP5 (515527) 161 kV Bus CKT 1 b. 13. Run for 4.02 cycles, Trip branch from VAN BUR5 (505522) 161 kV Bus TO VBI 5 (515339) 161 kV Bus KT Z1 b. 14. Run for 4.2 cycles, Trip branch from OAKPARK5 (515315) 161 kV Bus TO GERBRTP5 (515326) 161 kV Bus CKT 1 b. 15. Run for 2.4 cycles, Trip branch from MASSARD5 (515343) 161 kV Bus TO WHITESD5 (515341) 161 kV Bus CKT 1 b. 16. Run for 0.18 cycles, Trip branch from ROLANRD2 (515257) 69 kV Bus TO ROLANTP2 (515277) 69 kV Bus CKT 1 b. 17. Run for 2.82 cycles, Trip branch from HELBERG5 (515327) 161 kV Bus TO PUDDIN 5 (515346) 161 kV Bus CKT 1 b. 18. Run for 6.36 cycles, Trip branch from TAHLQH 5 (512655) 161 kV Bus TO HWY59TP5 (515527) 161 kV Bus CKT 1 b. 19. Run for 1.44 cycles, Trip branch from BRANCH 5 (515316) 161 kV Bus TO GRNDPRT5 (515524) 161 kV Bus CKT 1 b. 20. Run for 19.38 cycles, Disconnect Bus VBI 1 (515769) 13.8 kV b. 21. Run for 23.82 cycles, Trip branch from ROLANRD2 (515257) 69 kV Bus TO ROLANTP2 (515277) 69 kV Bus CKT 1 b. 22. Run for 18.36 cycles, Trip branch from TAHLQH 5 (512655) 161 kV Bus TO HWY59TP5 (515527) 161 kV Bus CKT 1 b. 23. Clear fault at bus VBI 5 (515339) 161 kV Bus b. 24. Drop Load A1 Bus 504191 b. 25. Drop Load A1 Bus 504192 b. 26. Drop Load 1 Bus 515332 b. 27. Drop Load A1 Bus 515332 b. 28. Drop Load A1 Bus 515333 b. 29. Drop Load 1 Bus 515334 b. 30. Drop Load A1 Bus 515337 b. 31. Drop Load A1 Bus 515340 b. 32. Drop Load 1 Bus 515341 b. 33. Drop Load A1 Bus 515346 b. 34. Drop Load 1 Bus 515350 b. 35. Drop Load 1 Bus 515351 b. 36. Drop Load 1 Bus 515360 b. 37. Drop Load 1 Bus 515406 b. 38. Disconnect Bus 504191 b. 39. Disconnect Bus 504192 b. 40. Disconnect Bus 515326 b. 41. Disconnect Bus 515329 b. 42. Disconnect Bus 515332 b. 43. Disconnect Bus 515333 b. 44. Disconnect Bus 515334 b. 45. Disconnect Bus 515337 b. 46. Disconnect Bus 515340 b. 47. Disconnect Bus 515341 b. 48. Disconnect Bus 515346 b. 49. Disconnect Bus 515348 b. 50. Disconnect Bus 515350 b. 51. Disconnect Bus 515351 b. 52. Disconnect Bus 515360 b. 53. Disconnect Bus 515406 b. 54. Disconnect Bus 515524 b. 55. Disconnect Bus 515527 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1103_P4 | a. Apply single-phase fault at WODWRD 2 (514782) 69 kV Bus b. 1. Run for 56.88 cycles, Trip WINDFRM4 (515785) 138 kV Bus TO WOODWRD4 (514785) 138 kV Bus CKT 1 b. 2. Run for 19.22 cycles, Disconnect Bus WOODWR21 (515771) 13.2 kV b. 3. Run for 0.66 cycles, Trip WINDFRM4 (515785) 138 kV Bus TO WOODWRD4 (514785) 138 kV Bus CKT 1 b. 4. Run for 49.74 cycles, Trip WODWRD 2 (514782) 69 kV Bus TO CEDARAV2 (514781) 69 kV Bus CKT 1 b. 5. Run for 7.14 cycles, Trip WINDFRM4 (515785) 138 kV Bus TO WOODWRD4 (514785) 138 kV Bus CKT 1 b. 6. Clear fault at WODWRD 2 (514782) 69 kV Bus c. 1. Apply single-phase fault at WODWRD 2 (514782) 69 kV Bus c. 2. Run for 12.84 cycles, Trip WODWRD 2 (514782) 69 kV Bus TO CEDARAV2 (514781) 69 kV Bus CKT 1 c. 3. Run for 126.6 cycles, Trip WODWRD 2 (514782) 69 kV Bus TO CEDARAV2 (514781) 69 kV Bus CKT 1 c. 4. Clear fault at WODWRD 2 (514782) 69 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1104_P4 | a. Apply single-phase fault at CTNWOOD4 (514827) 138 kV Bus b. 1. Run for 22 cycles, Trip MCELROY4 (515009) 138 kV Bus TO UNVRSTY4 (515181) 138 kV Bus CKT 1 b. 2. Run for 3.96 cycles, Trip KETCH 4 (514834) 138 kV Bus TO KETCHTP4 (514828) 138 kV Bus CKT 1 b. 3. Run for 0.3 cycles, Trip CRESENT4 (515377) 138 kV Bus TO CTNWOOD4 (514827) 138 kV Bus CKT 1 b. 4. Run for 1.74 cycles, Trip KINZE 4 (515008) 138 kV Bus TO KINZEGR4 (512710) 138 kV Bus CKT 1 b. 5. Run for 0.3 cycles, Trip WOODRNG4 (514714) 138 kV Bus TO MARSHL 4 (514733) 138 kV Bus CKT 1 b. 6. Run for 10.38 cycles, Trip ARCADIA4 (514907) 138 kV Bus TO CTNWOOD4 (514827) 138 kV Bus CKT 1 b. 7. Run for 3.3 cycles, Trip MCELROY4 (515009) 138 kV Bus TO UNVRSTY4 (515181) 138 kV Bus CKT 1 b. 8. Run for 3.96 cycles, Trip KETCH 4 (514834) 138 kV Bus TO KETCHTP4 (514828) 138 kV Bus CKT 1 b. 9. Run for 0.3 cycles, Trip CRESENT4 515377) 138 kV Bus TO CTNWOOD4 (514827) 138 kV Bus CKT 1 b. 10. Run for 1.74 cycles, Trip KINZE 4 (515008) 138 kV Bus TO KINZEGR4 (512710) 138 kV Bus CKT 1 b. 11. Run for 0.3 cycles, Trip WOODRNG4 (514714) 138 kV Bus TO MARSHL 4 (514733) 138 kV Bus CKT 1 b. 12. Run for 9.3 cycles, Trip NORTWST4 (514879) 138 kV Bus TO KETCHTP4 (514828) 138 kV Bus CKT 1 b. 13. Run for 1.08 cycles, Trip ARCADIA4 (514907) 138 kV Bus TO CTNWOOD4 (514827) 138 kV Bus CKT 1 b. 14. Run for 5.34 cycles, Trip MCELROY4 (515009) 138 kV Bus TO UNVRSTY4 (515181) 138 kV Bus CKT 1 b. 15. Run for 7.92 cycles, Trip KETCH 4 (514834) 138 kV Bus TO KETCHTP4 (514828) 138 kV Bus CKT 1 b. 16. Run for 0.6 cycles, Trip CRESENT4 (515377) 138 kV Bus TO CTNWOOD4 (514827) 138 kV Bus CKT 1 b. 17. Run for 3.48 cycles, Trip KINZE 4 (515008) 138 kV Bus TO KINZEGR4 (512710) 138 kV Bus CKT 1 b. 18. Run for 0.6 cycles, Trip WOODRNG4 (514714) 138 kV Bus TO MARSHL 4 (514733) 138 kV Bus CKT 1 b. 19. Run for 0.96 cycles, Trip NORTWST4 (514879) 138 kV Bus TO KETCHTP4 (514828) 138 kV Bus CKT 1 b. 20. Run for 19.8 cycles, Trip ARCADIA4 (514907) 138 kV Bus TO CTNWOOD4 (514827) 138 kV Bus CKT 1 b. 21. Run for 37.8 cycles, Trip NORTWST4 (514879) 138 kV Bus TO KETCHTP4 (514828) 138 kV Bus CKT 1 b. 22. Clear fault at CTNWOOD4 ( 514827 ) 138 kV Bus b. 23. Drop Load 1 Bus 514827 b. 24. Drop Load 1 Bus 514829 b. 25. Drop Load 2 Bus 514829 b. 26. Drop Load 1 Bus 514830 b. 27. Drop Load 1 Bus 514831 b. 28. Drop Load 1 Bus 515181 b. 29. Drop Load 1 Bus 515373 b. 30. Drop Load 1 Bus 515466 b. 31. Drop Load 1 Bus 515467 b. 32. Drop Load 1 Bus 521006 b. 33. Disconnect Bus 514733 b. 34. Disconnect Bus 514827 b. 35. Disconnect Bus 514828 b. 36. Disconnect Bus 514829 b. 37. Disconnect Bus 514830 b. 38. Disconnect Bus 514831 b. 39. Disconnect Bus 515008 b. 40. Disconnect Bus 515181 b. 41. Disconnect Bus 515373 b. 42. Disconnect Bus 515466 b. 43. Disconnect Bus 515467 b. 44. Disconnect Bus 521006 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1105_P4 | a. Apply single phase fault at CARPENTER 7 (523823) 345 kV CB OR335 Stuck b. Clear Fault after 16 cycles: b. 1. Trip branch from CARPENTER 7 (523823) 345 kV to FINNEY 7 (523853) 345 kV CKT 1 b. 2. Disconnect Bus CARPENTER 7 (523823) 345 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1106_P4 | a. Apply single phase fault at CROSSROADS 7 (527656) 345 kV CB 6R30 Stuck b. Clear Fault after 16 cycles: b. 1. Trip branch from CROSSROADS 7 (527656) 345 kV to EDDY_CNTY 7 (527802) 345 kV CKT 1 b. 2. Trip branch from TOLK 7 (525549) 345 kV to CROSSROADS 7 (527656) 345 kV CKT 1 b. 3. Trip branch from RSVLT_CC_E 7 (527655) 345 kV to CROSSROADS 7 (527656) 345 kV CKT 1 b. 4. Disconnect Bus RSVLT_CC_E 7 (527655) 345 kV b. 5. Disconnect Bus MILO_WIND 1 (527653) 0.7 kV b. 6. Disconnect Bus RSVLT_GEN1 1 (527651) 0.69 kV b. 7. Disconnect Bus RSVLT_GEN2 1 (527652) 0.69 kV b. 8. Disconnect Bus RSVLT_CC_W 7 (527654) 345 kV b. 9. Disconnect Bus CROSSROADS 7 (527656) 345 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1107_P4 | a. Apply single phase fault at EDDY_CNTY 7 (527802) 345 kV CB 4R00 Stuck b. Clear Fault after 16 cycles: b. 1. Trip branch from EDDY_CNTY 7 (527802) 345 kV to KIOWA 7 (527965) 345 kV CKT 1 b. 2. Trip branch from EDDY_CNTY 7 (527802) 345 kV to CROSSROADS 7 (527656) 345 kV CKT 1 b. 3. Trip three winding transformer from EDDY_TR 1 (527796) 13.2 kV to EDDY_NORTH 6 (527799) kV to EDDY_CNTY 7 (527802) 345 kV CKT1 b. 4. Disconnect Bus EDDY_TR 1 (527796) 13.2 kV b. 5. Disconnect Bus EDDY_CNTY 7 (527802) 345 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1108_P4 | a. Apply single phase fault at EDDY_CNTY 7 (527802) 345 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from EDDY_CNTY 7 (527802) 345 kV to KIOWA 7 (527965) 345 kV CKT 1 b. 2. Trip branch from CROSSROADS 7 (527656) 345 kV to EDDY_CNTY 7 (527802) 345 kV CKT 1 b. 3. Disconnect Bus EDDY_TR 1 (527796) 13.2 kV b. 4. Disconnect Bus EDDY_CNTY 7 (527802) 345 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1109_P4 | a. Apply single phase fault at EDDY_CNTY 7 (527802) 345 kV CB J24 Stuck b. Clear Fault after 16 cycles: b. 1. Trip three winding transformer from EDDY_TR 1 (527796) 13.2 kV to EDDY_NORTH 6 (527799) kV to EDDY_CNTY 7 (527802) 345 kV CKT1 b. 2. Trip branch from CROSSROADS 7 (527656) 345 kV to EDDY_CNTY 7 (527802) 345 kV CKT 1 b. 3. Trip branch from EDDY_CNTY 7 (527802) 345 kV to KIOWA 7 (527965) 345 kV CKT 1 b. 4. Disconnect Bus EDDY_TR 1 (527796) 13.2 kV b. 5. Disconnect Bus EDDY_CNTY 7 (527802) 345 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1110_P4 | a. Apply single phase fault at EDDY_CNTY 7 (527802) 345 kV CB TF Stuck b. Clear Fault after 16 cycles: b. 1. Trip three winding transformer from EDDY_TR 1 (527796) 13.2 kV to EDDY_NORTH 6 (527799) kV to EDDY_CNTY 7 (527802) 345 kV CKT1 b. 2. Trip branch from EDDY_CNTY 7 (527802) 345 kV to KIOWA 7 (527965) 345 kV CKT 1 b. 3. Trip branch from EDDY_CNTY 7 (527802) 345 kV to CROSSROADS 7 (527656) 345 kV CKT 1 b. 4. Trip three winding transformer from EDDY_TR 1 (527796) 13.2 kV to EDDY_NORTH 6 (527799) kV to EDDY_CNTY 7 (527802) 345 kV CKT1 b. 5. Disconnect Bus EDDY_TR 1 (527796) 13.2 kV b. 6. Disconnect Bus EDDY_CNTY 7 (527802) 345 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1111_P4 | a. Apply single phase fault at FINNEY 7 (523853) 345 kV CB OR70 Stuck b. Clear Fault after 16 cycles: b. 1. Trip branch from CARPENTER 7 (523823) 345 kV to FINNEY 7 (523853) 345 kV CKT 1 b. 2. Trip branch from FINNEY 7 (523853) 345 kV to HOLCOMB7 (531449) 345 kV CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1112_P4 | a. Apply single phase fault at HITCHLAND 7 (523097) 345 kV CB 1R15 Stuck b. Clear Fault after 16 cycles: b. 1. Trip branch from HITCHLAND 7 (523097) 345 kV to POTTER_CO 7 (523961) 345 kV CKT 1 b. 2. Disconnect Bus NOBLE_TR 1 (523102) 13.8 kV b. 3. Disconnect Bus NOBLE_WND 3 (523103) 115 kV b. 4. Disconnect Bus GRPLNS-HV4-3 (523130) 115 kV b. 5. Disconnect Bus GRPLNS-HV2-3 (523131) 115 kV b. 6. Disconnect Bus GRPLNS-LV4-1 (523127) 34.5 kV b. 7. Disconnect Bus GRPLNS-LV2-1 (523129) 34.5 kV b. 8. Disconnect Bus GRPLNS-CB4-1 (523124) 34.5 kV b. 9. Disconnect Bus GRPLNS-CB2-1 (523126) 34.5 kV b. 10. Disconnect Bus GRPLNS-WT4-1 (523121) 0.575 kV b. 11. Disconnect Bus GRPLNS-WT2-1 (523123) 0.575 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1113_P4 | a. Apply single phase fault at HITCHLAND 7 (523097) 345 kV CB 1R30 Stuck b. Clear Fault after 16 cycles: b. 1. Trip branch from HITCHLAND 7 (523097) 345 kV to CARPENTER 7 (523823) 345 kV CKT 1 b. 2. Drop Shunt 1 HITCHLAND 7 (523097) 345 kV b. 3. Trip three winding transformer from HITCHLD_TR21 (523094) 13.2 kV to HITCHLAND 6 (523095) kV to HITCHLAND 7 (523097) 345 kV CKT2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1114_P4 | a. Apply single phase fault at HITCHLAND 7 (523097) 345 kV CB 1R75 Stuck b. Clear Fault after 16 cycles: b. 1. Trip branch from BVRCNTY7 (515554) 345 kV to HITCHLAND 7 (523097) 345 kV CKT 2 b. 2. Disconnect Bus NOVUS_WND 1 (523107) 4.16 kV b. 3. Disconnect Bus NOVUS1 1 (523109) 34.5 kV b. 4. Disconnect Bus NOVUS1 3 (523111) 115 kV b. 5. Disconnect Bus NOVUS1_TR1 1 (523110) 13.8 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1115_P4 | a. Apply single phase fault at HOBBS_INT 7 (527896) 345 kV CB 4R240 Stuck b. Clear Fault after 16 cycles: b. 1. Trip branch from HOBBS_INT 7 (527896) 345 kV to KIOWA 7 (527965) 345 kV CKT 1 b. 2. Disconnect Bus HOBBS_TR3 1 (527895) 13.2 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1117_P4 | a. Apply single phase fault at L.E.S.-7 (511468) 345 kV CB 3429B Stuck b. Clear Fault after 16 cycles: b. 1. Trip branch from L.E.S.-7 (511468) 345 kV to O.K.U.-7 (511456) 345 kV CKT 1 b. 2. Trip three winding transformer from LES#5-1 (511411) 13.8 kV to L.E.S.-4 (511467) kV to L.E.S.-7 (511468) 345 kV CKT2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Low voltage ride through fails due to the tripping of G18-115-GEN10 and G18-115-GEN20 units. No cascading was observed and the issue was localised. Model tuning is recommended.
04 - Southeast | 25S | Transfer | Group4_Fault_1118_P4 | a. Apply single phase fault at L.E.S.-7 (511468) 345 kV CB 3433A Stuck b. Clear Fault after 16 cycles: b. 1. Trip branch from L.E.S.-7 (511468) 345 kV to O.K.U.-7 (511456) 345 kV CKT 1 b. 2. Trip branch from L.E.S.-7 (511468) 345 kV to G17-171-TAP (760938) 345 kV CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Low voltage ride through fails due to the tripping of G18-115-GEN10 and G18-115-GEN20 units. No cascading was observed and the issue was localised. Model tuning is recommended.
04 - Southeast | 25S | Transfer | Group4_Fault_1119_P4 | a. Apply single phase fault at L.E.S.-7 (511468) 345 kV CB 3433A_2 Stuck b. Clear Fault after 16 cycles: b. 1. Trip branch from O.K.U.-7 (511456) 345 kV to L.E.S.-7 (511468) 345 kV CKT 1 b. 2. Trip branch from L.E.S.-7 (511468) 345 kV to G17-171-TAP (760938) 345 kV CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Low voltage ride through fails due to the tripping of G18-115-GEN10 and G18-115-GEN20 units. No cascading was observed and the issue was localised. Model tuning is recommended.
04 - Southeast | 25S | Transfer | Group4_Fault_1120_P4 | a. Apply single phase fault at N_LOVING 7 (528185) 345 kV CB 4S105 Stuck b. Clear Fault after 16 cycles: b. 1. Trip three winding transformer from NORTH_LOVNG3 (528182) 115 kV to N_LOVING 7 (528185) kV to N_LOVING TR1 (528186) 13.2 kV CKT1 b. 2. Trip branch from N_LOVING 7 (528185) 345 kV to CHINA_DRAW 7 (528223) 345 kV CKT 1 b. 3. Trip branch from KIOWA 7 (527965) 345 kV to N_LOVING 7 (528185) 345 kV CKT 1 b. 4. Disconnect Bus N_LOVING TR1 (528186) 13.2 kV b. 5. Disconnect Bus N_LOVING 7 (528185) 345 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1121_P4 | a. Apply single phase fault at N_LOVING 7 (528185) 345 kV CB 4S110 Stuck b. Clear Fault after 16 cycles: b. 1. Trip three winding transformer from NORTH_LOVNG3 (528182) 115 kV to N_LOVING 7 (528185) kV to N_LOVING TR1 (528186) 13.2 kV CKT1 b. 2. Trip branch from KIOWA 7 (527965) 345 kV to N_LOVING 7 (528185) 345 kV CKT 1 b. 3. Trip branch from N_LOVING 7 (528185) 345 kV to CHINA_DRAW 7 (528223) 345 kV CKT 1 b. 4. Trip three winding transformer from NORTH_LOVNG3 (528182) 115 kV to N_LOVING 7 (528185) kV to N_LOVING TR1 (528186) 13.2 kV CKT1 b. 5. Disconnect Bus N_LOVING TR1 (528186) 13.2 kV b. 6. Disconnect Bus N_LOVING 7 (528185) 345 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1122_P4 | a. Apply single phase fault at N_LOVING 7 (528185) 345 kV CB 4S120 Stuck b. Clear Fault after 16 cycles: b. 1. Trip branch from N_LOVING 7 (528185) 345 kV to CHINA_DRAW 7 (528223) 345 kV CKT 1 b. 2. Trip branch from KIOWA 7 (527965) 345 kV to N_LOVING 7 (528185) 345 kV CKT 1 b. 3. Trip three winding transformer from NORTH_LOVNG3 (528182) 115 kV to N_LOVING 7 (528185) kV to N_LOVING TR1 (528186) 13.2 kV CKT1 b. 4. Disconnect Bus N_LOVING TR1 (528186) 13.2 kV b. 5. Disconnect Bus N_LOVING 7 (528185) 345 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1123_P4 | a. Apply single phase fault at BATTLEFIELD5 (549959) 161 kV CB 111 Stuck b. Clear Fault after 16 cycles: b. 1. Trip branch from GOLDEN 2 (549911) 69 kV to BATTLEFIELD2 (549979) 69 kV CKT 1 b. 2. Trip branch from DAYTON 2 (549913) 69 kV to BATTLEFIELD2 (549979) 69 kV CKT 1 b. 3. Trip branch from MAIN STREET5 (549958) 161 kV to BATTLEFIELD5 (549959) 161 kV CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1124_P4 | a. Apply single phase fault at O.K.U.-7 (511456) 345 kV CB 3409A Stuck b. Clear Fault after 16 cycles: b. 1. Trip branch from O.K.U.-7 (511456) 345 kV to L.E.S.-7 (511468) 345 kV CKT 1 b. 2. Trip branch from O.K.U.-7 (511456) 345 kV to G18-092-TAP (763215) 345 kV CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1125_P4 | a. Apply single phase fault at POTTER_CO 7 (523961) 345 kV CB 2R05 Stuck b. Clear Fault after 16 cycles: b. 1. Trip branch from HITCHLAND 7 (523097) 345 kV to POTTER_CO 7 (523961) 345 kV CKT 1 b. 2. Trip three winding transformer from POTTER_TR 1 (523957) 13.2 kV to POTTER_CO 6 (523959) kV to POTTER_CO 7 (523961) 345 kV CKT1 b. 3. Disconnect Bus BUFF_DUNES23 (523061) 0.69 kV b. 4. Disconnect Bus SPNSPUR_WND7 (524296) 345 kV b. 5. Disconnect Bus SPNSPUR_GEN1 (524295) 0.69 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1126_P4 | a. Apply single phase fault at BVRCNTY7 (515554) 345 kV CB PRE19S Stuck b. Clear Fault after 16 cycles: b. 1. Trip branch from BVRCNTY7 (515554) 345 kV to HITCHLAND 7 (523097) 345 kV CKT 1 b. 2. Trip branch from BVRCNTY7 (515554) 345 kV to HITCHLAND 7 (523097) 345 kV CKT 2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1128_P4 | a. Apply single phase fault at TUCO_INT 7 (525832) 345 kV CB NR05 Stuck b. Clear Fault after 16 cycles: b. 1. Disconnect Bus TUCO_TR1 1 (525824) 13.2 kV b. 2. Trip branch from CRAWFISH_DR (560022) 345 kV to TUCO_INT 7 (525832) 345 kV CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1129_P4 | a. Apply single phase fault at TUCO_INT 7 (525832) 345 kV CB NR20 Stuck b. Clear Fault after 16 cycles: b. 1. Disconnect Bus TUCO_TR1 1 (525824) 13.2 kV b. 2. Trip branch from CRAWFISH_DR (560022) 345 kV to TUCO_INT 7 (525832) 345 kV CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1130_P4 | a. Apply single phase fault at YOAKUM_345 (526936) 345 kV CB J17 Stuck b. Clear Fault after 16 cycles: b. 1. Trip three winding transformer from YOAKUM 6 (526935) 230 kV to YOAKUM_345 (526936) kV to YOAKUM_TR1 (526937) 13.2 kV CKT1 b. 2. Trip branch from TUCO_INT 7 (525832) 345 kV to YOAKUM_345 (526936) 345 kV CKT 1 b. 3. Trip branch from YOAKUM_345 (526936) 345 kV to HOBBS_INT 7 (527896) 345 kV CKT 1 b. 4. Disconnect Bus YOAKUM_TR1 (526937) 13.2 kV b. 5. Disconnect Bus YOAKUM_345 (526936) 345 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1131_P4 | a. Apply single phase fault at YOAKUM_345 (526936) 345 kV CB J18 Stuck b. Clear Fault after 16 cycles: b. 1. Trip branch from TUCO_INT 7 (525832) 345 kV to YOAKUM_345 (526936) 345 kV CKT 1 b. 2. Trip branch from YOAKUM_345 (526936) 345 kV to HOBBS_INT 7 (527896) 345 kV CKT 1 b. 3. Trip three winding transformer from YOAKUM 6 (526935) 230 kV to YOAKUM_345 (526936) kV to YOAKUM_TR1 (526937) 13.2 kV CKT1 b. 4. Disconnect Bus YOAKUM_TR1 (526937) 13.2 kV b. 5. Disconnect Bus YOAKUM_345 (526936) 345 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1132_P4 | a. Apply single phase fault at YOAKUM_345 (526936) 345 kV CB J18_2 Stuck b. Clear Fault after 16 cycles: b. 1. Trip branch from TUCO_INT 7 (525832) 345 kV to YOAKUM_345 (526936) 345 kV CKT 1 b. 2. Trip branch from YOAKUM_345 (526936) 345 kV to HOBBS_INT 7 (527896) 345 kV CKT 1 b. 3. Disconnect Bus YOAKUM_TR1 (526937) 13.2 kV b. 4. Disconnect Bus YOAKUM_345 (526936) 345 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1133_P4 | a. Apply single phase fault at YOAKUM_345 (526936) 345 kV CB TF Stuck b. Clear Fault after 16 cycles: b. 1. Trip three winding transformer from YOAKUM 6 (526935) 230 kV to YOAKUM_345 (526936) kV to YOAKUM_TR1 (526937) 13.2 kV CKT1 b. 2. Trip branch from YOAKUM_345 (526936) 345 kV to HOBBS_INT 7 (527896) 345 kV CKT 1 b. 3. Trip branch from TUCO_INT 7 (525832) 345 kV to YOAKUM_345 (526936) 345 kV CKT 1 b. 4. Trip three winding transformer from YOAKUM 6 (526935) 230 kV to YOAKUM_345 (526936) kV to YOAKUM_TR1 (526937) 13.2 kV CKT1 b. 5. Disconnect Bus YOAKUM_TR1 (526937) 13.2 kV b. 6. Disconnect Bus YOAKUM_345 (526936) 345 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1134_P4 | a. Apply single-phase fault at BULL SH5 (505460) 161 kV Bus b. 1. Run for 5 cycles, Trip branch from Bus NORFORK5 (505448) 161 kV Bus TO 5SOUTHLAND# (338814) 161 kV Bus CKT 1 b. 2. Clear fault and run for 12 cycles, Disconnect Bus BULL SH5 (505460) 161 kV b. 3. Drop Generator 1 Bus 505462 b. 4. Drop Generator 2 Bus 505464 b. 5. Drop Generator 3 Bus 505466 b. 6. Drop Generator 4 Bus 505466 b. 7. Drop Load 1 Bus 338125 b. 8. Drop Load A1 Bus 338813 b. 9. Drop Load A1 Bus 338814 b. 10. Disconnect Bus 338125 b. 11. Disconnect Bus 338606 b. 12. Disconnect Bus 338607 b. 13. Disconnect Bus 338608 b. 14. Disconnect Bus 338609 b. 15. Disconnect Bus 338813 b. 16. Disconnect Bus 338814 b. 17. Disconnect Bus 505462 b. 18. Disconnect Bus 505464 b. 19. Disconnect Bus 505466 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1135_P4 | a. Apply single-phase fault at BULL SH5 (505460) 161 kV Bus b. 1. Run for 5 Cycles, Trip branch from Bus 5HARRISON.E! (338104) 161 kV To Bus 5SUMMIT (338121) 161 kV CKT 1 b. 2. Clear fault and run for 12 cycles, Disconnect Bus BULL SH5 (505460) 161 kV b. 3. Drop Generator 1 Bus 505462 b. 4. Drop Generator 2 Bus 505464 b. 5. Drop Generator 3 Bus 505466 b. 6. Drop Generator 4 Bus 505466 b. 7. Drop Load 1 Bus 338121 b. 8. Drop Load 1 Bus 338122 b. 9. Drop Load 1 Bus 338124 b. 10. Disconnect Bus 338121 b. 11. Disconnect Bus 338122 b. 12. Disconnect Bus 338123 b. 13. Disconnect Bus 338124 b. 14. Disconnect Bus 505462 b. 15. Disconnect Bus 505464 b. 16. Disconnect Bus 505466 b. 17. Drop Load A1 Bus 338813 b. 18. Disconnect Bus 338813 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1136_P4 | a. Apply single-phase fault at BULL SH5 (505460) 161 kV Bus b. 1. Run for 5 cycles, Trip branch from Bus 5MANSFDMN (300095) 161 kV To Bus 5GAINES (300081) 161 kV CKT 1 b. 2. Clear fault and run for 12 cycles, Disconnect Bus BULL SH5 (505460) 161 kV b. 3. Drop Generator 1 Bus 505462 b. 4. Drop Generator 2 Bus 505464 b. 5. Drop Generator 3 Bus 505466 b. 6. Drop Generator 4 Bus 505466 b. 7. Disconnect Bus 505462 b. 8. Disconnect Bus 505464 b. 9. Disconnect Bus 505466 b. 10. Drop Load A1 Bus 338813 b. 11. Disconnect Bus 338813 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1137_P4 | a. Apply single-phase fault at TABLE R5 (505472) 161 kV b. 1. Run for 5 cycles, Trip branch from Bus BULL SH W5 (505461) 161 kV To Bus 5S.LEAD HILL (338120) 161 kV CKT 1 b. 2. Clear fault and run for 12 cycles, Disconnect Bus TABLE R5 (505472) 161 kV b. 3. Drop Generator 1 Bus 505476 b. 4. Drop Generator 2 Bus 505476 b. 5. Drop Generator 3 Bus 505478 b. 6. Drop Generator 4 Bus 505478 b. 7. Drop Load 1 Bus 300718 b. 8. Drop Load 1 Bus 338120 b. 9. Disconnect Bus 300718 b. 10. Disconnect Bus 338120 b. 11. Disconnect Bus 505473 b. 12. Disconnect Bus 505475 b. 13. Disconnect Bus 505476 b. 14. Disconnect Bus 505478 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1138_P4 | a. Apply single-phase fault at TABLE R5 (505472) 161 kV b. 1. Run for 5 cycles, Open Line From Bus 5RENOHLWTP (300130) 161 kV To Bus 5RIVERSIDE (300805) 161 kV CKT 1 b. 2. Clear fault and run for 12 cycles, Disconnect Bus TABLE R5 (505472) 161 kV b. 3. Drop Generator 1 Bus 505476 b. 4. Drop Generator 2 Bus 505476 b. 5. Drop Generator 3 Bus 505478 b. 6. Drop Generator 4 Bus 505478 b. 7. Disconnect Bus 505473 b. 8. Disconnect Bus 505475 b. 9. Disconnect Bus 505476 b. 10. Disconnect Bus 505478 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1139_P4 | a. Apply single-phase fault at TABLE R5 (505472) 161 kV Run For 5.0 Cycles, Open Line From Bus 5GRANDVIEW% (338099) 161 kV To Bus TABLE R5 (505472) 161 kV CKT 1 b. 2. Clear fault and run for 12 cycles, Disconnect Bus TABLE R5 (505472) 161 kV b. 3. Drop Generator 1 Bus 505476 b. 4. Drop Generator 2 Bus 505476 b. 5. Drop Generator 3 Bus 505478 b. 6. Drop Generator 4 Bus 505478 b. 7. Disconnect Bus 505473 b. 8. Disconnect Bus 505475 b. 9. Disconnect Bus 505476 b. 10. Disconnect Bus 505478 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1140_P4 | a. Apply single-phase fault at TABLE R5 (505472) 161 kV b. 1. Run For 5.0 Cycles, Open Line From Bus NIXA 5 (505496) 161 kV To Bus TABLE R5 (505472) 161 CKT 1 b. 2. Clear fault and run for 12 cycles, Disconnect Bus TABLE R5 (505472) 161 kV b. 3. Drop Generator 1 Bus 505476 b. 4. Drop Generator 2 Bus 505476 b. 5. Drop Generator 3 Bus 505478 b. 6. Drop Generator 4 Bus 505478 b. 7. Disconnect Bus 505473 b. 8. Disconnect Bus 505475 b. 9. Disconnect Bus 505476 b. 10. Disconnect Bus 505478 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1141_P4 | a. Apply single-phase fault at TABLE R5 (505472) 161 kV b. 1. Run for 5 cycles, Open Line From Bus RVS438 5 (547497) 161 kV To TABLE R5 (505472) 161 kV Bus CKT 1 b. 2. Clear fault and run for 12 cycles, Disconnect Bus TABLE R5 (505472) 161 kV b. 3. Drop Generator 1 Bus 505476 b. 4. Drop Generator 2 Bus 505476 b. 5. Drop Generator 3 Bus 505478 b. 6. Drop Generator 4 Bus 505478 b. 7. Disconnect Bus 505473 b. 8. Disconnect Bus 505475 b. 9. Disconnect Bus 505476 b. 10. Disconnect Bus 505478 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1142_P4 | a. Apply single-phase fault at TABLE R5 (505472) 161 kV b. 1. Run for 5 cycles, Trip Three winding transformer from TABLE R5 (505472) 161 kV To Bus TABLE R2 (505474) 69 kV To Bus TBR X1 1 (505473) 13.8 kV CKT 1 b. 2. Run For 12.0 cycles, Trip Three winding transformer from TABLE R5 (505472) 161 kV To Bus TABLE R2 (505474) 69 kV To Bus TBR X2 1 (505475) 13.8 kV CKT 1 b. 3. Clear fault at TABLE R5 (505472) 161 kV b. 4. Disconnect Bus TBR X1 1 (505473) 13.8 kV b. 5. Drop Generator 1 Bus 505476 b. 6. Drop Generator 2 Bus 505476 b. 7. Drop Generator 3 Bus 505478 b. 8. Drop Generator 4 Bus 505478 b. 7. Disconnect Bus 505473 b. 9. Disconnect Bus 505475 b. 10. Disconnect Bus 505476 b. 11. Disconnect Bus 505478 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1143_P4 | a. Apply single-phase fault at BULL SH W5 (505461) 161 kV Bus b. 1. Run for 5 cycles, Trip branch from Bus TABLE R5 (505472) 161 kV To Bus 5CLEVCOV (300718) 161 kV CKT 1 b. 2. Clear fault and run for 12 cycles, Disconnect Bus BULL SH W5 (505461) 161 kV b. 3. Drop Generator 5 Bus 505468 b. 4. Drop Generator 6 Bus 505468 b. 5. Drop Generator 7 Bus 505470 b. 6. Drop Generator 8 Bus 505470 b. 7. Drop Load 1 Bus 300718 b. 8. Drop Load 1 Bus 338120 b. 9. Disconnect Bus 300718 b. 10. Disconnect Bus 338120 b. 11. Disconnect Bus 505468 b. 12. Disconnect Bus 505470 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1144_P4 | a. Apply single-phase fault at BULL SH W5 (505461) 161 kV Bus b. 1. Run for 5 cycles, Trip branch from Bus NORFORK5 (505448) 161 kV To Bus BUFORD 5 (504440) 161 kV CKT 1 b. 2. Clear fault and run for 12 cycles, Disconnect Bus BULL SH W5 (505461) 161 kV b. 3. Drop Generator 5 Bus 505468 b. 4. Drop Generator 6 Bus 505468 b. 5. Drop Generator 7 Bus 505470 b. 6. Drop Generator 8 Bus 505470 b. 7. Drop Load A1 Bus 504440 b. 8. Disconnect Bus 504440 b. 9. Disconnect Bus 505468 b. 10. Disconnect Bus 505470 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1145_P4 | a. Apply single-phase fault at BULL SH W5 (505461) 161 kV Bus Run For 5 Cycles, Trip branch from Bus 5HILLTOP% (338110) 161 kV To Bus BULL SH W5 (505461) 161 kV CKT 1 b. 2. Clear fault and run for 12 cycles, Disconnect Bus BULL SH W5 (505461) 161 kV b. 3. Drop Generator 5 Bus 505468 b. 4. Drop Generator 6 Bus 505468 b. 5. Drop Generator 7 Bus 505470 b. 6. Drop Generator 8 Bus 505470 b. 7. Disconnect Bus 505468 b. 8. Disconnect Bus 505470 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1146_P4 | a. Apply single-phase fault at BATTLEFIELD2 (549979) 69 kV b. 1. Run for 8 cycles: b. 2. Trip branch from GOLDEN 2 (549911) 69 kV Bus TO BATTLEFIELD2 (549979) 69 kV Bus CKT 1 b. 3. Trip branch from DAYTON 2 (549913) 69 kV Bus TO BATTLEFIELD2 (549979) 69 kV Bus CKT 1 b. 4. Clear fault and run for 10 cycles, Trip branch from MAIN STREET5 (549958) 161 kV Bus TO BATTLEFIELD5 (549959) 161 kV Bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1147_P4 | a. Apply single-phase fault at CARPENTER 7 (523823) 345 kV Bus CB OR335 Stuck b. Clear Fault after 21 cycles: b. 1. Trip branch from CARPENTER 7 (523823) 345 kV Bus TO FINNEY 7 (523853) 345 kV Bus CKT 1 b. 2. Clear fault and Disconnect CARPENTER 7 (523823) 345 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1148_P4 | a. Apply single-phase fault at CROSSROADS 7 (527656) 345 kV CB 6R30 Stuck b. Clear Fault after 21 cycles: b. 1. Trip branch from EDDY_CNTY 7 (527802) 345 kV Bus TO CROSSROADS 7 (527656) 345 kV Bus CKT 1 b. 2. Trip branch from TOLK 7 (525549) 345 kV Bus TO CROSSROADS 7 (527656) 345 kV Bus CKT 1 b. 3. Disconnect Bus RSVLT_CC_E 7 (527655) 345 kV b. 4. Disconnect Bus MILO_WIND 1 (527653) 0.70 kV b. 5. Disconnect Bus RSVLT_GEN1 1 (527651) 0.69 kV b. 6. Disconnect Bus RSVLT_GEN2 1 (527652) 0.69 kV b. 7. Disconnect Bus RSVLT_CC_W 7 (527654) 345 kV b. 8. Drop Generator 1 Bus SAGSFT3_2.21 (527605) 0.70 kV b. 9. Drop Generator 1 Bus SAGSFT4_2.21 (527607) 0.70 kV b. 10. Drop Generator 1 Bus SAGSFT1_2.21 (527614) 0.70 kV b. 11. Drop Generator 1 Bus SAGSFT1_2.01 (527615) 0.70 kV b. 12. Drop Generator 1 Bus SAGSFT2_2.21 (527617) 0.70 kV b. 13. Drop Generator 1 Bus SAGSFT2_2.01 (527618) 0.70 kV b. 14. Drop Load 1 Bus SAGA_SCOL 7 (527610) 345 kV b. 15. Drop Load 2 Bus SAGA_SCOL 7 (527610) 345 kV b. 16. Disconnect Bus SAGA_NDCOL 7 (527598) 345 kV b. 17. Disconnect Bus SAGA_SDCOL 7 (527599) 345 kV b. 18. Disconnect Bus SAGA_SMEAS 7 (527600) 345 kV b. 19. Disconnect Bus SAGA_NCOL 7 (527601) 345 kV b. 20. Disconnect Bus SAGANCOL1 1 (527602) 34.5 kV b. 21. Disconnect Bus SAGANCOL2 1 (527603) 34.5 kV b. 22. Disconnect Bus GRDXFR3 1 (527604) 0.50 kV b. 23. Disconnect Bus SAGSFT3_2.21 (527605) 0.70 kV b. 24. Disconnect Bus GRDXFR4 1 (527606) 0.50 kV b. 25. Disconnect Bus SAGSFT4_2.21 (527607) 0.70 kV b. 26. Disconnect Bus SUB BUS #3 1 (527608) 34.5 kV b. 27. Disconnect Bus SUB BUS #4 1 (527609) 34.5 kV b. 28. Disconnect Bus SAGA_SCOL 7 (527610) 345 kV b. 29. Disconnect Bus SAGASCOL1 1 (527611) 34.5 kV b. 30. Disconnect Bus SAGASCOL2 1 (527612) 34.5 kV b. 31. Disconnect Bus GRDXFR1 1 (527613) 0.50 kV b. 32. Disconnect Bus SAGSFT1_2.21 (527614) 0.70 kV b. 33.Disconnect Bus SAGSFT1_2.01 (527615) 0.70 kV b. 34. Disconnect Bus GRDXFR2 1 (527616) 0.50 kV b. 35. Disconnect Bus SAGSFT2_2.21 (527617) 0.70 kV b. 36. Disconnect Bus SAGSFT2_2.01 (527618) 0.70 kV b. 37. Disconnect Bus SAGA_NCLTR31 (527621) 13.8 kV b. 38. Disconnect Bus SAGA_NCLTR41 (527622) 13.8 kV b. 39. Disconnect Bus SAGA_SCLTR11 (527623) 13.8 kV b. 40. Disconnect Bus SAGA_SCLTR21 (527624) 13.8 kV b. 41. Disconnect Bus SUB BUS #1 (527628) 34.5 kV b. 42. Disconnect Bus SUB BUS #2 (527629) 34.5 kV b. 43. Disconnect Bus CROSSROADS 7 (527656) 345 kV b. 44. Disconnect Bus RSVLT_WIND11 (527658) 34.5 kV b. 45. Disconnect Bus RSVLT_WIND21 (527659) 34.5 kV b. 46. Disconnect Bus RSVLT_COL1 1 (527660) 34.5 kV b. 47. Disconnect Bus RSVLT_COL2 1 (527661) 34.5 kV b. 48. Disconnect Bus RSVLT_TR1 1 (527662) 13.2 kV b. 49. Disconnect Bus RSVLT_TR2 1 (527663) 13.2 kV b. 50. Disconnect Bus RSVLT_COL1 7 (527666) 345 kV b. 51. Disconnect Bus RSVLT_COL2 7 (527667) 345 kV b. 52. Disconnect Bus MILO_CB (577120) 34.5 kV b. 53. Disconnect Bus MILO_WND (577121) 34.5 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1150_P4 | a. Apply single-phase fault at CHINA_DRAW 7 (528223) 345 kV Bus CB 4T805 Stuck b. Clear Fault after 16 cycles: b. 1. Trip branch from CHINA_DRAW 7 (528223) 345 kV Bus TO PHANTOM 7 (528015) 345 kV Bus CKT 1 b. 2. Disconnect Bus CHINA_DRAW 1 (528219) 13.2 kV b. 3. Disconnect Bus CARPENTER 7 (523823) 345 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1151_P4 | a. Apply single-phase fault at CHINA_DRAW 7 (528223) 345 kV Bus CB TF#### Stuck b. 1. Run for 5 cycles, Disconnect Bus CHINA_DRAW 1 (528219) 13.2 kV b. 2. Run for 11 cycles, Trip branch from CHINA_DRAW 7 (528223) 345 kV Bus TO N_LOVING 7 (528185) 345 kV Bus CKT 1 b. 3. Clear fault and run for 5 cycles, Trip branch from CHINA_DRAW 7 (528223) 345 kV Bus TO PHANTOM 7 (528015) 345 kV Bus CKT 1 b. 4. Disconnect Bus CHINA_DRAW 1 (528219) 13.2 kV b. 5. Disconnect Bus CARPENTER 7 (523823) 345 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1152_P4 | a. Apply single-phase fault at CHINA_DRAW 7 (528223) 345 kV Bus CB J27#### Stuck b. 1. Run for 16 cycles, Disconnect Bus CHINA_DRAW 1 (528219) 13.2 kV b. 2. Clear fault and run for 5 cycles: b. 3. Trip branch from CHINA_DRAW 7 (528223) 345 kV Bus TO N_LOVING 7 (528185) 345 kV Bus CKT 1 b. 4. Trip branch from CHINA_DRAW 7 (528223) 345 kV Bus TO PHANTOM 7 (528015) 345 kV Bus CKT 1 b. 5. Disconnect Bus CHINA_DRAW 1 (528219) 13.2 kV b. 6. Disconnect Bus CARPENTER 7 (523823) 345 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1153_P4 | a. Apply single-phase fault at EDDY_CNTY 7 (527802) 345 kV Bus CB 4R00 Stuck b. 1. Run for 16 cycles, Trip branch from EDDY_CNTY 7 (527802) 345 kV Bus TO KIOWA 7 (527965) 345 kV Bus CKT 1 b. 2. Clear fault and run for 5 cycles, Trip branch from EDDY_CNTY 7 (527802) 345 kV Bus TO CROSSROADS 7 (527656) 345 kV Bus CKT 1 b. 3. Disconnect Bus EDDY_TR 1 (527796) 13.2 kV b. 4. Disconnect Bus EDDY_CNTY 7 (527802) 345 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1154_P4 | a. Apply single-phase fault at EDDY_CNTY 7 (527802) 345 kV Bus CB J24#### Stuck b. 1. Run for 16 cycles, Disconnect Bus EDDY_TR 1 (527796) 13.2 kV b. 2. Clear fault and run for 5 cycles: b. 3. Trip branch from EDDY_CNTY 7 (527802) 345 kV Bus TO CROSSROADS 7 (527656) 345 kV Bus CKT 1 b. 4. Trip branch from EDDY_CNTY 7 (527802) 345 kV Bus TO KIOWA 7 (527965) 345 kV Bus CKT 1 b. 5. Disconnect Bus EDDY_TR 1 (527796) 13.2 kV b. 6. Disconnect Bus EDDY_CNTY 7 (527802) 345 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1155_P4 | a. Apply single-phase fault at EDDY_CNTY 7 (527802) 345 kV Bus CB TF#### Stuck b. 1. Run for 5 cycles, Disconnect Bus EDDY_TR 1 (527796) 13.2 kV b. 2. Run for 11 cycles, Trip branch from EDDY_CNTY 7 (527802) 345 kV Bus TO CROSSROADS 7 (527656) 345 kV Bus CKT 1 b. 3. Clear fault and run for 5 cycles, Trip branch from EDDY_CNTY 7 (527802) 345 kV Bus TO KIOWA 7 (527965) 345 kV Bus CKT 1 b. 4. Disconnect Bus EDDY_TR 1 (527796) 13.2 kV b. 5. Disconnect Bus EDDY_CNTY 7 (527802) 345 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1156_P4 | a. Apply single-phase fault at FINNEY 7 (523853) 345 kV Bus CB OR70 Stuck b. Clear Fault after 21 cycles: b. 1. Trip branch from HOLCOMB7 (531449) 345 kV Bus TO FINNEY 7 (523853) 345 kV Bus CKT 1 b. 2. Trip branch from CARPENTER 7 (523823) 345 kV TO FINNEY 7 (523853) 345 kV Bus CKT 1 b. 3. Disconnect Bus 523853 b. 4. Disconnect Bus 599950 b. 5. Disconnect Bus 599951 b. 6. Disconnect Bus 523118 b. 7. Disconnect Bus 523114 b. 8. Disconnect Bus 523115 b. 9. Disconnect Bus 523116 b. 10. Disconnect Bus 523117 b. 11. Drop Generator 1 Bus 523061 b. 12. Drop Generator 1 Bus 523062 b. 13. Disconnect Bus 523061 b. 14. Disconnect Bus 523062 b. 15. Disconnect Bus 523063 b. 16. Disconnect Bus 523064 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1157_P4 | a. Apply single-phase fault at HITCHLAND 7 (523097) 345 kV Bus CB 1R75 Stuck b. Clear Fault after 21 cycles: b. 1. Trip branch from HITCHLAND 7 (523097) 345 kV Bus TO BVRCNTY7 (515554) 345 kV Bus CKT 2 b. 2. Disconnect Bus 523112 b. 3. Disconnect Bus 523111 b. 4. Disconnect Bus 523109 b. 5. Disconnect Bus 523107 b. 6. Disconnect Bus 523110 b. 7. Drop Generator 1 Bus 523107 b. 8. Drop Load A1 Bus 523107 b. 9. Drop Generator 1 Bus 560585 b. 10. Drop Generator 1 Bus 560586 b. 11. Disconnect Bus 560577 b. 12. Disconnect Bus 560582 b. 13. Disconnect Bus 560585 b. 14. Disconnect Bus 560583 b. 15. Disconnect Bus 560586 b. 16. Disconnect Bus 560578 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1158_P4 | a. Apply single-phase fault at HOBBS_INT 7 (527896) 345 kV Bus CB 4R240 Stuck b. Clear Fault after 21 cycles: b. 1. Trip branch from HOBBS_INT 7 (527896) 345 kV Bus TO KIOWA 7 (527965) 345 kV Bus CKT 1 b. 2. Trip branch from HOBBS_INT 7 (527896) 345 kV Bus TO YOAKUM_345 (526936) 345 kV Bus CKT 1 b. 3. Disconnect Bus HOBBS_TR3 1 (527895) 13.2 kV b. 4. Disconnect Bus HOBBS_INT 7 (527896) 345 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1159_P4 | a. Apply single-phase fault at POTTER_CO 7 (523961) 345 kV Bus CB 2R05 Stuck b. Clear Fault after 21 cycles: b. 1. Trip branch from HITCHLAND 7 (523097) 345 kV Bus TO POTTER_CO 7 (523961) 345 kV Bus CKT 1 b. 2. Disconnect bus 523957 b. 3. Disconnect bus 523957 b. 4. Disconnect bus 523961 b. 5. Disconnect bus 524296 b. 6. Disconnect bus 524299 b. 7. Disconnect bus 524298 b. 8. Disconnect bus 524294 b. 9. Disconnect bus 524295 b. 10. Disconnect bus 524297 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1160_P4 | a. Apply single-phase fault at YOAKUM_345 (526936) 345 kV Bus CB J18#### Stuck b. 1. Run for 16 cycles, Trip branch from YOAKUM_345 (526936) 345 kV Bus TO TUCO_INT 7 (525832) 345 kV Bus CKT 1 b. 2. Clear fault and run for 5 cycles, Tri branch from YOAKUM_345 (526936) 345 kV Bus TO HOBBS_INT 7 (527896) 345 kV Bus CKT 1 b. 3. Disconnect Bus YOAKUM_TR1 (526937) 13.2 kV b. 4. Disconnect Bus YOAKUM_345 (526936) 345 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1161_P4 | a. Apply single-phase fault at YOAKUM_345 (526936) 345 kV Bus CB TF##### Stuck b. 1. Run for 5 cycles, Disconnect Bus YOAKUM_TR1 (526937) 13.2 kV b. 2. Run for 11 cycles, Trip branch from YOAKUM_345 (526936) 345 kV Bus TO HOBBS_INT 7 (527896) 345 kV Bus CKT 1 b. 3. Clear fault and run for 5 cycles, Trip branch from YOAKUM_345 (526936) 345 kV Bus TO TUCO_INT 7 (525832) 345 kV Bus CKT 1 b. 4. Disconnect Bus YOAKUM_345 (526936) 345 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1162_P4 | a. Apply single-phase fault at YOAKUM_345 (526936) 345 kV Bus CB J17#### Stuck b. 1. Run for 16 cycles, Disconnect Bus YOAKUM_TR1 (526937) 13.2 kV b. 2. Clear fault and run for 5 cycles: b. 3. Trip branch from YOAKUM_345 (526936) 345 kV Bus TO TUCO_INT 7 (525832) 345 kV Bus CKT 1 b. 4. Trip branch from YOAKUM_345 (526936) 345 kV Bus TO HOBBS_INT 7 (527896) 345 kV Bus CKT 1 b. 5. Disconnect Bus YOAKUM_345 (526936) 345 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1163_P4 | a. Apply single-phase fault at TUCO_INT 7 (525832) 345 kV Bus CB NR20 Stuck b. 1. Run for 5 cycles, Disconnect Bus TUCO_TR1 1 (525824) 13.2 kV b. 2. Clear fault and run for 11 cycles, Trip branch from TUCO_INT 7 (525832) 345 kV Bus TO CRAWFISH_DR (560022) 345 kV Bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 763084 [G18-073-GEN20.6600]
04 - Southeast | 25S | Transfer | Group4_Fault_1164_P4 | a. Apply single-phase fault at MUSTANG 3 (527146) 115 kV Bus b. 1. Run for 5 cycles, Disconnect Bus MUSTANG_2 1 (527162) 13.2 kV b. 2. Clear fault and run for 11 cycles, Trip branch from SEAGRAVES 3 (527202) 115 kV Bus TO MUSTANG 3 (527146) 115 kV Bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1165_P4 | a. Apply SLG fault at NICHOLS 6 (524044) 230 kV Bus b. Clear Fault after 21 cycles: b. 1. Trip branch from NICHOLS (523978) 230 kV Bus TO NICHOLS 6 (524044) 230 kV Bus CKT 2 b. 2. Trip branch from HUTCHISON 6 (523551) 230 kV Bus TO NICHOLS 6 (524044) 230 kV Bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1167_P4 | a. Apply single-phase fault at POTTER_CO 6 (523959) 230 kV Bus b. Clear Fault after 21 cycles: b. 1. Trip branch from POTTER_CO 6 (523959) 230 kV Bus TO BUSHLAND 6 (524267) 230 kV Bus CKT 1 b. 2. Trip branch from POTTER_CO 6 (523959) 230 kV Bus TO ROLLHILLS 6 (524010) 230 kV Bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1168_P4 | a. Apply single-phase fault at YOAKUM 6 (526935) 230 kV Bus b. 1. Run for 5 cycles, Disconnect Bus YOAKUM_TR1 1 (526931) 13.2 kV b. 2. Clear fault and run for 11 cycles, Trip branch from YOAKUM 6 (526935) 230 kV Bus TO NEEDMORE 6 (525586) 230 kV Bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1169_P4 | a. Apply single-phase fault at TUCO_INT 7 (525832) 345 kV Bus b. Clear Fault after 21 cycles: b. 1. Trip branch from TUCO_INT 7 (525832) 345 kV Bus TO CRAWFISH_DR (560022) 345 kV Bus CKT 1 b. 2. Disconnect Bus TUCO_TR1 1 (525824) 13.2 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1170_P4 | a. Apply single-phase fault at TUCO_INT 7 (525832) 345 kV Bus b. Clear Fault after 21 cycles: b. 1. Trip branch from TUCO_INT 7 (525832) 345 kV Bus TO CRAWFISH_DR (560022) 345 kV Bus CKT 1 b. 2. Disconnect Bus TUCO_TR2 1 (525825) 13.2 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1171_P4 | a. Apply single-phase fault at WHEELER 6 (523777) 230 kV Bus b. 1. Run for 21.0 Cycles: b. 2. WHEELER 6 (523777) 230 kV Bus TO STLN-DEMARC6 (523779) 230 kV Bus CKT 1 b. 3. Disconnect Bus 523777 b. 4. Disconnect Bus 523774 b. 5. Clear Fault Bus 523777 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1172_P4 | a. Apply single-phase fault at TUCO_INT 7 (525832) 345 kV Bus b. 1. Run for 5 cycles, Disconnect Bus TUCO_TR2 1 (525825) 13.2 kV b. 2. Clear fault and run for 11 cycles, Trip branch from TUCO_INT 7 (525832) 345 kV Bus TO CRAWFISH_DR (560022) 345 kV Bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 763084 [G18-073-GEN20.6600]
04 - Southeast | 25S | Transfer | Group4_Fault_1173_P4 | a. Apply fault at bus HITCHLAND 7 (523097) 345 kV b. 1. Run for 5.0 cycles, Disconnect bus 523091 b. 2. Run for 11.0 cycles, Disconnect bus 523091 b. 3. Clear fault bus 523097 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1174_P4 | a. Apply Fault at Bus WHEELER 6 (523777) 230 kV b. 1. Run for 5 cycles, Disconnect Bus 523774 b. 2. Run for 11 cycles: b. 3. Disconnect Bus 523777 b. 4. Disconnect Bus 523774 b. 5. Clear Fault Bus 523777 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1175_P4 | a. Apply single-phase fault at POTTER_CO 7 (523961) 345 kV Bus b. 1. Run for 5 cycles, Disconnect Bus POTTER_TR 1 (523957) 13.2 kV b. 2. Clear fault and run for 11 cycles, Disconnect Bus POTTER_TR 1 (523957) 13.2 kV b. 3. Run for 5 cycles: b. 4. Trip branch from HITCHLAND 7 (523097) 345 kV Bus TO POTTER_CO 7 (523961) 345 kV Bus CKT 1 b. 5. Disconnect bus 523957 b. 6. Disconnect bus 523961 b. 7. Disconnect bus 524296 b. 8. Disconnect bus 524299 b. 9. Disconnect bus 524298 b. 10. Disconnect bus 524294 b. 11. Disconnect bus 524295 b. 12. Disconnect bus 524297 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1176_P4 | a. Apply single-phase fault at BUSHLAND 6 (524267) 230 kV b. 1. Run for 5 cycles, Drop Shunt 1 BUSHLAND 6 (524267) 230 kV b. 2. Run for 11 cycles: b. 3. Disconnect bus 524267 b. 4. Disconnect bus 524285 b. 5. Disconnect bus 524287 b. 6. Clear fault at bus 524267 b. 7. Disconnect Bus 524263 b. 8. Disconnect Bus 524275 b. 9. Disconnect Bus 524276 b. 10. Disconnect Bus 524289 b. 11. Disconnect Bus 524290 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1177_P4 | a. Apply single-phase fault at SWISHER 6 (525213) 230 kV b. 1. Run for 5 cycles, Drop Shunt 1 SWISHER 6 (525213) 230 kV b. 2. Clear fault and run for 11 cycles, Trip branch from SWISHER 6 (525213) 230 kV Bus TO TUCO_INT 6 (525830) 230 kV Bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1178_P4 | a. Apply single-phase fault at TUCO_INT 6 (525830) 230 kV b. 1. Run for 5 cycles, Drop Shunt 1 TUCO_INT 6 (525830) 230 kV b. 2. Run for 11 cycles: b. 3. Disconnect bus TUCO_TR3 1 (525819) 13.2 kV b. 4. Clear fault at bus TUCO_INT 6 (525830) 230 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1179_P4 | a. Apply single-phase fault at BUSHLAND 6 (524267) 230 kV Bus b. Clear Fault after 5 cycles: b. 1. Trip branch from BUSHLAND 6 (524267) 230 kV Bus TO WILDOR2_JUS6 (524290) 230 kV Bus CKT 1 b. 2. Drop Shunt 1 BUSHLAND 6 (524267) 230 kV Bus b. 3. Disconnect Bus BSHLND_TR1 1 (524263) 13.2 kV b. 4. Disconnect Bus WILDORA_GEN1 (524285) 0.69 kV b. 5. Disconnect Bus GS-PHWD_GEN1 (524287) 0.69 kV b. 6. Trip branch from BUSHLAND 6 (524267) 230 kV Bus TO POTTER_CO 6 (523959) 230 kV Bus CKT 1 b. 7. Clear Fault after 16 cycles: b. 8. Trip branch from BUSHLAND 6 (524267) 230 kV Bus TO DEAFSMITH 6 (524623) 230 kV Bus CKT 1 b. 9. Disconnect Bus WILDOR_WND 1 (524275) 34.5 kV b. 10. Disconnect Bus WILDOR_WND 6 (524276) 230 kV b. 11. Disconnect Bus GS-PHWDRNCH1 (524289) 34.5 kV b. 12. Disconnect Bus WILDOR2_JUS6 (524290) 230 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1182_P4 | a. Apply single-phase fault at HARRNG_EST 6 (523979) 230 kV Bus b. Clear Fault after 16 cycles: b. 1. Trip branch from HARRNG_EST 6 (523979) 230 kV Bus TO PRINGLE 6 (523267) 230 kV Bus CKT 1 b. 2. Trip branch from HARRNG_EST 6 (523979) 230 kV Bus TO POTTER_CO 6 (523959) 230 kV Bus CKT 1 b. 3. Disconnect Bus HARRNG_EST 6 (523979) 230 kV b. 4. Disconnect Bus HARRNGTON3 1 (523973) 24 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1184_P4 | a. Apply single-phase fault at 531449 b. 1. Run For 12.0 Cycles, Open Line From Bus 531449 To Bus 531465 CKT 1 b. 2. Clear Fault Bus 531449 b. 3. Open Line From Bus 523853 To Bus 531449 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1185_P4 | a. Apply single-phase fault at 520814 b. 1. Run For 6.0 Cycles b. 2. Open Line From Bus 520864 To Bus 520900 CKT 1 b. 3. Open Line From Bus 520912 To Bus 520900 CKT 1 b. 4. Open Line From Bus 520923 To Bus 520912 CKT 1 b. 5. Run For 9.0 Cycles b. 6. Open Line From Bus 520814 To Bus 520422 CKT 1 b. 7. Open Line From Bus 520422 To Bus 520473 CKT 1 b. 8. Open Line From Bus 520473 To Bus 520867 CKT 1 b. 9. Open Line From Bus 520888 To Bus 520510 CKT 1 b. 10. Open Line From Bus 520867 To Bus 520510 CKT 1 b. 11. Clear Fault Bus 520814 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1187_P4 | a. Apply single-phase fault at 520814 b. 1. Run For 6.0 Cycles, Open Line From Bus 520814 To Bus 521129 CKT 1 b. 1. Clear fault and run For 9.0 Cycles, Open Line From Bus 511477 To Bus 520814 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1188_P4 | a. Apply single-phase fault at 520917 b. 1. Run For 6.0 Cycles b. 2. Open Line From Bus 520400 To Bus 520842 CKT 1 b. 3. Run For 9.0 Cycles b. 4. Disconnect Bus 514946 b. 5. Open Line From Bus 520917 To Bus 520975 CKT 1 b. 6. Clear Fault Bus 520917 b. 7. Drop Load 1 Bus 520400 b. 8. Drop Load 1 Bus 520975 b. 9. Disconnect Bus 520400 b. 10. Disconnect Bus 520975 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1189_P4 | a. Apply single-phase fault at 520920 b. 1. Run For 6.0 Cycles b. 2. Open Line From Bus 520920 To Bus 520922 CKT 1 b. 3. Drop Generator 1 Bus 521145 b. 4. Disconnect Bus 520922 b. 5. Disconnect Bus 521141 b. 6. Disconnect Bus 521144 b. 7. Disconnect Bus 521145 b. 8. Disconnect Bus 521151 b. 9. Run For 9.0 Cycles Print 0 Plot 3 Crtplt 0 b. 10. Open Line From Bus 520957 To Bus 520999 CKT 1 b. 11. Clear Fault Bus 520920 b. 12. Open Line From Bus 520920 To Bus 520957 CKT 1 b. 13. Drop Load 1 Bus 520957 b. 14. Disconnect Bus 520957 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1190_P4 | a. Apply single-phase fault at 520948 b. 1. Run For 6.0 Cycles, Open Line From Bus 510887 To Bus 520968 CKT 1 b. 2. Run For 9.0 Cycles b. 3. Open Line From Bus 520948 To Bus 520918 CKT 1 b. 4. Open Line From Bus 505602 To Bus 521049 CKT 1 b. 5. Clear Fault Bus 520948 b. 6. Drop Load 1 Bus 515370 b. 7. Drop Load 1 Bus 515568 b. 8. Drop Load 1 Bus 520463 b. 9. Drop Load 1 Bus 520483 b. 10. Drop Load 1 Bus 520497 b. 11. Drop Load 1 Bus 520918 b. 12. Drop Load 1 Bus 521077 b. 13. Drop Load 1 Bus 521115 b. 14. Disconnect Bus 515370 b. 15. Disconnect Bus 515568 b. 16. Disconnect Bus 520463 b. 17. Disconnect Bus 520483 b. 18. Disconnect Bus 520497 b. 19. Disconnect Bus 520826 b. 20. Disconnect Bus 520884 b. 21. Disconnect Bus 520918 b. 22. Disconnect Bus 521049 b. 23. Disconnect Bus 521077 b. 24. Disconnect Bus 521098 b. 25. Disconnect Bus 521115 b. 26. Drop Load 1 Bus 520411 b. 27. Drop Load 1 Bus 520874 b. 28. Drop Load 1 Bus 520968 b. 29. Drop Load 1 Bus 521036 b. 30. Disconnect Bus 520411 b. 31. Disconnect Bus 520874 b. 32. Disconnect Bus 520968 b. 33. Disconnect Bus 521036 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1192_P4 | a. Apply single-phase fault at MARIETA4 (520988) 138 kV CB 472 Stuck b. 1. Run for 6 cycles, Trip branch from CANEYCK4 (515150) 138 kV To Bus 521067 CKT 1 b. 2 Run For 9 cycles: b. 3. Trip branch from 5MARIETA4 (520988) 138 kV To Bus TEXOMAJ4 (521061)138 kV CKT 1 b. 4. Trip branch from 520981 To Bus 520939 CKT 1 b. 5. Clear Fault Bus 520988 b. 6. Drop Load 1 Bus 520455 b. 7. Drop Load 1 Bus 520487 b. 8. Drop Load 1 Bus 520488 b. 9. Drop Load 1 Bus 520511 b. 10. Drop Load 1 Bus 520901 b. 11. Drop Load 1 Bus 521038 b. 12. Drop Load 1 Bus 521061 b. 13. Drop Load 1 Bus 521066 b. 14. Disconnect Bus 520455 b. 15. Disconnect Bus 520467 b. 16. Disconnect Bus 520487 b. 17. Disconnect Bus 520488 b. 18. Disconnect Bus 520511 b. 19. Disconnect Bus 520901 b. 20. Disconnect Bus 520939 b. 21. Disconnect Bus 520972 b. 22. Disconnect Bus 521038 b. 23. Disconnect Bus 521061 b. 24. Disconnect Bus 521066 b. 25. Disconnect Bus 521067 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1193_P4 | a. Apply single-phase fault at NOELSW 4 (520430) 138 kV Bus b. 1. Run for 6 cycles, Trip branch from DRIFTWD4 (521200) 138 kV Bus TO CHRKCTY4 (520431) 138 kV Bus CKT 1 b. 2. Run for 9 cycles: b. 3. Trip branch from ROSEVLY4 (520436) 138 kV Bus TO NOELSW 4 (520430) 138 kV Bus CKT 1 b. 4. Trip branch from NOELSW 4 (520430) 138 kV Bus TO SALTPLN4 (520437) 138 kV Bus CKT 1 b. 5. Clear fault at NOELSW 4 (520430) 138 kV Bus b. 6. Drop Load 1 Bus 520431 b. 7. Drop Load 1 Bus 520437 b. 8. Drop Load 2 Bus 520437 b. 9. Disconnect Bus 520431 b. 10. Disconnect Bus 520437 b. 11. Drop Load 1 Bus 520436 b. 12. Drop Load 1 Bus 520601 b. 13. Disconnect Bus 520436 b. 14. Disconnect Bus 520601 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1194_P4 | a. Apply single-phase fault at PAYNESW4 (520888) 138 kV Bus b. 1. Run for 6 cycles, Trip branch from DOVERSW4 (520882) 138 kV Bus TO OKEENE 4 (521016) 138 kV Bus CKT 1 b. 2. Clear fault and run for 9 cycles, Trip branch MOORLND4 (520999) 138 kV Bus TO PIC4 (520425) 138 kV Bus CKT 1 Bus CKT 1 b. 3. Drop Load 1 Bus 520425 b. 4. Drop Load 1 Bus 520507 b. 5. Disconnect Bus 520425 b. 6. Disconnect Bus 520848 b. 7. Disconnect Bus 520507 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1195_P4 | a. Apply single-phase fault at PAYNESW4 (520888) 138 kV Bus b. 1. Run for 6 cycles, Trip branch from OU SW 4 (521104) 138 kV Bus TO COLE 4 (520861) 138 kV Bus CKT 1 b. 2. Run for 9 cycles: b. 3. Trip PAYNESW4 (520888) 138 kV Bus TO NAPLSTP4 (520510) 138 kV Bus CKT 1 b. 4. Trip PAYNESW4 (520888) 138 kV Bus TO CRINER 4 (520868) 138 kV Bus CKT 1 b. 5. Trip CORNVIL4 (511449) 138 kV Bus TO CORN TP4 (520867) 138 kV Bus CKT 1 b. 6. Trip ANADARK4 (520814) 138 kV Bus TO CLVLDSW4 (520508) 138 kV Bus CKT 1 b. 7. Clear fault at PAYNESW4 (520888) 138 kV Bus Drop Load 1 at 520547 Drop Load 2 at 520547 Drop Load 1A at 520604 Disconnect Bus 520422 Disconnect Bus 520510 Disconnect Bus 520867 Disconnect Bus 520547 Drop Load 1 Bus 520861 Drop Load 1 Bus 520868 Disconnect Bus 520861 Disconnect Bus 520868 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1196_P4 | a. Apply single-phase fault at WASHITA4 (521089) 138 kV Bus b. 1. Run for 6 cycles, Trip branch CLINTJC4 (511485) 138 kV Bus TO CLINTON4 (520856) 138 kV Bus CKT 1 b. 2. Run for 9 cycles: b. 3. Trip branch GRACMNT4 (515802) 138 kV Bus TO WASHITA4 (521089) 138 kV Bus CKT 1 b. 3. Trip branch ONEY 4 (521017) 138 kV Bus TO WASHITA4 (521089) 138 kV Bus CKT 1 b. 4. Clear fault at WASHITA4 (521089) 138 kV Bus b. 5. Drop Load 1 Bus 520468 b. 6. Drop Load 1 Bus 520503 b. 7. Drop Load 1 Bus 520856 b. 8. Drop Load 1 Bus 520950 b. 9. Drop Load 1 Bus 521010 b. 10. Drop Load 2 Bus 521010 b. 11. Drop Load 1 Bus 521017 b. 12. Drop Load 1 Bus 521050 b. 13. Drop Load 1 Bus 521092 b. 14. Disconnect Bus 520468 b. 15. Disconnect Bus 520503 b. 16. Disconnect Bus 520827 b. 17. Disconnect Bus 520856 b. 18. Disconnect Bus 520950 b. 19. Disconnect Bus 521010 b. 20. Disconnect Bus 521017 b. 21. Disconnect Bus 521050 b. 22. Disconnect Bus 521092 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1197_P4 | a. Apply single-phase fault at WASHITA4 (521089) 138 kV Bus b. 1. Run for 6 cycles, Trip branch GRACMNT4 (515802) 138 kV Bus TO WASHITA4 (521089) 138 kV Bus CKT 1 b. 2. Clear fault and run for 9 cycles, Trip branch GRACMNT4 (515802) 138 kV Bus TO WASHITA4 (521089) 138 kV Bus CKT 2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1198_P4 | a. Apply single-phase fault at ANADARK4 (520814) 138 kV Bus b. 1. Run for 6 cycles: b. 2. Trip branch from COMANCH4 (520864) 138 kV Bus TO EMPIRE 4 (520900) kV 138 kV Bus CKT 1 b. 3. Trip Three winding transformer from FLETCH-4 (520912) 138 kV TO FLETCHR2 (520911) 69 kV TO FLCHTERT (521168) 13.8 kV CKT 1 b. 4. Run for 9 cycles: b. 5. Trip branch from SEQUOYAHJ4 (520422) 138 kV Bus TO ANADARK4 (520814) kV 138 kV Bus CKT 1 b. 6. Trip branch from PAYNESW4 (520888) 138 kV Bus TO NAPLSTP4 (520510) kV 138 kV Bus CKT 1 b. 7. Trip branch from CORNVIL4 (511449) 138 kV Bus TO CORN TP4 (520867) 138 kV Bus CKT 1 b. 8. Clear fault at ANADARK4 (520814) 138 kV Bus b. 9. Drop Load 1 Bus 520547 b. 10. Drop Load 2 Bus 520547 b. 11. Drop Load 1a Bus 520604 b. 12. Disconnect Bus 520422 b. 13. Disconnect Bus 520510 b. 14. Disconnect Bus 520604 b. 15. Disconnect Bus 520867 b. 16. Disconnect Bus 520547 b. 17. Drop Load 1 Bus 520900 b. 18. Drop Load 1 Bus 520923 b. 19. Disconnect Bus 520900 b. 20. Disconnect Bus 520923 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1199_P4 | a. Apply single-phase fault at PAYNESW4 (520888) 138 kV Bus b. 1. Run for 6 cycles, Trip branch from OU SW 4 (521104) 138 kV Bus TO COLE 4 (520861) 138 kV Bus CKT 1 b. 2. Run for 9 cycles: b. 3. Trip PAYNESW4 (520888) 138 kV Bus TO NAPLSTP4 (520510) 138 kV Bus CKT 1 b. 4. Trip PAYNESW4 (520888) 138 kV Bus TO CRINER 4 (520868) 138 kV Bus CKT 1 b. 5. Trip CORNVIL4 (511449) 138 kV Bus TO CORN TP4 (520867) 138 kV Bus CKT 1 b. 6. Trip ANADARK4 (520814) 138 kV Bus TO CLVLDSW4 (520508) 138 kV Bus CKT 1 b. 7. Clear fault at PAYNESW4 (520888) 138 kV Bus Drop Load 1 at 520547 Drop Load 2 at 520547 Drop Load 1A at 520604 Disconnect Bus 520422 Disconnect Bus 520510 Disconnect Bus 520604 Disconnect Bus 520867 Disconnect Bus 520547 Drop Load 1 Bus 520861 Drop Load 1 Bus 520868 Disconnect Bus 520861 Disconnect Bus 520868 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0001_P4 | a. Apply SLG fault at SW SHV 7 (507760) 345 kV Bus CB 10500 Stuck b. 1. Run for 5 cycles, Trip branch from SW SHV 7 (507760) 345 kV Bus TO DIANA 7 (508832) 345 kV Bus CKT 1 b. 2. Clear Fault after 10 cycles and trip SW SHV 7 (507760) 345 kV Bus TO LONGWD 7 (508809) 345 kV Bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0002_P4 | a. Apply SLG fault at WELSH 7 (508359) 345 kV Bus CB #10610Stuck b. 1. Run for 5 cycles, Trip branch from WELSH 7 (508359) 345 kV Bus TO NWTXARK7 (508072) 345 kV Bus CKT 1 b. 2. Clear Fault after 10 cycles and trip WELSH 7 (508359) 345 kV Bus TO WILKES 7 (508841) 345 kV Bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0003_P4 | a. Apply SLG fault at WELSH 7 (508359) 345 kV Bus CB 11990 Stuck b. 1. Run for 5 cycles, Trip branch from WELSH 7 (508359) 345 kV Bus TO DIANA 7 (508832) 345 kV Bus CKT 1 b. 2. Clear Fault after 10 cycles and trip WELSH 7 (508359) 345 kV Bus TO DIANA 7 (508832) 345 kV Bus CKT 2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0004_P4 | a. Apply single-phase fault at WILKES 7 (508841) 345 kV Bus CB #1W10 Stuck b. 1. Run for 5 cycles, Trip branch from WILKES 7 (508841) 345 kV Bus TO LONGWD 7 (508809) 345 kV Bus CKT 1 b. 2. Clear Fault after 10 cycles and trip WILKES 7 (508841) 345 kV Bus TO WELSH 7 (508359) 345 kV Bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0005_P4 | a. Apply single-phase fault at DIANA 7 (508832) 345 kV Bus CB 11990 Stuck b. 1. Run for 5 cycles, Trip branch from DIANA 7 (508832) 345 kV Bus TO PIRKEY 7 (508563) 345 kV Bus CKT 1 b. 2. Clear Fault after 10 cycles and trip DIANA 7 (508832) 345 kV Bus TO SW SHV 7 (507760) 345 kV Bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0006_P4 | a. Apply single-phase fault at DIANA 7 (508832) 345 kV Bus CB 1N60 Stuck b. 1. Run for 5 cycles, Trip branch from DIANA 7 (508832) 345 kV Bus TO WELSH 7 (508359) 345 kV Bus CKT 1 b. 2. Clear Fault after 10 cycles and trip DIANA 7 (508832) 345 kV Bus TO SW SHV 7 (507760) 345 kV Bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0007_P4 | a. Apply single-phase fault on ONETA--7 (509807) 345 kV Bus CB #3405A Stuck b. 1. Run for 5 cycles, Trip branch from ONETA--7 (509807) 345 kV Bus TO R.S.S.-7 (509782) 345 kV Bus CKT 1 b. 2. Clear Fault after 10 cycles and trip ONETA--7 (509807) 345 kV Bus TO CLARKSV7 (509745) 345 kV Bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0008_P4 | a. Apply single-phase fault at R.S.S.-7 (509782) 345 kV Bus CB #3405A Stuck b. 1. Run for 5 cycles, Trip branch from R.S.S.-7 (509782) 345 kV Bus TO REDBUD 7 (514909) 345 kV Bus CKT 1 b. 2. Clear Fault after 10 cycles and trip R.S.S.-7 (509782) 345 kV Bus TO SAPLPRD7 (509870) 345 kV Bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0009_P4 | a. Apply single-phase fault at LONGWD 7 (508809) 345 kV Bus CB 10280 Stuck b. 1. Run for 5 cycles, Trip branch from LONGWD 7 (508809) 345 kV Bus TO WILKES 7 (508841) 345 kV Bus CKT 1 b. 2. Clear Fault after 10 cycles and trip LONGWD 7 (508809) 345 kV Bus TO SW SHV 7 (507760) 345 kV Bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0010_P4 | a. Apply single-phase fault at LONGWD 7 (508809) 345 kV Bus CB 10500 Stuck b. 1. Run for 5 cycles, Trip branch from LONGWD 7 (508809) 345 kV Bus TO 7SAREPTA% (337376) 345 kV Bus CKT 1 b. 2. Clear Fault after 10 cycles and trip LONGWD 7 (508809) 345 kV Bus TO SW SHV 7 (507760) 345 kV Bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0011_P4 | a. Apply single-phase fault at NEO SPA5 (505486) 161 kV Bus 16119 Stuck b. 1. Run for 5 cycles, Trip branch NEO SPA5 (505486) 161 kV Bus TO TIP292 5 (547472) 161 kV Bus CKT 1 b. 2. Run for 60 cycles, Trip branch RNM393 5 (547500) 161 kV Bus TO TIP292 5 (547472) 161 kV Bus CKT 1 b. 3. Run for 20 cycles, Trip branch MON383 5 (547480) 161 kV Bus TO TIP292 5 (547472) 161 kV Bus CKT 1 b. 4. Run for 3 cycles, Trip branch RNM393 5 (547500) 161 kV Bus TO TIP292 5 (547472) 161 kV Bus CKT 1 b. 5. Run for 37 cycles, Trip branch JOP389 5 (547483) 161 kV Bus TO TIP292 5 (547472) 161 kV Bus CKT 1 b. 6. Clear Fault and run for 13 cycles, Trip branch RNM393 5 (547500) 161 kV Bus TO TIP292 5 (547472) 161 kV Bus CKT 1 b. 7. Drop Load 1 TIP292 5 (547472) 161 kV b. 8. Disconnect Bus TIP292 5 (547472) 161 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0012_P4 | a. Apply single-phase fault at ASB349 5 (547476) 161 kV Bus CB 16118 Stuck b. 1. Run for 5 cycles, Trip branch CAR395 5 (547485) 161 kV Bus TO CARTHAG5 (505488) 161 kV Bus CKT 1 b. 2. Run for 2 cycles, Trip branch ASB349 5 (547476) 161 kV Bus TO PUR421 5 (547491) 161 kV Bus CKT 1 b. 3. Run for 12 cycles, Trip branch ASB349 5 (547476) 161 kV Bus TO CJ 366 5 (547477) 161 kV Bus CKT 1 b. 4. Clear fault and run for 15 cycles, Trip branch ASB349 5 (547476) 161 kV Bus TO CJ 366 5 (547477) 161 kV Bus CKT 1 b. 6. Drop Load 1 Bus CAR395 5 (547485) 161 kV b. 7. Drop Load 1 Bus PUR421 5 (547491) 161 kV b. 8. Disconnect Bus CAR395 5 (547485) 161 kV b. 9. Disconnect Bus PUR421 5 (547491) 161 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0013_P4 | a. Apply single-phase fault on RIV4525 (547469) 161 kV Bus CB 16110 Stuck b. 1. Run for 5 cycles, Trip branch RIV4525 (547469) 161 kV Bus TO NEOSHO 5 (532937) 161 kV Bus CKT 1 b. 2. Run for 2 cycles, Trip branch NEOSHO 5 (532937) 161 kV Bus TO RIV4525 (547469) 161 kV Bus CKT 1 b. 3. Run for 12 cycles, Trip branch HOC404 5 (547487) 161 kV Bus TO BAX488 5 (547729) 161 kV Bus CKT 1 b. 4. Clear fault after 86 cycles and Trip BAX488 5 (547729) 161 kV Bus TO HOC404 5 (547487) 161 kV Bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0014_P4 | a. Apply single-phase fault on RIV4525 (547469) 161 kV Bus CB 161120 Stuck b. 1. Run for 5 cycles, Trip branch ORO110 5 (547467) 161 kV Bus TO RIV4525 (547469) 161 kV Bus CKT 1 b. 2. Run for 12 cycles, Trip branch RIV4525 (547469) 161 kV Bus TO STL439 5 (547498) 161 kV Bus CKT 1 b. 3. Clear fault after 98 cycles and Trip branch STL439 5 (547498) 161 kV Bus TO STL439 5 (547498) 161 kV Bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0015_P4 | a. Apply single-phase fault on TIP292 5 (547472) 161 kV Bus CB 16110 Stuck b. 1. Run for 5 cycles, Trip branch TIP292 5 (547472) 161 kV Bus TO JOP389 5 (547483) 161 kV Bus CKT 1 b. 2. Run for 60 cycles: b. 3. Trip branch TIP292 5 (547472) 161 kV Bus TO NEO SPA5 (505486) 161 kV Bus CKT 1 b. 4. Trip branch NEO SPA5 (505486) 161 kV Bus TO CARTHAG5 (505488) 161 kV Bus CKT 1 b. 5. Run for 5 cycles, Trip branch RNM393 5 (547500) 161 kV Bus TO TIP292 5 (547472) 161 kV Bus CKT 1 b. 6. Clear fault and run for 15 cycles: b. 7. Trip branch MON383 5 (547480) 161 kV Bus TO TIP292 5 (547472) 161 kV Bus CKT 1 b. 8. Drop Load 1 Bus TIP292 5 (547472) 161 kV b. 9. Disconnect Bus TIP292 5 (547472) 161 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0016_P4 | a. Apply single-phase fault on L1G382 1 (547651) 13.2 kV Bus TO LAR382 5 (547479) kV Bus CKT 1 b. 1. Run for 5 cycles, Trip branch L1G382 1 (547651) 13.2 kV Bus TO LAR382 5 (547479) kV Bus CKT 1 b. 2. Run for 12 cycles, Trip LAR382 5 ( 547479 ) 161 kV Bus TO MON383 5 ( 547480 ) 345 kV Bus CKT 1 b. 3. Clear fault and run for 95 cycles: b. 4. Trip branch MON383 5 ( 547480 ) 161 kV Bus TO LAR382 5 ( 547479 ) 345 kV Bus CKT 1 b. 5. Drop GENERATOR 1 BUS 547651 b. 6. Drop LOAD S1 BUS 547651 b. 7. Disconnect BUS 547651 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0018_P4 | a. Apply single-phase fault on LEBROCK7 (508572) 345 kV Bus TO TENRUSK7 (508585) 345 kV Bus CKT 1 b. 1. Run for 15 cycles, Trip branch LEBROCK7 (508572) 345 kV Bus TO TENRUSK7 (508585) 345 kV Bus CKT 1 b. 2. Clear fault after 15 cycles and Trip LEBROCK7 ( 508572 ) 161 kV Bus TO TENRUSK7 ( 508585 ) 345 kV Bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0019_P4 | a. Apply single-phase fault on BENTON 7 (532791) 345 kV Bus TO ROSEHIL7 (532794) 345 kV Bus CKT 1 b. 1. Clear fault after 4.75 cycles, Trip branch BENTON 7 (532791) 345 kV Bus TO ROSEHIL7 (532794) 345 kV Bus CKT 1 c. Reclose the fault d. 1. Clear fault after 12 cycles, Disconnect BUS 532791 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0020_P4 | a. Apply single-phase fault on BENTON 7 (532791) 345 kV Bus TO WICHITA7 (532796) 345 kV Bus CKT 1 b. 1. Clear fault after 4.75 cycles, Trip branch BENTON 7 (532791) 345 kV Bus TO WICHITA7 (532796) 345 kV Bus CKT 1 c. Reclose the fault d. 1. Clear fault after 12 cycles, Trip branch BENTON 7 (532791) 345 kV Bus TO WOLFCRK7 (532797) 345 kV Bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0021_P4 | a. Apply single-phase fault on BENTON 7 (532791) 345 kV Bus TO WOLFCRK7 (532797) 345 kV Bus CKT 1 b. 1. Clear fault after 4.75 cycles, Trip branch BENTON 7 (532791) 345 kV Bus TO WOLFCRK7 (532797) 345 kV Bus CKT 1 c. Reclose the fault d. 1. Clear fault after 12 cycles, Trip branch BENTON 7 (532791) 345 kV Bus TO WOLFCRK7 (532797) 345 kV Bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0022_P4 | a. Apply single-phase fault on ROSEHIL7 (532794) 345 kV Bus TO WOLFCRK7 (532797) 345 kV Bus CKT 1 b. 1. Clear fault after 3.75 cycles, Trip branch ROSEHIL7 (532794) 345 kV Bus TO WOLFCRK7 (532797) 345 kV Bus CKT 1 c. Reclose the fault d. 1. Clear fault after 13 cycles, Disconnect BUS 532831 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0023_P4 | a. Apply single-phase fault on WOLFCRK7 (532797) 345 kV Bus TO BENTON 7 (532791) 345 kV Bus CKT 1 b. 1. Clear fault after 3.75 cycles, Trip branch WOLFCRK7 (532797) 345 kV Bus TO BENTON 7 (532791) 345 kV Bus CKT 1 c. Reclose the fault d. 1. Clear fault after 6.75 cycles, Trip branch WOLFCRK7 (532797) 345 kV Bus TO BENTON 7 (532791) 345 kV Bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0024_P4 | a. Apply single-phase fault on WOLFCRK7 (532797) 345 kV Bus TO ROSEHIL7 (532794) 345 kV Bus CKT 1 b. 1. Clear fault after 3.75 cycles, Trip branch WOLFCRK7 (532797) 345 kV Bus TO ROSEHIL7 (532794) 345 kV Bus CKT 1 c. Reclose the fault d. 1. Clear fault after 6.75 cycles, Trip branch WOLFCRK7 (532797) 345 kV Bus TO ROSEHIL7 (532794) 345 kV Bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0025_P4 | a. Apply single-phase fault on WOLFCRK7 (532797) 345 kV Bus TO BENTON 7 (532791) 345 kV Bus CKT 1 b. 1. Clear fault after 3.75 cycles, Trip branch WOLFCRK7 (532797) 345 kV Bus TO BENTON 7 (532791) 345 kV Bus CKT 1 c. Reclose the fault d. 1. Clear fault after 6.75 cycles: d. 2. Trip branch WOLFCRK7 (532797) 345 kV Bus TO BENTON 7 (532791) 345 kV Bus CKT 1 d. 3. Disconnect BUS 532962 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0026_P4 | a. Apply single-phase fault on CRAIG 7 (542977) 345 kV Bus TO W.GRDNR7 (542965) 345 kV Bus CKT 1 b. 1. Clear fault after 21 cycles: b. 2. Trip branch CRAIG 7 (542977) 345 kV Bus TO W.GRDNR7 (542965) 345 kV Bus CKT 1 b. 3. Disconnect BUS 543641 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0027_P4 | a. Apply single-phase fault on CRAIG 7 (542977) 345 kV Bus TO W.GRDNR7 (542965) 345 kV Bus CKT 1 b. 1. Clear fault after 21 cycles: b. 2. Trip branch CRAIG 7 (542977) 345 kV Bus TO W.GRDNR7 (542965) 345 kV Bus CKT 1 b. 3. Disconnect BUS 543643 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0028_P4 | a. Apply single-phase fault on LACYGNE7 (542981) 345 kV Bus TO W.GRDNR7 (542965) 345 kV Bus CKT 1 b. 1. Clear fault after 11 cycles: b. 2. Trip branch LACYGNE7 (542981) 345 kV Bus TO W.GRDNR7 (542965) 345 kV Bus CKT 1 b. 3. Trip branch LACYGNE7 (542981) 345 kV Bus TO WAVERLY7 (532799) 345 kV Bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0029_P4 | a. Apply single-phase fault on LACYGNE7 (542981) 345 kV Bus TO STILWEL7 (542968) 345 kV Bus CKT 1 b. 1. Clear fault after 11 cycles: b. 2. Trip branch LACYGNE7 (542981) 345 kV Bus TO STILWEL7 (542968) 345 kV Bus CKT 1 b. 3. Disconnect BUS 542955 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0030_P4 | a. Apply single-phase fault on LACYGNE7 (542981) 345 kV Bus TO WAVERLY7 (532799) 345 kV Bus CKT 1 b. 1. Clear fault after 11 cycles: b. 2. Trip branch LACYGNE7 (542981) 345 kV Bus TO WAVERLY7 (532799) 345 kV Bus CKT 1 b. 3. Disconnect BUS 542955 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0031_P4 | a. Apply single-phase fault on LACYGNE7 (542981) 345 kV Bus TO W.GRDNR7 (542965) 345 kV Bus CKT 1 b. 1. Clear fault after 11 cycles: b. 2. Trip branch LACYGNE7 (542981) 345 kV Bus TO W.GRDNR7 (542965) 345 kV Bus CKT 1 b. 3. Disconnect BUS 542956 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0032_P4 | a. Apply single-phase fault on PECULR 7 (541198) 345 kV Bus TO STILWEL7 (542968) 345 kV Bus CKT 1 b. 1. Clear fault after 11 cycles: b. 2. Trip branch PECULR 7 (541198) 345 kV Bus TO STILWEL7 (542968) 345 kV Bus CKT 1 b. 3. Trip branch LACYGNE7 (542981) 345 kV Bus TO STILWEL7 (542968) 345 kV Bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0033_P4 | a. Apply single-phase fault on W.GRDNR7 (542965) 345 kV Bus TO CRAIG 7 (542977) 345 kV Bus CKT 1 b. 1. Clear fault after 11 cycles: b. 2. Trip branch W.GRDNR7 (542965) 345 kV Bus TO CRAIG 7 (542977) 345 kV Bus CKT 1 b. 3. Trip branch SWISVAL7 (532774) 345 kV Bus TO W.GRDNR7 (542965) 345 kV Bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0034_P4 | a. Apply single-phase fault on W.GRDNR7 (542965) 345 kV Bus TO LACYGNE7 (542981) 345 kV Bus CKT 1 b. 1. Clear fault after 11 cycles: b. 2. Trip branch W.GRDNR7 (542965) 345 kV Bus TO LACYGNE7 (542981) 345 kV Bus CKT 1 b. 3. Trip branch STILWEL7 (542968) 345 kV Bus TO W.GRDNR7 (542965) 345 kV Bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0035_P4 | a. Apply single-phase fault on ROSEHIL7 (532794) 345 kV Bus TO WOLFCRK7 (532797) 345 kV Bus CKT 1 b. 1. Clear fault after 3.75 cycles, Disconnect BUS 532831 c. Reclose the fault d. 1. Clear fault after 13 cycles, Trip branch ROSEHIL7 (532794) 345 kV Bus TO WOLFCRK7 (532797) 345 kV Bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0036_P1 | 3 phase fault on TONNEC2 (512753) 69 kV Bus a. Apply Fault at the TONNEC2 (512753) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from TONNEC2 (512753) 69 kV Bus to TONECESTR2 (512756) 69 kV Bus CKT 1 b. 2. Trip branch from TONECESTR2 (512756) 69 kV Bus to ARKLIN2 (512728) 69 kV Bus CKT 1 b. 3. Trip branch from ARKLIN2 (512728) 69 kV Bus to SSNEWN2 (512747) 69 kV Bus CKT 1 b. 4. Trip branch from SSNEWN2 (512747) 69 kV Bus to SSNORT2 (512746) 69 kV Bus CKT 1 b. 5. Trip branch from SSNORT2 (512746) 69 kV Bus to SSLINC2 (512745) 69 kV Bus CKT 1 b. 6. Drop Load 1 at SSNORT2 (512746) 69 kV Bus b. 7. Drop Load 1 at SSLINC2 (512745) 69 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 763002 [G18-064-GEN10.5500]
04 - Southeast | 25W | Transfer | Group4_Fault_0037_P1 | 3 phase fault on FLINTCR7 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 (506935) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from FLINTCR7 (506935) 345 kV Bus to FLINTCR5 (506934) 161 kV Bus to FLINT2-1 (506920) 13.8 kV Bus CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0038_P1 | 3 phase fault on SPRGFLD2 (505494) 69 kV Bus a. Apply Fault at the SPRGFLD2 (505494) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from SPRGFLD2 (505494) 69 kV Bus to 2ELWOOD (300669) 69 kV Bus CKT 1 b. 2. Trip branch from 2ELWOOD (300669) 69 kV Bus to 2ASHGRV (300657) 69 kV Bus CKT 1 b. 3. Drop Load 1 at 2ELWOOD (300669) 69 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0039_P1 | 3 phase fault on NICHOLS 5 (549956) 161 kV Bus a. Apply Fault at the NICHOLS 5 (549956) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from NICHOLS 5 (549956) 161 kV Bus to NICHOLS 2 (549925) 69 kV Bus to NICHOL XF1 1 (549940) 13.2 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0040_P1 | 3 phase fault on NICHOLS 5 (549956) 161 kV Bus a. Apply Fault at the NICHOLS 5 (549956) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from NICHOLS 5 (549956) 161 kV Bus to WEST BELT 5 (549957) 161 kV Bus CKT 1 b. 2. Trip branch from WEST BELT 5 (549957) 161 kV Bus to MAIN STREET5 (549958) 161 kV Bus CKT 1 b. 3. Drop Load W at WEST BELT 5 (549957) 161 kV Bus b. 4. Drop Load E at WEST BELT 5 (549957) 161 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0041_P1 | 3 phase fault on HERRON 5 (513591) 161 kV Bus a. Apply Fault at the HERRON 5 (513591) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from HERRON 5 (513591) 161 kV Bus to CUSTDAY1 5 (513590) 161 kV Bus CKT 1 b. 2. Drop Load 1 at CUSTDAY1 5 (513590) 161 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0042_P1 | 3 phase fault on HERRON 5 (513591) 161 kV Bus a. Apply Fault at the HERRON 5 (513591) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from HERRON 5 (513591) 161 kV Bus to CUSTDAY1 5 (513590) 161 kV Bus CKT 2 b. 2. Drop Load 1 at CUSTDAY1 5 (513590) 161 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0043_P1 | 3 phase fault on BATTLEFIELD2 (549979) 69 kV Bus a. Apply Fault at the BATTLEFIELD2 (549979) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from BATTLEFIELD2 (549979) 69 kV Bus to GOLDEN 2 (549911) 69 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0044_P1 | 3 phase fault on BATTLEFIELD2 (549979) 69 kV Bus a. Apply Fault at the BATTLEFIELD2 (549979) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from BATTLEFIELD2 (549979) 69 kV Bus to DAYTON 2 (549913) 69 kV Bus CKT 1 b. 2. Trip branch from DAYTON 2 (549913) 69 kV Bus to FORT 2 (549914) 69 kV Bus CKT 1 b. 3. Trip branch from FORT 2 (549914) 69 kV Bus to SUNSET 2 (549907) 69 kV Bus CKT 1 b. 4. Drop Load 1 at DAYTON 2 (549913) 69 kV Bus b. 5. Drop Load N at FORT 2 (549914) 69 kV Bus b. 6. Drop Load S at FORT 2 (549914) 69 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0045_P1 | 3 phase fault on GOLDEN 2 (549911) 69 kV Bus a. Apply Fault at the GOLDEN 2 (549911) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from GOLDEN 2 (549911) 69 kV Bus to LAUREL 2 (549924) 69 kV Bus CKT 1 b. 2. Trip branch from LAUREL 2 (549924) 69 kV Bus to NICHOLS 2 (549925) 69 kV Bus CKT 1 b. 3. Drop Load N at LAUREL 2 (549924) 69 kV Bus b. 4. Drop Load S at LAUREL 2 (549924) 69 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0046_P1 | 3 phase fault on GOLDEN 2 (549911) 69 kV Bus a. Apply Fault at the GOLDEN 2 (549911) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from GOLDEN 2 (549911) 69 kV Bus to COX 2 (549910) 69 kV Bus CKT 1 b. 2. Trip branch from COX 2 (549910) 69 kV Bus to PLAINVIEW 2 (549905) 69 kV Bus CKT 1 b. 3. Trip branch from PLAINVIEW 2 (549905) 69 kV Bus to JRPS 69B-2 2 (549903) 69 kV Bus CKT 1 b. 4. Drop Load N at COX 2 (549910) 69 kV Bus b. 5. Drop Load S at COX 2 (549910) 69 kV Bus b. 6. Drop Load E at PLAINVIEW 2 (549905) 69 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0047_P1 | 3 phase fault on NICHOLS 2 (549925) 69 kV Bus a. Apply Fault at the NICHOLS 2 (549925) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from NICHOLS 2 (549925) 69 kV Bus to NIC170 2 (547542) 69 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0048_P1 | 3 phase fault on SHIPERD7 (506979) 345 kV Bus a. Apply Fault at the SHIPERD7 (506979) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from SHIPERD7 (506979) 345 kV Bus to SHIPERD5 (506980) 161 kV Bus to SHIPERD1 (506981) 13.8 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0049_P1 | 3 phase fault on NICHOLS 2 (549925) 69 kV Bus a. Apply Fault at the NICHOLS 2 (549925) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from NICHOLS 2 (549925) 69 kV Bus to FRISCO 2 (549926) 69 kV Bus CKT 1 b. 2. Trip branch from FRISCO 2 (549926) 69 kV Bus to N HWY13 2 (549927) 69 kV Bus CKT 1 b. 3. Trip branch from N HWY13 2 (549927) 69 kV Bus to NORTON 2 (549928) 69 kV Bus CKT 1 b. 4. Drop Load N at FRISCO 2 (549926) 69 kV Bus b. 5. Drop Load S at FRISCO 2 (549926) 69 kV Bus b. 6. Drop Load E at N HWY13 2 (549927) 69 kV Bus b. 7. Drop Load W at N HWY13 2 (549927) 69 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0050_P1 | 3 phase fault on NIC170 2 (547542) 69 kV Bus a. Apply Fault at the NIC170 2 (547542) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from NIC170 2 (547542) 69 kV Bus to SED 80 2 (547529) 69 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0051_P1 | 3 phase fault on NIC170 2 (547542) 69 kV Bus a. Apply Fault at the NIC170 2 (547542) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from NIC170 2 (547542) 69 kV Bus to NIX114 2 (547535) 69 kV Bus CKT 1 b. 2. Trip branch from NIX114 2 (547535) 69 kV Bus to BHJ415 2 (547604) 69 kV Bus CKT 1 b. 3. Drop Load 1 at NIX114 2 (547535) 69 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0052_P1 | 3 phase fault on NIC170 2 (547542) 69 kV Bus a. Apply Fault at the NIC170 2 (547542) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from NIC170 2 (547542) 69 kV Bus to REP345 2 (547576) 69 kV Bus CKT 1 b. 2. Trip branch from REP345 2 (547576) 69 kV Bus to REP451 2 (547443) 69 kV Bus CKT 1 b. 3. Trip branch from REP451 2 (547443) 69 kV Bus to REP359 2 (547580) 69 kV Bus CKT 1 b. 4. Trip branch from REP359 2 (547580) 69 kV Bus to BIL221 2 (547546) 69 kV Bus CKT 1 b. 5. Drop Load 1 at REP345 2 (547576) 69 kV Bus b. 6. Drop Load 1 at REP451 2 (547443) 69 kV Bus b. 7. Drop Load 1 at REP359 2 (547580) 69 kV Bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0053_P1 | 3 phase fault on KANSATP5 (512714) 161 kV Bus a. Apply Fault at the KANSATP5 (512714) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from KANSATP5 (512714) 161 kV Bus to SILSPWW5 (512642) 161 kV Bus CKT 1 b. 2. Trip branch from SILSPWW5 (512642) 161 kV Bus to SILMCTY5 (512643) 161 kV Bus CKT 1 b. 3. Drop Load 1 at SILSPWW5 (512642) 161 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0054_P1 | 3 phase fault on CHAMSPR5 (506944) 161 kV Bus a. Apply Fault at the CHAMSPR5 (506944) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from CHAMSPR5 (506944) 161 kV Bus to WEDINGTON (506992) 161 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0055_P1 | 3 phase fault on WEDINGTON (506992) 161 kV Bus a. Apply Fault at the WEDINGTON (506992) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from WEDINGTON (506992) 161 kV Bus to WEDINGTON5 (504275) 161 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0056_P1 | 3 phase fault on WEDINGTON (506992) 161 kV Bus a. Apply Fault at the WEDINGTON (506992) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from WEDINGTON (506992) 161 kV Bus to FARMNGTN 5 (504020) 161 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0058_P1 | 3 phase fault on 7MORGAN (300045) 345 kV Bus a. Apply Fault at the 7MORGAN (300045) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from 7MORGAN (300045) 345 kV Bus to 7HUBEN (300042) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 999925 [GI85-GEN1 0.6450], 999927 [GI85-ESS1 0.6450], 999935 [GI85-GEN2 0.6450], 999937 [GI85-ESS2 0.6450], 999945 [GI85-GEN3 0.6450], 999947 [GI85-ESS3 0.6450]
04 - Southeast | 25W | Transfer | Group4_Fault_0059_P1 | 3 phase fault on FLINTCR5 (506934) 161 kV Bus a. Apply Fault at the FLINTCR5 (506934) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from FLINTCR5 (506934) 161 kV Bus to GENTRY 5 (504201) 161 kV Bus CKT 1 b. 2. Trip branch from GENTRY 5 (504201) 161 kV Bus to BEN279_5 (506960) 161 kV Bus CKT 1 b. 3. Trip branch from BEN279_5 (506960) 161 kV Bus to GREENHOUSE 5 (506990) 161 kV Bus CKT 1 b. 4. Trip branch from GREENHOUSE 5 (506990) 161 kV Bus to ECNTRTN5 (506929) 161 kV Bus CKT 1 b. 5. Drop Load A1 at GENTRY 5 (504201) 161 kV Bus b. 6. Drop Load 1 at BEN279_5 (506960) 161 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0061_P1 | 3 phase fault on 7MORGAN (300045) 345 kV Bus a. Apply Fault at the 7MORGAN (300045) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from 7MORGAN (300045) 345 kV Bus to 5MORGANXF2 (301622) 161 kV Bus CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 999925 [GI85-GEN1 0.6450], 999927 [GI85-ESS1 0.6450], 999935 [GI85-GEN2 0.6450], 999937 [GI85-ESS2 0.6450], 999945 [GI85-GEN3 0.6450], 999947 [GI85-ESS3 0.6450]
04 - Southeast | 25W | Transfer | Group4_Fault_0062_P1 | 3 phase fault on 5MORGANXF2 (301622) 161 kV Bus a. Apply Fault at the 5MORGANXF2 (301622) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from 5MORGANXF2 (301622) 161 kV Bus to 5MORGAN (300101) 161 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0063_P1 | 3 phase fault on TONTITN5 (506957) 161 kV Bus a. Apply Fault at the TONTITN5 (506957) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from TONTITN5 (506957) 161 kV Bus to DYESS 5 (506927) 161 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0064_P1 | 3 phase fault on EROGERS5 (506931) 161 kV Bus a. Apply Fault at the EROGERS5 (506931) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from EROGERS5 (506931) 161 kV Bus to DYESS 5 (506927) 161 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0065_P1 | 3 phase fault on DYESS 5 (506927) 161 kV Bus a. Apply Fault at the DYESS 5 (506927) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from DYESS 5 (506927) 161 kV Bus to DYESS 2 (506926) 69 kV Bus to DYESS1-1 (506914) 13.2 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0066_P1 | 3 phase fault on DYESS 5 (506927) 161 kV Bus a. Apply Fault at the DYESS 5 (506927) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from DYESS 5 (506927) 161 kV Bus to DYESS 2 (506926) 69 kV Bus to DYES2-1 (506915) 13.2 kV Bus CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0067_P1 | 3 phase fault on DYESS 5 (506927) 161 kV Bus a. Apply Fault at the DYESS 5 (506927) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from DYESS 5 (506927) 161 kV Bus to DYESS 2 (506926) 69 kV Bus to DYES3-1 (506916) 13.2 kV Bus CKT 3 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0068_P1 | 3 phase fault on DYESS 5 (506927) 161 kV Bus a. Apply Fault at the DYESS 5 (506927) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from DYESS 5 (506927) 161 kV Bus to CARLEYRD 5 (504274) 161 kV Bus CKT 1 b. 2. Trip branch from CARLEYRD 5 (504274) 161 kV Bus to VANASCH5 (506939) 161 kV Bus CKT 1 b. 3. Trip branch from VANASCH5 (506939) 161 kV Bus to GREGGST5 (506983) 161 kV Bus CKT 1 b. 4. Trip branch from GREGGST5 (506983) 161 kV Bus to FAYETVL5 (506933) 161 kV Bus CKT 1 b. 5. Trip branch from FAYETVL5 (506933) 161 kV Bus to SFAYTVL5 (506947) 161 kV Bus CKT 1 b. 6. Drop Load A1 at CARLEYRD 5 (504274) 161 kV Bus b. 7. Drop Load 1 at VANASCH5 (506939) 161 kV Bus b. 8. Drop Load 1 at GREGGST5 (506983) 161 kV Bus b. 9. Drop Load 1 at FAYETVL5 (506933) 161 kV Bus b. 10. Drop Shunt 1 at VANASCH5 (506939) 161 kV Bus1 b. 11. Drop Shunt 1 at FAYETVL5 (506933) 161 kV Bus1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0069_P1 | 3 phase fault on DYESS 5 (506927) 161 kV Bus a. Apply Fault at the DYESS 5 (506927) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from DYESS 5 (506927) 161 kV Bus to SOSPRDL5 (506949) 161 kV Bus CKT 1 b. 2. Trip branch from SOSPRDL5 (506949) 161 kV Bus to OSBURN (506985) 161 kV Bus CKT 1 b. 3. Trip branch from OSBURN (506985) 161 kV Bus to EFAYETVL 5 (504015) 161 kV Bus CKT 1 b. 4. Drop Load 1 at SOSPRDL5 (506949) 161 kV Bus b. 5. Drop Load 1 at OSBURN (506985) 161 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0070_P1 | 3 phase fault on FLINTCR5 (506934) 161 kV Bus a. Apply Fault at the FLINTCR5 (506934) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from FLINTCR5 (506934) 161 kV Bus to DEC392 5 (547484) 161 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0071_P1 | 3 phase fault on NOL435 5 (547496) 161 kV Bus a. Apply Fault at the NOL435 5 (547496) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from NOL435 5 (547496) 161 kV Bus to GROVE 5 (510411) 161 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0072_P1 | 3 phase fault on NOL435 5 (547496) 161 kV Bus a. Apply Fault at the NOL435 5 (547496) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from NOL435 5 (547496) 161 kV Bus to NEO184 5 (547471) 161 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0073_P1 | 3 phase fault on NOL435 5 (547496) 161 kV Bus a. Apply Fault at the NOL435 5 (547496) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from NOL435 5 (547496) 161 kV Bus to NOL435 2 (547610) 69 kV Bus to NOL435 1 (547720) 12.5 kV Bus CKT 1 b. 2. Drop Shunt 1 at NOL435 1 (547720) 12.5 kV Bus1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0074_P1 | 3 phase fault on 5SPORTSMAN (300741) 161 kV Bus a. Apply Fault at the 5SPORTSMAN (300741) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from 5SPORTSMAN (300741) 161 kV Bus to 5CHOTEAU2 (301348) 161 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0075_P1 | 3 phase fault on CLARMR 5 (512651) 161 kV Bus a. Apply Fault at the CLARMR 5 (512651) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from CLARMR 5 (512651) 161 kV Bus to CLARMR 2 (512679) 69 kV Bus to CLARMR1 (512814) 13.8 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0076_P1 | 3 phase fault on CLARMR 5 (512651) 161 kV Bus a. Apply Fault at the CLARMR 5 (512651) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from CLARMR 5 (512651) 161 kV Bus to CLARMR 2 (512679) 69 kV Bus to CLARMR2 (512815) 13.8 kV Bus CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0077_P1 | 3 phase fault on CLARMR 5 (512651) 161 kV Bus a. Apply Fault at the CLARMR 5 (512651) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from CLARMR 5 (512651) 161 kV Bus to 5KETONVL (300997) 161 kV Bus CKT 1 b. 2. Trip branch from 5KETONVL (300997) 161 kV Bus to COLINS 5 (512627) 161 kV Bus CKT 1 b. 3. Drop Load 1 at 5KETONVL (300997) 161 kV Bus b. 4. Drop Load 1 at 5KETONVL (300997) 161 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0078_P1 | 3 phase fault on WAGNOR 5 (512700) 161 kV Bus a. Apply Fault at the WAGNOR 5 (512700) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from WAGNOR 5 (512700) 161 kV Bus to OKAYGR 5 (512640) 161 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0079_P1 | 3 phase fault on WAGNOR 5 (512700) 161 kV Bus a. Apply Fault at the WAGNOR 5 (512700) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from WAGNOR 5 (512700) 161 kV Bus to WAGNOR 2 (512697) 69 kV Bus to WAGNOR1 (512818) 13.8 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0080_P1 | 3 phase fault on 5MORGAN (300101) 161 kV Bus a. Apply Fault at the 5MORGAN (300101) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from 5MORGAN (300101) 161 kV Bus to STOCKTN5 (505498) 161 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0081_P1 | 3 phase fault on FLINTCR5 (506934) 161 kV Bus a. Apply Fault at the FLINTCR5 (506934) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from FLINTCR5 (506934) 161 kV Bus to TONTITN5 (506957) 161 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0082_P1 | 3 phase fault on 5MORGAN (300101) 161 kV Bus a. Apply Fault at the 5MORGAN (300101) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from 5MORGAN (300101) 161 kV Bus to DAD368 5 (547478) 161 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0083_P1 | 3 phase fault on 5MORGAN (300101) 161 kV Bus a. Apply Fault at the 5MORGAN (300101) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from 5MORGAN (300101) 161 kV Bus to 2MORGAN (300782) 69 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0084_P1 | 3 phase fault on SSSWTP2 (512737) 69 kV Bus a. Apply Fault at the SSSWTP2 (512737) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from SSSWTP2 (512737) 69 kV Bus to SSMOSS2 (512744) 69 kV Bus CKT 1 b. 2. Drop Load 1 at SSMOSS2 (512744) 69 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0085_P1 | 3 phase fault on 5CHOTEAU2 (301348) 161 kV Bus a. Apply Fault at the 5CHOTEAU2 (301348) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from 5CHOTEAU2 (301348) 161 kV Bus to 5CHOTEAU1 (300069) 161 kV Bus CKT Z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0086_P1 | 3 phase fault on PENSA 5 (512654) 161 kV Bus a. Apply Fault at the PENSA 5 (512654) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from PENSA 5 (512654) 161 kV Bus to DRYGULCH5 (512629) 161 kV Bus CKT 1 b. 2. Drop Load 1 at DRYGULCH5 (512629) 161 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0087_P1 | 3 phase fault on PENSA 5 (512654) 161 kV Bus a. Apply Fault at the PENSA 5 (512654) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from PENSA 5 (512654) 161 kV Bus to KERR GR5 (512635) 161 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0088_P1 | 3 phase fault on KERR GR5 (512635) 161 kV Bus a. Apply Fault at the KERR GR5 (512635) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from KERR GR5 (512635) 161 kV Bus to 412SUB 5 (512637) 161 kV Bus CKT 1 b. 2. Trip branch from 412SUB 5 (512637) 161 kV Bus to KANSATP5 (512714) 161 kV Bus CKT 1 b. 3. Drop Load 1 at 412SUB 5 (512637) 161 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0089_P1 | 3 phase fault on KERR GR5 (512635) 161 kV Bus a. Apply Fault at the KERR GR5 (512635) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from KERR GR5 (512635) 161 kV Bus to KERR BRK1 5 (512770) 161 kV Bus CKT Z0 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0090_P1 | 3 phase fault on KERR GR5 (512635) 161 kV Bus a. Apply Fault at the KERR GR5 (512635) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from KERR GR5 (512635) 161 kV Bus to KERR BRK4 5 (512771) 161 kV Bus CKT Z0 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0091_P1 | 3 phase fault on KERR GR5 (512635) 161 kV Bus a. Apply Fault at the KERR GR5 (512635) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from KERR GR5 (512635) 161 kV Bus to SALNCRK5 (512805) 161 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0092_P1 | 3 phase fault on FLINTCR5 (506934) 161 kV Bus a. Apply Fault at the FLINTCR5 (506934) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from FLINTCR5 (506934) 161 kV Bus to SILOAMSP 5 (504202) 161 kV Bus CKT 1 b. 2. Trip branch from SILOAMSP 5 (504202) 161 kV Bus to CHAMSPR5 (506944) 161 kV Bus CKT 1 b. 3. Drop Load A1 at SILOAMSP 5 (504202) 161 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0093_P1 | 3 phase fault on KERR GR5 (512635) 161 kV Bus a. Apply Fault at the KERR GR5 (512635) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from KERR GR5 (512635) 161 kV Bus to SALNCRK5 (512805) 161 kV Bus CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0094_P1 | 3 phase fault on CATSAGR5 (512638) 161 kV Bus a. Apply Fault at the CATSAGR5 (512638) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from CATSAGR5 (512638) 161 kV Bus to CATOOSA4 (509790) 138 kV Bus to CATTER1 1 (512833) 13.8 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0095_P1 | 3 phase fault on CATSAGR5 (512638) 161 kV Bus a. Apply Fault at the CATSAGR5 (512638) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from CATSAGR5 (512638) 161 kV Bus to CATOOSA4 (509790) 138 kV Bus to CATTER2 1 (512834) 13.8 kV Bus CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0096_P1 | 3 phase fault on CATSAGR5 (512638) 161 kV Bus a. Apply Fault at the CATSAGR5 (512638) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from CATSAGR5 (512638) 161 kV Bus to 5ELMCRK (300993) 161 kV Bus CKT 1 b. 2. Trip branch from 5ELMCRK (300993) 161 kV Bus to COLINS 5 (512627) 161 kV Bus CKT 1 b. 3. Drop Load 1 at 5ELMCRK (300993) 161 kV Bus b. 4. Drop Load 2 at 5ELMCRK (300993) 161 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0097_P1 | 3 phase fault on NIXA 5 (505496) 161 kV Bus a. Apply Fault at the NIXA 5 (505496) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from NIXA 5 (505496) 161 kV Bus to TABLE R5 (505472) 161 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0098_P1 | 3 phase fault on NIXA 5 (505496) 161 kV Bus a. Apply Fault at the NIXA 5 (505496) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from NIXA 5 (505496) 161 kV Bus to NIXA 2 (505501) 69 kV Bus to NXA X2 1 (505499) 13.8 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0099_P1 | 3 phase fault on NIXA 5 (505496) 161 kV Bus a. Apply Fault at the NIXA 5 (505496) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from NIXA 5 (505496) 161 kV Bus to NIXA 2 (505501) 69 kV Bus to NXA X1 1 (505497) 13.8 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0100_P1 | 3 phase fault on LAR382 5 (547479) 161 kV Bus a. Apply Fault at the LAR382 5 (547479) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from LAR382 5 (547479) 161 kV Bus to CARTHAG5 (505488) 161 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0101_P1 | 3 phase fault on LAR382 5 (547479) 161 kV Bus a. Apply Fault at the LAR382 5 (547479) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from LAR382 5 (547479) 161 kV Bus to MON383 5 (547480) 161 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0102_P1 | 3 phase fault on CLAY 5 (549970) 161 kV Bus a. Apply Fault at the CLAY 5 (549970) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from CLAY 5 (549970) 161 kV Bus to MILL 5 (549962) 161 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0103_P1 | 3 phase fault on FLINTCR5 (506934) 161 kV Bus a. Apply Fault at the FLINTCR5 (506934) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from FLINTCR5 (506934) 161 kV Bus to SILOAM 5 (506948) 161 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0104_P1 | 3 phase fault on CLAY 5 (549970) 161 kV Bus a. Apply Fault at the CLAY 5 (549970) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from CLAY 5 (549970) 161 kV Bus to MENTOR 5 (549963) 161 kV Bus CKT 1 b. 2. Trip branch from MENTOR 5 (549963) 161 kV Bus to JAMES RIVER5 (549961) 161 kV Bus CKT 1 b. 3. Drop Load S at MENTOR 5 (549963) 161 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0105_P1 | 3 phase fault on CLAY 5 (549970) 161 kV Bus a. Apply Fault at the CLAY 5 (549970) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from CLAY 5 (549970) 161 kV Bus to 5LOGAN (301161) 161 kV Bus CKT 1 b. 2. Trip branch from 5LOGAN (301161) 161 kV Bus to 5MANSFDMN (300095) 161 kV Bus CKT 1 b. 3. Drop Load 1 at 5LOGAN (301161) 161 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0106_P1 | 3 phase fault on JAMES RIVER5 (549961) 161 kV Bus a. Apply Fault at the JAMES RIVER5 (549961) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from JAMES RIVER5 (549961) 161 kV Bus to JRPS 69B-2 2 (549903) 69 kV Bus to JRPS XF2 1 (549945) 13.2 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0107_P1 | 3 phase fault on JAMES RIVER5 (549961) 161 kV Bus a. Apply Fault at the JAMES RIVER5 (549961) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from JAMES RIVER5 (549961) 161 kV Bus to JAMES RIVER2 (549904) 69 kV Bus to JRPS XF1 1 (549944) 13.2 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0108_P1 | 3 phase fault on MAIN STREET5 (549958) 161 kV Bus a. Apply Fault at the MAIN STREET5 (549958) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from MAIN STREET5 (549958) 161 kV Bus to MAIN STREET2 (549921) 69 kV Bus to MAINST XF1 1 (549936) 13.2 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0109_P1 | 3 phase fault on MAIN STREET5 (549958) 161 kV Bus a. Apply Fault at the MAIN STREET5 (549958) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from MAIN STREET5 (549958) 161 kV Bus to MAIN STREET2 (549921) 69 kV Bus to MAINST XF2 1 (549938) 13.2 kV Bus CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0110_P1 | 3 phase fault on SUMMIT 5 (549966) 161 kV Bus a. Apply Fault at the SUMMIT 5 (549966) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from SUMMIT 5 (549966) 161 kV Bus to MC CARTNEY 5 (549968) 161 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0111_P1 | 3 phase fault on SUMMIT 5 (549966) 161 kV Bus a. Apply Fault at the SUMMIT 5 (549966) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from SUMMIT 5 (549966) 161 kV Bus to NORTON 5 (549967) 161 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0112_P1 | 3 phase fault on KANSATP5 (512714) 161 kV Bus a. Apply Fault at the KANSATP5 (512714) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from KANSATP5 (512714) 161 kV Bus to KANSAS 5 (512716) 161 kV Bus CKT 1 b. 2. Trip three winding transformer from KANSAS 5 (512716) 161 kV Bus to KANSAS 2 (512715) 69 kV Bus to KANSAS1 (512736) 13.8 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0113_P1 | 3 phase fault on KANSAS 2 (512715) 69 kV Bus a. Apply Fault at the KANSAS 2 (512715) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from KANSAS 2 (512715) 69 kV Bus to 2KANSASTP (301637) 69 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0114_P1 | 3 phase fault on SHIPERD5 (506980) 161 kV Bus a. Apply Fault at the SHIPERD5 (506980) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from SHIPERD5 (506980) 161 kV Bus to CENTRTN5 (506952) 161 kV Bus CKT 1 b. 2. Trip branch from CENTRTN5 (506952) 161 kV Bus to ECNTRTN5 (506929) 161 kV Bus CKT 1 b. 3. Drop Load 1 at CENTRTN5 (506952) 161 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0115_P1 | 3 phase fault on KANSAS 2 (512715) 69 kV Bus a. Apply Fault at the KANSAS 2 (512715) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from KANSAS 2 (512715) 69 kV Bus to 2WATTS (300987) 69 kV Bus CKT 1 b. 2. Trip branch from 2WATTS (300987) 69 kV Bus to 2WESTVIL (300988) 69 kV Bus CKT 1 b. 3. Trip branch from 2WESTVIL (300988) 69 kV Bus to 2BALDOR (300980) 69 kV Bus CKT 1 b. 4. Trip branch from 2BALDOR (300980) 69 kV Bus to STLWLGR2 (512721) 69 kV Bus CKT 1 b. 5. Drop Load 1 at 2WATTS (300987) 69 kV Bus b. 6. Drop Load 1 at 2WESTVIL (300988) 69 kV Bus b. 7. Drop Load 2 at 2WESTVIL (300988) 69 kV Bus b. 8. Drop Load 1 at 2BALDOR (300980) 69 kV Bus b. 9. Drop Shunt 1 at 2WESTVIL (300988) 69 kV Bus1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0116_P1 | 3 phase fault on 2KANSASTP (301637) 69 kV Bus a. Apply Fault at the 2KANSASTP (301637) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from 2KANSASTP (301637) 69 kV Bus to 2KANSASKM (301638) 69 kV Bus CKT 1 b. 2. Drop Load 2 at 2KANSASKM (301638) 69 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0117_P1 | 3 phase fault on 2KANSASTP (301637) 69 kV Bus a. Apply Fault at the 2KANSASTP (301637) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from 2KANSASTP (301637) 69 kV Bus to 2COLCOTP (301458) 69 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0118_P1 | 3 phase fault on SILMCTY5 (512643) 161 kV Bus a. Apply Fault at the SILMCTY5 (512643) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from SILMCTY5 (512643) 161 kV Bus to SILOAM 5 (506948) 161 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0119_P1 | 3 phase fault on SILMCTY5 (512643) 161 kV Bus a. Apply Fault at the SILMCTY5 (512643) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from SILMCTY5 (512643) 161 kV Bus to SILMCTY2 (512820) 69 kV Bus to SLMCTY1 1 (512849) 13.8 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0120_P1 | 3 phase fault on TONNEC2 (512753) 69 kV Bus a. Apply Fault at the TONNEC2 (512753) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from TONECE5 (512751) 161 kV Bus to TONNEC2 (512753) 69 kV Bus to TONNEC1 (512754) 13.2 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 763002 [G18-064-GEN10.5500]
04 - Southeast | 25W | Transfer | Group4_Fault_0121_P1 | 3 phase fault on SILMCTY5 (512643) 161 kV Bus a. Apply Fault at the SILMCTY5 (512643) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from SILMCTY5 (512643) 161 kV Bus to SILMCTY2 (512820) 69 kV Bus to SLMCTY2 1 (512850) 13.8 kV Bus CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0122_P1 | 3 phase fault on GRDA1 7 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 (512650) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from GRDA1 7 (512650) 345 kV Bus to GRDA1 5 (512656) 161 kV Bus to GRDA1 (512821) 13.8 kV Bus CKT 1 b. 2. Drop Shunt 1 at GRDA1 (512821) 13.8 kV Bus1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0123_P1 | 3 phase fault on GRDA1 7 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 (512650) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from GRDA1 7 (512650) 345 kV Bus to GRDA1 5 (512656) 161 kV Bus to GRDA2 1 (512826) 13.8 kV Bus CKT 2 b. 2. Drop Shunt 1 at GRDA2 1 (512826) 13.8 kV Bus1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0124_P1 | 3 phase fault on GRDA1 7 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 (512650) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from GRDA1 7 (512650) 345 kV Bus to 7SPORTSMAN (300740) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0125_P1 | 3 phase fault on GRDA1 7 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 (512650) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from GRDA1 7 (512650) 345 kV Bus to GREC TAP5 (512865) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0126_P1 | 3 phase fault on BROOKLINE 7 (549984) 345 kV Bus a. Apply Fault at the BROOKLINE 7 (549984) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from BROOKLINE 7 (549984) 345 kV Bus to BROOKLINE 5 (549969) 161 kV Bus to BRKLNE XF1 1 (549988) 13.2 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0127_P1 | 3 phase fault on BROOKLINE 7 (549984) 345 kV Bus a. Apply Fault at the BROOKLINE 7 (549984) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from BROOKLINE 7 (549984) 345 kV Bus to BROOKLINE 5 (549969) 161 kV Bus to BRKLNE XF2 1 (549989) 13.2 kV Bus CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0128_P1 | 3 phase fault on BROOKLINE 7 (549984) 345 kV Bus a. Apply Fault at the BROOKLINE 7 (549984) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from BROOKLINE 7 (549984) 345 kV Bus to 7MORGAN (300045) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0129_P1 | 3 phase fault on SILOAM 5 (506948) 161 kV Bus a. Apply Fault at the SILOAM 5 (506948) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from SILOAM 5 (506948) 161 kV Bus to CHAMSPR5 (506944) 161 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0130_P1 | 3 phase fault on SILOAM 5 (506948) 161 kV Bus a. Apply Fault at the SILOAM 5 (506948) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from SILOAM 5 (506948) 161 kV Bus to SILOAM 2 (506973) 69 kV Bus to SILOAM-1 (506917) 13.2 kV Bus CKT 1 b. 2. Drop Shunt 1 at SILOAM 2 (506973) 69 kV Bus1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0131_P1 | 3 phase fault on TONECE5 (512751) 161 kV Bus a. Apply Fault at the TONECE5 (512751) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from TONECE5 (512751) 161 kV Bus to SILMCTY5 (512643) 161 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 763002 [G18-064-GEN10.5500]
04 - Southeast | 25W | Transfer | Group4_Fault_0132_P1 | 3 phase fault on TONTITN5 (506957) 161 kV Bus a. Apply Fault at the TONTITN5 (506957) 161 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from TONTITN7 (506959) 345 kV Bus to TONTITN5 (506957) 161 kV Bus to TONTITN1 (506958) 13.8 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0133_P1 | 3 phase fault on TONTITN5 (506957) 161 kV Bus a. Apply Fault at the TONTITN5 (506957) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from TONTITN5 (506957) 161 kV Bus to CHAMSPR5 (506944) 161 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0134_P1 | 3 phase fault on DEC392 5 (547484) 161 kV Bus a. Apply Fault at the DEC392 5 (547484) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from DEC392 5 (547484) 161 kV Bus to DEC392 2 (547594) 69 kV Bus to DEC392 1 (547714) 12.5 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0135_P1 | 3 phase fault on DEC392 5 (547484) 161 kV Bus a. Apply Fault at the DEC392 5 (547484) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from DEC392 5 (547484) 161 kV Bus to NOL435 5 (547496) 161 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0136_P1 | 3 phase fault on SILMCTY2 (512820) 69 kV Bus a. Apply Fault at the SILMCTY2 (512820) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from SILMCTY2 (512820) 69 kV Bus to SSSWES2 (512730) 69 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0137_P1 | 3 phase fault on SILMCTY2 (512820) 69 kV Bus a. Apply Fault at the SILMCTY2 (512820) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from SILMCTY2 (512820) 69 kV Bus to SSSWTP2 (512737) 69 kV Bus CKT 1 b. 2. Trip branch from SSSWTP2 (512737) 69 kV Bus to SSMOSS2 (512744) 69 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0138_P1 | 3 phase fault on 7SPORTSMAN (300740) 345 kV Bus a. Apply Fault at the 7SPORTSMAN (300740) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from 7SPORTSMAN (300740) 345 kV Bus to 5SPORTSMAN (300741) 161 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0139_P1 | 3 phase fault on 7SPORTSMAN (300740) 345 kV Bus a. Apply Fault at the 7SPORTSMAN (300740) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from 7SPORTSMAN (300740) 345 kV Bus to 5SPORTSMAN (300741) 161 kV Bus CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0140_P1 | 3 phase fault on GREC TAP5 (512865) 345 kV Bus a. Apply Fault at the GREC TAP5 (512865) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from GREC TAP5 (512865) 345 kV Bus to IGLOOV 7 (513596) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0141_P1 | 3 phase fault on TONECE5 (512751) 161 kV Bus a. Apply Fault at the TONECE5 (512751) 161 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from TONECE7 (512750) 345 kV Bus to TONECE5 (512751) 161 kV Bus to TONECE1 (512752) 13.2 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 763002 [G18-064-GEN10.5500]
04 - Southeast | 25W | Transfer | Group4_Fault_0142_P1 | 3 phase fault on GRDA1 5 (512656) 161 kV Bus a. Apply Fault at the GRDA1 5 (512656) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from GRDA1 5 (512656) 161 kV Bus to MAID 5 (512648) 161 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0143_P1 | 3 phase fault on GRDA1 5 (512656) 161 kV Bus a. Apply Fault at the GRDA1 5 (512656) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from GRDA1 5 (512656) 161 kV Bus to CLARMR 5 (512651) 161 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0144_P1 | 3 phase fault on GRDA1 5 (512656) 161 kV Bus a. Apply Fault at the GRDA1 5 (512656) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from GRDA1 5 (512656) 161 kV Bus to WAGNOR 5 (512700) 161 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0145_P1 | 3 phase fault on GRDA1 5 (512656) 161 kV Bus a. Apply Fault at the GRDA1 5 (512656) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from GRDA1 5 (512656) 161 kV Bus to WMAIN ST5 (512742) 161 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0146_P1 | 3 phase fault on GRDA1 5 (512656) 161 kV Bus a. Apply Fault at the GRDA1 5 (512656) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from GRDA1 5 (512656) 161 kV Bus to GRDA1 2 (512727) 69 kV Bus to GRDA1 1 (512816) 13.8 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0147_P1 | 3 phase fault on BROOKLINE 5 (549969) 161 kV Bus a. Apply Fault at the BROOKLINE 5 (549969) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from BROOKLINE 5 (549969) 161 kV Bus to 5MORGAN (300101) 161 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0148_P1 | 3 phase fault on BROOKLINE 5 (549969) 161 kV Bus a. Apply Fault at the BROOKLINE 5 (549969) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from BROOKLINE 5 (549969) 161 kV Bus to SPRGFLD5 (505492) 161 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0149_P1 | 3 phase fault on BROOKLINE 5 (549969) 161 kV Bus a. Apply Fault at the BROOKLINE 5 (549969) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from BROOKLINE 5 (549969) 161 kV Bus to JTEC 5 (549954) 161 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0150_P1 | 3 phase fault on BROOKLINE 5 (549969) 161 kV Bus a. Apply Fault at the BROOKLINE 5 (549969) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from BROOKLINE 5 (549969) 161 kV Bus to JUNCTION 5 (549955) 161 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0151_P1 | 3 phase fault on SILOAM 2 (506973) 69 kV Bus a. Apply Fault at the SILOAM 2 (506973) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from SILOAM 2 (506973) 69 kV Bus to LINCOLN2 (506972) 69 kV Bus CKT 1 b. 2. Trip branch from LINCOLN2 (506972) 69 kV Bus to PRGROVE2 (506941) 69 kV Bus CKT 1 b. 3. Trip branch from PRGROVE2 (506941) 69 kV Bus to GREENLD2 (506936) 69 kV Bus CKT 1 b. 4. Drop Shunt 1 at SILOAM 2 (506973) 69 kV Bus1 b. 5. Drop Load A1 at LINCOLN2 (506972) 69 kV Bus b. 6. Drop Load 1 at PRGROVE2 (506941) 69 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0152_P1 | 3 phase fault on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from TONECE7 (512750) 345 kV Bus to GRDA1 7 (512650) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0153_P1 | 3 phase fault on TONTITN5 (506957) 161 kV Bus a. Apply Fault at the TONTITN5 (506957) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from TONTITN5 (506957) 161 kV Bus to ELMSPRGS 5 (504010) 161 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0154_P1 | 3 phase fault on TONTITN5 (506957) 161 kV Bus a. Apply Fault at the TONTITN5 (506957) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from TONTITN5 (506957) 161 kV Bus to BRUSHCRK_5 (506991) 161 kV Bus CKT 1 b. 2. Trip branch from BRUSHCRK_5 (506991) 161 kV Bus to LOWELL 5 (506938) 161 kV Bus CKT 1 b. 3. Trip branch from LOWELL 5 (506938) 161 kV Bus to ROGERS 5 (506942) 161 kV Bus CKT 1 b. 4. Trip branch from ROGERS 5 (506942) 161 kV Bus to EROGERS5 (506931) 161 kV Bus CKT 1 b. 5. Drop Load 1 at BRUSHCRK_5 (506991) 161 kV Bus b. 6. Drop Load 1 at LOWELL 5 (506938) 161 kV Bus b. 7. Drop Load 1 at ROGERS 5 (506942) 161 kV Bus b. 8. Drop Shunt 1 at ROGERS 5 (506942) 161 kV Bus1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0155_P1 | 3 phase fault on ELMSPRGS 5 (504010) 161 kV Bus a. Apply Fault at the ELMSPRGS 5 (504010) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from ELMSPRGS 5 (504010) 161 kV Bus to DYESS 5 (506927) 161 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0156_P1 | 3 phase fault on ELMSPRGS 5 (504010) 161 kV Bus a. Apply Fault at the ELMSPRGS 5 (504010) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from ELMSPRGS 5 (504010) 161 kV Bus to ELMSPG_1 2 (504011) 69 kV Bus to ELMSP_T1 1 (504012) 13.8 kV Bus CKT 1 b. 2. Drop Shunt 1 at ELMSPG_1 2 (504011) 69 kV Bus1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0157_P1 | 3 phase fault on ELMSPRGS 5 (504010) 161 kV Bus a. Apply Fault at the ELMSPRGS 5 (504010) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from ELMSPRGS 5 (504010) 161 kV Bus to ELMSPG_2 2 (504013) 69 kV Bus to ELMSP_T2 1 (504014) 13.8 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0158_P1 | 3 phase fault on TONTITN7 (506959) 345 kV Bus a. Apply Fault at the TONTITN7 (506959) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from TONTITN7 (506959) 345 kV Bus to CHAMSPR7 (506945) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0159_P1 | 3 phase fault on DEC392 2 (547594) 69 kV Bus a. Apply Fault at the DEC392 2 (547594) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from DEC392 2 (547594) 69 kV Bus to DEC467 2 (547569) 69 kV Bus CKT 1 b. 2. Trip branch from DEC467 2 (547569) 69 kV Bus to GRA700 2 (547617) 69 kV Bus CKT 1 b. 3. Trip branch from GRA700 2 (547617) 69 kV Bus to NOL435 2 (547610) 69 kV Bus CKT 1 b. 4. Drop Load 1 at DEC467 2 (547569) 69 kV Bus b. 5. Drop Load 1 at GRA700 2 (547617) 69 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0160_P1 | 3 phase fault on ECNTRTN5 (506929) 161 kV Bus a. Apply Fault at the ECNTRTN5 (506929) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from ECNTRTN5 (506929) 161 kV Bus to ECENT_1 2 (504006) 69 kV Bus to ECENT_T1 1 (504007) 13.8 kV Bus CKT 1 b. 2. Drop Shunt 1 at ECENT_1 2 (504006) 69 kV Bus1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0161_P1 | 3 phase fault on ECNTRTN5 (506929) 161 kV Bus a. Apply Fault at the ECNTRTN5 (506929) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from ECNTRTN5 (506929) 161 kV Bus to ECENT_2 2 (504008) 69 kV Bus to ECENT_T2 1 (504009) 13.8 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0162_P1 | 3 phase fault on ECNTRTN5 (506929) 161 kV Bus a. Apply Fault at the ECNTRTN5 (506929) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from ECNTRTN5 (506929) 161 kV Bus to ECNTRTN2 (506928) 69 kV Bus to ECNTR2-1 (506924) 12.47 kV Bus CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0163_P1 | 3 phase fault on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from TONECE7 (512750) 345 kV Bus to FLINTCR7 (506935) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0164_P1 | 3 phase fault on ECNTRTN5 (506929) 161 kV Bus a. Apply Fault at the ECNTRTN5 (506929) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from ECNTRTN5 (506929) 161 kV Bus to ECNTRTN2 (506928) 69 kV Bus to ECNTR1-1 (506923) 12.47 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0165_P1 | 3 phase fault on ECNTRTN5 (506929) 161 kV Bus a. Apply Fault at the ECNTRTN5 (506929) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from ECNTRTN5 (506929) 161 kV Bus to BENT_SL5 (506963) 161 kV Bus CKT 1 b. 2. Trip branch from BENT_SL5 (506963) 161 kV Bus to BENTVJ_5 (506962) 161 kV Bus CKT 1 b. 3. Trip branch from BENTVJ_5 (506962) 161 kV Bus to BENT ML5 (506955) 161 kV Bus CKT 1 b. 4. Trip branch from BENT ML5 (506955) 161 kV Bus to WROGERS 5 (504200) 161 kV Bus CKT 1 b. 5. Trip branch from WROGERS 5 (504200) 161 kV Bus to EROGERS5 (506931) 161 kV Bus CKT 1 b. 6. Drop Load 1 at BENT_SL5 (506963) 161 kV Bus b. 7. Drop Load 1 at BENTVJ_5 (506962) 161 kV Bus b. 8. Drop Load 1 at BENT ML5 (506955) 161 kV Bus b. 9. Drop Load A1 at WROGERS 5 (504200) 161 kV Bus b. 10. Drop Load A2 at WROGERS 5 (504200) 161 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0166_P1 | 3 phase fault on ECNTRTN2 (506928) 69 kV Bus a. Apply Fault at the ECNTRTN2 (506928) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from ECNTRTN2 (506928) 69 kV Bus to BENTNVL2 (506965) 69 kV Bus CKT 1 b. 2. Trip branch from BENTNVL2 (506965) 69 kV Bus to DIXLAND2 (506925) 69 kV Bus CKT 1 b. 3. Trip branch from DIXLAND2 (506925) 69 kV Bus to NROGERS2 (506940) 69 kV Bus CKT 1 b. 4. Drop Load 1 at BENTNVL2 (506965) 69 kV Bus b. 5. Drop Load 1 at DIXLAND2 (506925) 69 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0167_P1 | 3 phase fault on IGLOOV 7 (513596) 345 kV Bus a. Apply Fault at the IGLOOV 7 (513596) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from IGLOOV 7 (513596) 345 kV Bus to IGLOOV1 5 (513593) 161 kV Bus to IGLOTER1 1 (513592) 13.2 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0168_P1 | 3 phase fault on IGLOOV 7 (513596) 345 kV Bus a. Apply Fault at the IGLOOV 7 (513596) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from IGLOOV 7 (513596) 345 kV Bus to IGLOOV2 5 (513595) 161 kV Bus to IGLOTER2 1 (513594) 13.2 kV Bus CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0169_P1 | 3 phase fault on GRDA1 5 (512656) 161 kV Bus a. Apply Fault at the GRDA1 5 (512656) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from GRDA1 5 (512656) 161 kV Bus to MAID 5 (512648) 161 kV Bus CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0170_P1 | 3 phase fault on MAID 5 (512648) 161 kV Bus a. Apply Fault at the MAID 5 (512648) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from MAID 5 (512648) 161 kV Bus to 5CHOTEAU1 (300069) 161 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0171_P1 | 3 phase fault on MAID 5 (512648) 161 kV Bus a. Apply Fault at the MAID 5 (512648) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from MAID 5 (512648) 161 kV Bus to KERR GR5 (512635) 161 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0172_P1 | 3 phase fault on MAID 5 (512648) 161 kV Bus a. Apply Fault at the MAID 5 (512648) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from MAID 5 (512648) 161 kV Bus to KERR GR5 (512635) 161 kV Bus CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0173_P1 | 3 phase fault on FLINTCR7 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 (506935) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from FLINTCR7 (506935) 345 kV Bus to BROOKLINE 7 (549984) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0174_P1 | 3 phase fault on MAID 5 (512648) 161 kV Bus a. Apply Fault at the MAID 5 (512648) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from MAID 5 (512648) 161 kV Bus to CATSAGR5 (512638) 161 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0175_P1 | 3 phase fault on MAID 5 (512648) 161 kV Bus a. Apply Fault at the MAID 5 (512648) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from MAID 5 (512648) 161 kV Bus to CATSAGR5 (512638) 161 kV Bus CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0176_P1 | 3 phase fault on MAID 5 (512648) 161 kV Bus a. Apply Fault at the MAID 5 (512648) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from MAID 5 (512648) 161 kV Bus to LOCSTGVKM 5 (513050) 161 kV Bus CKT 1 b. 2. Trip branch from LOCSTGVKM 5 (513050) 161 kV Bus to 5CDRCRST (301344) 161 kV Bus CKT 1 b. 3. Drop Load 1 at LOCSTGVKM 5 (513050) 161 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0177_P1 | 3 phase fault on MAID 5 (512648) 161 kV Bus a. Apply Fault at the MAID 5 (512648) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from MAID 5 (512648) 161 kV Bus to MAID 2 (512626) 69 kV Bus to MAITER1 1 (512836) 13.2 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0178_P1 | 3 phase fault on MAID 5 (512648) 161 kV Bus a. Apply Fault at the MAID 5 (512648) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from MAID 5 (512648) 161 kV Bus to MAID 2 (512626) 69 kV Bus to MAITER2 1 (512837) 13.2 kV Bus CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0179_P1 | 3 phase fault on MAID 5 (512648) 161 kV Bus a. Apply Fault at the MAID 5 (512648) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from MAID 5 (512648) 161 kV Bus to DRYGULCH5 (512629) 161 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0180_P1 | 3 phase fault on MAID 5 (512648) 161 kV Bus a. Apply Fault at the MAID 5 (512648) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from MAID 5 (512648) 161 kV Bus to GERALDGAY5 (512760) 161 kV Bus CKT 1 b. 2. Trip branch from GERALDGAY5 (512760) 161 kV Bus to NWMAID5 (512757) 161 kV Bus CKT 1 b. 3. Drop Load 1 at GERALDGAY5 (512760) 161 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0181_P1 | 3 phase fault on WMAIN ST5 (512742) 161 kV Bus a. Apply Fault at the WMAIN ST5 (512742) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from WMAIN ST5 (512742) 161 kV Bus to NWMAID5 (512757) 161 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0182_P1 | 3 phase fault on GRDA1 2 (512727) 69 kV Bus a. Apply Fault at the GRDA1 2 (512727) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from GRDA1 2 (512727) 69 kV Bus to MAIDTP2 (512625) 69 kV Bus CKT 1 b. 2. Trip branch from MAIDTP2 (512625) 69 kV Bus to HUNT 2 (512671) 69 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0183_P1 | 3 phase fault on SPRGFLD5 (505492) 161 kV Bus a. Apply Fault at the SPRGFLD5 (505492) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from SPRGFLD5 (505492) 161 kV Bus to NIXA 5 (505496) 161 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0184_P1 | 3 phase fault on FLINTCR7 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 (506935) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from FLINTCR7 (506935) 345 kV Bus to SHIPERD7 (506979) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0185_P1 | 3 phase fault on SPRGFLD5 (505492) 161 kV Bus a. Apply Fault at the SPRGFLD5 (505492) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from SPRGFLD5 (505492) 161 kV Bus to BATTLEFIELD5 (549959) 161 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0186_P1 | 3 phase fault on SPRGFLD5 (505492) 161 kV Bus a. Apply Fault at the SPRGFLD5 (505492) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from SPRGFLD5 (505492) 161 kV Bus to CLAY 5 (549970) 161 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0187_P1 | 3 phase fault on SPRGFLD5 (505492) 161 kV Bus a. Apply Fault at the SPRGFLD5 (505492) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from SPRGFLD5 (505492) 161 kV Bus to 5NIXA-1 (300678) 161 kV Bus CKT 1 b. 2. Trip branch from 5NIXA-1 (300678) 161 kV Bus to 5JAMESV (300089) 161 kV Bus CKT 1 b. 3. Drop Load 1 at 5NIXA-1 (300678) 161 kV Bus b. 4. Drop Load 2 at 5NIXA-1 (300678) 161 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0188_P1 | 3 phase fault on SPRGFLD5 (505492) 161 kV Bus a. Apply Fault at the SPRGFLD5 (505492) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from SPRGFLD5 (505492) 161 kV Bus to SPRGFLD2 (505494) 69 kV Bus to SPF X1 1 (505491) 13.8 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0189_P1 | 3 phase fault on SPRGFLD5 (505492) 161 kV Bus a. Apply Fault at the SPRGFLD5 (505492) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from SPRGFLD5 (505492) 161 kV Bus to SPRGFLD2 (505494) 69 kV Bus to SPF X2 1 (505493) 13.8 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0190_P1 | 3 phase fault on SPRGFLD5 (505492) 161 kV Bus a. Apply Fault at the SPRGFLD5 (505492) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from SPRGFLD5 (505492) 161 kV Bus to SPRGFLD2 (505494) 69 kV Bus to SPF X3 1 (505495) 13.8 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0191_P1 | 3 phase fault on SPRGFLD5 (505492) 161 kV Bus a. Apply Fault at the SPRGFLD5 (505492) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from SPRGFLD5 (505492) 161 kV Bus to LAR382 5 (547479) 161 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0192_P1 | 3 phase fault on JTEC 5 (549954) 161 kV Bus a. Apply Fault at the JTEC 5 (549954) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from JTEC 5 (549954) 161 kV Bus to JAMES RIVER5 (549961) 161 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0193_P1 | 3 phase fault on JTEC 5 (549954) 161 kV Bus a. Apply Fault at the JTEC 5 (549954) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from JTEC 5 (549954) 161 kV Bus to 5BTLFD (300348) 161 kV Bus CKT 1 b. 2. Trip branch from 5BTLFD (300348) 161 kV Bus to 5JAMESV (300089) 161 kV Bus CKT 1 b. 3. Drop Load 1 at 5BTLFD (300348) 161 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0194_P1 | 3 phase fault on JTEC 5 (549954) 161 kV Bus a. Apply Fault at the JTEC 5 (549954) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from JTEC 5 (549954) 161 kV Bus to SW DISP PLT5 (549960) 161 kV Bus CKT 1 b. 2. Trip branch from SW DISP PLT5 (549960) 161 kV Bus to BATTLEFIELD5 (549959) 161 kV Bus CKT 1 b. 3. Drop Load W at SW DISP PLT5 (549960) 161 kV Bus b. 4. Drop Load E at SW DISP PLT5 (549960) 161 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0195_P1 | 3 phase fault on FLINTCR7 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 (506935) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from FLINTCR7 (506935) 345 kV Bus to FLINTCR5 (506934) 161 kV Bus to FLINT1-1 (506921) 13.8 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0196_P1 | 3 phase fault on JUNCTION 5 (549955) 161 kV Bus a. Apply Fault at the JUNCTION 5 (549955) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from JUNCTION 5 (549955) 161 kV Bus to NICHOLS 5 (549956) 161 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0197_P1 | 3 phase fault on JUNCTION 5 (549955) 161 kV Bus a. Apply Fault at the JUNCTION 5 (549955) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from JUNCTION 5 (549955) 161 kV Bus to PIC WEST 5 (549971) 161 kV Bus CKT 1 b. 2. Trip branch from PIC WEST 5 (549971) 161 kV Bus to SUMMIT 5 (549966) 161 kV Bus CKT 1 b. 3. Drop Load S at PIC WEST 5 (549971) 161 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0198_P1 | 3 phase fault on CHAMSPR7 (506945) 345 kV Bus a. Apply Fault at the CHAMSPR7 (506945) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from CHAMSPR7 (506945) 345 kV Bus to CHAMSPR5 (506944) 161 kV Bus to CHAMSPR1 (506919) 13.8 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0199_P1 | 3 phase fault on CHAMSPR7 (506945) 345 kV Bus a. Apply Fault at the CHAMSPR7 (506945) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from CHAMSPR7 (506945) 345 kV Bus to CLARKSV7 (509745) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0200_P1 | 3 phase fault on IGLOOV1 5 (513593) 161 kV Bus a. Apply Fault at the IGLOOV1 5 (513593) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from IGLOOV1 5 (513593) 161 kV Bus to HERRON 5 (513591) 161 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0201_P1 | 3 phase fault on IGLOOV2 5 (513595) 161 kV Bus a. Apply Fault at the IGLOOV2 5 (513595) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from IGLOOV2 5 (513595) 161 kV Bus to HERRON 5 (513591) 161 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0202_P1 | 3 phase fault on MAID 2 (512626) 69 kV Bus a. Apply Fault at the MAID 2 (512626) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from MAID 2 (512626) 69 kV Bus to REDDEN 2 (512698) 69 kV Bus CKT 1 b. 2. Trip branch from REDDEN 2 (512698) 69 kV Bus to CASTING TAP2 (512685) 69 kV Bus CKT 1 b. 3. Trip branch from CASTING TAP2 (512685) 69 kV Bus to AMERCAST N2 (512683) 69 kV Bus CKT 1 b. 4. Drop Load 1 at REDDEN 2 (512698) 69 kV Bus b. 5. Drop Load 1 at AMERCAST N2 (512683) 69 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0203_P1 | 3 phase fault on MAID 2 (512626) 69 kV Bus a. Apply Fault at the MAID 2 (512626) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from MAID 2 (512626) 69 kV Bus to AMERCAST S2 (512681) 69 kV Bus CKT 1 b. 2. Trip branch from AMERCAST S2 (512681) 69 kV Bus to CPPTAP 2 (512661) 69 kV Bus CKT 1 b. 3. Trip branch from CPPTAP 2 (512661) 69 kV Bus to PRYORCHEM2 (512699) 69 kV Bus CKT 1 b. 4. Trip branch from PRYORCHEM2 (512699) 69 kV Bus to AIRPROD2 (512687) 69 kV Bus CKT 1 b. 5. Trip branch from AIRPROD2 (512687) 69 kV Bus to HUNT 2 (512671) 69 kV Bus CKT 1 b. 6. Drop Load 1 at AMERCAST S2 (512681) 69 kV Bus b. 7. Drop Load 1 at PRYORCHEM2 (512699) 69 kV Bus b. 8. Drop Load 1 at AIRPROD2 (512687) 69 kV Bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0204_P1 | 3 phase fault on BATTLEFIELD5 (549959) 161 kV Bus a. Apply Fault at the BATTLEFIELD5 (549959) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from BATTLEFIELD5 (549959) 161 kV Bus to MAIN STREET5 (549958) 161 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0205_P1 | 3 phase fault on BATTLEFIELD5 (549959) 161 kV Bus a. Apply Fault at the BATTLEFIELD5 (549959) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from BATTLEFIELD5 (549959) 161 kV Bus to BATTLEFIELD2 (549979) 69 kV Bus to BATLEFLDXF11 (549980) 13.2 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0206_P4 | a. Apply single phase fault at FLINTCR7 (506935) 345 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from FLINTCR7 (506935) 345 kV to TONECE7 (512750) 345 kV CKT 1 b. 2. Trip branch from FLINTCR7 (506935) 345 kV to SHIPERD7 (506979) 345 kV CKT 1 b. 3. Trip three winding transformer from SHIPERD7 (506979) 345 kV to SHIPERD5 (506980) kV to SHIPERD1 (506981) 13.8 kV CKT1 b. 4. Trip branch from SHIPERD5 (506980) 161 kV to CENTRTN5 (506952) 161 kV CKT 1 b. 5. Trip branch from CENTRTN5 (506952) 161 kV to ECNTRTN5 (506929) 161 kV CKT 1 b. 6. Drop Load 1 CENTRTN5 (506952) 161 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0207_P4 | a. Apply single phase fault at SILMCTY5 (512643) 161 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from SILMCTY5 (512643) 161 kV to SILOAM 5 (506948) 161 kV CKT 1 b. 2. Trip branch from SILMCTY5 (512643) 161 kV to SILSPWW5 (512642) 161 kV CKT 1 b. 3. Trip branch from SILSPWW5 (512642) 161 kV to KANSATP5 (512714) 161 kV CKT 1 b. 4. Drop Load 1 SILSPWW5 (512642) 161 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0208_P4 | a. Apply single phase fault at FLINTCR5 (506934) 161 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from FLINTCR5 (506934) 161 kV to GENTRY 5 (504201) 161 kV CKT 1 b. 2. Trip branch from GENTRY 5 (504201) 161 kV to BEN279_5 (506960) 161 kV CKT 1 b. 3. Trip branch from BEN279_5 (506960) 161 kV to GREENHOUSE 5 (506990) 161 kV CKT 1 b. 4. Trip branch from GREENHOUSE 5 (506990) 161 kV to ECNTRTN5 (506929) 161 kV CKT 1 b. 5. Trip branch from FLINTCR5 (506934) 161 kV to TONTITN5 (506957) 161 kV CKT 1 b. 6. Drop Load A1 GENTRY 5 (504201) 161 kV b. 7. Drop Load 1 BEN279_5 (506960) 161 kV b. 8. Drop Load 1 GREENHOUSE 5 (506990) 161 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0210_P4 | a. Apply single phase fault at BROOKLINE 5 (549969) 161 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from BROOKLINE 5 (549969) 161 kV to SPRGFLD5 (505492) 161 kV CKT 1 b. 2. Trip branch from BROOKLINE 5 (549969) 161 kV to JUNCTION 5 (549955) 161 kV CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0211_P4 | a. Apply single phase fault at TAHLQH 5 (512655) 161 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from TAHLQH 5 (512655) 161 kV to 5CDRCRST (301344) 161 kV CKT 1 b. 2. Trip branch from TAHLQH 5 (512655) 161 kV to 7CLANS 5 (515956) 161 kV CKT 1 b. 3. Trip branch from 7CLANS 5 (515956) 161 kV to KETOWAH5 (516027) 161 kV CKT 1 b. 4. Trip branch from KETOWAH5 (516027) 161 kV to MUSKOGE5 (515222) 161 kV CKT 1 b. 5. Drop Load 1 SILSPWW5 (512642) 161 kV b. 6. Drop Load 1 7CLANS 5 (515956) 161 kV b. 7. Drop Load 1 KETOWAH5 (516027) 161 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0212_P4 | a. Apply single phase fault at CHAMSPR5 (506944) 161 kV b. Clear Fault after 16 cycles: b. 1. Trip three winding transformer from CHAMSPR5 (506944) 161 kV to CHAMSPR7 (506945) kV to CHAMSPR1 (506919) 13.8 kV CKT1 b. 2. Trip branch from CHAMSPR5 (506944) 161 kV to TONTITN5 (506957) 161 kV CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0213_P4 | a. Apply single phase fault at ECNTRTN5 (506929) 161 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from ECNTRTN5 (506929) 161 kV to CENTRTN5 (506952) 161 kV CKT 1 b. 2. Trip branch from CENTRTN5 (506952) 161 kV to SHIPERD5 (506980) 161 kV CKT 1 b. 3. Trip three winding transformer from SHIPERD7 (506979) 345 kV to SHIPERD5 (506980) kV to SHIPERD1 (506981) 13.8 kV CKT1 b. 4. Trip branch from ECNTRTN5 (506929) 161 kV to BENT_SL5 (506963) 161 kV CKT 1 b. 5. Trip branch from BENT_SL5 (506963) 161 kV to BENTVJ_5 (506962) 161 kV CKT 1 b. 6. Trip branch from BENTVJ_5 (506962) 161 kV to BENT ML5 (506955) 161 kV CKT 1 b. 7. Trip branch from BENT ML5 (506955) 161 kV to WROGERS 5 (504200) 161 kV CKT 1 b. 8. Trip branch from WROGERS 5 (504200) 161 kV to EROGERS5 (506931) 161 kV CKT 1 b. 9. Drop Load 1 CENTRTN5 (506952) 161 kV b. 10. Drop Load 1 BENT_SL5 (506963) 161 kV b. 11. Drop Load 1 BENTVJ_5 (506962) 161 kV b. 12. Drop Load 1 BENT ML5 (506955) 161 kV b. 13. Drop Load A1 WROGERS 5 (504200) 161 kV b. 14. Drop Load A2 WROGERS 5 (504200) 161 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0214_P4 | a. Apply single phase fault at STLWLGR2 (512721) 69 kV b. Clear Fault after 16 cycles: b. 1. Trip three winding transformer from STLWLGR2 (512721) 69 kV to STIWEL5 (512704) kV to STLWELL1 (512819) 13.8 kV CKT1 b. 2. Trip branch from STIWEL5 (512704) 161 kV to BRIGSKM 5 (513044) 161 kV CKT 1 b. 3. Trip branch from STLWLGR2 (512721) 69 kV to STILWELLCTY2 (512701) 69 kV CKT 1 b. 4. Drop Load 1 STILWELLCTY2 (512701) 69 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0215_P1 | 3 phase fault on RANCHRD7 (515576) 345 kV Bus a. Apply Fault at the RANCHRD7 (515576) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from RANCHRD7 (515576) 345 kV Bus to SOONER 7 (514803) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0216_P1 | 3 phase fault on SOONER 4 (514802) 138 kV Bus a. Apply Fault at the SOONER 4 (514802) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from SOONER 4 (514802) 138 kV Bus to MILLERT4 (514704) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0217_P1 | 3 phase fault on CTNWOOD4 (514827) 138 kV Bus a. Apply Fault at the CTNWOOD4 (514827) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from CTNWOOD4 (514827) 138 kV Bus to LBRTYLK4 (515373) 138 kV Bus CKT 1 b. 2. Trip branch from LBRTYLK4 (515373) 138 kV Bus to WATRLOO4 (514831) 138 kV Bus CKT 1 b. 3. Trip branch from WATRLOO4 (514831) 138 kV Bus to WHITESB4 (515467) 138 kV Bus CKT 1 b. 4. Trip branch from WHITESB4 (515467) 138 kV Bus to MITCHSB4 (515466) 138 kV Bus CKT 1 b. 5. Trip branch from MITCHSB4 (515466) 138 kV Bus to KETCHTP4 (514828) 138 kV Bus CKT 1 b. 6. Drop Load 1 at LBRTYLK4 (515373) 138 kV Bus b. 7. Drop Load 1 at WATRLOO4 (514831) 138 kV Bus b. 8. Drop Load 1 at WHITESB4 (515467) 138 kV Bus b. 9. Drop Load 1 at MITCHSB4 (515466) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0218_P1 | 3 phase fault on KETCHTP4 (514828) 138 kV Bus a. Apply Fault at the KETCHTP4 (514828) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from KETCHTP4 (514828) 138 kV Bus to NORTWST4 (514879) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0219_P1 | 3 phase fault on KETCHTP4 (514828) 138 kV Bus a. Apply Fault at the KETCHTP4 (514828) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from KETCHTP4 (514828) 138 kV Bus to KETCH 4 (514834) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0220_P1 | 3 phase fault on KETCH 4 (514834) 138 kV Bus a. Apply Fault at the KETCH 4 (514834) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from KETCH 4 (514834) 138 kV Bus to DANFRTH4 (514833) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0221_P1 | 3 phase fault on KETCH 4 (514834) 138 kV Bus a. Apply Fault at the KETCH 4 (514834) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from KETCH 4 (514834) 138 kV Bus to FAIRFLD4 (515468) 138 kV Bus CKT 1 b. 2. Trip branch from FAIRFLD4 (515468) 138 kV Bus to CHISHOM4 (515374) 138 kV Bus CKT 1 b. 3. Trip branch from CHISHOM4 (515374) 138 kV Bus to SKYLINE4 (514850) 138 kV Bus CKT 1 b. 4. Drop Load 1 at FAIRFLD4 (515468) 138 kV Bus b. 5. Drop Load 1 at CHISHOM4 (515374) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0222_P1 | 3 phase fault on SOONER 4 (514802) 138 kV Bus a. Apply Fault at the SOONER 4 (514802) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from SOONER 4 (514802) 138 kV Bus to PERRY 4 (514707) 138 kV Bus CKT 1 b. 2. Trip branch from PERRY 4 (514707) 138 kV Bus to COWCRK 4 (514706) 138 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0223_P1 | 3 phase fault on SOONER 4 (514802) 138 kV Bus a. Apply Fault at the SOONER 4 (514802) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from SOONER 4 (514802) 138 kV Bus to SNRPMPT4 (514798) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0224_P1 | 3 phase fault on SOONER 4 (514802) 138 kV Bus a. Apply Fault at the SOONER 4 (514802) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from SOONER 4 (514802) 138 kV Bus to MORISNT4 (515447) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0225_P1 | 3 phase fault on WEKIWA-7 (509755) 345 kV Bus a. Apply Fault at the WEKIWA-7 (509755) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from WEKIWA-7 (509755) 345 kV Bus to SAPLPRD7 (509870) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0226_P1 | 3 phase fault on WEKIWA-7 (509755) 345 kV Bus a. Apply Fault at the WEKIWA-7 (509755) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from WEKIWA-7 (509755) 345 kV Bus to WEKIWA-4 (509757) 138 kV Bus to WEKIW1-1 (509879) 34.5 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0227_P1 | 3 phase fault on PINTAIL7 (516010) 345 kV Bus a. Apply Fault at the PINTAIL7 (516010) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from PINTAIL7 (516010) 345 kV Bus to WOODRNG7 (514715) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0228_P1 | 3 phase fault on G16-119-TAP (587804) 345 kV Bus a. Apply Fault at the G16-119-TAP (587804) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from G16-119-TAP (587804) 345 kV Bus to SPRNGCK7 (514881) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 587953 [G16-119-GEN10.6900], 587958 [G16-119-GEN20.6900]
04 - Southeast | 25W | Transfer | Group4_Fault_0229_P1 | 3 phase fault on G15-052T (560053) 345 kV Bus a. Apply Fault at the G15-052T (560053) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from G15-052T (560053) 345 kV Bus to ROSEHIL7 (532794) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0230_P1 | 3 phase fault on RANCHRD7 (515576) 345 kV Bus a. Apply Fault at the RANCHRD7 (515576) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from RANCHRD7 (515576) 345 kV Bus to OPENSKY7 (515621) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0231_P1 | 3 phase fault on CLEVLND7 (512694) 345 kV Bus a. Apply Fault at the CLEVLND7 (512694) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from CLEVLND7 (512694) 345 kV Bus to CLEVLND 4 (512729) 138 kV Bus to CLEVLND1 (512817) 13.8 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0232_P1 | 3 phase fault on MILLERT4 (514704) 138 kV Bus a. Apply Fault at the MILLERT4 (514704) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from MILLERT4 (514704) 138 kV Bus to DMNCRKT4 (515412) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0233_P1 | 3 phase fault on MILLERT4 (514704) 138 kV Bus a. Apply Fault at the MILLERT4 (514704) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from MILLERT4 (514704) 138 kV Bus to OTOETAP4 (515978) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0234_P1 | 3 phase fault on SNRPMPT4 (514798) 138 kV Bus a. Apply Fault at the SNRPMPT4 (514798) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from SNRPMPT4 (514798) 138 kV Bus to OSAGE 4 (514743) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0235_P1 | 3 phase fault on SNRPMPT4 (514798) 138 kV Bus a. Apply Fault at the SNRPMPT4 (514798) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from SNRPMPT4 (514798) 138 kV Bus to SNRPMP 4 (514799) 138 kV Bus CKT 1 b. 2. Drop Load 1 at SNRPMP 4 (514799) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0236_P1 | 3 phase fault on MORISNT4 (515447) 138 kV Bus a. Apply Fault at the MORISNT4 (515447) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from MORISNT4 (515447) 138 kV Bus to STILWTR4 (515011) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0237_P1 | 3 phase fault on MORISNT4 (515447) 138 kV Bus a. Apply Fault at the MORISNT4 (515447) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from MORISNT4 (515447) 138 kV Bus to MORRISN4 (515006) 138 kV Bus CKT 1 b. 2. Trip branch from MORRISN4 (515006) 138 kV Bus to COWCRK 4 (514706) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0238_P1 | 3 phase fault on WEKIWA-4 (509757) 138 kV Bus a. Apply Fault at the WEKIWA-4 (509757) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from WEKIWA-4 (509757) 138 kV Bus to SHEFFD-4 (509812) 138 kV Bus CKT 1 b. 2. Trip branch from SHEFFD-4 (509812) 138 kV Bus to S.S.---4 (509815) 138 kV Bus CKT 1 b. 3. Drop Load 1 at SHEFFD-4 (509812) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0239_P1 | 3 phase fault on WEKIWA-4 (509757) 138 kV Bus a. Apply Fault at the WEKIWA-4 (509757) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from WEKIWA-4 (509757) 138 kV Bus to WED-TAP4 (509823) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0240_P1 | 3 phase fault on WEKIWA-4 (509757) 138 kV Bus a. Apply Fault at the WEKIWA-4 (509757) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from WEKIWA-4 (509757) 138 kV Bus to P&P WTP4 (509851) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0241_P1 | 3 phase fault on SOONER 7 (514803) 345 kV Bus a. Apply Fault at the SOONER 7 (514803) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from SOONER 7 (514803) 345 kV Bus to WEKIWA-7 (509755) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 587953 [G16-119-GEN10.6900], 587958 [G16-119-GEN20.6900]
04 - Southeast | 25W | Transfer | Group4_Fault_0242_P1 | 3 phase fault on WEKIWA-4 (509757) 138 kV Bus a. Apply Fault at the WEKIWA-4 (509757) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from WEKIWA-4 (509757) 138 kV Bus to SILVCTYGR4 (512726) 138 kV Bus CKT 1 b. 2. Trip branch from SILVCTYGR4 (512726) 138 kV Bus to 4SILVCTY (300140) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0243_P1 | 3 phase fault on WEKIWA-4 (509757) 138 kV Bus a. Apply Fault at the WEKIWA-4 (509757) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from WEKIWA-4 (509757) 138 kV Bus to KEYSTON4 (505610) 138 kV Bus CKT 1 b. 2. Trip branch from KEYSTON4 (505610) 138 kV Bus to 4FISHERTP (300131) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0244_P1 | 3 phase fault on CLEVLND 4 (512729) 138 kV Bus a. Apply Fault at the CLEVLND 4 (512729) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from CLEVLND 4 (512729) 138 kV Bus to 4CLEVLND (300138) 138 kV Bus CKT Z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0245_P1 | 3 phase fault on 4CLEVLND (300138) 138 kV Bus a. Apply Fault at the 4CLEVLND (300138) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from 4CLEVLND (300138) 138 kV Bus to PAWNSW4 (512749) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0246_P1 | 3 phase fault on 4CLEVLND (300138) 138 kV Bus a. Apply Fault at the 4CLEVLND (300138) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from 4CLEVLND (300138) 138 kV Bus to 4SILVCTY (300140) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0247_P1 | 3 phase fault on 4CLEVLND (300138) 138 kV Bus a. Apply Fault at the 4CLEVLND (300138) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from 4CLEVLND (300138) 138 kV Bus to 4JAVINE (300996) 138 kV Bus CKT 1 b. 2. Trip branch from 4JAVINE (300996) 138 kV Bus to 4SFORKKTP (301339) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0248_P1 | 3 phase fault on 4CLEVLND (300138) 138 kV Bus a. Apply Fault at the 4CLEVLND (300138) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from 4CLEVLND (300138) 138 kV Bus to 2CLEVLND (300927) 69 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0249_P1 | 3 phase fault on 4CLEVLND (300138) 138 kV Bus a. Apply Fault at the 4CLEVLND (300138) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from 4CLEVLND (300138) 138 kV Bus to 2CLEVLND (300927) 69 kV Bus CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0250_P1 | 3 phase fault on SAPLPRD7 (509870) 345 kV Bus a. Apply Fault at the SAPLPRD7 (509870) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from SAPLPRD7 (509870) 345 kV Bus to R.S.S.-7 (509782) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0251_P1 | 3 phase fault on SAPLPRD7 (509870) 345 kV Bus a. Apply Fault at the SAPLPRD7 (509870) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from SAPLPRD7 (509870) 345 kV Bus to SAPLPRD4 (509871) 138 kV Bus to SAPLPRD1 (509872) 13.8 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0252_P1 | 3 phase fault on SOONER 7 (514803) 345 kV Bus a. Apply Fault at the SOONER 7 (514803) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from SOONER 7 (514803) 345 kV Bus to G15-066T (560056) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 587953 [G16-119-GEN10.6900], 587958 [G16-119-GEN20.6900]
04 - Southeast | 25W | Transfer | Group4_Fault_0254_P1 | 3 phase fault on WOODRNG7 (514715) 345 kV Bus a. Apply Fault at the WOODRNG7 (514715) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from WOODRNG7 (514715) 345 kV Bus to HUNTERS7 (515476) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0255_P1 | 3 phase fault on WOODRNG7 (514715) 345 kV Bus a. Apply Fault at the WOODRNG7 (514715) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from WOODRNG7 (514715) 345 kV Bus to REDNGTN7 (515875) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0256_P1 | 3 phase fault on WOODRNG7 (514715) 345 kV Bus a. Apply Fault at the WOODRNG7 (514715) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from WOODRNG7 (514715) 345 kV Bus to WOODRNG4 (514714) 138 kV Bus to WOODRNG1 (515770) 13.8 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0257_P1 | 3 phase fault on SPRNGCK7 (514881) 345 kV Bus a. Apply Fault at the SPRNGCK7 (514881) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from SPRNGCK7 (514881) 345 kV Bus to NORTWST7 (514880) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 587953 [G16-119-GEN10.6900], 587958 [G16-119-GEN20.6900]
04 - Southeast | 25W | Transfer | Group4_Fault_0258_P1 | 3 phase fault on ROSEHIL7 (532794) 345 kV Bus a. Apply Fault at the ROSEHIL7 (532794) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from ROSEHIL7 (532794) 345 kV Bus to LATHAMS7 (532800) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0259_P1 | 3 phase fault on ROSEHIL7 (532794) 345 kV Bus a. Apply Fault at the ROSEHIL7 (532794) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from ROSEHIL7 (532794) 345 kV Bus to BENTON 7 (532791) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0260_P1 | 3 phase fault on ROSEHIL7 (532794) 345 kV Bus a. Apply Fault at the ROSEHIL7 (532794) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from ROSEHIL7 (532794) 345 kV Bus to WOLFCRK7 (532797) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0261_P1 | 3 phase fault on ROSEHIL7 (532794) 345 kV Bus a. Apply Fault at the ROSEHIL7 (532794) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from ROSEHIL7 (532794) 345 kV Bus to ROSEHIL4 (533062) 138 kV Bus to ROSEH1 1 (532826) 13.8 kV Bus CKT 1 b. 2. Drop Shunt 1 at ROSEH1 1 (532826) 13.8 kV Bus1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0262_P1 | 3 phase fault on ROSEHIL7 (532794) 345 kV Bus a. Apply Fault at the ROSEHIL7 (532794) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from ROSEHIL7 (532794) 345 kV Bus to ROSEHIL4 (533062) 138 kV Bus to ROSEH5 1 (532827) 13.8 kV Bus CKT 1 b. 2. Drop Shunt 1 at ROSEH5 1 (532827) 13.8 kV Bus1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0263_P1 | 3 phase fault on SOONER 7 (514803) 345 kV Bus a. Apply Fault at the SOONER 7 (514803) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from SOONER 7 (514803) 345 kV Bus to PINTAIL7 (516010) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 587953 [G16-119-GEN10.6900], 587958 [G16-119-GEN20.6900]
04 - Southeast | 25W | Transfer | Group4_Fault_0264_P1 | 3 phase fault on ROSEHIL7 (532794) 345 kV Bus a. Apply Fault at the ROSEHIL7 (532794) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from ROSEHIL7 (532794) 345 kV Bus to ROSEHIL4 (533062) 138 kV Bus to ROSEH3 1 (532831) 13.8 kV Bus CKT 1 b. 2. Drop Shunt 1 at ROSEH3 1 (532831) 13.8 kV Bus1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0265_P1 | 3 phase fault on DMNCRKT4 (515412) 138 kV Bus a. Apply Fault at the DMNCRKT4 (515412) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from DMNCRKT4 (515412) 138 kV Bus to WHEAGLE4 (514761) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0266_P1 | 3 phase fault on DMNCRKT4 (515412) 138 kV Bus a. Apply Fault at the DMNCRKT4 (515412) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from DMNCRKT4 (515412) 138 kV Bus to DMANCRK4 (515400) 138 kV Bus CKT 1 b. 2. Drop Load 1 at DMANCRK4 (515400) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0267_P1 | 3 phase fault on OTOETAP4 (515978) 138 kV Bus a. Apply Fault at the OTOETAP4 (515978) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from OTOETAP4 (515978) 138 kV Bus to 4REDRCK (301011) 138 kV Bus CKT 1 b. 2. Drop Load 1 at 4REDRCK (301011) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0268_P1 | 3 phase fault on OTOETAP4 (515978) 138 kV Bus a. Apply Fault at the OTOETAP4 (515978) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from OTOETAP4 (515978) 138 kV Bus to OTOE 4 (514737) 138 kV Bus CKT 1 b. 2. Drop Load 1 at OTOE 4 (514737) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0269_P1 | 3 phase fault on COWCRK 4 (514706) 138 kV Bus a. Apply Fault at the COWCRK 4 (514706) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from COWCRK 4 (514706) 138 kV Bus to WRVALLY4 (514713) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0270_P1 | 3 phase fault on COWCRK 4 (514706) 138 kV Bus a. Apply Fault at the COWCRK 4 (514706) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from COWCRK 4 (514706) 138 kV Bus to COWCRK 2 (514705) 69 kV Bus to COWCRK 1 (515717) 13.8 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0271_P1 | 3 phase fault on OSAGE 4 (514743) 138 kV Bus a. Apply Fault at the OSAGE 4 (514743) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from OSAGE 4 (514743) 138 kV Bus to WHEAGLE4 (514761) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0272_P1 | 3 phase fault on OSAGE 4 (514743) 138 kV Bus a. Apply Fault at the OSAGE 4 (514743) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from OSAGE 4 (514743) 138 kV Bus to WEBBTAP4 (510376) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0273_P1 | 3 phase fault on OSAGE 4 (514743) 138 kV Bus a. Apply Fault at the OSAGE 4 (514743) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from OSAGE 4 (514743) 138 kV Bus to MARLNDT4 (514770) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0274_P1 | 3 phase fault on SOONER 7 (514803) 345 kV Bus a. Apply Fault at the SOONER 7 (514803) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from SOONER 7 (514803) 345 kV Bus to G16-119-TAP (587804) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 587953 [G16-119-GEN10.6900], 587958 [G16-119-GEN20.6900]
04 - Southeast | 25W | Transfer | Group4_Fault_0275_P1 | 3 phase fault on OSAGE 4 (514743) 138 kV Bus a. Apply Fault at the OSAGE 4 (514743) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from OSAGE 4 (514743) 138 kV Bus to OSGE 2 (514742) 69 kV Bus to OSAGE 31 (515744) 13.2 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0276_P1 | 3 phase fault on OSAGE 4 (514743) 138 kV Bus a. Apply Fault at the OSAGE 4 (514743) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from OSAGE 4 (514743) 138 kV Bus to OSGE 2 (514742) 69 kV Bus to OSAGE 41 (515745) 13.2 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0277_P1 | 3 phase fault on OSAGE 4 (514743) 138 kV Bus a. Apply Fault at the OSAGE 4 (514743) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from OSAGE 4 (514743) 138 kV Bus to STDBEAR4 (514758) 138 kV Bus CKT 1 b. 2. Trip branch from STDBEAR4 (514758) 138 kV Bus to CONORTH4 (514753) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0278_P1 | 3 phase fault on STILWTR4 (515011) 138 kV Bus a. Apply Fault at the STILWTR4 (515011) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from STILWTR4 (515011) 138 kV Bus to SPGVLLY4 (515574) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0279_P1 | 3 phase fault on STILWTR4 (515011) 138 kV Bus a. Apply Fault at the STILWTR4 (515011) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from STILWTR4 (515011) 138 kV Bus to MCELROY4 (515009) 138 kV Bus CKT 1 b. 2. Trip branch from MCELROY4 (515009) 138 kV Bus to UNVRSTY4 (515181) 138 kV Bus CKT 1 b. 3. Trip branch from UNVRSTY4 (515181) 138 kV Bus to KINZE 4 (515008) 138 kV Bus CKT 1 b. 4. Drop Load 1 at MCELROY4 (515009) 138 kV Bus b. 5. Drop Load 1 at UNVRSTY4 (515181) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0280_P1 | 3 phase fault on P&P WTP4 (509851) 138 kV Bus a. Apply Fault at the P&P WTP4 (509851) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from P&P WTP4 (509851) 138 kV Bus to PP----W4 (509805) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0281_P1 | 3 phase fault on P&P WTP4 (509851) 138 kV Bus a. Apply Fault at the P&P WTP4 (509851) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from P&P WTP4 (509851) 138 kV Bus to T.NO.--4 (509817) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0282_P1 | 3 phase fault on 4SILVCTY (300140) 138 kV Bus a. Apply Fault at the 4SILVCTY (300140) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from 4SILVCTY (300140) 138 kV Bus to 4STILWTR (300141) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0283_P1 | 3 phase fault on 4SILVCTY (300140) 138 kV Bus a. Apply Fault at the 4SILVCTY (300140) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from 4SILVCTY (300140) 138 kV Bus to 4BRISTOW (300137) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0284_P1 | 3 phase fault on 4SILVCTY (300140) 138 kV Bus a. Apply Fault at the 4SILVCTY (300140) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from 4SILVCTY (300140) 138 kV Bus to 4FISHERTP (300131) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0285_P1 | 3 phase fault on SOONER 7 (514803) 345 kV Bus a. Apply Fault at the SOONER 7 (514803) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from SOONER 7 (514803) 345 kV Bus to SOONER 4 (514802) 138 kV Bus to SOONER 1 (515760) 13.8 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 587953 [G16-119-GEN10.6900], 587958 [G16-119-GEN20.6900]
04 - Southeast | 25W | Transfer | Group4_Fault_0286_P1 | 3 phase fault on 4SILVCTY (300140) 138 kV Bus a. Apply Fault at the 4SILVCTY (300140) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from 4SILVCTY (300140) 138 kV Bus to 2SILVCTY (300943) 69 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0287_P1 | 3 phase fault on 4SILVCTY (300140) 138 kV Bus a. Apply Fault at the 4SILVCTY (300140) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from 4SILVCTY (300140) 138 kV Bus to 2SILVCTY (300943) 69 kV Bus CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0288_P1 | 3 phase fault on 2CLEVLND (300927) 69 kV Bus a. Apply Fault at the 2CLEVLND (300927) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from 2CLEVLND (300927) 69 kV Bus to OSAGEK2 (512876) 69 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0289_P1 | 3 phase fault on PAWNSW4 (512749) 138 kV Bus a. Apply Fault at the PAWNSW4 (512749) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from PAWNSW4 (512749) 138 kV Bus to 4FAIRFAX (300139) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0290_P1 | 3 phase fault on PAWNSW4 (512749) 138 kV Bus a. Apply Fault at the PAWNSW4 (512749) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from PAWNSW4 (512749) 138 kV Bus to GLENCOKM 4 (513095) 138 kV Bus CKT 1 b. 2. Trip branch from GLENCOKM 4 (513095) 138 kV Bus to 4STILWTR (300141) 138 kV Bus CKT 1 b. 3. Drop Load 1 at GLENCOKM 4 (513095) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0291_P1 | 3 phase fault on T.NO.2-4 (509895) 138 kV Bus a. Apply Fault at the T.NO.2-4 (509895) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from T.NO.2-4 (509895) 138 kV Bus to T.NO.--4 (509817) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0292_P1 | 3 phase fault on SAPLPRD4 (509871) 138 kV Bus a. Apply Fault at the SAPLPRD4 (509871) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from SAPLPRD4 (509871) 138 kV Bus to DENV_WTAP4 (509896) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0293_P1 | 3 phase fault on SAPLPRD4 (509871) 138 kV Bus a. Apply Fault at the SAPLPRD4 (509871) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from SAPLPRD4 (509871) 138 kV Bus to DENV_WTAP4 (509896) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0294_P1 | 3 phase fault on SAPLPRD4 (509871) 138 kV Bus a. Apply Fault at the SAPLPRD4 (509871) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from SAPLPRD4 (509871) 138 kV Bus to OAKSWTP4 (509848) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0295_P1 | 3 phase fault on OPENSKY7 (515621) 345 kV Bus a. Apply Fault at the OPENSKY7 (515621) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from OPENSKY7 (515621) 345 kV Bus to G15-052T (560053) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0296_P1 | 3 phase fault on SAPLPRD4 (509871) 138 kV Bus a. Apply Fault at the SAPLPRD4 (509871) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from SAPLPRD4 (509871) 138 kV Bus to 72ELWOD4 (509888) 138 kV Bus CKT 1 b. 2. Trip branch from 72ELWOD4 (509888) 138 kV Bus to T.P.S.-4 (509788) 138 kV Bus CKT 1 b. 3. Drop Load 1 at 72ELWOD4 (509888) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0297_P1 | 3 phase fault on SAPLPRD4 (509871) 138 kV Bus a. Apply Fault at the SAPLPRD4 (509871) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from SAPLPRD4 (509871) 138 kV Bus to JENKS--4 (509759) 138 kV Bus CKT 1 b. 2. Trip branch from JENKS--4 (509759) 138 kV Bus to 116JENK4 (509753) 138 kV Bus CKT 1 b. 3. Trip branch from 116JENK4 (509753) 138 kV Bus to R.S.S.-4 (509783) 138 kV Bus CKT 1 b. 4. Drop Load 1 at JENKS--4 (509759) 138 kV Bus b. 5. Drop Load 1 at 116JENK4 (509753) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0298_P1 | 3 phase fault on WOODRNG4 (514714) 138 kV Bus a. Apply Fault at the WOODRNG4 (514714) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from WOODRNG4 (514714) 138 kV Bus to OTTER 4 (514708) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0299_P1 | 3 phase fault on WOODRNG4 (514714) 138 kV Bus a. Apply Fault at the WOODRNG4 (514714) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from WOODRNG4 (514714) 138 kV Bus to FRMNTAP4 (514709) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0300_P1 | 3 phase fault on WOODRNG4 (514714) 138 kV Bus a. Apply Fault at the WOODRNG4 (514714) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from WOODRNG4 (514714) 138 kV Bus to WAUKOTP4 (514711) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0301_P1 | 3 phase fault on WOODRNG4 (514714) 138 kV Bus a. Apply Fault at the WOODRNG4 (514714) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from WOODRNG4 (514714) 138 kV Bus to MARSHL 4 (514733) 138 kV Bus CKT 1 b. 2. Trip branch from MARSHL 4 (514733) 138 kV Bus to CTNWOOD4 (514827) 138 kV Bus CKT 1 b. 3. Trip branch from MARSHL 4 (514733) 138 kV Bus to MARSHAL4 (521006) 138 kV Bus CKT Z1 b. 4. Drop Load 1 at MARSHAL4 (521006) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0302_P1 | 3 phase fault on NORTWST7 (514880) 345 kV Bus a. Apply Fault at the NORTWST7 (514880) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from NORTWST7 (514880) 345 kV Bus to CIMARON7 (514901) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 587953 [G16-119-GEN10.6900], 587958 [G16-119-GEN20.6900], 761232 [G17-150GEN1 0.6600]
04 - Southeast | 25W | Transfer | Group4_Fault_0303_P1 | 3 phase fault on NORTWST7 (514880) 345 kV Bus a. Apply Fault at the NORTWST7 (514880) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from NORTWST7 (514880) 345 kV Bus to MATHWSN7 (515497) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 587953 [G16-119-GEN10.6900], 587958 [G16-119-GEN20.6900], 761232 [G17-150GEN1 0.6600]
04 - Southeast | 25W | Transfer | Group4_Fault_0304_P1 | 3 phase fault on G15-066T (560056) 345 kV Bus a. Apply Fault at the G15-066T (560056) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from G15-066T (560056) 345 kV Bus to CLEVLND7 (512694) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 587953 [G16-119-GEN10.6900], 587958 [G16-119-GEN20.6900]
04 - Southeast | 25W | Transfer | Group4_Fault_0305_P1 | 3 phase fault on KINZE 4 (515008) 138 kV Bus a. Apply Fault at the KINZE 4 (515008) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from KINZE 4 (515008) 138 kV Bus to KINZEGR4 (512710) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0306_P1 | 3 phase fault on KINZE 4 (515008) 138 kV Bus a. Apply Fault at the KINZE 4 (515008) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from KINZE 4 (515008) 138 kV Bus to FITZGRD4 (514830) 138 kV Bus CKT 1 b. 2. Trip branch from FITZGRD4 (514830) 138 kV Bus to PINE ST4 (514829) 138 kV Bus CKT 1 b. 3. Trip branch from PINE ST4 (514829) 138 kV Bus to CTNWOOD4 (514827) 138 kV Bus CKT 1 b. 4. Drop Load 1 at FITZGRD4 (514830) 138 kV Bus b. 5. Drop Load 1 at PINE ST4 (514829) 138 kV Bus b. 6. Drop Load 2 at PINE ST4 (514829) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0307_P1 | 3 phase fault on KINZEGR4 (512710) 138 kV Bus a. Apply Fault at the KINZEGR4 (512710) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from KINZEGR4 (512710) 138 kV Bus to NORTHTP4 (512731) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0308_P1 | 3 phase fault on KINZEGR4 (512710) 138 kV Bus a. Apply Fault at the KINZEGR4 (512710) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from KINZEGR4 (512710) 138 kV Bus to 19TH ST4 (512712) 138 kV Bus CKT 1 b. 2. Trip branch from 19TH ST4 (512712) 138 kV Bus to 4RAMSEY (300844) 138 kV Bus CKT 1 b. 3. Drop Load 1 at 19TH ST4 (512712) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0309_P1 | 3 phase fault on KINZEGR4 (512710) 138 kV Bus a. Apply Fault at the KINZEGR4 (512710) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from KINZEGR4 (512710) 138 kV Bus to KINZEGR2 (512713) 69 kV Bus CKT 1 b. 2. Trip branch from KINZEGR2 (512713) 69 kV Bus to ADMIRAL2 (512660) 69 kV Bus CKT 1 b. 3. Drop Shunt 1 at KINZEGR2 (512713) 69 kV Bus1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0310_P1 | 3 phase fault on CTNWOOD4 (514827) 138 kV Bus a. Apply Fault at the CTNWOOD4 (514827) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from CTNWOOD4 (514827) 138 kV Bus to ARCADIA4 (514907) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0311_P1 | 3 phase fault on CTNWOOD4 (514827) 138 kV Bus a. Apply Fault at the CTNWOOD4 (514827) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from CTNWOOD4 (514827) 138 kV Bus to CRESENT4 (515377) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0312_P4 | a. Apply single phase fault at SOONER 4 (514802) 138 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from SOONER 4 (514802) 138 kV to MORISNT4 (515447) 138 kV CKT 1 b. 2. Trip branch from SOONER 4 (514802) 138 kV to SNRPMPT4 (514798) 138 kV CKT 1 b. 3. Trip branch from SNRPMPT4 (514798) 138 kV to SNRPMP 4 (514799) 138 kV CKT 1 b. 4. Drop Load 1 SNRPMP 4 (514799) 138 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0313_P4 | a. Apply single phase fault at T.NO.--4 (509817) 138 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from T.NO.--4 (509817) 138 kV to T.NO.2-4 (509895) 138 kV CKT 1 b. 2. Trip branch from T.NO.--4 (509817) 138 kV to CDC-WT 4 (509842) 138 kV CKT 1 b. 3. Trip branch from CDC-WT 4 (509842) 138 kV to A.A.---4 (509784) 138 kV CKT 1 b. 4. Trip branch from CDC-WT 4 (509842) 138 kV to WHIRLPO4 (509840) 138 kV CKT 1 b. 5. Drop Load 1 WHIRLPO4 (509840) 138 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0314_P4 | a. Apply single phase fault at MEMRIAL4 (514835) 138 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from MEMRIAL4 (514835) 138 kV to TENESTP4 (514837) 138 kV CKT 1 b. 2. Trip branch from MEMRIAL4 (514835) 138 kV to BRYANT 4 (514839) 138 kV CKT 1 b. 3. Trip branch from BRYANT 4 (514839) 138 kV to ACORN 4 (515459) 138 kV CKT 1 b. 4. Trip branch from ACORN 4 (515459) 138 kV to JONESSB4 (515480) 138 kV CKT 1 b. 5. Drop Load 1 BRYANT 4 (514839) 138 kV b. 6. Drop Load 1 ACORN 4 (515459) 138 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0315_P4 | a. Apply single phase fault at S.S.---4 (509815) 138 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from S.S.---4 (509815) 138 kV to SHEFFD-4 (509812) 138 kV CKT 1 b. 2. Trip branch from SHEFFD-4 (509812) 138 kV to WEKIWA-4 (509757) 138 kV CKT 1 b. 3. Trip branch from S.S.---4 (509815) 138 kV to PRATTV-4 (509758) 138 kV CKT 1 b. 4. Trip branch from PRATTV-4 (509758) 138 kV to BLUEBEL4 (515242) 138 kV CKT 1 b. 5. Drop Load 1 PRATTV-4 (509758) 138 kV b. 6. Drop Load 1 SHEFFD-4 (509812) 138 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0316_P4 | a. Apply single phase fault at R.S.S.-4 (509783) 138 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from R.S.S.-4 (509783) 138 kV to ORU ETP4 (509849) 138 kV CKT 1 b. 2. Trip branch from ORU ETP4 (509849) 138 kV to WARNTAP4 (509858) 138 kV CKT 1 b. 3. Trip branch from ORU ETP4 (509849) 138 kV to ORU E4 (509738) 138 kV CKT 1 b. 4. Trip branch from R.S.S.-4 (509783) 138 kV to ORU-WTP4 (509853) 138 kV CKT 1 b. 5. Trip branch from ORU-WTP4 (509853) 138 kV to SHILETP4 (509813) 138 kV CKT 1 b. 6. Trip branch from ORU-WTP4 (509853) 138 kV to ORU W4 (509732) 138 kV CKT 1 b. 7. Drop Load 1 ORU W4 (509732) 138 kV b. 8. Drop Shunt 1 ORU W4 (509732) 138 kV b. 9. Drop Load 1 ORU E4 (509738) 138 kV b. 10. Drop Shunt 1 ORU E4 (509738) 138 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0317_P4 | a. Apply single phase fault at DVISION4 (514853) 138 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from DVISION4 (514853) 138 kV to LAKESID4 (514849) 138 kV CKT 1 b. 2. Trip branch from LAKESID4 (514849) 138 kV to HEFNER 4 (514848) 138 kV CKT 1 b. 3. Trip branch from DVISION4 (514853) 138 kV to SLVRLAK4 (514852) 138 kV CKT 1 b. 4. Drop Load 1 LAKESID4 (514849) 138 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0318_P4 | a. Apply single phase fault at T.NO.--7 (509852) 345 kV b. Clear Fault after 16 cycles: b. 1. Trip three winding transformer from T.NO.--7 (509852) 345 kV to T.NO.2-4 (509895) kV to TNO2-1 (509894) 34.5 kV CKT1 b. 2. Trip branch from T.NO.2-4 (509895) 138 kV to T.NO.--4 (509817) 138 kV CKT 1 b. 3. Trip branch from T.NO.--7 (509852) 345 kV to N.E.S.-7 (510406) 345 kV CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0319_P4 | a. Apply single phase fault at WEKIWA-4 (509757) 138 kV b. Clear Fault after 16 cycles: b. 1. Trip three winding transformer from WEKIWA-7 (509755) 345 kV to WEKIWA-4 (509757) kV to WEKIW1-1 (509879) 34.5 kV CKT1 b. 2. Trip branch from WEKIWA-4 (509757) 138 kV to SILVCTYGR4 (512726) 138 kV CKT 1 b. 3. Trip branch from SILVCTYGR4 (512726) 138 kV to 4SILVCTY (300140) 138 kV CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0320_P4 | a. Apply single phase fault at WOODRNG7 (514715) 345 kV b. Clear Fault after 16 cycles: b. 1. Trip three winding transformer from WOODRNG7 (514715) 345 kV to WOODRNG4 (514714) kV to WOODRNG1 (515770) 13.8 kV CKT1 b. 2. Trip branch from WOODRNG7 (514715) 345 kV to PINTAIL7 (516010) 345 kV CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0321_P4 | a. Apply single phase fault at 4CLEVLND (300138) 138 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from 4CLEVLND (300138) 138 kV to CLEVLND 4 (512729) 138 kV CKT Z1 b. 2. Trip three winding transformer from CLEVLND7 (512694) 345 kV to CLEVLND 4 (512729) kV to CLEVLND1 (512817) 13.8 kV CKT1 b. 3. Trip branch from 4CLEVLND (300138) 138 kV to PAWNSW4 (512749) 138 kV CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0322_P4 | a. Apply single phase fault at CTNWOOD4 (514827) 138 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from CTNWOOD4 (514827) 138 kV to ARCADIA4 (514907) 138 kV CKT 1 b. 2. Trip branch from CTNWOOD4 (514827) 138 kV to PINE ST4 (514829) 138 kV CKT 1 b. 3. Trip branch from PINE ST4 (514829) 138 kV to FITZGRD4 (514830) 138 kV CKT 1 b. 4. Trip branch from FITZGRD4 (514830) 138 kV to KINZE 4 (515008) 138 kV CKT 1 b. 5. Drop Load 1 PINE ST4 (514829) 138 kV b. 6. Drop Load 2 PINE ST4 (514829) 138 kV b. 7. Drop Load 1 FITZGRD4 (514830) 138 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0324_P4 | a. Apply single phase fault at SAPLPRD4 (509871) 138 kV b. Clear Fault after 16 cycles: b. 1. Trip three winding transformer from SAPLPRD4 (509871) 138 kV to SAPLPRD7 (509870) kV to SAPLPRD1 (509872) 13.8 kV CKT1 b. 2. Trip branch from SAPLPRD4 (509871) 138 kV to OAKSWTP4 (509848) 138 kV CKT 1 b. 3. Trip branch from OAKSWTP4 (509848) 138 kV to OAKS W4 (509727) 138 kV CKT 1 b. 4. Trip branch from OAKSWTP4 (509848) 138 kV to T.P.S.-4 (509788) 138 kV CKT 1 b. 5. Drop Load 1 OAKS W4 (509727) 138 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0325_P4 | a. Apply single phase fault at ARCADIA4 (514907) 138 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from ARCADIA4 (514907) 138 kV to RNDBARN4 (515461) 138 kV CKT 1 b. 2. Trip branch from RNDBARN4 (515461) 138 kV to BURGETT4 (514510) 138 kV CKT 1 b. 3. Trip branch from BURGETT4 (514510) 138 kV to DANFRTH4 (514833) 138 kV CKT 1 b. 4. Trip three winding transformer from ARCADIA4 (514907) 138 kV to ARCADIA7 (514908) kV to ARCADI41 (515700) 13.8 kV CKT1 b. 5. Drop Load 1 BURGETT4 (514510) 138 kV b. 6. Drop Load 1 RNDBARN4 (515461) 138 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0326_P4 | a. Apply single phase fault at BV-SE--4 (510391) 138 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from BV-SE--4 (510391) 138 kV to RICE CK4 (510385) 138 kV CKT 1 b. 2. Trip branch from RICE CK4 (510385) 138 kV to N.E.S.-4 (510396) 138 kV CKT 1 b. 3. Trip branch from BV-SE--4 (510391) 138 kV to BV-COM-4 (510390) 138 kV CKT 1 b. 4. Drop Load M1 RICE CK4 (510385) 138 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0327_P4 | a. Apply single phase fault at COFCTY2 (512735) 69 kV b. Clear Fault after 16 cycles: b. 1. Trip three winding transformer from FARML 4 (512734) 138 kV to COFCTY2 (512735) kV to COFFEY1 (512740) 13.8 kV CKT1 b. 2. Trip three winding transformer from FARML 4 (512734) 138 kV to COFCTY2 (512735) kV to COFFEY2 (512741) 13.8 kV CKT2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0328_P4 | a. Apply single phase fault at NEOSHO 7 (532793) 345 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from NEOSHO 7 (532793) 345 kV to G17-209-TAP (760921) 345 kV CKT 1 b. 2. Trip three winding transformer from NEOSHO 7 (532793) 345 kV to NEOSHO 5 (532937) kV to N345 2 1 (532825) 13.8 kV CKT1 b. 3. Drop Shunt 1 N345 2 1 (532825) 13.8 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0329_P4 | a. Apply single phase fault at N.E.S.-4 (510396) 138 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from N.E.S.-4 (510396) 138 kV to OOLOGAHKM 4 (513124) 138 kV CKT 1 b. 2. Trip branch from OOLOGAHKM 4 (513124) 138 kV to CLARMR 4 (512707) 138 kV CKT 1 b. 3. Trip three winding transformer from CLARMR 4 (512707) 138 kV to CLARMR 5 (512651) kV to CLARMR4 (512813) 13.8 kV CKT1 b. 4. Trip branch from N.E.S.-4 (510396) 138 kV to OWASO2_4 (509843) 138 kV CKT 1 b. 5. Trip branch from OWASO2_4 (509843) 138 kV to PCATSAT4 (509841) 138 kV CKT 1 b. 6. Drop Load 1 OOLOGAHKM 4 (513124) 138 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0330_P4 | a. Apply single phase fault at NEOSHO 4 (533021) 138 kV b. Clear Fault after 16 cycles: b. 1. Trip three winding transformer from NEOSHO 4 (533021) 138 kV to NEOSHO 7 (532793) kV to N345 1 1 (532824) 13.8 kV CKT1 b. 2. Trip branch from NEOSHO 4 (533021) 138 kV to NEOSHON4 (533022) 138 kV CKT Z1 b. 3. Drop Shunt 1 N345 1 1 (532824) 13.8 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0331_P4 | a. Apply single phase fault at NEOSHO 5 (532937) 161 kV b. Clear Fault after 16 cycles: b. 1. Trip three winding transformer from NEOSHO 5 (532937) 161 kV to NEOSHO 7 (532793) kV to N345 2 1 (532825) 13.8 kV CKT1 b. 2. Trip branch from NEOSHO 5 (532937) 161 kV to RIV4525 (547469) 161 kV CKT 1 b. 3. Drop Shunt 1 N345 2 1 (532825) 13.8 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0332_P4 | a. Apply single phase fault at NEOSHOS2 (533778) 69 kV b. Clear Fault after 16 cycles: b. 1. Trip three winding transformer from NEOSHO 4 (533021) 138 kV to NEOSHOS2 (533778) kV to NSES 2X1 (532710) 13.2 kV CKT1 b. 2. Trip branch from NEOSHOS2 (533778) 69 kV to BAKER 2 (532926) 69 kV CKT 1 b. 3. Trip branch from BAKER 2 (532926) 69 kV to SOPITT 2 (533773) 69 kV CKT 1 b. 4. Drop Load 1 BAKER 2 (532926) 69 kV b. 5. Drop Load 2 BAKER 2 (532926) 69 kV b. 6. Drop Load 3 BAKER 2 (532926) 69 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0333_P4 | a. Apply single phase fault at ALTOONA4 (533001) 138 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from ALTOONA4 (533001) 138 kV to G17-022-TAP (588664) 138 kV CKT 1 b. 2. Trip branch from ALTOONA4 (533001) 138 kV to TAYLOR 4 (533006) 138 kV CKT 1 b. 3. Trip branch from TAYLOR 4 (533006) 138 kV to MONTGOM4 (533004) 138 kV CKT 1 b. 4. Drop Load 1 TAYLOR 4 (533006) 138 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0334_P1 | 3 phase fault on G18-079-TAP (763113) 138 kV Bus a. Apply Fault at the G18-079-TAP (763113) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from G18-079-TAP (763113) 138 kV Bus to DELWARE4 (510379) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0335_P1 | 3 phase fault on N.E.S.-7 (510406) 345 kV Bus a. Apply Fault at the N.E.S.-7 (510406) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from N.E.S.-7 (510406) 345 kV Bus to ONETA--7 (509807) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0336_P1 | 3 phase fault on NEOSHO 7 (532793) 345 kV Bus a. Apply Fault at the NEOSHO 7 (532793) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from NEOSHO 7 (532793) 345 kV Bus to 7BLACKBERRY (300739) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0337_P1 | 3 phase fault on NEOSHO 7 (532793) 345 kV Bus a. Apply Fault at the NEOSHO 7 (532793) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from NEOSHO 7 (532793) 345 kV Bus to G17-009-TAP (532777) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0338_P1 | 3 phase fault on NEOSHO 7 (532793) 345 kV Bus a. Apply Fault at the NEOSHO 7 (532793) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from NEOSHO 7 (532793) 345 kV Bus to G17-209-TAP (760921) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0339_P1 | 3 phase fault on NEOSHO 7 (532793) 345 kV Bus a. Apply Fault at the NEOSHO 7 (532793) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from NEOSHO 7 (532793) 345 kV Bus to NEOSHO 4 (533021) 138 kV Bus to N345 1 1 (532824) 13.8 kV Bus CKT 1 b. 2. Drop Shunt 1 at N345 1 1 (532824) 13.8 kV Bus1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0340_P1 | 3 phase fault on NEOSHO 7 (532793) 345 kV Bus a. Apply Fault at the NEOSHO 7 (532793) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from NEOSHO 7 (532793) 345 kV Bus to NEOSHO 5 (532937) 161 kV Bus to N345 2 1 (532825) 13.8 kV Bus CKT 1 b. 2. Drop Shunt 1 at N345 2 1 (532825) 13.8 kV Bus1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0341_P1 | 3 phase fault on G17-009-TAP (532777) 345 kV Bus a. Apply Fault at the G17-009-TAP (532777) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from G17-009-TAP (532777) 345 kV Bus to CANEYRV7 (532780) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0342_P1 | 3 phase fault on NEOSHO 4 (533021) 138 kV Bus a. Apply Fault at the NEOSHO 4 (533021) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from NEOSHO 4 (533021) 138 kV Bus to NEOSHON4 (533022) 138 kV Bus CKT Z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0343_P1 | 3 phase fault on G18-079-TAP (763113) 138 kV Bus a. Apply Fault at the G18-079-TAP (763113) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from G18-079-TAP (763113) 138 kV Bus to FARML 4 (512734) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0344_P1 | 3 phase fault on NEOSHO 4 (533021) 138 kV Bus a. Apply Fault at the NEOSHO 4 (533021) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from NEOSHO 4 (533021) 138 kV Bus to NEOSHOS4 (533020) 138 kV Bus CKT Z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0345_P1 | 3 phase fault on NEOSHO 4 (533021) 138 kV Bus a. Apply Fault at the NEOSHO 4 (533021) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from NEOSHO 5 (532937) 161 kV Bus to NEOSHO 4 (533021) 138 kV Bus to NEOSH4 1 (532958) 13.2 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0346_P1 | 3 phase fault on NEOSHO 4 (533021) 138 kV Bus a. Apply Fault at the NEOSHO 4 (533021) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from NEOSHO 4 (533021) 138 kV Bus to NEOSHOS2 (533778) 69 kV Bus to NSES 2X1 (532710) 13.2 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0347_P1 | 3 phase fault on NEOSHO 5 (532937) 161 kV Bus a. Apply Fault at the NEOSHO 5 (532937) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from NEOSHO 5 (532937) 161 kV Bus to MARMTNW5 (532935) 161 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0348_P1 | 3 phase fault on NEOSHO 5 (532937) 161 kV Bus a. Apply Fault at the NEOSHO 5 (532937) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from NEOSHO 5 (532937) 161 kV Bus to RIV4525 (547469) 161 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0349_P1 | 3 phase fault on NEOSHO 5 (532937) 161 kV Bus a. Apply Fault at the NEOSHO 5 (532937) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from NEOSHO 5 (532937) 161 kV Bus to NEOSHOS4 (533020) 138 kV Bus to NEOSH5 1 (532959) 13.2 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0350_P1 | 3 phase fault on NEOSHOS4 (533020) 138 kV Bus a. Apply Fault at the NEOSHOS4 (533020) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from NEOSHOS4 (533020) 138 kV Bus to TV1MNDV4 (533008) 138 kV Bus CKT 1 b. 2. Trip branch from TV1MNDV4 (533008) 138 kV Bus to LIBERTY4 (533003) 138 kV Bus CKT 1 b. 3. Drop Load K1 at TV1MNDV4 (533008) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0351_P1 | 3 phase fault on NEOSHON4 (533022) 138 kV Bus a. Apply Fault at the NEOSHON4 (533022) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from NEOSHON4 (533022) 138 kV Bus to NEPARSN4 (533005) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0352_P1 | 3 phase fault on NEOSHON4 (533022) 138 kV Bus a. Apply Fault at the NEOSHON4 (533022) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from NEOSHON4 (533022) 138 kV Bus to NEOSHON2 (533768) 69 kV Bus to NEC U3 (532711) 12 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0353_P1 | 3 phase fault on NEOSHON4 (533022) 138 kV Bus a. Apply Fault at the NEOSHON4 (533022) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from NEOSHON4 (533022) 138 kV Bus to NEPARSN4 (533005) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0354_P1 | 3 phase fault on DELWARE4 (510379) 138 kV Bus a. Apply Fault at the DELWARE4 (510379) 138 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from DELWARE7 (510380) 345 kV Bus to DELWARE4 (510379) 138 kV Bus to DELAWAR1 (510370) 13.8 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0355_P1 | 3 phase fault on NEOSHOS2 (533778) 69 kV Bus a. Apply Fault at the NEOSHOS2 (533778) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from NEOSHOS2 (533778) 69 kV Bus to NEOSHON2 (533768) 69 kV Bus CKT Z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0356_P1 | 3 phase fault on NEOSHOS2 (533778) 69 kV Bus a. Apply Fault at the NEOSHOS2 (533778) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from NEOSHOS2 (533778) 69 kV Bus to BAKER 2 (532926) 69 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0357_P1 | 3 phase fault on NEOSHOS2 (533778) 69 kV Bus a. Apply Fault at the NEOSHOS2 (533778) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from NEOSHOS2 (533778) 69 kV Bus to CRAWFOR2 (533758) 69 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0358_P1 | 3 phase fault on NEOSHOS2 (533778) 69 kV Bus a. Apply Fault at the NEOSHOS2 (533778) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from NEOSHOS2 (533778) 69 kV Bus to ORDNJCT2 (533703) 69 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0359_P1 | 3 phase fault on COFFEYT4 (510422) 138 kV Bus a. Apply Fault at the COFFEYT4 (510422) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from COFFEYT4 (510422) 138 kV Bus to DEARING4 (533002) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0360_P1 | 3 phase fault on COFFEYT4 (510422) 138 kV Bus a. Apply Fault at the COFFEYT4 (510422) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from COFFEYT4 (510422) 138 kV Bus to NBVILLE4 (510386) 138 kV Bus CKT 1 b. 2. Trip branch from NBVILLE4 (510386) 138 kV Bus to BV-SE--4 (510391) 138 kV Bus CKT 1 b. 3. Drop Load M1 at NBVILLE4 (510386) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0361_P1 | 3 phase fault on ONETA--7 (509807) 345 kV Bus a. Apply Fault at the ONETA--7 (509807) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from ONETA--7 (509807) 345 kV Bus to R.S.S.-7 (509782) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 760392 [G17-140-GEN10.6300], 760412 [G17-141-GEN10.6300]
04 - Southeast | 25W | Transfer | Group4_Fault_0362_P1 | 3 phase fault on ONETA--7 (509807) 345 kV Bus a. Apply Fault at the ONETA--7 (509807) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from ONETA--7 (509807) 345 kV Bus to CLARKSV7 (509745) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 760392 [G17-140-GEN10.6300], 760412 [G17-141-GEN10.6300]
04 - Southeast | 25W | Transfer | Group4_Fault_0363_P1 | 3 phase fault on ONETA--7 (509807) 345 kV Bus a. Apply Fault at the ONETA--7 (509807) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from ONETA--7 (509807) 345 kV Bus to OEC 7 (509836) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 760392 [G17-140-GEN10.6300], 760412 [G17-141-GEN10.6300]
04 - Southeast | 25W | Transfer | Group4_Fault_0364_P1 | 3 phase fault on ONETA--7 (509807) 345 kV Bus a. Apply Fault at the ONETA--7 (509807) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from ONETA--7 (509807) 345 kV Bus to OEC 7 (509836) 345 kV Bus CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 760392 [G17-140-GEN10.6300], 760412 [G17-141-GEN10.6300]
04 - Southeast | 25W | Transfer | Group4_Fault_0365_P1 | 3 phase fault on FARML 4 (512734) 138 kV Bus a. Apply Fault at the FARML 4 (512734) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from FARML 4 (512734) 138 kV Bus to SCOFCTY4 (510378) 138 kV Bus CKT 1 b. 2. Trip branch from SCOFCTY4 (510378) 138 kV Bus to SCOFFEYV4 (510420) 138 kV Bus CKT 1 b. 3. Trip branch from SCOFCTY4 (510378) 138 kV Bus to COFFEYT4 (510422) 138 kV Bus CKT 1 b. 4. Drop Load 1 at SCOFFEYV4 (510420) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0366_P1 | 3 phase fault on ONETA--7 (509807) 345 kV Bus a. Apply Fault at the ONETA--7 (509807) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from ONETA--7 (509807) 345 kV Bus to ONETA--4 (509806) 138 kV Bus to ONETA1-1 (509881) 13.8 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 760392 [G17-140-GEN10.6300], 760412 [G17-141-GEN10.6300]
04 - Southeast | 25W | Transfer | Group4_Fault_0367_P1 | 3 phase fault on ONETA--7 (509807) 345 kV Bus a. Apply Fault at the ONETA--7 (509807) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from ONETA--7 (509807) 345 kV Bus to ONETA--4 (509806) 138 kV Bus to ONETA2-1 (509868) 34.5 kV Bus CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 760392 [G17-140-GEN10.6300], 760412 [G17-141-GEN10.6300]
04 - Southeast | 25W | Transfer | Group4_Fault_0368_P1 | 3 phase fault on ONETA--7 (509807) 345 kV Bus a. Apply Fault at the ONETA--7 (509807) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from ONETA--7 (509807) 345 kV Bus to ONETA--4 (509806) 138 kV Bus to ONETA5-1 (509874) 34.5 kV Bus CKT 3 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 760392 [G17-140-GEN10.6300], 760412 [G17-141-GEN10.6300]
04 - Southeast | 25W | Transfer | Group4_Fault_0369_P1 | 3 phase fault on T.NO.--7 (509852) 345 kV Bus a. Apply Fault at the T.NO.--7 (509852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from T.NO.--7 (509852) 345 kV Bus to WEKIWA-7 (509755) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0370_P1 | 3 phase fault on T.NO.--7 (509852) 345 kV Bus a. Apply Fault at the T.NO.--7 (509852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from T.NO.--7 (509852) 345 kV Bus to IGLOOV 7 (513596) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0371_P1 | 3 phase fault on T.NO.--7 (509852) 345 kV Bus a. Apply Fault at the T.NO.--7 (509852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from T.NO.--7 (509852) 345 kV Bus to N.E.S.-7 (510406) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0372_P1 | 3 phase fault on T.NO.--7 (509852) 345 kV Bus a. Apply Fault at the T.NO.--7 (509852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from T.NO.--7 (509852) 345 kV Bus to CLEVLND7 (512694) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0373_P1 | 3 phase fault on T.NO.--7 (509852) 345 kV Bus a. Apply Fault at the T.NO.--7 (509852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from T.NO.--7 (509852) 345 kV Bus to T.NO.2-4 (509895) 138 kV Bus to TNO2-1 (509894) 34.5 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0374_P1 | 3 phase fault on 7BLACKBERRY (300739) 345 kV Bus a. Apply Fault at the 7BLACKBERRY (300739) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from 7BLACKBERRY (300739) 345 kV Bus to WOLFCRK7 (532797) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0375_P1 | 3 phase fault on 7BLACKBERRY (300739) 345 kV Bus a. Apply Fault at the 7BLACKBERRY (300739) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from 7BLACKBERRY (300739) 345 kV Bus to 7SPORTSMAN (300740) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0376_P1 | 3 phase fault on FARML 4 (512734) 138 kV Bus a. Apply Fault at the FARML 4 (512734) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from FARML 4 (512734) 138 kV Bus to COFCTY2 (512735) 69 kV Bus to COFFEY2 (512741) 13.8 kV Bus CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0377_P1 | 3 phase fault on 7BLACKBERRY (300739) 345 kV Bus a. Apply Fault at the 7BLACKBERRY (300739) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from 7BLACKBERRY (300739) 345 kV Bus to 7JASPER (300949) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0378_P1 | 3 phase fault on G17-209-TAP (760921) 345 kV Bus a. Apply Fault at the G17-209-TAP (760921) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from G17-209-TAP (760921) 345 kV Bus to LACYGNE7 (542981) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0379_P1 | 3 phase fault on CANEYRV7 (532780) 345 kV Bus a. Apply Fault at the CANEYRV7 (532780) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from CANEYRV7 (532780) 345 kV Bus to LATHAMS7 (532800) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0381_P1 | 3 phase fault on MARMTNW5 (532935) 161 kV Bus a. Apply Fault at the MARMTNW5 (532935) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from MARMTNW5 (532935) 161 kV Bus to MARMTNE5 (532934) 161 kV Bus CKT Z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0382_P1 | 3 phase fault on MARMTNW5 (532935) 161 kV Bus a. Apply Fault at the MARMTNW5 (532935) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from MARMTNW5 (532935) 161 kV Bus to MARMATN2 (533639) 69 kV Bus to MARMATN1 (532955) 13.2 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0383_P1 | 3 phase fault on MARMTNE5 (532934) 161 kV Bus a. Apply Fault at the MARMTNE5 (532934) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from CRAWFOR2 (533758) 69 kV Bus to SE1GREE2 (533772) 69 kV Bus CKT 1 b. 2. Trip branch from SE1GREE2 (533772) 69 kV Bus to GIR JCT2 (533762) 69 kV Bus CKT 1 b. 3. Drop Load K1 at CRAWFOR2 (533758) 69 kV Bus b. 4. Drop Load 1 at CRAWFOR2 (533758) 69 kV Bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0384_P1 | 3 phase fault on 7JASPER (300949) 345 kV Bus a. Apply Fault at the 7JASPER (300949) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from 7JASPER (300949) 345 kV Bus to 5JASPER (300950) 161 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0385_P1 | 3 phase fault on 7JASPER (300949) 345 kV Bus a. Apply Fault at the 7JASPER (300949) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from 7JASPER (300949) 345 kV Bus to 7MORGAN (300045) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0387_P1 | 3 phase fault on FARML 4 (512734) 138 kV Bus a. Apply Fault at the FARML 4 (512734) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from FARML 4 (512734) 138 kV Bus to COFCTY2 (512735) 69 kV Bus to COFFEY1 (512740) 13.8 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0388_P1 | 3 phase fault on DELWARE7 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 (510380) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from DELWARE7 (510380) 345 kV Bus to NEOSHO 7 (532793) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0389_P1 | 3 phase fault on DELWARE7 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 (510380) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from DELWARE7 (510380) 345 kV Bus to N.E.S.-7 (510406) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0390_P4 | a. Apply single phase fault at SUNNYSD7 (515136) 345 kV b. Clear Fault after 16 cycles: b. 1. Trip three winding transformer from SUNNYSD7 (515136) 345 kV to SUNNYSD4 (515135) kV to SUNYSD 1 (515405) 13.8 kV CKT1 b. 2. Trip branch from SUNNYSD7 (515136) 345 kV to TERRYRD7 (511568) 345 kV CKT 1 b. 3. Drop Shunt SUNYSD 1 (515405) 13.8 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0391_P4 | a. Apply single phase fault at ARBUCKL4 (515117) 138 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from ARBUCKL4 (515117) 138 kV to VANOSTP4 (515531) 138 kV CKT 1 b. 2. Trip branch from ARBUCKL4 (515117) 138 kV to SULPHR 4 (515559) 138 kV CKT 1 b. 3. Trip branch from SULPHR 4 (515559) 138 kV to JOLLYVL4 (515118) 138 kV CKT 1 b. 4. Trip branch from JOLLYVL4 (515118) 138 kV to PRICESF4 (514814) 138 kV CKT 1 b. 5. Trip branch from PRICESF4 (514814) 138 kV to HONEYCK4 (515643) 138 kV CKT 1 b. 6. Drop Load 1 SULPHR 4 (515559) 138 kV b. 7. Drop Load 1 JOLLYVL4 (515118) 138 kV b. 8. Drop Load 1 PRICESF4 (514814) 138 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0392_P4 | a. Apply single phase fault at FTSMTHW5 (515301) 161 kV b. Clear Fault after 16 cycles: b. 1. Trip three winding transformer from FTSMTHW5 (515301) 161 kV to FTSMITH7 (515302) kV to FTSMTH51 (515728) 13.8 kV CKT5 b. 2. Trip branch from FTSMTHW5 (515301) 161 kV to ARKOMA 5 (515306) 161 kV CKT 1 b. 3. Trip branch from ARKOMA 5 (515306) 161 kV to 3RDST 5 (515308) 161 kV CKT 1 b. 4. Drop Shunt 1 ARKOMA 5 (515306) 161 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0393_P4 | a. Apply single phase fault at PARKLN 4 (515178) 138 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from PARKLN 4 (515178) 138 kV to LKKONWA4 (515977) 138 kV CKT 1 b. 2. Trip branch from LKKONWA4 (515977) 138 kV to SEMINOL4 (515044) 138 kV CKT 1 b. 3. Trip branch from PARKLN 4 (515178) 138 kV to SOTHADA4 (515318) 138 kV CKT 1 b. 4. Trip branch from SOTHADA4 (515318) 138 kV to HARDEN 4 (515362) 138 kV CKT 1 b. 5. Trip branch from HARDEN 4 (515362) 138 kV to EFITSTP4 (515699) 138 kV CKT 1 b. 6. Trip branch from EFITSTP4 (515699) 138 kV to LULA 4 (515192) 138 kV CKT 1 b. 7. Trip branch from EFITSTP4 (515699) 138 kV to EFITTS 4 (515809) 138 kV CKT 1 b. 8. Drop Load 1 LKKONWA4 (515977) 138 kV b. 9. Drop Load 1 SOTHADA4 (515318) 138 kV b. 10. Drop Load 1 HARDEN 4 (515362) 138 kV b. 11. Drop Load 1 EFITTS 4 (515809) 138 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0394_P4 | a. Apply single phase fault at LONEOAK4 (510897) 138 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from LONEOAK4 (510897) 138 kV to HARTSHN4 (520934) 138 kV CKT 1 b. 2. Trip branch from LONEOAK4 (510897) 138 kV to SMCALTP4 (510906) 138 kV CKT 1 b. 3. Trip branch from SMCALTP4 (510906) 138 kV to MCALEST4 (510908) 138 kV CKT 1 b. 4. Trip branch from SMCALTP4 (510906) 138 kV to S-MCALT4 (510865) 138 kV CKT 1 b. 5. Drop Load 1 S-MCALT4 (510865) 138 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0395_P4 | a. Apply single phase fault at FTSMTHE5 (515300) 161 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from FTSMTHE5 (515300) 161 kV to QUANXTP5 (515310) 161 kV CKT 1 b. 2. Trip branch from QUANXTP5 (515310) 161 kV to BARLING5 (515311) 161 kV CKT 1 b. 3. Trip branch from QUANXTP5 (515310) 161 kV to QUANEXS5 (515474) 161 kV CKT 1 b. 4. Trip branch from BARLING5 (515311) 161 kV to MASSARD5 (515343) 161 kV CKT 1 b. 5. Trip branch from FTSMTHE5 (515300) 161 kV to COLONY 5 (515345) 161 kV CKT 1 b. 6. Trip branch from COLONY 5 (515345) 161 kV to BATTLEF5 (515349) 161 kV CKT 1 b. 7. Trip branch from BATTLEF5 (515349) 161 kV to RYHLLTP5 (515523) 161 kV CKT 1 b. 8. Drop Load 1 BARLING5 (515311) 161 kV b. 9. Drop Load 1 QUANEXS5 (515474) 161 kV b. 10. Drop Load 1 COLONY 5 (515345) 161 kV b. 11. Drop Load 1 BATTLEF5 (515349) 161 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0396_P4 | a. Apply single phase fault at WELETK4 (510902) 138 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from WELETK4 (510902) 138 kV to WELEETK4 (505592) 138 kV CKT 1 b. 2. Trip branch from WELETK4 (510902) 138 kV to EC.HEN-4 (510923) 138 kV CKT 1 b. 3. Trip branch from EC.HEN-4 (510923) 138 kV to OKMULGE4 (510898) 138 kV CKT 1 b. 4. Drop Load 1 EC.HEN-4 (510923) 138 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0397_P4 | a. Apply single phase fault at MASSARD5 (515343) 161 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from MASSARD5 (515343) 161 kV to RYHLLTP5 (515523) 161 kV CKT 1 b. 2. Trip branch from MASSARD5 (515343) 161 kV to BARLING5 (515311) 161 kV CKT 1 b. 3. Trip branch from BARLING5 (515311) 161 kV to QUANXTP5 (515310) 161 kV CKT 1 b. 4. Trip branch from QUANXTP5 (515310) 161 kV to FTSMTHE5 (515300) 161 kV CKT 1 b. 5. Trip branch from QUANXTP5 (515310) 161 kV to QUANEXS5 (515474) 161 kV CKT 1 b. 6. Drop Load 1 BARLING5 (515311) 161 kV b. 7. Drop Load 1 QUANEXS5 (515474) 161 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0398_P4 | a. Apply single phase fault at ARCADIA7 (514908) 345 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from ARCADIA7 (514908) 345 kV to REDBUD 7 (514909) 345 kV CKT 1 b. 2. Trip branch from ARCADIA7 (514908) 345 kV to NORTWST7 (514880) 345 kV CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0399_P4 | a. Apply single phase fault at DRAPER 7 (514934) 345 kV b. Clear Fault after 16 cycles: b. 1. Trip three winding transformer from DRAPER 7 (514934) 345 kV to DRAPER 4 (514933) kV to DRAPER41 (515721) 13.8 kV CKT1 b. 2. Trip branch from DRAPER 7 (514934) 345 kV to NSUB345 (555234) kV CKT 1 b. 3. Drop Shunt 1 DRAPER41 (515721) 13.8 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0400_P4 | a. Apply single phase fault at MUSKOGE7 (515224) 345 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from MUSKOGE7 (515224) 345 kV to FTSMITH7 (515302) 345 kV CKT 1 b. 2. Trip branch from MUSKOGE7 (515224) 345 kV to H_SPRNG-TAP (588839) 345 kV CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0401_P4 | a. Apply single phase fault at SEMINOL4 (515044) 138 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from SEMINOL4 (515044) 138 kV to LKKONWA4 (515977) 138 kV CKT 1 b. 2. Trip branch from LKKONWA4 (515977) 138 kV to PARKLN 4 (515178) 138 kV CKT 1 b. 3. Trip branch from SEMINOL4 (515044) 138 kV to MAUD 4 (515055) 138 kV CKT 1 b. 4. Drop Load 1 LKKONWA4 (515977) 138 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0402_P4 | a. Apply single phase fault at CHIKSAW4 (515171) 138 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from CHIKSAW4 (515171) 138 kV to CARTER 4 (515138) 138 kV CKT 1 b. 2. Trip branch from CHIKSAW4 (515171) 138 kV to FNDTION4 (515162) 138 kV CKT 1 b. 3. Trip branch from FNDTION4 (515162) 138 kV to SPRNDAL4 (515172) 138 kV CKT 1 b. 4. Drop Load 1 FNDTION4 (515162) 138 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0403_P4 | a. Apply single phase fault at SUNNYSD4 (515135) 138 kV b. Clear Fault after 16 cycles: b. 1. Trip three winding transformer from SUNNYSD4 (515135) 138 kV to SUNNYSD7 (515136) kV to SUNYSD 1 (515405) 13.8 kV CKT1 b. 2. Trip three winding transformer from SUNNYSD4 (515135) 138 kV to SUNNYSD7 (515136) kV to SUNNYSD1 (515762) 13.8 kV CKT1 b. 3. Drop Shunt 1 SUNYSD 1 (515405) 13.8 kV b. 4. Drop Shunt 1 SUNNYSD1 (515762) 13.8 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0404_P4 | a. Apply single phase fault at MCALEST4 (510908) 138 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from MCALEST4 (510908) 138 kV to TALAWANDA 4 (510951) 138 kV CKT 1 b. 2. Trip branch from TALAWANDA 4 (510951) 138 kV to MCALESTIND 4 (510909) 138 kV CKT 1 b. 3. Trip branch from TALAWANDA 4 (510951) 138 kV to C-RIVER4 (510946) 138 kV CKT 1 b. 4. Trip branch from MCALEST4 (510908) 138 kV to SMCALTP4 (510906) 138 kV CKT 1 b. 5. Trip branch from SMCALTP4 (510906) 138 kV to LONEOAK4 (510897) 138 kV CKT 1 b. 6. Trip branch from SMCALTP4 (510906) 138 kV to S-MCALT4 (510865) 138 kV CKT 1 b. 7. Drop Load 1 S-MCALT4 (510865) 138 kV b. 8. Drop Load 1 MCALESTIND 4 (510909) 138 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0405_P4 | a. Apply single phase fault at S BROWN4 (505602) 138 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from S BROWN4 (505602) 138 kV to RUSSETT4 (521044) 138 kV CKT 1 b. 2. Trip branch from RUSSETT4 (521044) 138 kV to RUSSET-4 (515120) 138 kV CKT 1 b. 3. Trip branch from RUSSETT4 (521044) 138 kV to REAGAN 4 (520465) 138 kV CKT 1 b. 4. Trip branch from S BROWN4 (505602) 138 kV to COLBRTP4 (515159) 138 kV CKT 1 b. 5. Drop Load 1 RUSSETT4 (521044) 138 kV b. 6. Drop Load 1 REAGAN 4 (520465) 138 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0406_P1 | 3 phase fault on PITTSB-7 (510907) 345 kV Bus a. Apply Fault at the PITTSB-7 (510907) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from PITTSB-7 (510907) 345 kV Bus to C-RIVER7 (515422) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 763134 [G18-082-GEN10.6900], 763137 [G18-082-GEN20.6900]
04 - Southeast | 25W | Transfer | Group4_Fault_0407_P1 | 3 phase fault on VALIANT7 (510911) 345 kV Bus a. Apply Fault at the VALIANT7 (510911) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from VALIANT7 (510911) 345 kV Bus to HUGO 7 (521157) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Low voltage ride through fails due to the tripping of G18-115-GEN10 and G18-115-GEN20 units. No cascading was observed and the issue was localised. Model tuning is recommended.
04 - Southeast | 25W | Transfer | Group4_Fault_0408_P1 | 3 phase fault on VALIANT7 (510911) 345 kV Bus a. Apply Fault at the VALIANT7 (510911) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from VALIANT7 (510911) 345 kV Bus to VALIANT4 (510918) 138 kV Bus to VALN3-1 (510939) 13.8 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Low voltage ride through fails due to the tripping of G18-115-GEN10 and G18-115-GEN20 units. No cascading was observed and the issue was localised. Model tuning is recommended.
04 - Southeast | 25W | Transfer | Group4_Fault_0409_P1 | 3 phase fault on VALIANT7 (510911) 345 kV Bus a. Apply Fault at the VALIANT7 (510911) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from VALIANT7 (510911) 345 kV Bus to VALIANT4 (510918) 138 kV Bus to VALN2-1 (510938) 13.8 kV Bus CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Low voltage ride through fails due to the tripping of G18-115-GEN10 and G18-115-GEN20 units. No cascading was observed and the issue was localised. Model tuning is recommended.
04 - Southeast | 25W | Transfer | Group4_Fault_0410_P1 | 3 phase fault on JOHNCO 7 (514809) 345 kV Bus a. Apply Fault at the JOHNCO 7 (514809) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from JOHNCO 7 (514809) 345 kV Bus to SUNNYSD7 (515136) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 588713 [G17-027-GEN10.6900], 588714 [G17-027-GEN20.6900], 588715 [G17-027-GEN30.6900], 588716 [G17-027-GEN40.6900], 762903 [G18-055-GEN10.6600]
04 - Southeast | 25W | Transfer | Group4_Fault_0411_P1 | 3 phase fault on JOHNCO 7 (514809) 345 kV Bus a. Apply Fault at the JOHNCO 7 (514809) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from JOHNCO 7 (514809) 345 kV Bus to JOHNCO 4 (514808) 138 kV Bus to JOHNCO11 (514810) 13.8 kV Bus CKT 1 b. 2. Drop Shunt 1 at JOHNCO11 (514810) 13.8 kV Bus1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 588713 [G17-027-GEN10.6900], 588714 [G17-027-GEN20.6900], 588715 [G17-027-GEN30.6900], 588716 [G17-027-GEN40.6900], 762903 [G18-055-GEN10.6600]
04 - Southeast | 25W | Transfer | Group4_Fault_0412_P1 | 3 phase fault on SEMINOL7 (515045) 345 kV Bus a. Apply Fault at the SEMINOL7 (515045) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from SEMINOL7 (515045) 345 kV Bus to ARCADIA7 (514908) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0413_P1 | 3 phase fault on SEMINOL7 (515045) 345 kV Bus a. Apply Fault at the SEMINOL7 (515045) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from SEMINOL7 (515045) 345 kV Bus to DRAPER 7 (514934) 345 kV Bus CKT 3 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0414_P1 | 3 phase fault on SEMINOL7 (515045) 345 kV Bus a. Apply Fault at the SEMINOL7 (515045) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from SEMINOL7 (515045) 345 kV Bus to DRAPER 7 (514934) 345 kV Bus CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0415_P1 | 3 phase fault on SEMINOL7 (515045) 345 kV Bus a. Apply Fault at the SEMINOL7 (515045) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from SEMINOL7 (515045) 345 kV Bus to H_SPRNG-TAP (588839) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0416_P1 | 3 phase fault on PITTSB-7 (510907) 345 kV Bus a. Apply Fault at the PITTSB-7 (510907) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from PITTSB-7 (510907) 345 kV Bus to SEMINOL7 (515045) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 763134 [G18-082-GEN10.6900], 763137 [G18-082-GEN20.6900]
04 - Southeast | 25W | Transfer | Group4_Fault_0417_P1 | 3 phase fault on SEMINOL7 (515045) 345 kV Bus a. Apply Fault at the SEMINOL7 (515045) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from SEMINOL7 (515045) 345 kV Bus to SEMINOL4 (515044) 138 kV Bus to SEMINO11 (515756) 14.4 kV Bus CKT 1 b. 2. Drop Shunt 1 at SEMINO11 (515756) 14.4 kV Bus1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0418_P1 | 3 phase fault on SEMINOL7 (515045) 345 kV Bus a. Apply Fault at the SEMINOL7 (515045) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from SEMINOL7 (515045) 345 kV Bus to SEMINOL4 (515044) 138 kV Bus to SEMINO21 (515757) 14.4 kV Bus CKT 1 b. 2. Drop Shunt 1 at SEMINO21 (515757) 14.4 kV Bus1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0419_P1 | 3 phase fault on C-RIVER7 (515422) 345 kV Bus a. Apply Fault at the C-RIVER7 (515422) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from C-RIVER7 (515422) 345 kV Bus to C-RIVER4 (510946) 138 kV Bus to C-RIVER1 (510947) 13.8 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0420_P1 | 3 phase fault on C-RIVER7 (515422) 345 kV Bus a. Apply Fault at the C-RIVER7 (515422) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from C-RIVER7 (515422) 345 kV Bus to H_SPRNG-TAP (588839) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0421_P1 | 3 phase fault on VALIANT4 (510918) 138 kV Bus a. Apply Fault at the VALIANT4 (510918) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from VALIANT4 (510918) 138 kV Bus to VALIANT2 (510910) 69 kV Bus to VALN1-1 (510937) 13.8 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0422_P1 | 3 phase fault on VALIANT4 (510918) 138 kV Bus a. Apply Fault at the VALIANT4 (510918) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from VALIANT4 (510918) 138 kV Bus to V-WEYCO4 (510866) 138 kV Bus CKT 1 b. 2. Drop Shunt 1 at V-WEYCO4 (510866) 138 kV Bus1 b. 3. Drop Load 1 at V-WEYCO4 (510866) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0423_P1 | 3 phase fault on VALIANT4 (510918) 138 kV Bus a. Apply Fault at the VALIANT4 (510918) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from VALIANT4 (510918) 138 kV Bus to IDABEL-4 (510886) 138 kV Bus CKT 1 b. 2. Trip branch from IDABEL-4 (510886) 138 kV Bus to B.BOWTP4 (510888) 138 kV Bus CKT 1 b. 3. Drop Load 1 at IDABEL-4 (510886) 138 kV Bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0424_P1 | 3 phase fault on VALIANT4 (510918) 138 kV Bus a. Apply Fault at the VALIANT4 (510918) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from VALIANT4 (510918) 138 kV Bus to HUGO---4 (510901) 138 kV Bus CKT 1 b. 2. Drop Load 1 at HUGO---4 (510901) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0425_P1 | 3 phase fault on VALIANT4 (510918) 138 kV Bus a. Apply Fault at the VALIANT4 (510918) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from VALIANT4 (510918) 138 kV Bus to HUGO PP4 (520948) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0426_P1 | 3 phase fault on JOHNCO 4 (514808) 138 kV Bus a. Apply Fault at the JOHNCO 4 (514808) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from JOHNCO 4 (514808) 138 kV Bus to CANEYCK4 (515150) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0427_P1 | 3 phase fault on PITTSB-7 (510907) 345 kV Bus a. Apply Fault at the PITTSB-7 (510907) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from PITTSB-7 (510907) 345 kV Bus to JOHNCO 7 (514809) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 763134 [G18-082-GEN10.6900], 763137 [G18-082-GEN20.6900]
04 - Southeast | 25W | Transfer | Group4_Fault_0428_P1 | 3 phase fault on JOHNCO 4 (514808) 138 kV Bus a. Apply Fault at the JOHNCO 4 (514808) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from JOHNCO 4 (514808) 138 kV Bus to RUSSET-4 (515120) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0429_P1 | 3 phase fault on JOHNCO 4 (514808) 138 kV Bus a. Apply Fault at the JOHNCO 4 (514808) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from JOHNCO 4 (514808) 138 kV Bus to SXMLCKT4 (515122) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0430_P1 | 3 phase fault on SEMINOL4 (515044) 138 kV Bus a. Apply Fault at the SEMINOL4 (515044) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from SEMINOL4 (515044) 138 kV Bus to VANOSTP4 (515531) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Low voltage ride through fails due to the tripping of G18-115-GEN10 and G18-115-GEN20 units. No cascading was observed and the issue was localised. Model tuning is recommended.
04 - Southeast | 25W | Transfer | Group4_Fault_0431_P1 | 3 phase fault on SEMINOL4 (515044) 138 kV Bus a. Apply Fault at the SEMINOL4 (515044) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from SEMINOL4 (515044) 138 kV Bus to PAOLI- 4 (515100) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Low voltage ride through fails due to the tripping of G18-115-GEN10 and G18-115-GEN20 units. No cascading was observed and the issue was localised. Model tuning is recommended.
04 - Southeast | 25W | Transfer | Group4_Fault_0432_P1 | 3 phase fault on SEMINOL4 (515044) 138 kV Bus a. Apply Fault at the SEMINOL4 (515044) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from SEMINOL4 (515044) 138 kV Bus to MAUD 4 (515055) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Low voltage ride through fails due to the tripping of G18-115-GEN10 and G18-115-GEN20 units. No cascading was observed and the issue was localised. Model tuning is recommended.
04 - Southeast | 25W | Transfer | Group4_Fault_0433_P1 | 3 phase fault on SEMINOL4 (515044) 138 kV Bus a. Apply Fault at the SEMINOL4 (515044) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from SEMINOL4 (515044) 138 kV Bus to LKKONWA4 (515977) 138 kV Bus CKT 1 b. 2. Trip branch from LKKONWA4 (515977) 138 kV Bus to PARKLN 4 (515178) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0434_P1 | 3 phase fault on C-RIVER4 (510946) 138 kV Bus a. Apply Fault at the C-RIVER4 (510946) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from C-RIVER4 (510946) 138 kV Bus to TALAWANDA 4 (510951) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0435_P1 | 3 phase fault on VALIANT2 (510910) 69 kV Bus a. Apply Fault at the VALIANT2 (510910) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from VALIANT2 (510910) 69 kV Bus to WCITYTP2 (510870) 69 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0436_P1 | 3 phase fault on VALIANT2 (510910) 69 kV Bus a. Apply Fault at the VALIANT2 (510910) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from VALIANT2 (510910) 69 kV Bus to KIPUMPT2 (510876) 69 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0437_P1 | 3 phase fault on TURK 7 (507455) 345 kV Bus a. Apply Fault at the TURK 7 (507455) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from TURK 7 (507455) 345 kV Bus to NWTXARK7 (508072) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0438_P1 | 3 phase fault on PITTSB-7 (510907) 345 kV Bus a. Apply Fault at the PITTSB-7 (510907) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from PITTSB-7 (510907) 345 kV Bus to VALIANT7 (510911) 345 kV Bus CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 763134 [G18-082-GEN10.6900], 763137 [G18-082-GEN20.6900]
04 - Southeast | 25W | Transfer | Group4_Fault_0439_P1 | 3 phase fault on TURK 7 (507455) 345 kV Bus a. Apply Fault at the TURK 7 (507455) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from TURK 7 (507455) 345 kV Bus to TURK 4 (507454) 138 kV Bus to TURK 1 (507457) 13.8 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0440_P1 | 3 phase fault on NWTXARK7 (508072) 345 kV Bus a. Apply Fault at the NWTXARK7 (508072) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from NWTXARK7 (508072) 345 kV Bus to NWTXARK4 (508071) 138 kV Bus to NWTEX1-1 (508100) 13.8 kV Bus CKT 1 b. 2. Drop Shunt 1 at NWTEX1-1 (508100) 13.8 kV Bus1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0441_P1 | 3 phase fault on NWTXARK7 (508072) 345 kV Bus a. Apply Fault at the NWTXARK7 (508072) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from NWTXARK7 (508072) 345 kV Bus to NWTXARK4 (508071) 138 kV Bus to NWTEX2-1 (508101) 13.8 kV Bus CKT 2 b. 2. Drop Shunt 1 at NWTEX2-1 (508101) 13.8 kV Bus1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0442_P1 | 3 phase fault on NWTXARK7 (508072) 345 kV Bus a. Apply Fault at the NWTXARK7 (508072) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from NWTXARK7 (508072) 345 kV Bus to LYDIA 7 (508298) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0443_P1 | 3 phase fault on NWTXARK7 (508072) 345 kV Bus a. Apply Fault at the NWTXARK7 (508072) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from NWTXARK7 (508072) 345 kV Bus to WILKES 7 (508841) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0444_P1 | 3 phase fault on NWTXARK7 (508072) 345 kV Bus a. Apply Fault at the NWTXARK7 (508072) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from NWTXARK7 (508072) 345 kV Bus to WELSH 7 (508359) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0445_P1 | 3 phase fault on LYDIA 7 (508298) 345 kV Bus a. Apply Fault at the LYDIA 7 (508298) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from LYDIA 7 (508298) 345 kV Bus to WELSH 7 (508359) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0446_P1 | 3 phase fault on HUGO 7 (521157) 345 kV Bus a. Apply Fault at the HUGO 7 (521157) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from HUGO 7 (521157) 345 kV Bus to HUGOITC4 (520560) 138 kV Bus to HUGO TERTA (521189) 13.8 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0447_P1 | 3 phase fault on SUNNYSD7 (515136) 345 kV Bus a. Apply Fault at the SUNNYSD7 (515136) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from SUNNYSD7 (515136) 345 kV Bus to SUNNYSD4 (515135) 138 kV Bus to SUNNYSD1 (515762) 13.8 kV Bus CKT 1 b. 2. Drop Shunt 1 at SUNNYSD1 (515762) 13.8 kV Bus1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Low voltage ride through fails due to the tripping of G18-115-GEN10 and G18-115-GEN20 units. No cascading was observed and the issue was localised. Model tuning is recommended. |  |  | Generator relays were disabled for the following generators: 588713 [G17-027-GEN10.6900], 588714 [G17-027-GEN20.6900], 588715 [G17-027-GEN30.6900], 588716 [G17-027-GEN40.6900], 762903 [G18-055-GEN10.6600]
04 - Southeast | 25W | Transfer | Group4_Fault_0448_P1 | 3 phase fault on SUNNYSD7 (515136) 345 kV Bus a. Apply Fault at the SUNNYSD7 (515136) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from SUNNYSD7 (515136) 345 kV Bus to SUNNYSD4 (515135) 138 kV Bus to SUNYSD 1 (515405) 13.8 kV Bus CKT 1 b. 2. Drop Shunt 1 at SUNYSD 1 (515405) 13.8 kV Bus1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Low voltage ride through fails due to the tripping of G18-115-GEN10 and G18-115-GEN20 units. No cascading was observed and the issue was localised. Model tuning is recommended. |  |  | Generator relays were disabled for the following generators: 588713 [G17-027-GEN10.6900], 588714 [G17-027-GEN20.6900], 588715 [G17-027-GEN30.6900], 588716 [G17-027-GEN40.6900], 762903 [G18-055-GEN10.6600]
04 - Southeast | 25W | Transfer | Group4_Fault_0449_P1 | 3 phase fault on PITTSB-7 (510907) 345 kV Bus a. Apply Fault at the PITTSB-7 (510907) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from PITTSB-7 (510907) 345 kV Bus to VALIANT7 (510911) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 763134 [G18-082-GEN10.6900], 763137 [G18-082-GEN20.6900]
04 - Southeast | 25W | Transfer | Group4_Fault_0450_P1 | 3 phase fault on SUNNYSD7 (515136) 345 kV Bus a. Apply Fault at the SUNNYSD7 (515136) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from SUNNYSD7 (515136) 345 kV Bus to TERRYRD7 (511568) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Low voltage ride through fails due to the tripping of G18-115-GEN10 and G18-115-GEN20 units. No cascading was observed and the issue was localised. Model tuning is recommended. |  |  | Generator relays were disabled for the following generators: 584862 [G15-045-GEN10.4800], 588713 [G17-027-GEN10.6900], 588714 [G17-027-GEN20.6900], 588715 [G17-027-GEN30.6900], 588716 [G17-027-GEN40.6900], 762903 [G18-055-GEN10.6600]
04 - Southeast | 25W | Transfer | Group4_Fault_0451_P1 | 3 phase fault on ARCADIA7 (514908) 345 kV Bus a. Apply Fault at the ARCADIA7 (514908) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from ARCADIA7 (514908) 345 kV Bus to REDBUD 7 (514909) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0452_P1 | 3 phase fault on ARCADIA7 (514908) 345 kV Bus a. Apply Fault at the ARCADIA7 (514908) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from ARCADIA7 (514908) 345 kV Bus to NORTWST7 (514880) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0453_P1 | 3 phase fault on ARCADIA7 (514908) 345 kV Bus a. Apply Fault at the ARCADIA7 (514908) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from ARCADIA7 (514908) 345 kV Bus to ARCADIA4 (514907) 138 kV Bus to ARCADI41 (515700) 13.8 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0454_P1 | 3 phase fault on ARCADIA7 (514908) 345 kV Bus a. Apply Fault at the ARCADIA7 (514908) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from ARCADIA7 (514908) 345 kV Bus to ARCADIA4 (514907) 138 kV Bus to ARCADI31 (515704) 13.8 kV Bus CKT 1 b. 2. Drop Shunt 1 at ARCADI31 (515704) 13.8 kV Bus1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0455_P1 | 3 phase fault on ARCADIA7 (514908) 345 kV Bus a. Apply Fault at the ARCADIA7 (514908) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from ARCADIA7 (514908) 345 kV Bus to ARCADIA4 (514907) 138 kV Bus to ARCADI21 (515703) 13.8 kV Bus CKT 1 b. 2. Drop Shunt 1 at ARCADI21 (515703) 13.8 kV Bus1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0456_P1 | 3 phase fault on DRAPER 7 (514934) 345 kV Bus a. Apply Fault at the DRAPER 7 (514934) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from DRAPER 7 (514934) 345 kV Bus to DRAPER 4 (514933) 138 kV Bus to DRAPER21 (515792) 13.8 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 761232 [G17-150GEN1 0.6600]
04 - Southeast | 25W | Transfer | Group4_Fault_0457_P1 | 3 phase fault on DRAPER 7 (514934) 345 kV Bus a. Apply Fault at the DRAPER 7 (514934) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from DRAPER 7 (514934) 345 kV Bus to DRAPER 4 (514933) 138 kV Bus to DRAPER41 (515721) 13.8 kV Bus CKT 1 b. 2. Drop Shunt 1 at DRAPER41 (515721) 13.8 kV Bus1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Low voltage ride through fails due to the tripping of G18-115-GEN10 unit. No cascading was observed and the issue was localised. Model tuning is recommended. |  |  | Generator relays were disabled for the following generators: 761232 [G17-150GEN1 0.6600]
04 - Southeast | 25W | Transfer | Group4_Fault_0458_P1 | 3 phase fault on DRAPER 7 (514934) 345 kV Bus a. Apply Fault at the DRAPER 7 (514934) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from DRAPER 7 (514934) 345 kV Bus to DRAPER 4 (514933) 138 kV Bus to DRAPER31 (515720) 13.8 kV Bus CKT 1 b. 2. Drop Shunt 1 at DRAPER31 (515720) 13.8 kV Bus1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Low voltage ride through fails due to the tripping of G18-115-GEN10 unit. No cascading was observed and the issue was localised. Model tuning is recommended. |  |  | Generator relays were disabled for the following generators: 761232 [G17-150GEN1 0.6600]
04 - Southeast | 25W | Transfer | Group4_Fault_0459_P1 | 3 phase fault on DRAPER 7 (514934) 345 kV Bus a. Apply Fault at the DRAPER 7 (514934) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from DRAPER 7 (514934) 345 kV Bus to NSUB345 (555234) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 761232 [G17-150GEN1 0.6600]
04 - Southeast | 25W | Transfer | Group4_Fault_0460_P1 | 3 phase fault on VALIANT7 (510911) 345 kV Bus a. Apply Fault at the VALIANT7 (510911) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from VALIANT7 (510911) 345 kV Bus to TURK 7 (507455) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Low voltage ride through fails due to the tripping of G18-115-GEN10 and G18-115-GEN20 units. No cascading was observed and the issue was localised. Model tuning is recommended.
04 - Southeast | 25W | Transfer | Group4_Fault_0461_P1 | 3 phase fault on DRAPER 7 (514934) 345 kV Bus a. Apply Fault at the DRAPER 7 (514934) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from DRAPER 7 (514934) 345 kV Bus to NSUB345 (555234) 345 kV Bus CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 761232 [G17-150GEN1 0.6600]
04 - Southeast | 25W | Transfer | Group4_Fault_0462_P1 | 3 phase fault on MUSKOGE7 (515224) 345 kV Bus a. Apply Fault at the MUSKOGE7 (515224) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from MUSKOGE7 (515224) 345 kV Bus to H_SPRNG-TAP (588839) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 760392 [G17-140-GEN10.6300], 760412 [G17-141-GEN10.6300]
04 - Southeast | 25W | Transfer | Group4_Fault_0463_P1 | 3 phase fault on MUSKOGE7 (515224) 345 kV Bus a. Apply Fault at the MUSKOGE7 (515224) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from MUSKOGE7 (515224) 345 kV Bus to CLARKSV7 (509745) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 760392 [G17-140-GEN10.6300], 760412 [G17-141-GEN10.6300]
04 - Southeast | 25W | Transfer | Group4_Fault_0464_P1 | 3 phase fault on MUSKOGE7 (515224) 345 kV Bus a. Apply Fault at the MUSKOGE7 (515224) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from MUSKOGE7 (515224) 345 kV Bus to PECANCK7 (515235) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 760392 [G17-140-GEN10.6300], 760412 [G17-141-GEN10.6300]
04 - Southeast | 25W | Transfer | Group4_Fault_0465_P1 | 3 phase fault on MUSKOGE7 (515224) 345 kV Bus a. Apply Fault at the MUSKOGE7 (515224) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from MUSKOGE7 (515224) 345 kV Bus to PECANCK7 (515235) 345 kV Bus CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 760392 [G17-140-GEN10.6300], 760412 [G17-141-GEN10.6300]
04 - Southeast | 25W | Transfer | Group4_Fault_0466_P1 | 3 phase fault on HUGO---4 (510901) 138 kV Bus a. Apply Fault at the HUGO---4 (510901) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from HUGO---4 (510901) 138 kV Bus to HUGO---2 (510893) 69 kV Bus to HUGO4-1 (510859) 13.8 kV Bus CKT 1 b. 2. Drop Load 1 at HUGO---4 (510901) 138 kV Bus b. 3. Drop Load 1 at HUGO---2 (510893) 69 kV Bus b. 4. Drop Shunt 1 at HUGO---2 (510893) 69 kV Bus1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0467_P1 | 3 phase fault on HUGO PP4 (520948) 138 kV Bus a. Apply Fault at the HUGO PP4 (520948) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from HUGO PP4 (520948) 138 kV Bus to HUGOITC4 (520560) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0468_P1 | 3 phase fault on HUGO PP4 (520948) 138 kV Bus a. Apply Fault at the HUGO PP4 (520948) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from HUGO PP4 (520948) 138 kV Bus to VALLANT4 (521079) 138 kV Bus CKT 1 b. 2. Trip branch from VALLANT4 (521079) 138 kV Bus to GARVIN4 (520419) 138 kV Bus CKT 1 b. 3. Trip branch from GARVIN4 (520419) 138 kV Bus to IDABEL 4 (520953) 138 kV Bus CKT 1 b. 4. Drop Load 1 at VALLANT4 (521079) 138 kV Bus b. 5. Drop Load 1 at GARVIN4 (520419) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0469_P1 | 3 phase fault on HUGO PP4 (520948) 138 kV Bus a. Apply Fault at the HUGO PP4 (520948) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from HUGO PP4 (520948) 138 kV Bus to FROGVIL4 (520918) 138 kV Bus CKT 1 b. 2. Trip branch from FROGVIL4 (520918) 138 kV Bus to WSBNKTP4 (521098) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0470_P1 | 3 phase fault on HUGO PP4 (520948) 138 kV Bus a. Apply Fault at the HUGO PP4 (520948) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from HUGO PP4 (520948) 138 kV Bus to SAWYER4 (520411) 138 kV Bus CKT 1 b. 2. Trip branch from SAWYER4 (520411) 138 kV Bus to RATTAN 4 (521036) 138 kV Bus CKT 1 b. 3. Trip branch from RATTAN 4 (521036) 138 kV Bus to DARWIN 4 (520874) 138 kV Bus CKT 1 b. 4. Trip branch from DARWIN 4 (520874) 138 kV Bus to LANE 4 (520968) 138 kV Bus CKT 1 b. 5. Trip branch from LANE 4 (520968) 138 kV Bus to ATOKA--4 (510887) 138 kV Bus CKT 1 b. 6. Drop Load 1 at SAWYER4 (520411) 138 kV Bus b. 7. Drop Load 1 at RATTAN 4 (521036) 138 kV Bus b. 8. Drop Load 1 at DARWIN 4 (520874) 138 kV Bus b. 9. Drop Load 1 at LANE 4 (520968) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0471_P1 | 3 phase fault on VALIANT7 (510911) 345 kV Bus a. Apply Fault at the VALIANT7 (510911) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from VALIANT7 (510911) 345 kV Bus to NWTXARK7 (508072) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Low voltage ride through fails due to the tripping of G18-115-GEN10 and G18-115-GEN20 units. No cascading was observed and the issue was localised. Model tuning is recommended.
04 - Southeast | 25W | Transfer | Group4_Fault_0472_P1 | 3 phase fault on RUSSET-4 (515120) 138 kV Bus a. Apply Fault at the RUSSET-4 (515120) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from RUSSET-4 (515120) 138 kV Bus to RUSSETT4 (521044) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0473_P1 | 3 phase fault on RUSSET-4 (515120) 138 kV Bus a. Apply Fault at the RUSSET-4 (515120) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from RUSSET-4 (515120) 138 kV Bus to GLASSES4 (515147) 138 kV Bus CKT 1 b. 2. Trip branch from GLASSES4 (515147) 138 kV Bus to MADINDT4 (515149) 138 kV Bus CKT 1 b. 3. Drop Load 1 at GLASSES4 (515147) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0474_P1 | 3 phase fault on RUSSET-4 (515120) 138 kV Bus a. Apply Fault at the RUSSET-4 (515120) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from RUSSET-4 (515120) 138 kV Bus to STIRLNG4 (515932) 138 kV Bus CKT 1 b. 2. Trip branch from STIRLNG4 (515932) 138 kV Bus to DRPSPRG4 (515873) 138 kV Bus CKT 1 b. 3. Trip branch from DRPSPRG4 (515873) 138 kV Bus to SPRNDAL4 (515172) 138 kV Bus CKT 1 b. 4. Drop Load 1 at STIRLNG4 (515932) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0475_P1 | 3 phase fault on SXMLCKT4 (515122) 138 kV Bus a. Apply Fault at the SXMLCKT4 (515122) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from SXMLCKT4 (515122) 138 kV Bus to HOWE 4 (521122) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0476_P1 | 3 phase fault on SXMLCKT4 (515122) 138 kV Bus a. Apply Fault at the SXMLCKT4 (515122) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from SXMLCKT4 (515122) 138 kV Bus to MILLCKT4 (515121) 138 kV Bus CKT 1 b. 2. Trip branch from MILLCKT4 (515121) 138 kV Bus to MILLCRK4 (515196) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0477_P1 | 3 phase fault on CANEYCK4 (515150) 138 kV Bus a. Apply Fault at the CANEYCK4 (515150) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from CANEYCK4 (515150) 138 kV Bus to TEXOMAJ4 (521067) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0478_P1 | 3 phase fault on CANEYCK4 (515150) 138 kV Bus a. Apply Fault at the CANEYCK4 (515150) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from CANEYCK4 (515150) 138 kV Bus to TEXOMAJ4 (521067) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0479_P1 | 3 phase fault on CANEYCK4 (515150) 138 kV Bus a. Apply Fault at the CANEYCK4 (515150) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from CANEYCK4 (515150) 138 kV Bus to LTLCITY4 (515151) 138 kV Bus CKT 1 b. 2. Trip branch from LTLCITY4 (515151) 138 kV Bus to BROWNTP4 (515152) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0480_P1 | 3 phase fault on CANEYCK4 (515150) 138 kV Bus a. Apply Fault at the CANEYCK4 (515150) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from CANEYCK4 (515150) 138 kV Bus to MADINDT4 (515149) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0481_P1 | 3 phase fault on ARCADIA7 (514908) 345 kV Bus a. Apply Fault at the ARCADIA7 (514908) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from ARCADIA7 (514908) 345 kV Bus to REDBUD 7 (514909) 345 kV Bus CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0482_P1 | 3 phase fault on ARCADIA7 (514908) 345 kV Bus a. Apply Fault at the ARCADIA7 (514908) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from ARCADIA7 (514908) 345 kV Bus to REDBUD 7 (514909) 345 kV Bus CKT 3 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0483_P1 | 3 phase fault on SEMINOL7 (515045) 345 kV Bus a. Apply Fault at the SEMINOL7 (515045) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from SEMINOL7 (515045) 345 kV Bus to DRAPER 7 (514934) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0484_P1 | 3 phase fault on VALIANT7 (510911) 345 kV Bus a. Apply Fault at the VALIANT7 (510911) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from VALIANT7 (510911) 345 kV Bus to LYDIA 7 (508298) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Low voltage ride through fails due to the tripping of G18-115-GEN10 and G18-115-GEN20 units. No cascading was observed and the issue was localised. Model tuning is recommended.
04 - Southeast | 25W | Transfer | Group4_Fault_0485_P4 | a. Apply single phase fault at LYDIA 7 (508298) 345 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from LYDIA 7 (508298) 345 kV to WELSH 7 (508359) 345 kV CKT 1 b. 2. Trip branch from LYDIA 7 (508298) 345 kV to VALIANT7 (510911) 345 kV CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0486_P4 | a. Apply single phase fault at DIANA 4 (508831) 138 kV b. Clear Fault after 16 cycles: b. 1. Trip three winding transformer from DIANA 4 (508831) 138 kV to DIANA 7 (508832) kV to DIANA-N1 (508845) 13.8 kV CKT3 b. 2. Trip branch from DIANA 4 (508831) 138 kV to PERDUE 4 (508351) 138 kV CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0487_P4 | a. Apply single phase fault at BANN 4 (508054) 138 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from BANN 4 (508054) 138 kV to NWT-BNT4 (508070) 138 kV CKT 1 b. 2. Trip branch from BANN 4 (508054) 138 kV to REDSPRG4 (508075) 138 kV CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0488_P4 | a. Apply single phase fault at LONGWD 4 (508808) 138 kV b. Clear Fault after 16 cycles: b. 1. Trip three winding transformer from LONGWD 4 (508808) 138 kV to LONGWD 7 (508809) kV to LONGW1-1 (508819) 13.2 kV CKT1 b. 2. Trip branch from LONGWD 4 (508808) 138 kV to LIEBERM4 (508806) 138 kV CKT 1 b. 3. Drop Shunt 1 LONGW1-1 (508819) 13.2 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0489_P4 | a. Apply single phase fault at SW SHV 4 (507759) 138 kV b. Clear Fault after 16 cycles: b. 1. Trip three winding transformer from SW SHV 4 (507759) 138 kV to SW SHV 7 (507760) kV to SWSHV1-1 (507778) 13.8 kV CKT1 b. 2. Trip branch from SW SHV 4 (507759) 138 kV to LEASIDE 4 (507793) 138 kV CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0490_P4 | a. Apply single phase fault at PIRKEY 4 (508562) 138 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from PIRKEY 4 (508562) 138 kV to EASTON 4 (509092) 138 kV CKT 1 b. 2. Trip branch from EASTON 4 (509092) 138 kV to BRANDYBR (508596) 138 kV CKT 1 b. 3. Trip branch from BRANDYBR (508596) 138 kV to KNOXLEE4 (508548) 138 kV CKT 1 b. 4. Trip branch from PIRKEY 4 (508562) 138 kV to HALLSVLS4 (508595) 138 kV CKT 1 b. 5. Trip branch from HALLSVLS4 (508595) 138 kV to WHITNEY4 (508575) 138 kV CKT 1 b. 6. Drop Load 1 EASTON 4 (509092) 138 kV b. 7. Drop Load 1 WHITNEY4 (508575) 138 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0491_P4 | a. Apply single phase fault at NWTXARK7 (508072) 345 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from NWTXARK7 (508072) 345 kV to TURK 7 (507455) 345 kV CKT 1 b. 2. Trip branch from NWTXARK7 (508072) 345 kV to VALIANT7 (510911) 345 kV CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0492_P4 | a. Apply single phase fault at VALIANT7 (510911) 345 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from VALIANT7 (510911) 345 kV to PITTSB-7 (510907) 345 kV CKT 1 b. 2. Trip branch from VALIANT7 (510911) 345 kV to PITTSB-7 (510907) 345 kV CKT 2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0493_P4 | a. Apply single phase fault at NWTXARK4 (508071) 138 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from NWTXARK4 (508071) 138 kV to NWT-BNT4 (508070) 138 kV CKT 1 b. 2. Trip three winding transformer from NWTXARK7 (508072) 345 kV to NWTXARK4 (508071) kV to NWTEX1-1 (508100) 13.8 kV CKT1 b. 3. Drop Shunt 1 NWTEX1-1 (508100) 13.8 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0494_P4 | a. Apply single phase fault at PITTSB-7 (510907) 345 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from PITTSB-7 (510907) 345 kV to SEMINOL7 (515045) 345 kV CKT 1 b. 2. Trip branch from PITTSB-7 (510907) 345 kV to VALIANT7 (510911) 345 kV CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0495_P4 | a. Apply single phase fault at VALIANT4 (510918) 138 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from VALIANT4 (510918) 138 kV to HUGO PP4 (520948) 138 kV CKT 1 b. 2. Trip branch from VALIANT4 (510918) 138 kV to IDABEL-4 (510886) 138 kV CKT 1 b. 3. Trip branch from IDABEL-4 (510886) 138 kV to B.BOWTP4 (510888) 138 kV CKT 1 b. 4. Trip branch from B.BOWTP4 (510888) 138 kV to CRAIGJT4 (510890) 138 kV CKT 1 b. 5. Trip branch from B.BOWTP4 (510888) 138 kV to B.BOW 4 (510864) 138 kV CKT 1 b. 6. Drop Load 1 IDABEL-4 (510886) 138 kV b. 7. Drop Load 1 B.BOW 4 (510864) 138 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0496_P4 | a. Apply single phase fault at TURK 4 (507454) 138 kV b. Clear Fault after 16 cycles: b. 1. Trip three winding transformer from TURK 4 (507454) 138 kV to TURK 7 (507455) kV to TURK 1 (507457) 13.8 kV CKT1 b. 2. Trip branch from TURK 4 (507454) 138 kV to MANDEVILTP4 (508105) 138 kV CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0497_P4 | a. Apply single phase fault at WILKES 4 (508840) 138 kV b. Clear Fault after 16 cycles: b. 1. Trip three winding transformer from WILKES 4 (508840) 138 kV to WILKES 7 (508841) kV to WILKES-1 (508826) 13.2 kV CKT1 b. 2. Trip branch from WILKES 4 (508840) 138 kV to LSSOUTH4 (508297) 138 kV CKT 1 b. 3. Drop Shunt 1 WILKES-1 (508826) 13.2 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0498_P4 | a. Apply single phase fault at PIRKEY 7 (508563) 345 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from PIRKEY 7 (508563) 345 kV to DIANA 7 (508832) 345 kV CKT 1 b. 2. Trip branch from PIRKEY 7 (508563) 345 kV to LEBROCK7 (508572) 345 kV CKT 2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0499_P1 | 3 phase fault on DIANA 7 (508832) 345 kV Bus a. Apply Fault at the DIANA 7 (508832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from DIANA 7 (508832) 345 kV Bus to DIANA 4 (508831) 138 kV Bus to DIANA-M1 (508843) 13.8 kV Bus CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0500_P1 | 3 phase fault on DIANA 7 (508832) 345 kV Bus a. Apply Fault at the DIANA 7 (508832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from DIANA 7 (508832) 345 kV Bus to DIANA 4 (508831) 138 kV Bus to DIANA-N1 (508845) 13.8 kV Bus CKT 3 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0501_P1 | 3 phase fault on WELSH 7 (508359) 345 kV Bus a. Apply Fault at the WELSH 7 (508359) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from WELSH 7 (508359) 345 kV Bus to DIANA 7 (508832) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0502_P1 | 3 phase fault on TURK 4 (507454) 138 kV Bus a. Apply Fault at the TURK 4 (507454) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from TURK 4 (507454) 138 kV Bus to TURK 3 (507456) 115 kV Bus to TURK1 1 (507458) 13.2 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0503_P1 | 3 phase fault on WELSH 7 (508359) 345 kV Bus a. Apply Fault at the WELSH 7 (508359) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from WELSH 7 (508359) 345 kV Bus to DIANA 7 (508832) 345 kV Bus CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0504_P1 | 3 phase fault on WELSH 7 (508359) 345 kV Bus a. Apply Fault at the WELSH 7 (508359) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from WELSH 7 (508359) 345 kV Bus to SPPMAINBUS (5917) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0505_P1 | 3 phase fault on DIANA 7 (508832) 345 kV Bus a. Apply Fault at the DIANA 7 (508832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from DIANA 7 (508832) 345 kV Bus to SW SHV 7 (507760) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0506_P1 | 3 phase fault on DIANA 7 (508832) 345 kV Bus a. Apply Fault at the DIANA 7 (508832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from DIANA 7 (508832) 345 kV Bus to DIANA 4 (508831) 138 kV Bus to DIANA-S1 (508844) 13.8 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0507_P1 | 3 phase fault on LONGWD 7 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 (508809) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from LONGWD 7 (508809) 345 kV Bus to WILKES 7 (508841) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0508_P1 | 3 phase fault on WHITNEY4 (508575) 138 kV Bus a. Apply Fault at the WHITNEY4 (508575) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from WHITNEY4 (508575) 138 kV Bus to EASTEX 4 (508582) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0509_P1 | 3 phase fault on WHITNEY4 (508575) 138 kV Bus a. Apply Fault at the WHITNEY4 (508575) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from WHITNEY4 (508575) 138 kV Bus to WHITNEY2 (508574) 69 kV Bus to WHIT1-1 (508589) 12.47 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0510_P1 | 3 phase fault on WHITNEY4 (508575) 138 kV Bus a. Apply Fault at the WHITNEY4 (508575) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from WHITNEY4 (508575) 138 kV Bus to WHITNEY2 (508574) 69 kV Bus to WHIT2-1 (508590) 12.47 kV Bus CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0511_P1 | 3 phase fault on LONGWD 4 (508808) 138 kV Bus a. Apply Fault at the LONGWD 4 (508808) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from LONGWD 4 (508808) 138 kV Bus to OAKPH 4 (508816) 138 kV Bus CKT 1 b. 2. Trip branch from OAKPH 4 (508816) 138 kV Bus to FLOURNY4 (507727) 138 kV Bus CKT 1 b. 3. Drop Load 1 at OAKPH 4 (508816) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0512_P1 | 3 phase fault on LONGWD 4 (508808) 138 kV Bus a. Apply Fault at the LONGWD 4 (508808) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from LONGWD 4 (508808) 138 kV Bus to NORAM 4 (507774) 138 kV Bus CKT 1 b. 2. Trip branch from NORAM 4 (507774) 138 kV Bus to RAINES 4 (507749) 138 kV Bus CKT 1 b. 3. Trip branch from RAINES 4 (507749) 138 kV Bus to ARSHILL4 (507711) 138 kV Bus CKT 1 b. 4. Drop Load 1 at NORAM 4 (507774) 138 kV Bus b. 5. Drop Load 1 at RAINES 4 (507749) 138 kV Bus b. 6. Drop Shunt 1 at RAINES 4 (507749) 138 kV Bus1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0513_P1 | 3 phase fault on LONGWD 4 (508808) 138 kV Bus a. Apply Fault at the LONGWD 4 (508808) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from LONGWD 4 (508808) 138 kV Bus to LIEBERM4 (508806) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0514_P1 | 3 phase fault on FLOURNY4 (507727) 138 kV Bus a. Apply Fault at the FLOURNY4 (507727) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from FLOURNY4 (507727) 138 kV Bus to FLOURNY2 (507726) 69 kV Bus to FLOURNY1 (507740) 12.47 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0515_P1 | 3 phase fault on FLOURNY4 (507727) 138 kV Bus a. Apply Fault at the FLOURNY4 (507727) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from FLOURNY4 (507727) 138 kV Bus to GENMOTR4 (507732) 138 kV Bus CKT 1 b. 2. Trip branch from GENMOTR4 (507732) 138 kV Bus to SW SHV 4 (507759) 138 kV Bus CKT 1 b. 3. Drop Load 1 at GENMOTR4 (507732) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0516_P1 | 3 phase fault on FLOURNY2 (507726) 69 kV Bus a. Apply Fault at the FLOURNY2 (507726) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from FLOURNY2 (507726) 69 kV Bus to WOOLWTP2 (507770) 69 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0517_P1 | 3 phase fault on FLOURNY2 (507726) 69 kV Bus a. Apply Fault at the FLOURNY2 (507726) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from FLOURNY2 (507726) 69 kV Bus to PINESRD2 (507747) 69 kV Bus CKT 1 b. 2. Trip branch from PINESRD2 (507747) 69 kV Bus to HARDY 2 (507734) 69 kV Bus CKT 1 b. 3. Drop Load 1 at PINESRD2 (507747) 69 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0518_P1 | 3 phase fault on FLOURNY2 (507726) 69 kV Bus a. Apply Fault at the FLOURNY2 (507726) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from FLOURNY2 (507726) 69 kV Bus to WASKOM 2 (508839) 69 kV Bus CKT 1 b. 2. Trip branch from WASKOM 2 (508839) 69 kV Bus to MVPIPET2 (508825) 69 kV Bus CKT 1 b. 3. Drop Load 1 at WASKOM 2 (508839) 69 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0519_P1 | 3 phase fault on ARSHILL4 (507711) 138 kV Bus a. Apply Fault at the ARSHILL4 (507711) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from ARSHILL4 (507711) 138 kV Bus to FTHUMBG4 (507731) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0520_P1 | 3 phase fault on ARSHILL4 (507711) 138 kV Bus a. Apply Fault at the ARSHILL4 (507711) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from ARSHILL4 (507711) 138 kV Bus to MCWILLI4 (507742) 138 kV Bus CKT 1 b. 2. Trip branch from MCWILLI4 (507742) 138 kV Bus to LINWOOD4 (507738) 138 kV Bus CKT 1 b. 3. Drop Load 1 at MCWILLI4 (507742) 138 kV Bus b. 4. Drop Shunt 1 at MCWILLI4 (507742) 138 kV Bus1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0521_P1 | 3 phase fault on ARSHILL4 (507711) 138 kV Bus a. Apply Fault at the ARSHILL4 (507711) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from ARSHILL4 (507711) 138 kV Bus to ARSHILL2 (507710) 69 kV Bus to ARSH1-1 (507712) 12.47 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0522_P1 | 3 phase fault on ARSHILL4 (507711) 138 kV Bus a. Apply Fault at the ARSHILL4 (507711) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from ARSHILL4 (507711) 138 kV Bus to ARSHILL2 (507710) 69 kV Bus to ARSH2-1 (507714) 14.5 kV Bus CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0523_P1 | 3 phase fault on ARSHILL4 (507711) 138 kV Bus a. Apply Fault at the ARSHILL4 (507711) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from ARSHILL4 (507711) 138 kV Bus to LIEBERM4 (508806) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0524_P1 | 3 phase fault on LIEBERM4 (508806) 138 kV Bus a. Apply Fault at the LIEBERM4 (508806) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from LIEBERM4 (508806) 138 kV Bus to IPCJEFF4 (508833) 138 kV Bus CKT 1 b. 2. Trip branch from IPCJEFF4 (508833) 138 kV Bus to JEFFRSN4 (508835) 138 kV Bus CKT 1 b. 3. Drop Load 1 at IPCJEFF4 (508833) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0526_P1 | 3 phase fault on LEBROCK7 (508572) 345 kV Bus a. Apply Fault at the LEBROCK7 (508572) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from LEBROCK7 (508572) 345 kV Bus to PIRKEY 7 (508563) 345 kV Bus CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0527_P1 | 3 phase fault on LEBROCK7 (508572) 345 kV Bus a. Apply Fault at the LEBROCK7 (508572) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from LEBROCK7 (508572) 345 kV Bus to TENRUSK7 (508585) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0528_P1 | 3 phase fault on TENRUSK7 (508585) 345 kV Bus a. Apply Fault at the TENRUSK7 (508585) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from TENRUSK7 (508585) 345 kV Bus to CROCKET7 (509241) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0529_P1 | 3 phase fault on CROCKET7 (509241) 345 kV Bus a. Apply Fault at the CROCKET7 (509241) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from CROCKET7 (509241) 345 kV Bus to 7GRIMES% (334028) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0530_P1 | 3 phase fault on SW SHV 4 (507759) 138 kV Bus a. Apply Fault at the SW SHV 4 (507759) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from SW SHV 4 (507759) 138 kV Bus to LEASIDE 4 (507793) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0531_P1 | 3 phase fault on SW SHV 4 (507759) 138 kV Bus a. Apply Fault at the SW SHV 4 (507759) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from SW SHV 4 (507759) 138 kV Bus to S SHV 4 (507755) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0532_P1 | 3 phase fault on SW SHV 4 (507759) 138 kV Bus a. Apply Fault at the SW SHV 4 (507759) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from SW SHV 4 (507759) 138 kV Bus to POWELL 4 (507748) 138 kV Bus CKT 1 b. 2. Trip branch from POWELL 4 (507748) 138 kV Bus to LINWOOD4 (507738) 138 kV Bus CKT 1 b. 3. Drop Load 1 at POWELL 4 (507748) 138 kV Bus b. 4. Drop Shunt 1 at POWELL 4 (507748) 138 kV Bus1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0533_P1 | 3 phase fault on SW SHV 4 (507759) 138 kV Bus a. Apply Fault at the SW SHV 4 (507759) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from SW SHV 4 (507759) 138 kV Bus to SPRIDGE4 (507757) 138 kV Bus CKT 1 b. 2. Trip branch from SPRIDGE4 (507757) 138 kV Bus to WLNTSPRINGS4 (509103) 138 kV Bus CKT 1 b. 3. Trip branch from WLNTSPRINGS4 (509103) 138 kV Bus to ROKHILL4 (509083) 138 kV Bus CKT 1 b. 4. Drop Load 1 at SPRIDGE4 (507757) 138 kV Bus b. 5. Drop Load 2 at SPRIDGE4 (507757) 138 kV Bus b. 6. Drop Load 1 at WLNTSPRINGS4 (509103) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0534_P1 | 3 phase fault on DOLHILL6 (500260) 230 kV Bus a. Apply Fault at the DOLHILL6 (500260) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from DOLHILL6 (500260) 230 kV Bus to CARROLL6 (500140) 230 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0535_P1 | 3 phase fault on DOLHILL6 (500260) 230 kV Bus a. Apply Fault at the DOLHILL6 (500260) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from DOLHILL6 (500260) 230 kV Bus to REDBAYOU_6 (500255) 230 kV Bus CKT 1 b. 2. Trip branch from REDBAYOU_6 (500255) 230 kV Bus to MANCOMP 6 (500525) 230 kV Bus CKT 1 b. 3. Trip branch from MANCOMP 6 (500525) 230 kV Bus to J1673 POI (46734) 230 kV Bus CKT 1 b. 4. Drop Load IN at REDBAYOU_6 (500255) 230 kV Bus b. 5. Drop Load IN at MANCOMP 6 (500525) 230 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0536_P1 | 3 phase fault on J1673 POI (46734) 230 kV Bus a. Apply Fault at the J1673 POI (46734) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from J1673 POI (46734) 230 kV Bus to FISHER 6 (500310) 230 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0537_P1 | 3 phase fault on SUNNYSD7 (515136) 345 kV Bus a. Apply Fault at the SUNNYSD7 (515136) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from SUNNYSD7 (515136) 345 kV Bus to G16-063-TAP (560088) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Low voltage ride through fails due to the tripping of G18-115-GEN10 and G18-115-GEN20 units. No cascading was observed and the issue was localised. Model tuning is recommended. |  |  | Generator relays were disabled for the following generators: 584862 [G15-045-GEN10.4800], 588713 [G17-027-GEN10.6900], 588714 [G17-027-GEN20.6900], 588715 [G17-027-GEN30.6900], 588716 [G17-027-GEN40.6900], 762903 [G18-055-GEN10.6600]
04 - Southeast | 25W | Transfer | Group4_Fault_0538_P1 | 3 phase fault on B.BOWTP4 (510888) 138 kV Bus a. Apply Fault at the B.BOWTP4 (510888) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from B.BOWTP4 (510888) 138 kV Bus to CRAIGJT4 (510890) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0539_P1 | 3 phase fault on B.BOWTP4 (510888) 138 kV Bus a. Apply Fault at the B.BOWTP4 (510888) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from B.BOWTP4 (510888) 138 kV Bus to B.BOW 4 (510864) 138 kV Bus CKT 1 b. 2. Drop Load 1 at B.BOW 4 (510864) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0540_P1 | 3 phase fault on SUGARHL4 (508080) 138 kV Bus a. Apply Fault at the SUGARHL4 (508080) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from SUGARHL4 (508080) 138 kV Bus to SUGARHL2 (508079) 69 kV Bus to SHILL1-1 (508103) 12.47 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0541_P1 | 3 phase fault on HOPE 3 (507453) 115 kV Bus a. Apply Fault at the HOPE 3 (507453) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from HOPE 3 (507453) 115 kV Bus to HOPESWI3 (507452) 115 kV Bus CKT 1 b. 2. Drop Shunt 1 at HOPE 3 (507453) 115 kV Bus1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0542_P1 | 3 phase fault on MANDEVILTP4 (508105) 138 kV Bus a. Apply Fault at the MANDEVILTP4 (508105) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from MANDEVILTP4 (508105) 138 kV Bus to SETEXAR4 (508078) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0543_P1 | 3 phase fault on MANDEVILTP4 (508105) 138 kV Bus a. Apply Fault at the MANDEVILTP4 (508105) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from MANDEVILTP4 (508105) 138 kV Bus to NE-TEXARK2 (504363) 69 kV Bus to NE-TEXARK1 (504364) 13.8 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0544_P1 | 3 phase fault on OKAY 4 (507428) 138 kV Bus a. Apply Fault at the OKAY 4 (507428) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from OKAY 4 (507428) 138 kV Bus to OKAY 2 (507427) 69 kV Bus to OKAY1-1 (507442) 13.8 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0545_P1 | 3 phase fault on BANN 4 (508054) 138 kV Bus a. Apply Fault at the BANN 4 (508054) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from BANN 4 (508054) 138 kV Bus to BANN 2 (508053) 69 kV Bus to BANN1-1 (508097) 13.8 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0546_P1 | 3 phase fault on BANN 4 (508054) 138 kV Bus a. Apply Fault at the BANN 4 (508054) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from BANN 4 (508054) 138 kV Bus to BANN 2 (508053) 69 kV Bus to BANN2-1 (508096) 14.5 kV Bus CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0547_P1 | 3 phase fault on BANN 4 (508054) 138 kV Bus a. Apply Fault at the BANN 4 (508054) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from BANN 4 (508054) 138 kV Bus to REDSPRG4 (508075) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0548_P1 | 3 phase fault on BANN 4 (508054) 138 kV Bus a. Apply Fault at the BANN 4 (508054) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from BANN 4 (508054) 138 kV Bus to SETEXAR4 (508078) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0549_P1 | 3 phase fault on BANN 4 (508054) 138 kV Bus a. Apply Fault at the BANN 4 (508054) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from BANN 4 (508054) 138 kV Bus to NWT-BNT4 (508070) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0550_P1 | 3 phase fault on CROCKET7 (509241) 345 kV Bus a. Apply Fault at the CROCKET7 (509241) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from CROCKET7 (509241) 345 kV Bus to CROCKET4 (509240) 138 kV Bus to CROCK-B1 (509243) 13.8 kV Bus CKT 1 b. 2. Trip branch from CROCKET4 (509240) 138 kV Bus to GRAPLND4 (509322) 138 kV Bus CKT 1 b. 3. Trip branch from GRAPLND4 (509322) 138 kV Bus to SLOCUM 4 (509326) 138 kV Bus CKT 1 b. 4. Trip branch from SLOCUM 4 (509326) 138 kV Bus to ALTO 4 (509320) 138 kV Bus CKT 1 b. 5. Trip branch from ALTO 4 (509320) 138 kV Bus to PINEGRV4 (509324) 138 kV Bus CKT 1 b. 6. Trip branch from PINEGRV4 (509324) 138 kV Bus to JACKSNV4 (509242) 138 kV Bus CKT 1 b. 7. Trip branch from JACKSNV4 (509242) 138 kV Bus to OVERTON4 (509080) 138 kV Bus CKT 1 b. 8. Drop Load 1 at GRAPLND4 (509322) 138 kV Bus b. 9. Drop Load 1 at SLOCUM 4 (509326) 138 kV Bus b. 10. Drop Load 1 at SLOCUM 4 (509326) 138 kV Bus b. 11. Drop Load 1 at ALTO 4 (509320) 138 kV Bus b. 12. Drop Load 1 at PINEGRV4 (509324) 138 kV Bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0551_P1 | 3 phase fault on 7GRIMES% (334028) 345 kV Bus a. Apply Fault at the 7GRIMES% (334028) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from 7GRIMES% (334028) 345 kV Bus to 7ROCKYCRK% (334197) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0552_P1 | 3 phase fault on 7GRIMES% (334028) 345 kV Bus a. Apply Fault at the 7GRIMES% (334028) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from 7GRIMES% (334028) 345 kV Bus to 4GRIMES% (334026) 138 kV Bus to 1GRIMES_1 (334163) 13.8 kV Bus CKT 1 b. 2. Drop Shunt 1 at 1GRIMES_1 (334163) 13.8 kV Bus1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0553_P1 | 3 phase fault on 7GRIMES% (334028) 345 kV Bus a. Apply Fault at the 7GRIMES% (334028) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from 7GRIMES% (334028) 345 kV Bus to 4GRIMES% (334026) 138 kV Bus to 1GRIMES_2 (334018) 13.8 kV Bus CKT 2 b. 2. Drop Shunt 1 at 1GRIMES_2 (334018) 13.8 kV Bus1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0554_P1 | 3 phase fault on 7GRIMES% (334028) 345 kV Bus a. Apply Fault at the 7GRIMES% (334028) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from 7GRIMES% (334028) 345 kV Bus to 6GRIMES! (334027) 230 kV Bus CKT 1 b. 2. Trip branch from 6GRIMES! (334027) 230 kV Bus to 6PONDEROSA! (334088) 230 kV Bus CKT 1 b. 3. Trip three winding transformer from 6PONDEROSA! (334088) 230 kV Bus to 4PONDEROSA% (334087) 138 kV Bus to 1PONDEROSA (334094) 13.8 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0555_P1 | 3 phase fault on 7ROCKYCRK% (334197) 345 kV Bus a. Apply Fault at the 7ROCKYCRK% (334197) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from 7ROCKYCRK% (334197) 345 kV Bus to 6ROCKYCRK (334198) 230 kV Bus CKT 1 b. 2. Trip branch from 6ROCKYCRK (334198) 230 kV Bus to J1671 POI (46714) 230 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0556_P1 | 3 phase fault on LEASIDE 4 (507793) 138 kV Bus a. Apply Fault at the LEASIDE 4 (507793) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from LEASIDE 4 (507793) 138 kV Bus to LEASIDE 2 (507794) 69 kV Bus to LEASIDE 1-1 (507795) 13.8 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0557_P1 | 3 phase fault on LEASIDE 4 (507793) 138 kV Bus a. Apply Fault at the LEASIDE 4 (507793) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from LEASIDE 4 (507793) 138 kV Bus to WESTELC4 (507767) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0558_P1 | 3 phase fault on LEASIDE 4 (507793) 138 kV Bus a. Apply Fault at the LEASIDE 4 (507793) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from LEASIDE 4 (507793) 138 kV Bus to STONWAL4 (509052) 138 kV Bus CKT 1 b. 2. Trip branch from STONWAL4 (509052) 138 kV Bus to KEATCHI4 (509050) 138 kV Bus CKT 1 b. 3. Trip branch from KEATCHI4 (509050) 138 kV Bus to GEORPAC4 (509064) 138 kV Bus CKT 1 b. 4. Trip branch from GEORPAC4 (509064) 138 kV Bus to LOGANSP4 (509071) 138 kV Bus CKT 1 b. 5. Drop Load 1 at STONWAL4 (509052) 138 kV Bus b. 6. Drop Load 1 at KEATCHI4 (509050) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0559_P1 | 3 phase fault on WILKES 4 (508840) 138 kV Bus a. Apply Fault at the WILKES 4 (508840) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from WILKES 4 (508840) 138 kV Bus to LSSOUTH4 (508297) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0560_P1 | 3 phase fault on WILKES 4 (508840) 138 kV Bus a. Apply Fault at the WILKES 4 (508840) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from WILKES 4 (508840) 138 kV Bus to WELSHRE4 (508355) 138 kV Bus CKT 1 b. 2. Trip branch from WELSHRE4 (508355) 138 kV Bus to CHAPELH4 (508337) 138 kV Bus CKT 1 b. 3. Drop Load 1 at WELSHRE4 (508355) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0561_P1 | 3 phase fault on LONGWD 7 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 (508809) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from LONGWD 7 (508809) 345 kV Bus to SW SHV 7 (507760) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0562_P1 | 3 phase fault on WILKES 4 (508840) 138 kV Bus a. Apply Fault at the WILKES 4 (508840) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from WILKES 4 (508840) 138 kV Bus to JEFFRSN4 (508835) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0563_P1 | 3 phase fault on WILKES 4 (508840) 138 kV Bus a. Apply Fault at the WILKES 4 (508840) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from WILKES 4 (508840) 138 kV Bus to WATLANT4 (508090) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0564_P1 | 3 phase fault on WILKES 4 (508840) 138 kV Bus a. Apply Fault at the WILKES 4 (508840) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from WILKES 4 (508840) 138 kV Bus to MUNZCTY4 (508064) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0565_P1 | 3 phase fault on SPPMAINBUS (5917) 345 kV Bus a. Apply Fault at the SPPMAINBUS (5917) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from SPPMAINBUS (5917) 345 kV Bus to SPP-CAP1 (5921) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0566_P1 | 3 phase fault on SPPMAINBUS (5917) 345 kV Bus a. Apply Fault at the SPPMAINBUS (5917) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from SPPMAINBUS (5917) 345 kV Bus to SPP-CAP2 (5922) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0567_P1 | 3 phase fault on SPPMAINBUS (5917) 345 kV Bus a. Apply Fault at the SPPMAINBUS (5917) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from SPPMAINBUS (5917) 345 kV Bus to SPP-CAP3 (5923) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0568_P1 | 3 phase fault on SPPMAINBUS (5917) 345 kV Bus a. Apply Fault at the SPPMAINBUS (5917) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from SPPMAINBUS (5917) 345 kV Bus to SPP-REAC1 (5924) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0569_P1 | 3 phase fault on SPPMAINBUS (5917) 345 kV Bus a. Apply Fault at the SPPMAINBUS (5917) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from SPPMAINBUS (5917) 345 kV Bus to WELSHDC1 (5919) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0570_P1 | 3 phase fault on LONGWD 7 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 (508809) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from LONGWD 7 (508809) 345 kV Bus to 7SAREPTA% (337376) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0571_P1 | 3 phase fault on DIANA 7 (508832) 345 kV Bus a. Apply Fault at the DIANA 7 (508832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from DIANA 7 (508832) 345 kV Bus to PIRKEY 7 (508563) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0572_P1 | 3 phase fault on LONGWD 7 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 (508809) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from LONGWD 7 (508809) 345 kV Bus to LONGWD 4 (508808) 138 kV Bus to LONGW1-1 (508819) 13.2 kV Bus CKT 1 b. 2. Drop Shunt 1 at LONGW1-1 (508819) 13.2 kV Bus1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0573_P1 | 3 phase fault on NWTXARK4 (508071) 138 kV Bus a. Apply Fault at the NWTXARK4 (508071) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from NWTXARK4 (508071) 138 kV Bus to NASH 4 (508049) 138 kV Bus CKT 1 b. 2. Trip branch from NASH 4 (508049) 138 kV Bus to ALUMAX 4 (508091) 138 kV Bus CKT 1 b. 3. Trip branch from NASH 4 (508049) 138 kV Bus to BANN 4 (508054) 138 kV Bus CKT 1 b. 4. Drop Load 1 at NASH 4 (508049) 138 kV Bus b. 5. Drop Load 1 at NASH 4 (508049) 138 kV Bus b. 6. Drop Load 1 at ALUMAX 4 (508091) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault b. 12. Trip branch from NWTXARK4 (508071) 138 kV Bus to NASH 4 (508049) 138 kV Bus CKT 1 b. 13. Trip branch from NASH 4 (508049) 138 kV Bus to ALUMAX 4 (508091) 138 kV Bus CKT 1 b. 14. Trip branch from NASH 4 (508049) 138 kV Bus to BANN 4 (508054) 138 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0574_P1 | 3 phase fault on NWTXARK4 (508071) 138 kV Bus a. Apply Fault at the NWTXARK4 (508071) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from NWTXARK4 (508071) 138 kV Bus to PATTERS4 (507431) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0575_P1 | 3 phase fault on NWTXARK4 (508071) 138 kV Bus a. Apply Fault at the NWTXARK4 (508071) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from NWTXARK4 (508071) 138 kV Bus to NWT-BNT4 (508070) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0576_P1 | 3 phase fault on NWTXARK4 (508071) 138 kV Bus a. Apply Fault at the NWTXARK4 (508071) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from NWTXARK4 (508071) 138 kV Bus to SUGARHL4 (508080) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0577_P1 | 3 phase fault on LSSOUTH4 (508297) 138 kV Bus a. Apply Fault at the LSSOUTH4 (508297) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from LSSOUTH4 (508297) 138 kV Bus to PITTSB_4 (508313) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0578_P1 | 3 phase fault on LSSOUTH4 (508297) 138 kV Bus a. Apply Fault at the LSSOUTH4 (508297) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from LSSOUTH4 (508297) 138 kV Bus to DIANA 4 (508831) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0579_P1 | 3 phase fault on LSSOUTH4 (508297) 138 kV Bus a. Apply Fault at the LSSOUTH4 (508297) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from LSSOUTH4 (508297) 138 kV Bus to LSSOUTH2 (508296) 69 kV Bus to LSS-1 (508325) 12.47 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0580_P1 | 3 phase fault on CHAPELH4 (508337) 138 kV Bus a. Apply Fault at the CHAPELH4 (508337) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from CHAPELH4 (508337) 138 kV Bus to PETTY 4 (508310) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0581_P1 | 3 phase fault on WILKES 7 (508841) 345 kV Bus a. Apply Fault at the WILKES 7 (508841) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from WILKES 7 (508841) 345 kV Bus to WELSH 7 (508359) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0582_P1 | 3 phase fault on CHAPELH4 (508337) 138 kV Bus a. Apply Fault at the CHAPELH4 (508337) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from CHAPELH4 (508337) 138 kV Bus to CHAPLHL4 (509664) 138 kV Bus CKT 1 b. 2. Trip branch from CHAPLHL4 (509664) 138 kV Bus to LIBERTH4 (509643) 138 kV Bus CKT 1 b. 3. Trip branch from LIBERTH4 (509643) 138 kV Bus to ARGO 4 (509665) 138 kV Bus CKT 1 b. 4. Drop Load 1 at CHAPLHL4 (509664) 138 kV Bus b. 5. Drop Load 1 at LIBERTH4 (509643) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0583_P1 | 3 phase fault on ARGO 4 (509665) 138 kV Bus a. Apply Fault at the ARGO 4 (509665) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from ARGO 4 (509665) 138 kV Bus to ARGO 2 (509642) 69 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0584_P1 | 3 phase fault on DIANA 4 (508831) 138 kV Bus a. Apply Fault at the DIANA 4 (508831) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from DIANA 4 (508831) 138 kV Bus to PERDUE 4 (508351) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0585_P1 | 3 phase fault on DIANA 4 (508831) 138 kV Bus a. Apply Fault at the DIANA 4 (508831) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from DIANA 4 (508831) 138 kV Bus to NGPLTAP4 (508837) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0586_P1 | 3 phase fault on DIANA 4 (508831) 138 kV Bus a. Apply Fault at the DIANA 4 (508831) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from DIANA 4 (508831) 138 kV Bus to DIANASW4 (509639) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0587_P1 | 3 phase fault on DIANA 4 (508831) 138 kV Bus a. Apply Fault at the DIANA 4 (508831) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from DIANA 4 (508831) 138 kV Bus to SPRHILL4 (508571) 138 kV Bus CKT 1 b. 2. Trip branch from SPRHILL4 (508571) 138 kV Bus to LLAMOND4 (508552) 138 kV Bus CKT 1 b. 3. Trip three winding transformer from LLAMOND4 (508552) 138 kV Bus to LLAMOND2 (508551) 69 kV Bus to LLAMON1- (508593) 13.8 kV Bus CKT 1 b. 4. Drop Load 1 at SPRHILL4 (508571) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0588_P1 | 3 phase fault on PIRKEY 7 (508563) 345 kV Bus a. Apply Fault at the PIRKEY 7 (508563) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from PIRKEY 7 (508563) 345 kV Bus to PIRKEY 4 (508562) 138 kV Bus to PIRKY1-1 (508587) 13.8 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0589_P1 | 3 phase fault on PIRKEY 7 (508563) 345 kV Bus a. Apply Fault at the PIRKEY 7 (508563) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from PIRKEY 7 (508563) 345 kV Bus to PIRKEY 4 (508562) 138 kV Bus to PIRKY2-1 (508588) 13.8 kV Bus CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0590_P1 | 3 phase fault on LEBROCK7 (508572) 345 kV Bus a. Apply Fault at the LEBROCK7 (508572) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from LEBROCK7 (508572) 345 kV Bus to PIRKEY 7 (508563) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0591_P1 | 3 phase fault on SW SHV 7 (507760) 345 kV Bus a. Apply Fault at the SW SHV 7 (507760) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from SW SHV 7 (507760) 345 kV Bus to SW SHV 4 (507759) 138 kV Bus to SWSHV1-1 (507778) 13.8 kV Bus CKT 1 b. 2. Drop Shunt 1 at SWSHV1-1 (507778) 13.8 kV Bus1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0592_P1 | 3 phase fault on SW SHV 7 (507760) 345 kV Bus a. Apply Fault at the SW SHV 7 (507760) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from SW SHV 7 (507760) 345 kV Bus to SW SHV 4 (507759) 138 kV Bus to SWSHV2-1 (507777) 13.8 kV Bus CKT 2 b. 2. Drop Shunt 1 at SWSHV2-1 (507777) 13.8 kV Bus1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0593_P1 | 3 phase fault on HUGO 7 (521157) 345 kV Bus a. Apply Fault at the HUGO 7 (521157) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from HUGO 7 (521157) 345 kV Bus to G16-063-TAP (560088) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0594_P1 | 3 phase fault on WILKES 7 (508841) 345 kV Bus a. Apply Fault at the WILKES 7 (508841) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from WILKES 7 (508841) 345 kV Bus to WILKES 4 (508840) 138 kV Bus to WILKES-1 (508826) 13.2 kV Bus CKT 1 b. 2. Drop Shunt 1 at WILKES-1 (508826) 13.2 kV Bus1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0595_P1 | 3 phase fault on TURK 4 (507454) 138 kV Bus a. Apply Fault at the TURK 4 (507454) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from TURK 4 (507454) 138 kV Bus to SUGARHL4 (508080) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0596_P1 | 3 phase fault on TURK 4 (507454) 138 kV Bus a. Apply Fault at the TURK 4 (507454) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from TURK 4 (507454) 138 kV Bus to OKAY 4 (507428) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0597_P1 | 3 phase fault on TURK 4 (507454) 138 kV Bus a. Apply Fault at the TURK 4 (507454) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from TURK 4 (507454) 138 kV Bus to MANDEVILTP4 (508105) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0598_P1 | 3 phase fault on PATTERS4 (507431) 138 kV Bus a. Apply Fault at the PATTERS4 (507431) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from PATTERS4 (507431) 138 kV Bus to ASHDWNR4 (507402) 138 kV Bus CKT 1 b. 2. Trip branch from ASHDWNR4 (507402) 138 kV Bus to OKAY 4 (507428) 138 kV Bus CKT 1 b. 3. Drop Load A1 at ASHDWNR4 (507402) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0599_P1 | 3 phase fault on PATTERS4 (507431) 138 kV Bus a. Apply Fault at the PATTERS4 (507431) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from PATTERS4 (507431) 138 kV Bus to ASHDWN_W 4 (504124) 138 kV Bus CKT 1 b. 2. Trip branch from ASHDWN_W 4 (504124) 138 kV Bus to CRAIGJT4 (510890) 138 kV Bus CKT 1 b. 3. Drop Load A1 at ASHDWN_W 4 (504124) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0600_P1 | 3 phase fault on PATTERS4 (507431) 138 kV Bus a. Apply Fault at the PATTERS4 (507431) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from PATTERS4 (507431) 138 kV Bus to PATTERS2 (507429) 69 kV Bus to PATTN1-1 (507443) 13.2 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0601_P1 | 3 phase fault on PATTERS4 (507431) 138 kV Bus a. Apply Fault at the PATTERS4 (507431) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from PATTERS4 (507431) 138 kV Bus to PATTERS2 (507429) 69 kV Bus to PATTN2-1 (507444) 12.47 kV Bus CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0602_P1 | 3 phase fault on NWT-BNT4 (508070) 138 kV Bus a. Apply Fault at the NWT-BNT4 (508070) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from NWT-BNT4 (508070) 138 kV Bus to G18-003-TAP (762431) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0603_P1 | 3 phase fault on PERDUE 4 (508351) 138 kV Bus a. Apply Fault at the PERDUE 4 (508351) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from PERDUE 4 (508351) 138 kV Bus to PERDUE 2 (508350) 69 kV Bus to PERDUE 1 (508356) 13.8 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0604_P1 | 3 phase fault on PERDUE 4 (508351) 138 kV Bus a. Apply Fault at the PERDUE 4 (508351) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from PERDUE 4 (508351) 138 kV Bus to EXXONM 4 (508369) 138 kV Bus CKT 1 b. 2. Trip branch from EXXONM 4 (508369) 138 kV Bus to LHAWKIN4 (508358) 138 kV Bus CKT 1 b. 3. Drop Load 1 at EXXONM 4 (508369) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0605_P1 | 3 phase fault on PERDUE 4 (508351) 138 kV Bus a. Apply Fault at the PERDUE 4 (508351) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from PERDUE 4 (508351) 138 kV Bus to BIGSAND4 (509603) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0606_P1 | 3 phase fault on PERDUE 4 (508351) 138 kV Bus a. Apply Fault at the PERDUE 4 (508351) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from PERDUE 4 (508351) 138 kV Bus to NEWGLAD4 (508560) 138 kV Bus CKT 1 b. 2. Trip branch from NEWGLAD4 (508560) 138 kV Bus to LIBCYTP4 (508550) 138 kV Bus CKT 1 b. 3. Drop Load 1 at NEWGLAD4 (508560) 138 kV Bus b. 4. Drop Shunt 1 at NEWGLAD4 (508560) 138 kV Bus1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0607_P1 | 3 phase fault on NGPLTAP4 (508837) 138 kV Bus a. Apply Fault at the NGPLTAP4 (508837) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from NGPLTAP4 (508837) 138 kV Bus to NGPL 4 (508827) 138 kV Bus CKT 1 b. 2. Drop Load 1 at NGPL 4 (508827) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0608_P1 | 3 phase fault on NGPLTAP4 (508837) 138 kV Bus a. Apply Fault at the NGPLTAP4 (508837) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from NGPLTAP4 (508837) 138 kV Bus to PLILER 4 (508564) 138 kV Bus CKT 1 b. 2. Trip branch from PLILER 4 (508564) 138 kV Bus to LONGVHT4 (508554) 138 kV Bus CKT 1 b. 3. Trip branch from LONGVHT4 (508554) 138 kV Bus to WHITNEY4 (508575) 138 kV Bus CKT 1 b. 4. Drop Load 1 at PLILER 4 (508564) 138 kV Bus b. 5. Drop Load 1 at LONGVHT4 (508554) 138 kV Bus b. 6. Drop Shunt 1 at LONGVHT4 (508554) 138 kV Bus1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0609_P1 | 3 phase fault on PIRKEY 4 (508562) 138 kV Bus a. Apply Fault at the PIRKEY 4 (508562) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from PIRKEY 4 (508562) 138 kV Bus to MARSHL-4 (508557) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0610_P1 | 3 phase fault on PIRKEY 4 (508562) 138 kV Bus a. Apply Fault at the PIRKEY 4 (508562) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from PIRKEY 4 (508562) 138 kV Bus to SABMINT4 (508566) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0611_P1 | 3 phase fault on PIRKEY 4 (508562) 138 kV Bus a. Apply Fault at the PIRKEY 4 (508562) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from PIRKEY 4 (508562) 138 kV Bus to HALLSVLS4 (508595) 138 kV Bus CKT 1 b. 2. Trip branch from HALLSVLS4 (508595) 138 kV Bus to WHITNEY4 (508575) 138 kV Bus CKT 1 b. 3. Drop Load 1 at HALLSVLS4 (508595) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0612_P1 | 3 phase fault on PIRKEY 4 (508562) 138 kV Bus a. Apply Fault at the PIRKEY 4 (508562) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from PIRKEY 4 (508562) 138 kV Bus to EASTON 4 (509092) 138 kV Bus CKT 1 b. 2. Trip branch from EASTON 4 (509092) 138 kV Bus to BRANDYBR (508596) 138 kV Bus CKT 1 b. 3. Trip branch from BRANDYBR (508596) 138 kV Bus to KNOXLEE4 (508548) 138 kV Bus CKT 1 b. 4. Drop Load 1 at EASTON 4 (509092) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0613_P1 | 3 phase fault on MARSHL-4 (508557) 138 kV Bus a. Apply Fault at the MARSHL-4 (508557) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from MARSHL-4 (508557) 138 kV Bus to MARAUTO2 (508576) 69 kV Bus to MRSH4#11 (508591) 12.47 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0614_P1 | 3 phase fault on MARSHL-4 (508557) 138 kV Bus a. Apply Fault at the MARSHL-4 (508557) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from MARSHL-4 (508557) 138 kV Bus to MARAUTO2 (508576) 69 kV Bus to MRSH4#21 (508592) 12.47 kV Bus CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0615_P1 | 3 phase fault on MARSHL-4 (508557) 138 kV Bus a. Apply Fault at the MARSHL-4 (508557) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from MARSHL-4 (508557) 138 kV Bus to JEFFRSN4 (508835) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0616_P1 | 3 phase fault on KNOXLEE4 (508548) 138 kV Bus a. Apply Fault at the KNOXLEE4 (508548) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from KNOXLEE4 (508548) 138 kV Bus to CHEROKE4 (509059) 138 kV Bus CKT 1 b. 2. Trip branch from CHEROKE4 (509059) 138 kV Bus to TATUM 4 (509087) 138 kV Bus CKT 1 b. 3. Trip branch from TATUM 4 (509087) 138 kV Bus to ROKHILL4 (509083) 138 kV Bus CKT 1 b. 4. Drop Load 1 at CHEROKE4 (509059) 138 kV Bus b. 5. Drop Load 1 at TATUM 4 (509087) 138 kV Bus b. 6. Drop Load 2 at TATUM 4 (509087) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0617_P1 | 3 phase fault on KNOXLEE4 (508548) 138 kV Bus a. Apply Fault at the KNOXLEE4 (508548) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from KNOXLEE4 (508548) 138 kV Bus to OAK2HIL4 (509078) 138 kV Bus CKT 1 b. 2. Trip branch from OAK2HIL4 (509078) 138 kV Bus to OAK1HIL4 (509077) 138 kV Bus CKT 1 b. 3. Trip branch from OAK1HIL4 (509077) 138 kV Bus to NWHENDR4 (509076) 138 kV Bus CKT 1 b. 4. Drop Load 1 at OAK2HIL4 (509078) 138 kV Bus b. 5. Drop Load 1 at OAK1HIL4 (509077) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0618_P1 | 3 phase fault on SABMINT4 (508566) 138 kV Bus a. Apply Fault at the SABMINT4 (508566) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from SABMINT4 (508566) 138 kV Bus to SABINEM4 (508577) 138 kV Bus CKT 1 b. 2. Drop Load 1 at SABINEM4 (508577) 138 kV Bus b. 3. Drop Load 2 at SABINEM4 (508577) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0619_P1 | 3 phase fault on SABMINT4 (508566) 138 kV Bus a. Apply Fault at the SABMINT4 (508566) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from SABMINT4 (508566) 138 kV Bus to SEMRSHL4 (508569) 138 kV Bus CKT 1 b. 2. Trip branch from SEMRSHL4 (508569) 138 kV Bus to SCOTTSV4 (508567) 138 kV Bus CKT 1 b. 3. Trip branch from SCOTTSV4 (508567) 138 kV Bus to LONGWD 4 (508808) 138 kV Bus CKT 1 b. 4. Drop Load 1 at SEMRSHL4 (508569) 138 kV Bus b. 5. Drop Load 1 at SCOTTSV4 (508567) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0620_P4 | a. Apply single phase fault at 3SAREPTA! (337363) 115 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from 3SAREPTA! (337363) 115 kV to 7SAREPTA% (337376) 345 kV CKT 1 b. 2. Trip branch from 3SAREPTA! (337363) 115 kV to 3MINDEN_LA! (337361) 115 kV CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0621_P4 | a. Apply single phase fault at 3STERLING% (337415) 115 kV b. Clear Fault after 16 cycles: b. 1. Trip three winding transformer from 3STERLING% (337415) 115 kV to 8STERLING% (337420) kV to 1STERLING3 (337412) 13.8 kV CKT3 b. 2. Trip branch from 3STERLING% (337415) 115 kV to 8STERLING2% (337413) 500 kV CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0622_P4 | a. Apply single phase fault at 3STERL2% (337414) 115 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from 3STERL2% (337414) 115 kV to 3DREW_LA (337382) 115 kV CKT 1 b. 2. Trip branch from 3DREW_LA (337382) 115 kV to 3CHENIERE (337383) 115 kV CKT 1 b. 3. Trip branch from 3CHENIERE (337383) 115 kV to 3RISER (337384) 115 kV CKT 1 b. 4. Trip branch from 3RISER (337384) 115 kV to 3FROSTKRAFT! (337385) 115 kV CKT 1 b. 5. Trip branch from 3STERL2% (337414) 115 kV to 8STERLING2% (337413) 500 kV CKT 2 b. 6. Drop Load 1 3DREW_LA (337382) 115 kV b. 7. Drop Load 1 3CHENIERE (337383) 115 kV b. 8. Drop Load 1 3RISER (337384) 115 kV b. 9. Drop Shunt 1 3SHULER (337521) 115 kV b. 10. Drop Shunt 1 3RISER (337384) 115 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0623_P4 | a. Apply single phase fault at 8EL DORADO% (337561) 500 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from 8EL DORADO% (337561) 500 kV to 8MT_OLIVE% (337368) 500 kV CKT 1 b. 2. Trip branch from 8EL DORADO% (337561) 500 kV to 8STERLING% (337420) 500 kV CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0624_P4 | a. Apply single phase fault at LIEBERM4 (508806) 138 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from LIEBERM4 (508806) 138 kV to LONGWD 4 (508808) 138 kV CKT 1 b. 2. Trip branch from LIEBERM4 (508806) 138 kV to G16-167-TAP (588404) 138 kV CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0625_P4 | a. Apply single phase fault at 3MINDEN_LA! (337361) 115 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from 3MINDEN_LA! (337361) 115 kV to 3SAREPTA! (337363) 115 kV CKT 1 b. 2. Trip branch from 3MINDEN_LA! (337361) 115 kV to 3MINDEN_LG (303302) 115 kV CKT 1 b. 3. Trip branch from 3MINDEN_LG (303302) 115 kV to 3ARCADIA (337367) 115 kV CKT 1 b. 4. Trip branch from 3ARCADIA (337367) 115 kV to 3REESE (337380) 115 kV CKT 1 b. 5. Trip branch from 3REESE (337380) 115 kV to 3TRUSSEL_CR (303310) 115 kV CKT 1 b. 6. Trip branch from 3TRUSSEL_CR (303310) 115 kV to 3VIENNA_LA! (337371) 115 kV CKT 1 b. 7. Drop Load 1 3MINDEN_LG (303302) 115 kV b. 8. Drop Load 1 3ARCADIA (337367) 115 kV b. 9. Drop Load LG 3ARCADIA (337367) 115 kV b. 10. Drop Load IN 3REESE (337380) 115 kV b. 11. Drop Load 1 3TRUSSEL_CR (303310) 115 kV b. 12. Drop Shunt 1 3MINDEN_LG (303302) 115 kV b. 13. Drop Load 1 3ARCADIA (337367) 115 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0626_P4 | a. Apply single phase fault at 3EL DORADO! (337539) 115 kV b. Clear Fault after 16 cycles: b. 1. Trip three winding transformer from 3EL DORADO! (337539) 115 kV to 8EL DORADO% (337561) kV to 1EL DORADO1 (337564) 13.8 kV CKT1 b. 2. Trip branch from 3EL DORADO! (337539) 115 kV to 3ELDORADO.E! (337553) 115 kV CKT 1 b. 3. Drop Shunt 1 1EL DORADO1 (337564) 13.8 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0627_P4 | a. Apply single phase fault at ARSHILL4 (507711) 138 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from ARSHILL4 (507711) 138 kV to FTHUMBG4 (507731) 138 kV CKT 1 b. 2. Trip three winding transformer from ARSHILL4 (507711) 138 kV to ARSHILL2 (507710) kV to ARSH1-1 (507712) 12.47 kV CKT1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0628_P4 | a. Apply single phase fault at 3MCNEIL! (337516) 115 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from 3MCNEIL! (337516) 115 kV to 8MCNEIL% (337515) 500 kV CKT 1 b. 2. Trip branch from 3MCNEIL! (337516) 115 kV to 3MAGNOLIA.W (337519) 115 kV CKT 1 b. 3. Trip branch from 3MAGNOLIA.W (337519) 115 kV to 3MAGNOLIA.S (337520) 115 kV CKT 1 b. 4. Trip branch from 3MAGNOLIA.S (337520) 115 kV to 3SHULER (337521) 115 kV CKT 1 b. 5. Trip branch from 3SHULER (337521) 115 kV to 3WYATT! (337544) 115 kV CKT 1 b. 6. Drop Load IN 3MAGNOLIA.W (337519) 115 kV b. 7. Drop Load 1 3MAGNOLIA.S (337520) 115 kV b. 8. Drop Load IN 3SHULER (337521) 115 kV b. 9. Drop Load 1 3SHULER (337521) 115 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0629_P4 | a. Apply single phase fault at 8STERLING2% (337413) 500 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from 8STERLING2% (337413) 500 kV to 8PERRYVILLE% (337427) 500 kV CKT 1 b. 2. Trip branch from 8STERLING2% (337413) 500 kV to 8STERLING% (337420) 500 kV CKT Z1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0630_P4 | a. Apply single phase fault at 8PERRYVILLE% (337427) 500 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from 8PERRYVILLE% (337427) 500 kV to 8BXTRWILSON% (336830) 500 kV CKT 1 b. 2. Trip branch from 8PERRYVILLE% (337427) 500 kV to 8STERLING% (337420) 500 kV CKT 2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0631_P1 | 3 phase fault on L.E.S.-7 (511468) 345 kV Bus a. Apply Fault at the L.E.S.-7 (511468) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from L.E.S.-7 (511468) 345 kV Bus to G16-091-TAP (587744) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 584862 [G15-045-GEN10.4800], 762903 [G18-055-GEN10.6600]
04 - Southeast | 25W | Transfer | Group4_Fault_0632_P1 | 3 phase fault on GRACMNT7 (515800) 345 kV Bus a. Apply Fault at the GRACMNT7 (515800) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from GRACMNT7 (515800) 345 kV Bus to GRACMNT4 (515802) 138 kV Bus to GRCMNT11 (515801) 13.8 kV Bus CKT 2 b. 2. Drop Shunt 1 at GRCMNT11 (515801) 13.8 kV Bus1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Low voltage ride through fails due to the tripping of G18-115-GEN10 and G18-115-GEN20 units. No cascading was observed and the issue was localised. Model tuning is recommended. |  |  | Generator relays were disabled for the following generators: 587793 [G16-097-GEN10.6900], 761232 [G17-150GEN1 0.6600], 762903 [G18-055-GEN10.6600], 920001 [BLUCAN2-WTG10.6900], 920002 [BLUCAN2-WTG20.6900], 920003 [BLUCAN2-WTG30.6900], 920004 [BLUCAN2-WTG40.6900]
04 - Southeast | 25W | Transfer | Group4_Fault_0633_P1 | 3 phase fault on MINCO 7 (514801) 345 kV Bus a. Apply Fault at the MINCO 7 (514801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from MINCO 7 (514801) 345 kV Bus to CIMARON7 (514901) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Low voltage ride through fails due to the tripping of G18-115-GEN10 and G18-115-GEN20 units. No cascading was observed and the issue was localised. Model tuning is recommended. |  |  | Generator relays were disabled for the following generators: 515439 [MNCOWNG3 0.6900], 515445 [MNCOWNG2 0.6900], 515551 [MINCO-WTG32 0.6900], 515907 [MNCOWNG1 0.6900], 599117 [MINCO-WTG31 0.6900], 599119 [MINCO-WTG33 0.6900], 599120 [MINCO-WTG34 0.6900], 761232 [G17-150GEN1 0.6600]
04 - Southeast | 25W | Transfer | Group4_Fault_0634_P1 | 3 phase fault on MINCO 7 (514801) 345 kV Bus a. Apply Fault at the MINCO 7 (514801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from MINCO 7 (514801) 345 kV Bus to NSUB345 (555234) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Low voltage ride through fails due to the tripping of G18-115-GEN10 and G18-115-GEN20 units. No cascading was observed and the issue was localised. Model tuning is recommended. |  |  | Generator relays were disabled for the following generators: 515439 [MNCOWNG3 0.6900], 515445 [MNCOWNG2 0.6900], 515551 [MINCO-WTG32 0.6900], 515907 [MNCOWNG1 0.6900], 599117 [MINCO-WTG31 0.6900], 599119 [MINCO-WTG33 0.6900], 599120 [MINCO-WTG34 0.6900], 761232 [G17-150GEN1 0.6600]
04 - Southeast | 25W | Transfer | Group4_Fault_0635_P1 | 3 phase fault on G16-037-TAP (560078) 345 kV Bus a. Apply Fault at the G16-037-TAP (560078) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from G16-037-TAP (560078) 345 kV Bus to CHISHOLM7 (511553) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0636_P1 | 3 phase fault on GRACMNT4 (515802) 138 kV Bus a. Apply Fault at the GRACMNT4 (515802) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from GRACMNT4 (515802) 138 kV Bus to WASHITA4 (521089) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Low voltage ride through fails due to the tripping of G18-115-GEN10 and G18-115-GEN20 units. No cascading was observed and the issue was localised. Model tuning is recommended. |  |  | Generator relays were disabled for the following generators: 520522 [BCVI_WTG1 0.6900], 920001 [BLUCAN2-WTG10.6900], 920002 [BLUCAN2-WTG20.6900], 920003 [BLUCAN2-WTG30.6900], 920004 [BLUCAN2-WTG40.6900]
04 - Southeast | 25W | Transfer | Group4_Fault_0637_P1 | 3 phase fault on GRACMNT4 (515802) 138 kV Bus a. Apply Fault at the GRACMNT4 (515802) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from GRACMNT4 (515802) 138 kV Bus to ANADARK4 (520814) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Low voltage ride through fails due to the tripping of G18-115-GEN10 and G18-115-GEN20 units. No cascading was observed and the issue was localised. Model tuning is recommended. |  |  | Generator relays were disabled for the following generators: 520522 [BCVI_WTG1 0.6900], 920001 [BLUCAN2-WTG10.6900], 920002 [BLUCAN2-WTG20.6900], 920003 [BLUCAN2-WTG30.6900], 920004 [BLUCAN2-WTG40.6900]
04 - Southeast | 25W | Transfer | Group4_Fault_0638_P1 | 3 phase fault on O.K.U.-7 (511456) 345 kV Bus a. Apply Fault at the O.K.U.-7 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from O.K.U.-7 (511456) 345 kV Bus to OKLAUN HVDC7 (511565) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Low voltage ride through fails due to the tripping of G18-115-GEN10 and G18-115-GEN20 units. No cascading was observed and the issue was localised. Model tuning is recommended.
04 - Southeast | 25W | Transfer | Group4_Fault_0639_P1 | 3 phase fault on O.K.U.-7 (511456) 345 kV Bus a. Apply Fault at the O.K.U.-7 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from O.K.U.-7 (511456) 345 kV Bus to G18-092-TAP (763215) 345 kV Bus CKT 1 b. 2. Drop Shunt 1 at OKLAUN HVDC7 (511565) 345 kV Bus1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Low voltage ride through fails due to the tripping of G18-115-GEN10 and G18-115-GEN20 units. No cascading was observed and the issue was localised. Model tuning is recommended.
04 - Southeast | 25W | Transfer | Group4_Fault_0640_P1 | 3 phase fault on L.E.S.-7 (511468) 345 kV Bus a. Apply Fault at the L.E.S.-7 (511468) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from L.E.S.-7 (511468) 345 kV Bus to O.K.U.-7 (511456) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 584862 [G15-045-GEN10.4800], 762903 [G18-055-GEN10.6600]
04 - Southeast | 25W | Transfer | Group4_Fault_0641_P1 | 3 phase fault on G17-171-TAP (760938) 345 kV Bus a. Apply Fault at the G17-171-TAP (760938) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from G17-171-TAP (760938) 345 kV Bus to TERRYRD7 (511568) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 584862 [G15-045-GEN10.4800], 762903 [G18-055-GEN10.6600]
04 - Southeast | 25W | Transfer | Group4_Fault_0642_P1 | 3 phase fault on G18-092-TAP (763215) 345 kV Bus a. Apply Fault at the G18-092-TAP (763215) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from G18-092-TAP (763215) 345 kV Bus to G18-015-TAP (762467) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0643_P1 | 3 phase fault on G18-015-TAP (762467) 345 kV Bus a. Apply Fault at the G18-015-TAP (762467) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from G18-015-TAP (762467) 345 kV Bus to G17-151TAP (762216) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0644_P1 | 3 phase fault on L.E.S.-7 (511468) 345 kV Bus a. Apply Fault at the L.E.S.-7 (511468) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from L.E.S.-7 (511468) 345 kV Bus to G17-171-TAP (760938) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 584862 [G15-045-GEN10.4800], 762903 [G18-055-GEN10.6600]
04 - Southeast | 25W | Transfer | Group4_Fault_0645_P1 | 3 phase fault on G18-015-TAP (762467) 345 kV Bus a. Apply Fault at the G18-015-TAP (762467) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from G18-015-TAP (762467) 345 kV Bus to G17-151TAP (762216) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0646_P1 | 3 phase fault on NSUB345 (555234) 345 kV Bus a. Apply Fault at the NSUB345 (555234) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from NSUB345 (555234) 345 kV Bus to CIMARON7 (514901) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Low voltage ride through fails due to the tripping of G18-115-GEN10 and G18-115-GEN20 units. No cascading was observed and the issue was localised. Model tuning is recommended. |  |  | Generator relays were disabled for the following generators: 761232 [G17-150GEN1 0.6600]
04 - Southeast | 25W | Transfer | Group4_Fault_0647_P1 | 3 phase fault on NSUB345 (555234) 345 kV Bus a. Apply Fault at the NSUB345 (555234) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from NSUB345 (555234) 345 kV Bus to PLVALLY4 (514929) 138 kV Bus to NEWBUS13.8 (750000) 13.8 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Low voltage ride through fails due to the tripping of G18-115-GEN10 and G18-115-GEN20 units. No cascading was observed and the issue was localised. Model tuning is recommended. |  |  | Generator relays were disabled for the following generators: 761232 [G17-150GEN1 0.6600]
04 - Southeast | 25W | Transfer | Group4_Fault_0648_P1 | 3 phase fault on NSUB345 (555234) 345 kV Bus a. Apply Fault at the NSUB345 (555234) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from NSUB345 (555234) 345 kV Bus to PLVALLY4 (514929) 138 kV Bus to NEWBUS13.8 (750001) 13.8 kV Bus CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Low voltage ride through fails due to the tripping of G18-115-GEN10 and G18-115-GEN20 units. No cascading was observed and the issue was localised. Model tuning is recommended. |  |  | Generator relays were disabled for the following generators: 761232 [G17-150GEN1 0.6600]
04 - Southeast | 25W | Transfer | Group4_Fault_0649_P1 | 3 phase fault on CHISHOLM7 (511553) 345 kV Bus a. Apply Fault at the CHISHOLM7 (511553) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from CHISHOLM7 (511553) 345 kV Bus to CHISHOLM6 (511557) 230 kV Bus to CHISHOLM1 (511558) 13.2 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0650_P1 | 3 phase fault on L.E.S.-7 (511468) 345 kV Bus a. Apply Fault at the L.E.S.-7 (511468) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from L.E.S.-7 (511468) 345 kV Bus to L.E.S.-4 (511467) 138 kV Bus to LES#4-1 (511414) 13.8 kV Bus CKT 1 b. 2. Drop Shunt 1 at LES#4-1 (511414) 13.8 kV Bus1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 584862 [G15-045-GEN10.4800], 762903 [G18-055-GEN10.6600]
04 - Southeast | 25W | Transfer | Group4_Fault_0651_P1 | 3 phase fault on CIMARON7 (514901) 345 kV Bus a. Apply Fault at the CIMARON7 (514901) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from CIMARON7 (514901) 345 kV Bus to MATHWSN7 (515497) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Low voltage ride through fails due to the tripping of G18-115-GEN10 and G18-115-GEN20 units. No cascading was observed and the issue was localised. Model tuning is recommended. |  |  | Generator relays were disabled for the following generators: 587953 [G16-119-GEN10.6900], 587958 [G16-119-GEN20.6900], 761232 [G17-150GEN1 0.6600], 763841 [G19-052-GEN20.6000], 763959 [G19-067-GEN10.7200]
04 - Southeast | 25W | Transfer | Group4_Fault_0652_P1 | 3 phase fault on CIMARON7 (514901) 345 kV Bus a. Apply Fault at the CIMARON7 (514901) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from CIMARON7 (514901) 345 kV Bus to MATHWSN7 (515497) 345 kV Bus CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Low voltage ride through fails due to the tripping of G18-115-GEN10 and G18-115-GEN20 units. No cascading was observed and the issue was localised. Model tuning is recommended. |  |  | Generator relays were disabled for the following generators: 587953 [G16-119-GEN10.6900], 587958 [G16-119-GEN20.6900], 761232 [G17-150GEN1 0.6600], 763841 [G19-052-GEN20.6000], 763959 [G19-067-GEN10.7200]
04 - Southeast | 25W | Transfer | Group4_Fault_0653_P1 | 3 phase fault on CIMARON7 (514901) 345 kV Bus a. Apply Fault at the CIMARON7 (514901) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from CIMARON7 (514901) 345 kV Bus to CIMARON4 (514898) 138 kV Bus to CIMARO11 (515714) 13.8 kV Bus CKT 1 b. 2. Drop Shunt 1 at CIMARO11 (515714) 13.8 kV Bus1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Low voltage ride through fails due to the tripping of G18-115-GEN10 and G18-115-GEN20 units. No cascading was observed and the issue was localised. Model tuning is recommended. |  |  | Generator relays were disabled for the following generators: 587953 [G16-119-GEN10.6900], 587958 [G16-119-GEN20.6900], 761232 [G17-150GEN1 0.6600], 763841 [G19-052-GEN20.6000], 763959 [G19-067-GEN10.7200]
04 - Southeast | 25W | Transfer | Group4_Fault_0654_P1 | 3 phase fault on CIMARON7 (514901) 345 kV Bus a. Apply Fault at the CIMARON7 (514901) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from CIMARON7 (514901) 345 kV Bus to CIMARON4 (514898) 138 kV Bus to CIMARO21 (515715) 13.8 kV Bus CKT 1 b. 2. Drop Shunt 1 at CIMARO21 (515715) 13.8 kV Bus1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Low voltage ride through fails due to the tripping of G18-115-GEN10 and G18-115-GEN20 units. No cascading was observed and the issue was localised. Model tuning is recommended. |  |  | Generator relays were disabled for the following generators: 587953 [G16-119-GEN10.6900], 587958 [G16-119-GEN20.6900], 761232 [G17-150GEN1 0.6600], 763841 [G19-052-GEN20.6000], 763959 [G19-067-GEN10.7200]
04 - Southeast | 25W | Transfer | Group4_Fault_0655_P1 | 3 phase fault on L.E.S.-7 (511468) 345 kV Bus a. Apply Fault at the L.E.S.-7 (511468) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from L.E.S.-7 (511468) 345 kV Bus to L.E.S.-4 (511467) 138 kV Bus to LES#5-1 (511411) 13.8 kV Bus CKT 2 b. 2. Drop Shunt 1 at LES#4-1 (511414) 13.8 kV Bus1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 584862 [G15-045-GEN10.4800], 762903 [G18-055-GEN10.6600]
04 - Southeast | 25W | Transfer | Group4_Fault_0656_P1 | 3 phase fault on FLE TAP4 (511423) 138 kV Bus a. Apply Fault at the FLE TAP4 (511423) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from FLE TAP4 (511423) 138 kV Bus to FLETCHR4 (511422) 138 kV Bus CKT 1 b. 2. Drop Load 1 at FLETCHR4 (511422) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Low voltage ride through fails due to the tripping of G18-115-GEN10 and G18-115-GEN20 units. No cascading was observed and the issue was localised. Model tuning is recommended.
04 - Southeast | 25W | Transfer | Group4_Fault_0657_P1 | 3 phase fault on L.E.S.-4 (511467) 138 kV Bus a. Apply Fault at the L.E.S.-4 (511467) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from L.E.S.-4 (511467) 138 kV Bus to COMANC-4 (511437) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Low voltage ride through fails due to the tripping of G18-115-GEN10 and G18-115-GEN20 units. No cascading was observed and the issue was localised. Model tuning is recommended. |  |  | Generator relays were disabled for the following generators: 762903 [G18-055-GEN10.6600]
04 - Southeast | 25W | Transfer | Group4_Fault_0658_P1 | 3 phase fault on FLE TAP4 (511423) 138 kV Bus a. Apply Fault at the FLE TAP4 (511423) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from FLE TAP4 (511423) 138 kV Bus to L.E.S.-4 (511467) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Low voltage ride through fails due to the tripping of G18-115-GEN10 and G18-115-GEN20 units. No cascading was observed and the issue was localised. Model tuning is recommended.
04 - Southeast | 25W | Transfer | Group4_Fault_0659_P1 | 3 phase fault on L.E.S.-4 (511467) 138 kV Bus a. Apply Fault at the L.E.S.-4 (511467) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from L.E.S.-4 (511467) 138 kV Bus to ELGINJT4 (511486) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Low voltage ride through fails due to the tripping of G18-115-GEN10 and G18-115-GEN20 units. No cascading was observed and the issue was localised. Model tuning is recommended. |  |  | Generator relays were disabled for the following generators: 762903 [G18-055-GEN10.6600]
04 - Southeast | 25W | Transfer | Group4_Fault_0660_P1 | 3 phase fault on L.E.S.-4 (511467) 138 kV Bus a. Apply Fault at the L.E.S.-4 (511467) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from L.E.S.-4 (511467) 138 kV Bus to LWSTAP 4 (511439) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Low voltage ride through fails due to the tripping of G18-115-GEN10 and G18-115-GEN20 units. No cascading was observed and the issue was localised. Model tuning is recommended. |  |  | Generator relays were disabled for the following generators: 762903 [G18-055-GEN10.6600]
04 - Southeast | 25W | Transfer | Group4_Fault_0661_P1 | 3 phase fault on L.E.S.-4 (511467) 138 kV Bus a. Apply Fault at the L.E.S.-4 (511467) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from L.E.S.-4 (511467) 138 kV Bus to SHERID4 (511474) 138 kV Bus CKT 1 b. 2. Trip branch from SHERID4 (511474) 138 kV Bus to ARTVLTP4 (511537) 138 kV Bus CKT 1 b. 3. Drop Load 1 at SHERID4 (511474) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Low voltage ride through fails due to the tripping of G18-115-GEN10 and G18-115-GEN20 units. No cascading was observed and the issue was localised. Model tuning is recommended. |  |  | Generator relays were disabled for the following generators: 584862 [G15-045-GEN10.4800], 762903 [G18-055-GEN10.6600]
04 - Southeast | 25W | Transfer | Group4_Fault_0662_P1 | 3 phase fault on L.E.S.-4 (511467) 138 kV Bus a. Apply Fault at the L.E.S.-4 (511467) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from L.E.S.-4 (511467) 138 kV Bus to COMMTAP4 (511494) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Low voltage ride through fails due to the tripping of G18-115-GEN10 and G18-115-GEN20 units. No cascading was observed and the issue was localised. Model tuning is recommended. |  |  | Generator relays were disabled for the following generators: 762903 [G18-055-GEN10.6600]
04 - Southeast | 25W | Transfer | Group4_Fault_0663_P1 | 3 phase fault on L.E.S.-4 (511467) 138 kV Bus a. Apply Fault at the L.E.S.-4 (511467) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from L.E.S.-4 (511467) 138 kV Bus to L.E.S.-2 (511466) 69 kV Bus to LES#1-1 (511416) 13.8 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Low voltage ride through fails due to the tripping of G18-115-GEN10 and G18-115-GEN20 units. No cascading was observed and the issue was localised. Model tuning is recommended. |  |  | Generator relays were disabled for the following generators: 762903 [G18-055-GEN10.6600]
04 - Southeast | 25W | Transfer | Group4_Fault_0664_P1 | 3 phase fault on L.E.S.-4 (511467) 138 kV Bus a. Apply Fault at the L.E.S.-4 (511467) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from L.E.S.-4 (511467) 138 kV Bus to L.E.S.-2 (511466) 69 kV Bus to LES#2-1 (511415) 13.8 kV Bus CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Low voltage ride through fails due to the tripping of G18-115-GEN10 and G18-115-GEN20 units. No cascading was observed and the issue was localised. Model tuning is recommended. |  |  | Generator relays were disabled for the following generators: 762903 [G18-055-GEN10.6600]
04 - Southeast | 25W | Transfer | Group4_Fault_0665_P1 | 3 phase fault on GRACMNT4 (515802) 138 kV Bus a. Apply Fault at the GRACMNT4 (515802) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from GRACMNT4 (515802) 138 kV Bus to WASHITA4 (521089) 138 kV Bus CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Low voltage ride through fails due to the tripping of G18-115-GEN10 and G18-115-GEN20 units. No cascading was observed and the issue was localised. Model tuning is recommended. |  |  | Generator relays were disabled for the following generators: 520522 [BCVI_WTG1 0.6900], 920001 [BLUCAN2-WTG10.6900], 920002 [BLUCAN2-WTG20.6900], 920003 [BLUCAN2-WTG30.6900], 920004 [BLUCAN2-WTG40.6900]
04 - Southeast | 25W | Transfer | Group4_Fault_0666_P1 | 3 phase fault on G16-091-TAP (587744) 345 kV Bus a. Apply Fault at the G16-091-TAP (587744) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from G16-091-TAP (587744) 345 kV Bus to GRACMNT7 (515800) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 584862 [G15-045-GEN10.4800], 587773 [G16-095-GEN10.6900], 762903 [G18-055-GEN10.6600]
04 - Southeast | 25W | Transfer | Group4_Fault_0667_P1 | 3 phase fault on GRACMNT4 (515802) 138 kV Bus a. Apply Fault at the GRACMNT4 (515802) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from GRACMNT4 (515802) 138 kV Bus to ANADARK4 (520814) 138 kV Bus CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Low voltage ride through fails due to the tripping of G18-115-GEN10 and G18-115-GEN20 units. No cascading was observed and the issue was localised. Model tuning is recommended. |  |  | Generator relays were disabled for the following generators: 520522 [BCVI_WTG1 0.6900], 920001 [BLUCAN2-WTG10.6900], 920002 [BLUCAN2-WTG20.6900], 920003 [BLUCAN2-WTG30.6900], 920004 [BLUCAN2-WTG40.6900]
04 - Southeast | 25W | Transfer | Group4_Fault_0668_P1 | 3 phase fault on COMMTAP4 (511494) 138 kV Bus a. Apply Fault at the COMMTAP4 (511494) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from COMMTAP4 (511494) 138 kV Bus to COMANC-4 (511437) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Low voltage ride through fails due to the tripping of G18-115-GEN10 and G18-115-GEN20 units. No cascading was observed and the issue was localised. Model tuning is recommended.
04 - Southeast | 25W | Transfer | Group4_Fault_0669_P1 | 3 phase fault on COMMTAP4 (511494) 138 kV Bus a. Apply Fault at the COMMTAP4 (511494) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from COMMTAP4 (511494) 138 kV Bus to OMDUNCN4 (529304) 138 kV Bus CKT 1 b. 2. Trip branch from OMDUNCN4 (529304) 138 kV Bus to DUNCAN-4 (511453) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Low voltage ride through fails due to the tripping of G18-115-GEN10 and G18-115-GEN20 units. No cascading was observed and the issue was localised. Model tuning is recommended.
04 - Southeast | 25W | Transfer | Group4_Fault_0670_P1 | 3 phase fault on FLE TAP4 (511423) 138 kV Bus a. Apply Fault at the FLE TAP4 (511423) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from FLE TAP4 (511423) 138 kV Bus to G16-097-TAP (587794) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Low voltage ride through fails due to the tripping of G18-115-GEN10 and G18-115-GEN20 units. No cascading was observed and the issue was localised. Model tuning is recommended. |  |  | Generator relays were disabled for the following generators: 587793 [G16-097-GEN10.6900]
04 - Southeast | 25W | Transfer | Group4_Fault_0671_P1 | 3 phase fault on COMANC-4 (511437) 138 kV Bus a. Apply Fault at the COMANC-4 (511437) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from COMANC-4 (511437) 138 kV Bus to 112GORE4 (511488) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Low voltage ride through fails due to the tripping of G18-115-GEN10 and G18-115-GEN20 units. No cascading was observed and the issue was localised. Model tuning is recommended.
04 - Southeast | 25W | Transfer | Group4_Fault_0672_P1 | 3 phase fault on LWSTAP 4 (511439) 138 kV Bus a. Apply Fault at the LWSTAP 4 (511439) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from LWSTAP 4 (511439) 138 kV Bus to LWS S4 (511431) 138 kV Bus CKT 1 b. 2. Drop Load 1 at LWS S4 (511431) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Low voltage ride through fails due to the tripping of G18-115-GEN10 and G18-115-GEN20 units. No cascading was observed and the issue was localised. Model tuning is recommended.
04 - Southeast | 25W | Transfer | Group4_Fault_0673_P1 | 3 phase fault on LWSTAP 4 (511439) 138 kV Bus a. Apply Fault at the LWSTAP 4 (511439) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from LWSTAP 4 (511439) 138 kV Bus to RPPAPER4 (511512) 138 kV Bus CKT 1 b. 2. Trip branch from RPPAPER4 (511512) 138 kV Bus to 112GORE4 (511488) 138 kV Bus CKT 1 b. 3. Drop Load 1 at RPPAPER4 (511512) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Low voltage ride through fails due to the tripping of G18-115-GEN10 and G18-115-GEN20 units. No cascading was observed and the issue was localised. Model tuning is recommended.
04 - Southeast | 25W | Transfer | Group4_Fault_0674_P1 | 3 phase fault on ELGINJT4 (511486) 138 kV Bus a. Apply Fault at the ELGINJT4 (511486) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from ELGINJT4 (511486) 138 kV Bus to ELSWORTH 4 (511563) 138 kV Bus CKT 1 b. 2. Trip branch from ELSWORTH 4 (511563) 138 kV Bus to S.W.S.-4 (511477) 138 kV Bus CKT 1 b. 3. Drop Load 1 at ELSWORTH 4 (511563) 138 kV Bus b. 4. Drop Load 2 at ELSWORTH 4 (511563) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0675_P1 | 3 phase fault on ELGINJT4 (511486) 138 kV Bus a. Apply Fault at the ELGINJT4 (511486) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from ELGINJT4 (511486) 138 kV Bus to ELGINJT2 (511487) 69 kV Bus to ELGJT1-1 (511412) 13.8 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0676_P1 | 3 phase fault on ANADARK4 (520814) 138 kV Bus a. Apply Fault at the ANADARK4 (520814) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from ANADARK4 (520814) 138 kV Bus to SEQUOYAHJ4 (520422) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Low voltage ride through fails due to the tripping of G18-115-GEN10 and G18-115-GEN20 units. No cascading was observed and the issue was localised. Model tuning is recommended. |  |  | Generator relays were disabled for the following generators: 920003 [BLUCAN2-WTG30.6900], 920004 [BLUCAN2-WTG40.6900]
04 - Southeast | 25W | Transfer | Group4_Fault_0677_P1 | 3 phase fault on GRACMNT7 (515800) 345 kV Bus a. Apply Fault at the GRACMNT7 (515800) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from GRACMNT7 (515800) 345 kV Bus to MINCO 7 (514801) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Low voltage ride through fails due to the tripping of G18-115-GEN10 and G18-115-GEN20 units. No cascading was observed and the issue was localised. Model tuning is recommended. |  |  | Generator relays were disabled for the following generators: 761232 [G17-150GEN1 0.6600], 762903 [G18-055-GEN10.6600], 920001 [BLUCAN2-WTG10.6900], 920002 [BLUCAN2-WTG20.6900], 920003 [BLUCAN2-WTG30.6900], 920004 [BLUCAN2-WTG40.6900]
04 - Southeast | 25W | Transfer | Group4_Fault_0678_P1 | 3 phase fault on ANADARK4 (520814) 138 kV Bus a. Apply Fault at the ANADARK4 (520814) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from ANADARK4 (520814) 138 kV Bus to CLVLDSW4 (520508) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Low voltage ride through fails due to the tripping of G18-115-GEN10 and G18-115-GEN20 units. No cascading was observed and the issue was localised. Model tuning is recommended.
04 - Southeast | 25W | Transfer | Group4_Fault_0679_P1 | 3 phase fault on ANADARK4 (520814) 138 kV Bus a. Apply Fault at the ANADARK4 (520814) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from ANADARK4 (520814) 138 kV Bus to CHERRYRD 4 (521129) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Low voltage ride through fails due to the tripping of G18-115-GEN10 and G18-115-GEN20 units. No cascading was observed and the issue was localised. Model tuning is recommended.
04 - Southeast | 25W | Transfer | Group4_Fault_0680_P1 | 3 phase fault on ANADARK4 (520814) 138 kV Bus a. Apply Fault at the ANADARK4 (520814) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from ANADARK4 (520814) 138 kV Bus to POCASET4 (521031) 138 kV Bus CKT 1 b. 2. Trip branch from POCASET4 (521031) 138 kV Bus to TUTLETP4 (521072) 138 kV Bus CKT 1 b. 3. Drop Load 1 at POCASET4 (521031) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Low voltage ride through fails due to the tripping of G18-115-GEN10 and G18-115-GEN20 units. No cascading was observed and the issue was localised. Model tuning is recommended.
04 - Southeast | 25W | Transfer | Group4_Fault_0681_P1 | 3 phase fault on ANADARK4 (520814) 138 kV Bus a. Apply Fault at the ANADARK4 (520814) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from ANADARK4 (520814) 138 kV Bus to GEORGIA4 (520923) 138 kV Bus CKT 1 b. 2. Trip branch from GEORGIA4 (520923) 138 kV Bus to FLETCH-4 (520912) 138 kV Bus CKT 1 b. 3. Drop Load 1 at GEORGIA4 (520923) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Low voltage ride through fails due to the tripping of G18-115-GEN10 and G18-115-GEN20 units. No cascading was observed and the issue was localised. Model tuning is recommended.
04 - Southeast | 25W | Transfer | Group4_Fault_0682_P1 | 3 phase fault on ANADARK4 (520814) 138 kV Bus a. Apply Fault at the ANADARK4 (520814) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from ANADARK4 (520814) 138 kV Bus to ANADARK2 (520810) 69 kV Bus to ADRKTERT (521181) 13.8 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Low voltage ride through fails due to the tripping of G18-115-GEN10 and G18-115-GEN20 units. No cascading was observed and the issue was localised. Model tuning is recommended. |  |  | Generator relays were disabled for the following generators: 920003 [BLUCAN2-WTG30.6900], 920004 [BLUCAN2-WTG40.6900]
04 - Southeast | 25W | Transfer | Group4_Fault_0683_P1 | 3 phase fault on WASHITA4 (521089) 138 kV Bus a. Apply Fault at the WASHITA4 (521089) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from WASHITA4 (521089) 138 kV Bus to S.W.S.-4 (511477) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Low voltage ride through fails due to the tripping of G18-115-GEN10 and G18-115-GEN20 units. No cascading was observed and the issue was localised. Model tuning is recommended. |  |  | Generator relays were disabled for the following generators: 587793 [G16-097-GEN10.6900]
04 - Southeast | 25W | Transfer | Group4_Fault_0685_P1 | 3 phase fault on WASHITA4 (521089) 138 kV Bus a. Apply Fault at the WASHITA4 (521089) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from WASHITA4 (521089) 138 kV Bus to WASHITA2 (521088) 69 kV Bus to WASHTERT (521179) 7.2 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Low voltage ride through fails due to the tripping of G18-115-GEN10 and G18-115-GEN20 units. No cascading was observed and the issue was localised. Model tuning is recommended. |  |  | Generator relays were disabled for the following generators: 587793 [G16-097-GEN10.6900]
04 - Southeast | 25W | Transfer | Group4_Fault_0686_P1 | 3 phase fault on WASHITA4 (521089) 138 kV Bus a. Apply Fault at the WASHITA4 (521089) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from WASHITA4 (521089) 138 kV Bus to ONEY 4 (521017) 138 kV Bus CKT 1 b. 2. Trip branch from ONEY 4 (521017) 138 kV Bus to BINGERJ4 (520827) 138 kV Bus CKT 1 b. 3. Drop Load 1 at ONEY 4 (521017) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Low voltage ride through fails due to the tripping of G18-115-GEN10 and G18-115-GEN20 units. No cascading was observed and the issue was localised. Model tuning is recommended. |  |  | Generator relays were disabled for the following generators: 587793 [G16-097-GEN10.6900], 599003 [BLUCAN2-WTG50.6900], 920001 [BLUCAN2-WTG10.6900], 920002 [BLUCAN2-WTG20.6900], 920003 [BLUCAN2-WTG30.6900], 920004 [BLUCAN2-WTG40.6900]
04 - Southeast | 25W | Transfer | Group4_Fault_0687_P1 | 3 phase fault on GRACMNT7 (515800) 345 kV Bus a. Apply Fault at the GRACMNT7 (515800) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from GRACMNT7 (515800) 345 kV Bus to G16-037-TAP (560078) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Low voltage ride through fails due to the tripping of G18-115-GEN10 and G18-115-GEN20 units. No cascading was observed and the issue was localised. Model tuning is recommended. |  |  | Generator relays were disabled for the following generators: 761232 [G17-150GEN1 0.6600], 762903 [G18-055-GEN10.6600], 920001 [BLUCAN2-WTG10.6900], 920002 [BLUCAN2-WTG20.6900], 920003 [BLUCAN2-WTG30.6900], 920004 [BLUCAN2-WTG40.6900]
04 - Southeast | 25W | Transfer | Group4_Fault_0688_P1 | 3 phase fault on GRACMNT7 (515800) 345 kV Bus a. Apply Fault at the GRACMNT7 (515800) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from GRACMNT7 (515800) 345 kV Bus to GRACMNT4 (515802) 138 kV Bus to GRCMNT11 (515801) 13.8 kV Bus CKT 1 b. 2. Drop Shunt 1 at GRCMNT11 (515801) 13.8 kV Bus1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Low voltage ride through fails due to the tripping of G18-115-GEN10 and G18-115-GEN20 units. No cascading was observed and the issue was localised. Model tuning is recommended. |  |  | Generator relays were disabled for the following generators: 587793 [G16-097-GEN10.6900], 761232 [G17-150GEN1 0.6600], 762903 [G18-055-GEN10.6600], 920001 [BLUCAN2-WTG10.6900], 920002 [BLUCAN2-WTG20.6900], 920003 [BLUCAN2-WTG30.6900], 920004 [BLUCAN2-WTG40.6900]
04 - Southeast | 25W | Transfer | Group4_Fault_0689_P4 | a. Apply single phase fault at L.E.S.-4 (511467) 138 kV b. Clear Fault after 16 cycles: b. 1. Trip three winding transformer from L.E.S.-4 (511467) 138 kV to L.E.S.-7 (511468) kV to LES#5-1 (511411) 13.8 kV CKT2 b. 2. Trip branch from L.E.S.-4 (511467) 138 kV to COMMTAP4 (511494) 138 kV CKT 1 b. 3. Drop Shunt 1 LES#5-1 (511411) 13.8 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0690_P4 | a. Apply single phase fault at MINCO 7 (514801) 345 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from MINCO 7 (514801) 345 kV to NSUB345 (555234) kV CKT 1 b. 2. Trip branch from MINCO 7 (514801) 345 kV to GRACMNT7 (515800) 345 kV CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Low voltage ride through fails due to the tripping of G18-115-GEN10 and G18-115-GEN20 units. No cascading was observed and the issue was localised. Model tuning is recommended. |  |  | Generator relays were disabled for the following generators: 761232 [G17-150GEN1 0.6600]
04 - Southeast | 25W | Transfer | Group4_Fault_0691_P4 | a. Apply single phase fault at GRACMNT4 (515802) 138 kV b. Clear Fault after 16 cycles: b. 1. Trip three winding transformer from GRACMNT4 (515802) 138 kV to GRACMNT7 (515800) kV to GRCMNT11 (515801) 13.8 kV CKT2 b. 2. Trip branch from GRACMNT4 (515802) 138 kV to ANADARK4 (520814) 138 kV CKT 1 b. 3. Drop Shunt 1 GRCMNT11 (515801) 13.8 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0692_P4 | a. Apply single phase fault at L.E.S.-2 (511466) 69 kV b. Clear Fault after 16 cycles: b. 1. Trip three winding transformer from L.E.S.-2 (511466) 69 kV to L.E.S.-4 (511467) kV to LES#1-1 (511416) 13.8 kV CKT1 b. 2. Trip branch from L.E.S.-2 (511466) 69 kV to LGORE-S2 (511470) 69 kV CKT 1 b. 3. Trip branch from LGORE-S2 (511470) 69 kV to LAW WC2 (511503) 69 kV CKT 1 b. 4. Drop Load 1 LGORE-S2 (511470) 69 kV b. 5. Drop Load 1 LAW WC2 (511503) 69 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0693_P4 | a. Apply single phase fault at 112GORE4 (511488) 138 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from 112GORE4 (511488) 138 kV to COMANC-4 (511437) 138 kV CKT 1 b. 2. Trip branch from 112GORE4 (511488) 138 kV to LAIRGST4 (511510) 138 kV CKT 1 b. 3. Trip branch from LAIRGST4 (511510) 138 kV to CACHE4 (511500) 138 kV CKT 1 b. 4. Trip branch from LAIRGST4 (511510) 138 kV to L AIRGS4 (511429) 138 kV CKT 1 b. 5. Trip branch from CACHE4 (511500) 138 kV to G17-036_TAP (588779) 138 kV CKT 1 b. 6. Drop Load 1 CACHE4 (511500) 138 kV b. 7. Drop Load 1 L AIRGS4 (511429) 138 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0694_P4 | a. Apply single phase fault at WWRDEHV7 (515375) 345 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from WWRDEHV7 (515375) 345 kV to WWDBORDT (755000) 345 kV CKT 1 b. 2. Trip branch from WWRDEHV7 (515375) 345 kV to TATONGA7 (515407) 345 kV CKT 2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0696_P4 | a. Apply single phase fault at ELKCTY-4 (511458) 138 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from ELKCTY-4 (511458) 138 kV to CLINTJC4 (511485) 138 kV CKT 1 b. 2. Trip branch from ELKCTY-4 (511458) 138 kV to REDHLSW4 (521116) 138 kV CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0697_P4 | a. Apply single phase fault at WWRDEHV4 (515376) 138 kV b. Clear Fault after 16 cycles: b. 1. Trip three winding transformer from WWRDEHV4 (515376) 138 kV to WWRDEHV7 (515375) kV to WWDEHV21 (515799) 13.8 kV CKT2 b. 2. Trip branch from WWRDEHV4 (515376) 138 kV to IODINE-4 (514796) 138 kV CKT 1 b. 3. Trip branch from IODINE-4 (514796) 138 kV to REDCLFT4 (515533) 138 kV CKT 1 b. 4. Trip branch from REDCLFT4 (515533) 138 kV to DEWEY 4 (514787) 138 kV CKT 1 b. 5. Trip branch from REDCLFT4 (515533) 138 kV to REDCLF 4 (515863) 138 kV CKT 1 b. 6. Drop Load 1 IODINE-4 (514796) 138 kV b. 7. Drop Load 1 REDCLF 4 (515863) 138 kV b. 8. Drop Shunt 1 WWDEHV21 (515799) 13.8 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0698_P4 | a. Apply single phase fault at TOLK 6 (525531) 230 kV b. Clear Fault after 16 cycles: b. 1. Trip three winding transformer from TOLK 6 (525531) 230 kV to TOLK 7 (525549) kV to TOLK_TR 1 (525537) 13.2 kV CKT1 b. 2. Trip branch from TOLK 6 (525531) 230 kV to PLANT_X 6 (525481) 230 kV CKT 2 b. 3. Drop Shunt 1 TOLK_TR 1 (525537) 13.2 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0699_P1 | 3 phase fault on SWEETWT6 (511541) 230 kV Bus a. Apply Fault at the SWEETWT6 (511541) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from SWEETWT6 (511541) 230 kV Bus to CHISHOLM6 (511557) 230 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 763346 [G18-117-GEN20.6000], 763541 [G19-013-GEN10.7200], 763948 [G19-066-GEN10.7200]
04 - Southeast | 25W | Transfer | Group4_Fault_0700_P1 | 3 phase fault on ELKCITY6 (511490) 230 kV Bus a. Apply Fault at the ELKCITY6 (511490) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from ELKCITY6 (511490) 230 kV Bus to ELKCTY-4 (511458) 138 kV Bus to ELKC2-1 (511482) 13.8 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0701_P1 | 3 phase fault on WHEELER 6 (523777) 230 kV Bus a. Apply Fault at the WHEELER 6 (523777) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from WHEELER 6 (523777) 230 kV Bus to GRAPEVINE 6 (523771) 230 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0702_P1 | 3 phase fault on WHEELER 6 (523777) 230 kV Bus a. Apply Fault at the WHEELER 6 (523777) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from WHEELER 6 (523777) 230 kV Bus to WHEELER 3 (523776) 115 kV Bus to WHEELER_TR11 (523774) 13.2 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0703_P1 | 3 phase fault on SWEETWT6 (511541) 230 kV Bus a. Apply Fault at the SWEETWT6 (511541) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from SWEETWT6 (511541) 230 kV Bus to STLN-DEMARC6 (523779) 230 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 763346 [G18-117-GEN20.6000], 763541 [G19-013-GEN10.7200], 763948 [G19-066-GEN10.7200]
04 - Southeast | 25W | Transfer | Group4_Fault_0704_P1 | 3 phase fault on NICHOLS 6 (524044) 230 kV Bus a. Apply Fault at the NICHOLS 6 (524044) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from NICHOLS 6 (524044) 230 kV Bus to GRAPEVINE 6 (523771) 230 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0705_P1 | 3 phase fault on GRAPEVINE 6 (523771) 230 kV Bus a. Apply Fault at the GRAPEVINE 6 (523771) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from GRAPEVINE 6 (523771) 230 kV Bus to GRAPEVINE 3 (523770) 115 kV Bus to GRAPEVN_TR11 (523769) 13.2 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0706_P1 | 3 phase fault on TOLK 7 (525549) 345 kV Bus a. Apply Fault at the TOLK 7 (525549) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from TOLK 7 (525549) 345 kV Bus to POTTER_CO 7 (523961) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0707_P1 | 3 phase fault on POTTER_CO 7 (523961) 345 kV Bus a. Apply Fault at the POTTER_CO 7 (523961) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from POTTER_CO 7 (523961) 345 kV Bus to POTTER_CO 6 (523959) 230 kV Bus to POTTER_TR 1 (523957) 13.2 kV Bus CKT 1 b. 2. Drop Shunt 1 at POTTER_TR 1 (523957) 13.2 kV Bus1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0708_P1 | 3 phase fault on HITCHLAND 7 (523097) 345 kV Bus a. Apply Fault at the HITCHLAND 7 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from HITCHLAND 7 (523097) 345 kV Bus to POTTER_CO 7 (523961) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0709_P1 | 3 phase fault on MATHWSN7 (515497) 345 kV Bus a. Apply Fault at the MATHWSN7 (515497) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from MATHWSN7 (515497) 345 kV Bus to TATONGA7 (515407) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Low voltage ride through fails due to the tripping of G18-115-GEN10 and G18-115-GEN20 units. No cascading was observed and the issue was localised. Model tuning is recommended. |  |  | Generator relays were disabled for the following generators: 587953 [G16-119-GEN10.6900], 587958 [G16-119-GEN20.6900], 761232 [G17-150GEN1 0.6600]
04 - Southeast | 25W | Transfer | Group4_Fault_0710_P1 | 3 phase fault on MATHWSN7 (515497) 345 kV Bus a. Apply Fault at the MATHWSN7 (515497) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from MATHWSN7 (515497) 345 kV Bus to TATONGA7 (515407) 345 kV Bus CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Low voltage ride through fails due to the tripping of G18-115-GEN10 and G18-115-GEN20 units. No cascading was observed and the issue was localised. Model tuning is recommended. |  |  | Generator relays were disabled for the following generators: 587953 [G16-119-GEN10.6900], 587958 [G16-119-GEN20.6900], 761232 [G17-150GEN1 0.6600]
04 - Southeast | 25W | Transfer | Group4_Fault_0711_P1 | 3 phase fault on ELKCITY6 (511490) 230 kV Bus a. Apply Fault at the ELKCITY6 (511490) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from ELKCITY6 (511490) 230 kV Bus to CHISHOLM6 (511557) 230 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0712_P1 | 3 phase fault on BVRCNTY7 (515554) 345 kV Bus a. Apply Fault at the BVRCNTY7 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from BVRCNTY7 (515554) 345 kV Bus to HITCHLAND 7 (523097) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0713_P1 | 3 phase fault on BVRCNTY7 (515554) 345 kV Bus a. Apply Fault at the BVRCNTY7 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from BVRCNTY7 (515554) 345 kV Bus to HITCHLAND 7 (523097) 345 kV Bus CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0714_P1 | 3 phase fault on BVRCNTY7 (515554) 345 kV Bus a. Apply Fault at the BVRCNTY7 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from BVRCNTY7 (515554) 345 kV Bus to BADGER 7 (515677) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0715_P1 | 3 phase fault on BVRCNTY7 (515554) 345 kV Bus a. Apply Fault at the BVRCNTY7 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from BVRCNTY7 (515554) 345 kV Bus to BADGER 7 (515677) 345 kV Bus CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0716_P1 | 3 phase fault on DGRASSE7 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 (515852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from DGRASSE7 (515852) 345 kV Bus to THISTLE7 (539801) 345 kV Bus CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0717_P1 | 3 phase fault on DGRASSE7 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 (515852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from DGRASSE7 (515852) 345 kV Bus to THISTLE7 (539801) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0718_P1 | 3 phase fault on DGRASSE7 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 (515852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from DGRASSE7 (515852) 345 kV Bus to DGRASSE4 (515853) 138 kV Bus to DGRASSE1 (515854) 13.8 kV Bus CKT 1 b. 2. Drop Shunt 1 at DGRASSE1 (515854) 13.8 kV Bus1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0719_P1 | 3 phase fault on TOLK 7 (525549) 345 kV Bus a. Apply Fault at the TOLK 7 (525549) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from TOLK 7 (525549) 345 kV Bus to TOLK 6 (525531) 230 kV Bus to TOLK_TF3 (525539) kV Bus CKT 3 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0720_P1 | 3 phase fault on WHEELER 6 (523777) 230 kV Bus a. Apply Fault at the WHEELER 6 (523777) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from WHEELER 6 (523777) 230 kV Bus to STLN-DEMARC6 (523779) 230 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0721_P4 | a. Apply single phase fault at CLARMR 5 (512651) 161 kV b. Clear Fault after 16 cycles: b. 1. Trip three winding transformer from CLARMR 5 (512651) 161 kV to CLARMR 4 (512707) kV to CLARMR4 (512813) 13.8 kV CKT1 b. 2. Trip branch from CLARMR 4 (512707) 138 kV to OOLOGAHKM 4 (513124) 138 kV CKT 1 b. 3. Trip branch from OOLOGAHKM 4 (513124) 138 kV to N.E.S.-4 (510396) 138 kV CKT 1 b. 4. Trip three winding transformer from CLARMR 5 (512651) 161 kV to CLARMR 2 (512679) kV to CLARMR1 (512814) 13.8 kV CKT1 b. 5. Drop Load 1 OOLOGAHKM 4 (513124) 138 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0722_P4 | a. Apply single phase fault at 4SILVCTY (300140) 138 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from 4SILVCTY (300140) 138 kV to 4BRISTOW (300137) 138 kV CKT 1 b. 2. Trip branch from 4SILVCTY (300140) 138 kV to SILVCTYGR4 (512726) 138 kV CKT 1 b. 3. Trip branch from SILVCTYGR4 (512726) 138 kV to WEKIWA-4 (509757) 138 kV CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0723_P4 | a. Apply single phase fault at GORE GR2 (512644) 69 kV b. Clear Fault after 16 cycles: b. 1. Trip three winding transformer from GORE GR2 (512644) 69 kV to GORE 5 (505552) kV to GORTER1 (512832) 13.8 kV CKT1 b. 2. Trip branch from GORE GR2 (512644) 69 kV to 2VIAN (300879) 69 kV CKT 1 b. 3. Drop Load 1 2VIAN (300879) 69 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0724_P4 | a. Apply single phase fault at CATSAGR5 (512638) 161 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from CATSAGR5 (512638) 161 kV to 5ELMCRK (300993) 161 kV CKT 1 b. 2. Trip branch from 5ELMCRK (300993) 161 kV to COLINS 5 (512627) 161 kV CKT 1 b. 3. Trip branch from CATSAGR5 (512638) 161 kV to MAID 5 (512648) 161 kV CKT 1 b. 4. Drop Load 1 5ELMCRK (300993) 161 kV b. 5. Drop Load 2 5ELMCRK (300993) 161 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0725_P4 | a. Apply single phase fault at CLARMR 2 (512679) 69 kV b. Clear Fault after 16 cycles: b. 1. Trip three winding transformer from CLARMR 2 (512679) 69 kV to CLARMR 5 (512651) kV to CLARMR1 (512814) 13.8 kV CKT1 b. 2. Trip branch from CLARMR 2 (512679) 69 kV to CLARCTY4 2 (513014) 69 kV CKT 1 b. 3. Trip branch from CLARCTY4 2 (513014) 69 kV to CLARCTY1 2 (513010) 69 kV CKT 1 b. 4. Drop Load 1 CLARCTY4 2 (513014) 69 kV b. 5. Drop Load 1 CLARCTY1 2 (513010) 69 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0726_P4 | a. Apply single phase fault at CATOOSA4 (509790) 138 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from CATOOSA4 (509790) 138 kV to TERNITP4 (509835) 138 kV CKT 1 b. 2. Trip branch from TERNITP4 (509835) 138 kV to TER-NIT4 (509723) 138 kV CKT 1 b. 3. Trip branch from TERNITP4 (509835) 138 kV to VERDIGS4 (509854) 138 kV CKT 1 b. 4. Trip branch from VERDIGS4 (509854) 138 kV to CLARTOK4 (509864) 138 kV CKT 1 b. 5. Trip branch from CLARTOK4 (509864) 138 kV to N.E.S.-4 (510396) 138 kV CKT 1 b. 6. Trip branch from CATOOSA4 (509790) 138 kV to INOLATP4 (509752) 138 kV CKT 1 b. 7. Trip branch from INOLATP4 (509752) 138 kV to INOLA 4 (509736) 138 kV CKT 1 b. 8. Trip branch from INOLATP4 (509752) 138 kV to ROCKPT-4 (510437) 138 kV CKT 1 b. 9. Trip branch from ROCKPT-4 (510437) 138 kV to CHOUTEA4 (510373) 138 kV CKT 1 b. 10. Trip branch from CHOUTEA4 (510373) 138 kV to EXCLART4 (510401) 138 kV CKT 1 b. 11. Drop Load 1 TER-NIT4 (509723) 138 kV b. 12. Drop Shunt 1 TER-NIT4 (509723) 138 kV b. 13. Drop Load M1 VERDIGS4 (509854) 138 kV b. 14. Drop Load M2 VERDIGS4 (509854) 138 kV b. 15. Drop Load 1 CLARTOK4 (509864) 138 kV b. 16. Drop Load 1 INOLA 4 (509736) 138 kV b. 17. Drop Load 1 ROCKPT-4 (510437) 138 kV b. 18. Drop Load 1 CHOUTEA4 (510373) 138 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0727_P4 | a. Apply single phase fault at COLINS 5 (512627) 161 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from COLINS 5 (512627) 161 kV to 5ELMCRK (300993) 161 kV CKT 1 b. 2. Trip branch from 5ELMCRK (300993) 161 kV to CATSAGR5 (512638) 161 kV CKT 1 b. 3. Trip branch from COLINS 5 (512627) 161 kV to 5KETONVL (300997) 161 kV CKT 1 b. 4. Trip branch from 5KETONVL (300997) 161 kV to CLARMR 5 (512651) 161 kV CKT 1 b. 5. Drop Load 2 5ELMCRK (300993) 161 kV b. 6. Drop Load 1 5KETONVL (300997) 161 kV b. 7. Drop Load 2 5KETONVL (300997) 161 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0728_P4 | a. Apply single phase fault at HUNT 2 (512671) 69 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from HUNT 2 (512671) 69 kV to MAIDTP2 (512625) 69 kV CKT 1 b. 2. Trip branch from MAIDTP2 (512625) 69 kV to GRDA1 2 (512727) 69 kV CKT 1 b. 3. Trip three winding transformer from GRDA1 2 (512727) 69 kV to GRDA1 5 (512656) kV to GRDA1 1 (512816) 13.8 kV CKT1 b. 4. Trip branch from HUNT 2 (512671) 69 kV to PRY0RC22 (512639) 69 kV CKT 1 b. 5. Trip branch from PRY0RC22 (512639) 69 kV to PRYORC32 (512622) 69 kV CKT 1 b. 6. Trip branch from PRYORC32 (512622) 69 kV to PRYORC12 (512810) 69 kV CKT 1 b. 7. Drop Load 1 PRY0RC22 (512639) 69 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0729_P4 | a. Apply single phase fault at COLNSGR2 (512870) 69 kV b. Clear Fault after 16 cycles: b. 1. Trip three winding transformer from COLNSGR2 (512870) 69 kV to COLINS 5 (512627) kV to COLLIN3 1 (512840) 13.8 kV CKT2 b. 2. Trip branch from COLNSGR2 (512870) 69 kV to PARKMEDTP (512703) 69 kV CKT 1 b. 3. Trip branch from PARKMEDTP (512703) 69 kV to 2PARKMDWS (301999) 69 kV CKT 1 b. 4. Trip branch from PARKMEDTP (512703) 69 kV to SKIATTP2 (512871) 69 kV CKT 1 b. 5. Drop Load 1 2PARKMDWS (301999) 69 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0730_P4 | a. Apply single phase fault at SPRGFLD5 (505492) 161 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from SPRGFLD5 (505492) 161 kV to BROOKLINE 5 (549969) 161 kV CKT 1 b. 2. Trip branch from SPRGFLD5 (505492) 161 kV to CLAY 5 (549970) 161 kV CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0731_P4 | a. Apply single phase fault at JTEC 5 (549954) 161 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from JTEC 5 (549954) 161 kV to SW DISP PLT5 (549960) 161 kV CKT 1 b. 2. Trip branch from SW DISP PLT5 (549960) 161 kV to BATTLEFIELD5 (549959) 161 kV CKT 1 b. 3. Trip branch from JTEC 5 (549954) 161 kV to 5BTLFD (300348) 161 kV CKT 1 b. 4. Trip branch from 5BTLFD (300348) 161 kV to 5JAMESV (300089) 161 kV CKT 1 b. 5. Drop Load W SW DISP PLT5 (549960) 161 kV b. 6. Drop Load E SW DISP PLT5 (549960) 161 kV b. 7. Drop Load E 5KETONVL (300997) 161 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0732_P1 | 3 phase fault on 5CDRCRST (301344) 161 kV Bus a. Apply Fault at the 5CDRCRST (301344) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from 5CDRCRST (301344) 161 kV Bus to 2CDRCRST (301345) 69 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0733_P1 | 3 phase fault on SHIPERD7 (506979) 345 kV Bus a. Apply Fault at the SHIPERD7 (506979) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from SHIPERD7 (506979) 345 kV Bus to SHIPERD5 (506980) 161 kV Bus to SHIPERD1 (506981) 13.8 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0734_P1 | 3 phase fault on WOLFCRK7 (532797) 345 kV Bus a. Apply Fault at the WOLFCRK7 (532797) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from WOLFCRK7 (532797) 345 kV Bus to BENTON 7 (532791) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0735_P1 | 3 phase fault on WOLFCRK7 (532797) 345 kV Bus a. Apply Fault at the WOLFCRK7 (532797) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from WOLFCRK7 (532797) 345 kV Bus to WAVERLY7 (532799) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0736_P1 | 3 phase fault on WOLFCRK7 (532797) 345 kV Bus a. Apply Fault at the WOLFCRK7 (532797) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from WOLFCRK7 (532797) 345 kV Bus to W.GRDNR7 (542965) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0737_P1 | 3 phase fault on WOLFCRK7 (532797) 345 kV Bus a. Apply Fault at the WOLFCRK7 (532797) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from WOLFCRK7 (532797) 345 kV Bus to WOLFCRK2 (533653) 69 kV Bus to WOLFCRK1 (532962) 17 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0738_P1 | 3 phase fault on LACYGNE7 (542981) 345 kV Bus a. Apply Fault at the LACYGNE7 (542981) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from LACYGNE7 (542981) 345 kV Bus to WAVERLY7 (532799) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0739_P1 | 3 phase fault on G17-009-TAP (532777) 345 kV Bus a. Apply Fault at the G17-009-TAP (532777) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from G17-009-TAP (532777) 345 kV Bus to CANEYRV7 (532780) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0740_P1 | 3 phase fault on CLARMR 5 (512651) 161 kV Bus a. Apply Fault at the CLARMR 5 (512651) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from CLARMR 5 (512651) 161 kV Bus to CLARMR 4 (512707) 138 kV Bus to CLARMR4 (512813) 13.8 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0741_P1 | 3 phase fault on FT GIB 5 (505560) 161 kV Bus a. Apply Fault at the FT GIB 5 (505560) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from FT GIB 5 (505560) 161 kV Bus to OKAYGR 5 (512640) 161 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0742_P1 | 3 phase fault on OKAYGR 5 (512640) 161 kV Bus a. Apply Fault at the OKAYGR 5 (512640) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from OKAYGR 5 (512640) 161 kV Bus to OKAYGR 2 (512646) 69 kV Bus to OKAY1 (512848) 13.8 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0743_P1 | 3 phase fault on PENSA 5 (512654) 161 kV Bus a. Apply Fault at the PENSA 5 (512654) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from PENSA 5 (512654) 161 kV Bus to KETCHUM5 (512669) 161 kV Bus CKT 1 b. 2. Trip branch from KETCHUM5 (512669) 161 kV Bus to AFTON 5 (512632) 161 kV Bus CKT 1 b. 3. Drop Load 1 at KETCHUM5 (512669) 161 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0744_P1 | 3 phase fault on PENSA 5 (512654) 161 kV Bus a. Apply Fault at the PENSA 5 (512654) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from PENSA 5 (512654) 161 kV Bus to PENSA 2 (512628) 69 kV Bus to PENSA 1 (512841) 13.8 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0745_P1 | 3 phase fault on 5CDRCRST (301344) 161 kV Bus a. Apply Fault at the 5CDRCRST (301344) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from 5CDRCRST (301344) 161 kV Bus to TAHLQH 5 (512655) 161 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0746_P4 | a. Apply single phase fault at TATONGA7 (515407) 345 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from TATONGA7 (515407) 345 kV to MATHWSN7 (515497) 345 kV CKT 2 b. 2. Trip branch from TATONGA7 (515407) 345 kV to WWRDEHV7 (515375) 345 kV CKT 2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0747_P4 | a. Apply single phase fault at HARPER 4 (539668) 138 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from HARPER 4 (539668) 138 kV to FLATRDG4 (539638) 138 kV CKT 1 b. 2. Trip branch from HARPER 4 (539668) 138 kV to MILANTP4 (539675) 138 kV CKT 1 b. 3. Trip branch from MILANTP4 (539675) 138 kV to CONWAY (539009) 138 kV CKT 1 b. 4. Trip branch from CONWAY (539009) 138 kV to VIOLA 4 (533075) 138 kV CKT 1 b. 5. Drop Load 1 CONWAY (539009) 138 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0748_P4 | a. Apply single phase fault at DGRASSE7 (515852) 345 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from DGRASSE7 (515852) 345 kV to THISTLE7 (539801) 345 kV CKT 1 b. 2. Trip branch from DGRASSE7 (515852) 345 kV to WWRDEHV7 (515375) 345 kV CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0749_P4 | a. Apply single phase fault at MATHWSN7 (515497) 345 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from MATHWSN7 (515497) 345 kV to CIMARON7 (514901) 345 kV CKT 2 b. 2. Trip branch from MATHWSN7 (515497) 345 kV to TATONGA7 (515407) 345 kV CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0750_P4 | a. Apply single phase fault at BADGER 7 (515677) 345 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from BADGER 7 (515677) 345 kV to BOBCAT 7 (516106) kV CKT 1 b. 2. Trip branch from BADGER 7 (515677) 345 kV to BOBCAT 7 (516106) kV CKT 2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0751_P4 | a. Apply single phase fault at THISTLE7 (539801) 345 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from THISTLE7 (539801) 345 kV to CLARKCOUNTY7 (539800) 345 kV CKT 1 b. 2. Trip branch from THISTLE7 (539801) 345 kV to BUFFALO7 (532782) 345 kV CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0752_P4 | a. Apply single phase fault at DGRASSE4 (515853) 138 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from DGRASSE4 (515853) 138 kV to KNOBHIL4 (514795) 138 kV CKT 1 b. 2. Trip branch from DGRASSE4 (515853) 138 kV to ROSEVLY4 (520436) 138 kV CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0753_P4 | a. Apply single phase fault at CIMARON7 (514901) 345 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from CIMARON7 (514901) 345 kV to MATHWSN7 (515497) 345 kV CKT 2 b. 2. Trip branch from CIMARON7 (514901) 345 kV to NSUB345 (555234) kV CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0754_P4 | a. Apply single phase fault at CLARKCOUNTY7 (539800) 345 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from CLARKCOUNTY7 (539800) 345 kV to THISTLE7 (539801) 345 kV CKT 1 b. 2. Trip branch from CLARKCOUNTY7 (539800) 345 kV to SPERVIL7 (531469) 345 kV CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0755_P1 | 3 phase fault on WWRDEHV7 (515375) 345 kV Bus a. Apply Fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from WWRDEHV7 (515375) 345 kV Bus to WWDBORDT (755000) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0756_P1 | 3 phase fault on WWRDEHV7 (515375) 345 kV Bus a. Apply Fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from WWRDEHV7 (515375) 345 kV Bus to WWRDEHV4 (515376) 138 kV Bus to WWDEHV21 (515799) 13.8 kV Bus CKT 2 b. 2. Drop Shunt 1 at WWDEHV21 (515799) 13.8 kV Bus1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0758_P1 | 3 phase fault on FINNEY 7 (523853) 345 kV Bus a. Apply Fault at the FINNEY 7 (523853) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from FINNEY 7 (523853) 345 kV Bus to HOLCOMB7 (531449) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0761_P1 | 3 phase fault on TOLK 7 (525549) 345 kV Bus a. Apply Fault at the TOLK 7 (525549) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from TOLK 7 (525549) 345 kV Bus to TOLK 6 (525531) 230 kV Bus to TOLK_TR 1 (525537) 13.2 kV Bus CKT 1 b. 2. Drop Shunt 1 at TOLK_TR 1 (525537) 13.2 kV Bus1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0762_P1 | 3 phase fault on TOLK 7 (525549) 345 kV Bus a. Apply Fault at the TOLK 7 (525549) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from TOLK 7 (525549) 345 kV Bus to TOLK 6 (525531) 230 kV Bus to TOLK_TF2 (525538) kV Bus CKT 2 b. 2. Drop Shunt 1 at TOLK_TF2 (525538) kV Bus1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0763_P1 | 3 phase fault on OCHILTREE 6 (523155) 230 kV Bus a. Apply Fault at the OCHILTREE 6 (523155) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from OCHILTREE 6 (523155) 230 kV Bus to OCHILTREE 3 (523154) 115 kV Bus to OCHLTRE_TR11 (523151) 13.2 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0764_P1 | 3 phase fault on FLATRDG4 (539638) 138 kV Bus a. Apply Fault at the FLATRDG4 (539638) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from FLATRDG4 (539638) 138 kV Bus to HARPER 4 (539668) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0765_P1 | 3 phase fault on FLATRDG4 (539638) 138 kV Bus a. Apply Fault at the FLATRDG4 (539638) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from FLATRDG4 (539638) 138 kV Bus to BARBER 4 (539674) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0766_P1 | 3 phase fault on WWRDEHV7 (515375) 345 kV Bus a. Apply Fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from WWRDEHV7 (515375) 345 kV Bus to WWRDEHV4 (515376) 138 kV Bus to WWDEHV31 (515795) 13.8 kV Bus CKT 1 b. 2. Drop Shunt 1 at WWDEHV31 (515795) 13.8 kV Bus1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0767_P1 | 3 phase fault on FLATRDG4 (539638) 138 kV Bus a. Apply Fault at the FLATRDG4 (539638) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from FLATRDG4 (539638) 138 kV Bus to BARBER 4 (539674) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0768_P1 | 3 phase fault on HOLCOMB7 (531449) 345 kV Bus a. Apply Fault at the HOLCOMB7 (531449) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from HOLCOMB7 (531449) 345 kV Bus to SETAB 7 (531465) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0769_P1 | 3 phase fault on HOLCOMB7 (531449) 345 kV Bus a. Apply Fault at the HOLCOMB7 (531449) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from HOLCOMB7 (531449) 345 kV Bus to HOLCOMB3 (531448) 115 kV Bus to HOLCTER1 (531450) 13.8 kV Bus CKT 1 b. 2. Drop Shunt 1 at HOLCTER1 (531450) 13.8 kV Bus1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0770_P1 | 3 phase fault on HOLCOMB7 (531449) 345 kV Bus a. Apply Fault at the HOLCOMB7 (531449) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from HOLCOMB7 (531449) 345 kV Bus to BUCKNER7 (531501) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0771_P1 | 3 phase fault on WALKMYR3 (531405) 115 kV Bus a. Apply Fault at the WALKMYR3 (531405) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from WALKMYR3 (531405) 115 kV Bus to HUGOTON3 (531481) 115 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0772_P1 | 3 phase fault on WALKMYR3 (531405) 115 kV Bus a. Apply Fault at the WALKMYR3 (531405) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from WALKMYR3 (531405) 115 kV Bus to CIM-PLT3 (539654) 115 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0773_P1 | 3 phase fault on WALKMYR3 (531405) 115 kV Bus a. Apply Fault at the WALKMYR3 (531405) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from WALKMYR3 (531405) 115 kV Bus to HUGOTON3 (531481) 115 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0774_P1 | 3 phase fault on REDCLFT4 (515533) 138 kV Bus a. Apply Fault at the REDCLFT4 (515533) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from REDCLFT4 (515533) 138 kV Bus to REDCLF 4 (515863) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0775_P1 | 3 phase fault on ARCADIA7 (514908) 345 kV Bus a. Apply Fault at the ARCADIA7 (514908) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from ARCADIA7 (514908) 345 kV Bus to ARCADIA4 (514907) 138 kV Bus to ARCADI31 (515704) 13.8 kV Bus CKT 1 b. 2. Drop Shunt 1 at ARCADI31 (515704) 13.8 kV Bus1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0776_P1 | 3 phase fault on ARCADIA7 (514908) 345 kV Bus a. Apply Fault at the ARCADIA7 (514908) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from ARCADIA7 (514908) 345 kV Bus to ARCADIA4 (514907) 138 kV Bus to ARCADI21 (515703) 13.8 kV Bus CKT 1 b. 2. Drop Shunt 1 at ARCADI21 (515703) 13.8 kV Bus1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0777_P1 | 3 phase fault on ARCADIA7 (514908) 345 kV Bus a. Apply Fault at the ARCADIA7 (514908) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from ARCADIA7 (514908) 345 kV Bus to ARCADIA4 (514907) 138 kV Bus to ARCADI41 (515700) 13.8 kV Bus CKT 1 b. 2. Drop Shunt 1 at ARCADI21 (515703) 13.8 kV Bus1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0778_P1 | 3 phase fault on NORTWST4 (514879) 138 kV Bus a. Apply Fault at the NORTWST4 (514879) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from NORTWST4 (514879) 138 kV Bus to BRADEN 4 (514854) 138 kV Bus CKT 1 b. 2. Trip branch from BRADEN 4 (514854) 138 kV Bus to SLVRLAK4 (514852) 138 kV Bus CKT 1 b. 3. Drop Load 1 at BRADEN 4 (514854) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Low voltage ride through fails due to the tripping of G18-115-GEN10 and G18-115-GEN20 units. No cascading was observed and the issue was localised. Model tuning is recommended.
04 - Southeast | 25W | Transfer | Group4_Fault_0779_P1 | 3 phase fault on SPERVIL7 (531469) 345 kV Bus a. Apply Fault at the SPERVIL7 (531469) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from SPERVIL7 (531469) 345 kV Bus to IRONWOOD7 (539803) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0780_P1 | 3 phase fault on TOLK 6 (525531) 230 kV Bus a. Apply Fault at the TOLK 6 (525531) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from TOLK 6 (525531) 230 kV Bus to LAMB_CNTY 6 (525637) 230 kV Bus CKT 1 b. 2. Trip three winding transformer from LAMB_CNTY 6 (525637) 230 kV Bus to LAMB_CNTY 3 (525636) 115 kV Bus to LAMB_TR3 1 (525633) 13.2 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 763254 [G18-099-GEN10.6900], 763257 [G18-099-GEN20.6900]
04 - Southeast | 25W | Transfer | Group4_Fault_0781_P1 | 3 phase fault on OCHILTREE 3 (523154) 115 kV Bus a. Apply Fault at the OCHILTREE 3 (523154) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from OCHILTREE 3 (523154) 115 kV Bus to PERRYTON 3 (523158) 115 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0782_P1 | 3 phase fault on OCHILTREE 3 (523154) 115 kV Bus a. Apply Fault at the OCHILTREE 3 (523154) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from OCHILTREE 3 (523154) 115 kV Bus to PERRYTON 3 (523158) 115 kV Bus CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0783_P1 | 3 phase fault on CIM-PLT3 (539654) 115 kV Bus a. Apply Fault at the CIM-PLT3 (539654) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from CIM-PLT3 (539654) 115 kV Bus to N-CIMRN3 (539749) 115 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0784_P1 | 3 phase fault on MOORLND2 (520995) 69 kV Bus a. Apply Fault at the MOORLND2 (520995) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from MOORLND2 (520995) 69 kV Bus to CRTSJCT2 (521197) 69 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0785_P1 | 3 phase fault on SLVRLAK4 (514852) 138 kV Bus a. Apply Fault at the SLVRLAK4 (514852) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from SLVRLAK4 (514852) 138 kV Bus to DVISION4 (514853) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0786_P1 | 3 phase fault on WWDBORDT (755000) 345 kV Bus a. Apply Fault at the WWDBORDT (755000) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from WWDBORDT (755000) 345 kV Bus to CHISHOLM7 (511553) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0787_P1 | 3 phase fault on WWDBORDT (755000) 345 kV Bus a. Apply Fault at the WWDBORDT (755000) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from WWDBORDT (755000) 345 kV Bus to BORDER 7 (515458) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0788_P1 | 3 phase fault on BORDER 7 (515458) 345 kV Bus a. Apply Fault at the BORDER 7 (515458) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from BORDER 7 (515458) 345 kV Bus to CRAWFISH_DR (560022) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0789_P1 | 3 phase fault on CRAWFISH_DR (560022) 345 kV Bus a. Apply Fault at the CRAWFISH_DR (560022) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from CRAWFISH_DR (560022) 345 kV Bus to TUCO_INT 7 (525832) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 763084 [G18-073-GEN20.6600], 763090 [G18-073-GEN10.6600]
04 - Southeast | 25W | Transfer | Group4_Fault_0790_P1 | 3 phase fault on CRAWFISH_DR (560022) 345 kV Bus a. Apply Fault at the CRAWFISH_DR (560022) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from CRAWFISH_DR (560022) 345 kV Bus to TUCO_INT 7 (525832) 345 kV Bus CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 763084 [G18-073-GEN20.6600], 763090 [G18-073-GEN10.6600]
04 - Southeast | 25W | Transfer | Group4_Fault_0791_P1 | 3 phase fault on G17-151TAP (762216) 345 kV Bus a. Apply Fault at the G17-151TAP (762216) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from G17-151TAP (762216) 345 kV Bus to CRAWFISH_DR (560022) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 763084 [G18-073-GEN20.6600]
04 - Southeast | 25W | Transfer | Group4_Fault_0792_P1 | 3 phase fault on CHISHOLM7 (511553) 345 kV Bus a. Apply Fault at the CHISHOLM7 (511553) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from CHISHOLM7 (511553) 345 kV Bus to GRAPEVINE (560035) 345 kV Bus CKT 1 b. 2. Trip branch from GRAPEVINE (560035) 345 kV Bus to POTTER_CO 7 (523961) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0793_P1 | 3 phase fault on TATONGA7 (515407) 345 kV Bus a. Apply Fault at the TATONGA7 (515407) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from TATONGA7 (515407) 345 kV Bus to MATHWSN7 (515497) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0794_P1 | 3 phase fault on TATONGA7 (515407) 345 kV Bus a. Apply Fault at the TATONGA7 (515407) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from TATONGA7 (515407) 345 kV Bus to MATHWSN7 (515497) 345 kV Bus CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0796_P1 | 3 phase fault on MATHWSN7 (515497) 345 kV Bus a. Apply Fault at the MATHWSN7 (515497) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from MATHWSN7 (515497) 345 kV Bus to REDNGTN7 (515875) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Low voltage ride through fails due to the tripping of G18-115-GEN10 and G18-115-GEN20 units. No cascading was observed and the issue was localised. Model tuning is recommended. |  |  | Generator relays were disabled for the following generators: 587953 [G16-119-GEN10.6900], 587958 [G16-119-GEN20.6900], 761232 [G17-150GEN1 0.6600]
04 - Southeast | 25W | Transfer | Group4_Fault_0797_P1 | 3 phase fault on WWRDEHV7 (515375) 345 kV Bus a. Apply Fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from WWRDEHV7 (515375) 345 kV Bus to TATONGA7 (515407) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Low voltage ride through fails due to the tripping of G18-115-GEN10 and G18-115-GEN20 units. No cascading was observed and the issue was localised. Model tuning is recommended.
04 - Southeast | 25W | Transfer | Group4_Fault_0798_P1 | 3 phase fault on MATHWSN7 (515497) 345 kV Bus a. Apply Fault at the MATHWSN7 (515497) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from MATHWSN7 (515497) 345 kV Bus to NORTWST7 (514880) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Low voltage ride through fails due to the tripping of G18-115-GEN10 and G18-115-GEN20 units. No cascading was observed and the issue was localised. Model tuning is recommended. |  |  | Generator relays were disabled for the following generators: 587953 [G16-119-GEN10.6900], 587958 [G16-119-GEN20.6900], 761232 [G17-150GEN1 0.6600]
04 - Southeast | 25W | Transfer | Group4_Fault_0799_P1 | 3 phase fault on NORTWST7 (514880) 345 kV Bus a. Apply Fault at the NORTWST7 (514880) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from NORTWST7 (514880) 345 kV Bus to NORTWST4 (514879) 138 kV Bus to NORTWS41 (514885) 13.8 kV Bus CKT 1 b. 2. Drop Shunt 1 at NORTWS41 (514885) 13.8 kV Bus1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 587953 [G16-119-GEN10.6900], 587958 [G16-119-GEN20.6900], 761232 [G17-150GEN1 0.6600]
04 - Southeast | 25W | Transfer | Group4_Fault_0800_P1 | 3 phase fault on NORTWST7 (514880) 345 kV Bus a. Apply Fault at the NORTWST7 (514880) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from NORTWST7 (514880) 345 kV Bus to NORTWST4 (514879) 138 kV Bus to NORTWS31 (515743) 13.8 kV Bus CKT 1 b. 2. Drop Shunt 1 at NORTWS31 (515743) 13.8 kV Bus1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 587953 [G16-119-GEN10.6900], 587958 [G16-119-GEN20.6900], 761232 [G17-150GEN1 0.6600]
04 - Southeast | 25W | Transfer | Group4_Fault_0801_P1 | 3 phase fault on NORTWST7 (514880) 345 kV Bus a. Apply Fault at the NORTWST7 (514880) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from NORTWST7 (514880) 345 kV Bus to NORTWST4 (514879) 138 kV Bus to NORTWS21 (515742) 13.8 kV Bus CKT 1 b. 2. Drop Shunt 1 at NORTWS21 (515742) 13.8 kV Bus1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 587953 [G16-119-GEN10.6900], 587958 [G16-119-GEN20.6900], 761232 [G17-150GEN1 0.6600]
04 - Southeast | 25W | Transfer | Group4_Fault_0802_P1 | 3 phase fault on BVRCNTY7 (515554) 345 kV Bus a. Apply Fault at the BVRCNTY7 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from BVRCNTY7 (515554) 345 kV Bus to BADGER 7 (515677) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0803_P1 | 3 phase fault on WWRDEHV7 (515375) 345 kV Bus a. Apply Fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from WWRDEHV7 (515375) 345 kV Bus to BVRCNTY7 (515554) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Low voltage ride through fails due to the tripping of G18-115-GEN10 and G18-115-GEN20 units. No cascading was observed and the issue was localised. Model tuning is recommended.
04 - Southeast | 25W | Transfer | Group4_Fault_0804_P1 | 3 phase fault on BVRCNTY7 (515554) 345 kV Bus a. Apply Fault at the BVRCNTY7 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from BVRCNTY7 (515554) 345 kV Bus to BADGER 7 (515677) 345 kV Bus CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0805_P1 | 3 phase fault on BVRCNTY7 (515554) 345 kV Bus a. Apply Fault at the BVRCNTY7 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from BVRCNTY7 (515554) 345 kV Bus to HITCHLAND 7 (523097) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0806_P1 | 3 phase fault on BVRCNTY7 (515554) 345 kV Bus a. Apply Fault at the BVRCNTY7 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from BVRCNTY7 (515554) 345 kV Bus to HITCHLAND 7 (523097) 345 kV Bus CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0807_P1 | 3 phase fault on DGRASSE7 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 (515852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from DGRASSE7 (515852) 345 kV Bus to THISTLE7 (539801) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0808_P1 | 3 phase fault on DGRASSE7 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 (515852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from DGRASSE7 (515852) 345 kV Bus to THISTLE7 (539801) 345 kV Bus CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0809_P1 | 3 phase fault on THISTLE7 (539801) 345 kV Bus a. Apply Fault at the THISTLE7 (539801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from THISTLE7 (539801) 345 kV Bus to BUFFALO7 (532782) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0810_P1 | 3 phase fault on THISTLE7 (539801) 345 kV Bus a. Apply Fault at the THISTLE7 (539801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from THISTLE7 (539801) 345 kV Bus to BUFFALO7 (532782) 345 kV Bus CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0811_P1 | 3 phase fault on WWRDEHV7 (515375) 345 kV Bus a. Apply Fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from WWRDEHV7 (515375) 345 kV Bus to TATONGA7 (515407) 345 kV Bus CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Low voltage ride through fails due to the tripping of G18-115-GEN10 and G18-115-GEN20 units. No cascading was observed and the issue was localised. Model tuning is recommended.
04 - Southeast | 25W | Transfer | Group4_Fault_0812_P1 | 3 phase fault on THISTLE7 (539801) 345 kV Bus a. Apply Fault at the THISTLE7 (539801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from THISTLE7 (539801) 345 kV Bus to THISTLE4 (539804) 138 kV Bus to THISTLE T1 (539802) 13.8 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0813_P1 | 3 phase fault on THISTLE7 (539801) 345 kV Bus a. Apply Fault at the THISTLE7 (539801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from THISTLE7 (539801) 345 kV Bus to CLARKCOUNTY7 (539800) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0814_P1 | 3 phase fault on THISTLE7 (539801) 345 kV Bus a. Apply Fault at the THISTLE7 (539801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from THISTLE7 (539801) 345 kV Bus to CLARKCOUNTY7 (539800) 345 kV Bus CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0815_P1 | 3 phase fault on DGRASSE7 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 (515852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from DGRASSE7 (515852) 345 kV Bus to DGRASSE4 (515853) 138 kV Bus to DGRASSE1 (515854) 13.8 kV Bus CKT 1 b. 2. Drop Shunt 1 at DGRASSE1 (515854) 13.8 kV Bus1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0816_P1 | 3 phase fault on DGRASSE4 (515853) 138 kV Bus a. Apply Fault at the DGRASSE4 (515853) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from DGRASSE4 (515853) 138 kV Bus to KNOBHIL4 (514795) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0817_P1 | 3 phase fault on DGRASSE4 (515853) 138 kV Bus a. Apply Fault at the DGRASSE4 (515853) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from DGRASSE4 (515853) 138 kV Bus to MOORLND4 (520999) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0818_P1 | 3 phase fault on DGRASSE4 (515853) 138 kV Bus a. Apply Fault at the DGRASSE4 (515853) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from DGRASSE4 (515853) 138 kV Bus to ROSEVLY4 (520436) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0819_P1 | 3 phase fault on HITCHLAND 7 (523097) 345 kV Bus a. Apply Fault at the HITCHLAND 7 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from HITCHLAND 7 (523097) 345 kV Bus to CARPENTER 7 (523823) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0820_P1 | 3 phase fault on HITCHLAND 7 (523097) 345 kV Bus a. Apply Fault at the HITCHLAND 7 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from HITCHLAND 7 (523097) 345 kV Bus to HITCHLAND 6 (523095) 230 kV Bus to HITCHLD_TR21 (523094) 13.2 kV Bus CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0821_P1 | 3 phase fault on HITCHLAND 7 (523097) 345 kV Bus a. Apply Fault at the HITCHLAND 7 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from HITCHLAND 7 (523097) 345 kV Bus to HITCHLAND 6 (523095) 230 kV Bus to HITCHLD_TR01 (523091) 13.2 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0822_P1 | 3 phase fault on WWRDEHV7 (515375) 345 kV Bus a. Apply Fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from WWRDEHV7 (515375) 345 kV Bus to DGRASSE7 (515852) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Low voltage ride through fails due to the tripping of G18-115-GEN10 and G18-115-GEN20 units. No cascading was observed and the issue was localised. Model tuning is recommended.
04 - Southeast | 25W | Transfer | Group4_Fault_0823_P1 | 3 phase fault on CHISHOLM7 (511553) 345 kV Bus a. Apply Fault at the CHISHOLM7 (511553) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from CHISHOLM7 (511553) 345 kV Bus to CHISHOLM6 (511557) 230 kV Bus to CHISHOLM1 (511558) 13.2 kV Bus CKT 1 b. 2. Drop Shunt 1 at CHISHOLM1 (511558) 13.2 kV Bus1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0824_P1 | 3 phase fault on CHISHOLM6 (511557) 230 kV Bus a. Apply Fault at the CHISHOLM6 (511557) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from CHISHOLM6 (511557) 230 kV Bus to ELKCITY6 (511490) 230 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0825_P1 | 3 phase fault on CHISHOLM6 (511557) 230 kV Bus a. Apply Fault at the CHISHOLM6 (511557) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from CHISHOLM6 (511557) 230 kV Bus to SWEETWT6 (511541) 230 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 763346 [G18-117-GEN20.6000], 763541 [G19-013-GEN10.7200], 763948 [G19-066-GEN10.7200]
04 - Southeast | 25W | Transfer | Group4_Fault_0826_P1 | 3 phase fault on CARPENTER 7 (523823) 345 kV Bus a. Apply Fault at the CARPENTER 7 (523823) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from CARPENTER 7 (523823) 345 kV Bus to FINNEY 7 (523853) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0827_P1 | 3 phase fault on CARPENTER 7 (523823) 345 kV Bus a. Apply Fault at the CARPENTER 7 (523823) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from CARPENTER 7 (523823) 345 kV Bus to HARBNGR7 (531512) 345 kV Bus CKT Z1 b. 2. Trip three winding transformer from HARBNGR7 (531512) 345 kV Bus to HARBNGR3 (531510) 115 kV Bus to HARBNGR-T (531511) 13.8 kV Bus CKT 1 b. 3. Trip branch from HARBNGR3 (531510) 115 kV Bus to WALKMYR3 (531405) 115 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0828_P1 | 3 phase fault on CIMARON7 (514901) 345 kV Bus a. Apply Fault at the CIMARON7 (514901) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from CIMARON7 (514901) 345 kV Bus to NSUB345 (555234) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Low voltage ride through fails due to the tripping of G18-115-GEN10 and G18-115-GEN20 units. No cascading was observed and the issue was localised. Model tuning is recommended. |  |  | Generator relays were disabled for the following generators: 587953 [G16-119-GEN10.6900], 587958 [G16-119-GEN20.6900], 761232 [G17-150GEN1 0.6600], 763841 [G19-052-GEN20.6000], 763959 [G19-067-GEN10.7200]
04 - Southeast | 25W | Transfer | Group4_Fault_0829_P1 | 3 phase fault on CIMARON7 (514901) 345 kV Bus a. Apply Fault at the CIMARON7 (514901) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from CIMARON7 (514901) 345 kV Bus to NSUB345 (555234) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Low voltage ride through fails due to the tripping of G18-115-GEN10 and G18-115-GEN20 units. No cascading was observed and the issue was localised. Model tuning is recommended. |  |  | Generator relays were disabled for the following generators: 587953 [G16-119-GEN10.6900], 587958 [G16-119-GEN20.6900], 761232 [G17-150GEN1 0.6600], 763841 [G19-052-GEN20.6000], 763959 [G19-067-GEN10.7200]
04 - Southeast | 25W | Transfer | Group4_Fault_0830_P1 | 3 phase fault on WWRDEHV7 (515375) 345 kV Bus a. Apply Fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from WWRDEHV7 (515375) 345 kV Bus to DGRASSE7 (515852) 345 kV Bus CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Low voltage ride through fails due to the tripping of G18-115-GEN10 and G18-115-GEN20 units. No cascading was observed and the issue was localised. Model tuning is recommended.
04 - Southeast | 25W | Transfer | Group4_Fault_0831_P1 | 3 phase fault on REDNGTN7 (515875) 345 kV Bus a. Apply Fault at the REDNGTN7 (515875) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from REDNGTN7 (515875) 345 kV Bus to WOODRNG7 (514715) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0832_P1 | 3 phase fault on HITCHLAND 6 (523095) 230 kV Bus a. Apply Fault at the HITCHLAND 6 (523095) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from HITCHLAND 6 (523095) 230 kV Bus to OCHILTREE 6 (523155) 230 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0833_P1 | 3 phase fault on HITCHLAND 6 (523095) 230 kV Bus a. Apply Fault at the HITCHLAND 6 (523095) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from HITCHLAND 6 (523095) 230 kV Bus to MOORE_CNTY 6 (523309) 230 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0834_P1 | 3 phase fault on HITCHLAND 6 (523095) 230 kV Bus a. Apply Fault at the HITCHLAND 6 (523095) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from HITCHLAND 6 (523095) 230 kV Bus to HITCHLAND 3 (523093) 115 kV Bus to HITCHLD_TR11 (523092) 13.2 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0835_P1 | 3 phase fault on HITCHLAND 6 (523095) 230 kV Bus a. Apply Fault at the HITCHLAND 6 (523095) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from HITCHLAND 6 (523095) 230 kV Bus to HITCHLAND 3 (523093) 115 kV Bus to HITCHLD_TR41 (523098) 13.2 kV Bus CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0836_P1 | 3 phase fault on BUFFALO7 (532782) 345 kV Bus a. Apply Fault at the BUFFALO7 (532782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from BUFFALO7 (532782) 345 kV Bus to WICHITA7 (532796) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0837_P1 | 3 phase fault on BUFFALO7 (532782) 345 kV Bus a. Apply Fault at the BUFFALO7 (532782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from BUFFALO7 (532782) 345 kV Bus to WICHITA7 (532796) 345 kV Bus CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0839_P1 | 3 phase fault on THISTLE4 (539804) 138 kV Bus a. Apply Fault at the THISTLE4 (539804) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from THISTLE4 (539804) 138 kV Bus to FLATRDG4 (539638) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0840_P1 | 3 phase fault on MOORLND4 (520999) 138 kV Bus a. Apply Fault at the MOORLND4 (520999) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from MOORLND4 (520999) 138 kV Bus to MOORLND2 (520995) 69 kV Bus to MLNDTERT (521180) 2.4 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0841_P1 | 3 phase fault on MOORLND4 (520999) 138 kV Bus a. Apply Fault at the MOORLND4 (520999) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from MOORLND4 (520999) 138 kV Bus to IODINE 4 (520957) 138 kV Bus CKT 1 b. 2. Trip branch from IODINE 4 (520957) 138 kV Bus to FTSUPLY4 (520920) 138 kV Bus CKT 1 b. 3. Drop Load 1 at IODINE 4 (520957) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0842_P1 | 3 phase fault on MOORLND4 (520999) 138 kV Bus a. Apply Fault at the MOORLND4 (520999) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from MOORLND4 (520999) 138 kV Bus to SEILING4 (520553) 138 kV Bus CKT 1 b. 2. Trip branch from SEILING4 (520553) 138 kV Bus to TALOGA 4 (521065) 138 kV Bus CKT 1 b. 3. Drop Load 1 at SEILING4 (520553) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0843_P1 | 3 phase fault on MOORLND4 (520999) 138 kV Bus a. Apply Fault at the MOORLND4 (520999) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from MOORLND4 (520999) 138 kV Bus to ASPEN 4 (520462) 138 kV Bus CKT 1 b. 2. Trip branch from ASPEN 4 (520462) 138 kV Bus to BEARCAT4 (520500) 138 kV Bus CKT 1 b. 3. Trip branch from BEARCAT4 (520500) 138 kV Bus to NINMLTP4 (521128) 138 kV Bus CKT 1 b. 4. Drop Load 1 at ASPEN 4 (520462) 138 kV Bus b. 5. Drop Load 1 at BEARCAT4 (520500) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0844_P1 | 3 phase fault on MOORLND4 (520999) 138 kV Bus a. Apply Fault at the MOORLND4 (520999) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from MOORLND4 (520999) 138 kV Bus to PIC4 (520425) 138 kV Bus CKT 1 b. 2. Trip branch from PIC4 (520425) 138 kV Bus to CDRDLTP4 (520848) 138 kV Bus CKT 1 b. 3. Drop Load 1 at PIC4 (520425) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0845_P1 | 3 phase fault on MOORLND4 (520999) 138 kV Bus a. Apply Fault at the MOORLND4 (520999) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from MOORLND4 (520999) 138 kV Bus to GLASMTN4 (514788) 138 kV Bus CKT 1 b. 2. Trip branch from GLASMTN4 (514788) 138 kV Bus to CLEOCOR4 (514778) 138 kV Bus CKT 1 b. 3. Drop Load 1 at GLASMTN4 (514788) 138 kV Bus b. 4. Drop Load 2 at GLASMTN4 (514788) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 516022 [SUNDCG11 0.6900]
04 - Southeast | 25W | Transfer | Group4_Fault_0846_P1 | 3 phase fault on TUCO_INT 7 (525832) 345 kV Bus a. Apply Fault at the TUCO_INT 7 (525832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from TUCO_INT 7 (525832) 345 kV Bus to YOAKUM_345 (526936) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 763084 [G18-073-GEN20.6600], 763090 [G18-073-GEN10.6600]
04 - Southeast | 25W | Transfer | Group4_Fault_0847_P1 | 3 phase fault on TUCO_INT 7 (525832) 345 kV Bus a. Apply Fault at the TUCO_INT 7 (525832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from TUCO_INT 7 (525832) 345 kV Bus to TUCO_INT 6 (525830) 230 kV Bus to TUCO_TR1 1 (525824) 13.2 kV Bus CKT 1 b. 2. Drop Shunt 1 at TUCO_TR1 1 (525824) 13.2 kV Bus1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 763084 [G18-073-GEN20.6600], 763090 [G18-073-GEN10.6600]
04 - Southeast | 25W | Transfer | Group4_Fault_0848_P1 | 3 phase fault on TUCO_INT 7 (525832) 345 kV Bus a. Apply Fault at the TUCO_INT 7 (525832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from TUCO_INT 7 (525832) 345 kV Bus to TUCO_INT 6 (525830) 230 kV Bus to TUCO_TR2 1 (525825) 13.2 kV Bus CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 763084 [G18-073-GEN20.6600], 763090 [G18-073-GEN10.6600]
04 - Southeast | 25W | Transfer | Group4_Fault_0849_P1 | 3 phase fault on ELKCITY6 (511490) 230 kV Bus a. Apply Fault at the ELKCITY6 (511490) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from ELKCITY6 (511490) 230 kV Bus to ELKCTY-4 (511458) 138 kV Bus to ELKC2-1 (511482) 13.8 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0850_P1 | 3 phase fault on SWEETWT6 (511541) 230 kV Bus a. Apply Fault at the SWEETWT6 (511541) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from SWEETWT6 (511541) 230 kV Bus to STLN-DEMARC6 (523779) 230 kV Bus CKT 1 b. 2. Trip branch from STLN-DEMARC6 (523779) 230 kV Bus to WHEELER 6 (523777) 230 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 763346 [G18-117-GEN20.6000], 763541 [G19-013-GEN10.7200], 763948 [G19-066-GEN10.7200]
04 - Southeast | 25W | Transfer | Group4_Fault_0854_P1 | 3 phase fault on LAMAR7 (599950) 345 kV Bus a. Apply Fault at the LAMAR7 (599950) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from LAMAR7 (599950) 345 kV Bus to G18-030-TAP (762662) 345 kV Bus CKT 1 b. 2. Drop Load 1 at LAMAR7 (599950) 345 kV Bus b. 3. Drop Shunt 1 at LAMAR7 (599950) 345 kV Bus1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0855_P1 | 3 phase fault on WHEELER 3 (523776) 115 kV Bus a. Apply Fault at the WHEELER 3 (523776) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from WHEELER 3 (523776) 115 kV Bus to COBRN_CREEK3 (523772) 115 kV Bus CKT 1 b. 2. Drop Load 1 at COBRN_CREEK3 (523772) 115 kV Bus b. 3. Drop Load 1 at COBRN_CREEK3 (523772) 115 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0856_P1 | 3 phase fault on WHEELER 3 (523776) 115 kV Bus a. Apply Fault at the WHEELER 3 (523776) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from WHEELER 3 (523776) 115 kV Bus to HOWARD 3 (523797) 115 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0857_P1 | 3 phase fault on NICHOLS 6 (524044) 230 kV Bus a. Apply Fault at the NICHOLS 6 (524044) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from NICHOLS 6 (524044) 230 kV Bus to NICHOLS 3 (524043) 115 kV Bus to NICHOLS_TR11 (524041) 13.2 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0858_P1 | 3 phase fault on NICHOLS 6 (524044) 230 kV Bus a. Apply Fault at the NICHOLS 6 (524044) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from NICHOLS 6 (524044) 230 kV Bus to NICHOLS 3 (524043) 115 kV Bus to NICHOLS_TR21 (524042) 13.2 kV Bus CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0859_P1 | 3 phase fault on NICHOLS 6 (524044) 230 kV Bus a. Apply Fault at the NICHOLS 6 (524044) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from NICHOLS 6 (524044) 230 kV Bus to HUTCHISON 6 (523551) 230 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0860_P1 | 3 phase fault on NICHOLS 6 (524044) 230 kV Bus a. Apply Fault at the NICHOLS 6 (524044) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from NICHOLS 6 (524044) 230 kV Bus to AMA_SOUTH 6 (524415) 230 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0861_P1 | 3 phase fault on NICHOLS 6 (524044) 230 kV Bus a. Apply Fault at the NICHOLS 6 (524044) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from NICHOLS 6 (524044) 230 kV Bus to HARRNG_MID 6 (523978) 230 kV Bus CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0862_P1 | 3 phase fault on NICHOLS 6 (524044) 230 kV Bus a. Apply Fault at the NICHOLS 6 (524044) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from NICHOLS 6 (524044) 230 kV Bus to HARRNG_WST 6 (523977) 230 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0863_P1 | 3 phase fault on GRAPEVINE 3 (523770) 115 kV Bus a. Apply Fault at the GRAPEVINE 3 (523770) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from GRAPEVINE 3 (523770) 115 kV Bus to BOWERS 3 (523748) 115 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0864_P1 | 3 phase fault on GRAPEVINE 3 (523770) 115 kV Bus a. Apply Fault at the GRAPEVINE 3 (523770) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from GRAPEVINE 3 (523770) 115 kV Bus to KIRBY 3 (524088) 115 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0865_P1 | 3 phase fault on HUTCHISON 6 (523551) 230 kV Bus a. Apply Fault at the HUTCHISON 6 (523551) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from HUTCHISON 6 (523551) 230 kV Bus to HUTCH_N 3 (523544) 115 kV Bus to HUTCH_TR1N 1 (523540) 13.2 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0866_P1 | 3 phase fault on HUTCHISON 6 (523551) 230 kV Bus a. Apply Fault at the HUTCHISON 6 (523551) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from HUTCHISON 6 (523551) 230 kV Bus to HUTCH_S 3 (523546) 115 kV Bus to HUTCH_TR2S 1 (523541) 13.2 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0867_P1 | 3 phase fault on HARRNG_WST 6 (523977) 230 kV Bus a. Apply Fault at the HARRNG_WST 6 (523977) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from HARRNG_WST 6 (523977) 230 kV Bus to ROLLHILLS 6 (524010) 230 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0868_P1 | 3 phase fault on HARRNG_WST 6 (523977) 230 kV Bus a. Apply Fault at the HARRNG_WST 6 (523977) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from HARRNG_WST 6 (523977) 230 kV Bus to EAST_PLANT 6 (524163) 230 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0869_P1 | 3 phase fault on HARRNG_WST 6 (523977) 230 kV Bus a. Apply Fault at the HARRNG_WST 6 (523977) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from HARRNG_WST 6 (523977) 230 kV Bus to HARRNG_MID 6 (523978) 230 kV Bus CKT @1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0870_P1 | 3 phase fault on HARRNG_MID 6 (523978) 230 kV Bus a. Apply Fault at the HARRNG_MID 6 (523978) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from HARRNG_MID 6 (523978) 230 kV Bus to HARRNG_EST 6 (523979) 230 kV Bus CKT @1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0871_P1 | 3 phase fault on HARRNG_MID 6 (523978) 230 kV Bus a. Apply Fault at the HARRNG_MID 6 (523978) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from HARRNG_MID 6 (523978) 230 kV Bus to RANDALL 6 (524365) 230 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0872_P1 | 3 phase fault on HARRNG_EST 6 (523979) 230 kV Bus a. Apply Fault at the HARRNG_EST 6 (523979) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from HARRNG_EST 6 (523979) 230 kV Bus to POTTER_CO 6 (523959) 230 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0873_P1 | 3 phase fault on POTTER_CO 6 (523959) 230 kV Bus a. Apply Fault at the POTTER_CO 6 (523959) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from POTTER_CO 6 (523959) 230 kV Bus to ROLLHILLS 6 (524010) 230 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0874_P1 | 3 phase fault on POTTER_CO 6 (523959) 230 kV Bus a. Apply Fault at the POTTER_CO 6 (523959) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from POTTER_CO 6 (523959) 230 kV Bus to NEWHART 6 (525461) 230 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0875_P1 | 3 phase fault on POTTER_CO 6 (523959) 230 kV Bus a. Apply Fault at the POTTER_CO 6 (523959) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from POTTER_CO 6 (523959) 230 kV Bus to BUSHLAND 6 (524267) 230 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0876_P1 | 3 phase fault on POTTER_CO 6 (523959) 230 kV Bus a. Apply Fault at the POTTER_CO 6 (523959) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from POTTER_CO 6 (523959) 230 kV Bus to CHAN+TASCOS6 (523869) 230 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0877_P1 | 3 phase fault on POTTER_CO 6 (523959) 230 kV Bus a. Apply Fault at the POTTER_CO 6 (523959) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from POTTER_CO 6 (523959) 230 kV Bus to MCDWL_CREEK6 (523323) 230 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0878_P1 | 3 phase fault on NICHOLS 3 (524043) 115 kV Bus a. Apply Fault at the NICHOLS 3 (524043) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from NICHOLS 3 (524043) 115 kV Bus to FAIN 3 (523339) 115 kV Bus CKT 1 b. 2. Trip branch from FAIN 3 (523339) 115 kV Bus to MCDWL_CREEK3 (523322) 115 kV Bus CKT 1 b. 3. Drop Load 1 at FAIN 3 (523339) 115 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0879_P1 | 3 phase fault on NICHOLS 3 (524043) 115 kV Bus a. Apply Fault at the NICHOLS 3 (524043) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from NICHOLS 3 (524043) 115 kV Bus to ASARCO 3 (524016) 115 kV Bus CKT 1 b. 2. Drop Load 1 at ASARCO 3 (524016) 115 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0880_P1 | 3 phase fault on NICHOLS 3 (524043) 115 kV Bus a. Apply Fault at the NICHOLS 3 (524043) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from NICHOLS 3 (524043) 115 kV Bus to ASARCO_TP 3 (524018) 115 kV Bus CKT 1 b. 2. Trip branch from ASARCO_TP 3 (524018) 115 kV Bus to HIGHLAND_TP3 (523931) 115 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0881_P1 | 3 phase fault on KIRBY 3 (524088) 115 kV Bus a. Apply Fault at the KIRBY 3 (524088) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from KIRBY 3 (524088) 115 kV Bus to MCCLELLAN 3 (523804) 115 kV Bus CKT 1 b. 2. Trip branch from MCCLELLAN 3 (523804) 115 kV Bus to MCLEAN 3 (523811) 115 kV Bus CKT 1 b. 3. Trip branch from MCLEAN 3 (523811) 115 kV Bus to SHAM 3WT (512107) 115 kV Bus CKT 1 b. 4. Drop Load 1 at MCCLELLAN 3 (523804) 115 kV Bus b. 5. Drop Load 1 at MCLEAN 3 (523811) 115 kV Bus b. 6. Drop Load D1 at MCLEAN 3 (523811) 115 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0882_P1 | 3 phase fault on HUTCH_N 3 (523544) 115 kV Bus a. Apply Fault at the HUTCH_N 3 (523544) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from HUTCH_N 3 (523544) 115 kV Bus to CAMX/AGR TP3 (523485) 115 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0883_P1 | 3 phase fault on HUTCH_N 3 (523544) 115 kV Bus a. Apply Fault at the HUTCH_N 3 (523544) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from HUTCH_N 3 (523544) 115 kV Bus to HUTCH_S 3 (523546) 115 kV Bus CKT @1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0884_P1 | 3 phase fault on EAST_PLANT 3 (524162) 115 kV Bus a. Apply Fault at the EAST_PLANT 3 (524162) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from EAST_PLANT 3 (524162) 115 kV Bus to HASTINGS 3 (524136) 115 kV Bus CKT 1 b. 2. Trip branch from HASTINGS 3 (524136) 115 kV Bus to ROLLHILLS 3 (524007) 115 kV Bus CKT 1 b. 3. Drop Load 1 at HASTINGS 3 (524136) 115 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0885_P1 | 3 phase fault on EAST_PLANT 3 (524162) 115 kV Bus a. Apply Fault at the EAST_PLANT 3 (524162) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from EAST_PLANT 3 (524162) 115 kV Bus to PIERCE_TP 3 (524185) 115 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0886_P1 | 3 phase fault on CHAN+TASCOS6 (523869) 230 kV Bus a. Apply Fault at the CHAN+TASCOS6 (523869) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from CHAN+TASCOS6 (523869) 230 kV Bus to XIT_INTG 6 (523221) 230 kV Bus CKT 1 b. 2. Trip three winding transformer from XIT_INTG 6 (523221) 230 kV Bus to XIT_INTG 3 (523220) 115 kV Bus to XIT_INTG TR1 (523219) 13.2 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0887_P1 | 3 phase fault on CAMX/AGR TP3 (523485) 115 kV Bus a. Apply Fault at the CAMX/AGR TP3 (523485) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from CAMX/AGR TP3 (523485) 115 kV Bus to CAMEX/AGRM 3 (523486) 115 kV Bus CKT 1 b. 2. Drop Load 1 at CAMEX/AGRM 3 (523486) 115 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0888_P1 | 3 phase fault on BLKHAWK_E 3 (523346) 115 kV Bus a. Apply Fault at the BLKHAWK_E 3 (523346) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from BLKHAWK_E 3 (523346) 115 kV Bus to BLKHAWK_W 3 (523344) 115 kV Bus CKT @1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0889_P1 | 3 phase fault on EAST_PLANT 3 (524162) 115 kV Bus a. Apply Fault at the EAST_PLANT 3 (524162) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from EAST_PLANT 3 (524162) 115 kV Bus to HASTINGS 3 (524136) 115 kV Bus CKT 1 b. 2. Trip branch from HASTINGS 3 (524136) 115 kV Bus to ROLLHILLS 3 (524007) 115 kV Bus CKT 1 b. 3. Drop Load 1 at HASTINGS 3 (524136) 115 kV Bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0890_P1 | 3 phase fault on WWRDEHV4 (515376) 138 kV Bus a. Apply Fault at the WWRDEHV4 (515376) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from WWRDEHV4 (515376) 138 kV Bus to IODINE-4 (514796) 138 kV Bus CKT 1 b. 2. Trip branch from IODINE-4 (514796) 138 kV Bus to REDCLFT4 (515533) 138 kV Bus CKT 1 b. 3. Drop Load 1 at IODINE-4 (514796) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0891_P4 | a. Apply single phase fault at MOORLND4 (520999) 138 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from MOORLND4 (520999) 138 kV to PIC4 (520425) 138 kV CKT 1 b. 2. Trip branch from PIC4 (520425) 138 kV to CDRDLTP4 (520848) 138 kV CKT 1 b. 3. Trip branch from CDRDLTP4 (520848) 138 kV to CEDRDAL4 (520507) 138 kV CKT 1 b. 4. Trip branch from CDRDLTP4 (520848) 138 kV to OKEENE 4 (521016) 138 kV CKT 1 b. 5. Trip branch from MOORLND4 (520999) 138 kV to ASPEN 4 (520462) 138 kV CKT 1 b. 6. Trip branch from ASPEN 4 (520462) 138 kV to BEARCAT4 (520500) 138 kV CKT 1 b. 7. Trip branch from BEARCAT4 (520500) 138 kV to NINMLTP4 (521128) 138 kV CKT 1 b. 8. Trip branch from NINMLTP4 (521128) 138 kV to NINMILE4 (520492) 138 kV CKT 1 b. 9. Trip branch from NINMLTP4 (521128) 138 kV to MORWODS4 (521001) 138 kV CKT 1 b. 10. Drop Load 1 CEDRDAL4 (520507) 138 kV b. 11. Drop Load 1 PIC4 (520425) 138 kV b. 12. Drop Load 1 ASPEN 4 (520462) 138 kV b. 13. Drop Load 1 BEARCAT4 (520500) 138 kV b. 14. Drop Load 1 NINMILE4 (520492) 138 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0892_P1 | 3 phase fault on DGRASSE4 (515853) 138 kV Bus a. Apply Fault at the DGRASSE4 (515853) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from DGRASSE4 (515853) 138 kV Bus to KNOBHIL4 (514795) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0893_P1 | 3 phase fault on ROSEVLY4 (520436) 138 kV Bus a. Apply Fault at the ROSEVLY4 (520436) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from ROSEVLY4 (520436) 138 kV Bus to AVARD 4 (520601) 138 kV Bus CKT 1 b. 2. Drop Load 1 at AVARD 4 (520601) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0894_P1 | 3 phase fault on NOELSW 4 (520430) 138 kV Bus a. Apply Fault at the NOELSW 4 (520430) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from NOELSW 4 (520430) 138 kV Bus to ROSEVLY4 (520436) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0895_P1 | 3 phase fault on MOORLND4 (520999) 138 kV Bus a. Apply Fault at the MOORLND4 (520999) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from MOORLND4 (520999) 138 kV Bus to GLASMTN4 (514788) 138 kV Bus CKT 1 b. 2. Trip branch from GLASMTN4 (514788) 138 kV Bus to CLEOCOR4 (514778) 138 kV Bus CKT 1 b. 3. Drop Load 1 at GLASMTN4 (514788) 138 kV Bus b. 4. Drop Load 2 at GLASMTN4 (514788) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 516022 [SUNDCG11 0.6900]
04 - Southeast | 25W | Transfer | Group4_Fault_0896_P1 | 3 phase fault on MOORLND4 (520999) 138 kV Bus a. Apply Fault at the MOORLND4 (520999) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from MOORLND4 (520999) 138 kV Bus to WINDFRM4 (515785) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0897_P1 | 3 phase fault on DGRASSE4 (515853) 138 kV Bus a. Apply Fault at the DGRASSE4 (515853) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from DGRASSE4 (515853) 138 kV Bus to ROSEVLY4 (520436) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0898_P1 | 3 phase fault on WOODWRD4 (514785) 138 kV Bus a. Apply Fault at the WOODWRD4 (514785) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from WOODWRD4 (514785) 138 kV Bus to WINDFRM4 (515785) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0899_P1 | 3 phase fault on KNOBHIL2 (514794) 69 kV Bus a. Apply Fault at the KNOBHIL2 (514794) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from KNOBHIL2 (514794) 69 kV Bus to ALVAOGE2 (514792) 69 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0900_P1 | 3 phase fault on KNOBHIL2 (514794) 69 kV Bus a. Apply Fault at the KNOBHIL2 (514794) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from KNOBHIL2 (514794) 69 kV Bus to CZYCRVT2 (515560) 69 kV Bus CKT 1 b. 2. Trip branch from CZYCRVT2 (515560) 69 kV Bus to SALINE 2 (514716) 69 kV Bus CKT 1 b. 3. Trip branch from SALINE 2 (514716) 69 kV Bus to HELENAT2 (515371) 69 kV Bus CKT 1 b. 4. Drop Load 1 at CZYCRVT2 (515560) 69 kV Bus b. 5. Drop Shunt 1 at CZYCRVT2 (515560) 69 kV Bus1 b. 6. Drop Load 1 at SALINE 2 (514716) 69 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0901_P1 | 3 phase fault on MOORLND2 (520995) 69 kV Bus a. Apply Fault at the MOORLND2 (520995) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from MOORLND2 (520995) 69 kV Bus to CRTSJCT2 (521197) 69 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0902_P1 | 3 phase fault on DGRASSE4 (515853) 138 kV Bus a. Apply Fault at the DGRASSE4 (515853) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from DGRASSE4 (515853) 138 kV Bus to MOORLND4 (520999) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0903_P1 | 3 phase fault on WOODWRD4 (514785) 138 kV Bus a. Apply Fault at the WOODWRD4 (514785) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from WOODWRD4 (514785) 138 kV Bus to WODWRD 2 (514782) 69 kV Bus to WOODWR21 (515771) 13.2 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0904_P1 | 3 phase fault on NINMLTP4 (521128) 138 kV Bus a. Apply Fault at the NINMLTP4 (521128) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from NINMLTP4 (521128) 138 kV Bus to MORWODS4 (521001) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0905_P1 | 3 phase fault on NINMLTP4 (521128) 138 kV Bus a. Apply Fault at the NINMLTP4 (521128) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from NINMLTP4 (521128) 138 kV Bus to NINMILE4 (520492) 138 kV Bus CKT 1 b. 2. Drop Load 1 at NINMILE4 (520492) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0906_P1 | 3 phase fault on CRTSJCT2 (521197) 69 kV Bus a. Apply Fault at the CRTSJCT2 (521197) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from CRTSJCT2 (521197) 69 kV Bus to WOODWRD2 (521096) 69 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0907_P1 | 3 phase fault on CRTSJCT2 (521197) 69 kV Bus a. Apply Fault at the CRTSJCT2 (521197) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from CRTSJCT2 (521197) 69 kV Bus to CURTIS 2 (520480) 69 kV Bus CKT 1 b. 2. Drop Load 1 at CURTIS 2 (520480) 69 kV Bus b. 3. Drop Load 2 at CURTIS 2 (520480) 69 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0908_P1 | 3 phase fault on ALVAOGE2 (514792) 69 kV Bus a. Apply Fault at the ALVAOGE2 (514792) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from ALVAOGE2 (514792) 69 kV Bus to ALVA 2 (520806) 69 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0909_P1 | 3 phase fault on ALVAOGE2 (514792) 69 kV Bus a. Apply Fault at the ALVAOGE2 (514792) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from ALVAOGE2 (514792) 69 kV Bus to ALINETP2 (515803) 69 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0910_P1 | 3 phase fault on NOELSW 4 (520430) 138 kV Bus a. Apply Fault at the NOELSW 4 (520430) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from NOELSW 4 (520430) 138 kV Bus to KNOBHIL4 (514795) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0911_P1 | 3 phase fault on CLEOCOR4 (514778) 138 kV Bus a. Apply Fault at the CLEOCOR4 (514778) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from CLEOCOR4 (514778) 138 kV Bus to CLEOPLT4 (515562) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 516022 [SUNDCG11 0.6900]
04 - Southeast | 25W | Transfer | Group4_Fault_0912_P1 | 3 phase fault on CLEOCOR4 (514778) 138 kV Bus a. Apply Fault at the CLEOCOR4 (514778) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from CLEOCOR4 (514778) 138 kV Bus to CLEOCOR2 (514777) 69 kV Bus to CLEOCOR1 (515716) 13.8 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 516022 [SUNDCG11 0.6900]
04 - Southeast | 25W | Transfer | Group4_Fault_0913_P1 | 3 phase fault on CDRDLTP4 (520848) 138 kV Bus a. Apply Fault at the CDRDLTP4 (520848) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from CDRDLTP4 (520848) 138 kV Bus to OKEENE 4 (521016) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0914_P1 | 3 phase fault on CDRDLTP4 (520848) 138 kV Bus a. Apply Fault at the CDRDLTP4 (520848) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from CDRDLTP4 (520848) 138 kV Bus to CEDRDAL4 (520507) 138 kV Bus CKT 1 b. 2. Drop Load 1 at CEDRDAL4 (520507) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0915_P1 | 3 phase fault on TALOGA 4 (521065) 138 kV Bus a. Apply Fault at the TALOGA 4 (521065) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from TALOGA 4 (521065) 138 kV Bus to TALOGA 2 (521064) 69 kV Bus to TLGTERT (521178) 13.8 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0916_P1 | 3 phase fault on TALOGA 4 (521065) 138 kV Bus a. Apply Fault at the TALOGA 4 (521065) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from TALOGA 4 (521065) 138 kV Bus to DEWEY 4 (514787) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0917_P1 | 3 phase fault on FTSUPLY4 (520920) 138 kV Bus a. Apply Fault at the FTSUPLY4 (520920) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from FTSUPLY4 (520920) 138 kV Bus to FTSUPLY2 (520919) 69 kV Bus to FTSUPTERT (521170) 13.8 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0918_P1 | 3 phase fault on FTSUPLY4 (520920) 138 kV Bus a. Apply Fault at the FTSUPLY4 (520920) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from FTSUPLY4 (520920) 138 kV Bus to FTSUPLY2 (520919) 69 kV Bus to FTSUPTERTB (521182) 13.8 kV Bus CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0919_P1 | 3 phase fault on NOELSW 4 (520430) 138 kV Bus a. Apply Fault at the NOELSW 4 (520430) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from NOELSW 4 (520430) 138 kV Bus to KNOBHIL4 (514795) 138 kV Bus CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0920_P1 | 3 phase fault on KNOBHIL4 (514795) 138 kV Bus a. Apply Fault at the KNOBHIL4 (514795) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from KNOBHIL4 (514795) 138 kV Bus to KNOBHIL2 (514794) 69 kV Bus to KNOBHIL1 (515732) 13.2 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0921_P1 | 3 phase fault on CLARKCOUNTY7 (539800) 345 kV Bus a. Apply Fault at the CLARKCOUNTY7 (539800) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from CLARKCOUNTY7 (539800) 345 kV Bus to SPERVIL7 (531469) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 763895 [G19-058-GEN20.6000]
04 - Southeast | 25W | Transfer | Group4_Fault_0922_P1 | 3 phase fault on WODWRD 2 (514782) 69 kV Bus a. Apply Fault at the WODWRD 2 (514782) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from WODWRD 2 (514782) 69 kV Bus to NEWGRTP2 (514776) 69 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0923_P1 | 3 phase fault on WODWRD 2 (514782) 69 kV Bus a. Apply Fault at the WODWRD 2 (514782) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from WODWRD 2 (514782) 69 kV Bus to WOODWRD2 (521096) 69 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0924_P1 | 3 phase fault on WODWRD 2 (514782) 69 kV Bus a. Apply Fault at the WODWRD 2 (514782) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from WODWRD 2 (514782) 69 kV Bus to CEDARAV2 (514781) 69 kV Bus CKT 1 b. 2. Trip branch from CEDARAV2 (514781) 69 kV Bus to TANGRTP2 (514775) 69 kV Bus CKT 1 b. 3. Drop Load 1 at CEDARAV2 (514781) 69 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0925_P1 | 3 phase fault on NOELSW 4 (520430) 138 kV Bus a. Apply Fault at the NOELSW 4 (520430) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from NOELSW 4 (520430) 138 kV Bus to SALTPLN4 (520437) 138 kV Bus CKT 1 b. 2. Trip branch from SALTPLN4 (520437) 138 kV Bus to CHRKCTY4 (520431) 138 kV Bus CKT 1 b. 3. Trip branch from CHRKCTY4 (520431) 138 kV Bus to DRIFTWD4 (521200) 138 kV Bus CKT 1 b. 4. Drop Load 1 at SALTPLN4 (520437) 138 kV Bus b. 5. Drop Load 2 at SALTPLN4 (520437) 138 kV Bus b. 6. Drop Load 1 at CHRKCTY4 (520431) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0926_P1 | 3 phase fault on MORWODS4 (521001) 138 kV Bus a. Apply Fault at the MORWODS4 (521001) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from MORWODS4 (521001) 138 kV Bus to MORWOOD4 (521002) 138 kV Bus CKT 1 b. 2. Trip branch from MORWOOD4 (521002) 138 kV Bus to BRANTLEY4 (520832) 138 kV Bus CKT 1 b. 3. Trip branch from BRANTLEY4 (520832) 138 kV Bus to DURHAM 4 (520885) 138 kV Bus CKT 1 b. 4. Trip branch from DURHAM 4 (520885) 138 kV Bus to SWEETWR4 (521060) 138 kV Bus CKT 1 b. 5. Trip branch from SWEETWR4 (521060) 138 kV Bus to BULOJ4 (520402) 138 kV Bus CKT 1 b. 6. Trip branch from BULOJ4 (520402) 138 kV Bus to ERICK 4 (520903) 138 kV Bus CKT 1 b. 7. Trip branch from ERICK 4 (520903) 138 kV Bus to SAYRE--4 (511504) 138 kV Bus CKT 1 b. 8. Trip branch from SAYRE--4 (511504) 138 kV Bus to FALCNRD4 (511511) 138 kV Bus CKT 1 b. 9. Trip branch from FALCNRD4 (511511) 138 kV Bus to ELKCTY-4 (511458) 138 kV Bus CKT 1 b. 10. Drop Load 1 at BRANTLEY4 (520832) 138 kV Bus b. 11. Drop Load 1 at DURHAM 4 (520885) 138 kV Bus b. 12. Drop Load 1 at SWEETWR4 (521060) 138 kV Bus b. 13. Drop Load 1 at BULOJ4 (520402) 138 kV Bus b. 14. Drop Load 1 at ERICK 4 (520903) 138 kV Bus b. 15. Drop Load 1 at SAYRE--4 (511504) 138 kV Bus b. 16. Drop Load 1 at FALCNRD4 (511511) 138 kV Bus b. 17. Drop Shunt 1 at SAYRE--4 (511504) 138 kV Bus1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0927_P1 | 3 phase fault on MORWODS4 (521001) 138 kV Bus a. Apply Fault at the MORWODS4 (521001) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from MORWODS4 (521001) 138 kV Bus to ELLIS 4 (511561) 138 kV Bus CKT 1 b. 2. Trip branch from ELLIS 4 (511561) 138 kV Bus to CUSTER 4 (520459) 138 kV Bus CKT 1 b. 3. Trip branch from CUSTER 4 (520459) 138 kV Bus to REDHLSW4 (521116) 138 kV Bus CKT 1 b. 4. Drop Load 1 at ELLIS 4 (511561) 138 kV Bus b. 5. Drop Load 1 at CUSTER 4 (520459) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0928_P1 | 3 phase fault on MORWODS4 (521001) 138 kV Bus a. Apply Fault at the MORWODS4 (521001) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from MORWODS4 (521001) 138 kV Bus to MORWODS2 (521000) 69 kV Bus to MRWDTERT (521172) 13.8 kV Bus CKT 1 b. 2. Trip branch from MORWODS2 (521000) 69 kV Bus to BTLRJCT2 (520457) 69 kV Bus CKT 1 b. 3. Trip branch from BTLRJCT2 (520457) 69 kV Bus to BUTLER 2 (520458) 69 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0929_P1 | 3 phase fault on WOODWRD2 (521096) 69 kV Bus a. Apply Fault at the WOODWRD2 (521096) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from WOODWRD2 (521096) 69 kV Bus to FARGOJCT2 (521196) 69 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0930_P1 | 3 phase fault on WOODWRD2 (521096) 69 kV Bus a. Apply Fault at the WOODWRD2 (521096) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from WOODWRD2 (521096) 69 kV Bus to VICI 2 (521082) 69 kV Bus CKT 1 b. 2. Trip branch from VICI 2 (521082) 69 kV Bus to TALOGA 2 (521064) 69 kV Bus CKT 1 b. 3. Drop Load 1 at VICI 2 (521082) 69 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0931_P1 | 3 phase fault on DRIFTWD4 (521200) 138 kV Bus a. Apply Fault at the DRIFTWD4 (521200) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from DRIFTWD4 (521200) 138 kV Bus to DRIFTWD2 (521201) 69 kV Bus to DRFTWDTERT (521185) 13.8 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0932_P1 | 3 phase fault on DRIFTWD4 (521200) 138 kV Bus a. Apply Fault at the DRIFTWD4 (521200) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from DRIFTWD4 (521200) 138 kV Bus to BYRONTP4 (520432) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0933_P1 | 3 phase fault on CLEOPLT4 (515562) 138 kV Bus a. Apply Fault at the CLEOPLT4 (515562) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from CLEOPLT4 (515562) 138 kV Bus to CLEO PL4 (515553) 138 kV Bus CKT 1 b. 2. Drop Load 1 at CLEO PL4 (515553) 138 kV Bus b. 3. Drop Shunt 1 at CLEO PL4 (515553) 138 kV Bus1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 516022 [SUNDCG11 0.6900]
04 - Southeast | 25W | Transfer | Group4_Fault_0934_P1 | 3 phase fault on CLEOPLT4 (515562) 138 kV Bus a. Apply Fault at the CLEOPLT4 (515562) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from CLEOPLT4 (515562) 138 kV Bus to MENOTAP4 (514789) 138 kV Bus CKT 1 b. 2. Trip branch from MENOTAP4 (514789) 138 kV Bus to IMO 4 (514790) 138 kV Bus CKT 1 b. 3. Drop Load 1 at MENOTAP4 (514789) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 516022 [SUNDCG11 0.6900]
04 - Southeast | 25W | Transfer | Group4_Fault_0935_P1 | 3 phase fault on NOELSW 4 (520430) 138 kV Bus a. Apply Fault at the NOELSW 4 (520430) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from NOELSW 4 (520430) 138 kV Bus to ROSEVLY4 (520436) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0936_P1 | 3 phase fault on ALINETP2 (515803) 69 kV Bus a. Apply Fault at the ALINETP2 (515803) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from ALINETP2 (515803) 69 kV Bus to ALINE 2 (514793) 69 kV Bus CKT 1 b. 2. Drop Load 1 at ALINE 2 (514793) 69 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0937_P1 | 3 phase fault on ALINETP2 (515803) 69 kV Bus a. Apply Fault at the ALINETP2 (515803) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from ALINETP2 (515803) 69 kV Bus to CLEOTP 2 (515804) 69 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0938_P1 | 3 phase fault on CLEOTP 2 (515804) 69 kV Bus a. Apply Fault at the CLEOTP 2 (515804) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from CLEOTP 2 (515804) 69 kV Bus to CLEOCOR2 (514777) 69 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0939_P1 | 3 phase fault on CLEOTP 2 (515804) 69 kV Bus a. Apply Fault at the CLEOTP 2 (515804) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from CLEOTP 2 (515804) 69 kV Bus to CLEO 2 (514791) 69 kV Bus CKT 1 b. 2. Drop Load 1 at CLEO 2 (514791) 69 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0940_P1 | 3 phase fault on DRIFTWD2 (521201) 69 kV Bus a. Apply Fault at the DRIFTWD2 (521201) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from DRIFTWD2 (521201) 69 kV Bus to HAZLTBJ2 (521202) 69 kV Bus CKT 1 b. 2. Trip branch from HAZLTBJ2 (521202) 69 kV Bus to MEDLDGE2 (522396) 69 kV Bus CKT 1 b. 3. Trip branch from MEDLDGE2 (522396) 69 kV Bus to HAZELTN2 (520937) 69 kV Bus CKT 1 b. 4. Drop Load 1 at MEDLDGE2 (522396) 69 kV Bus b. 5. Drop Load 1 at HAZELTN2 (520937) 69 kV Bus b. 6. Drop Shunt 1 at HAZELTN2 (520937) 69 kV Bus1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0941_P1 | 3 phase fault on DRIFTWD2 (521201) 69 kV Bus a. Apply Fault at the DRIFTWD2 (521201) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from DRIFTWD2 (521201) 69 kV Bus to HAZLTAJ2 (520938) 69 kV Bus CKT 1 b. 2. Trip branch from HAZLTAJ2 (520938) 69 kV Bus to BRLNGTN2 (520833) 69 kV Bus CKT 1 b. 3. Trip branch from BRLNGTN2 (520833) 69 kV Bus to CHEROKS2 (520851) 69 kV Bus CKT 1 b. 4. Drop Load 1 at BRLNGTN2 (520833) 69 kV Bus b. 5. Drop Load 2K at BRLNGTN2 (520833) 69 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0942_P1 | 3 phase fault on OU TAP 4 (514931) 138 kV Bus a. Apply Fault at the OU TAP 4 (514931) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from OU TAP 4 (514931) 138 kV Bus to WILKINS4 (514950) 138 kV Bus CKT 1 b. 2. Trip branch from WILKINS4 (514950) 138 kV Bus to OAKTRET4 (514930) 138 kV Bus CKT 1 b. 3. Trip branch from OAKTRET4 (514930) 138 kV Bus to SOONRTP4 (514949) 138 kV Bus CKT 1 b. 4. Drop Load 1 at WILKINS4 (514950) 138 kV Bus b. 5. Drop Load 1 at OAKTRET4 (514930) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0943_P1 | 3 phase fault on OU TAP 4 (514931) 138 kV Bus a. Apply Fault at the OU TAP 4 (514931) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from OU TAP 4 (514931) 138 kV Bus to OUBROOK4 (514903) 138 kV Bus CKT 1 b. 2. Drop Load 1 at OUBROOK4 (514903) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0944_P1 | 3 phase fault on QUAILCK4 (514851) 138 kV Bus a. Apply Fault at the QUAILCK4 (514851) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from QUAILCK4 (514851) 138 kV Bus to SKYLINE4 (514850) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0945_P1 | 3 phase fault on PENN 4 (514925) 138 kV Bus a. Apply Fault at the PENN 4 (514925) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from PENN 4 (514925) 138 kV Bus to WRAIRPT4 (514889) 138 kV Bus CKT 1 b. 2. Trip branch from WRAIRPT4 (514889) 138 kV Bus to 36&MER 4 (514888) 138 kV Bus CKT 1 b. 3. Drop Load 1 at WRAIRPT4 (514889) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0946_P1 | 3 phase fault on PENN 4 (514925) 138 kV Bus a. Apply Fault at the PENN 4 (514925) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from PENN 4 (514925) 138 kV Bus to SANTAFE4 (514926) 138 kV Bus CKT 1 b. 2. Trip branch from SANTAFE4 (514926) 138 kV Bus to OAKCRK 4 (514960) 138 kV Bus CKT 1 b. 3. Drop Load 1 at SANTAFE4 (514926) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0947_P1 | 3 phase fault on PENN 4 (514925) 138 kV Bus a. Apply Fault at the PENN 4 (514925) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from PENN 4 (514925) 138 kV Bus to PENN 2 (514924) 69 kV Bus to PENN 1 (515751) 13.2 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0948_P1 | 3 phase fault on CIMARON4 (514898) 138 kV Bus a. Apply Fault at the CIMARON4 (514898) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from CIMARON4 (514898) 138 kV Bus to TUTCONT4 (511425) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0949_P1 | 3 phase fault on CIMARON4 (514898) 138 kV Bus a. Apply Fault at the CIMARON4 (514898) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from CIMARON4 (514898) 138 kV Bus to EL-RENO4 (514819) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0950_P1 | 3 phase fault on CIMARON4 (514898) 138 kV Bus a. Apply Fault at the CIMARON4 (514898) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from CIMARON4 (514898) 138 kV Bus to JENSENT4 (514820) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0951_P1 | 3 phase fault on CIMARON4 (514898) 138 kV Bus a. Apply Fault at the CIMARON4 (514898) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from CIMARON4 (514898) 138 kV Bus to HAYMAKR4 (514863) 138 kV Bus CKT 1 b. 2. Trip branch from HAYMAKR4 (514863) 138 kV Bus to DVISION4 (514853) 138 kV Bus CKT 1 b. 3. Drop Load 1 at HAYMAKR4 (514863) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0952_P1 | 3 phase fault on CIMARON4 (514898) 138 kV Bus a. Apply Fault at the CIMARON4 (514898) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from CIMARON4 (514898) 138 kV Bus to SARA 4 (514895) 138 kV Bus CKT 1 b. 2. Trip branch from SARA 4 (514895) 138 kV Bus to MCCLAIN4 (514902) 138 kV Bus CKT 1 b. 3. Drop Load 1 at SARA 4 (514895) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0953_P1 | 3 phase fault on CIMARON4 (514898) 138 kV Bus a. Apply Fault at the CIMARON4 (514898) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from CIMARON4 (514898) 138 kV Bus to CZECHAL4 (514894) 138 kV Bus CKT 1 b. 2. Trip branch from CZECHAL4 (514894) 138 kV Bus to XEROX 4 (514893) 138 kV Bus CKT 1 b. 3. Trip branch from XEROX 4 (514893) 138 kV Bus to MORGAN 4 (514896) 138 kV Bus CKT 1 b. 4. Trip branch from MORGAN 4 (514896) 138 kV Bus to MUSTANG4 (514861) 138 kV Bus CKT 1 b. 5. Drop Load 1 at CZECHAL4 (514894) 138 kV Bus b. 6. Drop Load 1 at XEROX 4 (514893) 138 kV Bus b. 7. Drop Load 1 at MORGAN 4 (514896) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0954_P1 | 3 phase fault on NORTWST4 (514879) 138 kV Bus a. Apply Fault at the NORTWST4 (514879) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from NORTWST4 (514879) 138 kV Bus to BRADEN 4 (514854) 138 kV Bus CKT 1 b. 2. Trip branch from BRADEN 4 (514854) 138 kV Bus to SLVRLAK4 (514852) 138 kV Bus CKT 1 b. 3. Drop Load 1 at BRADEN 4 (514854) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Low voltage ride through fails due to the tripping of G18-115-GEN10 and G18-115-GEN20 units. No cascading was observed and the issue was localised. Model tuning is recommended.
04 - Southeast | 25W | Transfer | Group4_Fault_0955_P1 | 3 phase fault on NORTWST4 (514879) 138 kV Bus a. Apply Fault at the NORTWST4 (514879) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from NORTWST4 (514879) 138 kV Bus to PIEDMNT4 (514864) 138 kV Bus CKT 1 b. 2. Trip branch from PIEDMNT4 (514864) 138 kV Bus to RICHRDS4 (514862) 138 kV Bus CKT 1 b. 3. Trip branch from RICHRDS4 (514862) 138 kV Bus to DVISION4 (514853) 138 kV Bus CKT 1 b. 4. Drop Load 1 at PIEDMNT4 (514864) 138 kV Bus b. 5. Drop Load 1 at RICHRDS4 (514862) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Low voltage ride through fails due to the tripping of G18-115-GEN10 and G18-115-GEN20 units. No cascading was observed and the issue was localised. Model tuning is recommended.
04 - Southeast | 25W | Transfer | Group4_Fault_0956_P1 | 3 phase fault on NORTWST4 (514879) 138 kV Bus a. Apply Fault at the NORTWST4 (514879) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from NORTWST4 (514879) 138 kV Bus to LNEOAK 4 (514873) 138 kV Bus CKT 1 b. 2. Trip branch from LNEOAK 4 (514873) 138 kV Bus to QUAILCK4 (514851) 138 kV Bus CKT 1 b. 3. Drop Load 1 at LNEOAK 4 (514873) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Low voltage ride through fails due to the tripping of G18-115-GEN10 and G18-115-GEN20 units. No cascading was observed and the issue was localised. Model tuning is recommended.
04 - Southeast | 25W | Transfer | Group4_Fault_0957_P1 | 3 phase fault on PLVALLY4 (514929) 138 kV Bus a. Apply Fault at the PLVALLY4 (514929) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from PLVALLY4 (514929) 138 kV Bus to HOLLYWD4 (514953) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0958_P1 | 3 phase fault on PLVALLY4 (514929) 138 kV Bus a. Apply Fault at the PLVALLY4 (514929) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from PLVALLY4 (514929) 138 kV Bus to MCCLAIN4 (514902) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0959_P1 | 3 phase fault on PLVALLY4 (514929) 138 kV Bus a. Apply Fault at the PLVALLY4 (514929) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from PLVALLY4 (514929) 138 kV Bus to TURNER 4 (514992) 138 kV Bus CKT 1 b. 2. Trip branch from TURNER 4 (514992) 138 kV Bus to SOGATE 4 (514928) 138 kV Bus CKT 1 b. 3. Trip branch from SOGATE 4 (514928) 138 kV Bus to SW134TP4 (514876) 138 kV Bus CKT 1 b. 4. Drop Load 1 at TURNER 4 (514992) 138 kV Bus b. 5. Drop Load 1 at SOGATE 4 (514928) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0960_P1 | 3 phase fault on PLVALLY4 (514929) 138 kV Bus a. Apply Fault at the PLVALLY4 (514929) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from PLVALLY4 (514929) 138 kV Bus to CHERYCK4 (514957) 138 kV Bus CKT 1 b. 2. Trip branch from CHERYCK4 (514957) 138 kV Bus to BOYD 4 (514958) 138 kV Bus CKT 1 b. 3. Trip branch from BOYD 4 (514958) 138 kV Bus to CEDARLN4 (514948) 138 kV Bus CKT 1 b. 4. Drop Load 1 at CHERYCK4 (514957) 138 kV Bus b. 5. Drop Load 1 at BOYD 4 (514958) 138 kV Bus b. 6. Drop Shunt 1 at BOYD 4 (514958) 138 kV Bus1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0961_P1 | 3 phase fault on REDBUD 7 (514909) 345 kV Bus a. Apply Fault at the REDBUD 7 (514909) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from REDBUD 7 (514909) 345 kV Bus to R.S.S.-7 (509782) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Low voltage ride through fails due to the tripping of G18-115-GEN10 and G18-115-GEN20 units. No cascading was observed and the issue was localised. Model tuning is recommended.
04 - Southeast | 25W | Transfer | Group4_Fault_0962_P1 | 3 phase fault on HOLLYWD4 (514953) 138 kV Bus a. Apply Fault at the HOLLYWD4 (514953) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from HOLLYWD4 (514953) 138 kV Bus to MIDWEST4 (514946) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Low voltage ride through fails due to the tripping of G18-115-GEN10 and G18-115-GEN20 units. No cascading was observed and the issue was localised. Model tuning is recommended.
04 - Southeast | 25W | Transfer | Group4_Fault_0963_P1 | 3 phase fault on HOLLYWD4 (514953) 138 kV Bus a. Apply Fault at the HOLLYWD4 (514953) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from HOLLYWD4 (514953) 138 kV Bus to INDNHIL4 (514954) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Low voltage ride through fails due to the tripping of G18-115-GEN10 and G18-115-GEN20 units. No cascading was observed and the issue was localised. Model tuning is recommended.
04 - Southeast | 25W | Transfer | Group4_Fault_0964_P1 | 3 phase fault on HOLLYWD4 (514953) 138 kV Bus a. Apply Fault at the HOLLYWD4 (514953) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from HOLLYWD4 (514953) 138 kV Bus to STUBMAN4 (514952) 138 kV Bus CKT 1 b. 2. Trip branch from STUBMAN4 (514952) 138 kV Bus to MLENIUM4 (514932) 138 kV Bus CKT 1 b. 3. Trip branch from MLENIUM4 (514932) 138 kV Bus to OU TAP 4 (514931) 138 kV Bus CKT 1 b. 4. Drop Load 1 at STUBMAN4 (514952) 138 kV Bus b. 5. Drop Load 1 at MLENIUM4 (514932) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Low voltage ride through fails due to the tripping of G18-115-GEN10 and G18-115-GEN20 units. No cascading was observed and the issue was localised. Model tuning is recommended.
04 - Southeast | 25W | Transfer | Group4_Fault_0965_P1 | 3 phase fault on SLVRLAK4 (514852) 138 kV Bus a. Apply Fault at the SLVRLAK4 (514852) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from SLVRLAK4 (514852) 138 kV Bus to QUAILCK4 (514851) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0966_P1 | 3 phase fault on INDNHIL4 (514954) 138 kV Bus a. Apply Fault at the INDNHIL4 (514954) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from INDNHIL4 (514954) 138 kV Bus to WESTHSE4 (514904) 138 kV Bus CKT 1 b. 2. Drop Load 1 at WESTHSE4 (514904) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0967_P1 | 3 phase fault on INDNHIL4 (514954) 138 kV Bus a. Apply Fault at the INDNHIL4 (514954) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from INDNHIL4 (514954) 138 kV Bus to INDIANH4 (515380) 138 kV Bus CKT 1 b. 2. Trip branch from INDIANH4 (515380) 138 kV Bus to MOORE 4 (514955) 138 kV Bus CKT 1 b. 3. Trip branch from MOORE 4 (514955) 138 kV Bus to OAKCRK 4 (514960) 138 kV Bus CKT 1 b. 4. Drop Load 1 at INDIANH4 (515380) 138 kV Bus b. 5. Drop Load 1 at MOORE 4 (514955) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0968_P1 | 3 phase fault on DVISION4 (514853) 138 kV Bus a. Apply Fault at the DVISION4 (514853) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from DVISION4 (514853) 138 kV Bus to MUSTANG4 (514861) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0969_P1 | 3 phase fault on DVISION4 (514853) 138 kV Bus a. Apply Fault at the DVISION4 (514853) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from DVISION4 (514853) 138 kV Bus to LAKESID4 (514849) 138 kV Bus CKT 1 b. 2. Trip branch from LAKESID4 (514849) 138 kV Bus to HEFNER 4 (514848) 138 kV Bus CKT 1 b. 3. Drop Load 1 at LAKESID4 (514849) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0970_P1 | 3 phase fault on SW134TP4 (514876) 138 kV Bus a. Apply Fault at the SW134TP4 (514876) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from SW134TP4 (514876) 138 kV Bus to G17-152_TAP (914902) kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0971_P1 | 3 phase fault on SW134TP4 (514876) 138 kV Bus a. Apply Fault at the SW134TP4 (514876) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from SW134TP4 (514876) 138 kV Bus to WESTMOR4 (514887) 138 kV Bus CKT 1 b. 2. Trip branch from WESTMOR4 (514887) 138 kV Bus to PENN 4 (514925) 138 kV Bus CKT 1 b. 3. Drop Load 1 at WESTMOR4 (514887) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0972_P1 | 3 phase fault on TUTCONT4 (511425) 138 kV Bus a. Apply Fault at the TUTCONT4 (511425) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from TUTCONT4 (511425) 138 kV Bus to TUTTLE4 (511501) 138 kV Bus CKT 1 b. 2. Trip branch from TUTTLE4 (511501) 138 kV Bus to LEONARD4 (511575) 138 kV Bus CKT 1 b. 3. Drop Load 1 at TUTTLE4 (511501) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 511974 [REDBDPLNW0 0.6900]
04 - Southeast | 25W | Transfer | Group4_Fault_0973_P1 | 3 phase fault on TUTCONT4 (511425) 138 kV Bus a. Apply Fault at the TUTCONT4 (511425) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from TUTCONT4 (511425) 138 kV Bus to CEMRD_TP4 (511576) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 511974 [REDBDPLNW0 0.6900]
04 - Southeast | 25W | Transfer | Group4_Fault_0974_P1 | 3 phase fault on CEMRD_TP4 (511576) 138 kV Bus a. Apply Fault at the CEMRD_TP4 (511576) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from CEMRD_TP4 (511576) 138 kV Bus to T-CONCO4 (511424) 138 kV Bus CKT 1 b. 2. Drop Load 1 at T-CONCO4 (511424) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0975_P1 | 3 phase fault on CEMRD_TP4 (511576) 138 kV Bus a. Apply Fault at the CEMRD_TP4 (511576) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from CEMRD_TP4 (511576) 138 kV Bus to CMTRYRD4 (515864) 138 kV Bus CKT 1 b. 2. Drop Load 1 at CMTRYRD4 (515864) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0976_P1 | 3 phase fault on EL-RENO4 (514819) 138 kV Bus a. Apply Fault at the EL-RENO4 (514819) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from EL-RENO4 (514819) 138 kV Bus to JENSENT4 (514820) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0977_P1 | 3 phase fault on JENSENT4 (514820) 138 kV Bus a. Apply Fault at the JENSENT4 (514820) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from JENSENT4 (514820) 138 kV Bus to JENSEN 4 (514821) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0978_P1 | 3 phase fault on EL-RENO4 (514819) 138 kV Bus a. Apply Fault at the EL-RENO4 (514819) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from EL-RENO4 (514819) 138 kV Bus to OMEGA 4 (515962) 138 kV Bus CKT 1 b. 2. Trip branch from OMEGA 4 (515962) 138 kV Bus to ROMNOSE4 (514823) 138 kV Bus CKT 1 b. 3. Drop Load 1 at OMEGA 4 (515962) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0979_P1 | 3 phase fault on EL-RENO4 (514819) 138 kV Bus a. Apply Fault at the EL-RENO4 (514819) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from EL-RENO4 (514819) 138 kV Bus to ELRENO 2 (514818) 69 kV Bus to EL RENO1 (515722) 13.2 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0980_P1 | 3 phase fault on ARCADIA4 (514907) 138 kV Bus a. Apply Fault at the ARCADIA4 (514907) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from ARCADIA4 (514907) 138 kV Bus to JNSKAMO4 (514906) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0981_P1 | 3 phase fault on ARCADIA4 (514907) 138 kV Bus a. Apply Fault at the ARCADIA4 (514907) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from ARCADIA4 (514907) 138 kV Bus to RNDBARN4 (515461) 138 kV Bus CKT 1 b. 2. Trip branch from RNDBARN4 (515461) 138 kV Bus to BURGETT4 (514510) 138 kV Bus CKT 1 b. 3. Trip branch from BURGETT4 (514510) 138 kV Bus to DANFRTH4 (514833) 138 kV Bus CKT 1 b. 4. Drop Load 1 at RNDBARN4 (515461) 138 kV Bus b. 5. Drop Load 1 at BURGETT4 (514510) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0982_P1 | 3 phase fault on ARCADIA4 (514907) 138 kV Bus a. Apply Fault at the ARCADIA4 (514907) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from ARCADIA4 (514907) 138 kV Bus to LGARBER4 (515465) 138 kV Bus CKT 1 b. 2. Trip branch from LGARBER4 (515465) 138 kV Bus to CHTWOOD4 (514842) 138 kV Bus CKT 1 b. 3. Trip branch from CHTWOOD4 (514842) 138 kV Bus to JONESSB4 (515480) 138 kV Bus CKT 1 b. 4. Drop Load 1 at LGARBER4 (515465) 138 kV Bus b. 5. Drop Load 1 at CHTWOOD4 (514842) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0983_P1 | 3 phase fault on DRAPER 4 (514933) 138 kV Bus a. Apply Fault at the DRAPER 4 (514933) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from DRAPER 4 (514933) 138 kV Bus to BARNES 4 (515003) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0984_P1 | 3 phase fault on DRAPER 4 (514933) 138 kV Bus a. Apply Fault at the DRAPER 4 (514933) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from DRAPER 4 (514933) 138 kV Bus to SOONRTP4 (514949) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0985_P1 | 3 phase fault on DRAPER 4 (514933) 138 kV Bus a. Apply Fault at the DRAPER 4 (514933) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from DRAPER 4 (514933) 138 kV Bus to MIDWEST4 (514946) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0986_P1 | 3 phase fault on DRAPER 4 (514933) 138 kV Bus a. Apply Fault at the DRAPER 4 (514933) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from DRAPER 4 (514933) 138 kV Bus to GM 4 (514961) 138 kV Bus CKT 1 b. 2. Trip branch from GM 4 (514961) 138 kV Bus to AIRDEPT4 (515457) 138 kV Bus CKT 1 b. 3. Trip branch from AIRDEPT4 (515457) 138 kV Bus to WILDMRY4 (514984) 138 kV Bus CKT 1 b. 4. Trip branch from WILDMRY4 (514984) 138 kV Bus to OAKCRK 4 (514960) 138 kV Bus CKT 1 b. 5. Drop Load 1 at GM 4 (514961) 138 kV Bus b. 6. Drop Load 1 at AIRDEPT4 (515457) 138 kV Bus b. 7. Drop Load 1 at WILDMRY4 (514984) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0987_P1 | 3 phase fault on R.S.S.-7 (509782) 345 kV Bus a. Apply Fault at the R.S.S.-7 (509782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from R.S.S.-7 (509782) 345 kV Bus to PECANCK7 (515235) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0989_P1 | 3 phase fault on R.S.S.-7 (509782) 345 kV Bus a. Apply Fault at the R.S.S.-7 (509782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from R.S.S.-7 (509782) 345 kV Bus to RSS T1 4 (509773) 138 kV Bus to RSST1 T1 (509882) 13.8 kV Bus CKT 1 b. 2. Trip branch from RSS T1 4 (509773) 138 kV Bus to R.S.S.-4 (509783) 138 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0990_P1 | 3 phase fault on R.S.S.-7 (509782) 345 kV Bus a. Apply Fault at the R.S.S.-7 (509782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from R.S.S.-7 (509782) 345 kV Bus to RSS T2 4 (509875) 138 kV Bus to RSST2 T1 (509876) 13.8 kV Bus CKT 1 b. 2. Trip branch from RSS T2 4 (509875) 138 kV Bus to R.S.S.-4 (509783) 138 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0991_P1 | 3 phase fault on FRNKLNS4 (520917) 138 kV Bus a. Apply Fault at the FRNKLNS4 (520917) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from FRNKLNS4 (520917) 138 kV Bus to MIDWEST4 (514946) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Low voltage ride through fails due to the tripping of G18-115-GEN10 and G18-115-GEN20 units. No cascading was observed and the issue was localised. Model tuning is recommended.
04 - Southeast | 25W | Transfer | Group4_Fault_0992_P1 | 3 phase fault on MUSTANG4 (514861) 138 kV Bus a. Apply Fault at the MUSTANG4 (514861) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from MUSTANG4 (514861) 138 kV Bus to DAYTON 4 (514892) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0993_P1 | 3 phase fault on MUSTANG4 (514861) 138 kV Bus a. Apply Fault at the MUSTANG4 (514861) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from MUSTANG4 (514861) 138 kV Bus to SW 5TH 4 (514920) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0994_P1 | 3 phase fault on MUSTANG4 (514861) 138 kV Bus a. Apply Fault at the MUSTANG4 (514861) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from MUSTANG4 (514861) 138 kV Bus to COUNCIL4 (514865) 138 kV Bus CKT 1 b. 2. Trip branch from COUNCIL4 (514865) 138 kV Bus to WESTOAK4 (514866) 138 kV Bus CKT 1 b. 3. Trip branch from WESTOAK4 (514866) 138 kV Bus to MERIDAN4 (514867) 138 kV Bus CKT 1 b. 4. Trip branch from MERIDAN4 (514867) 138 kV Bus to DOUGLTP4 (514868) 138 kV Bus CKT 1 b. 5. Drop Load 1 at COUNCIL4 (514865) 138 kV Bus b. 6. Drop Load 1 at WESTOAK4 (514866) 138 kV Bus b. 7. Drop Load 1 at MERIDAN4 (514867) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0995_P1 | 3 phase fault on MUSTANG4 (514861) 138 kV Bus a. Apply Fault at the MUSTANG4 (514861) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from MUSTANG4 (514861) 138 kV Bus to MSTANG 2 (514860) 69 kV Bus to MUSTANG1 (515740) 13.2 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0996_P1 | 3 phase fault on MARAUTO2 (508576) 69 kV Bus a. Apply Fault at the MARAUTO2 (508576) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from MARAUTO2 (508576) 69 kV Bus to MARSHAL2 (508556) 69 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0997_P1 | 3 phase fault on JEFFRSN4 (508835) 138 kV Bus a. Apply Fault at the JEFFRSN4 (508835) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from JEFFRSN4 (508835) 138 kV Bus to LAKEPIN4 (509624) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0998_P1 | 3 phase fault on KNOXLEE4 (508548) 138 kV Bus a. Apply Fault at the KNOXLEE4 (508548) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from KNOXLEE4 (508548) 138 kV Bus to HARRISN4 (508544) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0999_P1 | 3 phase fault on LHAWKIN4 (508358) 138 kV Bus a. Apply Fault at the LHAWKIN4 (508358) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from LHAWKIN4 (508358) 138 kV Bus to NMINEOL4 (508349) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_1000_P1 | 3 phase fault on LHAWKIN4 (508358) 138 kV Bus a. Apply Fault at the LHAWKIN4 (508358) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from LHAWKIN4 (508358) 138 kV Bus to REDSPRW4 (508366) 138 kV Bus CKT 1 b. 2. Trip branch from REDSPRW4 (508366) 138 kV Bus to PECANHL4 (508365) 138 kV Bus CKT 1 b. 3. Trip branch from PECANHL4 (508365) 138 kV Bus to GARDVAL4 (508364) 138 kV Bus CKT 1 b. 4. Trip branch from GARDVAL4 (508364) 138 kV Bus to KENSULI4 (508363) 138 kV Bus CKT 1 b. 5. Trip branch from KENSULI4 (508363) 138 kV Bus to BENWHEL4 (508362) 138 kV Bus CKT 1 b. 6. Trip branch from BENWHEL4 (508362) 138 kV Bus to STARR 4 (508361) 138 kV Bus CKT 1 b. 7. Trip branch from STARR 4 (508361) 138 kV Bus to EBURGES4 (508360) 138 kV Bus CKT 1 b. 8. Trip branch from EBURGES4 (508360) 138 kV Bus to BURGEST4 (508357) 138 kV Bus CKT 1 b. 9. Drop Load 1 at REDSPRW4 (508366) 138 kV Bus b. 10. Drop Load 1 at PECANHL4 (508365) 138 kV Bus b. 11. Drop Load 1 at GARDVAL4 (508364) 138 kV Bus b. 12. Drop Load 1 at KENSULI4 (508363) 138 kV Bus b. 13. Drop Load 1 at BENWHEL4 (508362) 138 kV Bus b. 14. Drop Load 1 at STARR 4 (508361) 138 kV Bus b. 15. Drop Load 1 at EBURGES4 (508360) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_1001_P1 | 3 phase fault on BURGEST4 (508357) 138 kV Bus a. Apply Fault at the BURGEST4 (508357) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from BURGEST4 (508357) 138 kV Bus to MORTONST 4 (508373) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_1002_P1 | 3 phase fault on OVERTON4 (509080) 138 kV Bus a. Apply Fault at the OVERTON4 (509080) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from OVERTON4 (509080) 138 kV Bus to (763010) kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_1003_P1 | 3 phase fault on KNOXLEE4 (508548) 138 kV Bus a. Apply Fault at the KNOXLEE4 (508548) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from KNOXLEE4 (508548) 138 kV Bus to SOTXEST4 (508570) 138 kV Bus CKT 1 b. 2. Trip branch from SOTXEST4 (508570) 138 kV Bus to EASTEX 4 (508582) 138 kV Bus CKT 1 b. 3. Drop Load 1 at SOTXEST4 (508570) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_1004_P1 | 3 phase fault on KNOXLEE4 (508548) 138 kV Bus a. Apply Fault at the KNOXLEE4 (508548) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from KNOXLEE4 (508548) 138 kV Bus to KNOXLEE2 (508547) 69 kV Bus to KXLEE-1 (508584) 12.47 kV Bus CKT 1 b. 2. Trip branch from KNOXLEE2 (508547) 69 kV Bus to SELONGV2 (508568) 69 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_1005_P1 | 3 phase fault on NWHENDR4 (509076) 138 kV Bus a. Apply Fault at the NWHENDR4 (509076) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from NWHENDR4 (509076) 138 kV Bus to NWHENDR2 (509075) 69 kV Bus to NWHEN1-1 (509095) 13.2 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_1006_P1 | 3 phase fault on NWHENDR4 (509076) 138 kV Bus a. Apply Fault at the NWHENDR4 (509076) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from NWHENDR4 (509076) 138 kV Bus to NWHENDR2 (509075) 69 kV Bus to NWHEN2-1 (509096) 13.2 kV Bus CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_1007_P1 | 3 phase fault on KILGORE2 (508546) 69 kV Bus a. Apply Fault at the KILGORE2 (508546) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from KILGORE2 (508546) 69 kV Bus to MONROCR2 (508558) 69 kV Bus CKT 1 b. 2. Trip branch from MONROCR2 (508558) 69 kV Bus to WHITNEY2 (508574) 69 kV Bus CKT 1 b. 3. Drop Load 1 at MONROCR2 (508558) 69 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_1008_P1 | 3 phase fault on KILGORE2 (508546) 69 kV Bus a. Apply Fault at the KILGORE2 (508546) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from KILGORE2 (508546) 69 kV Bus to HOWELL 2 (508545) 69 kV Bus CKT 1 b. 2. Trip branch from HOWELL 2 (508545) 69 kV Bus to SABINE 2 (508565) 69 kV Bus CKT 1 b. 3. Trip branch from SABINE 2 (508565) 69 kV Bus to SPIPETP2 (508573) 69 kV Bus CKT 1 b. 4. Drop Load 1 at HOWELL 2 (508545) 69 kV Bus b. 5. Drop Load 1 at SABINE 2 (508565) 69 kV Bus b. 6. Drop Shunt 1 at HOWELL 2 (508545) 69 kV Bus1 b. 7. Drop Shunt 1 at SABINE 2 (508565) 69 kV Bus1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_1009_P1 | 3 phase fault on OVERTON4 (509080) 138 kV Bus a. Apply Fault at the OVERTON4 (509080) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from OVERTON4 (509080) 138 kV Bus to OVERTON2 (509079) 69 kV Bus to OVTON1-1 (509097) 13.2 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_1010_P1 | 3 phase fault on SPIPETP2 (508573) 69 kV Bus a. Apply Fault at the SPIPETP2 (508573) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from SPIPETP2 (508573) 69 kV Bus to SVCPIPE2 (508578) 69 kV Bus CKT 1 b. 2. Drop Load 1 at SVCPIPE2 (508578) 69 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_1011_P1 | 3 phase fault on SPIPETP2 (508573) 69 kV Bus a. Apply Fault at the SPIPETP2 (508573) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from SPIPETP2 (508573) 69 kV Bus to CLARKSV2 (508540) 69 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_1012_P1 | 3 phase fault on HARRISN4 (508544) 138 kV Bus a. Apply Fault at the HARRISN4 (508544) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from HARRISN4 (508544) 138 kV Bus to EASTEX 4 (508582) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_1013_P1 | 3 phase fault on HARRISN4 (508544) 138 kV Bus a. Apply Fault at the HARRISN4 (508544) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from HARRISN4 (508544) 138 kV Bus to LIBCYTP4 (508550) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_1014_P1 | 3 phase fault on OVERTON4 (509080) 138 kV Bus a. Apply Fault at the OVERTON4 (509080) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from OVERTON4 (509080) 138 kV Bus to OVERTON2 (509079) 69 kV Bus to OVTON2-1 (509098) 13.2 kV Bus CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_1015_P1 | 3 phase fault on EASTEX 4 (508582) 138 kV Bus a. Apply Fault at the EASTEX 4 (508582) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from EASTEX 4 (508582) 138 kV Bus to NTXEAST4 (508561) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_1016_P1 | 3 phase fault on EASTEX 4 (508582) 138 kV Bus a. Apply Fault at the EASTEX 4 (508582) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from EASTEX 4 (508582) 138 kV Bus to NTXEAST4 (508561) 138 kV Bus CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_1017_P1 | 3 phase fault on LIBCYTP4 (508550) 138 kV Bus a. Apply Fault at the LIBCYTP4 (508550) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from LIBCYTP4 (508550) 138 kV Bus to LIBCITY4 (508535) 138 kV Bus CKT 1 b. 2. Drop Load 1 at LIBCITY4 (508535) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_1018_P1 | 3 phase fault on ROKHILL4 (509083) 138 kV Bus a. Apply Fault at the ROKHILL4 (509083) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from ROKHILL4 (509083) 138 kV Bus to ROKHILL2 (509082) 69 kV Bus to RKHIL1-1 (509090) 13.2 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_1019_P1 | 3 phase fault on ROKHILL4 (509083) 138 kV Bus a. Apply Fault at the ROKHILL4 (509083) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from ROKHILL4 (509083) 138 kV Bus to ROKHILL2 (509082) 69 kV Bus to RKHIL2-1 (509091) 13.2 kV Bus CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_1020_P1 | 3 phase fault on ROKHILL4 (509083) 138 kV Bus a. Apply Fault at the ROKHILL4 (509083) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from ROKHILL4 (509083) 138 kV Bus to NEWPROS4 (509102) 138 kV Bus CKT 1 b. 2. Trip branch from NEWPROS4 (509102) 138 kV Bus to CARTPOD4 (509057) 138 kV Bus CKT 1 b. 3. Trip branch from CARTPOD4 (509057) 138 kV Bus to HULLTAP4 (509099) 138 kV Bus CKT 1 b. 4. Trip branch from HULLTAP4 (509099) 138 kV Bus to CARTHGT4 (509060) 138 kV Bus CKT 1 b. 5. Drop Load 1 at NEWPROS4 (509102) 138 kV Bus b. 6. Drop Load 1 at CARTPOD4 (509057) 138 kV Bus b. 7. Drop Load 1 at HULLTAP4 (509099) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_1021_P1 | 3 phase fault on SELONGV2 (508568) 69 kV Bus a. Apply Fault at the SELONGV2 (508568) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from SELONGV2 (508568) 69 kV Bus to BIG3TAP2 (508539) 69 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_1022_P1 | 3 phase fault on SELONGV2 (508568) 69 kV Bus a. Apply Fault at the SELONGV2 (508568) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from SELONGV2 (508568) 69 kV Bus to LETOURT2 (508549) 69 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_1023_P1 | 3 phase fault on G19-065-TAP (763010) kV Bus a. Apply Fault at the G19-065-TAP (763010) kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from G19-065-TAP (763010) kV Bus to LONDON 4 (509072) 138 kV Bus CKT 1 b. 2. Trip branch from LONDON 4 (509072) 138 kV Bus to FRIARSW4 (509062) 138 kV Bus CKT 1 b. 3. Trip branch from FRIARSW4 (509062) 138 kV Bus to FRIRSWR4 (509063) 138 kV Bus CKT 1 b. 4. Trip branch from FRIRSWR4 (509063) 138 kV Bus to NWHENDR4 (509076) 138 kV Bus CKT 1 b. 5. Drop Load 1 at LONDON 4 (509072) 138 kV Bus b. 6. Drop Load 1 at FRIARSW4 (509062) 138 kV Bus b. 7. Drop Load 1 at FRIRSWR4 (509063) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_1024_P1 | 3 phase fault on NWHENDR2 (509075) 69 kV Bus a. Apply Fault at the NWHENDR2 (509075) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from NWHENDR2 (509075) 69 kV Bus to EVENSID2 (509061) 69 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_1025_P1 | 3 phase fault on NWHENDR2 (509075) 69 kV Bus a. Apply Fault at the NWHENDR2 (509075) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from NWHENDR2 (509075) 69 kV Bus to POYNTER2 (509081) 69 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_1026_P1 | 3 phase fault on WHITNEY2 (508574) 69 kV Bus a. Apply Fault at the WHITNEY2 (508574) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from WHITNEY2 (508574) 69 kV Bus to LETOURT2 (508549) 69 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_1027_P1 | 3 phase fault on OVERTON4 (509080) 138 kV Bus a. Apply Fault at the OVERTON4 (509080) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from OVERTON4 (509080) 138 kV Bus to LEVERET4 (509069) 138 kV Bus CKT 1 b. 2. Trip branch from LEVERET4 (509069) 138 kV Bus to KILGORR4 (509067) 138 kV Bus CKT 1 b. 3. Trip branch from KILGORR4 (509067) 138 kV Bus to MONROER4 (509073) 138 kV Bus CKT 1 b. 4. Trip branch from MONROER4 (509073) 138 kV Bus to KNOXLEE4 (508548) 138 kV Bus CKT 1 b. 5. Drop Load 1 at LEVERET4 (509069) 138 kV Bus b. 6. Drop Load 1 at KILGORR4 (509067) 138 kV Bus b. 7. Drop Load 1 at MONROER4 (509073) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_1028_P1 | 3 phase fault on WHITNEY2 (508574) 69 kV Bus a. Apply Fault at the WHITNEY2 (508574) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from WHITNEY2 (508574) 69 kV Bus to LONGVHT2 (508553) 69 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_1029_P1 | 3 phase fault on WHITNEY2 (508574) 69 kV Bus a. Apply Fault at the WHITNEY2 (508574) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from WHITNEY2 (508574) 69 kV Bus to LONGVUE2 (508555) 69 kV Bus CKT 1 b. 2. Trip branch from LONGVUE2 (508555) 69 kV Bus to GATES 2 (508541) 69 kV Bus CKT 1 b. 3. Trip branch from GATES 2 (508541) 69 kV Bus to LLAMOND2 (508551) 69 kV Bus CKT 1 b. 4. Drop Load 1 at LONGVUE2 (508555) 69 kV Bus b. 5. Drop Shunt 1 at LONGVUE2 (508555) 69 kV Bus1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_1030_P1 | 3 phase fault on OVERTON2 (509079) 69 kV Bus a. Apply Fault at the OVERTON2 (509079) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from OVERTON2 (509079) 69 kV Bus to KILGORE2 (508546) 69 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_1031_P1 | 3 phase fault on NTXEAST4 (508561) 138 kV Bus a. Apply Fault at the NTXEAST4 (508561) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from NTXEAST4 (508561) 138 kV Bus to ESTGEN4 (508583) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_1032_P1 | 3 phase fault on NTXEAST4 (508561) 138 kV Bus a. Apply Fault at the NTXEAST4 (508561) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from NTXEAST4 (508561) 138 kV Bus to ESTGEN4 (508583) 138 kV Bus CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_1033_P1 | 3 phase fault on OVERTON2 (509079) 69 kV Bus a. Apply Fault at the OVERTON2 (509079) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from OVERTON2 (509079) 69 kV Bus to TURNERT2 (509089) 69 kV Bus CKT 1 b. 2. Drop Load 1 at TURNERT2 (509089) 69 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_1034_P1 | 3 phase fault on CARTHGT4 (509060) 138 kV Bus a. Apply Fault at the CARTHGT4 (509060) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from CARTHGT4 (509060) 138 kV Bus to MURVAULTP (509048) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_1035_P1 | 3 phase fault on CARTHGT4 (509060) 138 kV Bus a. Apply Fault at the CARTHGT4 (509060) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from CARTHGT4 (509060) 138 kV Bus to LOGANSP4 (509071) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_1036_P1 | 3 phase fault on ROKHILL2 (509082) 69 kV Bus a. Apply Fault at the ROKHILL2 (509082) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from ROKHILL2 (509082) 69 kV Bus to BECKVIL2 (509054) 69 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_1037_P1 | 3 phase fault on ROKHILL2 (509082) 69 kV Bus a. Apply Fault at the ROKHILL2 (509082) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from ROKHILL2 (509082) 69 kV Bus to ROSBORO2 (509085) 69 kV Bus CKT 1 b. 2. Trip branch from ROSBORO2 (509085) 69 kV Bus to BLOCKRT2 (509055) 69 kV Bus CKT 1 b. 3. Drop Load 1 at ROSBORO2 (509085) 69 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_1038_P1 | 3 phase fault on ROKHILL2 (509082) 69 kV Bus a. Apply Fault at the ROKHILL2 (509082) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from ROKHILL2 (509082) 69 kV Bus to CARTHAG2 (509056) 69 kV Bus CKT 1 b. 2. Trip branch from CARTHAG2 (509056) 69 kV Bus to LAPACIF2 (509068) 69 kV Bus CKT 1 b. 3. Drop Load 1 at CARTHAG2 (509056) 69 kV Bus b. 4. Drop Load 2 at CARTHAG2 (509056) 69 kV Bus b. 5. Drop Load 1 at LAPACIF2 (509068) 69 kV Bus b. 6. Drop Shunt 1 at CARTHAG2 (509056) 69 kV Bus1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_1039_P1 | 3 phase fault on BIG3TAP2 (508539) 69 kV Bus a. Apply Fault at the BIG3TAP2 (508539) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from BIG3TAP2 (508539) 69 kV Bus to BIG 3 2 (508537) 69 kV Bus CKT 1 b. 2. Drop Load 1 at BIG 3 2 (508537) 69 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_1040_P1 | 3 phase fault on BIG3TAP2 (508539) 69 kV Bus a. Apply Fault at the BIG3TAP2 (508539) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from BIG3TAP2 (508539) 69 kV Bus to LLAMOND2 (508551) 69 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_1041_P1 | 3 phase fault on LETOURT2 (508549) 69 kV Bus a. Apply Fault at the LETOURT2 (508549) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from LETOURT2 (508549) 69 kV Bus to LETOURN2 (508581) 69 kV Bus CKT 1 b. 2. Trip branch from LETOURN2 (508581) 69 kV Bus to LETRNST2 (508536) 69 kV Bus CKT 1 b. 3. Drop Load 1 at LETOURN2 (508581) 69 kV Bus b. 4. Drop Load 1 at LETRNST2 (508536) 69 kV Bus b. 5. Drop Shunt 1 at LETOURN2 (508581) 69 kV Bus1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_1042_P1 | 3 phase fault on EVENSID2 (509061) 69 kV Bus a. Apply Fault at the EVENSID2 (509061) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from EVENSID2 (509061) 69 kV Bus to FEARSCO2 (509086) 69 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_1043_P1 | 3 phase fault on EVENSID2 (509061) 69 kV Bus a. Apply Fault at the EVENSID2 (509061) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from EVENSID2 (509061) 69 kV Bus to POYNTER2 (509081) 69 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_1044_P1 | 3 phase fault on POYNTER2 (509081) 69 kV Bus a. Apply Fault at the POYNTER2 (509081) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from POYNTER2 (509081) 69 kV Bus to HNDRSNR2 (509065) 69 kV Bus CKT 1 b. 2. Trip branch from HNDRSNR2 (509065) 69 kV Bus to BEARCATTP 2 (509127) 69 kV Bus CKT 1 b. 3. Trip branch from BEARCATTP 2 (509127) 69 kV Bus to BECKVIL2 (509054) 69 kV Bus CKT 1 b. 4. Drop Load 1 at HNDRSNR2 (509065) 69 kV Bus b. 5. Drop Load 1 at BEARCATTP 2 (509127) 69 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_1045_P1 | 3 phase fault on 4GRIMES% (334026) 138 kV Bus a. Apply Fault at the 4GRIMES% (334026) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from 4GRIMES% (334026) 138 kV Bus to 4COLSTTA% (334021) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_1046_P1 | 3 phase fault on 4GRIMES% (334026) 138 kV Bus a. Apply Fault at the 4GRIMES% (334026) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from 4GRIMES% (334026) 138 kV Bus to 4MT.ZION (334060) 138 kV Bus CKT 1 b. 2. Trip branch from 4MT.ZION (334060) 138 kV Bus to 4L558T485 (334058) 138 kV Bus CKT 1 b. 3. Drop Load BZ at 4MT.ZION (334060) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_1047_P1 | 3 phase fault on 4GRIMES% (334026) 138 kV Bus a. Apply Fault at the 4GRIMES% (334026) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from 4GRIMES% (334026) 138 kV Bus to 4MAG AND (334025) 138 kV Bus CKT 1 b. 2. Trip branch from 4MAG AND (334025) 138 kV Bus to 4SOTA 1 (334024) 138 kV Bus CKT 1 b. 3. Trip branch from 4SOTA 1 (334024) 138 kV Bus to 4NAVSSPLT! (334019) 138 kV Bus CKT 1 b. 4. Drop Load BZ at 4SOTA 1 (334024) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_1048_P1 | 3 phase fault on 4GRIMES% (334026) 138 kV Bus a. Apply Fault at the 4GRIMES% (334026) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from 4GRIMES% (334026) 138 kV Bus to 4BENTWATER! (334039) 138 kV Bus CKT 1 b. 2. Trip branch from 4BENTWATER! (334039) 138 kV Bus to 4WALDEN (334040) 138 kV Bus CKT 1 b. 3. Trip branch from 4WALDEN (334040) 138 kV Bus to 4APRILTX (334041) 138 kV Bus CKT 1 b. 4. Trip branch from 4APRILTX (334041) 138 kV Bus to 4LFOREST (334042) 138 kV Bus CKT 1 b. 5. Trip branch from 4LFOREST (334042) 138 kV Bus to 4RABONCHAPEL (334049) 138 kV Bus CKT 1 b. 6. Trip branch from 4RABONCHAPEL (334049) 138 kV Bus to 4WDHAVN (334105) 138 kV Bus CKT 1 b. 7. Trip branch from 4WDHAVN (334105) 138 kV Bus to 4PONDEROSA% (334087) 138 kV Bus CKT 1 b. 8. Drop Load 1 at 4BENTWATER! (334039) 138 kV Bus b. 9. Drop Load 1 at 4WALDEN (334040) 138 kV Bus b. 10. Drop Load 1 at 4APRILTX (334041) 138 kV Bus b. 11. Drop Load BZ at 4LFOREST (334042) 138 kV Bus b. 12. Drop Load BZ at 4RABONCHAPEL (334049) 138 kV Bus b. 13. Drop Load BZ at 4WDHAVN (334105) 138 kV Bus b. 14. Drop Shunt 1 at 4BENTWATER! (334039) 138 kV Bus1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_1049_P1 | 3 phase fault on 4PONDEROSA% (334087) 138 kV Bus a. Apply Fault at the 4PONDEROSA% (334087) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from 4PONDEROSA% (334087) 138 kV Bus to 4FISHCRK (334045) 138 kV Bus CKT 1 b. 2. Trip branch from 4FISHCRK (334045) 138 kV Bus to 4DEERLAKE (334048) 138 kV Bus CKT 1 b. 3. Trip branch from 4DEERLAKE (334048) 138 kV Bus to 4SPRINGBRNCH (334046) 138 kV Bus CKT 1 b. 4. Trip branch from 4SPRINGBRNCH (334046) 138 kV Bus to 4DOBBIN! (334044) 138 kV Bus CKT 1 b. 5. Trip branch from 4DOBBIN! (334044) 138 kV Bus to 4TUBULAR (334043) 138 kV Bus CKT 1 b. 6. Drop Load BZ at 4FISHCRK (334045) 138 kV Bus b. 7. Drop Load BZ at 4DEERLAKE (334048) 138 kV Bus b. 8. Drop Load BZ at 4SPRINGBRNCH (334046) 138 kV Bus b. 9. Drop Load 1 at 4DOBBIN! (334044) 138 kV Bus b. 10. Drop Load BZ at 4DOBBIN! (334044) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_1050_P1 | 3 phase fault on 4PONDEROSA% (334087) 138 kV Bus a. Apply Fault at the 4PONDEROSA% (334087) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from 4PONDEROSA% (334087) 138 kV Bus to 4LONGMIR! (334075) 138 kV Bus CKT 1 b. 2. Trip branch from 4LONGMIR! (334075) 138 kV Bus to 4PANORAM (334074) 138 kV Bus CKT 1 b. 3. Trip branch from 4PANORAM (334074) 138 kV Bus to 4EGYPT (334073) 138 kV Bus CKT 1 b. 4. Trip branch from 4EGYPT (334073) 138 kV Bus to 4LEWIS% (334072) 138 kV Bus CKT 1 b. 5. Drop Load 1 at 4LONGMIR! (334075) 138 kV Bus b. 6. Drop Load 1 at 4PANORAM (334074) 138 kV Bus b. 7. Drop Load 1 at 4EGYPT (334073) 138 kV Bus b. 8. Drop Shunt 1 at 4LONGMIR! (334075) 138 kV Bus1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_1051_P1 | 3 phase fault on 4PONDEROSA% (334087) 138 kV Bus a. Apply Fault at the 4PONDEROSA% (334087) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from 4PONDEROSA% (334087) 138 kV Bus to 4CONROE1! (334104) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_1052_P1 | 3 phase fault on LLAMOND2 (508551) 69 kV Bus a. Apply Fault at the LLAMOND2 (508551) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from LLAMOND2 (508551) 69 kV Bus to GREGGTN2 (508542) 69 kV Bus CKT 1 b. 2. Trip branch from GREGGTN2 (508542) 69 kV Bus to NETTLTP2 (508559) 69 kV Bus CKT 1 b. 3. Drop Load 1 at GREGGTN2 (508542) 69 kV Bus b. 4. Drop Load 2 at GREGGTN2 (508542) 69 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_1053_P1 | 3 phase fault on LLAMOND2 (508551) 69 kV Bus a. Apply Fault at the LLAMOND2 (508551) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from LLAMOND2 (508551) 69 kV Bus to AIRLINE2 (508538) 69 kV Bus CKT 1 b. 2. Trip branch from AIRLINE2 (508538) 69 kV Bus to LONGVHT2 (508553) 69 kV Bus CKT 1 b. 3. Drop Load 1 at AIRLINE2 (508538) 69 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_1054_P4 | a. Apply single-phase fault on GRDA1 7 (512650) 345 kV Bus TO GREC TAP5 (512865) 345 kV Bus CKT 1 b. 1. Clear fault after 15 cycles: b. 2. Trip branch GRDA1 7 (512650) 345 kV Bus TO GREC TAP5 (512865) 345 kV Bus CKT 1 b. 3. Disconnect BUS 512821 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_1055_P4 | a. Apply single-phase fault on 7SPORTSMAN (300740) 345 kV Bus TO GRDA1 7 (512650) 345 kV Bus CKT 1 b. 1. Clear fault after 15 cycles: b. 2. Trip branch 7SPORTSMAN (300740) 345 kV Bus TO GRDA1 7 (512650) 345 kV Bus CKT 1 b. 3. Disconnect BUS 512821 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_1056_P4 | a. Apply single-phase fault on GRDA1 7 (512650) 345 kV Bus TO TONECE7 (512750) 345 kV Bus CKT 1 b. 1. Clear fault after 15 cycles: b. 2. Trip branch GRDA1 7 (512650) 345 kV Bus TO TONECE7 (512750) 345 kV Bus CKT 1 b. 3. Disconnect BUS 512821 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_1060_P4 | a. Apply single-phase fault on T.NO.--7 (509852) 345 kV Bus TO IGLOOV 7 (513596) 345 kV Bus CKT 1 b. 1. Clear fault after 15 cycles: b. 2. Trip branch T.NO.--7 (509852) 345 kV Bus TO IGLOOV 7 (513596) 345 kV Bus CKT 1 b. 3. Disconnect BUS 513592 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_1061_P4 | a. Apply single-phase fault on CLARMR 5 (512651) 161 kV Bus TO GRDA1 5 (512656) 161 kV Bus CKT 1 b. 1. Clear fault after 15 cycles: b. 2. Trip branch CLARMR 5 (512651) 161 kV Bus TO GRDA1 5 (512656) 161 kV Bus CKT 1 b. 3. Disconnect BUS 512700 b. 4. Disconnect BUS 512818 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_1062_P4 | a. Apply single-phase fault on MAID 5 (512648) 161 kV Bus TO GRDA1 5 (512656) 161 kV Bus CKT 1 b. 1. Clear fault after 15 cycles: b. 2. Trip branch MAID 5 (512648) 161 kV Bus TO GRDA1 5 (512656) 161 kV Bus CKT 1 b. 3. Trip branch GRDA1 5 (512656) 161 kV Bus TO WMAIN ST5 (512742) 161 kV Bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_1063_P4 | a. Apply single-phase fault at CLEVLND7 (512694) 345 kV Bus b. 1. Run for 15 cycles, Trip branch from T.NO.--7 (509852) 345 kV Bus TO CLEVLND7 (512694) 345 kV Bus CKT 1 b. 2. Clear fault at CLEVLND7 (512694) 345 kV Bus b. 3. Trip branch from CLEVLND7 (512694) 345 kV Bus TO G15-066T (560056) 345 kV Bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_1064_P4 | a. Apply single-phase fault at CLEVLND7 (512694) 345 kV Bus b. 1. Run for 15 cycles, Trip branch from T.NO.--7 (509852) 345 kV Bus TO CLEVLND7 (512694) 345 kV Bus CKT 1 b. 2. Clear fault at CLEVLND7 (512694) 345 kV Bus b. 3. Disconnect bus CLEVLND1 (512817) 13.8 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_1065_P4 | a. Apply single-phase fault at CLEVLND7 (512694) 345 kV Bus b. 1. Run for 15 cycles: b. 2. Trip branch from CLEVLND7 (512694) 345 kV Bus TO SOONER 7 (514803) 345 kV Bus CKT 1 b. 3. Trip three winding from CLEVLND7 (512694) 345 kV Bus TO CLEVLND 4 (512729) 138 kV Bus TO CLEVLND1 (512817) 13.8 kV CKT 1 b. 4. Clear fault at CLEVLND7 (512694) 345 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_1066_P4 | a. Apply single-phase fault at MAID 5 (512648) 161 kV Bus b. 1. Run for 15 cycles, Trip branch from 5CHOTEAU1 (300069) 161 kV Bus TO MAID 5 (512648) 161 kV Bus CKT 1 b. 2. Clear fault at MAID 5 (512648) 161 kV Bus b. 3. Disconnect bus MAITER1 1 (512836) 13.2 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_1067_P4 | a. Apply single-phase fault at MAID 5 (512648) 161 kV Bus b. 1. Run for 15 cycles, Trip branch from CATSAGR5 (512638) 161 kV Bus TO MAID 5 (512648) 161 kV Bus CKT 1 b. 2. Clear fault at MAID 5 (512648) 161 kV Bus b. 3. Disconnect bus MAITER1 1 (512836) 13.2 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_1068_P4 | a. Apply single-phase fault at MAID 5 (512648) 161 kV Bus b. 1. Run for 15 cycles, Trip branch from DRYGULCH5 (512629) 161 kV Bus TO MAID 5 (512648) 161 kV Bus CKT 1 b. 2. Clear fault at MAID 5 (512648) 161 kV Bus b. 3. Disconnect bus MAITER1 1 (512836) 13.2 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_1069_P4 | a. Apply single-phase fault at MAID 5 (512648) 161 kV Bus b. 1. Run for 15 cycles, Trip branch from KERR GR5 (512635) 161 kV Bus TO MAID 5 (512648) 161 kV Bus CKT 2 b. 2. Clear fault at MAID 5 (512648) 161 kV Bus b. 3. Disconnect bus MAITER1 1 (512836) 13.2 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_1070_P4 | a. Apply single-phase fault at MAID 5 (512648) 161 kV Bus b. 1. Run for 15 cycles, Trip branch from MAID 5 (512648) 161 kV Bus TO GRDA1 5 (512656) 161 kV Bus CKT 1 b. 2. Clear fault at MAID 5 (512648) 161 kV Bus b. 3. Disconnect bus MAITER1 1 (512836) 13.2 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_1071_P4 | a. Apply single-phase fault at MAID 5 (512648) 161 kV Bus b. 1. Run for 15 cycles, Trip branch from 5CHOTEAU1 (300069) 161 kV Bus TO MAID 5 (512648) 161 kV Bus CKT 1 b. 2. Clear fault at MAID 5 (512648) 161 kV Bus b. 3. Trip branch from MAID 5 (512648) 161 kV Bus TO GERALDGAY5 (512760) 161 kV Bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_1072_P4 | a. Apply single-phase fault at MAID 5 (512648) 161 kV Bus b. 1. Run for 15 cycles, Trip branch from CATSAGR5 (512638) 161 kV Bus TO MAID 5 (512648) 161 kV Bus CKT 1 b. 2. Clear fault at MAID 5 (512648) 161 kV Bus b. 3. Trip branch from CATSAGR5 (512638) 161 kV Bus TO MAID 5 (512648) 161 kV Bus CKT 2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_1073_P4 | a. Apply single-phase fault at MAID 5 (512648) 161 kV Bus b. 1. Run for 15 cycles, Trip branch from KERR GR5 (512635) 161 kV Bus TO MAID 5 (512648) 161 kV Bus CKT 1 b. 2. Clear fault at MAID 5 (512648) 161 kV Bus b. 3. KERR GR5 (512635) 161 kV Bus TO MAID 5 (512648) 161 kV Bus CKT 2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_1074_P4 | a. Apply single-phase fault at MAID 5 (512648) 161 kV Bus b. 1. Run for 15 cycles, Trip branch from MAID 5 (512648) 161 kV Bus TO GRDA1 5 (512656) 161 kV Bus CKT 1 b. 2. Clear fault at MAID 5 (512648) 161 kV Bus b. 3. Trip branch from MAID 5 (512648) 161 kV Bus TO GRDA1 5 (512656) 161 kV Bus CKT 2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_1076_P4 | a. Apply single-phase fault at KERR GR5 (512635) 161 kV Bus b. 1. Run for 15 cycles, Trip branch from KERR GR5 (512635) 161 kV Bus TO MAID 5 (512648) 161 kV Bus CKT 1 b. 2. Clear fault at KERR GR5 (512635) 161 kV Bus b. 3. Trip branch from KERR GR5 ( 512635 ) 161 kV Bus TO MAID 5 ( 512648 ) 161 kV Bus CKT 2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_1078_P4 | a. Apply single-phase fault at KETCHUM5 (512669) 161 kV Bus b. 1. Run for 15 cycles, Disconnect Bus 512632 b. 2. Clear fault at KETCHUM5 (512669) 161 kV Bus b. 3. Trip branch from PENSA 5 (512654) 161 kV Bus TO KETCHUM5 (512669) 161 kV Bus CKT 1 b. 4. Drop Load 1 Bus 512669 b. 5. Disconnect Bus 512669 b. 6. Disconnect Bus 512845 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_1079_P4 | a. Apply single-phase fault at PENSA 5 (512654) 161 kV Bus b. 1. Run for 15 cycles, Trip branch from DRYGULCH5 (512629) 161 kV Bus TO PENSA 5 (512654) 161 kV Bus CKT 1 b. 2. Clear fault at PENSA 5 (512654) 161 kV Bus b. 3. Disconnect bus PENSA 1 (512841) 13.8 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_1080_P4 | a. Apply single-phase fault at PENSA 5 (512654) 161 kV Bus b. 1. Run for 15 cycles, Trip branch from KERR GR5 (512635) 161 kV Bus TO PENSA 5 (512654) 161 kV Bus CKT 1 b. 2. Clear fault at PENSA 5 (512654) 161 kV Bus b. 3. Disconnect bus PENSA 1 (512841) 13.8 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_1081_P4 | a. Apply single-phase fault at PENSA 5 (512654) 161 kV Bus b. 1. Run for 15 cycles, Trip branch from DRYGULCH5 (512629) 161 kV Bus TO PENSA 5 (512654) 161 kV Bus CKT 1 b. 2. Clear fault at PENSA 5 (512654) 161 kV Bus b. 3. Trip branch from PENSA 5 (512654) 161 kV Bus TO KETCHUM5 (512669) 161 kV Bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_1084_P4 | a. Apply single-phase fault at TONECE5 (512751) 161 kV Bus b. 1. Run for 15 cycles, Trip branch from SILMCTY5 (512643) 161 kV Bus TO TONECE5 (512751) 161 kV Bus CKT 1 b. 2. Clear fault at TONECE5 (512751) 161 kV Bus b. 3. Disconnect Bus 512754 b. 4. Drop Load 1 Bus 512745 b. 5. Drop Load 1 Bus 512746 b. 6. Disconnect Bus 512728 b. 7. Disconnect Bus 512745 b. 8. Disconnect Bus 512746 b. 9. Disconnect Bus 512747 b. 10. Disconnect Bus 512756 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 763002 [G18-064-GEN10.5500]
04 - Southeast | 25W | Transfer | Group4_Fault_1085_P4 | a. Apply single-phase fault at TONECE7 (512750) 345 kV Bus b. 1. Run for 15 cycles, Trip branch from FLINTCR7 (506935) 345 kV Bus TO TONECE7 (512750) 345 kV Bus CKT 1 b. 2. Clear fault at TONECE7 (512750) 345 kV Bus b. 3. Trip branch from GRDA1 7 (512650) 345 kV Bus TO TONECE7 (512750) 345 kV Bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_1086_P4 | a. Apply single-phase fault at TONECE7 (512750) 345 kV Bus b. 1. Run for 15 cycles, Trip branch from GRDA1 7 (512650) 345 kV Bus TO TONECE7 (512750) 345 kV Bus CKT 1 b. 2. Clear fault at TONECE7 (512750) 345 kV Bus b. 3. Disconnect Bus 512752 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_1087_P4 | a. Apply single-phase fault at BVRCNTY7 (515554) 345 kV Bus CB 307 Stuck b. Clear Fault after 16 cycles: b. 1. Trip branch from BVRCNTY7 (515554) 345 kV Bus TO BADGER 7 (515677) 345 kV Bus CKT 1 b. 2. Trip branch from BVRCNTY7 (515554) 345 kV Bus TO BADGER 7 (515677) 345 kV Bus CKT 2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_1088_P4 | a. Apply single-phase fault at WINDFRM4 (515785) 138 kV Bus b. 1. Run for 16 cycles: b. 2. Trip branch from WINDFRM4 (515785) 138 kV Bus TO MOORLND4 (520999) 138 kV Bus CKT 1 b. 3. Trip branch from WOODWRD4 (514785) 138 kV Bus TO WINDFRM4 (515785) 138 kV Bus CKT 1 b. 4. Clear fault at WINDFRM4 (515785) 138 kV Bus b. 5. Drop Generator 1 Bus 515895 b. 6. Drop Load S1 Bus 515787 b. 7. Disconnect Bus 515785 b. 8. Disconnect Bus 515786 b. 9. Disconnect Bus 515787 b. 10. Disconnect Bus 515790 b. 11. Disconnect Bus 515895 b. 12. Disconnect Bus 515896 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_1089_P4 | a. Apply single-phase fault at SUNNYSD7 (515136) 345 kV Bus b. 1. Run for 16 cycles: b. 2. Trip three winding transformer from SUNNYSD7 (515136) 345 kV Bus TO SUNNYSD4 (515135) 138 kV TO SUNYSD 1 (515405) 13.8 kV CKT 1 b. 3. Disconnect Bus SUNYSD 1 (515405) 13.8 kV CKT 1 b. 4. Trip branch from SUNNYSD7 (515136) 345 kV Bus TO G16-063-TAP (560088) 138 kV Bus CKT 1 b. 5. Clear fault at SUNNYSD7 (515136) 345 kV Bus b. 6. Drop Shunt 1 Bus SUNYSD 1 (515405) 13.8 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_1090_P4 | a. Apply single-phase fault at DRAPER 4 (514933) 138 kV Bus b. 1. Run for 16 cycles: b. 2. Disconnect Bus 514946 b. 3. Trip branch from DRAPER 4 (514933) 138 kV Bus TO SOONRTP4 (514949) 138 kV Bus CKT 1 b. 4. Clear fault at DRAPER 4 (514933) 138 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_1091_P4 | a. Apply single-phase fault at WAUKOTP4 (514711) 138 kV Bus b. 1. Run for 16 cycles: b. 2. Trip branch from WAUKOTP4 (514711) 138 kV Bus TO SO4TH 4 (514731) 138 kV Bus CKT 1 b. 3. Trip branch from WAUKOTP4 (514711) 138 kV Bus TO WOODRNG4 (514714) 138 kV Bus CKT 1 b. 4. Run for 10 cycles: b. 5. Trip branch from FRMNTAP4 (514709) 138 kV Bus TO FAIRMON4 (514712) 138 kV Bus CKT 1 b. 6. Trip branch from FRMNTAP4 (514709) 138 kV Bus TO WOODRNG4 (514714) 138 kV Bus CKT 1 b. 7. Trip branch from FRMNTAP4 (514709) 138 kV Bus TO SO4TH 4 (514731) 138 kV Bus CKT 1 b. 8. Clear fault at WAUKOTP4 (514711) 138 kV Bus b. 9. Disconnect Bus WAUKOTP4 (514711) 138 kV b. 10. Disconnect Bus FRMNTAP4 (514709) 138 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_1092_P4 | a. Apply single-phase fault at JOHNCO 7 (514809) 345 kV Bus b. 1. Run for 16 cycles: b. 2. Trip branch from PITTSB-7 (510907) 345 kV Bus TO JOHNCO 7 (514809) 345 kV Bus CKT 1 b. 3. Trip branch from JOHNCO 7 (514809) 345 kV Bus TO SUNNYSD7 (515136) 345 kV Bus CKT 1 b. 4. Clear fault at JOHNCO 7 (514809) 345 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_1093_P4 | a. Apply single-phase fault at GRACMNT7 (515800) 345 kV Bus b. 1. Run for 16 cycles: b. 2. Trip branch from G16-091-TAP (587744) 345 kV Bus TO GRACMNT7 (515800) 345 kV Bus CKT 1 b. 3. Trip branch from MINCO 7 (514801) 345 kV Bus TO GRACMNT7 (515800) 345 kV Bus CKT 1 b. 4. Clear fault at GRACMNT7 (515800) 345 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_1095_P4 | a. Apply single-phase fault at PECANCK7 (515235) 345 kV Bus b. 1. Run for 16 cycles: b. 2. Trip branch from R.S.S.-7 (509782) 345 kV Bus TO PECANCK7 (515235) 345 kV Bus CKT 1 b. 3. Disconnect Bus PECANC21 (515759) 13.8 kV b. 4. Clear fault at PECANCK7 (515235) 345 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_1097_P4 | a. Apply single-phase fault at REDBUD 7 (514909) 345 kV Bus b. 1. Run for 16 cycles: b. 2. Trip branch from ARCADIA7 (514908) 345 kV Bus TO REDBUD 7 (514909) 345 kV Bus CKT 2 b. 3. Trip branch from R.S.S.-7 (509782) 345 kV Bus TO REDBUD 7 (514909) 345 kV Bus CKT 1 b. 4. Clear fault at REDBUD 7 (514909) 345 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_1098_P4 | a. Apply single-phase fault at FTSMITH8 (515305) 500 kV Bus b. 1. Run for 16 cycles: b. 2. Disconnect Bus FTSMTH31 (515727) 13.8 kV b. 3. Trip branch from 8ANO% (337909) 500 kV Bus TO FTSMITH8 (515305) 500 kV Bus CKT 1 b. 4. Clear fault at FTSMITH8 (515305) 500 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_1099_P4 | a. Apply single-phase fault at SEMINOL7 (515045) 345 kV Bus b. 1. Run for 16 cycles: b. 2. Trip branch from PITTSB-7 (510907) 345 kV Bus TO SEMINOL7 (515045) 345 kV Bus CKT 1 b. 3. Disconnect Bus SEMINO21 (515757) 14.4 kV b. 4. Clear fault at SEMINOL7 (515045) 345 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_1100_P4 | a. Apply single-phase fault at SOONER 7 (514803) 345 kV Bus b. 1. Run for 16 cycles: b. 2. Trip branch from G15-066T (560056) 345 kV Bus TO SOONER 7 (514803) 345 kV Bus CKT 1 b. 3. Disconnect Bus SOONER 1 (515760) 13.8 kV b. 4. Clear fault at SOONER 7 (514803) 345 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_1101_P4 | a. Apply single-phase fault at WWDBORDT (755000) 345 kV Bus CB 384 Stuck b. Clear Fault after 16 cycles: b. 1. Trip branch from WWDBORDT (755000) 345 kV Bus TO BORDER 7 (515458) 345 kV Bus CKT 1 b. 2. Trip branch from BORDER 7 (515458) 345 kV Bus TO CRAWFISH_DR (560022) 345 kV Bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_1102_P4 | a. Apply single-phase fault at VBI 5 (515339) 161 kV Bus b. 1. Run for 23.52 cycles, Trip branch from VAN BUR5 (505522) 161 kV Bus TO VBI 5 (515339) 161 kV Bus KT Z1 b. 2. Run for 2.1 cycles, Trip branch from OAKPARK5 (515315) 161 kV Bus TO GERBRTP5 (515326) 161 kV Bus CKT 1 b. 3. Run for 1.2 cycles, Trip branch from MASSARD5 (515343) 161 kV Bus TO WHITESD5 (515341) 161 kV Bus CKT 1 b. 4. Run for 1.5 cycles, Trip branch from HELBERG5 (515327) 161 kV Bus TO PUDDIN 5 (515346) 161 kV Bus CKT 1 b. 5. Run for 3.9 cycles, Trip branch from BRANCH 5 (515316) 161 kV Bus TO GRNDPRT5 (515524) 161 kV Bus CKT 1 b. 6. Run for 11.28 cycles, Trip branch from VAN BUR5 (505522) 161 kV Bus TO VBI 5 (515339) 161 kV Bus KT Z1 b. 7. Run for 2.1 cycles, Trip branch from OAKPARK5 (515315) 161 kV Bus TO GERBRTP5 (515326) 161 kV Bus CKT 1 b. 8. Run for 1.2 cycles, Trip branch from MASSARD5 (515343) 161 kV Bus TO WHITESD5 (515341) 161 kV Bus CKT 1 b. 9. Run for 1.5 cycles, Trip branch from HELBERG5 (515327) 161 kV Bus TO PUDDIN 5 (515346) 161 kV Bus CKT 1 b. 10. Run for 3.9 cycles, Trip branch from BRANCH 5 (515316) 161 kV Bus TO GRNDPRT5 (515524) 161 kV Bus CKT 1 b. 11. Run for 1.62 cycles, Trip branch from ROLANRD2 (515257) 69 kV Bus TO ROLANTP2 (515277) 69 kV Bus CKT 1 b. 12. Run for 9.18 cycles, Trip branch from TAHLQH 5 (512655) 161 kV Bus TO HWY59TP5 (515527) 161 kV Bus CKT 1 b. 13. Run for 4.02 cycles, Trip branch from VAN BUR5 (505522) 161 kV Bus TO VBI 5 (515339) 161 kV Bus KT Z1 b. 14. Run for 4.2 cycles, Trip branch from OAKPARK5 (515315) 161 kV Bus TO GERBRTP5 (515326) 161 kV Bus CKT 1 b. 15. Run for 2.4 cycles, Trip branch from MASSARD5 (515343) 161 kV Bus TO WHITESD5 (515341) 161 kV Bus CKT 1 b. 16. Run for 0.18 cycles, Trip branch from ROLANRD2 (515257) 69 kV Bus TO ROLANTP2 (515277) 69 kV Bus CKT 1 b. 17. Run for 2.82 cycles, Trip branch from HELBERG5 (515327) 161 kV Bus TO PUDDIN 5 (515346) 161 kV Bus CKT 1 b. 18. Run for 6.36 cycles, Trip branch from TAHLQH 5 (512655) 161 kV Bus TO HWY59TP5 (515527) 161 kV Bus CKT 1 b. 19. Run for 1.44 cycles, Trip branch from BRANCH 5 (515316) 161 kV Bus TO GRNDPRT5 (515524) 161 kV Bus CKT 1 b. 20. Run for 19.38 cycles, Disconnect Bus VBI 1 (515769) 13.8 kV b. 21. Run for 23.82 cycles, Trip branch from ROLANRD2 (515257) 69 kV Bus TO ROLANTP2 (515277) 69 kV Bus CKT 1 b. 22. Run for 18.36 cycles, Trip branch from TAHLQH 5 (512655) 161 kV Bus TO HWY59TP5 (515527) 161 kV Bus CKT 1 b. 23. Clear fault at bus VBI 5 (515339) 161 kV Bus b. 24. Drop Load A1 Bus 504191 b. 25. Drop Load A1 Bus 504192 b. 26. Drop Load 1 Bus 515332 b. 27. Drop Load A1 Bus 515332 b. 28. Drop Load A1 Bus 515333 b. 29. Drop Load 1 Bus 515334 b. 30. Drop Load A1 Bus 515337 b. 31. Drop Load A1 Bus 515340 b. 32. Drop Load 1 Bus 515341 b. 33. Drop Load A1 Bus 515346 b. 34. Drop Load 1 Bus 515350 b. 35. Drop Load 1 Bus 515351 b. 36. Drop Load 1 Bus 515360 b. 37. Drop Load 1 Bus 515406 b. 38. Disconnect Bus 504191 b. 39. Disconnect Bus 504192 b. 40. Disconnect Bus 515326 b. 41. Disconnect Bus 515329 b. 42. Disconnect Bus 515332 b. 43. Disconnect Bus 515333 b. 44. Disconnect Bus 515334 b. 45. Disconnect Bus 515337 b. 46. Disconnect Bus 515340 b. 47. Disconnect Bus 515341 b. 48. Disconnect Bus 515346 b. 49. Disconnect Bus 515348 b. 50. Disconnect Bus 515350 b. 51. Disconnect Bus 515351 b. 52. Disconnect Bus 515360 b. 53. Disconnect Bus 515406 b. 54. Disconnect Bus 515524 b. 55. Disconnect Bus 515527 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_1103_P4 | a. Apply single-phase fault at WODWRD 2 (514782) 69 kV Bus b. 1. Run for 56.88 cycles, Trip WINDFRM4 (515785) 138 kV Bus TO WOODWRD4 (514785) 138 kV Bus CKT 1 b. 2. Run for 19.22 cycles, Disconnect Bus WOODWR21 (515771) 13.2 kV b. 3. Run for 0.66 cycles, Trip WINDFRM4 (515785) 138 kV Bus TO WOODWRD4 (514785) 138 kV Bus CKT 1 b. 4. Run for 49.74 cycles, Trip WODWRD 2 (514782) 69 kV Bus TO CEDARAV2 (514781) 69 kV Bus CKT 1 b. 5. Run for 7.14 cycles, Trip WINDFRM4 (515785) 138 kV Bus TO WOODWRD4 (514785) 138 kV Bus CKT 1 b. 6. Clear fault at WODWRD 2 (514782) 69 kV Bus c. 1. Apply single-phase fault at WODWRD 2 (514782) 69 kV Bus c. 2. Run for 12.84 cycles, Trip WODWRD 2 (514782) 69 kV Bus TO CEDARAV2 (514781) 69 kV Bus CKT 1 c. 3. Run for 126.6 cycles, Trip WODWRD 2 (514782) 69 kV Bus TO CEDARAV2 (514781) 69 kV Bus CKT 1 c. 4. Clear fault at WODWRD 2 (514782) 69 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_1104_P4 | a. Apply single-phase fault at CTNWOOD4 (514827) 138 kV Bus b. 1. Run for 22 cycles, Trip MCELROY4 (515009) 138 kV Bus TO UNVRSTY4 (515181) 138 kV Bus CKT 1 b. 2. Run for 3.96 cycles, Trip KETCH 4 (514834) 138 kV Bus TO KETCHTP4 (514828) 138 kV Bus CKT 1 b. 3. Run for 0.3 cycles, Trip CRESENT4 (515377) 138 kV Bus TO CTNWOOD4 (514827) 138 kV Bus CKT 1 b. 4. Run for 1.74 cycles, Trip KINZE 4 (515008) 138 kV Bus TO KINZEGR4 (512710) 138 kV Bus CKT 1 b. 5. Run for 0.3 cycles, Trip WOODRNG4 (514714) 138 kV Bus TO MARSHL 4 (514733) 138 kV Bus CKT 1 b. 6. Run for 10.38 cycles, Trip ARCADIA4 (514907) 138 kV Bus TO CTNWOOD4 (514827) 138 kV Bus CKT 1 b. 7. Run for 3.3 cycles, Trip MCELROY4 (515009) 138 kV Bus TO UNVRSTY4 (515181) 138 kV Bus CKT 1 b. 8. Run for 3.96 cycles, Trip KETCH 4 (514834) 138 kV Bus TO KETCHTP4 (514828) 138 kV Bus CKT 1 b. 9. Run for 0.3 cycles, Trip CRESENT4 515377) 138 kV Bus TO CTNWOOD4 (514827) 138 kV Bus CKT 1 b. 10. Run for 1.74 cycles, Trip KINZE 4 (515008) 138 kV Bus TO KINZEGR4 (512710) 138 kV Bus CKT 1 b. 11. Run for 0.3 cycles, Trip WOODRNG4 (514714) 138 kV Bus TO MARSHL 4 (514733) 138 kV Bus CKT 1 b. 12. Run for 9.3 cycles, Trip NORTWST4 (514879) 138 kV Bus TO KETCHTP4 (514828) 138 kV Bus CKT 1 b. 13. Run for 1.08 cycles, Trip ARCADIA4 (514907) 138 kV Bus TO CTNWOOD4 (514827) 138 kV Bus CKT 1 b. 14. Run for 5.34 cycles, Trip MCELROY4 (515009) 138 kV Bus TO UNVRSTY4 (515181) 138 kV Bus CKT 1 b. 15. Run for 7.92 cycles, Trip KETCH 4 (514834) 138 kV Bus TO KETCHTP4 (514828) 138 kV Bus CKT 1 b. 16. Run for 0.6 cycles, Trip CRESENT4 (515377) 138 kV Bus TO CTNWOOD4 (514827) 138 kV Bus CKT 1 b. 17. Run for 3.48 cycles, Trip KINZE 4 (515008) 138 kV Bus TO KINZEGR4 (512710) 138 kV Bus CKT 1 b. 18. Run for 0.6 cycles, Trip WOODRNG4 (514714) 138 kV Bus TO MARSHL 4 (514733) 138 kV Bus CKT 1 b. 19. Run for 0.96 cycles, Trip NORTWST4 (514879) 138 kV Bus TO KETCHTP4 (514828) 138 kV Bus CKT 1 b. 20. Run for 19.8 cycles, Trip ARCADIA4 (514907) 138 kV Bus TO CTNWOOD4 (514827) 138 kV Bus CKT 1 b. 21. Run for 37.8 cycles, Trip NORTWST4 (514879) 138 kV Bus TO KETCHTP4 (514828) 138 kV Bus CKT 1 b. 22. Clear fault at CTNWOOD4 ( 514827 ) 138 kV Bus b. 23. Drop Load 1 Bus 514827 b. 24. Drop Load 1 Bus 514829 b. 25. Drop Load 2 Bus 514829 b. 26. Drop Load 1 Bus 514830 b. 27. Drop Load 1 Bus 514831 b. 28. Drop Load 1 Bus 515181 b. 29. Drop Load 1 Bus 515373 b. 30. Drop Load 1 Bus 515466 b. 31. Drop Load 1 Bus 515467 b. 32. Drop Load 1 Bus 521006 b. 33. Disconnect Bus 514733 b. 34. Disconnect Bus 514827 b. 35. Disconnect Bus 514828 b. 36. Disconnect Bus 514829 b. 37. Disconnect Bus 514830 b. 38. Disconnect Bus 514831 b. 39. Disconnect Bus 515008 b. 40. Disconnect Bus 515181 b. 41. Disconnect Bus 515373 b. 42. Disconnect Bus 515466 b. 43. Disconnect Bus 515467 b. 44. Disconnect Bus 521006 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_1105_P4 | a. Apply single phase fault at CARPENTER 7 (523823) 345 kV CB OR335 Stuck b. Clear Fault after 16 cycles: b. 1. Trip branch from CARPENTER 7 (523823) 345 kV to FINNEY 7 (523853) 345 kV CKT 1 b. 2. Disconnect Bus CARPENTER 7 (523823) 345 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_1106_P4 | a. Apply single phase fault at CROSSROADS 7 (527656) 345 kV CB 6R30 Stuck b. Clear Fault after 16 cycles: b. 1. Trip branch from CROSSROADS 7 (527656) 345 kV to EDDY_CNTY 7 (527802) 345 kV CKT 1 b. 2. Trip branch from TOLK 7 (525549) 345 kV to CROSSROADS 7 (527656) 345 kV CKT 1 b. 3. Trip branch from RSVLT_CC_E 7 (527655) 345 kV to CROSSROADS 7 (527656) 345 kV CKT 1 b. 4. Disconnect Bus RSVLT_CC_E 7 (527655) 345 kV b. 5. Disconnect Bus MILO_WIND 1 (527653) 0.7 kV b. 6. Disconnect Bus RSVLT_GEN1 1 (527651) 0.69 kV b. 7. Disconnect Bus RSVLT_GEN2 1 (527652) 0.69 kV b. 8. Disconnect Bus RSVLT_CC_W 7 (527654) 345 kV b. 9. Disconnect Bus CROSSROADS 7 (527656) 345 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_1107_P4 | a. Apply single phase fault at EDDY_CNTY 7 (527802) 345 kV CB 4R00 Stuck b. Clear Fault after 16 cycles: b. 1. Trip branch from EDDY_CNTY 7 (527802) 345 kV to KIOWA 7 (527965) 345 kV CKT 1 b. 2. Trip branch from EDDY_CNTY 7 (527802) 345 kV to CROSSROADS 7 (527656) 345 kV CKT 1 b. 3. Trip three winding transformer from EDDY_TR 1 (527796) 13.2 kV to EDDY_NORTH 6 (527799) kV to EDDY_CNTY 7 (527802) 345 kV CKT1 b. 4. Disconnect Bus EDDY_TR 1 (527796) 13.2 kV b. 5. Disconnect Bus EDDY_CNTY 7 (527802) 345 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_1108_P4 | a. Apply single phase fault at EDDY_CNTY 7 (527802) 345 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from EDDY_CNTY 7 (527802) 345 kV to KIOWA 7 (527965) 345 kV CKT 1 b. 2. Trip branch from CROSSROADS 7 (527656) 345 kV to EDDY_CNTY 7 (527802) 345 kV CKT 1 b. 3. Disconnect Bus EDDY_TR 1 (527796) 13.2 kV b. 4. Disconnect Bus EDDY_CNTY 7 (527802) 345 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_1109_P4 | a. Apply single phase fault at EDDY_CNTY 7 (527802) 345 kV CB J24 Stuck b. Clear Fault after 16 cycles: b. 1. Trip three winding transformer from EDDY_TR 1 (527796) 13.2 kV to EDDY_NORTH 6 (527799) kV to EDDY_CNTY 7 (527802) 345 kV CKT1 b. 2. Trip branch from CROSSROADS 7 (527656) 345 kV to EDDY_CNTY 7 (527802) 345 kV CKT 1 b. 3. Trip branch from EDDY_CNTY 7 (527802) 345 kV to KIOWA 7 (527965) 345 kV CKT 1 b. 4. Disconnect Bus EDDY_TR 1 (527796) 13.2 kV b. 5. Disconnect Bus EDDY_CNTY 7 (527802) 345 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_1110_P4 | a. Apply single phase fault at EDDY_CNTY 7 (527802) 345 kV CB TF Stuck b. Clear Fault after 16 cycles: b. 1. Trip three winding transformer from EDDY_TR 1 (527796) 13.2 kV to EDDY_NORTH 6 (527799) kV to EDDY_CNTY 7 (527802) 345 kV CKT1 b. 2. Trip branch from EDDY_CNTY 7 (527802) 345 kV to KIOWA 7 (527965) 345 kV CKT 1 b. 3. Trip branch from EDDY_CNTY 7 (527802) 345 kV to CROSSROADS 7 (527656) 345 kV CKT 1 b. 4. Trip three winding transformer from EDDY_TR 1 (527796) 13.2 kV to EDDY_NORTH 6 (527799) kV to EDDY_CNTY 7 (527802) 345 kV CKT1 b. 5. Disconnect Bus EDDY_TR 1 (527796) 13.2 kV b. 6. Disconnect Bus EDDY_CNTY 7 (527802) 345 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_1111_P4 | a. Apply single phase fault at FINNEY 7 (523853) 345 kV CB OR70 Stuck b. Clear Fault after 16 cycles: b. 1. Trip branch from CARPENTER 7 (523823) 345 kV to FINNEY 7 (523853) 345 kV CKT 1 b. 2. Trip branch from FINNEY 7 (523853) 345 kV to HOLCOMB7 (531449) 345 kV CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_1112_P4 | a. Apply single phase fault at HITCHLAND 7 (523097) 345 kV CB 1R15 Stuck b. Clear Fault after 16 cycles: b. 1. Trip branch from HITCHLAND 7 (523097) 345 kV to POTTER_CO 7 (523961) 345 kV CKT 1 b. 2. Disconnect Bus NOBLE_TR 1 (523102) 13.8 kV b. 3. Disconnect Bus NOBLE_WND 3 (523103) 115 kV b. 4. Disconnect Bus GRPLNS-HV4-3 (523130) 115 kV b. 5. Disconnect Bus GRPLNS-HV2-3 (523131) 115 kV b. 6. Disconnect Bus GRPLNS-LV4-1 (523127) 34.5 kV b. 7. Disconnect Bus GRPLNS-LV2-1 (523129) 34.5 kV b. 8. Disconnect Bus GRPLNS-CB4-1 (523124) 34.5 kV b. 9. Disconnect Bus GRPLNS-CB2-1 (523126) 34.5 kV b. 10. Disconnect Bus GRPLNS-WT4-1 (523121) 0.575 kV b. 11. Disconnect Bus GRPLNS-WT2-1 (523123) 0.575 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_1113_P4 | a. Apply single phase fault at HITCHLAND 7 (523097) 345 kV CB 1R30 Stuck b. Clear Fault after 16 cycles: b. 1. Trip branch from HITCHLAND 7 (523097) 345 kV to CARPENTER 7 (523823) 345 kV CKT 1 b. 2. Drop Shunt 1 HITCHLAND 7 (523097) 345 kV b. 3. Trip three winding transformer from HITCHLD_TR21 (523094) 13.2 kV to HITCHLAND 6 (523095) kV to HITCHLAND 7 (523097) 345 kV CKT2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_1114_P4 | a. Apply single phase fault at HITCHLAND 7 (523097) 345 kV CB 1R75 Stuck b. Clear Fault after 16 cycles: b. 1. Trip branch from BVRCNTY7 (515554) 345 kV to HITCHLAND 7 (523097) 345 kV CKT 2 b. 2. Disconnect Bus NOVUS_WND 1 (523107) 4.16 kV b. 3. Disconnect Bus NOVUS1 1 (523109) 34.5 kV b. 4. Disconnect Bus NOVUS1 3 (523111) 115 kV b. 5. Disconnect Bus NOVUS1_TR1 1 (523110) 13.8 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_1115_P4 | a. Apply single phase fault at HOBBS_INT 7 (527896) 345 kV CB 4R240 Stuck b. Clear Fault after 16 cycles: b. 1. Trip branch from HOBBS_INT 7 (527896) 345 kV to KIOWA 7 (527965) 345 kV CKT 1 b. 2. Disconnect Bus HOBBS_TR3 1 (527895) 13.2 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_1117_P4 | a. Apply single phase fault at L.E.S.-7 (511468) 345 kV CB 3429B Stuck b. Clear Fault after 16 cycles: b. 1. Trip branch from L.E.S.-7 (511468) 345 kV to O.K.U.-7 (511456) 345 kV CKT 1 b. 2. Trip three winding transformer from LES#5-1 (511411) 13.8 kV to L.E.S.-4 (511467) kV to L.E.S.-7 (511468) 345 kV CKT2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Low voltage ride through fails due to the tripping of G18-115-GEN10 and G18-115-GEN20 units. No cascading was observed and the issue was localised. Model tuning is recommended.
04 - Southeast | 25W | Transfer | Group4_Fault_1118_P4 | a. Apply single phase fault at L.E.S.-7 (511468) 345 kV CB 3433A Stuck b. Clear Fault after 16 cycles: b. 1. Trip branch from L.E.S.-7 (511468) 345 kV to O.K.U.-7 (511456) 345 kV CKT 1 b. 2. Trip branch from L.E.S.-7 (511468) 345 kV to G17-171-TAP (760938) 345 kV CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Low voltage ride through fails due to the tripping of G18-115-GEN10 and G18-115-GEN20 units. No cascading was observed and the issue was localised. Model tuning is recommended. |  |  | Generator relays were disabled for the following generators: 584862 [G15-045-GEN10.4800], 762903 [G18-055-GEN10.6600]
04 - Southeast | 25W | Transfer | Group4_Fault_1119_P4 | a. Apply single phase fault at L.E.S.-7 (511468) 345 kV CB 3433A_2 Stuck b. Clear Fault after 16 cycles: b. 1. Trip branch from O.K.U.-7 (511456) 345 kV to L.E.S.-7 (511468) 345 kV CKT 1 b. 2. Trip branch from L.E.S.-7 (511468) 345 kV to G17-171-TAP (760938) 345 kV CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Low voltage ride through fails due to the tripping of G18-115-GEN10 and G18-115-GEN20 units. No cascading was observed and the issue was localised. Model tuning is recommended. |  |  | Generator relays were disabled for the following generators: 584862 [G15-045-GEN10.4800], 762903 [G18-055-GEN10.6600]
04 - Southeast | 25W | Transfer | Group4_Fault_1120_P4 | a. Apply single phase fault at N_LOVING 7 (528185) 345 kV CB 4S105 Stuck b. Clear Fault after 16 cycles: b. 1. Trip three winding transformer from NORTH_LOVNG3 (528182) 115 kV to N_LOVING 7 (528185) kV to N_LOVING TR1 (528186) 13.2 kV CKT1 b. 2. Trip branch from N_LOVING 7 (528185) 345 kV to CHINA_DRAW 7 (528223) 345 kV CKT 1 b. 3. Trip branch from KIOWA 7 (527965) 345 kV to N_LOVING 7 (528185) 345 kV CKT 1 b. 4. Disconnect Bus N_LOVING TR1 (528186) 13.2 kV b. 5. Disconnect Bus N_LOVING 7 (528185) 345 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_1121_P4 | a. Apply single phase fault at N_LOVING 7 (528185) 345 kV CB 4S110 Stuck b. Clear Fault after 16 cycles: b. 1. Trip three winding transformer from NORTH_LOVNG3 (528182) 115 kV to N_LOVING 7 (528185) kV to N_LOVING TR1 (528186) 13.2 kV CKT1 b. 2. Trip branch from KIOWA 7 (527965) 345 kV to N_LOVING 7 (528185) 345 kV CKT 1 b. 3. Trip branch from N_LOVING 7 (528185) 345 kV to CHINA_DRAW 7 (528223) 345 kV CKT 1 b. 4. Trip three winding transformer from NORTH_LOVNG3 (528182) 115 kV to N_LOVING 7 (528185) kV to N_LOVING TR1 (528186) 13.2 kV CKT1 b. 5. Disconnect Bus N_LOVING TR1 (528186) 13.2 kV b. 6. Disconnect Bus N_LOVING 7 (528185) 345 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_1122_P4 | a. Apply single phase fault at N_LOVING 7 (528185) 345 kV CB 4S120 Stuck b. Clear Fault after 16 cycles: b. 1. Trip branch from N_LOVING 7 (528185) 345 kV to CHINA_DRAW 7 (528223) 345 kV CKT 1 b. 2. Trip branch from KIOWA 7 (527965) 345 kV to N_LOVING 7 (528185) 345 kV CKT 1 b. 3. Trip three winding transformer from NORTH_LOVNG3 (528182) 115 kV to N_LOVING 7 (528185) kV to N_LOVING TR1 (528186) 13.2 kV CKT1 b. 4. Disconnect Bus N_LOVING TR1 (528186) 13.2 kV b. 5. Disconnect Bus N_LOVING 7 (528185) 345 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_1123_P4 | a. Apply single phase fault at BATTLEFIELD5 (549959) 161 kV CB 111 Stuck b. Clear Fault after 16 cycles: b. 1. Trip branch from GOLDEN 2 (549911) 69 kV to BATTLEFIELD2 (549979) 69 kV CKT 1 b. 2. Trip branch from DAYTON 2 (549913) 69 kV to BATTLEFIELD2 (549979) 69 kV CKT 1 b. 3. Trip branch from MAIN STREET5 (549958) 161 kV to BATTLEFIELD5 (549959) 161 kV CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_1124_P4 | a. Apply single phase fault at O.K.U.-7 (511456) 345 kV CB 3409A Stuck b. Clear Fault after 16 cycles: b. 1. Trip branch from O.K.U.-7 (511456) 345 kV to L.E.S.-7 (511468) 345 kV CKT 1 b. 2. Trip branch from O.K.U.-7 (511456) 345 kV to G18-092-TAP (763215) 345 kV CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_1125_P4 | a. Apply single phase fault at POTTER_CO 7 (523961) 345 kV CB 2R05 Stuck b. Clear Fault after 16 cycles: b. 1. Trip branch from HITCHLAND 7 (523097) 345 kV to POTTER_CO 7 (523961) 345 kV CKT 1 b. 2. Trip three winding transformer from POTTER_TR 1 (523957) 13.2 kV to POTTER_CO 6 (523959) kV to POTTER_CO 7 (523961) 345 kV CKT1 b. 3. Disconnect Bus BUFF_DUNES23 (523061) 0.69 kV b. 4. Disconnect Bus SPNSPUR_WND7 (524296) 345 kV b. 5. Disconnect Bus SPNSPUR_GEN1 (524295) 0.69 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_1126_P4 | a. Apply single phase fault at BVRCNTY7 (515554) 345 kV CB PRE19S Stuck b. Clear Fault after 16 cycles: b. 1. Trip branch from BVRCNTY7 (515554) 345 kV to HITCHLAND 7 (523097) 345 kV CKT 1 b. 2. Trip branch from BVRCNTY7 (515554) 345 kV to HITCHLAND 7 (523097) 345 kV CKT 2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_1127_P4 | a. Apply single phase fault at TUCO_INT 7 (525832) 345 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from TUCO_INT 7 (525832) 345 kV to YOAKUM_345 (526936) 345 kV CKT 1 b. 2. Disconnect Bus ELK_CT1 (525850) 345 kV b. 3. Disconnect Bus ELK_1 1 (525844) 18 kV b. 4. Disconnect Bus ELK_2 1 (525845) 18 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 763084 [G18-073-GEN20.6600]
04 - Southeast | 25W | Transfer | Group4_Fault_1128_P4 | a. Apply single phase fault at TUCO_INT 7 (525832) 345 kV CB NR05 Stuck b. Clear Fault after 16 cycles: b. 1. Disconnect Bus TUCO_TR1 1 (525824) 13.2 kV b. 2. Trip branch from CRAWFISH_DR (560022) 345 kV to TUCO_INT 7 (525832) 345 kV CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 763084 [G18-073-GEN20.6600]
04 - Southeast | 25W | Transfer | Group4_Fault_1129_P4 | a. Apply single phase fault at TUCO_INT 7 (525832) 345 kV CB NR20 Stuck b. Clear Fault after 16 cycles: b. 1. Disconnect Bus TUCO_TR1 1 (525824) 13.2 kV b. 2. Trip branch from CRAWFISH_DR (560022) 345 kV to TUCO_INT 7 (525832) 345 kV CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 763084 [G18-073-GEN20.6600]
04 - Southeast | 25W | Transfer | Group4_Fault_1130_P4 | a. Apply single phase fault at YOAKUM_345 (526936) 345 kV CB J17 Stuck b. Clear Fault after 16 cycles: b. 1. Trip three winding transformer from YOAKUM 6 (526935) 230 kV to YOAKUM_345 (526936) kV to YOAKUM_TR1 (526937) 13.2 kV CKT1 b. 2. Trip branch from TUCO_INT 7 (525832) 345 kV to YOAKUM_345 (526936) 345 kV CKT 1 b. 3. Trip branch from YOAKUM_345 (526936) 345 kV to HOBBS_INT 7 (527896) 345 kV CKT 1 b. 4. Disconnect Bus YOAKUM_TR1 (526937) 13.2 kV b. 5. Disconnect Bus YOAKUM_345 (526936) 345 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_1131_P4 | a. Apply single phase fault at YOAKUM_345 (526936) 345 kV CB J18 Stuck b. Clear Fault after 16 cycles: b. 1. Trip branch from TUCO_INT 7 (525832) 345 kV to YOAKUM_345 (526936) 345 kV CKT 1 b. 2. Trip branch from YOAKUM_345 (526936) 345 kV to HOBBS_INT 7 (527896) 345 kV CKT 1 b. 3. Trip three winding transformer from YOAKUM 6 (526935) 230 kV to YOAKUM_345 (526936) kV to YOAKUM_TR1 (526937) 13.2 kV CKT1 b. 4. Disconnect Bus YOAKUM_TR1 (526937) 13.2 kV b. 5. Disconnect Bus YOAKUM_345 (526936) 345 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_1132_P4 | a. Apply single phase fault at YOAKUM_345 (526936) 345 kV CB J18_2 Stuck b. Clear Fault after 16 cycles: b. 1. Trip branch from TUCO_INT 7 (525832) 345 kV to YOAKUM_345 (526936) 345 kV CKT 1 b. 2. Trip branch from YOAKUM_345 (526936) 345 kV to HOBBS_INT 7 (527896) 345 kV CKT 1 b. 3. Disconnect Bus YOAKUM_TR1 (526937) 13.2 kV b. 4. Disconnect Bus YOAKUM_345 (526936) 345 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_1133_P4 | a. Apply single phase fault at YOAKUM_345 (526936) 345 kV CB TF Stuck b. Clear Fault after 16 cycles: b. 1. Trip three winding transformer from YOAKUM 6 (526935) 230 kV to YOAKUM_345 (526936) kV to YOAKUM_TR1 (526937) 13.2 kV CKT1 b. 2. Trip branch from YOAKUM_345 (526936) 345 kV to HOBBS_INT 7 (527896) 345 kV CKT 1 b. 3. Trip branch from TUCO_INT 7 (525832) 345 kV to YOAKUM_345 (526936) 345 kV CKT 1 b. 4. Trip three winding transformer from YOAKUM 6 (526935) 230 kV to YOAKUM_345 (526936) kV to YOAKUM_TR1 (526937) 13.2 kV CKT1 b. 5. Disconnect Bus YOAKUM_TR1 (526937) 13.2 kV b. 6. Disconnect Bus YOAKUM_345 (526936) 345 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_1134_P4 | a. Apply single-phase fault at BULL SH5 (505460) 161 kV Bus b. 1. Run for 5 cycles, Trip branch from Bus NORFORK5 (505448) 161 kV Bus TO 5SOUTHLAND# (338814) 161 kV Bus CKT 1 b. 2. Clear fault and run for 12 cycles, Disconnect Bus BULL SH5 (505460) 161 kV b. 3. Drop Generator 1 Bus 505462 b. 4. Drop Generator 2 Bus 505464 b. 5. Drop Generator 3 Bus 505466 b. 6. Drop Generator 4 Bus 505466 b. 7. Drop Load 1 Bus 338125 b. 8. Drop Load A1 Bus 338813 b. 9. Drop Load A1 Bus 338814 b. 10. Disconnect Bus 338125 b. 11. Disconnect Bus 338606 b. 12. Disconnect Bus 338607 b. 13. Disconnect Bus 338608 b. 14. Disconnect Bus 338609 b. 15. Disconnect Bus 338813 b. 16. Disconnect Bus 338814 b. 17. Disconnect Bus 505462 b. 18. Disconnect Bus 505464 b. 19. Disconnect Bus 505466 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_1135_P4 | a. Apply single-phase fault at BULL SH5 (505460) 161 kV Bus b. 1. Run for 5 Cycles, Trip branch from Bus 5HARRISON.E! (338104) 161 kV To Bus 5SUMMIT (338121) 161 kV CKT 1 b. 2. Clear fault and run for 12 cycles, Disconnect Bus BULL SH5 (505460) 161 kV b. 3. Drop Generator 1 Bus 505462 b. 4. Drop Generator 2 Bus 505464 b. 5. Drop Generator 3 Bus 505466 b. 6. Drop Generator 4 Bus 505466 b. 7. Drop Load 1 Bus 338121 b. 8. Drop Load 1 Bus 338122 b. 9. Drop Load 1 Bus 338124 b. 10. Disconnect Bus 338121 b. 11. Disconnect Bus 338122 b. 12. Disconnect Bus 338123 b. 13. Disconnect Bus 338124 b. 14. Disconnect Bus 505462 b. 15. Disconnect Bus 505464 b. 16. Disconnect Bus 505466 b. 17. Drop Load A1 Bus 338813 b. 18. Disconnect Bus 338813 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_1136_P4 | a. Apply single-phase fault at BULL SH5 (505460) 161 kV Bus b. 1. Run for 5 cycles, Trip branch from Bus 5MANSFDMN (300095) 161 kV To Bus 5GAINES (300081) 161 kV CKT 1 b. 2. Clear fault and run for 12 cycles, Disconnect Bus BULL SH5 (505460) 161 kV b. 3. Drop Generator 1 Bus 505462 b. 4. Drop Generator 2 Bus 505464 b. 5. Drop Generator 3 Bus 505466 b. 6. Drop Generator 4 Bus 505466 b. 7. Disconnect Bus 505462 b. 8. Disconnect Bus 505464 b. 9. Disconnect Bus 505466 b. 10. Drop Load A1 Bus 338813 b. 11. Disconnect Bus 338813 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_1137_P4 | a. Apply single-phase fault at TABLE R5 (505472) 161 kV b. 1. Run for 5 cycles, Trip branch from Bus BULL SH W5 (505461) 161 kV To Bus 5S.LEAD HILL (338120) 161 kV CKT 1 b. 2. Clear fault and run for 12 cycles, Disconnect Bus TABLE R5 (505472) 161 kV b. 3. Drop Generator 1 Bus 505476 b. 4. Drop Generator 2 Bus 505476 b. 5. Drop Generator 3 Bus 505478 b. 6. Drop Generator 4 Bus 505478 b. 7. Drop Load 1 Bus 300718 b. 8. Drop Load 1 Bus 338120 b. 9. Disconnect Bus 300718 b. 10. Disconnect Bus 338120 b. 11. Disconnect Bus 505473 b. 12. Disconnect Bus 505475 b. 13. Disconnect Bus 505476 b. 14. Disconnect Bus 505478 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_1138_P4 | a. Apply single-phase fault at TABLE R5 (505472) 161 kV b. 1. Run for 5 cycles, Open Line From Bus 5RENOHLWTP (300130) 161 kV To Bus 5RIVERSIDE (300805) 161 kV CKT 1 b. 2. Clear fault and run for 12 cycles, Disconnect Bus TABLE R5 (505472) 161 kV b. 3. Drop Generator 1 Bus 505476 b. 4. Drop Generator 2 Bus 505476 b. 5. Drop Generator 3 Bus 505478 b. 6. Drop Generator 4 Bus 505478 b. 7. Disconnect Bus 505473 b. 8. Disconnect Bus 505475 b. 9. Disconnect Bus 505476 b. 10. Disconnect Bus 505478 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_1139_P4 | a. Apply single-phase fault at TABLE R5 (505472) 161 kV Run For 5.0 Cycles, Open Line From Bus 5GRANDVIEW% (338099) 161 kV To Bus TABLE R5 (505472) 161 kV CKT 1 b. 2. Clear fault and run for 12 cycles, Disconnect Bus TABLE R5 (505472) 161 kV b. 3. Drop Generator 1 Bus 505476 b. 4. Drop Generator 2 Bus 505476 b. 5. Drop Generator 3 Bus 505478 b. 6. Drop Generator 4 Bus 505478 b. 7. Disconnect Bus 505473 b. 8. Disconnect Bus 505475 b. 9. Disconnect Bus 505476 b. 10. Disconnect Bus 505478 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_1140_P4 | a. Apply single-phase fault at TABLE R5 (505472) 161 kV b. 1. Run For 5.0 Cycles, Open Line From Bus NIXA 5 (505496) 161 kV To Bus TABLE R5 (505472) 161 CKT 1 b. 2. Clear fault and run for 12 cycles, Disconnect Bus TABLE R5 (505472) 161 kV b. 3. Drop Generator 1 Bus 505476 b. 4. Drop Generator 2 Bus 505476 b. 5. Drop Generator 3 Bus 505478 b. 6. Drop Generator 4 Bus 505478 b. 7. Disconnect Bus 505473 b. 8. Disconnect Bus 505475 b. 9. Disconnect Bus 505476 b. 10. Disconnect Bus 505478 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_1141_P4 | a. Apply single-phase fault at TABLE R5 (505472) 161 kV b. 1. Run for 5 cycles, Open Line From Bus RVS438 5 (547497) 161 kV To TABLE R5 (505472) 161 kV Bus CKT 1 b. 2. Clear fault and run for 12 cycles, Disconnect Bus TABLE R5 (505472) 161 kV b. 3. Drop Generator 1 Bus 505476 b. 4. Drop Generator 2 Bus 505476 b. 5. Drop Generator 3 Bus 505478 b. 6. Drop Generator 4 Bus 505478 b. 7. Disconnect Bus 505473 b. 8. Disconnect Bus 505475 b. 9. Disconnect Bus 505476 b. 10. Disconnect Bus 505478 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_1142_P4 | a. Apply single-phase fault at TABLE R5 (505472) 161 kV b. 1. Run for 5 cycles, Trip Three winding transformer from TABLE R5 (505472) 161 kV To Bus TABLE R2 (505474) 69 kV To Bus TBR X1 1 (505473) 13.8 kV CKT 1 b. 2. Run For 12.0 cycles, Trip Three winding transformer from TABLE R5 (505472) 161 kV To Bus TABLE R2 (505474) 69 kV To Bus TBR X2 1 (505475) 13.8 kV CKT 1 b. 3. Clear fault at TABLE R5 (505472) 161 kV b. 4. Disconnect Bus TBR X1 1 (505473) 13.8 kV b. 5. Drop Generator 1 Bus 505476 b. 6. Drop Generator 2 Bus 505476 b. 7. Drop Generator 3 Bus 505478 b. 8. Drop Generator 4 Bus 505478 b. 7. Disconnect Bus 505473 b. 9. Disconnect Bus 505475 b. 10. Disconnect Bus 505476 b. 11. Disconnect Bus 505478 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_1143_P4 | a. Apply single-phase fault at BULL SH W5 (505461) 161 kV Bus b. 1. Run for 5 cycles, Trip branch from Bus TABLE R5 (505472) 161 kV To Bus 5CLEVCOV (300718) 161 kV CKT 1 b. 2. Clear fault and run for 12 cycles, Disconnect Bus BULL SH W5 (505461) 161 kV b. 3. Drop Generator 5 Bus 505468 b. 4. Drop Generator 6 Bus 505468 b. 5. Drop Generator 7 Bus 505470 b. 6. Drop Generator 8 Bus 505470 b. 7. Drop Load 1 Bus 300718 b. 8. Drop Load 1 Bus 338120 b. 9. Disconnect Bus 300718 b. 10. Disconnect Bus 338120 b. 11. Disconnect Bus 505468 b. 12. Disconnect Bus 505470 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_1144_P4 | a. Apply single-phase fault at BULL SH W5 (505461) 161 kV Bus b. 1. Run for 5 cycles, Trip branch from Bus NORFORK5 (505448) 161 kV To Bus BUFORD 5 (504440) 161 kV CKT 1 b. 2. Clear fault and run for 12 cycles, Disconnect Bus BULL SH W5 (505461) 161 kV b. 3. Drop Generator 5 Bus 505468 b. 4. Drop Generator 6 Bus 505468 b. 5. Drop Generator 7 Bus 505470 b. 6. Drop Generator 8 Bus 505470 b. 7. Drop Load A1 Bus 504440 b. 8. Disconnect Bus 504440 b. 9. Disconnect Bus 505468 b. 10. Disconnect Bus 505470 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_1145_P4 | a. Apply single-phase fault at BULL SH W5 (505461) 161 kV Bus Run For 5 Cycles, Trip branch from Bus 5HILLTOP% (338110) 161 kV To Bus BULL SH W5 (505461) 161 kV CKT 1 b. 2. Clear fault and run for 12 cycles, Disconnect Bus BULL SH W5 (505461) 161 kV b. 3. Drop Generator 5 Bus 505468 b. 4. Drop Generator 6 Bus 505468 b. 5. Drop Generator 7 Bus 505470 b. 6. Drop Generator 8 Bus 505470 b. 7. Disconnect Bus 505468 b. 8. Disconnect Bus 505470 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_1146_P4 | a. Apply single-phase fault at BATTLEFIELD2 (549979) 69 kV b. 1. Run for 8 cycles: b. 2. Trip branch from GOLDEN 2 (549911) 69 kV Bus TO BATTLEFIELD2 (549979) 69 kV Bus CKT 1 b. 3. Trip branch from DAYTON 2 (549913) 69 kV Bus TO BATTLEFIELD2 (549979) 69 kV Bus CKT 1 b. 4. Clear fault and run for 10 cycles, Trip branch from MAIN STREET5 (549958) 161 kV Bus TO BATTLEFIELD5 (549959) 161 kV Bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_1147_P4 | a. Apply single-phase fault at CARPENTER 7 (523823) 345 kV Bus CB OR335 Stuck b. Clear Fault after 21 cycles: b. 1. Trip branch from CARPENTER 7 (523823) 345 kV Bus TO FINNEY 7 (523853) 345 kV Bus CKT 1 b. 2. Clear fault and Disconnect CARPENTER 7 (523823) 345 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_1148_P4 | a. Apply single-phase fault at CROSSROADS 7 (527656) 345 kV CB 6R30 Stuck b. Clear Fault after 21 cycles: b. 1. Trip branch from EDDY_CNTY 7 (527802) 345 kV Bus TO CROSSROADS 7 (527656) 345 kV Bus CKT 1 b. 2. Trip branch from TOLK 7 (525549) 345 kV Bus TO CROSSROADS 7 (527656) 345 kV Bus CKT 1 b. 3. Disconnect Bus RSVLT_CC_E 7 (527655) 345 kV b. 4. Disconnect Bus MILO_WIND 1 (527653) 0.70 kV b. 5. Disconnect Bus RSVLT_GEN1 1 (527651) 0.69 kV b. 6. Disconnect Bus RSVLT_GEN2 1 (527652) 0.69 kV b. 7. Disconnect Bus RSVLT_CC_W 7 (527654) 345 kV b. 8. Drop Generator 1 Bus SAGSFT3_2.21 (527605) 0.70 kV b. 9. Drop Generator 1 Bus SAGSFT4_2.21 (527607) 0.70 kV b. 10. Drop Generator 1 Bus SAGSFT1_2.21 (527614) 0.70 kV b. 11. Drop Generator 1 Bus SAGSFT1_2.01 (527615) 0.70 kV b. 12. Drop Generator 1 Bus SAGSFT2_2.21 (527617) 0.70 kV b. 13. Drop Generator 1 Bus SAGSFT2_2.01 (527618) 0.70 kV b. 14. Drop Load 1 Bus SAGA_SCOL 7 (527610) 345 kV b. 15. Drop Load 2 Bus SAGA_SCOL 7 (527610) 345 kV b. 16. Disconnect Bus SAGA_NDCOL 7 (527598) 345 kV b. 17. Disconnect Bus SAGA_SDCOL 7 (527599) 345 kV b. 18. Disconnect Bus SAGA_SMEAS 7 (527600) 345 kV b. 19. Disconnect Bus SAGA_NCOL 7 (527601) 345 kV b. 20. Disconnect Bus SAGANCOL1 1 (527602) 34.5 kV b. 21. Disconnect Bus SAGANCOL2 1 (527603) 34.5 kV b. 22. Disconnect Bus GRDXFR3 1 (527604) 0.50 kV b. 23. Disconnect Bus SAGSFT3_2.21 (527605) 0.70 kV b. 24. Disconnect Bus GRDXFR4 1 (527606) 0.50 kV b. 25. Disconnect Bus SAGSFT4_2.21 (527607) 0.70 kV b. 26. Disconnect Bus SUB BUS #3 1 (527608) 34.5 kV b. 27. Disconnect Bus SUB BUS #4 1 (527609) 34.5 kV b. 28. Disconnect Bus SAGA_SCOL 7 (527610) 345 kV b. 29. Disconnect Bus SAGASCOL1 1 (527611) 34.5 kV b. 30. Disconnect Bus SAGASCOL2 1 (527612) 34.5 kV b. 31. Disconnect Bus GRDXFR1 1 (527613) 0.50 kV b. 32. Disconnect Bus SAGSFT1_2.21 (527614) 0.70 kV b. 33.Disconnect Bus SAGSFT1_2.01 (527615) 0.70 kV b. 34. Disconnect Bus GRDXFR2 1 (527616) 0.50 kV b. 35. Disconnect Bus SAGSFT2_2.21 (527617) 0.70 kV b. 36. Disconnect Bus SAGSFT2_2.01 (527618) 0.70 kV b. 37. Disconnect Bus SAGA_NCLTR31 (527621) 13.8 kV b. 38. Disconnect Bus SAGA_NCLTR41 (527622) 13.8 kV b. 39. Disconnect Bus SAGA_SCLTR11 (527623) 13.8 kV b. 40. Disconnect Bus SAGA_SCLTR21 (527624) 13.8 kV b. 41. Disconnect Bus SUB BUS #1 (527628) 34.5 kV b. 42. Disconnect Bus SUB BUS #2 (527629) 34.5 kV b. 43. Disconnect Bus CROSSROADS 7 (527656) 345 kV b. 44. Disconnect Bus RSVLT_WIND11 (527658) 34.5 kV b. 45. Disconnect Bus RSVLT_WIND21 (527659) 34.5 kV b. 46. Disconnect Bus RSVLT_COL1 1 (527660) 34.5 kV b. 47. Disconnect Bus RSVLT_COL2 1 (527661) 34.5 kV b. 48. Disconnect Bus RSVLT_TR1 1 (527662) 13.2 kV b. 49. Disconnect Bus RSVLT_TR2 1 (527663) 13.2 kV b. 50. Disconnect Bus RSVLT_COL1 7 (527666) 345 kV b. 51. Disconnect Bus RSVLT_COL2 7 (527667) 345 kV b. 52. Disconnect Bus MILO_CB (577120) 34.5 kV b. 53. Disconnect Bus MILO_WND (577121) 34.5 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_1150_P4 | a. Apply single-phase fault at CHINA_DRAW 7 (528223) 345 kV Bus CB 4T805 Stuck b. Clear Fault after 16 cycles: b. 1. Trip branch from CHINA_DRAW 7 (528223) 345 kV Bus TO PHANTOM 7 (528015) 345 kV Bus CKT 1 b. 2. Disconnect Bus CHINA_DRAW 1 (528219) 13.2 kV b. 3. Disconnect Bus CARPENTER 7 (523823) 345 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_1151_P4 | a. Apply single-phase fault at CHINA_DRAW 7 (528223) 345 kV Bus CB TF#### Stuck b. 1. Run for 5 cycles, Disconnect Bus CHINA_DRAW 1 (528219) 13.2 kV b. 2. Run for 11 cycles, Trip branch from CHINA_DRAW 7 (528223) 345 kV Bus TO N_LOVING 7 (528185) 345 kV Bus CKT 1 b. 3. Clear fault and run for 5 cycles, Trip branch from CHINA_DRAW 7 (528223) 345 kV Bus TO PHANTOM 7 (528015) 345 kV Bus CKT 1 b. 4. Disconnect Bus CHINA_DRAW 1 (528219) 13.2 kV b. 5. Disconnect Bus CARPENTER 7 (523823) 345 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_1152_P4 | a. Apply single-phase fault at CHINA_DRAW 7 (528223) 345 kV Bus CB J27#### Stuck b. 1. Run for 16 cycles, Disconnect Bus CHINA_DRAW 1 (528219) 13.2 kV b. 2. Clear fault and run for 5 cycles: b. 3. Trip branch from CHINA_DRAW 7 (528223) 345 kV Bus TO N_LOVING 7 (528185) 345 kV Bus CKT 1 b. 4. Trip branch from CHINA_DRAW 7 (528223) 345 kV Bus TO PHANTOM 7 (528015) 345 kV Bus CKT 1 b. 5. Disconnect Bus CHINA_DRAW 1 (528219) 13.2 kV b. 6. Disconnect Bus CARPENTER 7 (523823) 345 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_1153_P4 | a. Apply single-phase fault at EDDY_CNTY 7 (527802) 345 kV Bus CB 4R00 Stuck b. 1. Run for 16 cycles, Trip branch from EDDY_CNTY 7 (527802) 345 kV Bus TO KIOWA 7 (527965) 345 kV Bus CKT 1 b. 2. Clear fault and run for 5 cycles, Trip branch from EDDY_CNTY 7 (527802) 345 kV Bus TO CROSSROADS 7 (527656) 345 kV Bus CKT 1 b. 3. Disconnect Bus EDDY_TR 1 (527796) 13.2 kV b. 4. Disconnect Bus EDDY_CNTY 7 (527802) 345 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_1154_P4 | a. Apply single-phase fault at EDDY_CNTY 7 (527802) 345 kV Bus CB J24#### Stuck b. 1. Run for 16 cycles, Disconnect Bus EDDY_TR 1 (527796) 13.2 kV b. 2. Clear fault and run for 5 cycles: b. 3. Trip branch from EDDY_CNTY 7 (527802) 345 kV Bus TO CROSSROADS 7 (527656) 345 kV Bus CKT 1 b. 4. Trip branch from EDDY_CNTY 7 (527802) 345 kV Bus TO KIOWA 7 (527965) 345 kV Bus CKT 1 b. 5. Disconnect Bus EDDY_TR 1 (527796) 13.2 kV b. 6. Disconnect Bus EDDY_CNTY 7 (527802) 345 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_1155_P4 | a. Apply single-phase fault at EDDY_CNTY 7 (527802) 345 kV Bus CB TF#### Stuck b. 1. Run for 5 cycles, Disconnect Bus EDDY_TR 1 (527796) 13.2 kV b. 2. Run for 11 cycles, Trip branch from EDDY_CNTY 7 (527802) 345 kV Bus TO CROSSROADS 7 (527656) 345 kV Bus CKT 1 b. 3. Clear fault and run for 5 cycles, Trip branch from EDDY_CNTY 7 (527802) 345 kV Bus TO KIOWA 7 (527965) 345 kV Bus CKT 1 b. 4. Disconnect Bus EDDY_TR 1 (527796) 13.2 kV b. 5. Disconnect Bus EDDY_CNTY 7 (527802) 345 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_1156_P4 | a. Apply single-phase fault at FINNEY 7 (523853) 345 kV Bus CB OR70 Stuck b. Clear Fault after 21 cycles: b. 1. Trip branch from HOLCOMB7 (531449) 345 kV Bus TO FINNEY 7 (523853) 345 kV Bus CKT 1 b. 2. Trip branch from CARPENTER 7 (523823) 345 kV TO FINNEY 7 (523853) 345 kV Bus CKT 1 b. 3. Disconnect Bus 523853 b. 4. Disconnect Bus 599950 b. 5. Disconnect Bus 599951 b. 6. Disconnect Bus 523118 b. 7. Disconnect Bus 523114 b. 8. Disconnect Bus 523115 b. 9. Disconnect Bus 523116 b. 10. Disconnect Bus 523117 b. 11. Drop Generator 1 Bus 523061 b. 12. Drop Generator 1 Bus 523062 b. 13. Disconnect Bus 523061 b. 14. Disconnect Bus 523062 b. 15. Disconnect Bus 523063 b. 16. Disconnect Bus 523064 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_1157_P4 | a. Apply single-phase fault at HITCHLAND 7 (523097) 345 kV Bus CB 1R75 Stuck b. Clear Fault after 21 cycles: b. 1. Trip branch from HITCHLAND 7 (523097) 345 kV Bus TO BVRCNTY7 (515554) 345 kV Bus CKT 2 b. 2. Disconnect Bus 523112 b. 3. Disconnect Bus 523111 b. 4. Disconnect Bus 523109 b. 5. Disconnect Bus 523107 b. 6. Disconnect Bus 523110 b. 7. Drop Generator 1 Bus 523107 b. 8. Drop Load A1 Bus 523107 b. 9. Drop Generator 1 Bus 560585 b. 10. Drop Generator 1 Bus 560586 b. 11. Disconnect Bus 560577 b. 12. Disconnect Bus 560582 b. 13. Disconnect Bus 560585 b. 14. Disconnect Bus 560583 b. 15. Disconnect Bus 560586 b. 16. Disconnect Bus 560578 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_1158_P4 | a. Apply single-phase fault at HOBBS_INT 7 (527896) 345 kV Bus CB 4R240 Stuck b. Clear Fault after 21 cycles: b. 1. Trip branch from HOBBS_INT 7 (527896) 345 kV Bus TO KIOWA 7 (527965) 345 kV Bus CKT 1 b. 2. Trip branch from HOBBS_INT 7 (527896) 345 kV Bus TO YOAKUM_345 (526936) 345 kV Bus CKT 1 b. 3. Disconnect Bus HOBBS_TR3 1 (527895) 13.2 kV b. 4. Disconnect Bus HOBBS_INT 7 (527896) 345 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_1159_P4 | a. Apply single-phase fault at POTTER_CO 7 (523961) 345 kV Bus CB 2R05 Stuck b. Clear Fault after 21 cycles: b. 1. Trip branch from HITCHLAND 7 (523097) 345 kV Bus TO POTTER_CO 7 (523961) 345 kV Bus CKT 1 b. 2. Disconnect bus 523957 b. 3. Disconnect bus 523957 b. 4. Disconnect bus 523961 b. 5. Disconnect bus 524296 b. 6. Disconnect bus 524299 b. 7. Disconnect bus 524298 b. 8. Disconnect bus 524294 b. 9. Disconnect bus 524295 b. 10. Disconnect bus 524297 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_1160_P4 | a. Apply single-phase fault at YOAKUM_345 (526936) 345 kV Bus CB J18#### Stuck b. 1. Run for 16 cycles, Trip branch from YOAKUM_345 (526936) 345 kV Bus TO TUCO_INT 7 (525832) 345 kV Bus CKT 1 b. 2. Clear fault and run for 5 cycles, Tri branch from YOAKUM_345 (526936) 345 kV Bus TO HOBBS_INT 7 (527896) 345 kV Bus CKT 1 b. 3. Disconnect Bus YOAKUM_TR1 (526937) 13.2 kV b. 4. Disconnect Bus YOAKUM_345 (526936) 345 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_1161_P4 | a. Apply single-phase fault at YOAKUM_345 (526936) 345 kV Bus CB TF##### Stuck b. 1. Run for 5 cycles, Disconnect Bus YOAKUM_TR1 (526937) 13.2 kV b. 2. Run for 11 cycles, Trip branch from YOAKUM_345 (526936) 345 kV Bus TO HOBBS_INT 7 (527896) 345 kV Bus CKT 1 b. 3. Clear fault and run for 5 cycles, Trip branch from YOAKUM_345 (526936) 345 kV Bus TO TUCO_INT 7 (525832) 345 kV Bus CKT 1 b. 4. Disconnect Bus YOAKUM_345 (526936) 345 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_1162_P4 | a. Apply single-phase fault at YOAKUM_345 (526936) 345 kV Bus CB J17#### Stuck b. 1. Run for 16 cycles, Disconnect Bus YOAKUM_TR1 (526937) 13.2 kV b. 2. Clear fault and run for 5 cycles: b. 3. Trip branch from YOAKUM_345 (526936) 345 kV Bus TO TUCO_INT 7 (525832) 345 kV Bus CKT 1 b. 4. Trip branch from YOAKUM_345 (526936) 345 kV Bus TO HOBBS_INT 7 (527896) 345 kV Bus CKT 1 b. 5. Disconnect Bus YOAKUM_345 (526936) 345 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_1163_P4 | a. Apply single-phase fault at TUCO_INT 7 (525832) 345 kV Bus CB NR20 Stuck b. 1. Run for 5 cycles, Disconnect Bus TUCO_TR1 1 (525824) 13.2 kV b. 2. Clear fault and run for 11 cycles, Trip branch from TUCO_INT 7 (525832) 345 kV Bus TO CRAWFISH_DR (560022) 345 kV Bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 763084 [G18-073-GEN20.6600]
04 - Southeast | 25W | Transfer | Group4_Fault_1164_P4 | a. Apply single-phase fault at MUSTANG 3 (527146) 115 kV Bus b. 1. Run for 5 cycles, Disconnect Bus MUSTANG_2 1 (527162) 13.2 kV b. 2. Clear fault and run for 11 cycles, Trip branch from SEAGRAVES 3 (527202) 115 kV Bus TO MUSTANG 3 (527146) 115 kV Bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_1165_P4 | a. Apply SLG fault at NICHOLS 6 (524044) 230 kV Bus b. Clear Fault after 21 cycles: b. 1. Trip branch from NICHOLS (523978) 230 kV Bus TO NICHOLS 6 (524044) 230 kV Bus CKT 2 b. 2. Trip branch from HUTCHISON 6 (523551) 230 kV Bus TO NICHOLS 6 (524044) 230 kV Bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_1167_P4 | a. Apply single-phase fault at POTTER_CO 6 (523959) 230 kV Bus b. Clear Fault after 21 cycles: b. 1. Trip branch from POTTER_CO 6 (523959) 230 kV Bus TO BUSHLAND 6 (524267) 230 kV Bus CKT 1 b. 2. Trip branch from POTTER_CO 6 (523959) 230 kV Bus TO ROLLHILLS 6 (524010) 230 kV Bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_1168_P4 | a. Apply single-phase fault at YOAKUM 6 (526935) 230 kV Bus b. 1. Run for 5 cycles, Disconnect Bus YOAKUM_TR1 1 (526931) 13.2 kV b. 2. Clear fault and run for 11 cycles, Trip branch from YOAKUM 6 (526935) 230 kV Bus TO NEEDMORE 6 (525586) 230 kV Bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_1169_P4 | a. Apply single-phase fault at TUCO_INT 7 (525832) 345 kV Bus b. Clear Fault after 21 cycles: b. 1. Trip branch from TUCO_INT 7 (525832) 345 kV Bus TO CRAWFISH_DR (560022) 345 kV Bus CKT 1 b. 2. Disconnect Bus TUCO_TR1 1 (525824) 13.2 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 763084 [G18-073-GEN20.6600]
04 - Southeast | 25W | Transfer | Group4_Fault_1170_P4 | a. Apply single-phase fault at TUCO_INT 7 (525832) 345 kV Bus b. Clear Fault after 21 cycles: b. 1. Trip branch from TUCO_INT 7 (525832) 345 kV Bus TO CRAWFISH_DR (560022) 345 kV Bus CKT 1 b. 2. Disconnect Bus TUCO_TR2 1 (525825) 13.2 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 763084 [G18-073-GEN20.6600]
04 - Southeast | 25W | Transfer | Group4_Fault_1171_P4 | a. Apply single-phase fault at WHEELER 6 (523777) 230 kV Bus b. 1. Run for 21.0 Cycles: b. 2. WHEELER 6 (523777) 230 kV Bus TO STLN-DEMARC6 (523779) 230 kV Bus CKT 1 b. 3. Disconnect Bus 523777 b. 4. Disconnect Bus 523774 b. 5. Clear Fault Bus 523777 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_1172_P4 | a. Apply single-phase fault at TUCO_INT 7 (525832) 345 kV Bus b. 1. Run for 5 cycles, Disconnect Bus TUCO_TR2 1 (525825) 13.2 kV b. 2. Clear fault and run for 11 cycles, Trip branch from TUCO_INT 7 (525832) 345 kV Bus TO CRAWFISH_DR (560022) 345 kV Bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 763084 [G18-073-GEN20.6600]
04 - Southeast | 25W | Transfer | Group4_Fault_1173_P4 | a. Apply fault at bus HITCHLAND 7 (523097) 345 kV b. 1. Run for 5.0 cycles, Disconnect bus 523091 b. 2. Run for 11.0 cycles, Disconnect bus 523091 b. 3. Clear fault bus 523097 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_1174_P4 | a. Apply Fault at Bus WHEELER 6 (523777) 230 kV b. 1. Run for 5 cycles, Disconnect Bus 523774 b. 2. Run for 11 cycles: b. 3. Disconnect Bus 523777 b. 4. Disconnect Bus 523774 b. 5. Clear Fault Bus 523777 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_1175_P4 | a. Apply single-phase fault at POTTER_CO 7 (523961) 345 kV Bus b. 1. Run for 5 cycles, Disconnect Bus POTTER_TR 1 (523957) 13.2 kV b. 2. Clear fault and run for 11 cycles, Disconnect Bus POTTER_TR 1 (523957) 13.2 kV b. 3. Run for 5 cycles: b. 4. Trip branch from HITCHLAND 7 (523097) 345 kV Bus TO POTTER_CO 7 (523961) 345 kV Bus CKT 1 b. 5. Disconnect bus 523957 b. 6. Disconnect bus 523961 b. 7. Disconnect bus 524296 b. 8. Disconnect bus 524299 b. 9. Disconnect bus 524298 b. 10. Disconnect bus 524294 b. 11. Disconnect bus 524295 b. 12. Disconnect bus 524297 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_1176_P4 | a. Apply single-phase fault at BUSHLAND 6 (524267) 230 kV b. 1. Run for 5 cycles, Drop Shunt 1 BUSHLAND 6 (524267) 230 kV b. 2. Run for 11 cycles: b. 3. Disconnect bus 524267 b. 4. Disconnect bus 524285 b. 5. Disconnect bus 524287 b. 6. Clear fault at bus 524267 b. 7. Disconnect Bus 524263 b. 8. Disconnect Bus 524275 b. 9. Disconnect Bus 524276 b. 10. Disconnect Bus 524289 b. 11. Disconnect Bus 524290 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_1177_P4 | a. Apply single-phase fault at SWISHER 6 (525213) 230 kV b. 1. Run for 5 cycles, Drop Shunt 1 SWISHER 6 (525213) 230 kV b. 2. Clear fault and run for 11 cycles, Trip branch from SWISHER 6 (525213) 230 kV Bus TO TUCO_INT 6 (525830) 230 kV Bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_1178_P4 | a. Apply single-phase fault at TUCO_INT 6 (525830) 230 kV b. 1. Run for 5 cycles, Drop Shunt 1 TUCO_INT 6 (525830) 230 kV b. 2. Run for 11 cycles: b. 3. Disconnect bus TUCO_TR3 1 (525819) 13.2 kV b. 4. Clear fault at bus TUCO_INT 6 (525830) 230 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 763084 [G18-073-GEN20.6600]
04 - Southeast | 25W | Transfer | Group4_Fault_1179_P4 | a. Apply single-phase fault at BUSHLAND 6 (524267) 230 kV Bus b. Clear Fault after 5 cycles: b. 1. Trip branch from BUSHLAND 6 (524267) 230 kV Bus TO WILDOR2_JUS6 (524290) 230 kV Bus CKT 1 b. 2. Drop Shunt 1 BUSHLAND 6 (524267) 230 kV Bus b. 3. Disconnect Bus BSHLND_TR1 1 (524263) 13.2 kV b. 4. Disconnect Bus WILDORA_GEN1 (524285) 0.69 kV b. 5. Disconnect Bus GS-PHWD_GEN1 (524287) 0.69 kV b. 6. Trip branch from BUSHLAND 6 (524267) 230 kV Bus TO POTTER_CO 6 (523959) 230 kV Bus CKT 1 b. 7. Clear Fault after 16 cycles: b. 8. Trip branch from BUSHLAND 6 (524267) 230 kV Bus TO DEAFSMITH 6 (524623) 230 kV Bus CKT 1 b. 9. Disconnect Bus WILDOR_WND 1 (524275) 34.5 kV b. 10. Disconnect Bus WILDOR_WND 6 (524276) 230 kV b. 11. Disconnect Bus GS-PHWDRNCH1 (524289) 34.5 kV b. 12. Disconnect Bus WILDOR2_JUS6 (524290) 230 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_1182_P4 | a. Apply single-phase fault at HARRNG_EST 6 (523979) 230 kV Bus b. Clear Fault after 16 cycles: b. 1. Trip branch from HARRNG_EST 6 (523979) 230 kV Bus TO PRINGLE 6 (523267) 230 kV Bus CKT 1 b. 2. Trip branch from HARRNG_EST 6 (523979) 230 kV Bus TO POTTER_CO 6 (523959) 230 kV Bus CKT 1 b. 3. Disconnect Bus HARRNG_EST 6 (523979) 230 kV b. 4. Disconnect Bus HARRNGTON3 1 (523973) 24 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_1184_P4 | a. Apply single-phase fault at 531449 b. 1. Run For 12.0 Cycles, Open Line From Bus 531449 To Bus 531465 CKT 1 b. 2. Clear Fault Bus 531449 b. 3. Open Line From Bus 523853 To Bus 531449 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_1185_P4 | a. Apply single-phase fault at 520814 b. 1. Run For 6.0 Cycles b. 2. Open Line From Bus 520864 To Bus 520900 CKT 1 b. 3. Open Line From Bus 520912 To Bus 520900 CKT 1 b. 4. Open Line From Bus 520923 To Bus 520912 CKT 1 b. 5. Run For 9.0 Cycles b. 6. Open Line From Bus 520814 To Bus 520422 CKT 1 b. 7. Open Line From Bus 520422 To Bus 520473 CKT 1 b. 8. Open Line From Bus 520473 To Bus 520867 CKT 1 b. 9. Open Line From Bus 520888 To Bus 520510 CKT 1 b. 10. Open Line From Bus 520867 To Bus 520510 CKT 1 b. 11. Clear Fault Bus 520814 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_1187_P4 | a. Apply single-phase fault at 520814 b. 1. Run For 6.0 Cycles, Open Line From Bus 520814 To Bus 521129 CKT 1 b. 1. Clear fault and run For 9.0 Cycles, Open Line From Bus 511477 To Bus 520814 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Low voltage ride through fails due to the tripping of G18-115-GEN10 and G18-115-GEN20 units. No cascading was observed and the issue was localised. Model tuning is recommended.
04 - Southeast | 25W | Transfer | Group4_Fault_1188_P4 | a. Apply single-phase fault at 520917 b. 1. Run For 6.0 Cycles b. 2. Open Line From Bus 520400 To Bus 520842 CKT 1 b. 3. Run For 9.0 Cycles b. 4. Disconnect Bus 514946 b. 5. Open Line From Bus 520917 To Bus 520975 CKT 1 b. 6. Clear Fault Bus 520917 b. 7. Drop Load 1 Bus 520400 b. 8. Drop Load 1 Bus 520975 b. 9. Disconnect Bus 520400 b. 10. Disconnect Bus 520975 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_1189_P4 | a. Apply single-phase fault at 520920 b. 1. Run For 6.0 Cycles b. 2. Open Line From Bus 520920 To Bus 520922 CKT 1 b. 3. Drop Generator 1 Bus 521145 b. 4. Disconnect Bus 520922 b. 5. Disconnect Bus 521141 b. 6. Disconnect Bus 521144 b. 7. Disconnect Bus 521145 b. 8. Disconnect Bus 521151 b. 9. Run For 9.0 Cycles Print 0 Plot 3 Crtplt 0 b. 10. Open Line From Bus 520957 To Bus 520999 CKT 1 b. 11. Clear Fault Bus 520920 b. 12. Open Line From Bus 520920 To Bus 520957 CKT 1 b. 13. Drop Load 1 Bus 520957 b. 14. Disconnect Bus 520957 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_1190_P4 | a. Apply single-phase fault at 520948 b. 1. Run For 6.0 Cycles, Open Line From Bus 510887 To Bus 520968 CKT 1 b. 2. Run For 9.0 Cycles b. 3. Open Line From Bus 520948 To Bus 520918 CKT 1 b. 4. Open Line From Bus 505602 To Bus 521049 CKT 1 b. 5. Clear Fault Bus 520948 b. 6. Drop Load 1 Bus 515370 b. 7. Drop Load 1 Bus 515568 b. 8. Drop Load 1 Bus 520463 b. 9. Drop Load 1 Bus 520483 b. 10. Drop Load 1 Bus 520497 b. 11. Drop Load 1 Bus 520918 b. 12. Drop Load 1 Bus 521077 b. 13. Drop Load 1 Bus 521115 b. 14. Disconnect Bus 515370 b. 15. Disconnect Bus 515568 b. 16. Disconnect Bus 520463 b. 17. Disconnect Bus 520483 b. 18. Disconnect Bus 520497 b. 19. Disconnect Bus 520826 b. 20. Disconnect Bus 520884 b. 21. Disconnect Bus 520918 b. 22. Disconnect Bus 521049 b. 23. Disconnect Bus 521077 b. 24. Disconnect Bus 521098 b. 25. Disconnect Bus 521115 b. 26. Drop Load 1 Bus 520411 b. 27. Drop Load 1 Bus 520874 b. 28. Drop Load 1 Bus 520968 b. 29. Drop Load 1 Bus 521036 b. 30. Disconnect Bus 520411 b. 31. Disconnect Bus 520874 b. 32. Disconnect Bus 520968 b. 33. Disconnect Bus 521036 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_1192_P4 | a. Apply single-phase fault at MARIETA4 (520988) 138 kV CB 472 Stuck b. 1. Run for 6 cycles, Trip branch from CANEYCK4 (515150) 138 kV To Bus 521067 CKT 1 b. 2 Run For 9 cycles: b. 3. Trip branch from 5MARIETA4 (520988) 138 kV To Bus TEXOMAJ4 (521061)138 kV CKT 1 b. 4. Trip branch from 520981 To Bus 520939 CKT 1 b. 5. Clear Fault Bus 520988 b. 6. Drop Load 1 Bus 520455 b. 7. Drop Load 1 Bus 520487 b. 8. Drop Load 1 Bus 520488 b. 9. Drop Load 1 Bus 520511 b. 10. Drop Load 1 Bus 520901 b. 11. Drop Load 1 Bus 521038 b. 12. Drop Load 1 Bus 521061 b. 13. Drop Load 1 Bus 521066 b. 14. Disconnect Bus 520455 b. 15. Disconnect Bus 520467 b. 16. Disconnect Bus 520487 b. 17. Disconnect Bus 520488 b. 18. Disconnect Bus 520511 b. 19. Disconnect Bus 520901 b. 20. Disconnect Bus 520939 b. 21. Disconnect Bus 520972 b. 22. Disconnect Bus 521038 b. 23. Disconnect Bus 521061 b. 24. Disconnect Bus 521066 b. 25. Disconnect Bus 521067 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_1193_P4 | a. Apply single-phase fault at NOELSW 4 (520430) 138 kV Bus b. 1. Run for 6 cycles, Trip branch from DRIFTWD4 (521200) 138 kV Bus TO CHRKCTY4 (520431) 138 kV Bus CKT 1 b. 2. Run for 9 cycles: b. 3. Trip branch from ROSEVLY4 (520436) 138 kV Bus TO NOELSW 4 (520430) 138 kV Bus CKT 1 b. 4. Trip branch from NOELSW 4 (520430) 138 kV Bus TO SALTPLN4 (520437) 138 kV Bus CKT 1 b. 5. Clear fault at NOELSW 4 (520430) 138 kV Bus b. 6. Drop Load 1 Bus 520431 b. 7. Drop Load 1 Bus 520437 b. 8. Drop Load 2 Bus 520437 b. 9. Disconnect Bus 520431 b. 10. Disconnect Bus 520437 b. 11. Drop Load 1 Bus 520436 b. 12. Drop Load 1 Bus 520601 b. 13. Disconnect Bus 520436 b. 14. Disconnect Bus 520601 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_1194_P4 | a. Apply single-phase fault at PAYNESW4 (520888) 138 kV Bus b. 1. Run for 6 cycles, Trip branch from DOVERSW4 (520882) 138 kV Bus TO OKEENE 4 (521016) 138 kV Bus CKT 1 b. 2. Clear fault and run for 9 cycles, Trip branch MOORLND4 (520999) 138 kV Bus TO PIC4 (520425) 138 kV Bus CKT 1 Bus CKT 1 b. 3. Drop Load 1 Bus 520425 b. 4. Drop Load 1 Bus 520507 b. 5. Disconnect Bus 520425 b. 6. Disconnect Bus 520848 b. 7. Disconnect Bus 520507 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_1195_P4 | a. Apply single-phase fault at PAYNESW4 (520888) 138 kV Bus b. 1. Run for 6 cycles, Trip branch from OU SW 4 (521104) 138 kV Bus TO COLE 4 (520861) 138 kV Bus CKT 1 b. 2. Run for 9 cycles: b. 3. Trip PAYNESW4 (520888) 138 kV Bus TO NAPLSTP4 (520510) 138 kV Bus CKT 1 b. 4. Trip PAYNESW4 (520888) 138 kV Bus TO CRINER 4 (520868) 138 kV Bus CKT 1 b. 5. Trip CORNVIL4 (511449) 138 kV Bus TO CORN TP4 (520867) 138 kV Bus CKT 1 b. 6. Trip ANADARK4 (520814) 138 kV Bus TO CLVLDSW4 (520508) 138 kV Bus CKT 1 b. 7. Clear fault at PAYNESW4 (520888) 138 kV Bus Drop Load 1 at 520547 Drop Load 2 at 520547 Drop Load 1A at 520604 Disconnect Bus 520422 Disconnect Bus 520510 Disconnect Bus 520867 Disconnect Bus 520547 Drop Load 1 Bus 520861 Drop Load 1 Bus 520868 Disconnect Bus 520861 Disconnect Bus 520868 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_1196_P4 | a. Apply single-phase fault at WASHITA4 (521089) 138 kV Bus b. 1. Run for 6 cycles, Trip branch CLINTJC4 (511485) 138 kV Bus TO CLINTON4 (520856) 138 kV Bus CKT 1 b. 2. Run for 9 cycles: b. 3. Trip branch GRACMNT4 (515802) 138 kV Bus TO WASHITA4 (521089) 138 kV Bus CKT 1 b. 3. Trip branch ONEY 4 (521017) 138 kV Bus TO WASHITA4 (521089) 138 kV Bus CKT 1 b. 4. Clear fault at WASHITA4 (521089) 138 kV Bus b. 5. Drop Load 1 Bus 520468 b. 6. Drop Load 1 Bus 520503 b. 7. Drop Load 1 Bus 520856 b. 8. Drop Load 1 Bus 520950 b. 9. Drop Load 1 Bus 521010 b. 10. Drop Load 2 Bus 521010 b. 11. Drop Load 1 Bus 521017 b. 12. Drop Load 1 Bus 521050 b. 13. Drop Load 1 Bus 521092 b. 14. Disconnect Bus 520468 b. 15. Disconnect Bus 520503 b. 16. Disconnect Bus 520827 b. 17. Disconnect Bus 520856 b. 18. Disconnect Bus 520950 b. 19. Disconnect Bus 521010 b. 20. Disconnect Bus 521017 b. 21. Disconnect Bus 521050 b. 22. Disconnect Bus 521092 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_1197_P4 | a. Apply single-phase fault at WASHITA4 (521089) 138 kV Bus b. 1. Run for 6 cycles, Trip branch GRACMNT4 (515802) 138 kV Bus TO WASHITA4 (521089) 138 kV Bus CKT 1 b. 2. Clear fault and run for 9 cycles, Trip branch GRACMNT4 (515802) 138 kV Bus TO WASHITA4 (521089) 138 kV Bus CKT 2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_1198_P4 | a. Apply single-phase fault at ANADARK4 (520814) 138 kV Bus b. 1. Run for 6 cycles: b. 2. Trip branch from COMANCH4 (520864) 138 kV Bus TO EMPIRE 4 (520900) kV 138 kV Bus CKT 1 b. 3. Trip Three winding transformer from FLETCH-4 (520912) 138 kV TO FLETCHR2 (520911) 69 kV TO FLCHTERT (521168) 13.8 kV CKT 1 b. 4. Run for 9 cycles: b. 5. Trip branch from SEQUOYAHJ4 (520422) 138 kV Bus TO ANADARK4 (520814) kV 138 kV Bus CKT 1 b. 6. Trip branch from PAYNESW4 (520888) 138 kV Bus TO NAPLSTP4 (520510) kV 138 kV Bus CKT 1 b. 7. Trip branch from CORNVIL4 (511449) 138 kV Bus TO CORN TP4 (520867) 138 kV Bus CKT 1 b. 8. Clear fault at ANADARK4 (520814) 138 kV Bus b. 9. Drop Load 1 Bus 520547 b. 10. Drop Load 2 Bus 520547 b. 11. Drop Load 1a Bus 520604 b. 12. Disconnect Bus 520422 b. 13. Disconnect Bus 520510 b. 14. Disconnect Bus 520604 b. 15. Disconnect Bus 520867 b. 16. Disconnect Bus 520547 b. 17. Drop Load 1 Bus 520900 b. 18. Drop Load 1 Bus 520923 b. 19. Disconnect Bus 520900 b. 20. Disconnect Bus 520923 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_1199_P4 | a. Apply single-phase fault at PAYNESW4 (520888) 138 kV Bus b. 1. Run for 6 cycles, Trip branch from OU SW 4 (521104) 138 kV Bus TO COLE 4 (520861) 138 kV Bus CKT 1 b. 2. Run for 9 cycles: b. 3. Trip PAYNESW4 (520888) 138 kV Bus TO NAPLSTP4 (520510) 138 kV Bus CKT 1 b. 4. Trip PAYNESW4 (520888) 138 kV Bus TO CRINER 4 (520868) 138 kV Bus CKT 1 b. 5. Trip CORNVIL4 (511449) 138 kV Bus TO CORN TP4 (520867) 138 kV Bus CKT 1 b. 6. Trip ANADARK4 (520814) 138 kV Bus TO CLVLDSW4 (520508) 138 kV Bus CKT 1 b. 7. Clear fault at PAYNESW4 (520888) 138 kV Bus Drop Load 1 at 520547 Drop Load 2 at 520547 Drop Load 1A at 520604 Disconnect Bus 520422 Disconnect Bus 520510 Disconnect Bus 520604 Disconnect Bus 520867 Disconnect Bus 520547 Drop Load 1 Bus 520861 Drop Load 1 Bus 520868 Disconnect Bus 520861 Disconnect Bus 520868 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | Group5_Fault_0001_P1 | 3 phase fault on NEWHART 6 (525461) 230 kV Bus a. Apply Fault at the NEWHART 6 (525461) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from NEWHART 6 (525461) 230 kV Bus to PLANT_X 6 (525481) 230 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | No | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points) |  | Generator relays were disabled for the following generators: 763189 [G18-089-GEN10.6900]
05 - Southwest | 25S | Transfer | Group5_Fault_0002_P1 | 3 phase fault on PLANT_X 6 (525481) 230 kV Bus a. Apply Fault at the PLANT_X 6 (525481) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from PLANT_X 6 (525481) 230 kV Bus to TOLK 6 (525531) 230 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0003_P1 | 3 phase fault on PLANT_X 6 (525481) 230 kV Bus a. Apply Fault at the PLANT_X 6 (525481) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from PLANT_X 6 (525481) 230 kV Bus to TOLK 6 (525531) 230 kV Bus CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0004_P1 | 3 phase fault on PLANT_X 6 (525481) 230 kV Bus a. Apply Fault at the PLANT_X 6 (525481) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from PLANT_X 6 (525481) 230 kV Bus to SUNDOWN 6 (526435) 230 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0005_P1 | 3 phase fault on PLANT_X 6 (525481) 230 kV Bus a. Apply Fault at the PLANT_X 6 (525481) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from PLANT_X 6 (525481) 230 kV Bus to G17-146-TAP (760498) 230 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | No | Yes | Damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer
05 - Southwest | 25S | Transfer | Group5_Fault_0006_P1 | 3 phase fault on PLANT_X 6 (525481) 230 kV Bus a. Apply Fault at the PLANT_X 6 (525481) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from PLANT_X 6 (525481) 230 kV Bus to PLANT_X 3 (525480) 115 kV Bus to PLANTX_TR1 1 (525479) 13.2 kV Bus CKT 1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0007_P1 | 3 phase fault on PLANT_X 6 (525481) 230 kV Bus a. Apply Fault at the PLANT_X 6 (525481) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from PLANT_X 6 (525481) 230 kV Bus to PLANT_X 3 (525480) 115 kV Bus to PLANTX_TR2 (525478) 13.2 kV Bus CKT 2 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0008_P1 | 3 phase fault on NEWHART 6 (525461) 230 kV Bus a. Apply Fault at the NEWHART 6 (525461) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from NEWHART 6 (525461) 230 kV Bus to POTTER_CO 6 (523959) 230 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | No | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points) |  | Generator relays were disabled for the following generators: 763189 [G18-089-GEN10.6900]
05 - Southwest | 25S | Transfer | Group5_Fault_0009_P1 | 3 phase fault on NEWHART 6 (525461) 230 kV Bus a. Apply Fault at the NEWHART 6 (525461) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from NEWHART 6 (525461) 230 kV Bus to SWISHER 6 (525213) 230 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | No | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points) |  | Generator relays were disabled for the following generators: 763189 [G18-089-GEN10.6900]
05 - Southwest | 25S | Transfer | Group5_Fault_0010_P1 | 3 phase fault on NEWHART 6 (525461) 230 kV Bus a. Apply Fault at the NEWHART 6 (525461) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from NEWHART 6 (525461) 230 kV Bus to NEWHART 3 (525460) 115 kV Bus to NEWHART_TR11 (525459) 13.2 kV Bus CKT 1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0011_P1 | 3 phase fault on NEWHART 6 (525461) 230 kV Bus a. Apply Fault at the NEWHART 6 (525461) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from NEWHART 6 (525461) 230 kV Bus to NEWHART 3 (525460) 115 kV Bus to NEWHART_TR21 (525458) 13.2 kV Bus CKT 2 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0012_P1 | 3 phase fault on TOLK 6 (525531) 230 kV Bus a. Apply Fault at the TOLK 6 (525531) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from TOLK 6 (525531) 230 kV Bus to ROOSEVELT 6 (524909) 230 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | No | No | Damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 763254 [G18-099-GEN10.6900], 763257 [G18-099-GEN20.6900]
05 - Southwest | 25S | Transfer | Group5_Fault_0013_P1 | 3 phase fault on TOLK 6 (525531) 230 kV Bus a. Apply Fault at the TOLK 6 (525531) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from TOLK 6 (525531) 230 kV Bus to NEEDMORE 6 (525586) 230 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | No | No | Damping issues observed | Potter to Tolk 345 kV Double Circuit Line Build Potter to Chisholm 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer Potter to Tolk 345 kV | Generator relays were disabled for the following generators: 763254 [G18-099-GEN10.6900], 763257 [G18-099-GEN20.6900], 763397 [G18-124-GEN1], 763309 [G18-112-GEN1]
05 - Southwest | 25S | Transfer | Group5_Fault_0014_P1 | 3 phase fault on TOLK 6 (525531) 230 kV Bus a. Apply Fault at the TOLK 6 (525531) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from TOLK 6 (525531) 230 kV Bus to TUCO_INT 6 (525830) 230 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | No | No | Damping issues observed | Potter to Tolk 345 kV Double Circuit Line Build Potter to Chisholm 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer Potter to Tolk 345 kV | Generator relays were disabled for the following generators: 763254 [G18-099-GEN10.6900], 763257 [G18-099-GEN20.6900], 763397 [G18-124-GEN1], 763309 [G18-112-GEN1]
05 - Southwest | 25S | Transfer | Group5_Fault_0015_P1 | 3 phase fault on TOLK 6 (525531) 230 kV Bus a. Apply Fault at the TOLK 6 (525531) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from TOLK 6 (525531) 230 kV Bus to ROOSEVELT 6 (524909) 230 kV Bus CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | No | No | Damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 763254 [G18-099-GEN10.6900], 763257 [G18-099-GEN20.6900]
05 - Southwest | 25S | Transfer | Group5_Fault_0016_P1 | 3 phase fault on SUNDOWN 6 (526435) 230 kV Bus a. Apply Fault at the SUNDOWN 6 (526435) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from SUNDOWN 6 (526435) 230 kV Bus to AMOCO_SS 6 (526460) 230 kV Bus CKT 1 b. 2. Trip branch from AMOCO_SS 6 (526460) 230 kV Bus to YOAKUM 6 (526935) 230 kV Bus CKT 1 b. 3. Drop Load 1 at AMOCO_SS 6 (526460) 230 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0017_P1 | 3 phase fault on SUNDOWN 6 (526435) 230 kV Bus a. Apply Fault at the SUNDOWN 6 (526435) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from SUNDOWN 6 (526435) 230 kV Bus to WOLFFORTH 6 (526525) 230 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0018_P1 | 3 phase fault on SUNDOWN 6 (526435) 230 kV Bus a. Apply Fault at the SUNDOWN 6 (526435) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from SUNDOWN 6 (526435) 230 kV Bus to SUNDOWN 3 (526434) 115 kV Bus to SUNDOWN_TR11 (526432) 13.8 kV Bus CKT 1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0019_P1 | 3 phase fault on G17-146-TAP (760498) 230 kV Bus a. Apply Fault at the G17-146-TAP (760498) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from G17-146-TAP (760498) 230 kV Bus to DEAFSMITH 6 (524623) 230 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | Group5_Fault_0020_P1 | 3 phase fault on PLANT_X 3 (525480) 115 kV Bus a. Apply Fault at the PLANT_X 3 (525480) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from PLANT_X 3 (525480) 115 kV Bus to MULSHVLY_TP3 (525019) 115 kV Bus CKT 1 b. 2. Trip branch from MULSHVLY_TP3 (525019) 115 kV Bus to MULESHVALLY3 (525018) 115 kV Bus CKT 1 b. 3. Trip branch from MULSHVLY_TP3 (525019) 115 kV Bus to BAILEYCO 3 (525028) 115 kV Bus CKT 1 b. 4. Drop Load 1 at MULESHVALLY3 (525018) 115 kV Bus b. 5. Drop Load 2 at MULESHVALLY3 (525018) 115 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0021_P1 | 3 phase fault on PLANT_X 3 (525480) 115 kV Bus a. Apply Fault at the PLANT_X 3 (525480) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from PLANT_X 3 (525480) 115 kV Bus to RKYFORD_TP 3 (525446) 115 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0022_P1 | 3 phase fault on PLANT_X 3 (525480) 115 kV Bus a. Apply Fault at the PLANT_X 3 (525480) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from PLANT_X 3 (525480) 115 kV Bus to LAMB_CNTY 3 (525636) 115 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0023_P1 | 3 phase fault on PLANT_X 3 (525480) 115 kV Bus a. Apply Fault at the PLANT_X 3 (525480) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from PLANT_X 3 (525480) 115 kV Bus to HALE_CNTY 3 (525454) 115 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0024_P1 | 3 phase fault on PLANT_X 3 (525480) 115 kV Bus a. Apply Fault at the PLANT_X 3 (525480) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from PLANT_X 3 (525480) 115 kV Bus to BC-EARTH 3 (525056) 115 kV Bus CKT 1 b. 2. Trip branch from BC-EARTH 3 (525056) 115 kV Bus to BC-KELLEY +3 (525050) 115 kV Bus CKT 1 b. 3. Trip branch from BC-KELLEY +3 (525050) 115 kV Bus to CASTRO_CNTY3 (524746) 115 kV Bus CKT 1 b. 4. Drop Load 1 at BC-EARTH 3 (525056) 115 kV Bus b. 5. Drop Load 1 at BC-KELLEY +3 (525050) 115 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0025_P1 | 3 phase fault on SWISHER 6 (525213) 230 kV Bus a. Apply Fault at the SWISHER 6 (525213) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from SWISHER 6 (525213) 230 kV Bus to AMA_SOUTH 6 (524415) 230 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | No | Yes | Damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer
05 - Southwest | 25S | Transfer | Group5_Fault_0026_P1 | 3 phase fault on SWISHER 6 (525213) 230 kV Bus a. Apply Fault at the SWISHER 6 (525213) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from SWISHER 6 (525213) 230 kV Bus to TUCO_INT 6 (525830) 230 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | No | Yes | Damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer
05 - Southwest | 25S | Transfer | Group5_Fault_0027_P1 | 3 phase fault on SWISHER 6 (525213) 230 kV Bus a. Apply Fault at the SWISHER 6 (525213) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from SWISHER 6 (525213) 230 kV Bus to SWISHER 3 (525212) 115 kV Bus to SWISHER_TR11 (525211) 13.2 kV Bus CKT 1 b. 2. Trip branch from SWISHER 3 (525212) 115 kV Bus to KRESS_INT 3 (525192) 115 kV Bus CKT 1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0028_P1 | 3 phase fault on NEWHART 3 (525460) 115 kV Bus a. Apply Fault at the NEWHART 3 (525460) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from NEWHART 3 (525460) 115 kV Bus to CASTRO_CNTY3 (524746) 115 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0029_P1 | 3 phase fault on NEWHART 3 (525460) 115 kV Bus a. Apply Fault at the NEWHART 3 (525460) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from NEWHART 3 (525460) 115 kV Bus to KRESS_INT 3 (525192) 115 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0030_P1 | 3 phase fault on NEWHART 3 (525460) 115 kV Bus a. Apply Fault at the NEWHART 3 (525460) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from NEWHART 3 (525460) 115 kV Bus to HART_INDUST3 (525124) 115 kV Bus CKT 1 b. 2. Trip branch from HART_INDUST3 (525124) 115 kV Bus to LAMTON 3 (525414) 115 kV Bus CKT 1 b. 3. Drop Load 1 at HART_INDUST3 (525124) 115 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0031_P1 | 3 phase fault on ROOSEVELT 6 (524909) 230 kV Bus a. Apply Fault at the ROOSEVELT 6 (524909) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from ROOSEVELT 6 (524909) 230 kV Bus to OASIS 6 (524875) 230 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0032_P1 | 3 phase fault on ROOSEVELT 6 (524909) 230 kV Bus a. Apply Fault at the ROOSEVELT 6 (524909) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from ROOSEVELT 6 (524909) 230 kV Bus to PNM-DC6 (599955) 230 kV Bus CKT @1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0033_P1 | 3 phase fault on ROOSEVELT 6 (524909) 230 kV Bus a. Apply Fault at the ROOSEVELT 6 (524909) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from ROOSEVELT 6 (524909) 230 kV Bus to ROOSEVELT 3 (524908) 115 kV Bus to ROSEVLT_TR11 (524907) 13.2 kV Bus CKT 1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0034_P1 | 3 phase fault on ROOSEVELT 6 (524909) 230 kV Bus a. Apply Fault at the ROOSEVELT 6 (524909) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from ROOSEVELT 6 (524909) 230 kV Bus to PLSNT_HILL 6 (524770) 230 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0035_P1 | 3 phase fault on NEEDMORE 6 (525586) 230 kV Bus a. Apply Fault at the NEEDMORE 6 (525586) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from NEEDMORE 6 (525586) 230 kV Bus to YOAKUM 6 (526935) 230 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0036_P1 | 3 phase fault on TUCO_INT 6 (525830) 230 kV Bus a. Apply Fault at the TUCO_INT 6 (525830) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from TUCO_INT 6 (525830) 230 kV Bus to CARLISLE 6 (526161) 230 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0037_P1 | 3 phase fault on TUCO_INT 6 (525830) 230 kV Bus a. Apply Fault at the TUCO_INT 6 (525830) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from TUCO_INT 6 (525830) 230 kV Bus to JONES 6 (526337) 230 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0038_P1 | 3 phase fault on TUCO_INT 6 (525830) 230 kV Bus a. Apply Fault at the TUCO_INT 6 (525830) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from TUCO_INT 6 (525830) 230 kV Bus to TUCO_INT 3 (525828) 115 kV Bus to TUCO_TR4 1 (525821) 13.2 kV Bus CKT 1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0039_P1 | 3 phase fault on TUCO_INT 6 (525830) 230 kV Bus a. Apply Fault at the TUCO_INT 6 (525830) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from TUCO_INT 6 (525830) 230 kV Bus to TUCO_INT 3 (525828) 115 kV Bus to TUCO_TR3 1 (525819) 13.2 kV Bus CKT 2 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0040_P1 | 3 phase fault on WOLFFORTH 6 (526525) 230 kV Bus a. Apply Fault at the WOLFFORTH 6 (526525) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from WOLFFORTH 6 (526525) 230 kV Bus to CARLISLE 6 (526161) 230 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | No | Yes | Damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer
05 - Southwest | 25S | Transfer | Group5_Fault_0041_P1 | 3 phase fault on WOLFFORTH 6 (526525) 230 kV Bus a. Apply Fault at the WOLFFORTH 6 (526525) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from WOLFFORTH 6 (526525) 230 kV Bus to WOLFFORTH 3 (526524) 115 kV Bus to WOLFRTH_TR11 (526522) 13.2 kV Bus CKT 1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0042_P1 | 3 phase fault on WOLFFORTH 6 (526525) 230 kV Bus a. Apply Fault at the WOLFFORTH 6 (526525) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from WOLFFORTH 6 (526525) 230 kV Bus to LUBBCK_STH 6 (526269) 230 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | No | Yes | Damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer
05 - Southwest | 25S | Transfer | Group5_Fault_0043_P1 | 3 phase fault on SUNDOWN 3 (526434) 115 kV Bus a. Apply Fault at the SUNDOWN 3 (526434) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from SUNDOWN 3 (526434) 115 kV Bus to AMOCO_TP 3 (526445) 115 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0044_P1 | 3 phase fault on SUNDOWN 3 (526434) 115 kV Bus a. Apply Fault at the SUNDOWN 3 (526434) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from SUNDOWN 3 (526434) 115 kV Bus to LC-OPDYKE 3 (526036) 115 kV Bus CKT 1 b. 2. Trip branch from LC-OPDYKE 3 (526036) 115 kV Bus to HOCKLEY 3 (526020) 115 kV Bus CKT 1 b. 3. Drop Load 1 at LC-OPDYKE 3 (526036) 115 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0045_P1 | 3 phase fault on SUNDOWN 3 (526434) 115 kV Bus a. Apply Fault at the SUNDOWN 3 (526434) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from SUNDOWN 3 (526434) 115 kV Bus to PACIFIC 3 (526424) 115 kV Bus CKT 1 b. 2. Trip branch from PACIFIC 3 (526424) 115 kV Bus to COCHRAN 3 (526361) 115 kV Bus CKT 1 b. 3. Drop Load 1 at PACIFIC 3 (526424) 115 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0046_P1 | 3 phase fault on DEAFSMITH 6 (524623) 230 kV Bus a. Apply Fault at the DEAFSMITH 6 (524623) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from DEAFSMITH 6 (524623) 230 kV Bus to BUSHLAND 6 (524267) 230 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0047_P1 | 3 phase fault on DEAFSMITH 6 (524623) 230 kV Bus a. Apply Fault at the DEAFSMITH 6 (524623) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from DEAFSMITH 6 (524623) 230 kV Bus to DFSMTH_EST 3 (524619) 115 kV Bus to DEFSMTH_TR21 (524621) 13.8 kV Bus CKT 2 b. 2. Trip branch from DFSMTH_EST 3 (524619) 115 kV Bus to TIERABLANCA3 (524630) 115 kV Bus CKT 1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0048_P1 | 3 phase fault on LC-OPDYKE 3 (526036) 115 kV Bus a. Apply Fault at the LC-OPDYKE 3 (526036) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from LC-OPDYKE 3 (526036) 115 kV Bus to HOCKLEY 3 (526020) 115 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0049_P1 | 3 phase fault on AMOCO_TP 3 (526445) 115 kV Bus a. Apply Fault at the AMOCO_TP 3 (526445) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from AMOCO_TP 3 (526445) 115 kV Bus to AMOCO_CRYO 3 (526452) 115 kV Bus CKT 1 b. 2. Drop Load 1 at AMOCO_CRYO 3 (526452) 115 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0050_P1 | 3 phase fault on AMOCO_TP 3 (526445) 115 kV Bus a. Apply Fault at the AMOCO_TP 3 (526445) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from AMOCO_TP 3 (526445) 115 kV Bus to LG-LEVELAND3 (526484) 115 kV Bus CKT 1 b. 2. Trip branch from LG-LEVELAND3 (526484) 115 kV Bus to LG-CLAUENE 3 (526491) 115 kV Bus CKT 1 b. 3. Trip branch from LG-CLAUENE 3 (526491) 115 kV Bus to TERRY_CNTY 3 (526736) 115 kV Bus CKT 1 b. 4. Drop Load 1 at LG-LEVELAND3 (526484) 115 kV Bus b. 5. Drop Load 1 at LG-CLAUENE 3 (526491) 115 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0051_P1 | 3 phase fault on LAMB_CNTY 3 (525636) 115 kV Bus a. Apply Fault at the LAMB_CNTY 3 (525636) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from LAMB_CNTY 3 (525636) 115 kV Bus to HOCKLEY 3 (526020) 115 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0052_P1 | 3 phase fault on LAMB_CNTY 3 (525636) 115 kV Bus a. Apply Fault at the LAMB_CNTY 3 (525636) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from LAMB_CNTY 3 (525636) 115 kV Bus to LAMB_CNTY 2 (525635) 69 kV Bus to LAMB_TR1 1 (525631) 13.2 kV Bus CKT 1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0053_P1 | 3 phase fault on LAMB_CNTY 3 (525636) 115 kV Bus a. Apply Fault at the LAMB_CNTY 3 (525636) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from LAMB_CNTY 3 (525636) 115 kV Bus to LAMB_CNTY 2 (525635) 69 kV Bus to LAMB_TR2 1 (525632) 13.2 kV Bus CKT 2 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0054_P1 | 3 phase fault on CARLISLE 3 (526160) 115 kV Bus a. Apply Fault at the CARLISLE 3 (526160) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from CARLISLE 3 (526160) 115 kV Bus to MURPHY 3 (526192) 115 kV Bus CKT 1 b. 2. Trip branch from MURPHY 3 (526192) 115 kV Bus to QUINCY 3 (526195) 115 kV Bus CKT 1 b. 3. Trip branch from QUINCY 3 (526195) 115 kV Bus to SP-MILWAUKEE (526196) 115 kV Bus CKT 1 b. 4. Trip branch from SP-MILWAUKEE (526196) 115 kV Bus to SP-UPLAND (526198) 115 kV Bus CKT 1 b. 5. Drop Load 1 at MURPHY 3 (526192) 115 kV Bus b. 6. Drop Load D2 at MURPHY 3 (526192) 115 kV Bus b. 7. Drop Load 1 at SP-MILWAUKEE (526196) 115 kV Bus b. 8. Drop Load 1 at SP-UPLAND (526198) 115 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0055_P1 | 3 phase fault on POTTER_CO 6 (523959) 230 kV Bus a. Apply Fault at the POTTER_CO 6 (523959) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from POTTER_CO 6 (523959) 230 kV Bus to CHAN+TASCOS6 (523869) 230 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | No | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points) |  | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000], 523941 [MAJSTC-WTG110.6900], 523942 [MAJSTC-WTG210.6900], 523942 [MAJSTC-WTG210.6900], 761358 [G17-239-GEN10.6900], 761361 [G17-239-GEN20.6900], 761799 [G17-187GEN1 0.6900], 761802 [G17-187GEN2 0.6900], 523936 [PANTEX_WIND10.6900], 524287 [GS-PHWD_GEN10.6900]
05 - Southwest | 25S | Transfer | Group5_Fault_0056_P1 | 3 phase fault on POTTER_CO 6 (523959) 230 kV Bus a. Apply Fault at the POTTER_CO 6 (523959) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from POTTER_CO 6 (523959) 230 kV Bus to MCDWL_CREEK6 (523323) 230 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | No | No | No | No | Yes | No | No | Out Of Step Generators and damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000], 523941 [MAJSTC-WTG110.6900], 523942 [MAJSTC-WTG210.6900], 523942 [MAJSTC-WTG210.6900], 761358 [G17-239-GEN10.6900], 761361 [G17-239-GEN20.6900], 761799 [G17-187GEN1 0.6900], 761802 [G17-187GEN2 0.6900], 523936 [PANTEX_WIND10.6900], 524287 [GS-PHWD_GEN10.6900]
05 - Southwest | 25S | Transfer | Group5_Fault_0057_P1 | 3 phase fault on POTTER_CO 6 (523959) 230 kV Bus a. Apply Fault at the POTTER_CO 6 (523959) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from POTTER_CO 6 (523959) 230 kV Bus to ROLLHILLS 6 (524010) 230 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | No | No | Damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000], 523941 [MAJSTC-WTG110.6900], 523942 [MAJSTC-WTG210.6900], 523942 [MAJSTC-WTG210.6900], 761358 [G17-239-GEN10.6900], 761361 [G17-239-GEN20.6900], 761799 [G17-187GEN1 0.6900], 761802 [G17-187GEN2 0.6900], 523936 [PANTEX_WIND10.6900], 524287 [GS-PHWD_GEN10.6900]
05 - Southwest | 25S | Transfer | Group5_Fault_0058_P1 | 3 phase fault on POTTER_CO 6 (523959) 230 kV Bus a. Apply Fault at the POTTER_CO 6 (523959) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from POTTER_CO 6 (523959) 230 kV Bus to HARRNG_EST 6 (523979) 230 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | No | No | Damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000], 523941 [MAJSTC-WTG110.6900], 523942 [MAJSTC-WTG210.6900], 523942 [MAJSTC-WTG210.6900], 761358 [G17-239-GEN10.6900], 761361 [G17-239-GEN20.6900], 761799 [G17-187GEN1 0.6900], 761802 [G17-187GEN2 0.6900], 523936 [PANTEX_WIND10.6900], 524287 [GS-PHWD_GEN10.6900]
05 - Southwest | 25S | Transfer | Group5_Fault_0059_P1 | 3 phase fault on POTTER_CO 6 (523959) 230 kV Bus a. Apply Fault at the POTTER_CO 6 (523959) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from POTTER_CO 6 (523959) 230 kV Bus to BUSHLAND 6 (524267) 230 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | No | No | No | No | No | No | No | Out Of Step Generators and damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000], 523941 [MAJSTC-WTG110.6900], 523942 [MAJSTC-WTG210.6900], 523942 [MAJSTC-WTG210.6900], 761358 [G17-239-GEN10.6900], 761361 [G17-239-GEN20.6900], 761799 [G17-187GEN1 0.6900], 761802 [G17-187GEN2 0.6900], 523936 [PANTEX_WIND10.6900], 524287 [GS-PHWD_GEN10.6900]
05 - Southwest | 25S | Transfer | Group5_Fault_0060_P1 | 3 phase fault on MCDWL_CREEK6 (523323) 230 kV Bus a. Apply Fault at the MCDWL_CREEK6 (523323) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from MCDWL_CREEK6 (523323) 230 kV Bus to MOORE_CNTY 6 (523309) 230 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | No | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points) |  | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25S | Transfer | Group5_Fault_0061_P1 | 3 phase fault on MCDWL_CREEK6 (523323) 230 kV Bus a. Apply Fault at the MCDWL_CREEK6 (523323) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from MCDWL_CREEK6 (523323) 230 kV Bus to MCDWL_CREEK3 (523322) 115 kV Bus to MCDWL_CRKTR1 (523321) 13.2 kV Bus CKT 1 | P1 | Yes | Yes | Yes | No | Yes | Yes | No | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points) |  | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25S | Transfer | Group5_Fault_0062_P1 | 3 phase fault on HARRNG_EST 6 (523979) 230 kV Bus a. Apply Fault at the HARRNG_EST 6 (523979) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from HARRNG_EST 6 (523979) 230 kV Bus to HARRNG_MID 6 (523978) 230 kV Bus CKT @1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | No | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points) |  | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000], 523941 [MAJSTC-WTG110.6900], 523942 [MAJSTC-WTG210.6900], 523942 [MAJSTC-WTG210.6900], 761358 [G17-239-GEN10.6900], 761361 [G17-239-GEN20.6900], 761799 [G17-187GEN1 0.6900], 761802 [G17-187GEN2 0.6900], 763084 [G18-073-GEN20.6600], 763090 [G18-073-GEN10.6600], 523936 [PANTEX_WIND10.6900], 524287 [GS-PHWD_GEN10.6900]
05 - Southwest | 25S | Transfer | Group5_Fault_0063_P1 | 3 phase fault on HARRNG_EST 6 (523979) 230 kV Bus a. Apply Fault at the HARRNG_EST 6 (523979) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from HARRNG_EST 6 (523979) 230 kV Bus to PRINGLE 6 (523267) 230 kV Bus CKT 1 b. 2. Trip three winding transformer from PRINGLE 6 (523267) 230 kV Bus to PRINGLE 3 (523266) 115 kV Bus to PRINGLE_TR 1 (523265) 13.2 kV Bus CKT 1 | P1 | Yes | Yes | Yes | No | Yes | Yes | No | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points) |  | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000], 523941 [MAJSTC-WTG110.6900], 523942 [MAJSTC-WTG210.6900], 523942 [MAJSTC-WTG210.6900], 761358 [G17-239-GEN10.6900], 761361 [G17-239-GEN20.6900], 761799 [G17-187GEN1 0.6900], 761802 [G17-187GEN2 0.6900], 763084 [G18-073-GEN20.6600], 763090 [G18-073-GEN10.6600], 523936 [PANTEX_WIND10.6900], 524287 [GS-PHWD_GEN10.6900]
05 - Southwest | 25S | Transfer | Group5_Fault_0064_P1 | 3 phase fault on ROLLHILLS 6 (524010) 230 kV Bus a. Apply Fault at the ROLLHILLS 6 (524010) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from ROLLHILLS 6 (524010) 230 kV Bus to ROLLHILLS 3 (524007) 115 kV Bus to ROLHILLS_TR1 (524008) 13.2 kV Bus CKT 1 | P1 | Yes | Yes | Yes | No | Yes | Yes | No | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points) |  | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25S | Transfer | Group5_Fault_0065_P1 | 3 phase fault on BUSHLAND 6 (524267) 230 kV Bus a. Apply Fault at the BUSHLAND 6 (524267) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from BUSHLAND 6 (524267) 230 kV Bus to BUSHLAND 3 (524266) 115 kV Bus to BSHLND_TR1 1 (524263) 13.2 kV Bus CKT 1 b. 2. Trip branch from BUSHLAND 3 (524266) 115 kV Bus to OUTPOST 3 (524243) 115 kV Bus CKT 1 b. 3. Trip branch from OUTPOST 3 (524243) 115 kV Bus to ARNOT 3 (524560) 115 kV Bus CKT 1 b. 4. Trip branch from ARNOT 3 (524560) 115 kV Bus to HILLSIDE 3 (524300) 115 kV Bus CKT 1 b. 5. Trip branch from HILLSIDE 3 (524300) 115 kV Bus to COULTER 3 (524306) 115 kV Bus CKT 1 b. 6. Drop Load 1 at OUTPOST 3 (524243) 115 kV Bus b. 7. Drop Load 1 at ARNOT 3 (524560) 115 kV Bus b. 8. Drop Load 1 at HILLSIDE 3 (524300) 115 kV Bus | P1 | Yes | Yes | Yes | No | Yes | Yes | No | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points) |  | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25S | Transfer | Group5_Fault_0066_P1 | 3 phase fault on NICHOLS 6 (524044) 230 kV Bus a. Apply Fault at the NICHOLS 6 (524044) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from NICHOLS 6 (524044) 230 kV Bus to AMA_SOUTH 6 (524415) 230 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | No | No | No | No | Yes | No | No | Out Of Step Generators and damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000], 523941 [MAJSTC-WTG110.6900], 523942 [MAJSTC-WTG210.6900], 523942 [MAJSTC-WTG210.6900], 761358 [G17-239-GEN10.6900], 761361 [G17-239-GEN20.6900], 761799 [G17-187GEN1 0.6900], 761802 [G17-187GEN2 0.6900], 763084 [G18-073-GEN20.6600], 763090 [G18-073-GEN10.6600], 523936 [PANTEX_WIND10.6900], 524287 [GS-PHWD_GEN10.6900]
05 - Southwest | 25S | Transfer | Group5_Fault_0067_P1 | 3 phase fault on RANDALL 6 (524365) 230 kV Bus a. Apply Fault at the RANDALL 6 (524365) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from RANDALL 6 (524365) 230 kV Bus to AMA_SOUTH 6 (524415) 230 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | No | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points) |  | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25S | Transfer | Group5_Fault_0068_P1 | 3 phase fault on AMA_SOUTH 6 (524415) 230 kV Bus a. Apply Fault at the AMA_SOUTH 6 (524415) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from AMA_SOUTH 6 (524415) 230 kV Bus to AMA_SOUTH 3 (524414) 115 kV Bus to AMA_SO_TR1 1 (524410) 13.2 kV Bus CKT 1 | P1 | Yes | Yes | Yes | No | Yes | Yes | No | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points) |  | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25S | Transfer | Group5_Fault_0069_P1 | 3 phase fault on TUCO_INT 6 (525830) 230 kV Bus a. Apply Fault at the TUCO_INT 6 (525830) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from TUCO_INT 6 (525830) 230 kV Bus to TOLK 6 (525531) 230 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0070_P1 | 3 phase fault on TUCO_INT 7 (525832) 345 kV Bus a. Apply Fault at the TUCO_INT 7 (525832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from TUCO_INT 7 (525832) 345 kV Bus to TUCO_INT 6 (525830) 230 kV Bus to TUCO_TR1 1 (525824) 13.2 kV Bus CKT 1 b. 2. Drop Shunt 1 at TUCO_TR1 1 (525824) 13.2 kV Bus | P1 | Yes | Yes | Yes | No | Yes | No | No | Damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 763090 [G18-073-GEN10.6600], 763084 [G18-073-GEN20.6600]
05 - Southwest | 25S | Transfer | Group5_Fault_0071_P1 | 3 phase fault on TUCO_INT 7 (525832) 345 kV Bus a. Apply Fault at the TUCO_INT 7 (525832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from TUCO_INT 7 (525832) 345 kV Bus to TUCO_INT 6 (525830) 230 kV Bus to TUCO_TR2 1 (525825) 13.2 kV Bus CKT 2 | P1 | Yes | Yes | Yes | No | Yes | No | No | Damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 763090 [G18-073-GEN10.6600], 763084 [G18-073-GEN20.6600]
05 - Southwest | 25S | Transfer | Group5_Fault_0072_P1 | 3 phase fault on HARRNG_WST 6 (523977) 230 kV Bus a. Apply Fault at the HARRNG_WST 6 (523977) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from HARRNG_WST 6 (523977) 230 kV Bus to HARRNG_MID 6 (523978) 230 kV Bus CKT @1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | No | No | No | No | Yes | No | No | Out Of Step Generators and damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000], 523941 [MAJSTC-WTG110.6900], 523942 [MAJSTC-WTG210.6900], 523942 [MAJSTC-WTG210.6900], 761358 [G17-239-GEN10.6900], 761361 [G17-239-GEN20.6900], 761799 [G17-187GEN1 0.6900], 761802 [G17-187GEN2 0.6900], 763084 [G18-073-GEN20.6600], 763090 [G18-073-GEN10.6600], 523936 [PANTEX_WIND10.6900], 524287 [GS-PHWD_GEN10.6900]
05 - Southwest | 25S | Transfer | Group5_Fault_0073_P1 | 3 phase fault on HARRNG_MID 6 (523978) 230 kV Bus a. Apply Fault at the HARRNG_MID 6 (523978) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from HARRNG_MID 6 (523978) 230 kV Bus to RANDALL 6 (524365) 230 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | No | No | No | No | Yes | No | No | Out Of Step Generators and damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000], 523941 [MAJSTC-WTG110.6900], 523942 [MAJSTC-WTG210.6900], 523942 [MAJSTC-WTG210.6900], 761358 [G17-239-GEN10.6900], 761361 [G17-239-GEN20.6900], 761799 [G17-187GEN1 0.6900], 761802 [G17-187GEN2 0.6900], 763084 [G18-073-GEN20.6600], 763090 [G18-073-GEN10.6600], 523936 [PANTEX_WIND10.6900], 524287 [GS-PHWD_GEN10.6900]
05 - Southwest | 25S | Transfer | Group5_Fault_0074_P1 | 3 phase fault on HARRNG_MID 6 (523978) 230 kV Bus a. Apply Fault at the HARRNG_MID 6 (523978) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from HARRNG_MID 6 (523978) 230 kV Bus to NICHOLS 6 (524044) 230 kV Bus CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | No | No | No | No | Yes | No | No | Out Of Step Generators and damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000], 523941 [MAJSTC-WTG110.6900], 523942 [MAJSTC-WTG210.6900], 523942 [MAJSTC-WTG210.6900], 761358 [G17-239-GEN10.6900], 761361 [G17-239-GEN20.6900], 761799 [G17-187GEN1 0.6900], 761802 [G17-187GEN2 0.6900], 763084 [G18-073-GEN20.6600], 763090 [G18-073-GEN10.6600], 523936 [PANTEX_WIND10.6900], 524287 [GS-PHWD_GEN10.6900]
05 - Southwest | 25S | Transfer | Group5_Fault_0075_P1 | 3 phase fault on CASTRO_CNTY3 (524746) 115 kV Bus a. Apply Fault at the CASTRO_CNTY3 (524746) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from CASTRO_CNTY3 (524746) 115 kV Bus to DS-#22 3 (524694) 115 kV Bus CKT 1 b. 2. Drop Load 1 at DS-#22 3 (524694) 115 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0076_P1 | 3 phase fault on CASTRO_CNTY3 (524746) 115 kV Bus a. Apply Fault at the CASTRO_CNTY3 (524746) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from CASTRO_CNTY3 (524746) 115 kV Bus to CASTRO_CNTY2 (524745) 69 kV Bus to CASTRO_TR1 1 (524744) 13.2 kV Bus CKT 1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0077_P1 | 3 phase fault on CASTRO_CNTY3 (524746) 115 kV Bus a. Apply Fault at the CASTRO_CNTY3 (524746) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from CASTRO_CNTY3 (524746) 115 kV Bus to CASTRO_CNTY2 (524745) 69 kV Bus to CASTRO_TR2 1 (524743) 13.2 kV Bus CKT 2 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0078_P1 | 3 phase fault on CASTRO_CNTY3 (524746) 115 kV Bus a. Apply Fault at the CASTRO_CNTY3 (524746) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from CASTRO_CNTY3 (524746) 115 kV Bus to DS-#21 3 (524734) 115 kV Bus CKT 1 b. 2. Trip branch from DS-#21 3 (524734) 115 kV Bus to TIERABLANCA3 (524630) 115 kV Bus CKT 1 b. 3. Drop Load 1 at DS-#21 3 (524734) 115 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0079_P1 | 3 phase fault on KRESS_INT 3 (525192) 115 kV Bus a. Apply Fault at the KRESS_INT 3 (525192) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from KRESS_INT 3 (525192) 115 kV Bus to KRS_RURL_TP3 (525226) 115 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0080_P1 | 3 phase fault on KRESS_INT 3 (525192) 115 kV Bus a. Apply Fault at the KRESS_INT 3 (525192) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from KRESS_INT 3 (525192) 115 kV Bus to KRESS_INT 2 (525191) 69 kV Bus to KRESS_TR1 1 (525190) 13.2 kV Bus CKT 1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0081_P1 | 3 phase fault on KRESS_INT 3 (525192) 115 kV Bus a. Apply Fault at the KRESS_INT 3 (525192) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from KRESS_INT 3 (525192) 115 kV Bus to TULIA_TP 3 (525179) 115 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0082_P1 | 3 phase fault on KRESS_INT 3 (525192) 115 kV Bus a. Apply Fault at the KRESS_INT 3 (525192) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from KRESS_INT 3 (525192) 115 kV Bus to HALE_CNTY 3 (525454) 115 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0083_P1 | 3 phase fault on MOORE_CNTY 6 (523309) 230 kV Bus a. Apply Fault at the MOORE_CNTY 6 (523309) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from MOORE_CNTY 6 (523309) 230 kV Bus to MOORE_E 3 (523308) 115 kV Bus to MOORE_TR1 1 (523302) 13.2 kV Bus CKT 1 | P1 | Yes | Yes | Yes | No | Yes | Yes | No | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points) |  | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25S | Transfer | Group5_Fault_0084_P1 | 3 phase fault on MCDWL_CREEK3 (523322) 115 kV Bus a. Apply Fault at the MCDWL_CREEK3 (523322) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from MCDWL_CREEK3 (523322) 115 kV Bus to EXELL_TP 3 (523332) 115 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | No | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points) |  | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25S | Transfer | Group5_Fault_0085_P1 | 3 phase fault on PLSNT_HILL 6 (524770) 230 kV Bus a. Apply Fault at the PLSNT_HILL 6 (524770) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from PLSNT_HILL 6 (524770) 230 kV Bus to PLSNT_HILL 3 (524768) 115 kV Bus to PLSNHIL_TR11 (524767) 13.2 kV Bus CKT 1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0086_P1 | 3 phase fault on PLSNT_HILL 6 (524770) 230 kV Bus a. Apply Fault at the PLSNT_HILL 6 (524770) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from PLSNT_HILL 6 (524770) 230 kV Bus to OASIS 6 (524875) 230 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0087_P1 | 3 phase fault on OASIS 6 (524875) 230 kV Bus a. Apply Fault at the OASIS 6 (524875) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from OASIS 6 (524875) 230 kV Bus to OASIS 3 (524874) 115 kV Bus to OASIS_TR1 113.200 (524872) kV Bus CKT 1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0088_P1 | 3 phase fault on OASIS 6 (524875) 230 kV Bus a. Apply Fault at the OASIS 6 (524875) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from OASIS 6 (524875) 230 kV Bus to SN_JUAN_TAP6 (524885) 230 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0089_P1 | 3 phase fault on ROOSEVELT 3 (524908) 115 kV Bus a. Apply Fault at the ROOSEVELT 3 (524908) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from ROOSEVELT 3 (524908) 115 kV Bus to CURRY 3 (524822) 115 kV Bus CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0090_P1 | 3 phase fault on ROOSEVELT 3 (524908) 115 kV Bus a. Apply Fault at the ROOSEVELT 3 (524908) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from ROOSEVELT 3 (524908) 115 kV Bus to PORTALES 3 (524924) 115 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0091_P1 | 3 phase fault on LAMB_CNTY 3 (525636) 115 kV Bus a. Apply Fault at the LAMB_CNTY 3 (525636) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from LAMB_CNTY 3 (525636) 115 kV Bus to HOCKLEY 3 (526020) 115 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0092_P1 | 3 phase fault on LAMB_CNTY 3 (525636) 115 kV Bus a. Apply Fault at the LAMB_CNTY 3 (525636) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from LAMB_CNTY 3 (525636) 115 kV Bus to LAMB_CNTY 2 (525635) 69 kV Bus to LAMB_TR1 1 (525631) 13.2 kV Bus CKT 1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0093_P1 | 3 phase fault on LAMB_CNTY 3 (525636) 115 kV Bus a. Apply Fault at the LAMB_CNTY 3 (525636) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from LAMB_CNTY 3 (525636) 115 kV Bus to LAMB_CNTY 2 (525635) 69 kV Bus to LAMB_TR2 1 (525632) 13.2 kV Bus CKT 2 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0094_P1 | 3 phase fault on CARLISLE 6 (526161) 230 kV Bus a. Apply Fault at the CARLISLE 6 (526161) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from CARLISLE 6 (526161) 230 kV Bus to CARLISLE 3 (526160) 115 kV Bus to CRLSLE_TR1 1 (526157) 13.2 kV Bus CKT 1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0095_P1 | 3 phase fault on JONES 6 (526337) 230 kV Bus a. Apply Fault at the JONES 6 (526337) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from JONES 6 (526337) 230 kV Bus to LUBBCK_STH 6 (526269) 230 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0096_P1 | 3 phase fault on JONES 6 (526337) 230 kV Bus a. Apply Fault at the JONES 6 (526337) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from JONES 6 (526337) 230 kV Bus to LUBBCK_STH 6 (526269) 230 kV Bus CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0097_P1 | 3 phase fault on JONES 6 (526337) 230 kV Bus a. Apply Fault at the JONES 6 (526337) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from JONES 6 (526337) 230 kV Bus to GRASSLAND 6 (526677) 230 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0098_P1 | 3 phase fault on JONES 6 (526337) 230 kV Bus a. Apply Fault at the JONES 6 (526337) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from JONES 6 (526337) 230 kV Bus to LUBBCK_EST 6 (526299) 230 kV Bus CKT 1 b. 2. Trip three winding transformer from LUBBCK_EST 6 (526299) 230 kV Bus to LUBBCK_EST 3 (526298) 115 kV Bus to LBB_EST TR11 (526294) 13.2 kV Bus CKT 1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0099_P1 | 3 phase fault on TUCO_INT 3 (525828) 115 kV Bus a. Apply Fault at the TUCO_INT 3 (525828) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from TUCO_INT 3 (525828) 115 kV Bus to HALE_CNTY 3 (525454) 115 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0100_P1 | 3 phase fault on TUCO_INT 3 (525828) 115 kV Bus a. Apply Fault at the TUCO_INT 3 (525828) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from TUCO_INT 3 (525828) 115 kV Bus to LUBBCK_EST 3 (526298) 115 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0101_P1 | 3 phase fault on PLSNT_HILL 3 (524768) 115 kV Bus a. Apply Fault at the PLSNT_HILL 3 (524768) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from PLSNT_HILL 3 (524768) 115 kV Bus to NORTON 3 (524502) 115 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | Group5_Fault_0102_P1 | 3 phase fault on PLSNT_HILL 3 (524768) 115 kV Bus a. Apply Fault at the PLSNT_HILL 3 (524768) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from PLSNT_HILL 3 (524768) 115 kV Bus to E_CLOVIS 3 (524773) 115 kV Bus CKT 1 b. 2. Trip branch from E_CLOVIS 3 (524773) 115 kV Bus to CURRY 3 (524822) 115 kV Bus CKT 1 b. 3. Drop Load 1 at E_CLOVIS 3 (524773) 115 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0103_P1 | 3 phase fault on PLSNT_HILL 3 (524768) 115 kV Bus a. Apply Fault at the PLSNT_HILL 3 (524768) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from PLSNT_HILL 3 (524768) 115 kV Bus to N_CLOVIS_TP3 (524776) 115 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0104_P1 | 3 phase fault on PLSNT_HILL 3 (524768) 115 kV Bus a. Apply Fault at the PLSNT_HILL 3 (524768) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from PLSNT_HILL 3 (524768) 115 kV Bus to FE-HOLLAND 3 (524831) 115 kV Bus CKT 1 b. 2. Trip branch from FE-HOLLAND 3 (524831) 115 kV Bus to FE-CLOVIS2+3 (524838) 115 kV Bus CKT 1 b. 3. Trip branch from FE-CLOVIS2+3 (524838) 115 kV Bus to CURRY 3 (524822) 115 kV Bus CKT 1 b. 4. Drop Load 1 at FE-HOLLAND 3 (524831) 115 kV Bus b. 5. Drop Load 1 at FE-CLOVIS2+3 (524838) 115 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0105_P1 | 3 phase fault on SN_JUAN_TAP6 (524885) 230 kV Bus a. Apply Fault at the SN_JUAN_TAP6 (524885) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from SN_JUAN_TAP6 (524885) 230 kV Bus to CHAVES_CNTY6 (527483) 230 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0106_P1 | 3 phase fault on OASIS 3 (524874) 115 kV Bus a. Apply Fault at the OASIS 3 (524874) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from OASIS 3 (524874) 115 kV Bus to PORTALES 3 (524924) 115 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0107_P1 | 3 phase fault on OASIS 3 (524874) 115 kV Bus a. Apply Fault at the OASIS 3 (524874) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from OASIS 3 (524874) 115 kV Bus to PERIMETER 3 (524797) 115 kV Bus CKT 1 b. 2. Trip branch from PERIMETER 3 (524797) 115 kV Bus to CANNON_TP 3 (524790) 115 kV Bus CKT 1 b. 3. Drop Load 1 at PERIMETER 3 (524797) 115 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0108_P1 | 3 phase fault on OASIS 3 (524874) 115 kV Bus a. Apply Fault at the OASIS 3 (524874) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from OASIS 3 (524874) 115 kV Bus to FE-CHZPLT 3 (524863) 115 kV Bus CKT 1 b. 2. Trip branch from FE-CHZPLT 3 (524863) 115 kV Bus to NORRIS_TP 3 (524764) 115 kV Bus CKT 1 b. 3. Drop Load 1 at FE-CHZPLT 3 (524863) 115 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0109_P1 | 3 phase fault on CURRY 3 (524822) 115 kV Bus a. Apply Fault at the CURRY 3 (524822) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from CURRY 3 (524822) 115 kV Bus to NORRIS_TP 3 (524764) 115 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0110_P1 | 3 phase fault on NORRIS_TP 3 (524764) 115 kV Bus a. Apply Fault at the NORRIS_TP 3 (524764) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from NORRIS_TP 3 (524764) 115 kV Bus to NORRIS 3 (524801) 115 kV Bus CKT 1 b. 2. Drop Load 1 at NORRIS 3 (524801) 115 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0111_P1 | 3 phase fault on CURRY 3 (524822) 115 kV Bus a. Apply Fault at the CURRY 3 (524822) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from CURRY 3 (524822) 115 kV Bus to CURRY 2 (524821) 69 kV Bus to CURRY_TR1 1 (524819) 13.2 kV Bus CKT 1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0112_P1 | 3 phase fault on CURRY 3 (524822) 115 kV Bus a. Apply Fault at the CURRY 3 (524822) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from CURRY 3 (524822) 115 kV Bus to CURRY 2 (524821) 69 kV Bus to CURRY_TR2 1 (524820) 13.2 kV Bus CKT 2 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0113_P1 | 3 phase fault on CURRY 3 (524822) 115 kV Bus a. Apply Fault at the CURRY 3 (524822) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from CURRY 3 (524822) 115 kV Bus to BAILEYCO 3 (525028) 115 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0114_P1 | 3 phase fault on PORTALES 3 (524924) 115 kV Bus a. Apply Fault at the PORTALES 3 (524924) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from PORTALES 3 (524924) 115 kV Bus to PORTALES 2 (524923) 69 kV Bus to PORTLES_TR11 (524921) 13.2 kV Bus CKT 1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0115_P1 | 3 phase fault on PORTALES 3 (524924) 115 kV Bus a. Apply Fault at the PORTALES 3 (524924) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from PORTALES 3 (524924) 115 kV Bus to PORTALES 2 (524923) 69 kV Bus to PORTLES_TR21 (524922) 13.2 kV Bus CKT 2 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0116_P1 | 3 phase fault on DEAFSMITH 6 (524623) 230 kV Bus a. Apply Fault at the DEAFSMITH 6 (524623) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from DEAFSMITH 6 (524623) 230 kV Bus to DFSMTH_WST 3 (524622) 115 kV Bus to DEFSMTH_TR11 (524620) 13.2 kV Bus CKT 1 b. 2. Trip branch from DFSMTH_WST 3 (524622) 115 kV Bus to TIERABLANCA3 (524630) 115 kV Bus CKT 2 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0117_P1 | 3 phase fault on INK_BASIN 6 (527028) 230 kV Bus a. Apply Fault at the INK_BASIN 6 (527028) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from INK_BASIN 6 (527028) 230 kV Bus to INK_BASIN 3 (527027) 115 kV Bus to INKBASN_TR 1 (527026) 13.2 kV Bus CKT 1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0118_P1 | 3 phase fault on HOCKLEY 3 (526020) 115 kV Bus a. Apply Fault at the HOCKLEY 3 (526020) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from HOCKLEY 3 (526020) 115 kV Bus to HOCKLEY 2 (526019) 69 kV Bus to HOCKLEY_TR11 (526017) 13.2 kV Bus CKT 1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0119_P1 | 3 phase fault on HOCKLEY 3 (526020) 115 kV Bus a. Apply Fault at the HOCKLEY 3 (526020) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from HOCKLEY 3 (526020) 115 kV Bus to HOCKLEY 2 (526019) 69 kV Bus to HOCKLEY_TR21 (526018) 13.2 kV Bus CKT 2 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0120_P1 | 3 phase fault on N_CLOVIS_TP3 (524776) 115 kV Bus a. Apply Fault at the N_CLOVIS_TP3 (524776) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from N_CLOVIS_TP3 (524776) 115 kV Bus to FE-CLVS_INT3 (524808) 115 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0121_P1 | 3 phase fault on N_CLOVIS_TP3 (524776) 115 kV Bus a. Apply Fault at the N_CLOVIS_TP3 (524776) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from N_CLOVIS_TP3 (524776) 115 kV Bus to N_CLOVIS 3 (524777) 115 kV Bus CKT 1 b. 2. Drop Load 1 at N_CLOVIS 3 (524777) 115 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | Group5_Fault_0122_P1 | 3 phase fault on NORTON 3 (524502) 115 kV Bus a. Apply Fault at the NORTON 3 (524502) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from NORTON 3 (524502) 115 kV Bus to FE-TUCMCARI3 (524509) 115 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0123_P1 | 3 phase fault on CHAVES_CNTY6 (527483) 230 kV Bus a. Apply Fault at the CHAVES_CNTY6 (527483) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from CHAVES_CNTY6 (527483) 230 kV Bus to EDDY_NORTH 6 (527799) 230 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0124_P1 | 3 phase fault on CHAVES_CNTY6 (527483) 230 kV Bus a. Apply Fault at the CHAVES_CNTY6 (527483) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from CHAVES_CNTY6 (527483) 230 kV Bus to CHAVES_CNTY3 (527482) 115 kV Bus to CHAVES_TR1 1 (527478) 13.2 kV Bus CKT 1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0125_P1 | 3 phase fault on CHAVES_CNTY6 (527483) 230 kV Bus a. Apply Fault at the CHAVES_CNTY6 (527483) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from CHAVES_CNTY6 (527483) 230 kV Bus to CHAVES_CNTY3 (527482) 115 kV Bus to CHAVES_TR2 1 (527479) 13.2 kV Bus CKT 2 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0126_P1 | 3 phase fault on EDDY_CNTY 7 (527802) 345 kV Bus a. Apply Fault at the EDDY_CNTY 7 (527802) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from EDDY_CNTY 7 (527802) 345 kV Bus to KIOWA 7 (527965) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | No | No | No | No | Yes | No | No | Out Of Step Generators and damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000], 523941 [MAJSTC-WTG110.6900], 523942 [MAJSTC-WTG210.6900], 523942 [MAJSTC-WTG210.6900], 761358 [G17-239-GEN10.6900], 761361 [G17-239-GEN20.6900], 761799 [G17-187GEN1 0.6900], 761802 [G17-187GEN2 0.6900], 763084 [G18-073-GEN20.6600], 763090 [G18-073-GEN10.6600], 523936 [PANTEX_WIND10.6900], 524287 [GS-PHWD_GEN10.6900]
05 - Southwest | 25S | Transfer | Group5_Fault_0127_P1 | 3 phase fault on EDDY_CNTY 7 (527802) 345 kV Bus a. Apply Fault at the EDDY_CNTY 7 (527802) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from EDDY_CNTY 7 (527802) 345 kV Bus to EDDY_NORTH 6 (527799) 230 kV Bus to EDDY_TR 1 (527796) 13.2 kV Bus CKT 1 b. 2. Drop Shunt 1 at EDDY_TR 1 (527796) 13.2 kV Bus | P1 | Yes | Yes | Yes | No | No | No | No | Damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000], 523941 [MAJSTC-WTG110.6900], 523942 [MAJSTC-WTG210.6900], 523942 [MAJSTC-WTG210.6900], 761358 [G17-239-GEN10.6900], 761361 [G17-239-GEN20.6900], 761799 [G17-187GEN1 0.6900], 761802 [G17-187GEN2 0.6900], 763084 [G18-073-GEN20.6600], 763090 [G18-073-GEN10.6600], 523936 [PANTEX_WIND10.6900], 524287 [GS-PHWD_GEN10.6900]
05 - Southwest | 25S | Transfer | Group5_Fault_0128_P1 | 3 phase fault on FE-CLVS_INT3 (524808) 115 kV Bus a. Apply Fault at the FE-CLVS_INT3 (524808) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from FE-CLVS_INT3 (524808) 115 kV Bus to W_CLOVIS 3 (524784) 115 kV Bus CKT 1 b. 2. Trip branch from W_CLOVIS 3 (524784) 115 kV Bus to CANNON_TP 3 (524790) 115 kV Bus CKT 1 b. 3. Drop Load 1 at W_CLOVIS 3 (524784) 115 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0129_P1 | 3 phase fault on CANNON_TP 3 (524790) 115 kV Bus a. Apply Fault at the CANNON_TP 3 (524790) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from CANNON_TP 3 (524790) 115 kV Bus to CANNONAFB 3 (524794) 115 kV Bus CKT 1 b. 2. Drop Load 1 at CANNONAFB 3 (524794) 115 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0130_P1 | 3 phase fault on EDDY_NORTH 6 (527799) 230 kV Bus a. Apply Fault at the EDDY_NORTH 6 (527799) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from EDDY_NORTH 6 (527799) 230 kV Bus to EDDY_NTH 3 (527798) 115 kV Bus to EDDY_TR2 1 (527797) 13.2 kV Bus CKT 1 | P1 | Yes | Yes | Yes | No | Yes | No | No | Damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000], 523941 [MAJSTC-WTG110.6900], 523942 [MAJSTC-WTG210.6900], 523942 [MAJSTC-WTG210.6900], 523936 [PANTEX_WIND10.6900], 524287 [GS-PHWD_GEN10.6900]
05 - Southwest | 25S | Transfer | Group5_Fault_0131_P1 | 3 phase fault on EDDY_NORTH 6 (527799) 230 kV Bus a. Apply Fault at the EDDY_NORTH 6 (527799) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from EDDY_NORTH 6 (527799) 230 kV Bus to EDDY_STH 3 (527793) 115 kV Bus to EDDY_TR3 1 (527795) 13.2 kV Bus CKT 2 | P1 | Yes | Yes | Yes | No | Yes | No | No | Damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000], 523941 [MAJSTC-WTG110.6900], 523942 [MAJSTC-WTG210.6900], 523942 [MAJSTC-WTG210.6900], 523936 [PANTEX_WIND10.6900], 524287 [GS-PHWD_GEN10.6900]
05 - Southwest | 25S | Transfer | Group5_Fault_0132_P1 | 3 phase fault on CHAVES_CNTY3 (527482) 115 kV Bus a. Apply Fault at the CHAVES_CNTY3 (527482) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from CHAVES_CNTY3 (527482) 115 kV Bus to PRICE_TAP 3 (527509) 115 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0133_P1 | 3 phase fault on CHAVES_CNTY3 (527482) 115 kV Bus a. Apply Fault at the CHAVES_CNTY3 (527482) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from CHAVES_CNTY3 (527482) 115 kV Bus to URTON 3 (527501) 115 kV Bus CKT 1 b. 2. Trip branch from URTON 3 (527501) 115 kV Bus to ROSWELL_CTY3 (527522) 115 kV Bus CKT 1 b. 3. Drop Load 1 at URTON 3 (527501) 115 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | No | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points) |  | Generator relays were disabled for the following generators: 583973 [G14-035-GEN10.5500]
05 - Southwest | 25S | Transfer | Group5_Fault_0134_P1 | 3 phase fault on CHAVES_CNTY3 (527482) 115 kV Bus a. Apply Fault at the CHAVES_CNTY3 (527482) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from CHAVES_CNTY3 (527482) 115 kV Bus to SAMSON 3 (527546) 115 kV Bus CKT 1 b. 2. Trip branch from SAMSON 3 (527546) 115 kV Bus to ROSWLL_INT 3 (527564) 115 kV Bus CKT 1 b. 3. Drop Load 1 at SAMSON 3 (527546) 115 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | No | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points) |  | Generator relays were disabled for the following generators: 583973 [G14-035-GEN10.5500]
05 - Southwest | 25S | Transfer | Group5_Fault_0135_P1 | 3 phase fault on CARLISLE 3 (526160) 115 kV Bus a. Apply Fault at the CARLISLE 3 (526160) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from CARLISLE 3 (526160) 115 kV Bus to LP-DOUD_TP 3 (526162) 115 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0136_P1 | 3 phase fault on LP-DOUD_TP 3 (526162) 115 kV Bus a. Apply Fault at the LP-DOUD_TP 3 (526162) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from LP-DOUD_TP 3 (526162) 115 kV Bus to SP-WOLF_TP 3 (526481) 115 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0137_P1 | 3 phase fault on LP-DOUD_TP 3 (526162) 115 kV Bus a. Apply Fault at the LP-DOUD_TP 3 (526162) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from LP-DOUD_TP 3 (526162) 115 kV Bus to LP-DOUD 3 (526176) 115 kV Bus CKT 1 b. 2. Drop Load 1 at LP-DOUD 3 (526176) 115 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0138_P1 | 3 phase fault on AMOCO_TP 3 (526445) 115 kV Bus a. Apply Fault at the AMOCO_TP 3 (526445) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from AMOCO_TP 3 (526445) 115 kV Bus to LG-LEVELAND3 (526484) 115 kV Bus CKT 1 b. 2. Trip branch from LG-LEVELAND3 (526484) 115 kV Bus to LG-CLAUENE 3 (526491) 115 kV Bus CKT 1 b. 3. Trip branch from LG-CLAUENE 3 (526491) 115 kV Bus to TERRY_CNTY 3 (526736) 115 kV Bus CKT 1 b. 4. Drop Load 1 at LG-LEVELAND3 (526484) 115 kV Bus b. 5. Drop Load 1 at LG-CLAUENE 3 (526491) 115 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0139_P1 | 3 phase fault on SP-WOLF_TP 3 (526481) 115 kV Bus a. Apply Fault at the SP-WOLF_TP 3 (526481) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from SP-WOLF_TP 3 (526481) 115 kV Bus to YUMA_INT 3 (526475) 115 kV Bus CKT 1 b. 2. Trip branch from YUMA_INT 3 (526475) 115 kV Bus to WOLFFORTH 3 (526524) 115 kV Bus CKT 1 b. 3. Drop Load 1 at YUMA_INT 3 (526475) 115 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0140_P1 | 3 phase fault on SP-WOLF_TP 3 (526481) 115 kV Bus a. Apply Fault at the SP-WOLF_TP 3 (526481) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from SP-WOLF_TP 3 (526481) 115 kV Bus to SP-WOLFORTH3 (526483) 115 kV Bus CKT 1 b. 2. Drop Load 1 at SP-WOLFORTH3 (526483) 115 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0141_P1 | 3 phase fault on RANDALL 3 (524364) 115 kV Bus a. Apply Fault at the RANDALL 3 (524364) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from RANDALL 3 (524364) 115 kV Bus to GEORGIA 3 (524322) 115 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | No | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points) |  | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25S | Transfer | Group5_Fault_0142_P1 | 3 phase fault on RANDALL 3 (524364) 115 kV Bus a. Apply Fault at the RANDALL 3 (524364) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from RANDALL 3 (524364) 115 kV Bus to PALO_DURO 3 (524530) 115 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | No | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points) |  | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25S | Transfer | Group5_Fault_0143_P1 | 3 phase fault on RANDALL 3 (524364) 115 kV Bus a. Apply Fault at the RANDALL 3 (524364) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from RANDALL 3 (524364) 115 kV Bus to CANYON_E_TP3 (524522) 115 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | No | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points) |  | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25S | Transfer | Group5_Fault_0144_P1 | 3 phase fault on RANDALL 3 (524364) 115 kV Bus a. Apply Fault at the RANDALL 3 (524364) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from RANDALL 3 (524364) 115 kV Bus to SOUTHEAST 3 (524338) 115 kV Bus CKT 1 b. 2. Trip branch from SOUTHEAST 3 (524338) 115 kV Bus to PULLMAN 3 (524331) 115 kV Bus CKT 1 b. 3. Drop Load 1 at SOUTHEAST 3 (524338) 115 kV Bus b. 4. Drop Load 1 at PULLMAN 3 (524331) 115 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | No | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points) |  | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25S | Transfer | Group5_Fault_0145_P1 | 3 phase fault on RANDALL 3 (524364) 115 kV Bus a. Apply Fault at the RANDALL 3 (524364) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from RANDALL 3 (524364) 115 kV Bus to MANHATTAN 3 (524224) 115 kV Bus CKT 1 b. 2. Trip branch from MANHATTAN 3 (524224) 115 kV Bus to EAST_PLANT 3 (524162) 115 kV Bus CKT 1 b. 3. Drop Load 1 at MANHATTAN 3 (524224) 115 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | No | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points) |  | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25S | Transfer | Group5_Fault_0146_P1 | 3 phase fault on RANDALL 6 (524365) 230 kV Bus a. Apply Fault at the RANDALL 6 (524365) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from RANDALL 6 (524365) 230 kV Bus to RANDALL 3 (524364) 115 kV Bus to RANDAL_TR1 1 (524361) 13.2 kV Bus CKT 1 | P1 | Yes | Yes | Yes | No | Yes | Yes | No | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points) |  | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25S | Transfer | Group5_Fault_0147_P1 | 3 phase fault on RANDALL 6 (524365) 230 kV Bus a. Apply Fault at the RANDALL 6 (524365) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from RANDALL 6 (524365) 230 kV Bus to RANDALL 3 (524364) 115 kV Bus to RANDAL_TR2 1 (524360) 13.2 kV Bus CKT 2 | P1 | Yes | Yes | Yes | No | Yes | Yes | No | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points) |  | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25S | Transfer | Group5_Fault_0148_P1 | 3 phase fault on GEORGIA 3 (524322) 115 kV Bus a. Apply Fault at the GEORGIA 3 (524322) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from GEORGIA 3 (524322) 115 kV Bus to WESTERN 3 (524325) 115 kV Bus CKT 1 b. 2. Trip branch from WESTERN 3 (524325) 115 kV Bus to 34TH_ST_TP 3 (524281) 115 kV Bus CKT 1 b. 3. Drop Load 1 at WESTERN 3 (524325) 115 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | No | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points) |  | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25S | Transfer | Group5_Fault_0149_P1 | 3 phase fault on GEORGIA 3 (524322) 115 kV Bus a. Apply Fault at the GEORGIA 3 (524322) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from GEORGIA 3 (524322) 115 kV Bus to GEORGIA 2 (524321) 69 kV Bus to GEORGIA_TR11 (524320) 13.2 kV Bus CKT 1 b. 2. Trip branch from GEORGIA 2 (524321) 69 kV Bus to LAWRENPRK1 2 (524209) 69 kV Bus CKT 1 b. 3. Trip branch from LAWRENPRK1 2 (524209) 69 kV Bus to LAWRENPRK2 2 (524216) 69 kV Bus CKT @1 b. 4. Trip branch from LAWRENPRK2 2 (524216) 69 kV Bus to SONCY 2 (524200) 69 kV Bus CKT 1 b. 5. Trip branch from SONCY 2 (524200) 69 kV Bus to SONCY_TP 2 (524251) 69 kV Bus CKT 1 b. 6. Drop Load 1 at LAWRENPRK1 2 (524209) 69 kV Bus b. 7. Drop Load 1 at LAWRENPRK2 2 (524216) 69 kV Bus | P1 | Yes | Yes | Yes | No | Yes | Yes | No | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points) |  | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25S | Transfer | Group5_Fault_0150_P1 | 3 phase fault on GEORGIA 3 (524322) 115 kV Bus a. Apply Fault at the GEORGIA 3 (524322) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from GEORGIA 3 (524322) 115 kV Bus to CRSE_HINDTP3 (524387) 115 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | No | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points) |  | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25S | Transfer | Group5_Fault_0151_P1 | 3 phase fault on CANYON_E_TP3 (524522) 115 kV Bus a. Apply Fault at the CANYON_E_TP3 (524522) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from CANYON_E_TP3 (524522) 115 kV Bus to HUNSLEY 3 (524520) 115 kV Bus CKT 1 b. 2. Trip branch from HUNSLEY 3 (524520) 115 kV Bus to CANYON_WEST3 (524516) 115 kV Bus CKT 1 b. 3. Trip branch from CANYON_WEST3 (524516) 115 kV Bus to DAWN 3 (524590) 115 kV Bus CKT 1 b. 4. Trip branch from DAWN 3 (524590) 115 kV Bus to PANDAHFD 3 (524597) 115 kV Bus CKT 1 b. 5. Trip branch from PANDAHFD 3 (524597) 115 kV Bus to DS-#25+ 3 (524575) 115 kV Bus CKT 1 b. 6. Trip branch from DS-#25+ 3 (524575) 115 kV Bus to TIERABLANCA3 (524630) 115 kV Bus CKT 1 b. 7. Drop Load 1 at HUNSLEY 3 (524520) 115 kV Bus b. 8. Drop Load 1 at CANYON_WEST3 (524516) 115 kV Bus b. 9. Drop Load 1 at DAWN 3 (524590) 115 kV Bus b. 10. Drop Load 1 at PANDAHFD 3 (524597) 115 kV Bus b. 11. Drop Load 1 at DS-#25+ 3 (524575) 115 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0152_P1 | 3 phase fault on CANYON_E_TP3 (524522) 115 kV Bus a. Apply Fault at the CANYON_E_TP3 (524522) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from CANYON_E_TP3 (524522) 115 kV Bus to CANYON_EAST3 (524523) 115 kV Bus CKT 1 b. 2. Drop Load 1 at CANYON_EAST3 (524523) 115 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0153_P1 | 3 phase fault on PALO_DURO 3 (524530) 115 kV Bus a. Apply Fault at the PALO_DURO 3 (524530) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from PALO_DURO 3 (524530) 115 kV Bus to HAPPY_INT 3 (525154) 115 kV Bus CKT 1 b. 2. Drop Load 1 at PALO_DURO 3 (524530) 115 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0154_P1 | 3 phase fault on CRSE_HINDTP3 (524387) 115 kV Bus a. Apply Fault at the CRSE_HINDTP3 (524387) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from CRSE_HINDTP3 (524387) 115 kV Bus to CROUSE_HIND3 (524388) 115 kV Bus CKT 1 b. 2. Drop Load 1 at CROUSE_HIND3 (524388) 115 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | No | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points) |  | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25S | Transfer | Group5_Fault_0155_P1 | 3 phase fault on CRSE_HINDTP3 (524387) 115 kV Bus a. Apply Fault at the CRSE_HINDTP3 (524387) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from CRSE_HINDTP3 (524387) 115 kV Bus to FARMERS 3 (524377) 115 kV Bus CKT 1 b. 2. Trip branch from FARMERS 3 (524377) 115 kV Bus to AMA_SOUTH 3 (524414) 115 kV Bus CKT 1 b. 3. Drop Load 1 at FARMERS 3 (524377) 115 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | No | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points) |  | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25S | Transfer | Group5_Fault_0156_P1 | 3 phase fault on 34TH_ST_TP 3 (524281) 115 kV Bus a. Apply Fault at the 34TH_ST_TP 3 (524281) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from 34TH_ST_TP 3 (524281) 115 kV Bus to 34TH_ST 3 (524282) 115 kV Bus CKT 1 b. 2. Drop Load 1 at 34TH_ST 3 (524282) 115 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | No | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points) |  | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25S | Transfer | Group5_Fault_0157_P1 | 3 phase fault on 34TH_ST_TP 3 (524281) 115 kV Bus a. Apply Fault at the 34TH_ST_TP 3 (524281) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from 34TH_ST_TP 3 (524281) 115 kV Bus to COULTER 3 (524306) 115 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | No | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points) |  | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25S | Transfer | Group5_Fault_0158_P1 | 3 phase fault on COULTER 3 (524306) 115 kV Bus a. Apply Fault at the COULTER 3 (524306) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from COULTER 3 (524306) 115 kV Bus to ESTACADO_TP3 (524425) 115 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | No | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points) |  | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25S | Transfer | Group5_Fault_0159_P1 | 3 phase fault on COULTER 3 (524306) 115 kV Bus a. Apply Fault at the COULTER 3 (524306) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from COULTER 3 (524306) 115 kV Bus to COULTER 2 (524305) 69 kV Bus to COLTER_TR1 1 (524304) 13.2 kV Bus CKT 1 b. 2. Trip branch from COULTER 2 (524305) 69 kV Bus to WATERFL_TP 2 (524234) 69 kV Bus CKT 1 | P1 | Yes | Yes | Yes | No | Yes | Yes | No | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points) |  | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25S | Transfer | Group5_Fault_0160_P1 | 3 phase fault on COULTER 3 (524306) 115 kV Bus a. Apply Fault at the COULTER 3 (524306) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from COULTER 3 (524306) 115 kV Bus to PUCKETT 3 (524256) 115 kV Bus CKT 1 b. 2. Trip branch from PUCKETT 3 (524256) 115 kV Bus to SONCY_TP 3 (524252) 115 kV Bus CKT 1 b. 3. Drop Load 1 at PUCKETT 3 (524256) 115 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | No | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points) |  | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25S | Transfer | Group5_Fault_0161_P1 | 3 phase fault on ESTACADO_TP3 (524425) 115 kV Bus a. Apply Fault at the ESTACADO_TP3 (524425) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from ESTACADO_TP3 (524425) 115 kV Bus to ESTACADO 3 (524432) 115 kV Bus CKT 1 b. 2. Drop Load 1 at ESTACADO 3 (524432) 115 kV Bus b. 3. Drop Load 2 at ESTACADO 3 (524432) 115 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | No | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points) |  | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25S | Transfer | Group5_Fault_0162_P1 | 3 phase fault on ESTACADO_TP3 (524425) 115 kV Bus a. Apply Fault at the ESTACADO_TP3 (524425) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from ESTACADO_TP3 (524425) 115 kV Bus to PRESTONWEST3 (524341) 115 kV Bus CKT 1 b. 2. Trip branch from PRESTONWEST3 (524341) 115 kV Bus to OWENSCORN 3 (524404) 115 kV Bus CKT 1 b. 3. Trip branch from OWENSCORN 3 (524404) 115 kV Bus to AMA_SOUTH 3 (524414) 115 kV Bus CKT 1 b. 4. Drop Load 1 at PRESTONWEST3 (524341) 115 kV Bus b. 5. Drop Load 1 at OWENSCORN 3 (524404) 115 kV Bus b. 6. Drop Shunt 1 at OWENSCORN 3 (524404) 115 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | No | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points) |  | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25S | Transfer | Group5_Fault_0163_P1 | 3 phase fault on NICHOLS 3 (524043) 115 kV Bus a. Apply Fault at the NICHOLS 3 (524043) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from NICHOLS 3 (524043) 115 kV Bus to WHITAKER 3 (524058) 115 kV Bus CKT 1 b. 2. Trip branch from WHITAKER 3 (524058) 115 kV Bus to EAST_PLANT 3 (524162) 115 kV Bus CKT 1 b. 3. Drop Load 1 at WHITAKER 3 (524058) 115 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | No | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points) |  | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000], 524021 [NICHOLS_1 113.800], 763309 [G18-112-GEN10.6600]
05 - Southwest | 25S | Transfer | Group5_Fault_0164_P1 | 3 phase fault on ROLLHILLS 3 (524007) 115 kV Bus a. Apply Fault at the ROLLHILLS 3 (524007) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from ROLLHILLS 3 (524007) 115 kV Bus to HASTINGS 3 (524136) 115 kV Bus CKT 1 b. 2. Trip branch from HASTINGS 3 (524136) 115 kV Bus to EAST_PLANT 3 (524162) 115 kV Bus CKT 1 b. 3. Drop Load 1 at HASTINGS 3 (524136) 115 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | No | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points) |  | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25S | Transfer | Group5_Fault_0165_P1 | 3 phase fault on EAST_PLANT 3 (524162) 115 kV Bus a. Apply Fault at the EAST_PLANT 3 (524162) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from EAST_PLANT 3 (524162) 115 kV Bus to PIERCE_TP 3 (524185) 115 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | No | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points) |  | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25S | Transfer | Group5_Fault_0166_P1 | 3 phase fault on EAST_PLANT 3 (524162) 115 kV Bus a. Apply Fault at the EAST_PLANT 3 (524162) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from EAST_PLANT 3 (524162) 115 kV Bus to EAST_PLANT 2 (524161) 69 kV Bus to EPLANT_TR1 1 (524158) 13.2 kV Bus CKT 1 | P1 | Yes | Yes | Yes | No | Yes | Yes | No | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points) |  | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25S | Transfer | Group5_Fault_0167_P1 | 3 phase fault on EAST_PLANT 3 (524162) 115 kV Bus a. Apply Fault at the EAST_PLANT 3 (524162) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from EAST_PLANT 3 (524162) 115 kV Bus to EAST_PLANT 2 (524161) 69 kV Bus to EPLANT_TR2 1 (524159) 13.2 kV Bus CKT 2 | P1 | Yes | Yes | Yes | No | Yes | Yes | No | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points) |  | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25S | Transfer | Group5_Fault_0168_P1 | 3 phase fault on EAST_PLANT 3 (524162) 115 kV Bus a. Apply Fault at the EAST_PLANT 3 (524162) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from EAST_PLANT 6 (524163) 230 kV Bus to EAST_PLANT 3 (524162) 115 kV Bus to EPLANT_TR3 1 (524160) 13.2 kV Bus CKT 1 b. 2. Trip branch from EAST_PLANT 6 (524163) 230 kV Bus to HARRNG_WST 6 (523977) 230 kV Bus CKT 1 | P1 | Yes | Yes | Yes | No | Yes | Yes | No | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points) |  | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25S | Transfer | Group5_Fault_0169_P1 | 3 phase fault on HAPPY_INT 3 (525154) 115 kV Bus a. Apply Fault at the HAPPY_INT 3 (525154) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from HAPPY_INT 3 (525154) 115 kV Bus to TULIA_TP 3 (525179) 115 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0170_P1 | 3 phase fault on HAPPY_INT 3 (525154) 115 kV Bus a. Apply Fault at the HAPPY_INT 3 (525154) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from HAPPY_INT 3 (525154) 115 kV Bus to HAPPY_INT 2 (525153) 69 kV Bus to HAPPY_TR1 1 (525151) 13.2 kV Bus CKT 1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0171_P1 | 3 phase fault on HAPPY_INT 3 (525154) 115 kV Bus a. Apply Fault at the HAPPY_INT 3 (525154) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from HAPPY_INT 3 (525154) 115 kV Bus to HAPPY_INT 2 (525153) 69 kV Bus to HAPPY_TR2 1 (525152) 13.2 kV Bus CKT 2 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0172_P1 | 3 phase fault on AMA_SOUTH 3 (524414) 115 kV Bus a. Apply Fault at the AMA_SOUTH 3 (524414) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from AMA_SOUTH 3 (524414) 115 kV Bus to ARROWHEAD 3 (524397) 115 kV Bus CKT 1 b. 2. Trip branch from ARROWHEAD 3 (524397) 115 kV Bus to OSAGE 3 (524345) 115 kV Bus CKT 1 b. 3. Trip branch from OSAGE 3 (524345) 115 kV Bus to PIERCE_TP 3 (524185) 115 kV Bus CKT 1 b. 4. Drop Load 1 at ARROWHEAD 3 (524397) 115 kV Bus b. 5. Drop Load 1 at OSAGE 3 (524345) 115 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | No | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points) |  | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25S | Transfer | Group5_Fault_0173_P1 | 3 phase fault on AMA_SOUTH 3 (524414) 115 kV Bus a. Apply Fault at the AMA_SOUTH 3 (524414) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from AMA_SOUTH 3 (524414) 115 kV Bus to SPRING_DRW 3 (524544) 115 kV Bus CKT 1 b. 2. Drop Load 1 at SPRING_DRW 3 (524544) 115 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | No | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points) |  | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25S | Transfer | Group5_Fault_0174_P1 | 3 phase fault on TULIA_TP 3 (525179) 115 kV Bus a. Apply Fault at the TULIA_TP 3 (525179) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from TULIA_TP 3 (525179) 115 kV Bus to MU-TULIA 3 (522800) 115 kV Bus CKT 1 b. 2. Drop Load 1 at MU-TULIA 3 (522800) 115 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0175_P1 | 3 phase fault on SONCY_TP 3 (524252) 115 kV Bus a. Apply Fault at the SONCY_TP 3 (524252) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from SONCY_TP 3 (524252) 115 kV Bus to SONCY 3 (524254) 115 kV Bus CKT 1 b. 2. Drop Load 1 at SONCY 3 (524254) 115 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | No | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points) |  | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25S | Transfer | Group5_Fault_0176_P1 | 3 phase fault on SONCY_TP 3 (524252) 115 kV Bus a. Apply Fault at the SONCY_TP 3 (524252) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from SONCY_TP 3 (524252) 115 kV Bus to SUNSET 3 (524249) 115 kV Bus CKT 1 b. 2. Trip branch from SUNSET 3 (524249) 115 kV Bus to NORTHWEST 3 (524106) 115 kV Bus CKT 1 b. 3. Drop Load 1 at SUNSET 3 (524249) 115 kV Bus b. 4. Drop Load 2 at SUNSET 3 (524249) 115 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | No | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points) |  | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25S | Transfer | Group5_Fault_0177_P1 | 3 phase fault on EAST_PLANT 2 (524161) 69 kV Bus a. Apply Fault at the EAST_PLANT 2 (524161) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from EAST_PLANT 2 (524161) 69 kV Bus to VANBUREN#1 2 (524142) 69 kV Bus CKT 1 b. 2. Drop Load 1 at VANBUREN#1 2 (524142) 69 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0178_P1 | 3 phase fault on EAST_PLANT 2 (524161) 69 kV Bus a. Apply Fault at the EAST_PLANT 2 (524161) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from EAST_PLANT 2 (524161) 69 kV Bus to VANBUREN#2 2 (524149) 69 kV Bus CKT 1 b. 2. Drop Load 1 at VANBUREN#2 2 (524149) 69 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0179_P1 | 3 phase fault on HAPPY_INT 2 (525153) 69 kV Bus a. Apply Fault at the HAPPY_INT 2 (525153) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from HAPPY_INT 2 (525153) 69 kV Bus to HAPPY_CTYTP2 (525143) 69 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0180_P1 | 3 phase fault on SONCY_TP 2 (524251) 69 kV Bus a. Apply Fault at the SONCY_TP 2 (524251) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from SONCY_TP 2 (524251) 69 kV Bus to NRTHWST_TP 2 (524096) 69 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0181_P1 | 3 phase fault on ROLLHILLS 3 (524007) 115 kV Bus a. Apply Fault at the ROLLHILLS 3 (524007) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from ROLLHILLS 3 (524007) 115 kV Bus to NORTHWEST 3 (524106) 115 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | No | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points) |  | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25S | Transfer | Group5_Fault_0182_P1 | 3 phase fault on NORTHWEST 3 (524106) 115 kV Bus a. Apply Fault at the NORTHWEST 3 (524106) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from NORTHWEST 3 (524106) 115 kV Bus to BUSH 3 (524124) 115 kV Bus CKT 1 b. 2. Drop Load 1 at BUSH 3 (524124) 115 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | No | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points) |  | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25S | Transfer | Group5_Fault_0183_P1 | 3 phase fault on NORTHWEST 3 (524106) 115 kV Bus a. Apply Fault at the NORTHWEST 3 (524106) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from NORTHWEST 3 (524106) 115 kV Bus to NORTHWEST 2 (524105) 69 kV Bus to NRTHWST_TR11 (524102) 13.2 kV Bus CKT 1 | P1 | Yes | Yes | Yes | No | Yes | Yes | No | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points) |  | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25S | Transfer | Group5_Fault_0184_P1 | 3 phase fault on NICHOLS 3 (524043) 115 kV Bus a. Apply Fault at the NICHOLS 3 (524043) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from NICHOLS 3 (524043) 115 kV Bus to YARNELL_TP 3 (524072) 115 kV Bus CKT 1 b. 2. Trip branch from YARNELL_TP 3 (524072) 115 kV Bus to CONWAY 3 (524079) 115 kV Bus CKT 1 b. 3. Trip branch from CONWAY 3 (524079) 115 kV Bus to KIRBY 3 (524088) 115 kV Bus CKT 1 b. 4. Drop Load 1 at CONWAY 3 (524079) 115 kV Bus b. 5. Drop Load D1 at CONWAY 3 (524079) 115 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | No | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points) |  | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25S | Transfer | Group5_Fault_0185_P1 | 3 phase fault on ROLLHILLS 3 (524007) 115 kV Bus a. Apply Fault at the ROLLHILLS 3 (524007) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from ROLLHILLS 3 (524007) 115 kV Bus to CHERRY 3 (524009) 115 kV Bus CKT 1 b. 2. Drop Load 1 at CHERRY 3 (524009) 115 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | No | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points) |  | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25S | Transfer | Group5_Fault_0186_P1 | 3 phase fault on PRINGLE 3 (523266) 115 kV Bus a. Apply Fault at the PRINGLE 3 (523266) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from PRINGLE 3 (523266) 115 kV Bus to Q_RYTON_TP 3 (523478) 115 kV Bus CKT 1 b. 2. Trip branch from Q_RYTON_TP 3 (523478) 115 kV Bus to BLKHAWK_E 3 (523346) 115 kV Bus CKT 1 b. 3. Drop Load 1 at Q_RYTON_TP 3 (523478) 115 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | No | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points) |  | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25S | Transfer | Group5_Fault_0187_P1 | 3 phase fault on KIRBY 3 (524088) 115 kV Bus a. Apply Fault at the KIRBY 3 (524088) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from KIRBY 3 (524088) 115 kV Bus to MCCLELLAN 3 (523804) 115 kV Bus CKT 1 b. 2. Trip branch from MCCLELLAN 3 (523804) 115 kV Bus to MCLEAN 3 (523811) 115 kV Bus CKT 1 b. 3. Trip branch from MCLEAN 3 (523811) 115 kV Bus to SHAM 3WT (512107) 115 kV Bus CKT 1 b. 4. Trip three winding transformer from SHAM 3WT (512107) 115 kV Bus to SHAM 2WT (512106) 69 kV Bus to SR1TERT (512109) 14.4 kV Bus CKT 1 b. 5. Drop Load 1 at MCCLELLAN 3 (523804) 115 kV Bus b. 6. Drop Load 1 at MCLEAN 3 (523811) 115 kV Bus b. 7. Drop Load D1 at MCLEAN 3 (523811) 115 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25S | Transfer | Group5_Fault_0188_P1 | 3 phase fault on CAMX/AGR TP3 (523485) 115 kV Bus a. Apply Fault at the CAMX/AGR TP3 (523485) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from CAMX/AGR TP3 (523485) 115 kV Bus to W_BORGER_TP3 (523516) 115 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | No | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points) |  | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25S | Transfer | Group5_Fault_0189_P1 | 3 phase fault on BLKHAWK_E 3 (523346) 115 kV Bus a. Apply Fault at the BLKHAWK_E 3 (523346) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from BLKHAWK_E 3 (523346) 115 kV Bus to BLKHAWK_W 3 (523344) 115 kV Bus CKT "@1" c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | No | Yes | No | Yes | Yes | No | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points) |  | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25S | Transfer | Group5_Fault_0190_P1 | 3 phase fault on BLKHAWK_E 3 (523346) 115 kV Bus a. Apply Fault at the BLKHAWK_E 3 (523346) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from BLKHAWK_E 3 (523346) 115 kV Bus to CPCOKER 3 (523470) 115 kV Bus CKT 1 b. 2. Trip branch from CPCOKER 3 (523470) 115 kV Bus to BLKHAWK_W 3 (523344) 115 kV Bus CKT 1 b. 3. Drop Load 1 at CPCOKER 3 (523470) 115 kV Bus b. 4. Drop Load 1 at CPCOKER 3 (523470) 115 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | No | Yes | No | Yes | Yes | No | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points) |  | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25S | Transfer | Group5_Fault_0191_P1 | 3 phase fault on O.K.U.-7 (511456) 345 kV Bus a. Apply Fault at the O.K.U.-7 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from O.K.U.-7 (511456) 345 kV Bus to OKLAUN HVDC7 (511565) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0192_P1 | 3 phase fault on TUCO_INT 7 (525832) 345 kV Bus a. Apply Fault at the TUCO_INT 7 (525832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from TUCO_INT 7 (525832) 345 kV Bus to YOAKUM_345 (526936) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | No | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points) |  | Generator relays were disabled for the following generators: 763090 [G18-073-GEN10.6600], 763084 [G18-073-GEN20.6600]
05 - Southwest | 25S | Transfer | Group5_Fault_0193_P1 | 3 phase fault on YOAKUM_345 (526936) 345 kV Bus a. Apply Fault at the YOAKUM_345 (526936) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from YOAKUM_345 (526936) 345 kV Bus to HOBBS_INT 7 (527896) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Low voltage ride through fails due to the tripping of G18-115-GEN10 unit. No cascading was observed and the issue was localised. Model tuning is recommended. |  |  | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000], 523941 [MAJSTC-WTG110.6900], 523942 [MAJSTC-WTG210.6900], 523942 [MAJSTC-WTG210.6900], 761358 [G17-239-GEN10.6900], 761361 [G17-239-GEN20.6900], 761799 [G17-187GEN1 0.6900], 761802 [G17-187GEN2 0.6900], 763084 [G18-073-GEN20.6600], 763090 [G18-073-GEN10.6600], 527883 [CUNINGHAM3 113.800], 525783 [LRNZ2.3_GEN10.6900], 584564 [G15-014-GE200.6900]
05 - Southwest | 25S | Transfer | Group5_Fault_0194_P1 | 3 phase fault on YOAKUM_345 (526936) 345 kV Bus a. Apply Fault at the YOAKUM_345 (526936) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from YOAKUM_345 (526936) 345 kV Bus to HOBBS_INT 7 (527896) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | No | Yes | No | Yes | No | No | Damping issues observed. Low voltage ride through fails due to the tripping of G18-115-GEN10 unit. No cascading was observed and the issue was localised. Model tuning is recommended. | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000], 523941 [MAJSTC-WTG110.6900], 523942 [MAJSTC-WTG210.6900], 523942 [MAJSTC-WTG210.6900], 761358 [G17-239-GEN10.6900], 761361 [G17-239-GEN20.6900], 761799 [G17-187GEN1 0.6900], 761802 [G17-187GEN2 0.6900], 763084 [G18-073-GEN20.6600], 763090 [G18-073-GEN10.6600], 527883 [CUNINGHAM3 113.800], 525783 [LRNZ2.3_GEN10.6900], 584564 [G15-014-GE200.6900]
05 - Southwest | 25S | Transfer | Group5_Fault_0195_P1 | 3 phase fault on YOAKUM_345 (526936) 345 kV Bus a. Apply Fault at the YOAKUM_345 (526936) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from YOAKUM_345 (526936) 345 kV Bus to YOAKUM 6 (526935) 230 kV Bus to YOAKUM_TR1 (526937) 13.2 kV Bus CKT 1 | P1 | Yes | Yes | Yes | No | Yes | Yes | No | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points) |  | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000], 523941 [MAJSTC-WTG110.6900], 523942 [MAJSTC-WTG210.6900], 523942 [MAJSTC-WTG210.6900], 761358 [G17-239-GEN10.6900], 761361 [G17-239-GEN20.6900], 761799 [G17-187GEN1 0.6900], 761802 [G17-187GEN2 0.6900], 763084 [G18-073-GEN20.6600], 763090 [G18-073-GEN10.6600], 584223 [G14-040-GEN10.6900], 763309 [G18-112-GEN10.6600], 584226 [G14-040-GEN20.6900], 527883 [CUNINGHAM3 113.800]
05 - Southwest | 25S | Transfer | Group5_Fault_0196_P1 | 3 phase fault on TUCO_INT 7 (525832) 345 kV Bus a. Apply Fault at the TUCO_INT 7 (525832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from TUCO_INT 7 (525832) 345 kV Bus to CRAWFISH_DR (560022) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | No | No | Damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 763090 [G18-073-GEN10.6600], 763084 [G18-073-GEN20.6600]
05 - Southwest | 25S | Transfer | Group5_Fault_0197_P1 | 3 phase fault on CRAWFISH_DR (560022) 345 kV Bus a. Apply Fault at the CRAWFISH_DR (560022) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from CRAWFISH_DR (560022) 345 kV Bus to TUCO_INT 7 (525832) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | No | No | Damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 763090 [G18-073-GEN10.6600], 763084 [G18-073-GEN20.6600]
05 - Southwest | 25S | Transfer | Group5_Fault_0198_P1 | 3 phase fault on G17-151TAP (762216) 345 kV Bus a. Apply Fault at the G17-151TAP (762216) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from G17-151TAP (762216) 345 kV Bus to CRAWFISH_DR (560022) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | No | No | Yes | No | Yes | Damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer
05 - Southwest | 25S | Transfer | Group5_Fault_0199_P1 | 3 phase fault on CROSSROADS 7 (527656) 345 kV Bus a. Apply Fault at the CROSSROADS 7 (527656) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from CROSSROADS 7 (527656) 345 kV Bus to EDDY_CNTY 7 (527802) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | No | No | Damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000], 523941 [MAJSTC-WTG110.6900], 523942 [MAJSTC-WTG210.6900], 523942 [MAJSTC-WTG210.6900], 761358 [G17-239-GEN10.6900], 761361 [G17-239-GEN20.6900], 761799 [G17-187GEN1 0.6900], 761802 [G17-187GEN2 0.6900], 763084 [G18-073-GEN20.6600], 763090 [G18-073-GEN10.6600], 523936 [PANTEX_WIND10.6900], 524287 [GS-PHWD_GEN10.6900]
05 - Southwest | 25S | Transfer | Group5_Fault_0200_P1 | 3 phase fault on HOBBS_INT 7 (527896) 345 kV Bus a. Apply Fault at the HOBBS_INT 7 (527896) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from HOBBS_INT 7 (527896) 345 kV Bus to HOBBS_INT 6 (527894) 230 kV Bus to HOBBS_TR3 1 (527895) 13.2 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | No | No | Low voltage ride through fails due to the tripping of G18-115-GEN10 and G18-115-GEN20 units. No cascading was observed and the issue was localised. Model tuning is recommended. | Potter to Tolk 345 kV Double Circuit Line Build Potter to Chisholm 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer Potter to Tolk 345 kV | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000], 523941 [MAJSTC-WTG110.6900], 523942 [MAJSTC-WTG210.6900], 523942 [MAJSTC-WTG210.6900], 761358 [G17-239-GEN10.6900], 761361 [G17-239-GEN20.6900], 761799 [G17-187GEN1 0.6900], 761802 [G17-187GEN2 0.6900], 763084 [G18-073-GEN20.6600], 763090 [G18-073-GEN10.6600], 523936 [PANTEX_WIND10.6900], 524287 [GS-PHWD_GEN10.6900], 763397 [G18-124-GEN1], 763309 [G18-112-GEN1]
05 - Southwest | 25S | Transfer | Group5_Fault_0201_P1 | 3 phase fault on YOAKUM 6 (526935) 230 kV Bus a. Apply Fault at the YOAKUM 6 (526935) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from YOAKUM 6 (526935) 230 kV Bus to YOAKUM 3 (526934) 115 kV Bus to YOAKUM_TR2 1 (526932) 13.2 kV Bus CKT 2 | P1 | No | No | No | No | Yes | No | No | Out Of Step Generators and damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000], 761358 [G17-239-GEN10.6900], 761361 [G17-239-GEN20.6900], 761799 [G17-187GEN1 0.6900], 761802 [G17-187GEN2 0.6900], 763084 [G18-073-GEN20.6600], 763090 [G18-073-GEN10.6600]
05 - Southwest | 25S | Transfer | Group5_Fault_0202_P1 | 3 phase fault on YOAKUM 6 (526935) 230 kV Bus a. Apply Fault at the YOAKUM 6 (526935) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from YOAKUM 6 (526935) 230 kV Bus to YOAKUM 3 (526934) 115 kV Bus to YOAKUM_TR1 1 (526931) 13.2 kV Bus CKT 1 | P1 | No | No | No | No | Yes | No | No | Out Of Step Generators and damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000], 761358 [G17-239-GEN10.6900], 761361 [G17-239-GEN20.6900], 761799 [G17-187GEN1 0.6900], 761802 [G17-187GEN2 0.6900], 763084 [G18-073-GEN20.6600], 763090 [G18-073-GEN10.6600], 527884 [CUNINGHAM4 113.800], 527883 [CUNINGHAM3 113.800], 528361 [MADDOX_1 113.800]
05 - Southwest | 25S | Transfer | Group5_Fault_0203_P1 | 3 phase fault on YOAKUM 6 (526935) 230 kV Bus a. Apply Fault at the YOAKUM 6 (526935) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from YOAKUM 6 (526935) 230 kV Bus to AMOCO_SS 6 (526460) 230 kV Bus CKT 1 b. 2. Trip branch from AMOCO_SS 6 (526460) 230 kV Bus to SUNDOWN 6 (526435) 230 kV Bus CKT 1 b. 3. Drop Load 1 at AMOCO_SS 6 (526460) 230 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | No | No | No | No | Yes | No | No | Out Of Step Generators and damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000], 761358 [G17-239-GEN10.6900], 761361 [G17-239-GEN20.6900], 761799 [G17-187GEN1 0.6900], 761802 [G17-187GEN2 0.6900], 763084 [G18-073-GEN20.6600], 763090 [G18-073-GEN10.6600], 527884 [CUNINGHAM4 113.800], 584564 [G15-014-GE200.6900]
05 - Southwest | 25S | Transfer | Group5_Fault_0204_P1 | 3 phase fault on YOAKUM 6 (526935) 230 kV Bus a. Apply Fault at the YOAKUM 6 (526935) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from YOAKUM 6 (526935) 230 kV Bus to INK_BASIN 6 (527028) 230 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | No | No | No | No | No | No | No | Out Of Step Generators and damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000], 761358 [G17-239-GEN10.6900], 761361 [G17-239-GEN20.6900], 761799 [G17-187GEN1 0.6900], 761802 [G17-187GEN2 0.6900], 763084 [G18-073-GEN20.6600], 763090 [G18-073-GEN10.6600], 527883 [CUNINGHAM3 113.800], 584223 [G14-040-GEN10.6900], 763397 [G18-124-GEN10.6600], 527884 [CUNINGHAM4 113.800]
05 - Southwest | 25S | Transfer | Group5_Fault_0205_P1 | 3 phase fault on YOAKUM 6 (526935) 230 kV Bus a. Apply Fault at the YOAKUM 6 (526935) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from YOAKUM 6 (526935) 230 kV Bus to BRU_SUB 6 (527009) 230 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | No | No | No | No | No | No | No | Out Of Step Generators and damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000], 761358 [G17-239-GEN10.6900], 761361 [G17-239-GEN20.6900], 761799 [G17-187GEN1 0.6900], 761802 [G17-187GEN2 0.6900], 763084 [G18-073-GEN20.6600], 763090 [G18-073-GEN10.6600], 584226 [G14-040-GEN20.6900]
05 - Southwest | 25S | Transfer | Group5_Fault_0206_P1 | 3 phase fault on YOAKUM 6 (526935) 230 kV Bus a. Apply Fault at the YOAKUM 6 (526935) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from YOAKUM 6 (526935) 230 kV Bus to MUSTANG 6 (527149) 230 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | No | No | No | Yes | Yes | No | No | Out Of Step Generators and damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000], 761358 [G17-239-GEN10.6900], 761361 [G17-239-GEN20.6900], 761799 [G17-187GEN1 0.6900], 761802 [G17-187GEN2 0.6900], 763084 [G18-073-GEN20.6600], 763090 [G18-073-GEN10.6600], 525783 [LRNZ2.3_GEN10.6900], 584563 [G15-014-GE170.6900]
05 - Southwest | 25S | Transfer | Group5_Fault_0207_P1 | 3 phase fault on TOLK 7 (525549) 345 kV Bus a. Apply Fault at the TOLK 7 (525549) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from TOLK 7 (525549) 345 kV Bus to POTTER_CO 7 (523961) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | Group5_Fault_0208_P1 | 3 phase fault on EDDY_CNTY 7 (527802) 345 kV Bus a. Apply Fault at the EDDY_CNTY 7 (527802) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from EDDY_CNTY 7 (527802) 345 kV Bus to KIOWA 7 (527965) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | No | No | No | No | Yes | No | No | Out Of Step Generators and damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000], 523941 [MAJSTC-WTG110.6900], 523942 [MAJSTC-WTG210.6900], 523942 [MAJSTC-WTG210.6900], 761358 [G17-239-GEN10.6900], 761361 [G17-239-GEN20.6900], 761799 [G17-187GEN1 0.6900], 761802 [G17-187GEN2 0.6900], 763084 [G18-073-GEN20.6600], 763090 [G18-073-GEN10.6600], 584563 [G15-014-GE170.6900], 584564 [G15-014-GE200.6900], 584565 [G15-014-GE230.6900]
05 - Southwest | 25S | Transfer | Group5_Fault_0209_P1 | 3 phase fault on EDDY_CNTY 7 (527802) 345 kV Bus a. Apply Fault at the EDDY_CNTY 7 (527802) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from EDDY_CNTY 7 (527802) 345 kV Bus to CROSSROADS 7 (527656) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | No | No | No | No | Yes | No | No | Out Of Step Generators and damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000], 523941 [MAJSTC-WTG110.6900], 523942 [MAJSTC-WTG210.6900], 523942 [MAJSTC-WTG210.6900], 761358 [G17-239-GEN10.6900], 761361 [G17-239-GEN20.6900], 761799 [G17-187GEN1 0.6900], 761802 [G17-187GEN2 0.6900], 763084 [G18-073-GEN20.6600], 763090 [G18-073-GEN10.6600], 584564 [G15-014-GE200.6900], 584565 [G15-014-GE230.6900], 527883 [CUNINGHAM3 113.800]
05 - Southwest | 25S | Transfer | Group5_Fault_0210_P1 | 3 phase fault on KIOWA 7 (527965) 345 kV Bus a. Apply Fault at the KIOWA 7 (527965) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from KIOWA 7 (527965) 345 kV Bus to N_LOVING 7 (528185) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | No | No | No | No | Yes | No | No | Out Of Step Generators and damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000], 523941 [MAJSTC-WTG110.6900], 523942 [MAJSTC-WTG210.6900], 523942 [MAJSTC-WTG210.6900], 761358 [G17-239-GEN10.6900], 761361 [G17-239-GEN20.6900], 761799 [G17-187GEN1 0.6900], 761802 [G17-187GEN2 0.6900], 763084 [G18-073-GEN20.6600], 763090 [G18-073-GEN10.6600], 584564 [G15-014-GE200.6900], 584565 [G15-014-GE230.6900], 527884 [CUNINGHAM4 113.800]
05 - Southwest | 25S | Transfer | Group5_Fault_0211_P1 | 3 phase fault on KIOWA 7 (527965) 345 kV Bus a. Apply Fault at the KIOWA 7 (527965) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from KIOWA 7 (527965) 345 kV Bus to RDRUNNER 7 (528027) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | No | No | No | No | No | No | No | Out Of Step Generators and damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000], 523941 [MAJSTC-WTG110.6900], 523942 [MAJSTC-WTG210.6900], 523942 [MAJSTC-WTG210.6900], 761358 [G17-239-GEN10.6900], 761361 [G17-239-GEN20.6900], 761799 [G17-187GEN1 0.6900], 761802 [G17-187GEN2 0.6900], 763084 [G18-073-GEN20.6600], 763090 [G18-073-GEN10.6600], 584564 [G15-014-GE200.6900], 584565 [G15-014-GE230.6900], 527884 [CUNINGHAM4 113.800]
05 - Southwest | 25S | Transfer | Group5_Fault_0212_P1 | 3 phase fault on KIOWA 7 (527965) 345 kV Bus a. Apply Fault at the KIOWA 7 (527965) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from KIOWA 7 (527965) 345 kV Bus to KIOWA 3 (527966) 115 kV Bus to KIOWA_TR1 1 (527964) 13.2 kV Bus CKT 1 b. 2. Trip branch from KIOWA 3 (527966) 115 kV Bus to POTASH_JCT 3 (527962) 115 kV Bus CKT 1 | P1 | Yes | Yes | Yes | No | Yes | No | No | Damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000], 523941 [MAJSTC-WTG110.6900], 523942 [MAJSTC-WTG210.6900], 523942 [MAJSTC-WTG210.6900], 761358 [G17-239-GEN10.6900], 761361 [G17-239-GEN20.6900], 761799 [G17-187GEN1 0.6900], 761802 [G17-187GEN2 0.6900], 763084 [G18-073-GEN20.6600], 763090 [G18-073-GEN10.6600], 525783 [LRNZ2.3_GEN10.6900], 763397 [G18-124-GEN10.6600], 524023 [NICHOLS_3 122.000]
05 - Southwest | 25S | Transfer | Group5_Fault_0213_P1 | 3 phase fault on HOBBS_INT 6 (527894) 230 kV Bus a. Apply Fault at the HOBBS_INT 6 (527894) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from HOBBS_INT 6 (527894) 230 kV Bus to ANDREWS 6 (528604) 230 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000], 523941 [MAJSTC-WTG110.6900], 523942 [MAJSTC-WTG210.6900], 523942 [MAJSTC-WTG210.6900], 761358 [G17-239-GEN10.6900], 761361 [G17-239-GEN20.6900], 761799 [G17-187GEN1 0.6900], 761802 [G17-187GEN2 0.6900], 763084 [G18-073-GEN20.6600], 763090 [G18-073-GEN10.6600], 584565 [G15-014-GE230.6900], 584226 [G14-040-GEN20.6900], 584223 [G14-040-GEN10.6900]
05 - Southwest | 25S | Transfer | Group5_Fault_0214_P1 | 3 phase fault on HOBBS_INT 6 (527894) 230 kV Bus a. Apply Fault at the HOBBS_INT 6 (527894) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from HOBBS_INT 6 (527894) 230 kV Bus to INK_BASIN 6 (527028) 230 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | No | No | No | No | Yes | No | No | Out Of Step Generators and damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000], 761358 [G17-239-GEN10.6900], 761361 [G17-239-GEN20.6900], 761799 [G17-187GEN1 0.6900], 761802 [G17-187GEN2 0.6900], 763084 [G18-073-GEN20.6600], 763090 [G18-073-GEN10.6600], 584564 [G15-014-GE200.6900], 584226 [G14-040-GEN20.6900], 584223 [G14-040-GEN10.6900]
05 - Southwest | 25S | Transfer | Group5_Fault_0215_P1 | 3 phase fault on HOBBS_INT 6 (527894) 230 kV Bus a. Apply Fault at the HOBBS_INT 6 (527894) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from HOBBS_INT 6 (527894) 230 kV Bus to CUNNIGHM_S 6 (527867) 230 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000], 761358 [G17-239-GEN10.6900], 761361 [G17-239-GEN20.6900], 761799 [G17-187GEN1 0.6900], 761802 [G17-187GEN2 0.6900], 763084 [G18-073-GEN20.6600], 763090 [G18-073-GEN10.6600], 584564 [G15-014-GE200.6900], 527883 [CUNINGHAM3 113.800], 584226 [G14-040-GEN20.6900]
05 - Southwest | 25S | Transfer | Group5_Fault_0216_P1 | 3 phase fault on HOBBS_INT 6 (527894) 230 kV Bus a. Apply Fault at the HOBBS_INT 6 (527894) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from HOBBS_INT 6 (527894) 230 kV Bus to HOBBS_INT 3 (527891) 115 kV Bus to HOBBS_TR2 1 (527889) 13.2 kV Bus CKT 2 | P1 | No | No | No | No | Yes | No | No | Out Of Step Generators and damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000], 761358 [G17-239-GEN10.6900], 761361 [G17-239-GEN20.6900], 761799 [G17-187GEN1 0.6900], 761802 [G17-187GEN2 0.6900], 763084 [G18-073-GEN20.6600], 763090 [G18-073-GEN10.6600]
05 - Southwest | 25S | Transfer | Group5_Fault_0217_P1 | 3 phase fault on HOBBS_INT 6 (527894) 230 kV Bus a. Apply Fault at the HOBBS_INT 6 (527894) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from HOBBS_INT 6 (527894) 230 kV Bus to HOBBS_INT 3 (527891) 115 kV Bus to HOBBS_TR1 1 (527890) 13.2 kV Bus CKT 1 | P1 | Yes | Yes | Yes | No | Yes | Yes | No | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points) |  | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000], 761358 [G17-239-GEN10.6900], 761361 [G17-239-GEN20.6900], 761799 [G17-187GEN1 0.6900], 761802 [G17-187GEN2 0.6900], 763084 [G18-073-GEN20.6600], 763090 [G18-073-GEN10.6600]
05 - Southwest | 25S | Transfer | Group5_Fault_0218_P1 | 3 phase fault on BRU_SUB 6 (527009) 230 kV Bus a. Apply Fault at the BRU_SUB 6 (527009) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from BRU_SUB 6 (527009) 230 kV Bus to XTO_MAHONEY6 (527011) 230 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | No | Yes | Damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer
05 - Southwest | 25S | Transfer | Group5_Fault_0219_P1 | 3 phase fault on BRU_SUB 6 (527009) 230 kV Bus a. Apply Fault at the BRU_SUB 6 (527009) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from BRU_SUB 6 (527009) 230 kV Bus to OXYBRU 6 (527010) 230 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | No | Yes | Damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer
05 - Southwest | 25S | Transfer | Group5_Fault_0220_P1 | 3 phase fault on YOAKUM 3 (526934) 115 kV Bus a. Apply Fault at the YOAKUM 3 (526934) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from YOAKUM 3 (526934) 115 kV Bus to PLAINS_INT 3 (526928) 115 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | No | Yes | Damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer
05 - Southwest | 25S | Transfer | Group5_Fault_0221_P1 | 3 phase fault on YOAKUM 3 (526934) 115 kV Bus a. Apply Fault at the YOAKUM 3 (526934) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from YOAKUM 3 (526934) 115 kV Bus to ARCO_TP 3 (527041) 115 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | No | Yes | Damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer
05 - Southwest | 25S | Transfer | Group5_Fault_0222_P1 | 3 phase fault on G18-015-TAP (762467) 345 kV Bus a. Apply Fault at the G18-015-TAP (762467) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from G18-015-TAP (762467) 345 kV Bus to G18-092-TAP (763215) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | No | No | No | No | Yes | No | No | Out Of Step Generators and damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000], 523941 [MAJSTC-WTG110.6900], 523942 [MAJSTC-WTG210.6900], 523942 [MAJSTC-WTG210.6900], 761358 [G17-239-GEN10.6900], 761361 [G17-239-GEN20.6900], 761799 [G17-187GEN1 0.6900], 761802 [G17-187GEN2 0.6900], 763084 [G18-073-GEN20.6600], 763090 [G18-073-GEN10.6600]
05 - Southwest | 25S | Transfer | Group5_Fault_0223_P1 | 3 phase fault on G18-015-TAP (762467) 345 kV Bus a. Apply Fault at the G18-015-TAP (762467) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from G18-015-TAP (762467) 345 kV Bus to G17-151TAP (762216) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | No | No | No | No | Yes | No | No | Out Of Step Generators and damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000], 763397 [G18-124-GEN10.6600], 763309 [G18-112-GEN10.6600]
05 - Southwest | 25S | Transfer | Group5_Fault_0224_P1 | 3 phase fault on CARLISLE 6 (526161) 230 kV Bus a. Apply Fault at the CARLISLE 6 (526161) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from CARLISLE 6 (526161) 230 kV Bus to CARLISLE 3 (526160) 115 kV Bus to CRLSLE_TR1 1 (526157) 13.2 kV Bus CKT 1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0225_P1 | 3 phase fault on TUCO_INT 3 (525828) 115 kV Bus a. Apply Fault at the TUCO_INT 3 (525828) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from TUCO_INT 3 (525828) 115 kV Bus to STANTON_W 3 (526076) 115 kV Bus CKT 1 b. 2. Trip branch from STANTON_W 3 (526076) 115 kV Bus to INDIANA 3 (526146) 115 kV Bus CKT 1 b. 3. Trip branch from INDIANA 3 (526146) 115 kV Bus to SP-ERSKINE 3 (526109) 115 kV Bus CKT 1 b. 4. Trip branch from SP-ERSKINE 3 (526109) 115 kV Bus to CARLISLE 3 (526160) 115 kV Bus CKT 1 b. 5. Drop Load 1 at STANTON_W 3 (526076) 115 kV Bus b. 6. Drop Load 1 at INDIANA 3 (526146) 115 kV Bus b. 7. Drop Load 2 at INDIANA 3 (526146) 115 kV Bus b. 8. Drop Load 1 at SP-ERSKINE 3 (526109) 115 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0226_P1 | 3 phase fault on TUCO_INT 3 (525828) 115 kV Bus a. Apply Fault at the TUCO_INT 3 (525828) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from TUCO_INT 3 (525828) 115 kV Bus to FLOYD_CNTY 3 (525780) 115 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0227_P1 | 3 phase fault on TUCO_INT 3 (525828) 115 kV Bus a. Apply Fault at the TUCO_INT 3 (525828) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from TUCO_INT 3 (525828) 115 kV Bus to TUCO_INT 2 (525826) 69 kV Bus to TUCO_TR5 1 (525822) 13.2 kV Bus CKT 2 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0228_P1 | 3 phase fault on TUCO_INT 3 (525828) 115 kV Bus a. Apply Fault at the TUCO_INT 3 (525828) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from TUCO_INT 3 (525828) 115 kV Bus to TUCO_INT 2 (525826) 69 kV Bus to TUCO_TR6 1 (525823) 13.2 kV Bus CKT 1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0229_P1 | 3 phase fault on TUCO_INT 3 (525828) 115 kV Bus a. Apply Fault at the TUCO_INT 3 (525828) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from TUCO_INT 3 (525828) 115 kV Bus to TUCO_INT2 2 (525816) 69 kV Bus to TUCO_TR7 1 (525814) 13.2 kV Bus CKT 1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0230_P1 | 3 phase fault on EDDY_NORTH 6 (527799) 230 kV Bus a. Apply Fault at the EDDY_NORTH 6 (527799) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from EDDY_NORTH 6 (527799) 230 kV Bus to CUNNIGHM_N 6 (527865) 230 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | No | No | Damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000], 523941 [MAJSTC-WTG110.6900], 523942 [MAJSTC-WTG210.6900], 523942 [MAJSTC-WTG210.6900], 761358 [G17-239-GEN10.6900], 761361 [G17-239-GEN20.6900], 761799 [G17-187GEN1 0.6900], 761802 [G17-187GEN2 0.6900], 763084 [G18-073-GEN20.6600], 763090 [G18-073-GEN10.6600], 584564 [G15-014-GE200.6900], 584565 [G15-014-GE230.6900], 524023 [NICHOLS_3 122.000]
05 - Southwest | 25S | Transfer | Group5_Fault_0231_P1 | 3 phase fault on EDDY_NORTH 6 (527799) 230 kV Bus a. Apply Fault at the EDDY_NORTH 6 (527799) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from EDDY_NORTH 6 (527799) 230 kV Bus to EDDY_STH 3 (527793) 115 kV Bus to EDDY_TR3 1 (527795) 13.2 kV Bus CKT 2 | P1 | Yes | Yes | Yes | No | Yes | No | No | Damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000], 523941 [MAJSTC-WTG110.6900], 523942 [MAJSTC-WTG210.6900], 523942 [MAJSTC-WTG210.6900], 584564 [G15-014-GE200.6900], 527884 [CUNINGHAM4 113.800], 527883 [CUNINGHAM3 113.800], 584563 [G15-014-GE170.6900]
05 - Southwest | 25S | Transfer | Group5_Fault_0232_P1 | 3 phase fault on EDDY_NORTH 6 (527799) 230 kV Bus a. Apply Fault at the EDDY_NORTH 6 (527799) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from EDDY_NORTH 6 (527799) 230 kV Bus to EDDY_NTH 3 (527798) 115 kV Bus to EDDY_TR2 1 (527797) 13.2 kV Bus CKT 1 | P1 | Yes | Yes | Yes | No | Yes | No | No | Damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000], 523941 [MAJSTC-WTG110.6900], 523942 [MAJSTC-WTG210.6900], 523942 [MAJSTC-WTG210.6900], 525783 [LRNZ2.3_GEN10.6900], 763309 [G18-112-GEN10.6600]
05 - Southwest | 25S | Transfer | Group5_Fault_0233_P1 | 3 phase fault on RDRUNNER 7 (528027) 345 kV Bus a. Apply Fault at the RDRUNNER 7 (528027) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from RDRUNNER 7 (528027) 345 kV Bus to RDRUNNER 3 (528025) 115 kV Bus to RDRNNER_TR11 (528023) 13.2 kV Bus CKT 1 | P1 | Yes | Yes | Yes | No | Yes | No | No | Damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000], 523941 [MAJSTC-WTG110.6900], 523942 [MAJSTC-WTG210.6900], 523942 [MAJSTC-WTG210.6900], 761358 [G17-239-GEN10.6900], 761361 [G17-239-GEN20.6900], 761799 [G17-187GEN1 0.6900], 761802 [G17-187GEN2 0.6900], 763084 [G18-073-GEN20.6600], 763090 [G18-073-GEN10.6600], 527884 [CUNINGHAM4 113.800], 763309 [G18-112-GEN10.6600], 527883 [CUNINGHAM3 113.800], 523812 [LANOGSU10.600.6000], 525783 [LRNZ2.3_GEN10.6900]
05 - Southwest | 25S | Transfer | Group5_Fault_0234_P1 | 3 phase fault on RDRUNNER 7 (528027) 345 kV Bus a. Apply Fault at the RDRUNNER 7 (528027) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from RDRUNNER 7 (528027) 345 kV Bus to PHANTOM 7 (528015) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | No | No | Yes | No | No | No | No | Out Of Step Generators and damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000], 523941 [MAJSTC-WTG110.6900], 523942 [MAJSTC-WTG210.6900], 523942 [MAJSTC-WTG210.6900], 761358 [G17-239-GEN10.6900], 761361 [G17-239-GEN20.6900], 761799 [G17-187GEN1 0.6900], 761802 [G17-187GEN2 0.6900], 763084 [G18-073-GEN20.6600], 763090 [G18-073-GEN10.6600], 584564 [G15-014-GE200.6900], 584565 [G15-014-GE230.6900], 527884 [CUNINGHAM4 113.800]
05 - Southwest | 25S | Transfer | Group5_Fault_0235_P1 | 3 phase fault on N_LOVING 7 (528185) 345 kV Bus a. Apply Fault at the N_LOVING 7 (528185) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from N_LOVING 7 (528185) 345 kV Bus to NORTH_LOVNG3 (528182) 115 kV Bus to N_LOVING TR1 (528186) 13.2 kV Bus CKT 1 | P1 | Yes | Yes | Yes | No | Yes | No | No | Damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000], 523941 [MAJSTC-WTG110.6900], 523942 [MAJSTC-WTG210.6900], 523942 [MAJSTC-WTG210.6900], 761358 [G17-239-GEN10.6900], 761361 [G17-239-GEN20.6900], 761799 [G17-187GEN1 0.6900], 761802 [G17-187GEN2 0.6900], 763084 [G18-073-GEN20.6600], 763090 [G18-073-GEN10.6600], 525783 [LRNZ2.3_GEN10.6900], 527884 [CUNINGHAM4 113.800], 527883 [CUNINGHAM3 113.800]
05 - Southwest | 25S | Transfer | Group5_Fault_0236_P1 | 3 phase fault on N_LOVING 7 (528185) 345 kV Bus a. Apply Fault at the N_LOVING 7 (528185) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from N_LOVING 7 (528185) 345 kV Bus to CHINA_DRAW 7 (528223) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | No | No | No | No | Yes | No | No | Out Of Step Generators and damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000], 523941 [MAJSTC-WTG110.6900], 523942 [MAJSTC-WTG210.6900], 523942 [MAJSTC-WTG210.6900], 761358 [G17-239-GEN10.6900], 761361 [G17-239-GEN20.6900], 761799 [G17-187GEN1 0.6900], 761802 [G17-187GEN2 0.6900], 763084 [G18-073-GEN20.6600], 763090 [G18-073-GEN10.6600], 584564 [G15-014-GE200.6900], 527883 [CUNINGHAM3 113.800], 527884 [CUNINGHAM4 113.800]
05 - Southwest | 25S | Transfer | Group5_Fault_0237_P1 | 3 phase fault on POTASH_JCT 3 (527962) 115 kV Bus a. Apply Fault at the POTASH_JCT 3 (527962) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from POTASH_JCT 3 (527962) 115 kV Bus to INTREPDW_TP3 (527999) 115 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | No | No | Damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000], 523941 [MAJSTC-WTG110.6900], 523942 [MAJSTC-WTG210.6900], 523942 [MAJSTC-WTG210.6900], 761358 [G17-239-GEN10.6900], 761361 [G17-239-GEN20.6900], 761799 [G17-187GEN1 0.6900], 761802 [G17-187GEN2 0.6900], 763084 [G18-073-GEN20.6600], 763090 [G18-073-GEN10.6600], 584223 [G14-040-GEN10.6900], 584226 [G14-040-GEN20.6900], 584563 [G15-014-GE170.6900]
05 - Southwest | 25S | Transfer | Group5_Fault_0238_P1 | 3 phase fault on POTASH_JCT 6 (527963) 230 kV Bus a. Apply Fault at the POTASH_JCT 6 (527963) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from POTASH_JCT 6 (527963) 230 kV Bus to POTASH_JCT 3 (527962) 115 kV Bus to POTASH_TR1 1 (527958) 13.2 kV Bus CKT 1 | P1 | Yes | Yes | Yes | No | Yes | No | Yes | Damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer
05 - Southwest | 25S | Transfer | Group5_Fault_0239_P1 | 3 phase fault on POTASH_JCT 3 (527962) 115 kV Bus a. Apply Fault at the POTASH_JCT 3 (527962) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from POTASH_JCT 3 (527962) 115 kV Bus to POTASH_JCT 2 (527961) 69 kV Bus to POTASH_TR2 1 (527959) 13.2 kV Bus CKT 1 | P1 | Yes | Yes | Yes | No | Yes | No | No | Damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25S | Transfer | Group5_Fault_0240_P1 | 3 phase fault on POTASH_JCT 3 (527962) 115 kV Bus a. Apply Fault at the POTASH_JCT 3 (527962) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from POTASH_JCT 3 (527962) 115 kV Bus to POTASH_JCT 2 (527961) 69 kV Bus to POTASH_TR3 1 (527960) 13.2 kV Bus CKT 2 | P1 | Yes | Yes | Yes | No | Yes | No | No | Damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25S | Transfer | Group5_Fault_0241_P1 | 3 phase fault on ANDREWS 6 (528604) 230 kV Bus a. Apply Fault at the ANDREWS 6 (528604) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from ANDREWS 6 (528604) 230 kV Bus to ANDREWS 3 (528602) 115 kV Bus to ANDREWS_TR21 (528600) 13.2 kV Bus CKT 2 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0242_P1 | 3 phase fault on ANDREWS 6 (528604) 230 kV Bus a. Apply Fault at the ANDREWS 6 (528604) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from ANDREWS 6 (528604) 230 kV Bus to ANDREWS 3 (528602) 115 kV Bus to ANDREWS_TR11 (528601) 13.2 kV Bus CKT 1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0243_P1 | 3 phase fault on POTASH_JCT 6 (527963) 230 kV Bus a. Apply Fault at the POTASH_JCT 6 (527963) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from POTASH_JCT 6 (527963) 230 kV Bus to PECOS 6 (528179) 230 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | No | Yes | Damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer
05 - Southwest | 25S | Transfer | Group5_Fault_0244_P1 | 3 phase fault on POTASH_JCT 6 (527963) 230 kV Bus a. Apply Fault at the POTASH_JCT 6 (527963) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from POTASH_JCT 6 (527963) 230 kV Bus to CUNNIGHM_N 6 (527865) 230 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | No | Yes | Damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer
05 - Southwest | 25S | Transfer | Group5_Fault_0245_P1 | 3 phase fault on CARLISLE 3 (526160) 115 kV Bus a. Apply Fault at the CARLISLE 3 (526160) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from CARLISLE 3 (526160) 115 kV Bus to LP-DOUD_TP 3 (526162) 115 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0246_P1 | 3 phase fault on HITCHLAND 7 (523097) 345 kV Bus a. Apply Fault at the HITCHLAND 7 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from HITCHLAND 7 (523097) 345 kV Bus to CARPENTER 7 (523823) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | No | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points) |  | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25S | Transfer | Group5_Fault_0247_P1 | 3 phase fault on RDRUNNER 3 (528025) 115 kV Bus a. Apply Fault at the RDRUNNER 3 (528025) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from RDRUNNER 3 (528025) 115 kV Bus to AGAVE_RHILL3 (528230) 115 kV Bus CKT 1 b. 2. Trip branch from AGAVE_RHILL3 (528230) 115 kV Bus to OCHOA 3 (528232) 115 kV Bus CKT 1 b. 3. Drop Load 1 at AGAVE_RHILL3 (528230) 115 kV Bus b. 4. Drop Load 1 at OCHOA 3 (528232) 115 kV Bus b. 5. Drop Load 1* at OCHOA 3 (528232) 115 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | No | No | Damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000], 523941 [MAJSTC-WTG110.6900], 523942 [MAJSTC-WTG210.6900], 523942 [MAJSTC-WTG210.6900], 761358 [G17-239-GEN10.6900], 761361 [G17-239-GEN20.6900], 761799 [G17-187GEN1 0.6900], 761802 [G17-187GEN2 0.6900], 763084 [G18-073-GEN20.6600], 763090 [G18-073-GEN10.6600], 527883 [CUNINGHAM3 113.800], 584223 [G14-040-GEN10.6900], 584226 [G14-040-GEN20.6900]
05 - Southwest | 25S | Transfer | Group5_Fault_0248_P1 | 3 phase fault on RDRUNNER 3 (528025) 115 kV Bus a. Apply Fault at the RDRUNNER 3 (528025) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from RDRUNNER 3 (528025) 115 kV Bus to AGAVE_RHIL23 (528231) 115 kV Bus CKT 1 b. 2. Drop Load 1 at AGAVE_RHIL23 (528231) 115 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | No | No | Damping issues observed. Low voltage ride through fails due to the tripping of G18-115-GEN10 unit. No cascading was observed and the issue was localised. Model tuning is recommended. | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000], 523941 [MAJSTC-WTG110.6900], 523942 [MAJSTC-WTG210.6900], 523942 [MAJSTC-WTG210.6900], 761358 [G17-239-GEN10.6900], 761361 [G17-239-GEN20.6900], 761799 [G17-187GEN1 0.6900], 761802 [G17-187GEN2 0.6900], 763084 [G18-073-GEN20.6600], 763090 [G18-073-GEN10.6600], 584564 [G15-014-GE200.6900], 527883 [CUNINGHAM3 113.800], 584223 [G14-040-GEN10.6900], 584226 [G14-040-GEN20.6900], 584563 [G15-014-GE170.6900]
05 - Southwest | 25S | Transfer | Group5_Fault_0249_P1 | 3 phase fault on RDRUNNER 3 (528025) 115 kV Bus a. Apply Fault at the RDRUNNER 3 (528025) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from RDRUNNER 3 (528025) 115 kV Bus to RR_SVC_HV 3 (528024) 115 kV Bus CKT Z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0250_P1 | 3 phase fault on NORTH_LOVNG3 (528182) 115 kV Bus a. Apply Fault at the NORTH_LOVNG3 (528182) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from NORTH_LOVNG3 (528182) 115 kV Bus to BLACKRIVER 3 (528193) 115 kV Bus CKT 1 b. 2. Trip branch from BLACKRIVER 3 (528193) 115 kV Bus to SENDERO +3 (528184) 115 kV Bus CKT 1 b. 3. Trip branch from SENDERO +3 (528184) 115 kV Bus to BLCKRVR_DST3 (528206) 115 kV Bus CKT 1 b. 4. Trip branch from BLCKRVR_DST3 (528206) 115 kV Bus to CHINA_DRAW 3 (528222) 115 kV Bus CKT 1 b. 5. Drop Load 1 at NORTH_LOVNG3 (528182) 115 kV Bus b. 6. Drop Load 1 at BLACKRIVER 3 (528193) 115 kV Bus b. 7. Drop Load 1 at SENDERO +3 (528184) 115 kV Bus b. 8. Drop Load 2 at SENDERO +3 (528184) 115 kV Bus b. 9. Drop Load 1 at BLCKRVR_DST3 (528206) 115 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | No | No | Damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000], 523941 [MAJSTC-WTG110.6900], 523942 [MAJSTC-WTG210.6900], 523942 [MAJSTC-WTG210.6900], 761358 [G17-239-GEN10.6900], 761361 [G17-239-GEN20.6900], 761799 [G17-187GEN1 0.6900], 761802 [G17-187GEN2 0.6900], 763084 [G18-073-GEN20.6600], 763090 [G18-073-GEN10.6600], 584564 [G15-014-GE200.6900], 525783 [LRNZ2.3_GEN10.6900], 584565 [G15-014-GE230.6900]
05 - Southwest | 25S | Transfer | Group5_Fault_0251_P1 | 3 phase fault on ANDREWS 3 (528602) 115 kV Bus a. Apply Fault at the ANDREWS 3 (528602) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from ANDREWS 3 (528602) 115 kV Bus to NA_ENRICH 3 (528603) 115 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0252_P1 | 3 phase fault on ALRDCRTZ_TP3 (527030) 115 kV Bus a. Apply Fault at the ALRDCRTZ_TP3 (527030) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from ALRDCRTZ_TP3 (527030) 115 kV Bus to ALLRED_SUB 3 (527024) 115 kV Bus CKT 1 b. 2. Trip branch from ALLRED_SUB 3 (527024) 115 kV Bus to APACHE_ROB 3 (527022) 115 kV Bus CKT 1 b. 3. Trip branch from APACHE_ROB 3 (527022) 115 kV Bus to CORTEZ 3 (527021) 115 kV Bus CKT 1 b. 4. Drop Load 1 at ALLRED_SUB 3 (527024) 115 kV Bus b. 5. Drop Load 1 at APACHE_ROB 3 (527022) 115 kV Bus b. 6. Drop Load 1 at CORTEZ 3 (527021) 115 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0253_P1 | 3 phase fault on ALRDCRTZ_TP3 (527030) 115 kV Bus a. Apply Fault at the ALRDCRTZ_TP3 (527030) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from ALRDCRTZ_TP3 (527030) 115 kV Bus to XTO_CORNEL+3 (527033) 115 kV Bus CKT 1 b. 2. Trip branch from XTO_CORNEL+3 (527033) 115 kV Bus to SHELLC3_TP 3 (527068) 115 kV Bus CKT 1 b. 3. Drop Load 1 at XTO_CORNEL+3 (527033) 115 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0254_P1 | 3 phase fault on LP-DOUD_TP 3 (526162) 115 kV Bus a. Apply Fault at the LP-DOUD_TP 3 (526162) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from LP-DOUD_TP 3 (526162) 115 kV Bus to SP-WOLF_TP 3 (526481) 115 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0255_P1 | 3 phase fault on NA_ENRICH 3 (528603) 115 kV Bus a. Apply Fault at the NA_ENRICH 3 (528603) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from NA_ENRICH 3 (528603) 115 kV Bus to DRINKARD 3 (528589) 115 kV Bus CKT 1 b. 2. Trip branch from DRINKARD 3 (528589) 115 kV Bus to DRINKARD_TP3 (528533) 115 kV Bus CKT 1 b. 3. Drop Load 1 at NA_ENRICH 3 (528603) 115 kV Bus b. 4. Drop Load 5* at NA_ENRICH 3 (528603) 115 kV Bus b. 5. Drop Load 1 at DRINKARD 3 (528589) 115 kV Bus b. 6. Drop Load 1* at DRINKARD 3 (528589) 115 kV Bus b. 7. Drop Shunt 1 at NA_ENRICH 3 (528603) 115 kV Bus b. 8. Drop Shunt 1 at DRINKARD 3 (528589) 115 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0256_P1 | 3 phase fault on NA_ENRICH 3 (528603) 115 kV Bus a. Apply Fault at the NA_ENRICH 3 (528603) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from NA_ENRICH 3 (528603) 115 kV Bus to TARGA 3 (528605) 115 kV Bus CKT 1 b. 2. Trip branch from TARGA 3 (528605) 115 kV Bus to CARDINAL 3 (528596) 115 kV Bus CKT 1 b. 3. Drop Load 1 at NA_ENRICH 3 (528603) 115 kV Bus b. 4. Drop Load 5* at NA_ENRICH 3 (528603) 115 kV Bus b. 5. Drop Load 1 at TARGA 3 (528605) 115 kV Bus b. 6. Drop Shunt 1 at NA_ENRICH 3 (528603) 115 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0257_P1 | 3 phase fault on SHELLC3_TP 3 (527068) 115 kV Bus a. Apply Fault at the SHELLC3_TP 3 (527068) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from SHELLC3_TP 3 (527068) 115 kV Bus to SHELL_C2 3 (527036) 115 kV Bus CKT 1 b. 2. Trip branch from SHELL_C2 3 (527036) 115 kV Bus to DENVER_S 3 (527136) 115 kV Bus CKT 1 b. 3. Drop Load 1 at SHELL_C2 3 (527036) 115 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0258_P1 | 3 phase fault on SHELLC3_TP 3 (527068) 115 kV Bus a. Apply Fault at the SHELLC3_TP 3 (527068) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from SHELLC3_TP 3 (527068) 115 kV Bus to SHELLC3 3 (527074) 115 kV Bus CKT 1 b. 2. Drop Load 1 at SHELLC3 3 (527074) 115 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0259_P1 | 3 phase fault on TUCO_INT 6 (525830) 230 kV Bus a. Apply Fault at the TUCO_INT 6 (525830) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from TUCO_INT 6 (525830) 230 kV Bus to JONES 6 (526337) 230 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0260_P1 | 3 phase fault on TUCO_INT 6 (525830) 230 kV Bus a. Apply Fault at the TUCO_INT 6 (525830) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from TUCO_INT 6 (525830) 230 kV Bus to ANTELOPE_1 6 (525840) 230 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | Group5_Fault_0261_P1 | 3 phase fault on TUCO_INT 6 (525830) 230 kV Bus a. Apply Fault at the TUCO_INT 6 (525830) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from TUCO_INT 6 (525830) 230 kV Bus to CARLISLE 6 (526161) 230 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0262_P1 | 3 phase fault on TUCO_INT 6 (525830) 230 kV Bus a. Apply Fault at the TUCO_INT 6 (525830) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from TUCO_INT 6 (525830) 230 kV Bus to SWISHER 6 (525213) 230 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0263_P1 | 3 phase fault on HOBBS_INT 7 (527896) 345 kV Bus a. Apply Fault at the HOBBS_INT 7 (527896) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from HOBBS_INT 7 (527896) 345 kV Bus to KIOWA 7 (527965) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | No | No | No | No | No | No | No | Out Of Step Generators and damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000], 761358 [G17-239-GEN10.6900], 761361 [G17-239-GEN20.6900], 761799 [G17-187GEN1 0.6900], 761802 [G17-187GEN2 0.6900]
05 - Southwest | 25S | Transfer | Group5_Fault_0264_P1 | 3 phase fault on CARLISLE 6 (526161) 230 kV Bus a. Apply Fault at the CARLISLE 6 (526161) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from CARLISLE 6 (526161) 230 kV Bus to WOLFFORTH 6 (526525) 230 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0265_P1 | 3 phase fault on CARPENTER 7 (523823) 345 kV Bus a. Apply Fault at the CARPENTER 7 (523823) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from CARPENTER 7 (523823) 345 kV Bus to HARBNGR7 (531512) 345 kV Bus CKT Z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0266_P1 | 3 phase fault on G18-092-TAP (763215) 345 kV Bus a. Apply Fault at the G18-092-TAP (763215) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from G18-092-TAP (763215) 345 kV Bus to O.K.U.-7 (511456) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | No | No | No | No | No | No | No | Out Of Step Generators and damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000], 523941 [MAJSTC-WTG110.6900], 523942 [MAJSTC-WTG210.6900], 523942 [MAJSTC-WTG210.6900], 761358 [G17-239-GEN10.6900], 761361 [G17-239-GEN20.6900], 761799 [G17-187GEN1 0.6900], 761802 [G17-187GEN2 0.6900], 763084 [G18-073-GEN20.6600], 763090 [G18-073-GEN10.6600], 523936 [PANTEX_WIND10.6900], 524287 [GS-PHWD_GEN10.6900]
05 - Southwest | 25S | Transfer | Group5_Fault_0267_P1 | 3 phase fault on HOBBS_INT 3 (527891) 115 kV Bus a. Apply Fault at the HOBBS_INT 3 (527891) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from HOBBS_INT 3 (527891) 115 kV Bus to CUNNINHAM 3 (527864) 115 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | No | No | No | No | Yes | No | No | Out Of Step Generators and damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000], 523941 [MAJSTC-WTG110.6900], 523942 [MAJSTC-WTG210.6900], 523942 [MAJSTC-WTG210.6900], 761358 [G17-239-GEN10.6900], 761361 [G17-239-GEN20.6900], 761799 [G17-187GEN1 0.6900], 761802 [G17-187GEN2 0.6900], 762441 [G18-004-GEN10.6300], 763084 [G18-073-GEN20.6600], 763090 [G18-073-GEN10.6600], 523936 [PANTEX_WIND10.6900], 524287 [GS-PHWD_GEN10.6900]
05 - Southwest | 25S | Transfer | Group5_Fault_0268_P1 | 3 phase fault on HOBBS_INT 3 (527891) 115 kV Bus a. Apply Fault at the HOBBS_INT 3 (527891) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from HOBBS_INT 3 (527891) 115 kV Bus to CUNNINHAM 3 (527864) 115 kV Bus CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | No | No | No | No | Yes | No | No | Out Of Step Generators and damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000], 523941 [MAJSTC-WTG110.6900], 523942 [MAJSTC-WTG210.6900], 523942 [MAJSTC-WTG210.6900], 761358 [G17-239-GEN10.6900], 761361 [G17-239-GEN20.6900], 761799 [G17-187GEN1 0.6900], 761802 [G17-187GEN2 0.6900], 762441 [G18-004-GEN10.6300], 763084 [G18-073-GEN20.6600], 763090 [G18-073-GEN10.6600], 523936 [PANTEX_WIND10.6900], 524287 [GS-PHWD_GEN10.6900]
05 - Southwest | 25S | Transfer | Group5_Fault_0269_P1 | 3 phase fault on HOBBS_INT 3 (527891) 115 kV Bus a. Apply Fault at the HOBBS_INT 3 (527891) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from HOBBS_INT 3 (527891) 115 kV Bus to BENSING 3 (528433) 115 kV Bus CKT 1 b. 2. Trip branch from BENSING 3 (528433) 115 kV Bus to HIGG 3 (527363) 115 kV Bus CKT 1 b. 3. Drop Load 1 at BENSING 3 (528433) 115 kV Bus b. 4. Drop Load 1* at BENSING 3 (528433) 115 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | No | No | No | No | Yes | No | No | Out Of Step Generators and damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000], 523941 [MAJSTC-WTG110.6900], 523942 [MAJSTC-WTG210.6900], 523942 [MAJSTC-WTG210.6900], 761358 [G17-239-GEN10.6900], 761361 [G17-239-GEN20.6900], 761799 [G17-187GEN1 0.6900], 761802 [G17-187GEN2 0.6900], 762441 [G18-004-GEN10.6300], 523936 [PANTEX_WIND10.6900], 524287 [GS-PHWD_GEN10.6900]
05 - Southwest | 25S | Transfer | Group5_Fault_0270_P1 | 3 phase fault on HOBBS_INT 3 (527891) 115 kV Bus a. Apply Fault at the HOBBS_INT 3 (527891) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from HOBBS_INT 3 (527891) 115 kV Bus to MILLEN_TPW 3 (528434) 115 kV Bus CKT 1 b. 2. Trip branch from MILLEN_TPW 3 (528434) 115 kV Bus to MILLEN 3 (528435) 115 kV Bus CKT *1 b. 3. Trip branch from MILLEN 3 (528435) 115 kV Bus to MILLEN_TPE 3 (528436) 115 kV Bus CKT *1 b. 4. Trip branch from MILLEN_TPE 3 (528436) 115 kV Bus to NE_HOBBS 3 (528442) 115 kV Bus CKT 1 b. 5. Trip branch from NE_HOBBS 3 (528442) 115 kV Bus to TAYLOR 3 (528413) 115 kV Bus CKT 1 b. 6. Drop Load 1 at MILLEN 3 (528435) 115 kV Bus b. 7. Drop Load 1* at MILLEN 3 (528435) 115 kV Bus b. 8. Drop Load 1 at NE_HOBBS 3 (528442) 115 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | No | No | No | No | Yes | No | No | Out Of Step Generators and damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000], 523941 [MAJSTC-WTG110.6900], 523942 [MAJSTC-WTG210.6900], 523942 [MAJSTC-WTG210.6900], 762441 [G18-004-GEN10.6300], 523936 [PANTEX_WIND10.6900], 762226 [G17-151GEN3 0.6900], 524287 [GS-PHWD_GEN10.6900], 762223 [G17-151GEN2 0.6900], 762220 [G17-151GEN1 0.6900]
05 - Southwest | 25S | Transfer | Group5_Fault_0271_P1 | 3 phase fault on HOBBS_INT 3 (527891) 115 kV Bus a. Apply Fault at the HOBBS_INT 3 (527891) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from HOBBS_INT 3 (527891) 115 kV Bus to LE-WEST_SUB3 (528333) 115 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | No | No | No | No | Yes | No | No | Out Of Step Generators and damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000], 523941 [MAJSTC-WTG110.6900], 523942 [MAJSTC-WTG210.6900], 523942 [MAJSTC-WTG210.6900], 761358 [G17-239-GEN10.6900], 761361 [G17-239-GEN20.6900], 761799 [G17-187GEN1 0.6900], 761802 [G17-187GEN2 0.6900], 762441 [G18-004-GEN10.6300], 763084 [G18-073-GEN20.6600], 763090 [G18-073-GEN10.6600], 762441 [G18-004-GEN10.6300], 523936 [PANTEX_WIND10.6900], 524287 [GS-PHWD_GEN10.6900]
05 - Southwest | 25S | Transfer | Group5_Fault_0272_P1 | 3 phase fault on HOBBS_INT 3 (527891) 115 kV Bus a. Apply Fault at the HOBBS_INT 3 (527891) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from HOBBS_INT 3 (527891) 115 kV Bus to MADDOX 3 (528355) 115 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | No | No | No | No | Yes | No | No | Out Of Step Generators and damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000], 523941 [MAJSTC-WTG110.6900], 523942 [MAJSTC-WTG210.6900], 523942 [MAJSTC-WTG210.6900], 761358 [G17-239-GEN10.6900], 761361 [G17-239-GEN20.6900], 761799 [G17-187GEN1 0.6900], 761802 [G17-187GEN2 0.6900], 762441 [G18-004-GEN10.6300], 763084 [G18-073-GEN20.6600], 763090 [G18-073-GEN10.6600], 762441 [G18-004-GEN10.6300], 523936 [PANTEX_WIND10.6900], 524287 [GS-PHWD_GEN10.6900]
05 - Southwest | 25S | Transfer | Group5_Fault_0273_P1 | 3 phase fault on HOBBS_INT 3 (527891) 115 kV Bus a. Apply Fault at the HOBBS_INT 3 (527891) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from HOBBS_INT 3 (527891) 115 kV Bus to BENSING 3 (528433) 115 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | No | No | No | No | Yes | No | No | Out Of Step Generators and damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000], 523941 [MAJSTC-WTG110.6900], 523942 [MAJSTC-WTG210.6900], 523942 [MAJSTC-WTG210.6900], 761358 [G17-239-GEN10.6900], 761361 [G17-239-GEN20.6900], 761799 [G17-187GEN1 0.6900], 761802 [G17-187GEN2 0.6900], 762441 [G18-004-GEN10.6300], 763084 [G18-073-GEN20.6600], 763090 [G18-073-GEN10.6600], 523936 [PANTEX_WIND10.6900], 524287 [GS-PHWD_GEN10.6900]
05 - Southwest | 25S | Transfer | Group5_Fault_0274_P1 | 3 phase fault on CUNNINHAM 3 (527864) 115 kV Bus a. Apply Fault at the CUNNINHAM 3 (527864) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from CUNNINHAM 3 (527864) 115 kV Bus to BUCKEYE_TP 3 (528348) 115 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | No | No | No | No | Yes | No | No | Out Of Step Generators and damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000], 523941 [MAJSTC-WTG110.6900], 523942 [MAJSTC-WTG210.6900], 523942 [MAJSTC-WTG210.6900], 761358 [G17-239-GEN10.6900], 761361 [G17-239-GEN20.6900], 761799 [G17-187GEN1 0.6900], 761802 [G17-187GEN2 0.6900], 762441 [G18-004-GEN10.6300], 763084 [G18-073-GEN20.6600], 763090 [G18-073-GEN10.6600], 523936 [PANTEX_WIND10.6900], 524287 [GS-PHWD_GEN10.6900]
05 - Southwest | 25S | Transfer | Group5_Fault_0275_P1 | 3 phase fault on CUNNINHAM 3 (527864) 115 kV Bus a. Apply Fault at the CUNNINHAM 3 (527864) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from CUNNINHAM 3 (527864) 115 kV Bus to MADDOX 3 (528355) 115 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | No | No | No | No | Yes | No | No | Out Of Step Generators and damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000], 523941 [MAJSTC-WTG110.6900], 523942 [MAJSTC-WTG210.6900], 523942 [MAJSTC-WTG210.6900], 761358 [G17-239-GEN10.6900], 761361 [G17-239-GEN20.6900], 761799 [G17-187GEN1 0.6900], 761802 [G17-187GEN2 0.6900], 762441 [G18-004-GEN10.6300], 763084 [G18-073-GEN20.6600], 763090 [G18-073-GEN10.6600], 523936 [PANTEX_WIND10.6900], 524287 [GS-PHWD_GEN10.6900]
05 - Southwest | 25S | Transfer | Group5_Fault_0276_P1 | 3 phase fault on CUNNINHAM 3 (527864) 115 kV Bus a. Apply Fault at the CUNNINHAM 3 (527864) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from CUNNINHAM 3 (527864) 115 kV Bus to QUAHADA 3 (528394) 115 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | No | No | No | No | No | No | No | Out Of Step Generators and damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000], 523941 [MAJSTC-WTG110.6900], 523942 [MAJSTC-WTG210.6900], 523942 [MAJSTC-WTG210.6900], 761358 [G17-239-GEN10.6900], 761361 [G17-239-GEN20.6900], 761799 [G17-187GEN1 0.6900], 761802 [G17-187GEN2 0.6900], 762441 [G18-004-GEN10.6300], 763084 [G18-073-GEN20.6600], 763090 [G18-073-GEN10.6600], 523936 [PANTEX_WIND10.6900], 762441 [G18-004-GEN10.6300], 524287 [GS-PHWD_GEN10.6900]
05 - Southwest | 25S | Transfer | Group5_Fault_0277_P1 | 3 phase fault on CUNNINHAM 3 (527864) 115 kV Bus a. Apply Fault at the CUNNINHAM 3 (527864) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from CUNNINHAM 3 (527864) 115 kV Bus to MONUMNT_TP 3 (528568) 115 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | No | No | No | Yes | No | No | No | Out Of Step Generators and damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000], 523941 [MAJSTC-WTG110.6900], 523942 [MAJSTC-WTG210.6900], 523942 [MAJSTC-WTG210.6900], 761358 [G17-239-GEN10.6900], 761361 [G17-239-GEN20.6900], 761799 [G17-187GEN1 0.6900], 761802 [G17-187GEN2 0.6900], 762441 [G18-004-GEN10.6300], 763084 [G18-073-GEN20.6600], 763090 [G18-073-GEN10.6600], 762441 [G18-004-GEN10.6300], 523936 [PANTEX_WIND10.6900], 524287 [GS-PHWD_GEN10.6900]
05 - Southwest | 25S | Transfer | Group5_Fault_0278_P1 | 3 phase fault on CUNNINHAM 3 (527864) 115 kV Bus a. Apply Fault at the CUNNINHAM 3 (527864) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from CUNNINHAM 3 (527864) 115 kV Bus to CUNNIGHM_S 6 (527867) 230 kV Bus to CUNNHM_TR1 1 (527863) 13.2 kV Bus CKT 1 | P1 | Yes | Yes | Yes | No | Yes | No | No | Damping issues observed. Low voltage ride through fails due to the tripping of G18-115-GEN10 and G18-115-GEN20 units. No cascading was observed and the issue was localised. Model tuning is recommended. | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000], 523941 [MAJSTC-WTG110.6900], 523942 [MAJSTC-WTG210.6900], 523942 [MAJSTC-WTG210.6900], 761358 [G17-239-GEN10.6900], 761361 [G17-239-GEN20.6900], 761799 [G17-187GEN1 0.6900], 761802 [G17-187GEN2 0.6900], 763084 [G18-073-GEN20.6600], 763090 [G18-073-GEN10.6600], 523936 [PANTEX_WIND10.6900], 524287 [GS-PHWD_GEN10.6900]
05 - Southwest | 25S | Transfer | Group5_Fault_0279_P1 | 3 phase fault on LE-WEST_SUB3 (528333) 115 kV Bus a. Apply Fault at the LE-WEST_SUB3 (528333) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from LE-WEST_SUB3 (528333) 115 kV Bus to LE-NRTH_INT3 (528334) 115 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0280_P1 | 3 phase fault on MADDOX 3 (528355) 115 kV Bus a. Apply Fault at the MADDOX 3 (528355) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from MADDOX 3 (528355) 115 kV Bus to MONUMENT 3 (528491) 115 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | No | No | Damping issues observed. Low voltage ride through fails due to the tripping of G18-115-GEN10 unit. No cascading was observed and the issue was localised. Model tuning is recommended. | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000], 523941 [MAJSTC-WTG110.6900], 523942 [MAJSTC-WTG210.6900], 523942 [MAJSTC-WTG210.6900], 761358 [G17-239-GEN10.6900], 761361 [G17-239-GEN20.6900], 761799 [G17-187GEN1 0.6900], 761802 [G17-187GEN2 0.6900], 762441 [G18-004-GEN10.6300], 763084 [G18-073-GEN20.6600], 763090 [G18-073-GEN10.6600], 523936 [PANTEX_WIND10.6900], 524287 [GS-PHWD_GEN10.6900]
05 - Southwest | 25S | Transfer | Group5_Fault_0281_P1 | 3 phase fault on MADDOX 3 (528355) 115 kV Bus a. Apply Fault at the MADDOX 3 (528355) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from MADDOX 3 (528355) 115 kV Bus to G18-004-TAP (762442) 115 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | No | No | Damping issues observed. Low voltage ride through fails due to the tripping of G18-115-GEN10 unit. No cascading was observed and the issue was localised. Model tuning is recommended. | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000], 523941 [MAJSTC-WTG110.6900], 523942 [MAJSTC-WTG210.6900], 523942 [MAJSTC-WTG210.6900], 761358 [G17-239-GEN10.6900], 761361 [G17-239-GEN20.6900], 761799 [G17-187GEN1 0.6900], 761802 [G17-187GEN2 0.6900], 762441 [G18-004-GEN10.6300], 763084 [G18-073-GEN20.6600], 763090 [G18-073-GEN10.6600], 523936 [PANTEX_WIND10.6900], 524287 [GS-PHWD_GEN10.6900]
05 - Southwest | 25S | Transfer | Group5_Fault_0282_P1 | 3 phase fault on MADDOX 3 (528355) 115 kV Bus a. Apply Fault at the MADDOX 3 (528355) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from MADDOX 3 (528355) 115 kV Bus to PEARLE 3 (528392) 115 kV Bus CKT 1 b. 2. Trip branch from PEARLE 3 (528392) 115 kV Bus to ENRON_TP 3 (528317) 115 kV Bus CKT 1 b. 3. Drop Load 1 at PEARLE 3 (528392) 115 kV Bus b. 4. Drop Load 1* at PEARLE 3 (528392) 115 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | No | No | Damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 762441 [G18-004-GEN10.6300], 523812 [LANOGSU10.600.6000], 523936 [PANTEX_WIND10.6900], 524287 [GS-PHWD_GEN10.6900]
05 - Southwest | 25S | Transfer | Group5_Fault_0283_P1 | 3 phase fault on HIGG 3 (527363) 115 kV Bus a. Apply Fault at the HIGG 3 (527363) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from HIGG 3 (527363) 115 kV Bus to HIGGEAST 3 (527286) 115 kV Bus CKT 1 b. 2. Trip branch from HIGGEAST 3 (527286) 115 kV Bus to DENVER_N 3 (527130) 115 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0284_P1 | 3 phase fault on HIGG 3 (527363) 115 kV Bus a. Apply Fault at the HIGG 3 (527363) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from HIGG 3 (527363) 115 kV Bus to JOHNSON_DRW3 (527362) 115 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0285_P1 | 3 phase fault on HIGG 3 (527363) 115 kV Bus a. Apply Fault at the HIGG 3 (527363) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from HIGG 3 (527363) 115 kV Bus to RUSSELL 3 (527284) 115 kV Bus CKT 1 b. 2. Drop Load 1 at RUSSELL 3 (527284) 115 kV Bus b. 3. Drop Load 2 at RUSSELL 3 (527284) 115 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0286_P1 | 3 phase fault on INK_BASIN 6 (527028) 230 kV Bus a. Apply Fault at the INK_BASIN 6 (527028) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from INK_BASIN 6 (527028) 230 kV Bus to INK_BASIN 3 (527027) 115 kV Bus to INKBASN_TR 1 (527026) 13.2 kV Bus CKT 1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0287_P1 | 3 phase fault on CUNNIGHM_S 6 (527867) 230 kV Bus a. Apply Fault at the CUNNIGHM_S 6 (527867) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from CUNNIGHM_S 6 (527867) 230 kV Bus to CUNNIGHM_N 6 (527865) 230 kV Bus CKT *1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | No | No | No | No | No | No | No | Out Of Step Generators and damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000], 523941 [MAJSTC-WTG110.6900], 523942 [MAJSTC-WTG210.6900], 523942 [MAJSTC-WTG210.6900], 761358 [G17-239-GEN10.6900], 761361 [G17-239-GEN20.6900], 761799 [G17-187GEN1 0.6900], 761802 [G17-187GEN2 0.6900], 763084 [G18-073-GEN20.6600], 763090 [G18-073-GEN10.6600], 523936 [PANTEX_WIND10.6900], 524287 [GS-PHWD_GEN10.6900]
05 - Southwest | 25S | Transfer | Group5_Fault_0288_P1 | 3 phase fault on ANDREWS 6 (528604) 230 kV Bus a. Apply Fault at the ANDREWS 6 (528604) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from ANDREWS 6 (528604) 230 kV Bus to ANDREWS 3 (528602) 115 kV Bus to ANDREWS_TR21 (528600) 13.2 kV Bus CKT 2 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0289_P1 | 3 phase fault on ANDREWS 6 (528604) 230 kV Bus a. Apply Fault at the ANDREWS 6 (528604) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from ANDREWS 6 (528604) 230 kV Bus to ANDREWS 3 (528602) 115 kV Bus to ANDREWS_TR11 (528601) 13.2 kV Bus CKT 1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0290_P1 | 3 phase fault on TAYLOR 3 (528413) 115 kV Bus a. Apply Fault at the TAYLOR 3 (528413) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from TAYLOR 3 (528413) 115 kV Bus to JOHNSON_DRW3 (527362) 115 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0291_P1 | 3 phase fault on TAYLOR 3 (528413) 115 kV Bus a. Apply Fault at the TAYLOR 3 (528413) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from TAYLOR 3 (528413) 115 kV Bus to W_BENDER 3 (528449) 115 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0292_P1 | 3 phase fault on TAYLOR 3 (528413) 115 kV Bus a. Apply Fault at the TAYLOR 3 (528413) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from TAYLOR 3 (528413) 115 kV Bus to E_SANGER 3 (528470) 115 kV Bus CKT 1 b. 2. Trip branch from E_SANGER 3 (528470) 115 kV Bus to S_HOBBS 3 (528477) 115 kV Bus CKT 1 b. 3. Trip branch from S_HOBBS 3 (528477) 115 kV Bus to OXY_S_HOBBS3 (528480) 115 kV Bus CKT 1 b. 4. Trip branch from OXY_S_HOBBS3 (528480) 115 kV Bus to SW_4J44 3 (528484) 115 kV Bus CKT 1 b. 5. Trip branch from SW_4J44 3 (528484) 115 kV Bus to W_HOBBS 3 (528498) 115 kV Bus CKT 1 b. 6. Drop Load 1 at E_SANGER 3 (528470) 115 kV Bus b. 7. Drop Load 1 at S_HOBBS 3 (528477) 115 kV Bus b. 8. Drop Load 2 at S_HOBBS 3 (528477) 115 kV Bus b. 9. Drop Load 1 at OXY_S_HOBBS3 (528480) 115 kV Bus b. 10. Drop Load 2 at OXY_S_HOBBS3 (528480) 115 kV Bus b. 11. Drop Load 3 at OXY_S_HOBBS3 (528480) 115 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0293_P1 | 3 phase fault on LE-WAITS 3 (528325) 115 kV Bus a. Apply Fault at the LE-WAITS 3 (528325) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from LE-WAITS 3 (528325) 115 kV Bus to LE-NRTH_INT3 (528334) 115 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0294_P1 | 3 phase fault on LE-LOVINTON2 (528618) 69 kV Bus a. Apply Fault at the LE-LOVINTON2 (528618) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from LE-LOVINTON2 (528618) 69 kV Bus to LE-NRTH_INT3 (528334) 115 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0295_P1 | 3 phase fault on W_BENDER 3 (528449) 115 kV Bus a. Apply Fault at the W_BENDER 3 (528449) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from W_BENDER 3 (528449) 115 kV Bus to OXY_NHU_RCF3 (528574) 115 kV Bus CKT 1 b. 2. Trip branch from OXY_NHU_RCF3 (528574) 115 kV Bus to OXYPERMIAN 3 (528575) 115 kV Bus CKT 1 b. 3. Trip branch from OXYPERMIAN 3 (528575) 115 kV Bus to SANGER_SW 3 (528463) 115 kV Bus CKT 1 b. 4. Drop Load 1 at OXY_NHU_RCF3 (528574) 115 kV Bus b. 5. Drop Load 2 at OXY_NHU_RCF3 (528574) 115 kV Bus b. 6. Drop Load 2 at OXYPERMIAN 3 (528575) 115 kV Bus b. 7. Drop Load 1 at OXYPERMIAN 3 (528575) 115 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0296_P1 | 3 phase fault on W_BENDER 3 (528449) 115 kV Bus a. Apply Fault at the W_BENDER 3 (528449) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from W_BENDER 3 (528449) 115 kV Bus to N_HOBBS 3 (528456) 115 kV Bus CKT 1 b. 2. Drop Load 1 at N_HOBBS 3 (528456) 115 kV Bus b. 3. Drop Load 2 at N_HOBBS 3 (528456) 115 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0297_P1 | 3 phase fault on SANGER_SW 3 (528463) 115 kV Bus a. Apply Fault at the SANGER_SW 3 (528463) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from SANGER_SW 3 (528463) 115 kV Bus to G18-004-TAP (762442) 115 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0298_P1 | 3 phase fault on MONUMENT 3 (528491) 115 kV Bus a. Apply Fault at the MONUMENT 3 (528491) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from MONUMENT 3 (528491) 115 kV Bus to W_HOBBS 3 (528498) 115 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0299_P1 | 3 phase fault on W_HOBBS 3 (528498) 115 kV Bus a. Apply Fault at the W_HOBBS 3 (528498) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from W_HOBBS 3 (528498) 115 kV Bus to DRINKARD_TP3 (528533) 115 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0300_P1 | 3 phase fault on DRINKARD_TP3 (528533) 115 kV Bus a. Apply Fault at the DRINKARD_TP3 (528533) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from DRINKARD_TP3 (528533) 115 kV Bus to EUNICE 3 (528512) 115 kV Bus CKT 1 b. 2. Drop Load 1 at EUNICE 3 (528512) 115 kV Bus b. 3. Drop Load 1* at EUNICE 3 (528512) 115 kV Bus b. 4. Drop Shunt 1 at EUNICE 3 (528512) 115 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0301_P1 | 3 phase fault on MONUMNT_TP 3 (528568) 115 kV Bus a. Apply Fault at the MONUMNT_TP 3 (528568) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from MONUMNT_TP 3 (528568) 115 kV Bus to BYRD_TP 3 (528581) 115 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0302_P1 | 3 phase fault on JOHNSON_DRW3 (527362) 115 kV Bus a. Apply Fault at the JOHNSON_DRW3 (527362) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from JOHNSON_DRW3 (527362) 115 kV Bus to OXY_WSEM_TP3 (527325) 115 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0303_P1 | 3 phase fault on JOHNSON_DRW3 (527362) 115 kV Bus a. Apply Fault at the JOHNSON_DRW3 (527362) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from JOHNSON_DRW3 (527362) 115 kV Bus to LE-ERF 3 (528775) 115 kV Bus CKT "@1" c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0304_P1 | 3 phase fault on JOHNSON_DRW3 (527362) 115 kV Bus a. Apply Fault at the JOHNSON_DRW3 (527362) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from JOHNSON_DRW3 (527362) 115 kV Bus to MAPCO 3 (527360) 115 kV Bus CKT 1 b. 2. Trip branch from MAPCO 3 (527360) 115 kV Bus to AM_FRAC 3 (527300) 115 kV Bus CKT 1 b. 3. Drop Load 1 at MAPCO 3 (527360) 115 kV Bus b. 4. Drop Load 1 at AM_FRAC 3 (527300) 115 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0305_P1 | 3 phase fault on INK_BASIN 3 (527027) 115 kV Bus a. Apply Fault at the INK_BASIN 3 (527027) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from INK_BASIN 3 (527027) 115 kV Bus to ALRDCRTZ_TP3 (527030) 115 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0306_P1 | 3 phase fault on LE-WAITS 3 (528325) 115 kV Bus a. Apply Fault at the LE-WAITS 3 (528325) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from LE-WAITS 3 (528325) 115 kV Bus to LE-WAITS 2 (528617) 69 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0307_P1 | 3 phase fault on LE-LOVINTON2 (528618) 69 kV Bus a. Apply Fault at the LE-LOVINTON2 (528618) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from LE-LOVINTON2 (528618) 69 kV Bus to LE-DSYSRPOI2 (528677) 69 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0308_P1 | 3 phase fault on LE-LOVINTON2 (528618) 69 kV Bus a. Apply Fault at the LE-LOVINTON2 (528618) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from LE-LOVINTON2 (528618) 69 kV Bus to LE-TATMGOAB2 (528679) 69 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | Group5_Fault_0309_P1 | 3 phase fault on DENVER_N 3 (527130) 115 kV Bus a. Apply Fault at the DENVER_N 3 (527130) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from DENVER_N 3 (527130) 115 kV Bus to DENVER_S 3 (527136) 115 kV Bus CKT @1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | No | Yes | Damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer
05 - Southwest | 25S | Transfer | Group5_Fault_0310_P1 | 3 phase fault on DENVER_N 3 (527130) 115 kV Bus a. Apply Fault at the DENVER_N 3 (527130) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from DENVER_N 3 (527130) 115 kV Bus to MUSTANG 3 (527146) 115 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | No | Yes | Damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer
05 - Southwest | 25S | Transfer | Group5_Fault_0311_P1 | 3 phase fault on DENVER_N 3 (527130) 115 kV Bus a. Apply Fault at the DENVER_N 3 (527130) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from DENVER_N 3 (527130) 115 kV Bus to DENVER_CTY 2 (527125) 69 kV Bus to DNVER_N_TR11 (527122) 13.2 kV Bus CKT 1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0312_P1 | 3 phase fault on BYRD_TP 3 (528581) 115 kV Bus a. Apply Fault at the BYRD_TP 3 (528581) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from BYRD_TP 3 (528581) 115 kV Bus to BYRD 3 (528582) 115 kV Bus CKT 1 b. 2. Drop Load 1 at BYRD 3 (528582) 115 kV Bus b. 3. Drop Load 1* at BYRD 3 (528582) 115 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0313_P1 | 3 phase fault on BYRD_TP 3 (528581) 115 kV Bus a. Apply Fault at the BYRD_TP 3 (528581) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from BYRD_TP 3 (528581) 115 kV Bus to COOPER_RNCH3 (528554) 115 kV Bus CKT 1 b. 2. Trip branch from COOPER_RNCH3 (528554) 115 kV Bus to OIL_CENTER 3 (528552) 115 kV Bus CKT 1 b. 3. Trip branch from OIL_CENTER 3 (528552) 115 kV Bus to LEA_ROAD 3 (528505) 115 kV Bus CKT 1 b. 4. Drop Load 1 at COOPER_RNCH3 (528554) 115 kV Bus b. 5. Drop Load 1 at OIL_CENTER 3 (528552) 115 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0314_P1 | 3 phase fault on OXY_WSEM_TP3 (527325) 115 kV Bus a. Apply Fault at the OXY_WSEM_TP3 (527325) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from OXY_WSEM_TP3 (527325) 115 kV Bus to OXY_WSTSEM 3 (527323) 115 kV Bus CKT 1 b. 2. Drop Load 1 at OXY_WSTSEM 3 (527323) 115 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0315_P1 | 3 phase fault on OXY_WSEM_TP3 (527325) 115 kV Bus a. Apply Fault at the OXY_WSEM_TP3 (527325) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from OXY_WSEM_TP3 (527325) 115 kV Bus to GAINES 3 (527322) 115 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0316_P1 | 3 phase fault on LE-ERF 3 (528775) 115 kV Bus a. Apply Fault at the LE-ERF 3 (528775) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from LE-ERF 3 (528775) 115 kV Bus to LE-TALLCOTN3 (528779) 115 kV Bus CKT 1 b. 2. Trip branch from LE-TALLCOTN3 (528779) 115 kV Bus to LE-KCM 3 (527292) 115 kV Bus CKT 1 b. 3. Drop Load 1 at LE-TALLCOTN3 (528779) 115 kV Bus b. 4. Drop Load 1 at LE-KCM 3 (527292) 115 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0317_P1 | 3 phase fault on LE-ERF 3 (528775) 115 kV Bus a. Apply Fault at the LE-ERF 3 (528775) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from LE-ERF 3 (528775) 115 kV Bus to LE-ERF 2 (528774) 69 kV Bus to LE-ERF_TR 1 (528773) 12.47 kV Bus CKT 1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0318_P1 | 3 phase fault on POTASH_JCT 3 (527962) 115 kV Bus a. Apply Fault at the POTASH_JCT 3 (527962) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from POTASH_JCT 3 (527962) 115 kV Bus to PCA 3 (527930) 115 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | No | No | Damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000], 523941 [MAJSTC-WTG110.6900], 523942 [MAJSTC-WTG210.6900], 523942 [MAJSTC-WTG210.6900], 761358 [G17-239-GEN10.6900], 761361 [G17-239-GEN20.6900], 761799 [G17-187GEN1 0.6900], 761802 [G17-187GEN2 0.6900], 763084 [G18-073-GEN20.6600], 763090 [G18-073-GEN10.6600], 523936 [PANTEX_WIND10.6900], 524287 [GS-PHWD_GEN10.6900]
05 - Southwest | 25S | Transfer | Group5_Fault_0319_P1 | 3 phase fault on CARDINAL 3 (528596) 115 kV Bus a. Apply Fault at the CARDINAL 3 (528596) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from CARDINAL 3 (528596) 115 kV Bus to TEAGUE 3 (528526) 115 kV Bus CKT 1 b. 2. Trip branch from TEAGUE 3 (528526) 115 kV Bus to S_JAL 3 (528547) 115 kV Bus CKT 1 b. 3. Drop Load 1 at TEAGUE 3 (528526) 115 kV Bus b. 4. Drop Load 1* at TEAGUE 3 (528526) 115 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0320_P1 | 3 phase fault on CARDINAL 3 (528596) 115 kV Bus a. Apply Fault at the CARDINAL 3 (528596) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from CARDINAL 3 (528596) 115 kV Bus to SAGE_BRUSH 3 (527955) 115 kV Bus CKT 1 b. 2. Trip branch from SAGE_BRUSH 3 (527955) 115 kV Bus to MEDANOS 3 (527954) 115 kV Bus CKT 1 b. 3. Trip branch from MEDANOS 3 (527954) 115 kV Bus to LIVSTNRIDGE3 (527953) 115 kV Bus CKT 1 b. 4. Drop Load 1 at SAGE_BRUSH 3 (527955) 115 kV Bus b. 5. Drop Load 1* at SAGE_BRUSH 3 (527955) 115 kV Bus b. 6. Drop Load 1 at TEAGUE 3 (528526) 115 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0321_P1 | 3 phase fault on GAINES 3 (527322) 115 kV Bus a. Apply Fault at the GAINES 3 (527322) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from GAINES 3 (527322) 115 kV Bus to SEMINOLE 3 (527275) 115 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0322_P1 | 3 phase fault on GAINES 3 (527322) 115 kV Bus a. Apply Fault at the GAINES 3 (527322) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from GAINES 3 (527322) 115 kV Bus to LEGACY 3 (527346) 115 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0323_P1 | 3 phase fault on GAINES 3 (527322) 115 kV Bus a. Apply Fault at the GAINES 3 (527322) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from GAINES 3 (527322) 115 kV Bus to GAINES 2 (527321) 69 kV Bus to GAINES_TR1 1 (527319) 13.2 kV Bus CKT 1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0324_P1 | 3 phase fault on GAINES 3 (527322) 115 kV Bus a. Apply Fault at the GAINES 3 (527322) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from GAINES 3 (527322) 115 kV Bus to GAINES 2 (527321) 69 kV Bus to GAINES_TR2 1 (527320) 13.2 kV Bus CKT 2 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0325_P1 | 3 phase fault on SEMINOLE 3 (527275) 115 kV Bus a. Apply Fault at the SEMINOLE 3 (527275) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from SEMINOLE 3 (527275) 115 kV Bus to SAN_ANDS_TP3 (527105) 115 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | No | Yes | Damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer
05 - Southwest | 25S | Transfer | Group5_Fault_0326_P1 | 3 phase fault on SEMINOLE 3 (527275) 115 kV Bus a. Apply Fault at the SEMINOLE 3 (527275) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from SEMINOLE 3 (527275) 115 kV Bus to SEMINOLE 6 (527276) 230 kV Bus to SEMINLE_TR21 (527274) 13.2 kV Bus CKT 2 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0327_P1 | 3 phase fault on SEMINOLE 3 (527275) 115 kV Bus a. Apply Fault at the SEMINOLE 3 (527275) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from SEMINOLE 3 (527275) 115 kV Bus to SEMINOLE 6 (527276) 230 kV Bus to SEMINLE_TR11 (527273) 13.2 kV Bus CKT 1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0328_P1 | 3 phase fault on GAINES 2 (527321) 69 kV Bus a. Apply Fault at the GAINES 2 (527321) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from GAINES 2 (527321) 69 kV Bus to RILEY_TP 2 (527228) 69 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0329_P1 | 3 phase fault on SAN_ANDS_TP3 (527105) 115 kV Bus a. Apply Fault at the SAN_ANDS_TP3 (527105) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from SAN_ANDS_TP3 (527105) 115 kV Bus to DENVER_S 3 (527136) 115 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0330_P1 | 3 phase fault on RILEY_TP 2 (527228) 69 kV Bus a. Apply Fault at the RILEY_TP 2 (527228) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from RILEY_TP 2 (527228) 69 kV Bus to RILEY 2 (527331) 69 kV Bus CKT 1 b. 2. Drop Load 1 at RILEY 2 (527331) 69 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0331_P4 | a. Apply single phase fault at O.K.U.-7 (511456) 345 kV CB 3409A Stuck b. Clear Fault after 16 cycles: b. 1. Trip branch from O.K.U.-7 (511456) 345 kV to L.E.S.-7 (511468) 345 kV CKT 1 b. 2. Trip branch from O.K.U.-7 (511456) 345 kV to G18-092-TAP (763215) 345 kV CKT 1 | P4 | No | No | No | Yes | No | No | No | Out Of Step Generators and damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000], 523941 [MAJSTC-WTG110.6900], 523942 [MAJSTC-WTG210.6900], 523942 [MAJSTC-WTG210.6900], 761358 [G17-239-GEN10.6900], 761361 [G17-239-GEN20.6900], 761799 [G17-187GEN1 0.6900], 761802 [G17-187GEN2 0.6900], 763084 [G18-073-GEN20.6600], 763090 [G18-073-GEN10.6600], 584563 [G15-014-GE170.6900], 584564 [G15-014-GE200.6900], 584565 [G15-014-GE230.6900]
05 - Southwest | 25S | Transfer | Group5_Fault_0332_P4 | a. Apply single phase fault at L.E.S.-7 (511468) 345 kV CB 3429B Stuck b. Clear Fault after 16 cycles: b. 1. Trip branch from O.K.U.-7 (511456) 345 kV to L.E.S.-7 (511468) 345 kV CKT 1 b. 2. Trip three winding transformer from LES#5-1 (511411) 13.8 kV to L.E.S.-4 (511467) kV to L.E.S.-7 (511468) 345 kV CKT2 | P4 | No | No | No | No | Yes | No | No | Out Of Step Generators and damping issues observed | Lawton Eastside 345 kV Substation Upgrade to Double-Bus-Double-Breaker Configuration | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000], 761358 [G17-239-GEN10.6900], 761361 [G17-239-GEN20.6900], 761799 [G17-187GEN1 0.6900], 761802 [G17-187GEN2 0.6900], 763084 [G18-073-GEN20.6600], 763090 [G18-073-GEN10.6600]
05 - Southwest | 25S | Transfer | Group5_Fault_0333_P4 | a. Apply single phase fault at L.E.S.-7 (511468) 345 kV CB 3433A Stuck b. Clear Fault after 16 cycles: b. 1. Trip branch from L.E.S.-7 (511468) 345 kV to O.K.U.-7 (511456) 345 kV CKT 1 b. 2. Trip branch from L.E.S.-7 (511468) 345 kV to G17-171-TAP (760938) 345 kV CKT 1 | P4 | No | No | No | No | No | No | No | Out Of Step Generators and damping issues observed | Lawton Eastside 345 kV Substation Upgrade to Double-Bus-Double-Breaker Configuration | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000], 523941 [MAJSTC-WTG110.6900], 523942 [MAJSTC-WTG210.6900], 523942 [MAJSTC-WTG210.6900], 761358 [G17-239-GEN10.6900], 761361 [G17-239-GEN20.6900], 761799 [G17-187GEN1 0.6900], 761802 [G17-187GEN2 0.6900], 763084 [G18-073-GEN20.6600], 763090 [G18-073-GEN10.6600], 584563 [G15-014-GE170.6900], 584564 [G15-014-GE200.6900], 584565 [G15-014-GE230.6900]
05 - Southwest | 25S | Transfer | Group5_Fault_0334_P4 | a. Apply single phase fault at BVRCNTY7 (515554) 345 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from BVRCNTY7 (515554) 345 kV to HITCHLAND 7 (523097) 345 kV CKT 1 b. 2. Trip branch from BVRCNTY7 (515554) 345 kV to HITCHLAND 7 (523097) 345 kV CKT 2 | P4 | Yes | No | Yes | No | Yes | Yes | No | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points) |  | Generator relays were disabled for the following generators: 589383 [G17-100-GEN10.5500]
05 - Southwest | 25S | Transfer | Group5_Fault_0335_P4 | a. Apply single phase fault at CARPENTER 7 (523823) 345 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from CARPENTER 7 (523823) 345 kV to FINNEY 7 (523853) 345 kV CKT 1 b. 2. Disconnect Bus CARPENTER 7 (523823) 345 kV | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0336_P4 | a. Apply single phase fault at CROSSROADS 7 (527656) 345 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from CROSSROADS 7 (527656) 345 kV to EDDY_CNTY 7 (527802) 345 kV CKT 1 b. 2. Trip branch from CROSSROADS 7 (527656) 345 kV to TOLK 7 (525549) 345 kV CKT 1 b. 3. Trip branch from CROSSROADS 7 (527656) 345 kV to RSVLT_CC_E 7 (527655) 345 kV CKT 1 b. 4. Disconnect Bus RSVLT_CC_E 7 (527655) 345 kV b. 5. Disconnect Bus MILO_WIND 1 (527653) 0.7 kV b. 6. Disconnect Bus RSVLT_GEN1 1 (527651) 0.69 kV b. 7. Disconnect Bus RSVLT_GEN2 1 (527652) 0.69 kV b. 8. Disconnect Bus RSVLT_CC_W 7 (527654) 345 kV b. 9. Disconnect Bus CROSSROADS 7 (527656) 345 kV | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0337_P4 | a. Apply single phase fault at EDDY_CNTY 7 (527802) 345 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from EDDY_CNTY 7 (527802) 345 kV to KIOWA 7 (527965) 345 kV CKT 1 b. 2. Trip branch from EDDY_CNTY 7 (527802) 345 kV to CROSSROADS 7 (527656) 345 kV CKT 1 b. 3. Trip three winding transformer from EDDY_TR 1 (527796) 13.2 kV to EDDY_NORTH 6 (527799) kV to EDDY_CNTY 7 (527802) 345 kV CKT1 b. 4. Disconnect Bus EDDY_TR 1 (527796) 13.2 kV b. 5. Disconnect Bus EDDY_CNTY 7 (527802) 345 kV | P4 | Yes | Yes | Yes | No | Yes | Yes | No | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points) |  | Generator relays were disabled for the following generators: 763309 [G18-112-GEN10.6600]
05 - Southwest | 25S | Transfer | Group5_Fault_0338_P4 | a. Apply single phase fault at FINNEY 7 (523853) 345 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from FINNEY 7 (523853) 345 kV to CARPENTER 7 (523823) 345 kV CKT 1 b. 2. Trip branch from FINNEY 7 (523853) 345 kV to HOLCOMB7 (531449) 345 kV CKT 1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0339_P4 | a. Apply single phase fault at HITCHLAND 7 (523097) 345 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from HITCHLAND 7 (523097) 345 kV to BVRCNTY7 (515554) 345 kV CKT 2 b. 2. Disconnect Bus NOVUS_WND 1 (523107) 4.16 kV b. 3. Disconnect Bus NOVUS1 1 (523109) 34.5 kV b. 4. Disconnect Bus NOVUS1 3 (523111) 115 kV b. 5. Disconnect Bus NOVUS1_TR1 1 (523110) 13.8 kV | P4 | Yes | Yes | Yes | No | Yes | Yes | No | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points) |  | Generator relays were disabled for the following generators: 560584 [G06-44-2 4.1600]
05 - Southwest | 25S | Transfer | Group5_Fault_0340_P4 | a. Apply single phase fault at HITCHLAND 7 (523097) 345 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from HITCHLAND 7 (523097) 345 kV to CARPENTER 7 (523823) 345 kV CKT 1 b. 2. Drop Shunt HITCHLAND 7 (523097) 345 kV b. 3. Trip three winding transformer from HITCHLD_TR21 (523094) 13.2 kV to HITCHLAND 6 (523095) kV to HITCHLAND 7 (523097) 345 kV CKT2 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0341_P4 | a. Apply single phase fault at HITCHLAND 7 (523097) 345 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from HITCHLAND 7 (523097) 345 kV to POTTER_CO 7 (523961) 345 kV CKT 1 b. 2. Disconnect Bus NOBLE_TR 1 (523102) 13.8 kV b. 3. Disconnect Bus NOBLE_WND 3 (523103) 115 kV b. 4. Disconnect Bus GRPLNS-HV4-3 (523130) 115 kV b. 5. Disconnect Bus GRPLNS-HV2-3 (523131) 115 kV b. 6. Disconnect Bus GRPLNS-LV4-1 (523127) 34.5 kV b. 7. Disconnect Bus GRPLNS-LV2-1 (523129) 34.5 kV b. 8. Disconnect Bus GRPLNS-CB4-1 (523124) 34.5 kV b. 9. Disconnect Bus GRPLNS-CB2-1 (523126) 34.5 kV b. 10. Disconnect Bus GRPLNS-WT4-1 (523121) 0.575 kV b. 11. Disconnect Bus GRPLNS-WT2-1 (523123) 0.575 kV | P4 | Yes | Yes | Yes | No | Yes | No | No | Damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523122 [NBLWND-WTG110.7000]
05 - Southwest | 25S | Transfer | Group5_Fault_0342_P4 | a. Apply single phase fault at HOBBS_INT 7 (527896) 345 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from HOBBS_INT 7 (527896) 345 kV to KIOWA 7 (527965) 345 kV CKT 1 b. 2. Disconnect Bus HOBBS_TR3 1 (527895) 13.2 kV | P4 | Yes | Yes | Yes | No | Yes | No | No | Damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000], 523941 [MAJSTC-WTG110.6900], 523942 [MAJSTC-WTG210.6900], 523942 [MAJSTC-WTG210.6900], 761358 [G17-239-GEN10.6900], 761361 [G17-239-GEN20.6900], 761799 [G17-187GEN1 0.6900], 761802 [G17-187GEN2 0.6900], 763084 [G18-073-GEN20.6600], 763090 [G18-073-GEN10.6600], 523971 [HARRNGTON1 124.000], 524021 [NICHOLS_1 113.800], 524023 [NICHOLS_3 122.000]
05 - Southwest | 25S | Transfer | Group5_Fault_0343_P4 | a. Apply single phase fault at N_LOVING 7 (528185) 345 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from N_LOVING 7 (528185) 345 kV to CHINA_DRAW 7 (528223) 345 kV CKT 1 b. 2. Trip branch from N_LOVING 7 (528185) 345 kV to KIOWA 7 (527965) 345 kV CKT 1 b. 3. Trip three winding transformer from NORTH_LOVNG3 (528182) 115 kV to N_LOVING 7 (528185) kV to N_LOVING TR1 (528186) 13.2 kV CKT1 b. 4. Disconnect Bus N_LOVING TR1 (528186) 13.2 kV b. 5. Disconnect Bus N_LOVING 7 (528185) 345 kV | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0344_P4 | a. Apply single phase fault at POTTER_CO 7 (523961) 345 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from POTTER_CO 7 (523961) 345 kV to HITCHLAND 7 (523097) 345 kV CKT 1 b. 2. Trip three winding transformer from POTTER_TR 1 (523957) 13.2 kV to POTTER_CO 6 (523959) kV to POTTER_CO 7 (523961) 345 kV CKT1 b. 3. Disconnect Bus POTTER_CO 7 (523961) 345 kV b. 4. Disconnect Bus SPNSPUR_WND7 (524296) 345 kV b. 5. Disconnect Bus SPNSPUR_GEN1 (524295) 0.69 kV | P4 | Yes | Yes | Yes | No | Yes | No | No | Damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000], 523941 [MAJSTC-WTG110.6900], 523942 [MAJSTC-WTG210.6900], 523942 [MAJSTC-WTG210.6900], 761358 [G17-239-GEN10.6900], 761361 [G17-239-GEN20.6900], 761799 [G17-187GEN1 0.6900], 761802 [G17-187GEN2 0.6900], 763084 [G18-073-GEN20.6600], 763090 [G18-073-GEN10.6600], 523942 [MAJSTC-WTG210.6900], 523941 [MAJSTC-WTG110.6900], 524021 [NICHOLS_1 113.800]
05 - Southwest | 25S | Transfer | Group5_Fault_0345_P4 | a. Apply single phase fault at YOAKUM_345 (526936) 345 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from YOAKUM_345 (526936) 345 kV to TUCO_INT 7 (525832) 345 kV CKT 1 b. 2. Trip branch from YOAKUM_345 (526936) 345 kV to HOBBS_INT 7 (527896) 345 kV CKT 1 b. 3. Trip three winding transformer from YOAKUM 6 (526935) 230 kV to YOAKUM_345 (526936) kV to YOAKUM_TR1 (526937) 13.2 kV CKT1 b. 4. Disconnect Bus YOAKUM_TR1 (526937) 13.2 kV b. 5. Disconnect Bus YOAKUM_345 (526936) 345 kV | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0346_P4 | a. Apply single phase fault at TUCO_INT 7 (525832) 345 kV b. Clear Fault after 16 cycles: b. 1. Disconnect Bus TUCO_TR1 1 (525824) 13.2 kV b. 2. Trip branch from TUCO_INT 7 (525832) 345 kV to CRAWFISH_DR (560022) 345 kV CKT | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0347_P4 | a. Apply single phase fault at TUCO_INT 7 (525832) 345 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from TUCO_INT 7 (525832) 345 kV to YOAKUM_345 (526936) 345 kV CKT 1 b. 2. Disconnect Bus ELK_CT1 (525850) 345 kV b. 3. Disconnect Bus ELK_1 1 (525844) 18 kV b. 4. Disconnect Bus ELK_2 1 (525845) 18 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | Group5_Fault_0348_P4 | a. Apply single phase fault at EDDY_CNTY 7 (527802) 345 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from EDDY_CNTY 7 (527802) 345 kV to KIOWA 7 (527965) 345 kV CKT 1 b. 2. Trip branch from EDDY_CNTY 7 (527802) 345 kV to CROSSROADS 7 (527656) 345 kV CKT 1 b. 3. Disconnect Bus EDDY_TR 1 (527796) 13.2 kV b. 4. Disconnect Bus EDDY_CNTY 7 (527802) 345 kV | P4 | Yes | Yes | Yes | No | Yes | Yes | No | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points) |  | Generator relays were disabled for the following generators: 763309 [G18-112-GEN10.6600]
05 - Southwest | 25S | Transfer | Group5_Fault_0349_P4 | a. Apply single phase fault at HOBBS_INT 7 (527896) 345 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from HOBBS_INT 7 (527896) 345 kV to KIOWA 7 (527965) 345 kV CKT 1 b. 2. Disconnect Bus HOBBS_TR3 1 (527895) 13.2 kV | P4 | Yes | Yes | Yes | No | Yes | No | No | Damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000], 523941 [MAJSTC-WTG110.6900], 523942 [MAJSTC-WTG210.6900], 523942 [MAJSTC-WTG210.6900], 761358 [G17-239-GEN10.6900], 761361 [G17-239-GEN20.6900], 761799 [G17-187GEN1 0.6900], 761802 [G17-187GEN2 0.6900], 763084 [G18-073-GEN20.6600], 763090 [G18-073-GEN10.6600], 523971 [HARRNGTON1 124.000], 524021 [NICHOLS_1 113.800], 524023 [NICHOLS_3 122.000]
05 - Southwest | 25S | Transfer | Group5_Fault_0350_P4 | a. Apply single phase fault at YOAKUM_345 (526936) 345 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from YOAKUM_345 (526936) 345 kV to TUCO_INT 7 (525832) 345 kV CKT 1 b. 2. Trip branch from YOAKUM_345 (526936) 345 kV to HOBBS_INT 7 (527896) 345 kV CKT 1 b. 3. Disconnect Bus YOAKUM_TR1 (526937) 13.2 kV b. 4. Disconnect Bus YOAKUM_345 (526936) 345 kV | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0351_P4 | a. Apply single phase fault at N_LOVING 7 (528185) 345 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from N_LOVING 7 (528185) 345 kV to CHINA_DRAW 7 (528223) 345 kV CKT 1 b. 2. Trip branch from N_LOVING 7 (528185) 345 kV to KIOWA 7 (527965) 345 kV CKT 1 b. 3. Disconnect Bus N_LOVING TR1 (528186) 13.2 kV b. 4. Disconnect Bus N_LOVING 7 (528185) 345 kV | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0352_P4 | a. Apply single phase fault at CHINA_DRAW 7 (528223) 345 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from CHINA_DRAW 7 (528223) 345 kV to PHANTOM 7 (528015) 345 kV CKT 1 b. 2. Trip branch from CHINA_DRAW 7 (528223) 345 kV to N_LOVING 7 (528185) 345 kV CKT 1 b. 3. Disconnect Bus CHINA_DRAW 1 (528219) 13.2 kV b. 4. Disconnect Bus CHINA_DRAW 7 (528223) 345 kV | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0353_P4 | a. Apply single phase fault at RDRUNNER 7 (528027) 345 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from RDRUNNER 7 (528027) 345 kV to PHANTOM 7 (528015) 345 kV CKT 1 b. 2. Trip branch from RDRUNNER 7 (528027) 345 kV to KIOWA 7 (527965) 345 kV CKT 1 b. 3. Disconnect Bus RDRNNER_TR11 (528023) 13.2 kV b. 4. Disconnect Bus RDRUNNER 7 (528027) 345 kV | P4 | Yes | Yes | Yes | No | Yes | No | Yes | Damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer
05 - Southwest | 25S | Transfer | Group5_Fault_0354_P4 | a. Apply single phase fault at PHANTOM 7 (528015) 345 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from PHANTOM 7 (528015) 345 kV to CHINA_DRAW 7 (528223) 345 kV CKT 1 b. 2. Disconnect Bus PHANTOM TR21 (528012) 13.2 kV | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0355_P4 | a. Apply single phase fault at PHANTOM 7 (528015) 345 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from PHANTOM 7 (528015) 345 kV to RDRUNNER 7 (528027) 345 kV CKT 1 b. 2. Disconnect Bus PHANTOM TR11 (528011) 13.2 kV | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0356_P4 | a. Apply single phase fault at SUNDOWN 6 (526435) 230 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from SUNDOWN 6 (526435) 230 kV to AMOCO_SS 6 (526460) kV CKT 1 b. 2. Disconnect Bus AMOCO_SS 6 (526460) 230 kV | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0357_P4 | a. Apply single phase fault at BORDER 7 (515458) 345 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from BORDER 7 (515458) 345 kV to CRAWFISH_DR (560022) 345 kV CKT 1 b. 2. Trip branch from BORDER 7 (515458) 345 kV to WWDBORDT (755000) 345 kV CKT 1 | P4 | No | No | No | No | Yes | No | No | Out Of Step Generators and damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000], 523941 [MAJSTC-WTG110.6900], 523942 [MAJSTC-WTG210.6900], 523942 [MAJSTC-WTG210.6900], 761358 [G17-239-GEN10.6900], 761361 [G17-239-GEN20.6900], 761799 [G17-187GEN1 0.6900], 761802 [G17-187GEN2 0.6900], 763084 [G18-073-GEN20.6600], 763090 [G18-073-GEN10.6600], 523941 [MAJSTC-WTG110.6900]
05 - Southwest | 25S | Transfer | Group5_Fault_0358_P4 | a. Apply single phase fault at WWRDEHV7 (515375) 345 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from WWRDEHV7 (515375) 345 kV to WWDBORDT (755000) 345 kV CKT 1 b. 2. Trip branch from WWRDEHV7 (515375) 345 kV to TATONGA7 (515407) 345 kV CKT 1 b. 3. Trip three winding transformer from WWRDEHV7 (515375) 345 kV to WWRDEHV4 (515376) kV to WWDEHV21 (515799) 13.8 kV CKT2 b. 4. Drop Shunt 1 WWDEHV21 (515799) 13.8 kV | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0359_P4 | a. Apply single phase fault at SWEETWT6 (511541) 230 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from SWEETWT6 (511541) 230 kV to CHISHOLM6 (511557) 230 kV CKT 1 b. 2. Trip branch from SWEETWT6 (511541) 230 kV to STLN-DEMARC6 (523779) 230 kV CKT 1 b. 3. Trip branch from STLN-DEMARC6 (523779) 230 kV to WHEELER 6 (523777) 230 kV CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 511968 [ROARK0 0.6900], 511968 [ROARK0 0.6900]
05 - Southwest | 25S | Transfer | Group5_Fault_0360_P4 | a. Apply single phase fault at TUCO_INT 6 (525830) 230 kV b. Clear Fault after 16 cycles: b. 1. Trip three winding transformer from TUCO_INT 6 (525830) 230 kV to TUCO_INT 3 (525828) kV to TUCO_TR4 1 (525821) 13.2 kV CKT1 b. 2. Trip three winding transformer from TUCO_INT 6 (525830) 230 kV to TUCO_INT 7 (525832) kV to TUCO_TR2 1 (525825) 13.2 kV CKT2 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0361_P4 | a. Apply single phase fault at PLANT_X 6 (525481) 230 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from PLANT_X 6 (525481) 230 kV to SUNDOWN 6 (526435) 230 kV CKT 1 b. 2. Trip branch from PLANT_X 6 (525481) 230 kV to TOLK 6 (525531) 230 kV CKT 1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0362_P4 | a. Apply single phase fault at NEWHART 6 (525461) 230 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from NEWHART 6 (525461) 230 kV to POTTER_CO 6 (523959) 230 kV CKT 1 b. 2. Trip three winding transformer from NEWHART 6 (525461) 230 kV to NEWHART 3 (525460) kV to NEWHART_TR11 (525459) 13.2 kV CKT1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0363_P4 | a. Apply single phase fault at TOLK 6 (525531) 230 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from TOLK 6 (525531) 230 kV to ROOSEVELT 6 (524909) 230 kV CKT 1 b. 2. Trip three winding transformer from TOLK 7 (525549) 345 kV to TOLK 6 (525531) kV to TOLK_TR 1 (525537) 13.2 kV CKT1 b. 3. Drop Shunt 1 TOLK_TR 1 (525537) 13.2 kV | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0364_P4 | a. Apply single phase fault at PLANT_X 3 (525480) 115 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from PLANT_X 3 (525480) 115 kV to MULSHVLY_TP3 (525019) 115 kV CKT 1 b. 2. Trip branch from MULSHVLY_TP3 (525019) 115 kV to MULESHVALLY3 (525018) 115 kV CKT 1 b. 3. Trip branch from MULSHVLY_TP3 (525019) 115 kV to BAILEYCO 3 (525028) 115 kV CKT 1 b. 4. Drop Load 1 MULESHVALLY3 (525018) 115 kV b. 5. Drop Load 2 MULESHVALLY3 (525018) 115 kV | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0365_P4 | a. Apply single phase fault at ROOSEVELT 6 (524909) 230 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from ROOSEVELT 6 (524909) 230 kV to OASIS 6 (524875) 230 kV CKT 1 b. 2. Trip branch from ROOSEVELT 6 (524909) 230 kV to TOLK 6 (525531) 230 kV CKT 1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0366_P4 | a. Apply single phase fault at LAMB_CNTY 3 (525636) 115 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from LAMB_CNTY 3 (525636) 115 kV to HOCKLEY 3 (526020) 115 kV CKT 1 b. 2. Trip three winding transformer from LAMB_CNTY 6 (525637) 230 kV to LAMB_CNTY 3 (525636) kV to LAMB_TR3 1 (525633) 13.2 kV CKT1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0367_P4 | a. Apply single phase fault at CASTRO_CNTY3 (524746) 115 kV b. Clear Fault after 16 cycles: b. 1. Trip three winding transformer from CASTRO_CNTY3 (524746) 115 kV to CASTRO_CNTY2 (524745) kV to CASTRO_TR1 1 (524744) 13.2 kV CKT1 b. 2. Trip branch from CASTRO_CNTY3 (524746) 115 kV to DS-#21 3 (524734) 115 kV CKT 1 b. 3. Trip branch from DS-#21 3 (524734) 115 kV to TIERABLANCA3 (524630) 115 kV CKT 1 b. 4. Drop Load 1 DS-#21 3 (524734) 115 kV | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0368_P4 | a. Apply single phase fault at TUCO_INT 3 (525828) 115 kV b. Clear Fault after 16 cycles: b. 1. Trip three winding transformer from TUCO_INT 3 (525828) 115 kV to TUCO_INT 6 (525830) kV to TUCO_TR4 1 (525821) 13.2 kV CKT1 b. 2. Trip branch from TUCO_INT 3 (525828) 115 kV to FLOYD_CNTY 3 (525780) 115 kV CKT 1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0369_P4 | a. Apply single phase fault at KRESS_INT 3 (525192) 115 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from KRESS_INT 3 (525192) 115 kV to KRS_RURL_TP3 (525226) 115 kV CKT 1 b. 2. Trip three winding transformer from KRESS_INT 3 (525192) 115 kV to KRESS_INT 2 (525191) kV to KRESS_TR1 1 (525190) 13.2 kV CKT1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0370_P4 | a. Apply single phase fault at LUBBCK_STH 6 (526269) 230 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from WOLFFORTH 6 (526525) 230 kV to LUBBCK_STH 6 (526269) 230 kV CKT 1 b. 2. Trip branch from JONES 6 (526337) 230 kV to LUBBCK_STH 6 (526269) 230 kV CKT 1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0371_P4 | a. Apply single phase fault at YOAKUM 6 (526935) 230 kV b. Clear Fault after 16 cycles: b. 1. Trip three winding transformer from YOAKUM 6 (526935) 230 kV to YOAKUM 3 (526934) kV to YOAKUM_TR1 1 (526931) 13.2 kV CKT1 b. 2. Trip branch from YOAKUM 3 (526934) 115 kV to PLAINS_INT 3 (526928) 115 kV CKT 1 | P4 | Yes | Yes | Yes | No | Yes | No | Yes | Damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer
05 - Southwest | 25S | Transfer | Group5_Fault_0372_P4 | a. Apply single phase fault at TERRY_CNTY 3 (526736) 115 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from TERRY_CNTY 3 (526736) 115 kV to WOLFFORTH 3 (526524) 115 kV CKT 1 b. 2. Trip three winding transformer from TERRY_CNTY 3 (526736) 115 kV to TERRY_CNTY 2 (526735) kV to TERRY_TR1 1 (526733) 13.2 kV CKT1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0373_P4 | a. Apply single phase fault at TIERABLANCA3 (524630) 115 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from TIERABLANCA3 (524630) 115 kV to DFSMTH_EST 3 (524619) 115 kV CKT 1 b. 2. Trip three winding transformer from DEAFSMITH 6 (524623) 230 kV to DFSMTH_EST 3 (524619) kV to DEFSMTH_TR21 (524621) 13.8 kV CKT2 b. 3. Trip branch from TIERABLANCA3 (524630) 115 kV to NE_HEREFORD3 (524567) 115 kV CKT 1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0374_P4 | a. Apply single phase fault at ROLLHILLS 3 (524007) 115 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from ROLLHILLS 3 (524007) 115 kV to NORTHWEST 3 (524106) 115 kV CKT 1 b. 2. Drop Shunt 1 ROLLHILLS 3 (524007) 115 kV | P4 | Yes | Yes | Yes | No | Yes | Yes | No | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points) |  | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25S | Transfer | Group5_Fault_0375_P4 | a. Apply single phase fault at AMA_SOUTH 3 (524414) 115 kV b. Clear Fault after 16 cycles: b. 1. Trip three winding transformer from AMA_SOUTH 3 (524414) 115 kV to AMA_SOUTH 6 (524415) kV to AMA_SO_TR1 1 (524410) 13.2 kV CKT1 b. 2. Trip branch from AMA_SOUTH 3 (524414) 115 kV to OWENSCORN 3 (524404) 115 kV CKT 1 | P4 | Yes | Yes | Yes | No | Yes | Yes | No | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points) |  | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25S | Transfer | Group5_Fault_0376_P4 | a. Apply single phase fault at HITCHLAND 6 (523095) 230 kV b. Clear Fault after 16 cycles: b. 1. Trip three winding transformer from HITCHLAND 6 (523095) 230 kV to HITCHLAND 7 (523097) kV to HITCHLD_TR21 (523094) 13.2 kV CKT2 b. 2. Trip branch from HITCHLAND 6 (523095) 230 kV to MOORE_CNTY 6 (523309) 230 kV CKT 1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0377_P4 | a. Apply single phase fault at L.E.S.-4 (511467) 138 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from L.E.S.-4 (511467) 138 kV to SHERID4 (511474) 138 kV CKT 1 b. 2. Trip branch from SHERID4 (511474) 138 kV to ARTVLTP4 (511537) 138 kV CKT 1 b. 3. Trip branch from 53CACHE4 (511509) 138 kV to ARTVLTP4 (511537) 138 kV CKT 1 b. 4. Trip branch from ARTVLTP4 (511537) 138 kV to ARTVILL4 (511538) 138 kV CKT 1 b. 5. Trip branch from LWS-NTP4 (511471) 138 kV to 53CACHE4 (511509) 138 kV CKT 1 b. 6. Trip branch from LWS N4 (511430) 138 kV to LWS-NTP4 (511471) 138 kV CKT 1 b. 7. Drop Load 1 SHERID4 (511474) 138 kV b. 8. Drop Load 1 ARTVILL4 (511538) 138 kV b. 9. Drop Load 1 53CACHE4 (511509) 138 kV b. 10. Drop Load 1 LWS N4 (511430) 138 kV b. 11. Drop Shunt 1 ARTVILL4 (511538) 138 kV b. 12. Drop Shunt 1 LWS N4 (511430) 138 kV b. 13. Trip three winding transformer from L.E.S.-4 (511467) 138 kV to L.E.S.-7 (511468) kV to LES#5-1 (511411) 13.8 kV CKT2 b. 14. Drop Shunt 1 LES#5-1 (511411) 13.8 kV | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0378_P4 | a. Apply single phase fault at PLSNT_HILL 3 (524768) 115 kV b. Clear Fault after 16 cycles: b. 1. Trip three winding transformer from PLSNT_HILL 6 (524770) 230 kV to PLSNT_HILL 3 (524768) kV to PLSNHIL_TR11 (524767) 13.2 kV CKT1 b. 2. Trip branch from PLSNT_HILL 3 (524768) 115 kV to N_CLOVIS_TP3 (524776) 115 kV CKT 1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0379_P4 | a. Apply single phase fault at CURRY 3 (524822) 115 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from CURRY 3 (524822) 115 kV to ROOSEVELT 3 (524908) 115 kV CKT 2 b. 2. Trip branch from CURRY 3 (524822) 115 kV to NORRIS_TP 3 (524764) 115 kV CKT 1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0380_P4 | a. Apply single phase fault at PORTALES 3 (524924) 115 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from ROOSEVELT 3 (524908) 115 kV to PORTALES 3 (524924) 115 kV CKT 1 b. 2. Trip branch from OASIS 3 (524874) 115 kV to PORTALES 3 (524924) 115 kV CKT 1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0381_P4 | a. Apply single phase fault at NEWHART 3 (525460) 115 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from CASTRO_CNTY3 (524746) 115 kV to NEWHART 3 (525460) 115 kV CKT 1 b. 2. Trip three winding transformer from NEWHART 6 (525461) 230 kV to NEWHART 3 (525460) kV to NEWHART_TR21 (525458) 13.2 kV CKT2 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0382_P4 | a. Apply single phase fault at YOAKUM 3 (526934) 115 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from PLAINS_INT 3 (526928) 115 kV to YOAKUM 3 (526934) 115 kV CKT 1 b. 2. Trip three winding transformer from YOAKUM 6 (526935) 230 kV to YOAKUM 3 (526934) kV to YOAKUM_TR1 1 (526931) 13.2 kV CKT1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0383_P4 | a. Apply single phase fault at LAMB_CNTY 2 (525635) 69 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from W_LITTLFLD 2 (525613) 69 kV to LAMB_CNTY 2 (525635) 69 kV CKT 1 b. 2. Trip branch from AMHERST 2 (525606) 69 kV to W_LITTLFLD 2 (525613) 69 kV CKT 1 b. 3. Trip branch from LC-SANDHLL+2 (525599) 69 kV to AMHERST 2 (525606) 69 kV CKT 1 b. 4. Trip branch from SUDANRURAL 2 (525592) 69 kV to LC-SANDHLL+2 (525599) 69 kV CKT 1 b. 5. Drop Load 1 W_LITTLFLD 2 (525613) 69 kV b. 6. Drop Load 1 AMHERST 2 (525606) 69 kV b. 7. Drop Load 1 LC-SANDHLL+2 (525599) 69 kV b. 8. Drop Load 2 LC-SANDHLL+2 (525599) 69 kV b. 9. Drop Load 1 SUDANRURAL 2 (525592) 69 kV b. 10. Trip three winding transformer from LAMB_CNTY 3 (525636) 115 kV to LAMB_CNTY 2 (525635) kV to LAMB_TR1 1 (525631) 13.2 kV CKT1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0384_P4 | a. Apply single phase fault at CARLISLE 3 (526160) 115 kV b. Clear Fault after 16 cycles: b. 1. Trip three winding transformer from CARLISLE 6 (526161) 230 kV to CARLISLE 3 (526160) kV to CRLSLE_TR1 1 (526157) 13.2 kV CKT1 b. 2. Trip branch from CARLISLE 3 (526160) 115 kV to MURPHY 3 (526192) 115 kV CKT 1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0385_P4 | a. Apply single phase fault at FLOYD_CNTY 3 (525780) 115 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from FLOYD_CNTY 3 (525780) 115 kV to TUCO_INT 3 (525828) 115 kV CKT 1 b. 2. Trip three winding transformer from FLOYD_CNTY 3 (525780) 115 kV to FLOYD_CNTY 2 (525779) kV to FLOYD_TR1 1 (525777) 13.2 kV CKT1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0386_P4 | a. Apply single phase fault at TUCO_INT 2 (525826) 69 kV b. Clear Fault after 16 cycles: b. 1. Trip three winding transformer from TUCO_INT 3 (525828) 115 kV to TUCO_INT 2 (525826) kV to TUCO_TR6 1 (525823) 13.2 kV CKT1 b. 2. Trip branch from TUCO_INT 2 (525826) 69 kV to SP-NEWDEAL 2 (525885) 69 kV CKT 1 b. 3. Trip branch from SP-NEWDEAL 2 (525885) 69 kV to MONROE 2 (525892) 69 kV CKT 1 b. 4. Trip branch from WHITEHEAD 2 (525891) 69 kV to MONROE 2 (525892) 69 kV CKT 1 b. 5. Trip branch from WHITEHEAD 2 (525891) 69 kV to SP-SHALLWTR2 (525899) 69 kV CKT 1 b. 6. Trip branch from SP-SHALLWTR2 (525899) 69 kV to STANTON_N 2 (526073) 69 kV CKT 1 b. 7. Drop Load 1 SP-NEWDEAL 2 (525885) 69 kV b. 8. Drop Load 1 MONROE 2 (525892) 69 kV b. 9. Drop Load 1 WHITEHEAD 2 (525891) 69 kV b. 10. Drop Load SP-SHALLWTR2 (525899) 69 kV | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0387_P4 | a. Apply single phase fault at POTTER_CO 7 (523961) 345 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from POTTER_CO 7 (523961) 345 kV to TOLK 7 (525549) 345 kV CKT 1 b. 2. Trip branch from POTTER_CO 7 (523961) 345 kV to GRAPEVINE (560035) 345 kV CKT 1 b. 3. Trip branch from CHISHOLM7 (511553) 345 kV to GRAPEVINE (560035) 345 kV CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | Group5_Fault_0388_P4 | a. Apply single phase fault at CROSSROADS 7 (527656) 345 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from TOLK 7 (525549) 345 kV to CROSSROADS 7 (527656) 345 kV CKT 1 b. 2. Trip branch from CROSSROADS 7 (527656) 345 kV to EDDY_CNTY 7 (527802) 345 kV CKT 1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0389_P4 | a. Apply single phase fault at TUCO_INT 7 (525832) 345 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from TUCO_INT 7 (525832) 345 kV to YOAKUM_345 (526936) 345 kV CKT 1 b. 2. Trip three winding transformer from TUCO_INT 7 (525832) 345 kV to TUCO_INT 6 (525830) kV to TUCO_TR1 1 (525824) 13.2 kV CKT1 b. 3. Drop Shunt 1 TUCO_TR1 1 (525824) 13.2 kV | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0390_P4 | a. Apply single phase fault at HITCHLAND 7 (523097) 345 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from HITCHLAND 7 (523097) 345 kV to CARPENTER 7 (523823) 345 kV CKT 1 b. 2. Trip branch from BVRCNTY7 (515554) 345 kV to HITCHLAND 7 (523097) 345 kV CKT 1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0391_P4 | a. Apply single phase fault at POTTER_CO 6 (523959) 230 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from POTTER_CO 6 (523959) 230 kV to HARRNG_EST 6 (523979) 230 kV CKT 1 b. 2. Trip branch from POTTER_CO 6 (523959) 230 kV to ROLLHILLS 6 (524010) 230 kV CKT 1 | P4 | Yes | Yes | Yes | No | Yes | Yes | No | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points) |  | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25S | Transfer | Group5_Fault_0392_P4 | a. Apply single phase fault at YOAKUM_345 (526936) 345 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from YOAKUM_345 (526936) 345 kV to HOBBS_INT 7 (527896) 345 kV CKT 1 b. 2. Trip branch from TUCO_INT 7 (525832) 345 kV to YOAKUM_345 (526936) 345 kV CKT 1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0393_P4 | a. Apply single phase fault at HOBBS_INT 3 (527891) 115 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from HOBBS_INT 3 (527891) 115 kV to MADDOX 3 (528355) 115 kV CKT 1 b. 2. Trip branch from HOBBS_INT 3 (527891) 115 kV to MILLEN_TPW 3 (528434) 115 kV CKT 1 b. 3. Trip branch from MILLEN_TPW 3 (528434) 115 kV to MILLEN 3 (528435) 115 kV CKT *1 b. 4. Trip branch from MILLEN 3 (528435) 115 kV to MILLEN_TPE 3 (528436) 115 kV CKT *1 b. 5. Trip branch from MILLEN_TPE 3 (528436) 115 kV to NE_HOBBS 3 (528442) 115 kV CKT 1 b. 6. Trip branch from NE_HOBBS 3 (528442) 115 kV to TAYLOR 3 (528413) 115 kV CKT 1 b. 7. Drop Load 1 MILLEN 3 (528435) 115 kV b. 8. Drop Load 1* MILLEN 3 (528435) 115 kV b. 9. Drop Load 1 NE_HOBBS 3 (528442) 115 kV | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0394_P4 | a. Apply single phase fault at CUNNINHAM 3 (527864) 115 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from CUNNINHAM 3 (527864) 115 kV to BUCKEYE_TP 3 (528348) 115 kV CKT 1 b. 2. Trip branch from CUNNINHAM 3 (527864) 115 kV to QUAHADA 3 (528394) 115 kV CKT 1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0395_P4 | a. Apply single phase fault at MADDOX 3 (528355) 115 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from HOBBS_INT 3 (527891) 115 kV to MADDOX 3 (528355) 115 kV CKT 1 b. 2. Trip branch from MADDOX 3 (528355) 115 kV to G18-004-TAP (762442) 115 kV CKT 1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0396_P4 | a. Apply single phase fault at JOHNSON_DRW3 (527362) 115 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from JOHNSON_DRW3 (527362) 115 kV to LE-ERF 3 (528775) 115 kV CKT @1 b. 2. Trip branch from JOHNSON_DRW3 (527362) 115 kV to HIGG 3 (527363) 115 kV CKT 1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0397_P4 | a. Apply single phase fault at LE-LOVINTON2 (528618) 69 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from LE-LOVINTON2 (528618) 69 kV to LE-NRTH_INT3 (528334) 115 kV CKT 1 b. 2. Trip branch from LE-LOVINTON2 (528618) 69 kV to LE-DSYSRPOI2 (528677) 69 kV CKT 1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0398_P4 | a. Apply single phase fault at DENVER_N 3 (527130) 115 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from DENVER_N 3 (527130) 115 kV to MUSTANG 3 (527146) 115 kV CKT 1 b. 2. Trip branch from DENVER_N 3 (527130) 115 kV to HIGGEAST 3 (527286) 115 kV CKT 1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0399_P4 | a. Apply single phase fault at EDDY_NORTH 6 (527799) 230 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from EDDY_NORTH 6 (527799) 230 kV to CUNNIGHM_N 6 (527865) 230 kV CKT 1 b. 2. Trip three winding transformer from EDDY_CNTY 7 (527802) 345 kV to EDDY_NORTH 6 (527799) kV to EDDY_TR 1 (527796) 13.2 kV CKT1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0400_P4 | a. Apply single phase fault at POTASH_JCT 3 (527962) 115 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from POTASH_JCT 3 (527962) 115 kV to KIOWA 3 (527966) 115 kV CKT 1 b. 2. Trip three winding transformer from KIOWA 7 (527965) 345 kV to KIOWA 3 (527966) kV to KIOWA_TR1 1 (527964) 13.2 kV CKT1 b. 3. Trip three winding transformer from POTASH_JCT 6 (527963) 230 kV to POTASH_JCT 3 (527962) kV to POTASH_TR1 1 (527958) 13.2 kV CKT1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0401_P4 | a. Apply single phase fault at GAINES 3 (527322) 115 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from SEMINOLE 3 (527275) 115 kV to GAINES 3 (527322) 115 kV CKT 1 b. 2. Trip branch from GAINES 3 (527322) 115 kV to OXY_WSEM_TP3 (527325) 115 kV CKT 1 b. 3. Trip branch from OXY_WSTSEM 3 (527323) 115 kV to OXY_WSEM_TP3 (527325) 115 kV CKT 1 b. 4. Drop Load 1 OXY_WSTSEM 3 (527323) 115 kV | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0402_P4 | a. Apply single phase fault at HOBBS_INT 6 (527894) 230 kV b. Clear Fault after 16 cycles: b. 1. Trip three winding transformer from HOBBS_INT 7 (527896) 345 kV to HOBBS_INT 6 (527894) kV to HOBBS_TR3 1 (527895) 13.2 kV CKT1 b. 2. Trip branch from HOBBS_INT 6 (527894) 230 kV to ANDREWS 6 (528604) 230 kV CKT 1 | P4 | Yes | Yes | Yes | No | Yes | No | Yes | Damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer
05 - Southwest | 25S | Transfer | Group5_Fault_0403_P4 | a. Apply single phase fault at RANDALL 3 (524364) 115 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from GEORGIA 3 (524322) 115 kV to RANDALL 3 (524364) 115 kV CKT 1 b. 2. Trip three winding transformer from RANDALL 6 (524365) 230 kV to RANDALL 3 (524364) kV to RANDAL_TR1 1 (524361) 13.2 kV CKT1 | P4 | Yes | Yes | Yes | No | Yes | Yes | No | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points) |  | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25S | Transfer | Group5_Fault_0404_P4 | a. Apply single phase fault at COULTER 3 (524306) 115 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from 34TH_ST_TP 3 (524281) 115 kV to COULTER 3 (524306) 115 kV CKT 1 b. 2. Trip branch from COULTER 3 (524306) 115 kV to PUCKETT 3 (524256) 115 kV CKT 1 b. 3. Trip branch from PUCKETT 3 (524256) 115 kV to SONCY_TP 3 (524252) 115 kV CKT 1 b. 4. Drop Load 1 PUCKETT 3 (524256) 115 kV | P4 | Yes | Yes | Yes | No | Yes | Yes | No | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points) |  | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25S | Transfer | Group5_Fault_0405_P4 | a. Apply single phase fault at EAST_PLANT 3 (524162) 115 kV b. Clear Fault after 16 cycles: b. 1. Trip three winding transformer from EAST_PLANT 6 (524163) 230 kV to EAST_PLANT 3 (524162) kV to EPLANT_TR3 1 (524160) 13.2 kV CKT1 b. 2. Trip branch from HARRNG_WST 6 (523977) 230 kV to EAST_PLANT 6 (524163) 230 kV CKT 1 b. 3. Trip branch from EAST_PLANT 3 (524162) 115 kV to PIERCE_TP 3 (524185) 115 kV CKT 1 | P4 | Yes | Yes | Yes | No | Yes | Yes | No | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points) |  | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25S | Transfer | Group5_Fault_0406_P4 | a. Apply single phase fault at NICHOLS 3 (524043) 115 kV b. Clear Fault after 16 cycles: b. 1. Trip three winding transformer from NICHOLS 6 (524044) 230 kV to NICHOLS 3 (524043) kV to NICHOLS_TR11 (524041) 13.2 kV CKT1 b. 2. Trip branch from NICHOLS 3 (524043) 115 kV to WHITAKER 3 (524058) 115 kV CKT 1 b. 3. Trip branch from WHITAKER 3 (524058) 115 kV to EAST_PLANT 3 (524162) 115 kV CKT 1 | P4 | No | No | No | No | No | No | No | Out Of Step Generators and damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000], 523941 [MAJSTC-WTG110.6900], 523942 [MAJSTC-WTG210.6900], 523942 [MAJSTC-WTG210.6900], 761358 [G17-239-GEN10.6900], 761361 [G17-239-GEN20.6900], 761799 [G17-187GEN1 0.6900], 761802 [G17-187GEN2 0.6900], 763084 [G18-073-GEN20.6600], 763090 [G18-073-GEN10.6600], 524287 [GS-PHWD_GEN10.6900], 524021 [NICHOLS_1 113.800], 524022 [NICHOLS_2 113.800], 523972 [HARRNGTON2 124.000]
05 - Southwest | 25S | Transfer | Group5_Fault_0407_P4 | a. Apply single-phase fault at BVRCNTY7 (515554) 345 kV Bus CB 307 Stuck b. Clear Fault after 16 cycles: b. 1. Trip branch from BVRCNTY7 (515554) 345 kV Bus TO BADGER 7 (515677) 345 kV Bus CKT 1 b. 2. Trip branch from BVRCNTY7 (515554) 345 kV Bus TO BADGER 7 (515677) 345 kV Bus CKT 2 | P4 | Yes | Yes | Yes | No | Yes | Yes | No | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points) |  | Generator relays were disabled for the following generators: 589383 [G17-100-GEN10.5500]
05 - Southwest | 25S | Transfer | Group5_Fault_0408_P4 | a. Apply single-phase fault at WWDBORDT (755000) 345 kV Bus CB 384 Stuck b. Clear Fault after 16 cycles: b. 1. Trip branch from WWDBORDT (755000) 345 kV Bus TO BORDER 7 (515458) 345 kV Bus CKT 1 b. 2. Trip branch from BORDER 7 (515458) 345 kV Bus TO CRAWFISH_DR (560022) 345 kV Bus CKT 1 | P4 | No | No | No | No | Yes | No | No | Out Of Step Generators and damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000], 523941 [MAJSTC-WTG110.6900], 523942 [MAJSTC-WTG210.6900], 523942 [MAJSTC-WTG210.6900], 761358 [G17-239-GEN10.6900], 761361 [G17-239-GEN20.6900], 761799 [G17-187GEN1 0.6900], 761802 [G17-187GEN2 0.6900], 763084 [G18-073-GEN20.6600], 763090 [G18-073-GEN10.6600], 523942 [MAJSTC-WTG210.6900], 523942 [MAJSTC-WTG210.6900], 523936 [PANTEX_WIND10.6900]
05 - Southwest | 25S | Transfer | Group5_Fault_0409_P4 | a. Apply single-phase fault at CARPENTER 7 (523823) 345 kV Bus CB OR335 Stuck b. Clear Fault after 21 cycles: b. 1. Trip branch from CARPENTER 7 (523823) 345 kV Bus TO FINNEY 7 (523853) 345 kV Bus CKT 1 b. 2. Clear fault and Disconnect CARPENTER 7 (523823) 345 kV Bus | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0410_P4 | a. Apply single-phase fault at CROSSROADS 7 (527656) 345 kV CB 6R30 Stuck b. Clear Fault after 21 cycles: b. 1. Trip branch from EDDY_CNTY 7 (527802) 345 kV Bus TO CROSSROADS 7 (527656) 345 kV Bus CKT 1 b. 2. Trip branch from TOLK 7 (525549) 345 kV Bus TO CROSSROADS 7 (527656) 345 kV Bus CKT 1 b. 3. Disconnect Bus RSVLT_CC_E 7 (527655) 345 kV b. 4. Disconnect Bus MILO_WIND 1 (527653) 0.70 kV b. 5. Disconnect Bus RSVLT_GEN1 1 (527651) 0.69 kV b. 6. Disconnect Bus RSVLT_GEN2 1 (527652) 0.69 kV b. 7. Disconnect Bus RSVLT_CC_W 7 (527654) 345 kV b. 8. Drop Generator 1 Bus SAGSFT3_2.21 (527605) 0.70 kV b. 9. Drop Generator 1 Bus SAGSFT4_2.21 (527607) 0.70 kV b. 10. Drop Generator 1 Bus SAGSFT1_2.21 (527614) 0.70 kV b. 11. Drop Generator 1 Bus SAGSFT1_2.01 (527615) 0.70 kV b. 12. Drop Generator 1 Bus SAGSFT2_2.21 (527617) 0.70 kV b. 13. Drop Generator 1 Bus SAGSFT2_2.01 (527618) 0.70 kV b. 14. Drop Load 1 Bus SAGA_SCOL 7 (527610) 345 kV b. 15. Drop Load 2 Bus SAGA_SCOL 7 (527610) 345 kV b. 16. Disconnect Bus SAGA_NDCOL 7 (527598) 345 kV b. 17. Disconnect Bus SAGA_SDCOL 7 (527599) 345 kV b. 18. Disconnect Bus SAGA_SMEAS 7 (527600) 345 kV b. 19. Disconnect Bus SAGA_NCOL 7 (527601) 345 kV b. 20. Disconnect Bus SAGANCOL1 1 (527602) 34.5 kV b. 21. Disconnect Bus SAGANCOL2 1 (527603) 34.5 kV b. 22. Disconnect Bus GRDXFR3 1 (527604) 0.50 kV b. 23. Disconnect Bus SAGSFT3_2.21 (527605) 0.70 kV b. 24. Disconnect Bus GRDXFR4 1 (527606) 0.50 kV b. 25. Disconnect Bus SAGSFT4_2.21 (527607) 0.70 kV b. 26. Disconnect Bus SUB BUS #3 1 (527608) 34.5 kV b. 27. Disconnect Bus SUB BUS #4 1 (527609) 34.5 kV b. 28. Disconnect Bus SAGA_SCOL 7 (527610) 345 kV b. 29. Disconnect Bus SAGASCOL1 1 (527611) 34.5 kV b. 30. Disconnect Bus SAGASCOL2 1 (527612) 34.5 kV b. 31. Disconnect Bus GRDXFR1 1 (527613) 0.50 kV b. 32. Disconnect Bus SAGSFT1_2.21 (527614) 0.70 kV b. 33.Disconnect Bus SAGSFT1_2.01 (527615) 0.70 kV b. 34. Disconnect Bus GRDXFR2 1 (527616) 0.50 kV b. 35. Disconnect Bus SAGSFT2_2.21 (527617) 0.70 kV b. 36. Disconnect Bus SAGSFT2_2.01 (527618) 0.70 kV b. 37. Disconnect Bus SAGA_NCLTR31 (527621) 13.8 kV b. 38. Disconnect Bus SAGA_NCLTR41 (527622) 13.8 kV b. 39. Disconnect Bus SAGA_SCLTR11 (527623) 13.8 kV b. 40. Disconnect Bus SAGA_SCLTR21 (527624) 13.8 kV b. 41. Disconnect Bus SUB BUS #1 (527628) 34.5 kV b. 42. Disconnect Bus SUB BUS #2 (527629) 34.5 kV b. 43. Disconnect Bus CROSSROADS 7 (527656) 345 kV b. 44. Disconnect Bus RSVLT_WIND11 (527658) 34.5 kV b. 45. Disconnect Bus RSVLT_WIND21 (527659) 34.5 kV b. 46. Disconnect Bus RSVLT_COL1 1 (527660) 34.5 kV b. 47. Disconnect Bus RSVLT_COL2 1 (527661) 34.5 kV b. 48. Disconnect Bus RSVLT_TR1 1 (527662) 13.2 kV b. 49. Disconnect Bus RSVLT_TR2 1 (527663) 13.2 kV b. 50. Disconnect Bus RSVLT_COL1 7 (527666) 345 kV b. 51. Disconnect Bus RSVLT_COL2 7 (527667) 345 kV b. 52. Disconnect Bus MILO_CB (577120) 34.5 kV b. 53. Disconnect Bus MILO_WND (577121) 34.5 kV | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0411_P4 | Apply single-phase fault at CROSSROADS 7 (527656) 345 kV Bus CB 6R45 Stuck b. Run for 21 cycles: b. 1. Trip branch from CROSSROADS 7 (527656) 345 kV Bus TO TOLK 7 (525549) 345 kV Bus CKT 1 b. 2. Trip branch from CROSSROADS 7 (527656) 345 kV Bus TO SAGA_SCOL 7 (527610) 345 kV Bus CKT 1 b. 3. Disconnect Bus SAGSFT3_2.21 (527605) 0.70 kV b. 4. Disconnect Bus GRDXFR4 1 (527606) 0.50 kV b. 5. Disconnect Bus SAGSFT4_2.21 (527607) 0.70 kV b. 6. Disconnect Bus SUB BUS #3 1 (527608) 34.5 kV b. 7. Disconnect Bus SUB BUS #4 1 (527609) 34.5 kV b. 8. Disconnect Bus GRDXFR1 1 (527613) 0.5 kV b. 9. Disconnect Bus SAGSFT1_2.21 (527614) 0.70 kV b. 10. Disconnect Bus SAGSFT1_2.01 (527615) 0.70 kV b. 11. Disconnect Bus GRDXFR2 1 (527616) 0.5 kV b. 12. Disconnect Bus SAGSFT2_2.21 (527617) 0.70 kV b. 13. Disconnect Bus SAGSFT2_2.01 (527618) 0.70 kV b. 14. Clear fault at Bus CROSSROADS 7 (527656) 345 kV b. 15. Drop Load 1 Bus SAGA_SCOL 7 (527610) 345 kV b. 16. Drop Load 2 Bus SAGA_SCOL 7 (527610) 345 kV b. 17. Disconnect Bus SAGA_NDCOL 7 (527598) 345 kV b. 18. Disconnect Bus SAGA_SDCOL 7 (527599) 345 kV b. 19. Disconnect Bus SAGA_SMEAS 7 (527600) 345 kV b. 20. Disconnect Bus SAGA_NCOL 7 (527601) 345 kV b. 21. Disconnect Bus SAGANCOL1 1 (527602) 34.5 kV b. 22. Disconnect Bus SAGANCOL2 1 (527603) 34.5 kV b. 23. Disconnect Bus GRDXFR3 1 (527604) 0.50 kV b. 24. Disconnect Bus SAGA_SCOL 7 (527610) 345 kV b. 25. Disconnect Bus SAGASCOL1 1 (527611) 34.5 kV b. 26. Disconnect Bus SAGASCOL2 1 (527612) 34.5 kV b. 27. Disconnect Bus SAGA_NCLTR31 (527621) 13.8 kV b. 28. Disconnect Bus SAGA_NCLTR41 (527622) 13.8 kV b. 29. Disconnect Bus SAGA_SCLTR11 (527623) 13.8 kV b. 30. Disconnect Bus SAGA_SCLTR21 (527624) 13.8 kV b. 31. Disconnect Bus SUB BUS #1 (527628) 34.5 kV b. 32. Disconnect Bus SUB BUS #2 (527629) 34.5 kV | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0412_P4 | a. Apply single-phase fault at CHINA_DRAW 7 (528223) 345 kV Bus CB 4T805 Stuck b. Clear Fault after 16 cycles: b. 1. Trip branch from CHINA_DRAW 7 (528223) 345 kV Bus TO PHANTOM 7 (528015) 345 kV Bus CKT 1 b. 2. Disconnect Bus CHINA_DRAW 1 (528219) 13.2 kV b. 3. Disconnect Bus CARPENTER 7 (523823) 345 kV | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0413_P4 | a. Apply single-phase fault at CHINA_DRAW 7 (528223) 345 kV Bus CB TF#### Stuck b. 1. Run for 5 cycles, Disconnect Bus CHINA_DRAW 1 (528219) 13.2 kV b. 2. Run for 11 cycles, Trip branch from CHINA_DRAW 7 (528223) 345 kV Bus TO N_LOVING 7 (528185) 345 kV Bus CKT 1 b. 3. Clear fault and run for 5 cycles, Trip branch from CHINA_DRAW 7 (528223) 345 kV Bus TO PHANTOM 7 (528015) 345 kV Bus CKT 1 b. 4. Disconnect Bus CHINA_DRAW 1 (528219) 13.2 kV b. 5. Disconnect Bus CARPENTER 7 (523823) 345 kV | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0414_P4 | a. Apply single-phase fault at CHINA_DRAW 7 (528223) 345 kV Bus CB J27#### Stuck b. 1. Run for 16 cycles, Disconnect Bus CHINA_DRAW 1 (528219) 13.2 kV b. 2. Clear fault and run for 5 cycles: b. 3. Trip branch from CHINA_DRAW 7 (528223) 345 kV Bus TO N_LOVING 7 (528185) 345 kV Bus CKT 1 b. 4. Trip branch from CHINA_DRAW 7 (528223) 345 kV Bus TO PHANTOM 7 (528015) 345 kV Bus CKT 1 b. 5. Disconnect Bus CHINA_DRAW 1 (528219) 13.2 kV b. 6. Disconnect Bus CARPENTER 7 (523823) 345 kV | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0415_P4 | a. Apply single-phase fault at EDDY_CNTY 7 (527802) 345 kV Bus CB 4R00 Stuck b. 1. Run for 16 cycles, Trip branch from EDDY_CNTY 7 (527802) 345 kV Bus TO KIOWA 7 (527965) 345 kV Bus CKT 1 b. 2. Clear fault and run for 5 cycles, Trip branch from EDDY_CNTY 7 (527802) 345 kV Bus TO CROSSROADS 7 (527656) 345 kV Bus CKT 1 b. 3. Disconnect Bus EDDY_TR 1 (527796) 13.2 kV b. 4. Disconnect Bus EDDY_CNTY 7 (527802) 345 kV | P4 | Yes | Yes | Yes | No | Yes | Yes | No | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points) |  | Generator relays were disabled for the following generators: 763309 [G18-112-GEN10.6600]
05 - Southwest | 25S | Transfer | Group5_Fault_0416_P4 | a. Apply single-phase fault at EDDY_CNTY 7 (527802) 345 kV Bus CB J24#### Stuck b. 1. Run for 16 cycles, Disconnect Bus EDDY_TR 1 (527796) 13.2 kV b. 2. Clear fault and run for 5 cycles: b. 3. Trip branch from EDDY_CNTY 7 (527802) 345 kV Bus TO CROSSROADS 7 (527656) 345 kV Bus CKT 1 b. 4. Trip branch from EDDY_CNTY 7 (527802) 345 kV Bus TO KIOWA 7 (527965) 345 kV Bus CKT 1 b. 5. Disconnect Bus EDDY_TR 1 (527796) 13.2 kV b. 6. Disconnect Bus EDDY_CNTY 7 (527802) 345 kV | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0417_P4 | a. Apply single-phase fault at EDDY_CNTY 7 (527802) 345 kV Bus CB TF#### Stuck b. 1. Run for 5 cycles, Disconnect Bus EDDY_TR 1 (527796) 13.2 kV b. 2. Run for 11 cycles, Trip branch from EDDY_CNTY 7 (527802) 345 kV Bus TO CROSSROADS 7 (527656) 345 kV Bus CKT 1 b. 3. Clear fault and run for 5 cycles, Trip branch from EDDY_CNTY 7 (527802) 345 kV Bus TO KIOWA 7 (527965) 345 kV Bus CKT 1 b. 4. Disconnect Bus EDDY_TR 1 (527796) 13.2 kV b. 5. Disconnect Bus EDDY_CNTY 7 (527802) 345 kV | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0418_P4 | a. Apply single-phase fault at FINNEY 7 (523853) 345 kV Bus CB OR70 Stuck b. Clear Fault after 21 cycles: b. 1. Trip branch from HOLCOMB7 (531449) 345 kV Bus TO FINNEY 7 (523853) 345 kV Bus CKT 1 b. 2. Trip branch from CARPENTER 7 (523823) 345 kV TO FINNEY 7 (523853) 345 kV Bus CKT 1 b. 3. Disconnect Bus 523853 b. 4. Disconnect Bus 599950 b. 5. Disconnect Bus 599951 b. 6. Disconnect Bus 523118 b. 7. Disconnect Bus 523114 b. 8. Disconnect Bus 523115 b. 9. Disconnect Bus 523116 b. 10. Disconnect Bus 523117 b. 11. Drop Generator 1 Bus 523061 b. 12. Drop Generator 1 Bus 523062 b. 13. Disconnect Bus 523061 b. 14. Disconnect Bus 523062 b. 15. Disconnect Bus 523063 b. 16. Disconnect Bus 523064 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | Group5_Fault_0419_P4 | a. Apply single-phase fault at HITCHLAND 7 (523097) 345 kV Bus CB 1R75 Stuck b. Clear Fault after 21 cycles: b. 1. Trip branch from HITCHLAND 7 (523097) 345 kV Bus TO BVRCNTY7 (515554) 345 kV Bus CKT 2 b. 2. Disconnect Bus 523112 b. 3. Disconnect Bus 523111 b. 4. Disconnect Bus 523109 b. 5. Disconnect Bus 523107 b. 6. Disconnect Bus 523110 b. 7. Drop Generator 1 Bus 523107 b. 8. Drop Load A1 Bus 523107 b. 9. Drop Generator 1 Bus 560585 b. 10. Drop Generator 1 Bus 560586 b. 11. Disconnect Bus 560577 b. 12. Disconnect Bus 560582 b. 13. Disconnect Bus 560585 b. 14. Disconnect Bus 560583 b. 15. Disconnect Bus 560586 b. 16. Disconnect Bus 560578 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0420_P4 | a. Apply single-phase fault at HOBBS_INT 7 (527896) 345 kV Bus CB 4R240 Stuck b. Clear Fault after 21 cycles: b. 1. Trip branch from HOBBS_INT 7 (527896) 345 kV Bus TO KIOWA 7 (527965) 345 kV Bus CKT 1 b. 2. Trip branch from HOBBS_INT 7 (527896) 345 kV Bus TO YOAKUM_345 (526936) 345 kV Bus CKT 1 b. 3. Disconnect Bus HOBBS_TR3 1 (527895) 13.2 kV b. 4. Disconnect Bus HOBBS_INT 7 (527896) 345 kV | P4 | Yes | Yes | Yes | No | Yes | Yes | No | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points) |  | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000], 761358 [G17-239-GEN10.6900], 761361 [G17-239-GEN20.6900], 761799 [G17-187GEN1 0.6900], 761802 [G17-187GEN2 0.6900], 763084 [G18-073-GEN20.6600], 763090 [G18-073-GEN10.6600]
05 - Southwest | 25S | Transfer | Group5_Fault_0421_P4 | a. Apply single-phase fault at KIOWA 7 (527965) 345 kV Bus CB TF#### Stuck b. 1. Run for 5 cycles, Disconnect Bus KIOWA_TR1 1 (527964) 13.2 kV b. 2. Clear fault and run for 16 cycles, Trip branch from KIOWA 7 (527965) 345 kV TO RDRUNNER 7 (528027) Bus CKT 1 b. 3. Disconnect Bus KIOWA_TR1 1 (527964) 13.2 kV | P4 | Yes | Yes | Yes | No | Yes | No | No | Damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000], 523941 [MAJSTC-WTG110.6900], 523942 [MAJSTC-WTG210.6900], 523942 [MAJSTC-WTG210.6900], 761358 [G17-239-GEN10.6900], 761361 [G17-239-GEN20.6900], 761799 [G17-187GEN1 0.6900], 761802 [G17-187GEN2 0.6900], 763084 [G18-073-GEN20.6600], 763090 [G18-073-GEN10.6600], 584563 [G15-014-GE170.6900], 584564 [G15-014-GE200.6900], 584565 [G15-014-GE230.6900]
05 - Southwest | 25S | Transfer | Group5_Fault_0422_P4 | a. Apply single-phase fault at KIOWA 7 (527965) 345 kV Bus CB J23#### Stuck b. 1. Clear fault and run for 16 cycles, Trip branch from KIOWA 7 (527965) 345 kV TO RDRUNNER 7 (528027) Bus CKT 1 b. 2. Disconnect Bus KIOWA_TR1 1 (527964) 13.2 kV | P4 | Yes | Yes | Yes | No | Yes | No | No | Damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000], 523941 [MAJSTC-WTG110.6900], 523942 [MAJSTC-WTG210.6900], 523942 [MAJSTC-WTG210.6900], 761358 [G17-239-GEN10.6900], 761361 [G17-239-GEN20.6900], 761799 [G17-187GEN1 0.6900], 761802 [G17-187GEN2 0.6900], 763084 [G18-073-GEN20.6600], 763090 [G18-073-GEN10.6600], 584226 [G14-040-GEN20.6900], 584563 [G15-014-GE170.6900], 584564 [G15-014-GE200.6900]
05 - Southwest | 25S | Transfer | Group5_Fault_0423_P4 | a. Apply single-phase fault at N_LOVING (528185) 345 kV Bus CB 4S120 Stuck b. 1. Run for 16 cycles, Trip branch from N_LOVING (528185) 345 kV TO CHINA_DRAW 7 (528223) 345 kV Bus CKT 1 b. 2. Clear fault and run for 5 cycles, Trip branch from N_LOVING (528185) 345 kV TO KIOWA 7 (527965) 345 kV CKT 1 b. 3. Disconnect Bus N_LOVING TR1 (528186) 13.2 kV b. 4. Disconnect Bus N_LOVING (528185) 345 kV | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0424_P4 | a. Apply single-phase fault at N_LOVING (528185) 345 kV Bus CB 4S110 Stuck b. 1. Run for 5 cycles, Disconnect Bus N_LOVING TR1 (528186) 13.2 kV b. 2. Run for 11 cycles, Trip branch from N_LOVING (528185) 345 kV TO KIOWA 7 (527965) 345 kV CKT 1 b. 3. Clear fault and run for 5 cycles, Trip branch from N_LOVING (528185) 345 kV TO CHINA_DRAW 7 (528223) 345 kV Bus CKT 1 b. 4. Disconnect Bus N_LOVING (528185) 345 kV | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0425_P4 | a. Apply single-phase fault at N_LOVING (528185) 345 kV Bus CB 4S110 Stuck b. 1. Run for 16 cycles, Disconnect Bus N_LOVING TR1 (528186) 13.2 kV b. 2. Clear fault and run for 5 cycles: b. 3. Trip branch from N_LOVING (528185) 345 kV TO CHINA_DRAW 7 (528223) 345 kV Bus CKT 1 b. 4. Trip branch from N_LOVING (528185) 345 kV TO KIOWA 7 (527965) 345 kV CKT 1 b. 5. Disconnect Bus N_LOVING TR1 (528186) 13.2 kV b. 6. Disconnect Bus N_LOVING (528185) 345 kV | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0426_P4 | a. Apply single-phase fault at POTTER_CO 7 (523961) 345 kV Bus CB 2R05 Stuck b. Clear Fault after 21 cycles: b. 1. Trip branch from HITCHLAND 7 (523097) 345 kV Bus TO POTTER_CO 7 (523961) 345 kV Bus CKT 1 b. 2. Disconnect bus 523957 b. 3. Disconnect bus 523957 b. 4. Disconnect bus 523961 b. 5. Disconnect bus 524296 b. 6. Disconnect bus 524299 b. 7. Disconnect bus 524298 b. 8. Disconnect bus 524294 b. 9. Disconnect bus 524295 b. 10. Disconnect bus 524297 | P4 | Yes | Yes | Yes | No | Yes | No | No | Damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000], 523941 [MAJSTC-WTG110.6900], 523942 [MAJSTC-WTG210.6900], 523942 [MAJSTC-WTG210.6900], 761358 [G17-239-GEN10.6900], 761361 [G17-239-GEN20.6900], 761799 [G17-187GEN1 0.6900], 761802 [G17-187GEN2 0.6900], 763084 [G18-073-GEN20.6600], 763090 [G18-073-GEN10.6600], 523971 [HARRNGTON1 124.000], 523942 [MAJSTC-WTG210.6900], 523942 [MAJSTC-WTG210.6900]
05 - Southwest | 25S | Transfer | Group5_Fault_0427_P4 | a. Apply single-phase fault at RDRUNNER 7 (528027) 345 kV Bus CB J23#### Stuck b. 1. Run for 16 cycles, Trip branch from RDRUNNER 7(528027) 345 kV TO PHANTOM 7 (528015) 345 kV Bus CKT 1 b. 2. Clear fault and run for 5 cycles, Trip branch from KIOWA 7 (527965) 345 kV TO RDRUNNER 7 (528027) Bus CKT 1 b. 3. Disconnect Bus RDRNNER_TR11 (528023) 13.2 kV b. 4. Disconnect Bus RDRUNNER 7(528027) 345 kV | P4 | Yes | Yes | Yes | No | Yes | No | No | Damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000], 523941 [MAJSTC-WTG110.6900], 523942 [MAJSTC-WTG210.6900], 523942 [MAJSTC-WTG210.6900], 761358 [G17-239-GEN10.6900], 761361 [G17-239-GEN20.6900], 761799 [G17-187GEN1 0.6900], 761802 [G17-187GEN2 0.6900], 763084 [G18-073-GEN20.6600], 763090 [G18-073-GEN10.6600], 762463 [G18-015-GEN10.6600], 584563 [G15-014-GE170.6900], 584564 [G15-014-GE200.6900], 584565 [G15-014-GE230.6900]
05 - Southwest | 25S | Transfer | Group5_Fault_0428_P4 | a. Apply single-phase fault at RDRUNNER 7 (528027) 345 kV Bus CB #### Stuck b. 1. Run for 5 cycles, Disconnect Bus RDRNNER_TR11 (528023) 13.2 kV b. 2. Run for 11 cycles, Trip branch from KIOWA 7 (527965) 345 kV TO RDRUNNER 7 (528027) Bus CKT 1 b. 3. Clear fault and run for 5 cycles, Trip branch from RDRUNNER 7(528027) 345 kV TO PHANTOM 7 (528015) 345 kV Bus CKT 1 b. 4. Disconnect Bus RDRUNNER 7(528027) 345 kV | P4 | Yes | Yes | Yes | No | Yes | No | Yes | Damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer
05 - Southwest | 25S | Transfer | Group5_Fault_0429_P4 | a. Apply single-phase fault at RDRUNNER 7 (528027) 345 kV Bus CB J22#### Stuck b. 1. Run for 16 cycles, Disconnect Bus RDRNNER_TR11 (528023) 13.2 kV b. 2. Clear fault and run for 5 cycles: b. 3. Trip branch from RDRUNNER 7(528027) 345 kV TO PHANTOM 7 (528015) 345 kV Bus CKT 1 b. 4. Trip branch from KIOWA 7 (527965) 345 kV TO RDRUNNER 7 (528027) Bus CKT 1 b. 5. Disconnect Bus RDRUNNER 7(528027) 345 kV | P4 | Yes | Yes | Yes | No | Yes | No | No | Damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000], 523941 [MAJSTC-WTG110.6900], 523942 [MAJSTC-WTG210.6900], 523942 [MAJSTC-WTG210.6900], 761358 [G17-239-GEN10.6900], 761361 [G17-239-GEN20.6900], 761799 [G17-187GEN1 0.6900], 761802 [G17-187GEN2 0.6900], 763084 [G18-073-GEN20.6600], 763090 [G18-073-GEN10.6600], 584563 [G15-014-GE170.6900], 584564 [G15-014-GE200.6900], 584565 [G15-014-GE230.6900]
05 - Southwest | 25S | Transfer | Group5_Fault_0430_P4 | a. Apply single-phase fault at YOAKUM_345 (526936) 345 kV Bus CB J18#### Stuck b. 1. Run for 16 cycles, Trip branch from YOAKUM_345 (526936) 345 kV Bus TO TUCO_INT 7 (525832) 345 kV Bus CKT 1 b. 2. Clear fault and run for 5 cycles, Tri branch from YOAKUM_345 (526936) 345 kV Bus TO HOBBS_INT 7 (527896) 345 kV Bus CKT 1 b. 3. Disconnect Bus YOAKUM_TR1 (526937) 13.2 kV b. 4. Disconnect Bus YOAKUM_345 (526936) 345 kV | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0431_P4 | a. Apply single-phase fault at YOAKUM_345 (526936) 345 kV Bus CB TF##### Stuck b. 1. Run for 5 cycles, Disconnect Bus YOAKUM_TR1 (526937) 13.2 kV b. 2. Run for 11 cycles, Trip branch from YOAKUM_345 (526936) 345 kV Bus TO HOBBS_INT 7 (527896) 345 kV Bus CKT 1 b. 3. Clear fault and run for 5 cycles, Trip branch from YOAKUM_345 (526936) 345 kV Bus TO TUCO_INT 7 (525832) 345 kV Bus CKT 1 b. 4. Disconnect Bus YOAKUM_345 (526936) 345 kV | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0432_P4 | a. Apply single-phase fault at YOAKUM_345 (526936) 345 kV Bus CB J17#### Stuck b. 1. Run for 16 cycles, Disconnect Bus YOAKUM_TR1 (526937) 13.2 kV b. 2. Clear fault and run for 5 cycles: b. 3. Trip branch from YOAKUM_345 (526936) 345 kV Bus TO TUCO_INT 7 (525832) 345 kV Bus CKT 1 b. 4. Trip branch from YOAKUM_345 (526936) 345 kV Bus TO HOBBS_INT 7 (527896) 345 kV Bus CKT 1 b. 5. Disconnect Bus YOAKUM_345 (526936) 345 kV | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0433_P4 | a. Apply single-phase fault at TUCO_INT 7 (525832) 345 kV Bus CB NR20 Stuck b. 1. Run for 5 cycles, Disconnect Bus TUCO_TR1 1 (525824) 13.2 kV b. 2. Clear fault and run for 11 cycles, Trip branch from TUCO_INT 7 (525832) 345 kV Bus TO CRAWFISH_DR (560022) 345 kV Bus CKT 1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0434_P4 | a. Apply single-phase fault at MUSTANG 3 (527146) 115 kV Bus b. 1. Run for 5 cycles, Disconnect Bus MUSTANG_2 1 (527162) 13.2 kV b. 2. Clear fault and run for 11 cycles, Trip branch from SEAGRAVES 3 (527202) 115 kV Bus TO MUSTANG 3 (527146) 115 kV Bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | Group5_Fault_0435_P4 | a. Apply SLG fault at NICHOLS 6 (524044) 230 kV Bus b. Clear Fault after 21 cycles: b. 1. Trip branch from NICHOLS (523978) 230 kV Bus TO NICHOLS 6 (524044) 230 kV Bus CKT 2 b. 2. Trip branch from HUTCHISON 6 (523551) 230 kV Bus TO NICHOLS 6 (524044) 230 kV Bus CKT 1 | P4 | Yes | Yes | Yes | No | Yes | Yes | No | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points) |  | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000], 523941 [MAJSTC-WTG110.6900], 523942 [MAJSTC-WTG210.6900], 523942 [MAJSTC-WTG210.6900], 761358 [G17-239-GEN10.6900], 761361 [G17-239-GEN20.6900], 761799 [G17-187GEN1 0.6900], 761802 [G17-187GEN2 0.6900], 763084 [G18-073-GEN20.6600], 763090 [G18-073-GEN10.6600]
05 - Southwest | 25S | Transfer | Group5_Fault_0436_P4 | a. Apply single-phase fault at NICHOLS 6 (524044) 230 kV Bus b. 1. Run for 5 cycles, Disconnect Bus NICHOLS_TR11 (524041) 13.2 kV b. 2. Clear fault and run for 11 cycles, Disconnect Bus from NICHOLS_3 1 (524023) 22 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25S | Transfer | Group5_Fault_0437_P4 | a. Apply single-phase fault at POTTER_CO 6 (523959) 230 kV Bus b. Clear Fault after 21 cycles: b. 1. Trip branch from POTTER_CO 6 (523959) 230 kV Bus TO BUSHLAND 6 (524267) 230 kV Bus CKT 1 b. 2. Trip branch from POTTER_CO 6 (523959) 230 kV Bus TO ROLLHILLS 6 (524010) 230 kV Bus CKT 1 | P4 | Yes | Yes | Yes | No | Yes | Yes | No | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points) |  | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25S | Transfer | Group5_Fault_0438_P4 | a. Apply single-phase fault at YOAKUM 6 (526935) 230 kV Bus b. 1. Run for 5 cycles, Disconnect Bus YOAKUM_TR1 1 (526931) 13.2 kV b. 2. Clear fault and run for 11 cycles, Trip branch from YOAKUM 6 (526935) 230 kV Bus TO NEEDMORE 6 (525586) 230 kV Bus CKT 1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0439_P4 | a. Apply single-phase fault at TUCO_INT 7 (525832) 345 kV Bus b. Clear Fault after 21 cycles: b. 1. Trip branch from TUCO_INT 7 (525832) 345 kV Bus TO CRAWFISH_DR (560022) 345 kV Bus CKT 1 b. 2. Disconnect Bus TUCO_TR1 1 (525824) 13.2 kV | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0440_P4 | a. Apply single-phase fault at TUCO_INT 7 (525832) 345 kV Bus b. Clear Fault after 21 cycles: b. 1. Trip branch from TUCO_INT 7 (525832) 345 kV Bus TO CRAWFISH_DR (560022) 345 kV Bus CKT 1 b. 2. Disconnect Bus TUCO_TR2 1 (525825) 13.2 kV | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0441_P4 | a. Apply single-phase fault at TUCO_INT 7 (525832) 345 kV Bus b. 1. Run for 5 cycles, Disconnect Bus TUCO_TR2 1 (525825) 13.2 kV b. 2. Clear fault and run for 11 cycles, Trip branch from TUCO_INT 7 (525832) 345 kV Bus TO CRAWFISH_DR (560022) 345 kV Bus CKT 1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0442_P4 | a. Apply single-phase fault at HITCHLAND 7 (523097) 345 kV Bus b. 1. Run for 5 cycles, Disconnect Bus HITCHLD_TR01 (523091) 13.2 kV b. 2. Clear fault and run for 11 cycles, Disconnect Bus HITCHLD_TR01 (523091) 13.2 kV | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0443_P4 | a. Apply single-phase fault at POTTER_CO 7 (523961) 345 kV Bus b. 1. Run for 5 cycles, Disconnect Bus POTTER_TR 1 (523957) 13.2 kV b. 2. Clear fault and run for 11 cycles, Disconnect Bus POTTER_TR 1 (523957) 13.2 kV b. 3. Run for 5 cycles: b. 4. Trip branch from HITCHLAND 7 (523097) 345 kV Bus TO POTTER_CO 7 (523961) 345 kV Bus CKT 1 b. 5. Disconnect bus 523957 b. 6. Disconnect bus 523961 b. 7. Disconnect bus 524296 b. 8. Disconnect bus 524299 b. 9. Disconnect bus 524298 b. 10. Disconnect bus 524294 b. 11. Disconnect bus 524295 b. 12. Disconnect bus 524297 | P4 | Yes | Yes | Yes | No | Yes | No | No | Damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000], 523941 [MAJSTC-WTG110.6900], 523942 [MAJSTC-WTG210.6900], 523942 [MAJSTC-WTG210.6900], 761358 [G17-239-GEN10.6900], 761361 [G17-239-GEN20.6900], 761799 [G17-187GEN1 0.6900], 761802 [G17-187GEN2 0.6900], 763084 [G18-073-GEN20.6600], 763090 [G18-073-GEN10.6600]
05 - Southwest | 25S | Transfer | Group5_Fault_0444_P4 | a. Apply single-phase fault at BUSHLAND 6 (524267) 230 kV Bus b. 1. Run for 5 cycles, Drop Shunt 1 BUSHLAND 6 (524267) 230 kV Bus b. 2. Run for 11 cycles, Disconnect Bus BUSHLAND 6 (524267) 230 kV b. 3. Disconnect Bus WILDORA_GEN1 (524285) 0.69 kV b. 4. Disconnect Bus GS-PHWD_GEN1 (524287) 0.69 kV b. 5. Clear fault at BUSHLAND 6 (524267) 230 kV b. 6. Disconnect Bus BSHLND_TR1 1 (524263) 13.2 kV b. 7. Disconnect Bus WILDOR_WND 1 (524275) 34.5 kV b. 8. Disconnect Bus WILDOR_WND 6 (524276) 230 kV b. 9. Disconnect Bus GS-PHWDRNCH1 (524289) 34.5 kV b. 10. Disconnect Bus WILDOR2_JUS6 (524290) 230 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | Group5_Fault_0445_P4 | a. Apply single-phase fault at SWISHER 6 (525213) 230 kV b. 1. Run for 5 cycles, Drop Shunt 1 SWISHER 6 (525213) 230 kV b. 2. Clear fault and run for 11 cycles, Trip branch from SWISHER 6 (525213) 230 kV Bus TO TUCO_INT 6 (525830) 230 kV Bus CKT 1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0446_P4 | a. Apply single-phase fault at TUCO_INT 6 (525830) 230 kV b. 1. Run for 5 cycles, Drop Shunt 1 TUCO_INT 6 (525830) 230 kV b. 2. Clear fault and run for 11 cycles, Disconnect BusTUCO_TR3 1 (525819) 13.2 kV | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0447_P4 | a. Apply single-phase fault at BUSHLAND 6 (524267) 230 kV Bus b. Clear Fault after 5 cycles: b. 1. Trip branch from BUSHLAND 6 (524267) 230 kV Bus TO WILDOR2_JUS6 (524290) 230 kV Bus CKT 1 b. 2. Drop Shunt 1 BUSHLAND 6 (524267) 230 kV Bus b. 3. Disconnect Bus BSHLND_TR1 1 (524263) 13.2 kV b. 4. Disconnect Bus WILDORA_GEN1 (524285) 0.69 kV b. 5. Disconnect Bus GS-PHWD_GEN1 (524287) 0.69 kV b. 6. Trip branch from BUSHLAND 6 (524267) 230 kV Bus TO POTTER_CO 6 (523959) 230 kV Bus CKT 1 b. 7. Clear Fault after 16 cycles: b. 8. Trip branch from BUSHLAND 6 (524267) 230 kV Bus TO DEAFSMITH 6 (524623) 230 kV Bus CKT 1 b. 9. Disconnect Bus WILDOR_WND 1 (524275) 34.5 kV b. 10. Disconnect Bus WILDOR_WND 6 (524276) 230 kV b. 11. Disconnect Bus GS-PHWDRNCH1 (524289) 34.5 kV b. 12. Disconnect Bus WILDOR2_JUS6 (524290) 230 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | Group5_Fault_0448_P4 | a. Apply single-phase fault at HARRNG_WST 6 (523977) 230 kV Bus b. Clear Fault after 16 cycles: b. 1. Trip branch from HARRNG_WST 6 (523977) 230 kV Bus TO ROLLHILLS 6 (524010) 230 kV Bus CKT 1 b. 2. Trip branch from HARRNG_WST 6 (523977) 230 kV Bus TO EAST_PLANT 6 (524163) 230 kV Bus CKT 1 b. 3. Trip branch from HARRNG_WST 6 (523977) 230 kV Bus TO NICHOLS 6 (524044) 230 kV Bus CKT 1 b. 4. Disconnect Bus HARRNG_WST 6 (523977) 230 kV b. 5. Disconnect Bus HARRNGTON1 1 (523971) 24 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25S | Transfer | Group5_Fault_0449_P4 | a. Apply single-phase fault at HARRNG_MID 6 (523978) 230 kV Bus b. Clear Fault after 16 cycles: b. 1. Trip branch from HARRNG_MID 6 (523978) 230 kV Bus TO RANDALL 6 (524365) 230 kV Bus CKT 1 b. 2. Trip branch from HARRNG_MID 6 (523978) 230 kV Bus TO NICHOLS 6 (524044) 230 kV Bus CKT 2 b. 3. Disconnect Bus HARRNG_MID 6 (523978) 230 kV b. 4. Disconnect Bus HARRNGTON2 1 (523972) 24 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000], 763309 [G18-112-GEN10.6600]
05 - Southwest | 25S | Transfer | Group5_Fault_0450_P4 | a. Apply single-phase fault at HARRNG_EST 6 (523979) 230 kV Bus b. Clear Fault after 16 cycles: b. 1. Trip branch from HARRNG_EST 6 (523979) 230 kV Bus TO PRINGLE 6 (523267) 230 kV Bus CKT 1 b. 2. Trip branch from HARRNG_EST 6 (523979) 230 kV Bus TO POTTER_CO 6 (523959) 230 kV Bus CKT 1 b. 3. Disconnect Bus HARRNG_EST 6 (523979) 230 kV b. 4. Disconnect Bus HARRNGTON3 1 (523973) 24 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000], 763397 [G18-124-GEN10.6600], 763309 [G18-112-GEN10.6600]
05 - Southwest | 25S | Transfer | Group5_Fault_0451_P4 | a. Apply single-phase fault at JONES 6 (526337) 230 kV b. 1. Clear fault and run for 18 cycles, Disconnect Bus from JONES 6 (526337) 230 kV b. 2. Disconnect Bus from JONES_1 1 (526331) 22 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | Group5_Fault_0452_P4 | a. Apply single-phase fault at HARRNG_MID 6 (523978) 230 kV b. 1. Clear fault and run for 5 cycles, Disconnect Bus from HARRNG_MID 6 (523978) 230 kV b. 2. Drop Generator 1 Bus 523972 b. 3. Drop Load S1 Bus 523972 b. 4. Disconnect Bus 523972 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25S | Transfer | Group5_Fault_0453_P4 | a. Apply single-phase fault at MOORE_E 3 (523308) 115 kV b. 1. Clear fault and run for 5 cycles, Disconnect Bus from MOORE_E 3 (523308) 115 kV b. 2. Drop Generator 1 Bus 523297 b. 3. Drop Generator 3 Bus 523301 b. 4. Drop Load F1 Bus 523297 b. 5. Drop Load 1 Bus 523301 b. 6. Drop Load A3 Bus 523301 b. 7. Disconnect Bus 523294 b. 8. Disconnect Bus 523295 b. 9. Disconnect Bus 523296 b. 10. Disconnect Bus 523297 b. 11. Disconnect Bus 523301 b. 12. Disconnect Bus 523302 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0454_P4 | a. Apply single-phase fault at O.K.U.-7 (762467) 345 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from G18-092 TAP (763215) 345 kV Bus TO G18-015 TAP (762467) 345 kV Bus Ckt 1 b. 2. Trip branch from G17-151 (762216) 345 kV Bus TO G18-015 TAP (762467) 345 kV Bus Ckt 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | Group5_Fault_0001_P1 | 3 phase fault on NEWHART 6 (525461) 230 kV Bus a. Apply Fault at the NEWHART 6 (525461) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from NEWHART 6 (525461) 230 kV Bus to PLANT_X 6 (525481) 230 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | No | No | Damping issues observed. Low voltage ride through fails due to the tripping of G18-115-GEN10 and G18-115-GEN20 units. No cascading was observed and the issue was localised. Model tuning is recommended. | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25W | Transfer | Group5_Fault_0002_P1 | 3 phase fault on PLANT_X 6 (525481) 230 kV Bus a. Apply Fault at the PLANT_X 6 (525481) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from PLANT_X 6 (525481) 230 kV Bus to TOLK 6 (525531) 230 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | No | No | No | No | Yes | No | No | Out Of Step Generators and damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25W | Transfer | Group5_Fault_0003_P1 | 3 phase fault on PLANT_X 6 (525481) 230 kV Bus a. Apply Fault at the PLANT_X 6 (525481) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from PLANT_X 6 (525481) 230 kV Bus to TOLK 6 (525531) 230 kV Bus CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | No | No | No | Yes | No | No | No | Out Of Step Generators and damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25W | Transfer | Group5_Fault_0004_P1 | 3 phase fault on PLANT_X 6 (525481) 230 kV Bus a. Apply Fault at the PLANT_X 6 (525481) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from PLANT_X 6 (525481) 230 kV Bus to SUNDOWN 6 (526435) 230 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | No | No | No | No | Yes | No | Yes | Out Of Step Generators and damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer
05 - Southwest | 25W | Transfer | Group5_Fault_0005_P1 | 3 phase fault on PLANT_X 6 (525481) 230 kV Bus a. Apply Fault at the PLANT_X 6 (525481) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from PLANT_X 6 (525481) 230 kV Bus to G17-146-TAP (760498) 230 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | No | No | No | No | Yes | No | No | Out Of Step Generators and damping issues observed | Potter to Tolk 345 kV Double Circuit Line Build Potter to Chisholm 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer Potter to Tolk 345 kV | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000], 763397 [G18-124-GEN1], 763309 [G18-112-GEN1]
05 - Southwest | 25W | Transfer | Group5_Fault_0006_P1 | 3 phase fault on PLANT_X 6 (525481) 230 kV Bus a. Apply Fault at the PLANT_X 6 (525481) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from PLANT_X 6 (525481) 230 kV Bus to PLANT_X 3 (525480) 115 kV Bus to PLANTX_TR1 1 (525479) 13.2 kV Bus CKT 1 | P1 | No | No | No | No | No | No | No | Out Of Step Generators and damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25W | Transfer | Group5_Fault_0007_P1 | 3 phase fault on PLANT_X 6 (525481) 230 kV Bus a. Apply Fault at the PLANT_X 6 (525481) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from PLANT_X 6 (525481) 230 kV Bus to PLANT_X 3 (525480) 115 kV Bus to PLANTX_TR2 (525478) 13.2 kV Bus CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25W | Transfer | Group5_Fault_0008_P1 | 3 phase fault on NEWHART 6 (525461) 230 kV Bus a. Apply Fault at the NEWHART 6 (525461) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from NEWHART 6 (525461) 230 kV Bus to POTTER_CO 6 (523959) 230 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | No | No | No | No | Yes | No | No | Out Of Step Generators and damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25W | Transfer | Group5_Fault_0009_P1 | 3 phase fault on NEWHART 6 (525461) 230 kV Bus a. Apply Fault at the NEWHART 6 (525461) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from NEWHART 6 (525461) 230 kV Bus to SWISHER 6 (525213) 230 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | No | No | Damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25W | Transfer | Group5_Fault_0010_P1 | 3 phase fault on NEWHART 6 (525461) 230 kV Bus a. Apply Fault at the NEWHART 6 (525461) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from NEWHART 6 (525461) 230 kV Bus to NEWHART 3 (525460) 115 kV Bus to NEWHART_TR11 (525459) 13.2 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25W | Transfer | Group5_Fault_0011_P1 | 3 phase fault on NEWHART 6 (525461) 230 kV Bus a. Apply Fault at the NEWHART 6 (525461) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from NEWHART 6 (525461) 230 kV Bus to NEWHART 3 (525460) 115 kV Bus to NEWHART_TR21 (525458) 13.2 kV Bus CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25W | Transfer | Group5_Fault_0012_P1 | 3 phase fault on TOLK 6 (525531) 230 kV Bus a. Apply Fault at the TOLK 6 (525531) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from TOLK 6 (525531) 230 kV Bus to ROOSEVELT 6 (524909) 230 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | No | No | No | No | Yes | No | No | Out Of Step Generators and damping issues observed | Potter to Tolk 345 kV Double Circuit Line Build Potter to Chisholm 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer Potter to Tolk 345 kV | Generator relays were disabled for the following generators: 763254 [G18-099-GEN10.6900], 763397 [G18-124-GEN1], 763309 [G18-112-GEN1]
05 - Southwest | 25W | Transfer | Group5_Fault_0013_P1 | 3 phase fault on TOLK 6 (525531) 230 kV Bus a. Apply Fault at the TOLK 6 (525531) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from TOLK 6 (525531) 230 kV Bus to NEEDMORE 6 (525586) 230 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | No | No | No | Yes | No | No | No | Out Of Step Generators and damping issues observed | Potter to Tolk 345 kV Double Circuit Line Build Potter to Chisholm 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer Potter to Tolk 345 kV | Generator relays were disabled for the following generators: 763254 [G18-099-GEN10.6900], 763397 [G18-124-GEN1], 763309 [G18-112-GEN1]
05 - Southwest | 25W | Transfer | Group5_Fault_0014_P1 | 3 phase fault on TOLK 6 (525531) 230 kV Bus a. Apply Fault at the TOLK 6 (525531) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from TOLK 6 (525531) 230 kV Bus to TUCO_INT 6 (525830) 230 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | No | No | No | No | Yes | No | No | Out Of Step Generators and damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 763254 [G18-099-GEN10.6900]
05 - Southwest | 25W | Transfer | Group5_Fault_0015_P1 | 3 phase fault on TOLK 6 (525531) 230 kV Bus a. Apply Fault at the TOLK 6 (525531) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from TOLK 6 (525531) 230 kV Bus to ROOSEVELT 6 (524909) 230 kV Bus CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | No | No | No | Yes | No | No | No | Out Of Step Generators and damping issues observed | Potter to Tolk 345 kV Double Circuit Line Build Potter to Chisholm 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer Potter to Tolk 345 kV | Generator relays were disabled for the following generators: 763254 [G18-099-GEN10.6900], 763397 [G18-124-GEN1], 763309 [G18-112-GEN1]
05 - Southwest | 25W | Transfer | Group5_Fault_0016_P1 | 3 phase fault on SUNDOWN 6 (526435) 230 kV Bus a. Apply Fault at the SUNDOWN 6 (526435) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from SUNDOWN 6 (526435) 230 kV Bus to AMOCO_SS 6 (526460) 230 kV Bus CKT 1 b. 2. Trip branch from AMOCO_SS 6 (526460) 230 kV Bus to YOAKUM 6 (526935) 230 kV Bus CKT 1 b. 3. Drop Load 1 at AMOCO_SS 6 (526460) 230 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | No | No | No | No | Yes | No | Yes | Out Of Step Generators and damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer
05 - Southwest | 25W | Transfer | Group5_Fault_0017_P1 | 3 phase fault on SUNDOWN 6 (526435) 230 kV Bus a. Apply Fault at the SUNDOWN 6 (526435) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from SUNDOWN 6 (526435) 230 kV Bus to WOLFFORTH 6 (526525) 230 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | No | No | No | No | No | No | Yes | Out Of Step Generators and damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer
05 - Southwest | 25W | Transfer | Group5_Fault_0018_P1 | 3 phase fault on SUNDOWN 6 (526435) 230 kV Bus a. Apply Fault at the SUNDOWN 6 (526435) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from SUNDOWN 6 (526435) 230 kV Bus to SUNDOWN 3 (526434) 115 kV Bus to SUNDOWN_TR11 (526432) 13.8 kV Bus CKT 1 | P1 | Yes | No | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25W | Transfer | Group5_Fault_0019_P1 | 3 phase fault on G17-146-TAP (760498) 230 kV Bus a. Apply Fault at the G17-146-TAP (760498) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from G17-146-TAP (760498) 230 kV Bus to DEAFSMITH 6 (524623) 230 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | No | No | No | No | Yes | No | No | Out Of Step Generators and damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25W | Transfer | Group5_Fault_0020_P1 | 3 phase fault on PLANT_X 3 (525480) 115 kV Bus a. Apply Fault at the PLANT_X 3 (525480) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from PLANT_X 3 (525480) 115 kV Bus to MULSHVLY_TP3 (525019) 115 kV Bus CKT 1 b. 2. Trip branch from MULSHVLY_TP3 (525019) 115 kV Bus to MULESHVALLY3 (525018) 115 kV Bus CKT 1 b. 3. Trip branch from MULSHVLY_TP3 (525019) 115 kV Bus to BAILEYCO 3 (525028) 115 kV Bus CKT 1 b. 4. Drop Load 1 at MULESHVALLY3 (525018) 115 kV Bus b. 5. Drop Load 2 at MULESHVALLY3 (525018) 115 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | Group5_Fault_0021_P1 | 3 phase fault on PLANT_X 3 (525480) 115 kV Bus a. Apply Fault at the PLANT_X 3 (525480) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from PLANT_X 3 (525480) 115 kV Bus to RKYFORD_TP 3 (525446) 115 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | Group5_Fault_0022_P1 | 3 phase fault on PLANT_X 3 (525480) 115 kV Bus a. Apply Fault at the PLANT_X 3 (525480) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from PLANT_X 3 (525480) 115 kV Bus to LAMB_CNTY 3 (525636) 115 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | Group5_Fault_0023_P1 | 3 phase fault on PLANT_X 3 (525480) 115 kV Bus a. Apply Fault at the PLANT_X 3 (525480) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from PLANT_X 3 (525480) 115 kV Bus to HALE_CNTY 3 (525454) 115 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | Group5_Fault_0024_P1 | 3 phase fault on PLANT_X 3 (525480) 115 kV Bus a. Apply Fault at the PLANT_X 3 (525480) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from PLANT_X 3 (525480) 115 kV Bus to BC-EARTH 3 (525056) 115 kV Bus CKT 1 b. 2. Trip branch from BC-EARTH 3 (525056) 115 kV Bus to BC-KELLEY +3 (525050) 115 kV Bus CKT 1 b. 3. Trip branch from BC-KELLEY +3 (525050) 115 kV Bus to CASTRO_CNTY3 (524746) 115 kV Bus CKT 1 b. 4. Drop Load 1 at BC-EARTH 3 (525056) 115 kV Bus b. 5. Drop Load 1 at BC-KELLEY +3 (525050) 115 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | Group5_Fault_0025_P1 | 3 phase fault on SWISHER 6 (525213) 230 kV Bus a. Apply Fault at the SWISHER 6 (525213) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from SWISHER 6 (525213) 230 kV Bus to AMA_SOUTH 6 (524415) 230 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | No | Yes | No | Yes | Yes | No | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points) |  | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25W | Transfer | Group5_Fault_0026_P1 | 3 phase fault on SWISHER 6 (525213) 230 kV Bus a. Apply Fault at the SWISHER 6 (525213) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from SWISHER 6 (525213) 230 kV Bus to TUCO_INT 6 (525830) 230 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | No | No | Damping issues observed. Low voltage ride through fails due to the tripping of G18-115-GEN10 and G18-115-GEN20 units. No cascading was observed and the issue was localised. Model tuning is recommended. | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25W | Transfer | Group5_Fault_0027_P1 | 3 phase fault on SWISHER 6 (525213) 230 kV Bus a. Apply Fault at the SWISHER 6 (525213) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from SWISHER 6 (525213) 230 kV Bus to SWISHER 3 (525212) 115 kV Bus to SWISHER_TR11 (525211) 13.2 kV Bus CKT 1 b. 2. Trip branch from SWISHER 3 (525212) 115 kV Bus to KRESS_INT 3 (525192) 115 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25W | Transfer | Group5_Fault_0028_P1 | 3 phase fault on NEWHART 3 (525460) 115 kV Bus a. Apply Fault at the NEWHART 3 (525460) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from NEWHART 3 (525460) 115 kV Bus to CASTRO_CNTY3 (524746) 115 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer
05 - Southwest | 25W | Transfer | Group5_Fault_0029_P1 | 3 phase fault on NEWHART 3 (525460) 115 kV Bus a. Apply Fault at the NEWHART 3 (525460) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from NEWHART 3 (525460) 115 kV Bus to KRESS_INT 3 (525192) 115 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer
05 - Southwest | 25W | Transfer | Group5_Fault_0030_P1 | 3 phase fault on NEWHART 3 (525460) 115 kV Bus a. Apply Fault at the NEWHART 3 (525460) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from NEWHART 3 (525460) 115 kV Bus to HART_INDUST3 (525124) 115 kV Bus CKT 1 b. 2. Trip branch from HART_INDUST3 (525124) 115 kV Bus to LAMTON 3 (525414) 115 kV Bus CKT 1 b. 3. Drop Load 1 at HART_INDUST3 (525124) 115 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | Group5_Fault_0031_P1 | 3 phase fault on ROOSEVELT 6 (524909) 230 kV Bus a. Apply Fault at the ROOSEVELT 6 (524909) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from ROOSEVELT 6 (524909) 230 kV Bus to OASIS 6 (524875) 230 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | Group5_Fault_0032_P1 | 3 phase fault on ROOSEVELT 6 (524909) 230 kV Bus a. Apply Fault at the ROOSEVELT 6 (524909) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from ROOSEVELT 6 (524909) 230 kV Bus to PNM-DC6 (599955) 230 kV Bus CKT @1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | Group5_Fault_0033_P1 | 3 phase fault on ROOSEVELT 6 (524909) 230 kV Bus a. Apply Fault at the ROOSEVELT 6 (524909) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from ROOSEVELT 6 (524909) 230 kV Bus to ROOSEVELT 3 (524908) 115 kV Bus to ROSEVLT_TR11 (524907) 13.2 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | Group5_Fault_0034_P1 | 3 phase fault on ROOSEVELT 6 (524909) 230 kV Bus a. Apply Fault at the ROOSEVELT 6 (524909) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from ROOSEVELT 6 (524909) 230 kV Bus to PLSNT_HILL 6 (524770) 230 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | Group5_Fault_0035_P1 | 3 phase fault on NEEDMORE 6 (525586) 230 kV Bus a. Apply Fault at the NEEDMORE 6 (525586) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from NEEDMORE 6 (525586) 230 kV Bus to YOAKUM 6 (526935) 230 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | Group5_Fault_0036_P1 | 3 phase fault on TUCO_INT 6 (525830) 230 kV Bus a. Apply Fault at the TUCO_INT 6 (525830) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from TUCO_INT 6 (525830) 230 kV Bus to CARLISLE 6 (526161) 230 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 763084 [G18-073-GEN20.6600]
05 - Southwest | 25W | Transfer | Group5_Fault_0037_P1 | 3 phase fault on TUCO_INT 6 (525830) 230 kV Bus a. Apply Fault at the TUCO_INT 6 (525830) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from TUCO_INT 6 (525830) 230 kV Bus to JONES 6 (526337) 230 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 763084 [G18-073-GEN20.6600]
05 - Southwest | 25W | Transfer | Group5_Fault_0038_P1 | 3 phase fault on TUCO_INT 6 (525830) 230 kV Bus a. Apply Fault at the TUCO_INT 6 (525830) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from TUCO_INT 6 (525830) 230 kV Bus to TUCO_INT 3 (525828) 115 kV Bus to TUCO_TR4 1 (525821) 13.2 kV Bus CKT 1 | P1 | No | No | No | No | Yes | No | No | Out Of Step Generators and damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 763084 [G18-073-GEN20.6600]
05 - Southwest | 25W | Transfer | Group5_Fault_0039_P1 | 3 phase fault on TUCO_INT 6 (525830) 230 kV Bus a. Apply Fault at the TUCO_INT 6 (525830) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from TUCO_INT 6 (525830) 230 kV Bus to TUCO_INT 3 (525828) 115 kV Bus to TUCO_TR3 1 (525819) 13.2 kV Bus CKT 2 | P1 | No | No | No | No | Yes | No | No | Out Of Step Generators and damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 763084 [G18-073-GEN20.6600]
05 - Southwest | 25W | Transfer | Group5_Fault_0040_P1 | 3 phase fault on WOLFFORTH 6 (526525) 230 kV Bus a. Apply Fault at the WOLFFORTH 6 (526525) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from WOLFFORTH 6 (526525) 230 kV Bus to CARLISLE 6 (526161) 230 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | No | No | No | No | Yes | No | Yes | Out Of Step Generators and damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer
05 - Southwest | 25W | Transfer | Group5_Fault_0041_P1 | 3 phase fault on WOLFFORTH 6 (526525) 230 kV Bus a. Apply Fault at the WOLFFORTH 6 (526525) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from WOLFFORTH 6 (526525) 230 kV Bus to WOLFFORTH 3 (526524) 115 kV Bus to WOLFRTH_TR11 (526522) 13.2 kV Bus CKT 1 | P1 | No | No | No | No | No | No | Yes | Out Of Step Generators and damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer
05 - Southwest | 25W | Transfer | Group5_Fault_0042_P1 | 3 phase fault on WOLFFORTH 6 (526525) 230 kV Bus a. Apply Fault at the WOLFFORTH 6 (526525) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from WOLFFORTH 6 (526525) 230 kV Bus to LUBBCK_STH 6 (526269) 230 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | No | No | No | No | No | No | Yes | Out Of Step Generators and damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer
05 - Southwest | 25W | Transfer | Group5_Fault_0043_P1 | 3 phase fault on SUNDOWN 3 (526434) 115 kV Bus a. Apply Fault at the SUNDOWN 3 (526434) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from SUNDOWN 3 (526434) 115 kV Bus to AMOCO_TP 3 (526445) 115 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | Group5_Fault_0044_P1 | 3 phase fault on SUNDOWN 3 (526434) 115 kV Bus a. Apply Fault at the SUNDOWN 3 (526434) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from SUNDOWN 3 (526434) 115 kV Bus to LC-OPDYKE 3 (526036) 115 kV Bus CKT 1 b. 2. Trip branch from LC-OPDYKE 3 (526036) 115 kV Bus to HOCKLEY 3 (526020) 115 kV Bus CKT 1 b. 3. Drop Load 1 at LC-OPDYKE 3 (526036) 115 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | Group5_Fault_0045_P1 | 3 phase fault on SUNDOWN 3 (526434) 115 kV Bus a. Apply Fault at the SUNDOWN 3 (526434) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from SUNDOWN 3 (526434) 115 kV Bus to PACIFIC 3 (526424) 115 kV Bus CKT 1 b. 2. Trip branch from PACIFIC 3 (526424) 115 kV Bus to COCHRAN 3 (526361) 115 kV Bus CKT 1 b. 3. Drop Load 1 at PACIFIC 3 (526424) 115 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | Group5_Fault_0046_P1 | 3 phase fault on DEAFSMITH 6 (524623) 230 kV Bus a. Apply Fault at the DEAFSMITH 6 (524623) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from DEAFSMITH 6 (524623) 230 kV Bus to BUSHLAND 6 (524267) 230 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | No | No | No | No | Yes | No | No | Out Of Step Generators and damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25W | Transfer | Group5_Fault_0047_P1 | 3 phase fault on DEAFSMITH 6 (524623) 230 kV Bus a. Apply Fault at the DEAFSMITH 6 (524623) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from DEAFSMITH 6 (524623) 230 kV Bus to DFSMTH_EST 3 (524619) 115 kV Bus to DEFSMTH_TR21 (524621) 13.8 kV Bus CKT 2 b. 2. Trip branch from DFSMTH_EST 3 (524619) 115 kV Bus to TIERABLANCA3 (524630) 115 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | Group5_Fault_0048_P1 | 3 phase fault on LC-OPDYKE 3 (526036) 115 kV Bus a. Apply Fault at the LC-OPDYKE 3 (526036) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from LC-OPDYKE 3 (526036) 115 kV Bus to HOCKLEY 3 (526020) 115 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | Group5_Fault_0049_P1 | 3 phase fault on AMOCO_TP 3 (526445) 115 kV Bus a. Apply Fault at the AMOCO_TP 3 (526445) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from AMOCO_TP 3 (526445) 115 kV Bus to AMOCO_CRYO 3 (526452) 115 kV Bus CKT 1 b. 2. Drop Load 1 at AMOCO_CRYO 3 (526452) 115 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 763309 [G18-112-GEN10.6600]
05 - Southwest | 25W | Transfer | Group5_Fault_0050_P1 | 3 phase fault on AMOCO_TP 3 (526445) 115 kV Bus a. Apply Fault at the AMOCO_TP 3 (526445) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from AMOCO_TP 3 (526445) 115 kV Bus to LG-LEVELAND3 (526484) 115 kV Bus CKT 1 b. 2. Trip branch from LG-LEVELAND3 (526484) 115 kV Bus to LG-CLAUENE 3 (526491) 115 kV Bus CKT 1 b. 3. Trip branch from LG-CLAUENE 3 (526491) 115 kV Bus to TERRY_CNTY 3 (526736) 115 kV Bus CKT 1 b. 4. Drop Load 1 at LG-LEVELAND3 (526484) 115 kV Bus b. 5. Drop Load 1 at LG-CLAUENE 3 (526491) 115 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 763309 [G18-112-GEN10.6600]
05 - Southwest | 25W | Transfer | Group5_Fault_0051_P1 | 3 phase fault on LAMB_CNTY 3 (525636) 115 kV Bus a. Apply Fault at the LAMB_CNTY 3 (525636) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from LAMB_CNTY 3 (525636) 115 kV Bus to HOCKLEY 3 (526020) 115 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | Group5_Fault_0052_P1 | 3 phase fault on LAMB_CNTY 3 (525636) 115 kV Bus a. Apply Fault at the LAMB_CNTY 3 (525636) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from LAMB_CNTY 3 (525636) 115 kV Bus to LAMB_CNTY 2 (525635) 69 kV Bus to LAMB_TR1 1 (525631) 13.2 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | Group5_Fault_0053_P1 | 3 phase fault on LAMB_CNTY 3 (525636) 115 kV Bus a. Apply Fault at the LAMB_CNTY 3 (525636) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from LAMB_CNTY 3 (525636) 115 kV Bus to LAMB_CNTY 2 (525635) 69 kV Bus to LAMB_TR2 1 (525632) 13.2 kV Bus CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | Group5_Fault_0054_P1 | 3 phase fault on CARLISLE 3 (526160) 115 kV Bus a. Apply Fault at the CARLISLE 3 (526160) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from CARLISLE 3 (526160) 115 kV Bus to MURPHY 3 (526192) 115 kV Bus CKT 1 b. 2. Trip branch from MURPHY 3 (526192) 115 kV Bus to QUINCY 3 (526195) 115 kV Bus CKT 1 b. 3. Trip branch from QUINCY 3 (526195) 115 kV Bus to SP-MILWAUKEE (526196) 115 kV Bus CKT 1 b. 4. Trip branch from SP-MILWAUKEE (526196) 115 kV Bus to SP-UPLAND (526198) 115 kV Bus CKT 1 b. 5. Drop Load 1 at MURPHY 3 (526192) 115 kV Bus b. 6. Drop Load D2 at MURPHY 3 (526192) 115 kV Bus b. 7. Drop Load 1 at SP-MILWAUKEE (526196) 115 kV Bus b. 8. Drop Load 1 at SP-UPLAND (526198) 115 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | No | No | Damping issues observed. Low voltage ride through fails due to the tripping of G18-115-GEN10 and G18-115-GEN20 units. No cascading was observed and the issue was localised. Model tuning is recommended. | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer
05 - Southwest | 25W | Transfer | Group5_Fault_0055_P1 | 3 phase fault on POTTER_CO 6 (523959) 230 kV Bus a. Apply Fault at the POTTER_CO 6 (523959) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from POTTER_CO 6 (523959) 230 kV Bus to CHAN+TASCOS6 (523869) 230 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25W | Transfer | Group5_Fault_0056_P1 | 3 phase fault on POTTER_CO 6 (523959) 230 kV Bus a. Apply Fault at the POTTER_CO 6 (523959) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from POTTER_CO 6 (523959) 230 kV Bus to MCDWL_CREEK6 (523323) 230 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25W | Transfer | Group5_Fault_0057_P1 | 3 phase fault on POTTER_CO 6 (523959) 230 kV Bus a. Apply Fault at the POTTER_CO 6 (523959) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from POTTER_CO 6 (523959) 230 kV Bus to ROLLHILLS 6 (524010) 230 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25W | Transfer | Group5_Fault_0058_P1 | 3 phase fault on POTTER_CO 6 (523959) 230 kV Bus a. Apply Fault at the POTTER_CO 6 (523959) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from POTTER_CO 6 (523959) 230 kV Bus to HARRNG_EST 6 (523979) 230 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25W | Transfer | Group5_Fault_0059_P1 | 3 phase fault on POTTER_CO 6 (523959) 230 kV Bus a. Apply Fault at the POTTER_CO 6 (523959) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from POTTER_CO 6 (523959) 230 kV Bus to BUSHLAND 6 (524267) 230 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | No | No | No | No | No | No | No | Out Of Step Generators and damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25W | Transfer | Group5_Fault_0060_P1 | 3 phase fault on MCDWL_CREEK6 (523323) 230 kV Bus a. Apply Fault at the MCDWL_CREEK6 (523323) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from MCDWL_CREEK6 (523323) 230 kV Bus to MOORE_CNTY 6 (523309) 230 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Low voltage ride through fails due to the tripping of G18-115-GEN10 and G18-115-GEN20 units. No cascading was observed and the issue was localised. Model tuning is recommended. |  |  | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25W | Transfer | Group5_Fault_0061_P1 | 3 phase fault on MCDWL_CREEK6 (523323) 230 kV Bus a. Apply Fault at the MCDWL_CREEK6 (523323) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from MCDWL_CREEK6 (523323) 230 kV Bus to MCDWL_CREEK3 (523322) 115 kV Bus to MCDWL_CRKTR1 (523321) 13.2 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25W | Transfer | Group5_Fault_0062_P1 | 3 phase fault on HARRNG_EST 6 (523979) 230 kV Bus a. Apply Fault at the HARRNG_EST 6 (523979) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from HARRNG_EST 6 (523979) 230 kV Bus to HARRNG_MID 6 (523978) 230 kV Bus CKT @1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | No | No | No | No | Yes | No | No | Out Of Step Generators and damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25W | Transfer | Group5_Fault_0063_P1 | 3 phase fault on HARRNG_EST 6 (523979) 230 kV Bus a. Apply Fault at the HARRNG_EST 6 (523979) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from HARRNG_EST 6 (523979) 230 kV Bus to PRINGLE 6 (523267) 230 kV Bus CKT 1 b. 2. Trip three winding transformer from PRINGLE 6 (523267) 230 kV Bus to PRINGLE 3 (523266) 115 kV Bus to PRINGLE_TR 1 (523265) 13.2 kV Bus CKT 1 | P1 | No | No | No | No | No | No | No | Out Of Step Generators and damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25W | Transfer | Group5_Fault_0064_P1 | 3 phase fault on ROLLHILLS 6 (524010) 230 kV Bus a. Apply Fault at the ROLLHILLS 6 (524010) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from ROLLHILLS 6 (524010) 230 kV Bus to ROLLHILLS 3 (524007) 115 kV Bus to ROLHILLS_TR1 (524008) 13.2 kV Bus CKT 1 | P1 | No | No | No | Yes | No | No | No | Out Of Step Generators and damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25W | Transfer | Group5_Fault_0065_P1 | 3 phase fault on BUSHLAND 6 (524267) 230 kV Bus a. Apply Fault at the BUSHLAND 6 (524267) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from BUSHLAND 6 (524267) 230 kV Bus to BUSHLAND 3 (524266) 115 kV Bus to BSHLND_TR1 1 (524263) 13.2 kV Bus CKT 1 b. 2. Trip branch from BUSHLAND 3 (524266) 115 kV Bus to OUTPOST 3 (524243) 115 kV Bus CKT 1 b. 3. Trip branch from OUTPOST 3 (524243) 115 kV Bus to ARNOT 3 (524560) 115 kV Bus CKT 1 b. 4. Trip branch from ARNOT 3 (524560) 115 kV Bus to HILLSIDE 3 (524300) 115 kV Bus CKT 1 b. 5. Trip branch from HILLSIDE 3 (524300) 115 kV Bus to COULTER 3 (524306) 115 kV Bus CKT 1 b. 6. Drop Load 1 at OUTPOST 3 (524243) 115 kV Bus b. 7. Drop Load 1 at ARNOT 3 (524560) 115 kV Bus b. 8. Drop Load 1 at HILLSIDE 3 (524300) 115 kV Bus | P1 | Yes | Yes | Yes | No | Yes | Yes | No | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points) |  | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25W | Transfer | Group5_Fault_0066_P1 | 3 phase fault on NICHOLS 6 (524044) 230 kV Bus a. Apply Fault at the NICHOLS 6 (524044) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from NICHOLS 6 (524044) 230 kV Bus to AMA_SOUTH 6 (524415) 230 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | No | No | No | No | Yes | No | No | Out Of Step Generators and damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25W | Transfer | Group5_Fault_0067_P1 | 3 phase fault on RANDALL 6 (524365) 230 kV Bus a. Apply Fault at the RANDALL 6 (524365) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from RANDALL 6 (524365) 230 kV Bus to AMA_SOUTH 6 (524415) 230 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | No | No | No | No | No | No | No | Out Of Step Generators and damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25W | Transfer | Group5_Fault_0068_P1 | 3 phase fault on AMA_SOUTH 6 (524415) 230 kV Bus a. Apply Fault at the AMA_SOUTH 6 (524415) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from AMA_SOUTH 6 (524415) 230 kV Bus to AMA_SOUTH 3 (524414) 115 kV Bus to AMA_SO_TR1 1 (524410) 13.2 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | No | No | Damping issues observed. Low voltage ride through fails due to the tripping of G18-115-GEN10 and G18-115-GEN20 units. No cascading was observed and the issue was localised. Model tuning is recommended. | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25W | Transfer | Group5_Fault_0069_P1 | 3 phase fault on TUCO_INT 6 (525830) 230 kV Bus a. Apply Fault at the TUCO_INT 6 (525830) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from TUCO_INT 6 (525830) 230 kV Bus to TOLK 6 (525531) 230 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | No | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points) |  | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25W | Transfer | Group5_Fault_0070_P1 | 3 phase fault on TUCO_INT 7 (525832) 345 kV Bus a. Apply Fault at the TUCO_INT 7 (525832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from TUCO_INT 7 (525832) 345 kV Bus to TUCO_INT 6 (525830) 230 kV Bus to TUCO_TR1 1 (525824) 13.2 kV Bus CKT 1 b. 2. Drop Shunt 1 at TUCO_TR1 1 (525824) 13.2 kV Bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Low voltage ride through fails due to the tripping of G18-115-GEN10 and G18-115-GEN20 units. No cascading was observed and the issue was localised. Model tuning is recommended. |  |  | Generator relays were disabled for the following generators: 763084 [G18-073-GEN20.6600]
05 - Southwest | 25W | Transfer | Group5_Fault_0071_P1 | 3 phase fault on TUCO_INT 7 (525832) 345 kV Bus a. Apply Fault at the TUCO_INT 7 (525832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from TUCO_INT 7 (525832) 345 kV Bus to TUCO_INT 6 (525830) 230 kV Bus to TUCO_TR2 1 (525825) 13.2 kV Bus CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Low voltage ride through fails due to the tripping of G18-115-GEN10 and G18-115-GEN20 units. No cascading was observed and the issue was localised. Model tuning is recommended. |  |  | Generator relays were disabled for the following generators: 763084 [G18-073-GEN20.6600]
05 - Southwest | 25W | Transfer | Group5_Fault_0072_P1 | 3 phase fault on HARRNG_WST 6 (523977) 230 kV Bus a. Apply Fault at the HARRNG_WST 6 (523977) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from HARRNG_WST 6 (523977) 230 kV Bus to HARRNG_MID 6 (523978) 230 kV Bus CKT @1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | No | No | No | No | Yes | No | No | Out Of Step Generators and damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25W | Transfer | Group5_Fault_0073_P1 | 3 phase fault on HARRNG_MID 6 (523978) 230 kV Bus a. Apply Fault at the HARRNG_MID 6 (523978) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from HARRNG_MID 6 (523978) 230 kV Bus to RANDALL 6 (524365) 230 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | No | No | No | No | Yes | No | No | Out Of Step Generators and damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25W | Transfer | Group5_Fault_0074_P1 | 3 phase fault on HARRNG_MID 6 (523978) 230 kV Bus a. Apply Fault at the HARRNG_MID 6 (523978) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from HARRNG_MID 6 (523978) 230 kV Bus to NICHOLS 6 (524044) 230 kV Bus CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | No | No | No | No | No | No | No | Out Of Step Generators and damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25W | Transfer | Group5_Fault_0075_P1 | 3 phase fault on CASTRO_CNTY3 (524746) 115 kV Bus a. Apply Fault at the CASTRO_CNTY3 (524746) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from CASTRO_CNTY3 (524746) 115 kV Bus to DS-#22 3 (524694) 115 kV Bus CKT 1 b. 2. Drop Load 1 at DS-#22 3 (524694) 115 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | Group5_Fault_0076_P1 | 3 phase fault on CASTRO_CNTY3 (524746) 115 kV Bus a. Apply Fault at the CASTRO_CNTY3 (524746) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from CASTRO_CNTY3 (524746) 115 kV Bus to CASTRO_CNTY2 (524745) 69 kV Bus to CASTRO_TR1 1 (524744) 13.2 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | Group5_Fault_0077_P1 | 3 phase fault on CASTRO_CNTY3 (524746) 115 kV Bus a. Apply Fault at the CASTRO_CNTY3 (524746) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from CASTRO_CNTY3 (524746) 115 kV Bus to CASTRO_CNTY2 (524745) 69 kV Bus to CASTRO_TR2 1 (524743) 13.2 kV Bus CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | Group5_Fault_0078_P1 | 3 phase fault on CASTRO_CNTY3 (524746) 115 kV Bus a. Apply Fault at the CASTRO_CNTY3 (524746) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from CASTRO_CNTY3 (524746) 115 kV Bus to DS-#21 3 (524734) 115 kV Bus CKT 1 b. 2. Trip branch from DS-#21 3 (524734) 115 kV Bus to TIERABLANCA3 (524630) 115 kV Bus CKT 1 b. 3. Drop Load 1 at DS-#21 3 (524734) 115 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 584223 [G14-040-GEN10.6900]
05 - Southwest | 25W | Transfer | Group5_Fault_0079_P1 | 3 phase fault on KRESS_INT 3 (525192) 115 kV Bus a. Apply Fault at the KRESS_INT 3 (525192) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from KRESS_INT 3 (525192) 115 kV Bus to KRS_RURL_TP3 (525226) 115 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer
05 - Southwest | 25W | Transfer | Group5_Fault_0080_P1 | 3 phase fault on KRESS_INT 3 (525192) 115 kV Bus a. Apply Fault at the KRESS_INT 3 (525192) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from KRESS_INT 3 (525192) 115 kV Bus to KRESS_INT 2 (525191) 69 kV Bus to KRESS_TR1 1 (525190) 13.2 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | Group5_Fault_0081_P1 | 3 phase fault on KRESS_INT 3 (525192) 115 kV Bus a. Apply Fault at the KRESS_INT 3 (525192) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from KRESS_INT 3 (525192) 115 kV Bus to TULIA_TP 3 (525179) 115 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer
05 - Southwest | 25W | Transfer | Group5_Fault_0082_P1 | 3 phase fault on KRESS_INT 3 (525192) 115 kV Bus a. Apply Fault at the KRESS_INT 3 (525192) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from KRESS_INT 3 (525192) 115 kV Bus to HALE_CNTY 3 (525454) 115 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | Group5_Fault_0083_P1 | 3 phase fault on MOORE_CNTY 6 (523309) 230 kV Bus a. Apply Fault at the MOORE_CNTY 6 (523309) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from MOORE_CNTY 6 (523309) 230 kV Bus to MOORE_E 3 (523308) 115 kV Bus to MOORE_TR1 1 (523302) 13.2 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25W | Transfer | Group5_Fault_0084_P1 | 3 phase fault on MCDWL_CREEK3 (523322) 115 kV Bus a. Apply Fault at the MCDWL_CREEK3 (523322) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from MCDWL_CREEK3 (523322) 115 kV Bus to EXELL_TP 3 (523332) 115 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25W | Transfer | Group5_Fault_0085_P1 | 3 phase fault on PLSNT_HILL 6 (524770) 230 kV Bus a. Apply Fault at the PLSNT_HILL 6 (524770) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from PLSNT_HILL 6 (524770) 230 kV Bus to PLSNT_HILL 3 (524768) 115 kV Bus to PLSNHIL_TR11 (524767) 13.2 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | Group5_Fault_0086_P1 | 3 phase fault on PLSNT_HILL 6 (524770) 230 kV Bus a. Apply Fault at the PLSNT_HILL 6 (524770) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from PLSNT_HILL 6 (524770) 230 kV Bus to OASIS 6 (524875) 230 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | Group5_Fault_0087_P1 | 3 phase fault on OASIS 6 (524875) 230 kV Bus a. Apply Fault at the OASIS 6 (524875) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from OASIS 6 (524875) 230 kV Bus to OASIS 3 (524874) 115 kV Bus to OASIS_TR1 113.200 (524872) kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | Group5_Fault_0088_P1 | 3 phase fault on OASIS 6 (524875) 230 kV Bus a. Apply Fault at the OASIS 6 (524875) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from OASIS 6 (524875) 230 kV Bus to SN_JUAN_TAP6 (524885) 230 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25W | Transfer | Group5_Fault_0089_P1 | 3 phase fault on ROOSEVELT 3 (524908) 115 kV Bus a. Apply Fault at the ROOSEVELT 3 (524908) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from ROOSEVELT 3 (524908) 115 kV Bus to CURRY 3 (524822) 115 kV Bus CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | Group5_Fault_0090_P1 | 3 phase fault on ROOSEVELT 3 (524908) 115 kV Bus a. Apply Fault at the ROOSEVELT 3 (524908) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from ROOSEVELT 3 (524908) 115 kV Bus to PORTALES 3 (524924) 115 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | Group5_Fault_0091_P1 | 3 phase fault on LAMB_CNTY 3 (525636) 115 kV Bus a. Apply Fault at the LAMB_CNTY 3 (525636) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from LAMB_CNTY 3 (525636) 115 kV Bus to HOCKLEY 3 (526020) 115 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | Group5_Fault_0092_P1 | 3 phase fault on LAMB_CNTY 3 (525636) 115 kV Bus a. Apply Fault at the LAMB_CNTY 3 (525636) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from LAMB_CNTY 3 (525636) 115 kV Bus to LAMB_CNTY 2 (525635) 69 kV Bus to LAMB_TR1 1 (525631) 13.2 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | Group5_Fault_0093_P1 | 3 phase fault on LAMB_CNTY 3 (525636) 115 kV Bus a. Apply Fault at the LAMB_CNTY 3 (525636) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from LAMB_CNTY 3 (525636) 115 kV Bus to LAMB_CNTY 2 (525635) 69 kV Bus to LAMB_TR2 1 (525632) 13.2 kV Bus CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | Group5_Fault_0094_P1 | 3 phase fault on CARLISLE 6 (526161) 230 kV Bus a. Apply Fault at the CARLISLE 6 (526161) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from CARLISLE 6 (526161) 230 kV Bus to CARLISLE 3 (526160) 115 kV Bus to CRLSLE_TR1 1 (526157) 13.2 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Low voltage ride through fails due to the tripping of G18-115-GEN10 and G18-115-GEN20 units. No cascading was observed and the issue was localised. Model tuning is recommended.
05 - Southwest | 25W | Transfer | Group5_Fault_0095_P1 | 3 phase fault on JONES 6 (526337) 230 kV Bus a. Apply Fault at the JONES 6 (526337) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from JONES 6 (526337) 230 kV Bus to LUBBCK_STH 6 (526269) 230 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | No | No | No | Yes | No | No | No | Out Of Step Generators and damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25W | Transfer | Group5_Fault_0096_P1 | 3 phase fault on JONES 6 (526337) 230 kV Bus a. Apply Fault at the JONES 6 (526337) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from JONES 6 (526337) 230 kV Bus to LUBBCK_STH 6 (526269) 230 kV Bus CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | No | No | No | Yes | No | No | Yes | Out Of Step Generators and damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer
05 - Southwest | 25W | Transfer | Group5_Fault_0097_P1 | 3 phase fault on JONES 6 (526337) 230 kV Bus a. Apply Fault at the JONES 6 (526337) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from JONES 6 (526337) 230 kV Bus to GRASSLAND 6 (526677) 230 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | No | No | No | No | No | No | Yes | Out Of Step Generators and damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer
05 - Southwest | 25W | Transfer | Group5_Fault_0098_P1 | 3 phase fault on JONES 6 (526337) 230 kV Bus a. Apply Fault at the JONES 6 (526337) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from JONES 6 (526337) 230 kV Bus to LUBBCK_EST 6 (526299) 230 kV Bus CKT 1 b. 2. Trip three winding transformer from LUBBCK_EST 6 (526299) 230 kV Bus to LUBBCK_EST 3 (526298) 115 kV Bus to LBB_EST TR11 (526294) 13.2 kV Bus CKT 1 | P1 | No | No | No | Yes | No | No | Yes | Out Of Step Generators and damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer
05 - Southwest | 25W | Transfer | Group5_Fault_0099_P1 | 3 phase fault on TUCO_INT 3 (525828) 115 kV Bus a. Apply Fault at the TUCO_INT 3 (525828) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from TUCO_INT 3 (525828) 115 kV Bus to HALE_CNTY 3 (525454) 115 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | Group5_Fault_0100_P1 | 3 phase fault on TUCO_INT 3 (525828) 115 kV Bus a. Apply Fault at the TUCO_INT 3 (525828) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from TUCO_INT 3 (525828) 115 kV Bus to LUBBCK_EST 3 (526298) 115 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | Group5_Fault_0101_P1 | 3 phase fault on PLSNT_HILL 3 (524768) 115 kV Bus a. Apply Fault at the PLSNT_HILL 3 (524768) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from PLSNT_HILL 3 (524768) 115 kV Bus to NORTON 3 (524502) 115 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | Group5_Fault_0102_P1 | 3 phase fault on PLSNT_HILL 3 (524768) 115 kV Bus a. Apply Fault at the PLSNT_HILL 3 (524768) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from PLSNT_HILL 3 (524768) 115 kV Bus to E_CLOVIS 3 (524773) 115 kV Bus CKT 1 b. 2. Trip branch from E_CLOVIS 3 (524773) 115 kV Bus to CURRY 3 (524822) 115 kV Bus CKT 1 b. 3. Drop Load 1 at E_CLOVIS 3 (524773) 115 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | Group5_Fault_0103_P1 | 3 phase fault on PLSNT_HILL 3 (524768) 115 kV Bus a. Apply Fault at the PLSNT_HILL 3 (524768) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from PLSNT_HILL 3 (524768) 115 kV Bus to N_CLOVIS_TP3 (524776) 115 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | Group5_Fault_0104_P1 | 3 phase fault on PLSNT_HILL 3 (524768) 115 kV Bus a. Apply Fault at the PLSNT_HILL 3 (524768) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from PLSNT_HILL 3 (524768) 115 kV Bus to FE-HOLLAND 3 (524831) 115 kV Bus CKT 1 b. 2. Trip branch from FE-HOLLAND 3 (524831) 115 kV Bus to FE-CLOVIS2+3 (524838) 115 kV Bus CKT 1 b. 3. Trip branch from FE-CLOVIS2+3 (524838) 115 kV Bus to CURRY 3 (524822) 115 kV Bus CKT 1 b. 4. Drop Load 1 at FE-HOLLAND 3 (524831) 115 kV Bus b. 5. Drop Load 1 at FE-CLOVIS2+3 (524838) 115 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | Group5_Fault_0105_P1 | 3 phase fault on SN_JUAN_TAP6 (524885) 230 kV Bus a. Apply Fault at the SN_JUAN_TAP6 (524885) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from SN_JUAN_TAP6 (524885) 230 kV Bus to CHAVES_CNTY6 (527483) 230 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 763309 [G18-112-GEN10.6600]
05 - Southwest | 25W | Transfer | Group5_Fault_0106_P1 | 3 phase fault on OASIS 3 (524874) 115 kV Bus a. Apply Fault at the OASIS 3 (524874) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from OASIS 3 (524874) 115 kV Bus to PORTALES 3 (524924) 115 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | Group5_Fault_0107_P1 | 3 phase fault on OASIS 3 (524874) 115 kV Bus a. Apply Fault at the OASIS 3 (524874) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from OASIS 3 (524874) 115 kV Bus to PERIMETER 3 (524797) 115 kV Bus CKT 1 b. 2. Trip branch from PERIMETER 3 (524797) 115 kV Bus to CANNON_TP 3 (524790) 115 kV Bus CKT 1 b. 3. Drop Load 1 at PERIMETER 3 (524797) 115 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | Group5_Fault_0108_P1 | 3 phase fault on OASIS 3 (524874) 115 kV Bus a. Apply Fault at the OASIS 3 (524874) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from OASIS 3 (524874) 115 kV Bus to FE-CHZPLT 3 (524863) 115 kV Bus CKT 1 b. 2. Trip branch from FE-CHZPLT 3 (524863) 115 kV Bus to NORRIS_TP 3 (524764) 115 kV Bus CKT 1 b. 3. Drop Load 1 at FE-CHZPLT 3 (524863) 115 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | Group5_Fault_0109_P1 | 3 phase fault on CURRY 3 (524822) 115 kV Bus a. Apply Fault at the CURRY 3 (524822) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from CURRY 3 (524822) 115 kV Bus to NORRIS_TP 3 (524764) 115 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | Group5_Fault_0110_P1 | 3 phase fault on NORRIS_TP 3 (524764) 115 kV Bus a. Apply Fault at the NORRIS_TP 3 (524764) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from NORRIS_TP 3 (524764) 115 kV Bus to NORRIS 3 (524801) 115 kV Bus CKT 1 b. 2. Drop Load 1 at NORRIS 3 (524801) 115 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | Group5_Fault_0111_P1 | 3 phase fault on CURRY 3 (524822) 115 kV Bus a. Apply Fault at the CURRY 3 (524822) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from CURRY 3 (524822) 115 kV Bus to CURRY 2 (524821) 69 kV Bus to CURRY_TR1 1 (524819) 13.2 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | Group5_Fault_0112_P1 | 3 phase fault on CURRY 3 (524822) 115 kV Bus a. Apply Fault at the CURRY 3 (524822) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from CURRY 3 (524822) 115 kV Bus to CURRY 2 (524821) 69 kV Bus to CURRY_TR2 1 (524820) 13.2 kV Bus CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | Group5_Fault_0113_P1 | 3 phase fault on CURRY 3 (524822) 115 kV Bus a. Apply Fault at the CURRY 3 (524822) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from CURRY 3 (524822) 115 kV Bus to BAILEYCO 3 (525028) 115 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | Group5_Fault_0114_P1 | 3 phase fault on PORTALES 3 (524924) 115 kV Bus a. Apply Fault at the PORTALES 3 (524924) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from PORTALES 3 (524924) 115 kV Bus to PORTALES 2 (524923) 69 kV Bus to PORTLES_TR11 (524921) 13.2 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | Group5_Fault_0115_P1 | 3 phase fault on PORTALES 3 (524924) 115 kV Bus a. Apply Fault at the PORTALES 3 (524924) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from PORTALES 3 (524924) 115 kV Bus to PORTALES 2 (524923) 69 kV Bus to PORTLES_TR21 (524922) 13.2 kV Bus CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | Group5_Fault_0116_P1 | 3 phase fault on DEAFSMITH 6 (524623) 230 kV Bus a. Apply Fault at the DEAFSMITH 6 (524623) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from DEAFSMITH 6 (524623) 230 kV Bus to DFSMTH_WST 3 (524622) 115 kV Bus to DEFSMTH_TR11 (524620) 13.2 kV Bus CKT 1 b. 2. Trip branch from DFSMTH_WST 3 (524622) 115 kV Bus to TIERABLANCA3 (524630) 115 kV Bus CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | Group5_Fault_0117_P1 | 3 phase fault on INK_BASIN 6 (527028) 230 kV Bus a. Apply Fault at the INK_BASIN 6 (527028) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from INK_BASIN 6 (527028) 230 kV Bus to INK_BASIN 3 (527027) 115 kV Bus to INKBASN_TR 1 (527026) 13.2 kV Bus CKT 1 | P1 | Yes | No | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25W | Transfer | Group5_Fault_0118_P1 | 3 phase fault on HOCKLEY 3 (526020) 115 kV Bus a. Apply Fault at the HOCKLEY 3 (526020) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from HOCKLEY 3 (526020) 115 kV Bus to HOCKLEY 2 (526019) 69 kV Bus to HOCKLEY_TR11 (526017) 13.2 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | Group5_Fault_0119_P1 | 3 phase fault on HOCKLEY 3 (526020) 115 kV Bus a. Apply Fault at the HOCKLEY 3 (526020) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from HOCKLEY 3 (526020) 115 kV Bus to HOCKLEY 2 (526019) 69 kV Bus to HOCKLEY_TR21 (526018) 13.2 kV Bus CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | Group5_Fault_0120_P1 | 3 phase fault on N_CLOVIS_TP3 (524776) 115 kV Bus a. Apply Fault at the N_CLOVIS_TP3 (524776) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from N_CLOVIS_TP3 (524776) 115 kV Bus to FE-CLVS_INT3 (524808) 115 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 763309 [G18-112-GEN10.6600]
05 - Southwest | 25W | Transfer | Group5_Fault_0121_P1 | 3 phase fault on N_CLOVIS_TP3 (524776) 115 kV Bus a. Apply Fault at the N_CLOVIS_TP3 (524776) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from N_CLOVIS_TP3 (524776) 115 kV Bus to N_CLOVIS 3 (524777) 115 kV Bus CKT 1 b. 2. Drop Load 1 at N_CLOVIS 3 (524777) 115 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  | Generator relays were disabled for the following generators: 763309 [G18-112-GEN10.6600]
05 - Southwest | 25W | Transfer | Group5_Fault_0122_P1 | 3 phase fault on NORTON 3 (524502) 115 kV Bus a. Apply Fault at the NORTON 3 (524502) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from NORTON 3 (524502) 115 kV Bus to FE-TUCMCARI3 (524509) 115 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | Group5_Fault_0123_P1 | 3 phase fault on CHAVES_CNTY6 (527483) 230 kV Bus a. Apply Fault at the CHAVES_CNTY6 (527483) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from CHAVES_CNTY6 (527483) 230 kV Bus to EDDY_NORTH 6 (527799) 230 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 763309 [G18-112-GEN10.6600]
05 - Southwest | 25W | Transfer | Group5_Fault_0124_P1 | 3 phase fault on CHAVES_CNTY6 (527483) 230 kV Bus a. Apply Fault at the CHAVES_CNTY6 (527483) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from CHAVES_CNTY6 (527483) 230 kV Bus to CHAVES_CNTY3 (527482) 115 kV Bus to CHAVES_TR1 1 (527478) 13.2 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | Group5_Fault_0125_P1 | 3 phase fault on CHAVES_CNTY6 (527483) 230 kV Bus a. Apply Fault at the CHAVES_CNTY6 (527483) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from CHAVES_CNTY6 (527483) 230 kV Bus to CHAVES_CNTY3 (527482) 115 kV Bus to CHAVES_TR2 1 (527479) 13.2 kV Bus CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | Group5_Fault_0126_P1 | 3 phase fault on EDDY_CNTY 7 (527802) 345 kV Bus a. Apply Fault at the EDDY_CNTY 7 (527802) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from EDDY_CNTY 7 (527802) 345 kV Bus to KIOWA 7 (527965) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | No | No | No | No | No | No | No | Out Of Step Generators and damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25W | Transfer | Group5_Fault_0127_P1 | 3 phase fault on EDDY_CNTY 7 (527802) 345 kV Bus a. Apply Fault at the EDDY_CNTY 7 (527802) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from EDDY_CNTY 7 (527802) 345 kV Bus to EDDY_NORTH 6 (527799) 230 kV Bus to EDDY_TR 1 (527796) 13.2 kV Bus CKT 1 b. 2. Drop Shunt 1 at EDDY_TR 1 (527796) 13.2 kV Bus | P1 | No | No | No | No | Yes | No | No | Out Of Step Generators and damping issues observed | Potter to Tolk 345 kV Double Circuit Line Build Potter to Chisholm 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer Potter to Tolk 345 kV | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000], 763397 [G18-124-GEN1], 763309 [G18-112-GEN1]
05 - Southwest | 25W | Transfer | Group5_Fault_0128_P1 | 3 phase fault on FE-CLVS_INT3 (524808) 115 kV Bus a. Apply Fault at the FE-CLVS_INT3 (524808) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from FE-CLVS_INT3 (524808) 115 kV Bus to W_CLOVIS 3 (524784) 115 kV Bus CKT 1 b. 2. Trip branch from W_CLOVIS 3 (524784) 115 kV Bus to CANNON_TP 3 (524790) 115 kV Bus CKT 1 b. 3. Drop Load 1 at W_CLOVIS 3 (524784) 115 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | Group5_Fault_0129_P1 | 3 phase fault on CANNON_TP 3 (524790) 115 kV Bus a. Apply Fault at the CANNON_TP 3 (524790) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from CANNON_TP 3 (524790) 115 kV Bus to CANNONAFB 3 (524794) 115 kV Bus CKT 1 b. 2. Drop Load 1 at CANNONAFB 3 (524794) 115 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | Group5_Fault_0130_P1 | 3 phase fault on EDDY_NORTH 6 (527799) 230 kV Bus a. Apply Fault at the EDDY_NORTH 6 (527799) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from EDDY_NORTH 6 (527799) 230 kV Bus to EDDY_NTH 3 (527798) 115 kV Bus to EDDY_TR2 1 (527797) 13.2 kV Bus CKT 1 | P1 | No | No | No | No | No | No | No | Out Of Step Generators and damping issues observed | Potter to Tolk 345 kV Double Circuit Line Build Potter to Chisholm 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer Potter to Tolk 345 kV | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000], 763397 [G18-124-GEN1], 763309 [G18-112-GEN1]
05 - Southwest | 25W | Transfer | Group5_Fault_0131_P1 | 3 phase fault on EDDY_NORTH 6 (527799) 230 kV Bus a. Apply Fault at the EDDY_NORTH 6 (527799) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from EDDY_NORTH 6 (527799) 230 kV Bus to EDDY_STH 3 (527793) 115 kV Bus to EDDY_TR3 1 (527795) 13.2 kV Bus CKT 2 | P1 | No | No | No | Yes | No | No | No | Out Of Step Generators and damping issues observed | Potter to Tolk 345 kV Double Circuit Line Build Potter to Chisholm 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer Potter to Tolk 345 kV | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000], 763397 [G18-124-GEN1], 763309 [G18-112-GEN1]
05 - Southwest | 25W | Transfer | Group5_Fault_0132_P1 | 3 phase fault on CHAVES_CNTY3 (527482) 115 kV Bus a. Apply Fault at the CHAVES_CNTY3 (527482) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from CHAVES_CNTY3 (527482) 115 kV Bus to PRICE_TAP 3 (527509) 115 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | Group5_Fault_0133_P1 | 3 phase fault on CHAVES_CNTY3 (527482) 115 kV Bus a. Apply Fault at the CHAVES_CNTY3 (527482) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from CHAVES_CNTY3 (527482) 115 kV Bus to URTON 3 (527501) 115 kV Bus CKT 1 b. 2. Trip branch from URTON 3 (527501) 115 kV Bus to ROSWELL_CTY3 (527522) 115 kV Bus CKT 1 b. 3. Drop Load 1 at URTON 3 (527501) 115 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 583973 [G14-035-GEN10.5500]
05 - Southwest | 25W | Transfer | Group5_Fault_0134_P1 | 3 phase fault on CHAVES_CNTY3 (527482) 115 kV Bus a. Apply Fault at the CHAVES_CNTY3 (527482) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from CHAVES_CNTY3 (527482) 115 kV Bus to SAMSON 3 (527546) 115 kV Bus CKT 1 b. 2. Trip branch from SAMSON 3 (527546) 115 kV Bus to ROSWLL_INT 3 (527564) 115 kV Bus CKT 1 b. 3. Drop Load 1 at SAMSON 3 (527546) 115 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 583973 [G14-035-GEN10.5500]
05 - Southwest | 25W | Transfer | Group5_Fault_0135_P1 | 3 phase fault on CARLISLE 3 (526160) 115 kV Bus a. Apply Fault at the CARLISLE 3 (526160) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from CARLISLE 3 (526160) 115 kV Bus to LP-DOUD_TP 3 (526162) 115 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 763309 [G18-112-GEN10.6600]
05 - Southwest | 25W | Transfer | Group5_Fault_0136_P1 | 3 phase fault on LP-DOUD_TP 3 (526162) 115 kV Bus a. Apply Fault at the LP-DOUD_TP 3 (526162) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from LP-DOUD_TP 3 (526162) 115 kV Bus to SP-WOLF_TP 3 (526481) 115 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | No | Yes | Damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer
05 - Southwest | 25W | Transfer | Group5_Fault_0137_P1 | 3 phase fault on LP-DOUD_TP 3 (526162) 115 kV Bus a. Apply Fault at the LP-DOUD_TP 3 (526162) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from LP-DOUD_TP 3 (526162) 115 kV Bus to LP-DOUD 3 (526176) 115 kV Bus CKT 1 b. 2. Drop Load 1 at LP-DOUD 3 (526176) 115 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25W | Transfer | Group5_Fault_0138_P1 | 3 phase fault on AMOCO_TP 3 (526445) 115 kV Bus a. Apply Fault at the AMOCO_TP 3 (526445) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from AMOCO_TP 3 (526445) 115 kV Bus to LG-LEVELAND3 (526484) 115 kV Bus CKT 1 b. 2. Trip branch from LG-LEVELAND3 (526484) 115 kV Bus to LG-CLAUENE 3 (526491) 115 kV Bus CKT 1 b. 3. Trip branch from LG-CLAUENE 3 (526491) 115 kV Bus to TERRY_CNTY 3 (526736) 115 kV Bus CKT 1 b. 4. Drop Load 1 at LG-LEVELAND3 (526484) 115 kV Bus b. 5. Drop Load 1 at LG-CLAUENE 3 (526491) 115 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | Group5_Fault_0139_P1 | 3 phase fault on SP-WOLF_TP 3 (526481) 115 kV Bus a. Apply Fault at the SP-WOLF_TP 3 (526481) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from SP-WOLF_TP 3 (526481) 115 kV Bus to YUMA_INT 3 (526475) 115 kV Bus CKT 1 b. 2. Trip branch from YUMA_INT 3 (526475) 115 kV Bus to WOLFFORTH 3 (526524) 115 kV Bus CKT 1 b. 3. Drop Load 1 at YUMA_INT 3 (526475) 115 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | No | Yes | Damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer
05 - Southwest | 25W | Transfer | Group5_Fault_0140_P1 | 3 phase fault on SP-WOLF_TP 3 (526481) 115 kV Bus a. Apply Fault at the SP-WOLF_TP 3 (526481) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from SP-WOLF_TP 3 (526481) 115 kV Bus to SP-WOLFORTH3 (526483) 115 kV Bus CKT 1 b. 2. Drop Load 1 at SP-WOLFORTH3 (526483) 115 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | No | Yes | Damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer
05 - Southwest | 25W | Transfer | Group5_Fault_0141_P1 | 3 phase fault on RANDALL 3 (524364) 115 kV Bus a. Apply Fault at the RANDALL 3 (524364) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from RANDALL 3 (524364) 115 kV Bus to GEORGIA 3 (524322) 115 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | No | No | No | No | No | No | No | Out Of Step Generators and damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25W | Transfer | Group5_Fault_0142_P1 | 3 phase fault on RANDALL 3 (524364) 115 kV Bus a. Apply Fault at the RANDALL 3 (524364) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from RANDALL 3 (524364) 115 kV Bus to PALO_DURO 3 (524530) 115 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | No | No | No | No | No | No | No | Out Of Step Generators and damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25W | Transfer | Group5_Fault_0143_P1 | 3 phase fault on RANDALL 3 (524364) 115 kV Bus a. Apply Fault at the RANDALL 3 (524364) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from RANDALL 3 (524364) 115 kV Bus to CANYON_E_TP3 (524522) 115 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | No | No | No | Yes | No | No | No | Out Of Step Generators and damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25W | Transfer | Group5_Fault_0144_P1 | 3 phase fault on RANDALL 3 (524364) 115 kV Bus a. Apply Fault at the RANDALL 3 (524364) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from RANDALL 3 (524364) 115 kV Bus to SOUTHEAST 3 (524338) 115 kV Bus CKT 1 b. 2. Trip branch from SOUTHEAST 3 (524338) 115 kV Bus to PULLMAN 3 (524331) 115 kV Bus CKT 1 b. 3. Drop Load 1 at SOUTHEAST 3 (524338) 115 kV Bus b. 4. Drop Load 1 at PULLMAN 3 (524331) 115 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | No | No | No | No | Yes | No | No | Out Of Step Generators and damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25W | Transfer | Group5_Fault_0145_P1 | 3 phase fault on RANDALL 3 (524364) 115 kV Bus a. Apply Fault at the RANDALL 3 (524364) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from RANDALL 3 (524364) 115 kV Bus to MANHATTAN 3 (524224) 115 kV Bus CKT 1 b. 2. Trip branch from MANHATTAN 3 (524224) 115 kV Bus to EAST_PLANT 3 (524162) 115 kV Bus CKT 1 b. 3. Drop Load 1 at MANHATTAN 3 (524224) 115 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | No | Yes | Yes | Yes | No | No | Damping issues observed. Low voltage ride through fails due to the tripping of G18-115-GEN10 and G18-115-GEN20 units. No cascading was observed and the issue was localised. Model tuning is recommended. | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25W | Transfer | Group5_Fault_0146_P1 | 3 phase fault on RANDALL 6 (524365) 230 kV Bus a. Apply Fault at the RANDALL 6 (524365) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from RANDALL 6 (524365) 230 kV Bus to RANDALL 3 (524364) 115 kV Bus to RANDAL_TR1 1 (524361) 13.2 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | No | No | Damping issues observed. Low voltage ride through fails due to the tripping of G18-115-GEN10 and G18-115-GEN20 units. No cascading was observed and the issue was localised. Model tuning is recommended. | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25W | Transfer | Group5_Fault_0147_P1 | 3 phase fault on RANDALL 6 (524365) 230 kV Bus a. Apply Fault at the RANDALL 6 (524365) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from RANDALL 6 (524365) 230 kV Bus to RANDALL 3 (524364) 115 kV Bus to RANDAL_TR2 1 (524360) 13.2 kV Bus CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | No | No | Damping issues observed. Low voltage ride through fails due to the tripping of G18-115-GEN10 and G18-115-GEN20 units. No cascading was observed and the issue was localised. Model tuning is recommended. | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25W | Transfer | Group5_Fault_0148_P1 | 3 phase fault on GEORGIA 3 (524322) 115 kV Bus a. Apply Fault at the GEORGIA 3 (524322) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from GEORGIA 3 (524322) 115 kV Bus to WESTERN 3 (524325) 115 kV Bus CKT 1 b. 2. Trip branch from WESTERN 3 (524325) 115 kV Bus to 34TH_ST_TP 3 (524281) 115 kV Bus CKT 1 b. 3. Drop Load 1 at WESTERN 3 (524325) 115 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | No | No | Damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25W | Transfer | Group5_Fault_0149_P1 | 3 phase fault on GEORGIA 3 (524322) 115 kV Bus a. Apply Fault at the GEORGIA 3 (524322) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from GEORGIA 3 (524322) 115 kV Bus to GEORGIA 2 (524321) 69 kV Bus to GEORGIA_TR11 (524320) 13.2 kV Bus CKT 1 b. 2. Trip branch from GEORGIA 2 (524321) 69 kV Bus to LAWRENPRK1 2 (524209) 69 kV Bus CKT 1 b. 3. Trip branch from LAWRENPRK1 2 (524209) 69 kV Bus to LAWRENPRK2 2 (524216) 69 kV Bus CKT @1 b. 4. Trip branch from LAWRENPRK2 2 (524216) 69 kV Bus to SONCY 2 (524200) 69 kV Bus CKT 1 b. 5. Trip branch from SONCY 2 (524200) 69 kV Bus to SONCY_TP 2 (524251) 69 kV Bus CKT 1 b. 6. Drop Load 1 at LAWRENPRK1 2 (524209) 69 kV Bus b. 7. Drop Load 1 at LAWRENPRK2 2 (524216) 69 kV Bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25W | Transfer | Group5_Fault_0150_P1 | 3 phase fault on GEORGIA 3 (524322) 115 kV Bus a. Apply Fault at the GEORGIA 3 (524322) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from GEORGIA 3 (524322) 115 kV Bus to CRSE_HINDTP3 (524387) 115 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | No | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points) |  | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25W | Transfer | Group5_Fault_0151_P1 | 3 phase fault on CANYON_E_TP3 (524522) 115 kV Bus a. Apply Fault at the CANYON_E_TP3 (524522) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from CANYON_E_TP3 (524522) 115 kV Bus to HUNSLEY 3 (524520) 115 kV Bus CKT 1 b. 2. Trip branch from HUNSLEY 3 (524520) 115 kV Bus to CANYON_WEST3 (524516) 115 kV Bus CKT 1 b. 3. Trip branch from CANYON_WEST3 (524516) 115 kV Bus to DAWN 3 (524590) 115 kV Bus CKT 1 b. 4. Trip branch from DAWN 3 (524590) 115 kV Bus to PANDAHFD 3 (524597) 115 kV Bus CKT 1 b. 5. Trip branch from PANDAHFD 3 (524597) 115 kV Bus to DS-#25+ 3 (524575) 115 kV Bus CKT 1 b. 6. Trip branch from DS-#25+ 3 (524575) 115 kV Bus to TIERABLANCA3 (524630) 115 kV Bus CKT 1 b. 7. Drop Load 1 at HUNSLEY 3 (524520) 115 kV Bus b. 8. Drop Load 1 at CANYON_WEST3 (524516) 115 kV Bus b. 9. Drop Load 1 at DAWN 3 (524590) 115 kV Bus b. 10. Drop Load 1 at PANDAHFD 3 (524597) 115 kV Bus b. 11. Drop Load 1 at DS-#25+ 3 (524575) 115 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | Group5_Fault_0152_P1 | 3 phase fault on CANYON_E_TP3 (524522) 115 kV Bus a. Apply Fault at the CANYON_E_TP3 (524522) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from CANYON_E_TP3 (524522) 115 kV Bus to CANYON_EAST3 (524523) 115 kV Bus CKT 1 b. 2. Drop Load 1 at CANYON_EAST3 (524523) 115 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | Group5_Fault_0153_P1 | 3 phase fault on PALO_DURO 3 (524530) 115 kV Bus a. Apply Fault at the PALO_DURO 3 (524530) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from PALO_DURO 3 (524530) 115 kV Bus to HAPPY_INT 3 (525154) 115 kV Bus CKT 1 b. 2. Drop Load 1 at PALO_DURO 3 (524530) 115 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | Group5_Fault_0154_P1 | 3 phase fault on CRSE_HINDTP3 (524387) 115 kV Bus a. Apply Fault at the CRSE_HINDTP3 (524387) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from CRSE_HINDTP3 (524387) 115 kV Bus to CROUSE_HIND3 (524388) 115 kV Bus CKT 1 b. 2. Drop Load 1 at CROUSE_HIND3 (524388) 115 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | No | No | Damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25W | Transfer | Group5_Fault_0155_P1 | 3 phase fault on CRSE_HINDTP3 (524387) 115 kV Bus a. Apply Fault at the CRSE_HINDTP3 (524387) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from CRSE_HINDTP3 (524387) 115 kV Bus to FARMERS 3 (524377) 115 kV Bus CKT 1 b. 2. Trip branch from FARMERS 3 (524377) 115 kV Bus to AMA_SOUTH 3 (524414) 115 kV Bus CKT 1 b. 3. Drop Load 1 at FARMERS 3 (524377) 115 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | No | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points) |  | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25W | Transfer | Group5_Fault_0156_P1 | 3 phase fault on 34TH_ST_TP 3 (524281) 115 kV Bus a. Apply Fault at the 34TH_ST_TP 3 (524281) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from 34TH_ST_TP 3 (524281) 115 kV Bus to 34TH_ST 3 (524282) 115 kV Bus CKT 1 b. 2. Drop Load 1 at 34TH_ST 3 (524282) 115 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | No | No | Damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25W | Transfer | Group5_Fault_0157_P1 | 3 phase fault on 34TH_ST_TP 3 (524281) 115 kV Bus a. Apply Fault at the 34TH_ST_TP 3 (524281) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from 34TH_ST_TP 3 (524281) 115 kV Bus to COULTER 3 (524306) 115 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | No | No | Damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25W | Transfer | Group5_Fault_0158_P1 | 3 phase fault on COULTER 3 (524306) 115 kV Bus a. Apply Fault at the COULTER 3 (524306) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from COULTER 3 (524306) 115 kV Bus to ESTACADO_TP3 (524425) 115 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | No | No | Damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25W | Transfer | Group5_Fault_0159_P1 | 3 phase fault on COULTER 3 (524306) 115 kV Bus a. Apply Fault at the COULTER 3 (524306) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from COULTER 3 (524306) 115 kV Bus to COULTER 2 (524305) 69 kV Bus to COLTER_TR1 1 (524304) 13.2 kV Bus CKT 1 b. 2. Trip branch from COULTER 2 (524305) 69 kV Bus to WATERFL_TP 2 (524234) 69 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25W | Transfer | Group5_Fault_0160_P1 | 3 phase fault on COULTER 3 (524306) 115 kV Bus a. Apply Fault at the COULTER 3 (524306) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from COULTER 3 (524306) 115 kV Bus to PUCKETT 3 (524256) 115 kV Bus CKT 1 b. 2. Trip branch from PUCKETT 3 (524256) 115 kV Bus to SONCY_TP 3 (524252) 115 kV Bus CKT 1 b. 3. Drop Load 1 at PUCKETT 3 (524256) 115 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | No | No | Damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25W | Transfer | Group5_Fault_0161_P1 | 3 phase fault on ESTACADO_TP3 (524425) 115 kV Bus a. Apply Fault at the ESTACADO_TP3 (524425) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from ESTACADO_TP3 (524425) 115 kV Bus to ESTACADO 3 (524432) 115 kV Bus CKT 1 b. 2. Drop Load 1 at ESTACADO 3 (524432) 115 kV Bus b. 3. Drop Load 2 at ESTACADO 3 (524432) 115 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | No | No | Damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25W | Transfer | Group5_Fault_0162_P1 | 3 phase fault on ESTACADO_TP3 (524425) 115 kV Bus a. Apply Fault at the ESTACADO_TP3 (524425) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from ESTACADO_TP3 (524425) 115 kV Bus to PRESTONWEST3 (524341) 115 kV Bus CKT 1 b. 2. Trip branch from PRESTONWEST3 (524341) 115 kV Bus to OWENSCORN 3 (524404) 115 kV Bus CKT 1 b. 3. Trip branch from OWENSCORN 3 (524404) 115 kV Bus to AMA_SOUTH 3 (524414) 115 kV Bus CKT 1 b. 4. Drop Load 1 at PRESTONWEST3 (524341) 115 kV Bus b. 5. Drop Load 1 at OWENSCORN 3 (524404) 115 kV Bus b. 6. Drop Shunt 1 at OWENSCORN 3 (524404) 115 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25W | Transfer | Group5_Fault_0163_P1 | 3 phase fault on NICHOLS 3 (524043) 115 kV Bus a. Apply Fault at the NICHOLS 3 (524043) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from NICHOLS 3 (524043) 115 kV Bus to WHITAKER 3 (524058) 115 kV Bus CKT 1 b. 2. Trip branch from WHITAKER 3 (524058) 115 kV Bus to EAST_PLANT 3 (524162) 115 kV Bus CKT 1 b. 3. Drop Load 1 at WHITAKER 3 (524058) 115 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | No | No | Damping issues observed. Low voltage ride through fails due to the tripping of G18-115-GEN10 and G18-115-GEN20 units. No cascading was observed and the issue was localised. Model tuning is recommended. | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25W | Transfer | Group5_Fault_0164_P1 | 3 phase fault on ROLLHILLS 3 (524007) 115 kV Bus a. Apply Fault at the ROLLHILLS 3 (524007) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from ROLLHILLS 3 (524007) 115 kV Bus to HASTINGS 3 (524136) 115 kV Bus CKT 1 b. 2. Trip branch from HASTINGS 3 (524136) 115 kV Bus to EAST_PLANT 3 (524162) 115 kV Bus CKT 1 b. 3. Drop Load 1 at HASTINGS 3 (524136) 115 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | No | No | Damping issues observed. Low voltage ride through fails due to the tripping of G18-115-GEN10 and G18-115-GEN20 units. No cascading was observed and the issue was localised. Model tuning is recommended. | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25W | Transfer | Group5_Fault_0165_P1 | 3 phase fault on EAST_PLANT 3 (524162) 115 kV Bus a. Apply Fault at the EAST_PLANT 3 (524162) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from EAST_PLANT 3 (524162) 115 kV Bus to PIERCE_TP 3 (524185) 115 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | No | No | No | No | No | No | No | Out Of Step Generators and damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25W | Transfer | Group5_Fault_0166_P1 | 3 phase fault on EAST_PLANT 3 (524162) 115 kV Bus a. Apply Fault at the EAST_PLANT 3 (524162) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from EAST_PLANT 3 (524162) 115 kV Bus to EAST_PLANT 2 (524161) 69 kV Bus to EPLANT_TR1 1 (524158) 13.2 kV Bus CKT 1 | P1 | Yes | Yes | Yes | No | Yes | No | No | Damping issues observed. Low voltage ride through fails due to the tripping of G18-115-GEN10 and G18-115-GEN20 units. No cascading was observed and the issue was localised. Model tuning is recommended. | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25W | Transfer | Group5_Fault_0167_P1 | 3 phase fault on EAST_PLANT 3 (524162) 115 kV Bus a. Apply Fault at the EAST_PLANT 3 (524162) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from EAST_PLANT 3 (524162) 115 kV Bus to EAST_PLANT 2 (524161) 69 kV Bus to EPLANT_TR2 1 (524159) 13.2 kV Bus CKT 2 | P1 | Yes | Yes | Yes | No | Yes | No | No | Damping issues observed. Low voltage ride through fails due to the tripping of G18-115-GEN10 and G18-115-GEN20 units. No cascading was observed and the issue was localised. Model tuning is recommended. | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25W | Transfer | Group5_Fault_0168_P1 | 3 phase fault on EAST_PLANT 3 (524162) 115 kV Bus a. Apply Fault at the EAST_PLANT 3 (524162) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from EAST_PLANT 6 (524163) 230 kV Bus to EAST_PLANT 3 (524162) 115 kV Bus to EPLANT_TR3 1 (524160) 13.2 kV Bus CKT 1 b. 2. Trip branch from EAST_PLANT 6 (524163) 230 kV Bus to HARRNG_WST 6 (523977) 230 kV Bus CKT 1 | P1 | Yes | Yes | Yes | No | Yes | No | No | Damping issues observed. Low voltage ride through fails due to the tripping of G18-115-GEN10 and G18-115-GEN20 units. No cascading was observed and the issue was localised. Model tuning is recommended. | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25W | Transfer | Group5_Fault_0169_P1 | 3 phase fault on HAPPY_INT 3 (525154) 115 kV Bus a. Apply Fault at the HAPPY_INT 3 (525154) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from HAPPY_INT 3 (525154) 115 kV Bus to TULIA_TP 3 (525179) 115 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | Group5_Fault_0170_P1 | 3 phase fault on HAPPY_INT 3 (525154) 115 kV Bus a. Apply Fault at the HAPPY_INT 3 (525154) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from HAPPY_INT 3 (525154) 115 kV Bus to HAPPY_INT 2 (525153) 69 kV Bus to HAPPY_TR1 1 (525151) 13.2 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | Group5_Fault_0171_P1 | 3 phase fault on HAPPY_INT 3 (525154) 115 kV Bus a. Apply Fault at the HAPPY_INT 3 (525154) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from HAPPY_INT 3 (525154) 115 kV Bus to HAPPY_INT 2 (525153) 69 kV Bus to HAPPY_TR2 1 (525152) 13.2 kV Bus CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | Group5_Fault_0172_P1 | 3 phase fault on AMA_SOUTH 3 (524414) 115 kV Bus a. Apply Fault at the AMA_SOUTH 3 (524414) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from AMA_SOUTH 3 (524414) 115 kV Bus to ARROWHEAD 3 (524397) 115 kV Bus CKT 1 b. 2. Trip branch from ARROWHEAD 3 (524397) 115 kV Bus to OSAGE 3 (524345) 115 kV Bus CKT 1 b. 3. Trip branch from OSAGE 3 (524345) 115 kV Bus to PIERCE_TP 3 (524185) 115 kV Bus CKT 1 b. 4. Drop Load 1 at ARROWHEAD 3 (524397) 115 kV Bus b. 5. Drop Load 1 at OSAGE 3 (524345) 115 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | No | No | Damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25W | Transfer | Group5_Fault_0173_P1 | 3 phase fault on AMA_SOUTH 3 (524414) 115 kV Bus a. Apply Fault at the AMA_SOUTH 3 (524414) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from AMA_SOUTH 3 (524414) 115 kV Bus to SPRING_DRW 3 (524544) 115 kV Bus CKT 1 b. 2. Drop Load 1 at SPRING_DRW 3 (524544) 115 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | No | No | Damping issues observed. Low voltage ride through fails due to the tripping of G18-115-GEN10 and G18-115-GEN20 units. No cascading was observed and the issue was localised. Model tuning is recommended. | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25W | Transfer | Group5_Fault_0174_P1 | 3 phase fault on TULIA_TP 3 (525179) 115 kV Bus a. Apply Fault at the TULIA_TP 3 (525179) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from TULIA_TP 3 (525179) 115 kV Bus to MU-TULIA 3 (522800) 115 kV Bus CKT 1 b. 2. Drop Load 1 at MU-TULIA 3 (522800) 115 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | Group5_Fault_0175_P1 | 3 phase fault on SONCY_TP 3 (524252) 115 kV Bus a. Apply Fault at the SONCY_TP 3 (524252) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from SONCY_TP 3 (524252) 115 kV Bus to SONCY 3 (524254) 115 kV Bus CKT 1 b. 2. Drop Load 1 at SONCY 3 (524254) 115 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25W | Transfer | Group5_Fault_0176_P1 | 3 phase fault on SONCY_TP 3 (524252) 115 kV Bus a. Apply Fault at the SONCY_TP 3 (524252) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from SONCY_TP 3 (524252) 115 kV Bus to SUNSET 3 (524249) 115 kV Bus CKT 1 b. 2. Trip branch from SUNSET 3 (524249) 115 kV Bus to NORTHWEST 3 (524106) 115 kV Bus CKT 1 b. 3. Drop Load 1 at SUNSET 3 (524249) 115 kV Bus b. 4. Drop Load 2 at SUNSET 3 (524249) 115 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25W | Transfer | Group5_Fault_0177_P1 | 3 phase fault on EAST_PLANT 2 (524161) 69 kV Bus a. Apply Fault at the EAST_PLANT 2 (524161) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from EAST_PLANT 2 (524161) 69 kV Bus to VANBUREN#1 2 (524142) 69 kV Bus CKT 1 b. 2. Drop Load 1 at VANBUREN#1 2 (524142) 69 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25W | Transfer | Group5_Fault_0178_P1 | 3 phase fault on EAST_PLANT 2 (524161) 69 kV Bus a. Apply Fault at the EAST_PLANT 2 (524161) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from EAST_PLANT 2 (524161) 69 kV Bus to VANBUREN#2 2 (524149) 69 kV Bus CKT 1 b. 2. Drop Load 1 at VANBUREN#2 2 (524149) 69 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25W | Transfer | Group5_Fault_0179_P1 | 3 phase fault on HAPPY_INT 2 (525153) 69 kV Bus a. Apply Fault at the HAPPY_INT 2 (525153) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from HAPPY_INT 2 (525153) 69 kV Bus to HAPPY_CTYTP2 (525143) 69 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | Group5_Fault_0180_P1 | 3 phase fault on SONCY_TP 2 (524251) 69 kV Bus a. Apply Fault at the SONCY_TP 2 (524251) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from SONCY_TP 2 (524251) 69 kV Bus to NRTHWST_TP 2 (524096) 69 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | Group5_Fault_0181_P1 | 3 phase fault on ROLLHILLS 3 (524007) 115 kV Bus a. Apply Fault at the ROLLHILLS 3 (524007) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from ROLLHILLS 3 (524007) 115 kV Bus to NORTHWEST 3 (524106) 115 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | No | No | Damping issues observed. Low voltage ride through fails due to the tripping of G18-115-GEN10 and G18-115-GEN20 units. No cascading was observed and the issue was localised. Model tuning is recommended. | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25W | Transfer | Group5_Fault_0182_P1 | 3 phase fault on NORTHWEST 3 (524106) 115 kV Bus a. Apply Fault at the NORTHWEST 3 (524106) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from NORTHWEST 3 (524106) 115 kV Bus to BUSH 3 (524124) 115 kV Bus CKT 1 b. 2. Drop Load 1 at BUSH 3 (524124) 115 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25W | Transfer | Group5_Fault_0183_P1 | 3 phase fault on NORTHWEST 3 (524106) 115 kV Bus a. Apply Fault at the NORTHWEST 3 (524106) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from NORTHWEST 3 (524106) 115 kV Bus to NORTHWEST 2 (524105) 69 kV Bus to NRTHWST_TR11 (524102) 13.2 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25W | Transfer | Group5_Fault_0184_P1 | 3 phase fault on NICHOLS 3 (524043) 115 kV Bus a. Apply Fault at the NICHOLS 3 (524043) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from NICHOLS 3 (524043) 115 kV Bus to YARNELL_TP 3 (524072) 115 kV Bus CKT 1 b. 2. Trip branch from YARNELL_TP 3 (524072) 115 kV Bus to CONWAY 3 (524079) 115 kV Bus CKT 1 b. 3. Trip branch from CONWAY 3 (524079) 115 kV Bus to KIRBY 3 (524088) 115 kV Bus CKT 1 b. 4. Drop Load 1 at CONWAY 3 (524079) 115 kV Bus b. 5. Drop Load D1 at CONWAY 3 (524079) 115 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | No | Yes | Yes | Yes | No | No | Damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25W | Transfer | Group5_Fault_0185_P1 | 3 phase fault on ROLLHILLS 3 (524007) 115 kV Bus a. Apply Fault at the ROLLHILLS 3 (524007) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from ROLLHILLS 3 (524007) 115 kV Bus to CHERRY 3 (524009) 115 kV Bus CKT 1 b. 2. Drop Load 1 at CHERRY 3 (524009) 115 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | No | No | Damping issues observed. Low voltage ride through fails due to the tripping of G18-115-GEN10 and G18-115-GEN20 units. No cascading was observed and the issue was localised. Model tuning is recommended. | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25W | Transfer | Group5_Fault_0186_P1 | 3 phase fault on PRINGLE 3 (523266) 115 kV Bus a. Apply Fault at the PRINGLE 3 (523266) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from PRINGLE 3 (523266) 115 kV Bus to Q_RYTON_TP 3 (523478) 115 kV Bus CKT 1 b. 2. Trip branch from Q_RYTON_TP 3 (523478) 115 kV Bus to BLKHAWK_E 3 (523346) 115 kV Bus CKT 1 b. 3. Drop Load 1 at Q_RYTON_TP 3 (523478) 115 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25W | Transfer | Group5_Fault_0187_P1 | 3 phase fault on KIRBY 3 (524088) 115 kV Bus a. Apply Fault at the KIRBY 3 (524088) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from KIRBY 3 (524088) 115 kV Bus to MCCLELLAN 3 (523804) 115 kV Bus CKT 1 b. 2. Trip branch from MCCLELLAN 3 (523804) 115 kV Bus to MCLEAN 3 (523811) 115 kV Bus CKT 1 b. 3. Trip branch from MCLEAN 3 (523811) 115 kV Bus to SHAM 3WT (512107) 115 kV Bus CKT 1 b. 4. Trip three winding transformer from SHAM 3WT (512107) 115 kV Bus to SHAM 2WT (512106) 69 kV Bus to SR1TERT (512109) 14.4 kV Bus CKT 1 b. 5. Drop Load 1 at MCCLELLAN 3 (523804) 115 kV Bus b. 6. Drop Load 1 at MCLEAN 3 (523811) 115 kV Bus b. 7. Drop Load D1 at MCLEAN 3 (523811) 115 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25W | Transfer | Group5_Fault_0188_P1 | 3 phase fault on CAMX/AGR TP3 (523485) 115 kV Bus a. Apply Fault at the CAMX/AGR TP3 (523485) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from CAMX/AGR TP3 (523485) 115 kV Bus to W_BORGER_TP3 (523516) 115 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | No | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points) |  | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25W | Transfer | Group5_Fault_0189_P1 | 3 phase fault on BLKHAWK_E 3 (523346) 115 kV Bus a. Apply Fault at the BLKHAWK_E 3 (523346) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from BLKHAWK_E 3 (523346) 115 kV Bus to BLKHAWK_W 3 (523344) 115 kV Bus CKT "@1" c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | No | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points) |  | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25W | Transfer | Group5_Fault_0190_P1 | 3 phase fault on BLKHAWK_E 3 (523346) 115 kV Bus a. Apply Fault at the BLKHAWK_E 3 (523346) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from BLKHAWK_E 3 (523346) 115 kV Bus to CPCOKER 3 (523470) 115 kV Bus CKT 1 b. 2. Trip branch from CPCOKER 3 (523470) 115 kV Bus to BLKHAWK_W 3 (523344) 115 kV Bus CKT 1 b. 3. Drop Load 1 at CPCOKER 3 (523470) 115 kV Bus b. 4. Drop Load 1 at CPCOKER 3 (523470) 115 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | No | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points) |  | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25W | Transfer | Group5_Fault_0191_P1 | 3 phase fault on O.K.U.-7 (511456) 345 kV Bus a. Apply Fault at the O.K.U.-7 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from O.K.U.-7 (511456) 345 kV Bus to OKLAUN HVDC7 (511565) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | No | Yes | Yes | Yes | No | Yes | Damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer
05 - Southwest | 25W | Transfer | Group5_Fault_0192_P1 | 3 phase fault on TUCO_INT 7 (525832) 345 kV Bus a. Apply Fault at the TUCO_INT 7 (525832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from TUCO_INT 7 (525832) 345 kV Bus to YOAKUM_345 (526936) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | No | No | Damping issues observed. Low voltage ride through fails due to the tripping of G18-115-GEN10 and G18-115-GEN20 units. No cascading was observed and the issue was localised. Model tuning is recommended. | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 763084 [G18-073-GEN20.6600]
05 - Southwest | 25W | Transfer | Group5_Fault_0193_P1 | 3 phase fault on YOAKUM_345 (526936) 345 kV Bus a. Apply Fault at the YOAKUM_345 (526936) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from YOAKUM_345 (526936) 345 kV Bus to HOBBS_INT 7 (527896) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | No | No | Damping issues observed | Potter to Tolk 345 kV Double Circuit Line Build Potter to Chisholm 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer Potter to Tolk 345 kV | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000], 763397 [G18-124-GEN1], 763309 [G18-112-GEN1]
05 - Southwest | 25W | Transfer | Group5_Fault_0194_P1 | 3 phase fault on YOAKUM_345 (526936) 345 kV Bus a. Apply Fault at the YOAKUM_345 (526936) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from YOAKUM_345 (526936) 345 kV Bus to HOBBS_INT 7 (527896) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | No | No | No | No | No | No | No | Out Of Step Generators and damping issues observed | Potter to Tolk 345 kV Double Circuit Line Build Potter to Chisholm 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer Potter to Tolk 345 kV | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000], 763397 [G18-124-GEN1], 763309 [G18-112-GEN1]
05 - Southwest | 25W | Transfer | Group5_Fault_0195_P1 | 3 phase fault on YOAKUM_345 (526936) 345 kV Bus a. Apply Fault at the YOAKUM_345 (526936) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from YOAKUM_345 (526936) 345 kV Bus to YOAKUM 6 (526935) 230 kV Bus to YOAKUM_TR1 (526937) 13.2 kV Bus CKT 1 | P1 | No | No | No | No | Yes | No | No | Out Of Step Generators and damping issues observed | Potter to Tolk 345 kV Double Circuit Line Build Potter to Chisholm 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer Potter to Tolk 345 kV | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000], 763397 [G18-124-GEN1], 763309 [G18-112-GEN1]
05 - Southwest | 25W | Transfer | Group5_Fault_0196_P1 | 3 phase fault on TUCO_INT 7 (525832) 345 kV Bus a. Apply Fault at the TUCO_INT 7 (525832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from TUCO_INT 7 (525832) 345 kV Bus to CRAWFISH_DR (560022) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | No | Yes | No | Yes | No | No | Damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 763084 [G18-073-GEN20.6600]
05 - Southwest | 25W | Transfer | Group5_Fault_0197_P1 | 3 phase fault on CRAWFISH_DR (560022) 345 kV Bus a. Apply Fault at the CRAWFISH_DR (560022) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from CRAWFISH_DR (560022) 345 kV Bus to TUCO_INT 7 (525832) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | No | Yes | No | Yes | No | No | Damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 763084 [G18-073-GEN20.6600]
05 - Southwest | 25W | Transfer | Group5_Fault_0198_P1 | 3 phase fault on G17-151TAP (762216) 345 kV Bus a. Apply Fault at the G17-151TAP (762216) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from G17-151TAP (762216) 345 kV Bus to CRAWFISH_DR (560022) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | No | Yes | Yes | No | Yes | Damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer
05 - Southwest | 25W | Transfer | Group5_Fault_0199_P1 | 3 phase fault on CROSSROADS 7 (527656) 345 kV Bus a. Apply Fault at the CROSSROADS 7 (527656) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from CROSSROADS 7 (527656) 345 kV Bus to EDDY_CNTY 7 (527802) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | No | No | No | No | Yes | No | No | Out Of Step Generators and damping issues observed | Potter to Tolk 345 kV Double Circuit Line Build Potter to Chisholm 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer Potter to Tolk 345 kV | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000], 763397 [G18-124-GEN1], 763309 [G18-112-GEN1]
05 - Southwest | 25W | Transfer | Group5_Fault_0200_P1 | 3 phase fault on HOBBS_INT 7 (527896) 345 kV Bus a. Apply Fault at the HOBBS_INT 7 (527896) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from HOBBS_INT 7 (527896) 345 kV Bus to HOBBS_INT 6 (527894) 230 kV Bus to HOBBS_TR3 1 (527895) 13.2 kV Bus CKT 1 | P1 | No | No | No | Yes | No | No | No | Out Of Step Generators and damping issues observed | Potter to Tolk 345 kV Double Circuit Line Build Potter to Chisholm 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer Potter to Tolk 345 kV | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000], 763397 [G18-124-GEN1], 763309 [G18-112-GEN1]
05 - Southwest | 25W | Transfer | Group5_Fault_0201_P1 | 3 phase fault on YOAKUM 6 (526935) 230 kV Bus a. Apply Fault at the YOAKUM 6 (526935) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from YOAKUM 6 (526935) 230 kV Bus to YOAKUM 3 (526934) 115 kV Bus to YOAKUM_TR2 1 (526932) 13.2 kV Bus CKT 2 | P1 | No | No | No | Yes | No | No | No | Out Of Step Generators and damping issues observed | Potter to Tolk 345 kV Double Circuit Line Build Potter to Chisholm 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer Potter to Tolk 345 kV | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000], 763397 [G18-124-GEN1], 763309 [G18-112-GEN1]
05 - Southwest | 25W | Transfer | Group5_Fault_0202_P1 | 3 phase fault on YOAKUM 6 (526935) 230 kV Bus a. Apply Fault at the YOAKUM 6 (526935) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from YOAKUM 6 (526935) 230 kV Bus to YOAKUM 3 (526934) 115 kV Bus to YOAKUM_TR1 1 (526931) 13.2 kV Bus CKT 1 | P1 | No | No | No | No | No | No | No | Out Of Step Generators and damping issues observed | Potter to Tolk 345 kV Double Circuit Line Build Potter to Chisholm 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer Potter to Tolk 345 kV | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000], 763397 [G18-124-GEN1], 763309 [G18-112-GEN1]
05 - Southwest | 25W | Transfer | Group5_Fault_0203_P1 | 3 phase fault on YOAKUM 6 (526935) 230 kV Bus a. Apply Fault at the YOAKUM 6 (526935) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from YOAKUM 6 (526935) 230 kV Bus to AMOCO_SS 6 (526460) 230 kV Bus CKT 1 b. 2. Trip branch from AMOCO_SS 6 (526460) 230 kV Bus to SUNDOWN 6 (526435) 230 kV Bus CKT 1 b. 3. Drop Load 1 at AMOCO_SS 6 (526460) 230 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | No | No | No | No | No | No | No | Out Of Step Generators and damping issues observed | Potter to Tolk 345 kV Double Circuit Line Build Potter to Chisholm 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer Potter to Tolk 345 kV | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000], 763397 [G18-124-GEN1], 763309 [G18-112-GEN1]
05 - Southwest | 25W | Transfer | Group5_Fault_0204_P1 | 3 phase fault on YOAKUM 6 (526935) 230 kV Bus a. Apply Fault at the YOAKUM 6 (526935) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from YOAKUM 6 (526935) 230 kV Bus to INK_BASIN 6 (527028) 230 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | No | No | No | Yes | No | No | No | Out Of Step Generators and damping issues observed | Potter to Tolk 345 kV Double Circuit Line Build Potter to Chisholm 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer Potter to Tolk 345 kV | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000], 763397 [G18-124-GEN1], 763309 [G18-112-GEN1]
05 - Southwest | 25W | Transfer | Group5_Fault_0205_P1 | 3 phase fault on YOAKUM 6 (526935) 230 kV Bus a. Apply Fault at the YOAKUM 6 (526935) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from YOAKUM 6 (526935) 230 kV Bus to BRU_SUB 6 (527009) 230 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | No | No | No | No | Yes | No | No | Out Of Step Generators and damping issues observed | Potter to Tolk 345 kV Double Circuit Line Build Potter to Chisholm 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer Potter to Tolk 345 kV | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000], 763397 [G18-124-GEN1], 763309 [G18-112-GEN1]
05 - Southwest | 25W | Transfer | Group5_Fault_0206_P1 | 3 phase fault on YOAKUM 6 (526935) 230 kV Bus a. Apply Fault at the YOAKUM 6 (526935) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from YOAKUM 6 (526935) 230 kV Bus to MUSTANG 6 (527149) 230 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | No | No | No | No | Yes | No | No | Out Of Step Generators and damping issues observed | Potter to Tolk 345 kV Double Circuit Line Build Potter to Chisholm 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer Potter to Tolk 345 kV | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000], 763397 [G18-124-GEN1], 763309 [G18-112-GEN1]
05 - Southwest | 25W | Transfer | Group5_Fault_0207_P1 | 3 phase fault on TOLK 7 (525549) 345 kV Bus a. Apply Fault at the TOLK 7 (525549) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from TOLK 7 (525549) 345 kV Bus to POTTER_CO 7 (523961) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | Group5_Fault_0208_P1 | 3 phase fault on EDDY_CNTY 7 (527802) 345 kV Bus a. Apply Fault at the EDDY_CNTY 7 (527802) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from EDDY_CNTY 7 (527802) 345 kV Bus to KIOWA 7 (527965) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | No | No | No | No | No | No | No | Out Of Step Generators and damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25W | Transfer | Group5_Fault_0209_P1 | 3 phase fault on EDDY_CNTY 7 (527802) 345 kV Bus a. Apply Fault at the EDDY_CNTY 7 (527802) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from EDDY_CNTY 7 (527802) 345 kV Bus to CROSSROADS 7 (527656) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | No | No | No | No | No | No | No | Out Of Step Generators and damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25W | Transfer | Group5_Fault_0210_P1 | 3 phase fault on KIOWA 7 (527965) 345 kV Bus a. Apply Fault at the KIOWA 7 (527965) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from KIOWA 7 (527965) 345 kV Bus to N_LOVING 7 (528185) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | No | No | No | No | No | No | No | Out Of Step Generators and damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25W | Transfer | Group5_Fault_0211_P1 | 3 phase fault on KIOWA 7 (527965) 345 kV Bus a. Apply Fault at the KIOWA 7 (527965) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from KIOWA 7 (527965) 345 kV Bus to RDRUNNER 7 (528027) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | No | No | No | No | Yes | No | No | Out Of Step Generators and damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25W | Transfer | Group5_Fault_0212_P1 | 3 phase fault on KIOWA 7 (527965) 345 kV Bus a. Apply Fault at the KIOWA 7 (527965) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from KIOWA 7 (527965) 345 kV Bus to KIOWA 3 (527966) 115 kV Bus to KIOWA_TR1 1 (527964) 13.2 kV Bus CKT 1 b. 2. Trip branch from KIOWA 3 (527966) 115 kV Bus to POTASH_JCT 3 (527962) 115 kV Bus CKT 1 | P1 | No | No | No | No | No | No | No | Out Of Step Generators and damping issues observed | Potter to Tolk 345 kV Double Circuit Line Build Potter to Chisholm 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer Potter to Tolk 345 kV | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000], 763397 [G18-124-GEN1], 763309 [G18-112-GEN1]
05 - Southwest | 25W | Transfer | Group5_Fault_0213_P1 | 3 phase fault on HOBBS_INT 6 (527894) 230 kV Bus a. Apply Fault at the HOBBS_INT 6 (527894) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from HOBBS_INT 6 (527894) 230 kV Bus to ANDREWS 6 (528604) 230 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | No | No | Damping issues observed | Potter to Tolk 345 kV Double Circuit Line Build Potter to Chisholm 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer Potter to Tolk 345 kV | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000], 763397 [G18-124-GEN1], 763309 [G18-112-GEN1]
05 - Southwest | 25W | Transfer | Group5_Fault_0214_P1 | 3 phase fault on HOBBS_INT 6 (527894) 230 kV Bus a. Apply Fault at the HOBBS_INT 6 (527894) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from HOBBS_INT 6 (527894) 230 kV Bus to INK_BASIN 6 (527028) 230 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | No | No | No | Yes | No | No | No | Out Of Step Generators and damping issues observed | Potter to Tolk 345 kV Double Circuit Line Build Potter to Chisholm 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer Potter to Tolk 345 kV | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000], 763397 [G18-124-GEN1], 763309 [G18-112-GEN1]
05 - Southwest | 25W | Transfer | Group5_Fault_0215_P1 | 3 phase fault on HOBBS_INT 6 (527894) 230 kV Bus a. Apply Fault at the HOBBS_INT 6 (527894) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from HOBBS_INT 6 (527894) 230 kV Bus to CUNNIGHM_S 6 (527867) 230 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | No | No | Damping issues observed | Potter to Tolk 345 kV Double Circuit Line Build Potter to Chisholm 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer Potter to Tolk 345 kV | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000], 763397 [G18-124-GEN1], 763309 [G18-112-GEN1]
05 - Southwest | 25W | Transfer | Group5_Fault_0216_P1 | 3 phase fault on HOBBS_INT 6 (527894) 230 kV Bus a. Apply Fault at the HOBBS_INT 6 (527894) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from HOBBS_INT 6 (527894) 230 kV Bus to HOBBS_INT 3 (527891) 115 kV Bus to HOBBS_TR2 1 (527889) 13.2 kV Bus CKT 2 | P1 | No | No | No | No | Yes | No | No | Out Of Step Generators and damping issues observed | Potter to Tolk 345 kV Double Circuit Line Build Potter to Chisholm 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer Potter to Tolk 345 kV | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000], 763397 [G18-124-GEN1], 763309 [G18-112-GEN1]
05 - Southwest | 25W | Transfer | Group5_Fault_0217_P1 | 3 phase fault on HOBBS_INT 6 (527894) 230 kV Bus a. Apply Fault at the HOBBS_INT 6 (527894) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from HOBBS_INT 6 (527894) 230 kV Bus to HOBBS_INT 3 (527891) 115 kV Bus to HOBBS_TR1 1 (527890) 13.2 kV Bus CKT 1 | P1 | No | No | No | Yes | No | No | No | Out Of Step Generators and damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25W | Transfer | Group5_Fault_0218_P1 | 3 phase fault on BRU_SUB 6 (527009) 230 kV Bus a. Apply Fault at the BRU_SUB 6 (527009) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from BRU_SUB 6 (527009) 230 kV Bus to XTO_MAHONEY6 (527011) 230 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | No | No | No | Yes | No | No | No | Out Of Step Generators and damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25W | Transfer | Group5_Fault_0219_P1 | 3 phase fault on BRU_SUB 6 (527009) 230 kV Bus a. Apply Fault at the BRU_SUB 6 (527009) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from BRU_SUB 6 (527009) 230 kV Bus to OXYBRU 6 (527010) 230 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | No | No | No | No | No | No | No | Out Of Step Generators and damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25W | Transfer | Group5_Fault_0220_P1 | 3 phase fault on YOAKUM 3 (526934) 115 kV Bus a. Apply Fault at the YOAKUM 3 (526934) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from YOAKUM 3 (526934) 115 kV Bus to PLAINS_INT 3 (526928) 115 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | No | No | No | No | Yes | No | Yes | Out Of Step Generators and damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer
05 - Southwest | 25W | Transfer | Group5_Fault_0221_P1 | 3 phase fault on YOAKUM 3 (526934) 115 kV Bus a. Apply Fault at the YOAKUM 3 (526934) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from YOAKUM 3 (526934) 115 kV Bus to ARCO_TP 3 (527041) 115 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | No | No | No | No | No | No | Yes | Out Of Step Generators and damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer
05 - Southwest | 25W | Transfer | Group5_Fault_0222_P1 | 3 phase fault on G18-015-TAP (762467) 345 kV Bus a. Apply Fault at the G18-015-TAP (762467) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from G18-015-TAP (762467) 345 kV Bus to G18-092-TAP (763215) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | No | No | No | No | No | No | No | Out Of Step Generators and damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25W | Transfer | Group5_Fault_0223_P1 | 3 phase fault on G18-015-TAP (762467) 345 kV Bus a. Apply Fault at the G18-015-TAP (762467) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from G18-015-TAP (762467) 345 kV Bus to G17-151TAP (762216) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | No | No | No | No | No | No | No | Out Of Step Generators and damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25W | Transfer | Group5_Fault_0224_P1 | 3 phase fault on CARLISLE 6 (526161) 230 kV Bus a. Apply Fault at the CARLISLE 6 (526161) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from CARLISLE 6 (526161) 230 kV Bus to CARLISLE 3 (526160) 115 kV Bus to CRLSLE_TR1 1 (526157) 13.2 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Low voltage ride through fails due to the tripping of G18-115-GEN10 and G18-115-GEN20 units. No cascading was observed and the issue was localised. Model tuning is recommended.
05 - Southwest | 25W | Transfer | Group5_Fault_0225_P1 | 3 phase fault on TUCO_INT 3 (525828) 115 kV Bus a. Apply Fault at the TUCO_INT 3 (525828) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from TUCO_INT 3 (525828) 115 kV Bus to STANTON_W 3 (526076) 115 kV Bus CKT 1 b. 2. Trip branch from STANTON_W 3 (526076) 115 kV Bus to INDIANA 3 (526146) 115 kV Bus CKT 1 b. 3. Trip branch from INDIANA 3 (526146) 115 kV Bus to SP-ERSKINE 3 (526109) 115 kV Bus CKT 1 b. 4. Trip branch from SP-ERSKINE 3 (526109) 115 kV Bus to CARLISLE 3 (526160) 115 kV Bus CKT 1 b. 5. Drop Load 1 at STANTON_W 3 (526076) 115 kV Bus b. 6. Drop Load 1 at INDIANA 3 (526146) 115 kV Bus b. 7. Drop Load 2 at INDIANA 3 (526146) 115 kV Bus b. 8. Drop Load 1 at SP-ERSKINE 3 (526109) 115 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | No | No | Damping issues observed. Low voltage ride through fails due to the tripping of G18-115-GEN10 and G18-115-GEN20 units. No cascading was observed and the issue was localised. Model tuning is recommended. | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer
05 - Southwest | 25W | Transfer | Group5_Fault_0226_P1 | 3 phase fault on TUCO_INT 3 (525828) 115 kV Bus a. Apply Fault at the TUCO_INT 3 (525828) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from TUCO_INT 3 (525828) 115 kV Bus to FLOYD_CNTY 3 (525780) 115 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | Group5_Fault_0227_P1 | 3 phase fault on TUCO_INT 3 (525828) 115 kV Bus a. Apply Fault at the TUCO_INT 3 (525828) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from TUCO_INT 3 (525828) 115 kV Bus to TUCO_INT 2 (525826) 69 kV Bus to TUCO_TR5 1 (525822) 13.2 kV Bus CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | Group5_Fault_0228_P1 | 3 phase fault on TUCO_INT 3 (525828) 115 kV Bus a. Apply Fault at the TUCO_INT 3 (525828) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from TUCO_INT 3 (525828) 115 kV Bus to TUCO_INT 2 (525826) 69 kV Bus to TUCO_TR6 1 (525823) 13.2 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | Group5_Fault_0229_P1 | 3 phase fault on TUCO_INT 3 (525828) 115 kV Bus a. Apply Fault at the TUCO_INT 3 (525828) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from TUCO_INT 3 (525828) 115 kV Bus to TUCO_INT2 2 (525816) 69 kV Bus to TUCO_TR7 1 (525814) 13.2 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | Group5_Fault_0230_P1 | 3 phase fault on EDDY_NORTH 6 (527799) 230 kV Bus a. Apply Fault at the EDDY_NORTH 6 (527799) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from EDDY_NORTH 6 (527799) 230 kV Bus to CUNNIGHM_N 6 (527865) 230 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | No | No | No | No | Yes | No | No | Out Of Step Generators and damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25W | Transfer | Group5_Fault_0231_P1 | 3 phase fault on EDDY_NORTH 6 (527799) 230 kV Bus a. Apply Fault at the EDDY_NORTH 6 (527799) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from EDDY_NORTH 6 (527799) 230 kV Bus to EDDY_STH 3 (527793) 115 kV Bus to EDDY_TR3 1 (527795) 13.2 kV Bus CKT 2 | P1 | No | No | No | Yes | No | No | No | Out Of Step Generators and damping issues observed | Potter to Tolk 345 kV Double Circuit Line Build Potter to Chisholm 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer Potter to Tolk 345 kV | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000], 763397 [G18-124-GEN1], 763309 [G18-112-GEN1]
05 - Southwest | 25W | Transfer | Group5_Fault_0232_P1 | 3 phase fault on EDDY_NORTH 6 (527799) 230 kV Bus a. Apply Fault at the EDDY_NORTH 6 (527799) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from EDDY_NORTH 6 (527799) 230 kV Bus to EDDY_NTH 3 (527798) 115 kV Bus to EDDY_TR2 1 (527797) 13.2 kV Bus CKT 1 | P1 | No | No | No | No | No | No | No | Out Of Step Generators and damping issues observed | Potter to Tolk 345 kV Double Circuit Line Build Potter to Chisholm 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer Potter to Tolk 345 kV | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000], 763397 [G18-124-GEN1], 763309 [G18-112-GEN1]
05 - Southwest | 25W | Transfer | Group5_Fault_0233_P1 | 3 phase fault on RDRUNNER 7 (528027) 345 kV Bus a. Apply Fault at the RDRUNNER 7 (528027) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from RDRUNNER 7 (528027) 345 kV Bus to RDRUNNER 3 (528025) 115 kV Bus to RDRNNER_TR11 (528023) 13.2 kV Bus CKT 1 | P1 | No | No | No | No | No | No | No | Out Of Step Generators and damping issues observed | Potter to Tolk 345 kV Double Circuit Line Build Potter to Chisholm 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer Potter to Tolk 345 kV | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000], 763397 [G18-124-GEN1], 763309 [G18-112-GEN1]
05 - Southwest | 25W | Transfer | Group5_Fault_0234_P1 | 3 phase fault on RDRUNNER 7 (528027) 345 kV Bus a. Apply Fault at the RDRUNNER 7 (528027) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from RDRUNNER 7 (528027) 345 kV Bus to PHANTOM 7 (528015) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | No | No | No | No | No | No | No | Out Of Step Generators and damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25W | Transfer | Group5_Fault_0235_P1 | 3 phase fault on N_LOVING 7 (528185) 345 kV Bus a. Apply Fault at the N_LOVING 7 (528185) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from N_LOVING 7 (528185) 345 kV Bus to NORTH_LOVNG3 (528182) 115 kV Bus to N_LOVING TR1 (528186) 13.2 kV Bus CKT 1 | P1 | No | No | No | No | No | No | No | Out Of Step Generators and damping issues observed | Potter to Tolk 345 kV Double Circuit Line Build Potter to Chisholm 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer Potter to Tolk 345 kV | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000], 763397 [G18-124-GEN1], 763309 [G18-112-GEN1]
05 - Southwest | 25W | Transfer | Group5_Fault_0236_P1 | 3 phase fault on N_LOVING 7 (528185) 345 kV Bus a. Apply Fault at the N_LOVING 7 (528185) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from N_LOVING 7 (528185) 345 kV Bus to CHINA_DRAW 7 (528223) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | No | No | No | Yes | No | No | No | Out Of Step Generators and damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25W | Transfer | Group5_Fault_0237_P1 | 3 phase fault on POTASH_JCT 3 (527962) 115 kV Bus a. Apply Fault at the POTASH_JCT 3 (527962) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from POTASH_JCT 3 (527962) 115 kV Bus to INTREPDW_TP3 (527999) 115 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | No | No | No | No | No | No | No | Out Of Step Generators and damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25W | Transfer | Group5_Fault_0238_P1 | 3 phase fault on POTASH_JCT 6 (527963) 230 kV Bus a. Apply Fault at the POTASH_JCT 6 (527963) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from POTASH_JCT 6 (527963) 230 kV Bus to POTASH_JCT 3 (527962) 115 kV Bus to POTASH_TR1 1 (527958) 13.2 kV Bus CKT 1 | P1 | No | No | No | Yes | No | No | No | Out Of Step Generators and damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25W | Transfer | Group5_Fault_0239_P1 | 3 phase fault on POTASH_JCT 3 (527962) 115 kV Bus a. Apply Fault at the POTASH_JCT 3 (527962) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from POTASH_JCT 3 (527962) 115 kV Bus to POTASH_JCT 2 (527961) 69 kV Bus to POTASH_TR2 1 (527959) 13.2 kV Bus CKT 1 | P1 | No | No | No | Yes | No | No | No | Out Of Step Generators and damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25W | Transfer | Group5_Fault_0240_P1 | 3 phase fault on POTASH_JCT 3 (527962) 115 kV Bus a. Apply Fault at the POTASH_JCT 3 (527962) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from POTASH_JCT 3 (527962) 115 kV Bus to POTASH_JCT 2 (527961) 69 kV Bus to POTASH_TR3 1 (527960) 13.2 kV Bus CKT 2 | P1 | No | No | No | No | No | No | No | Out Of Step Generators and damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25W | Transfer | Group5_Fault_0241_P1 | 3 phase fault on ANDREWS 6 (528604) 230 kV Bus a. Apply Fault at the ANDREWS 6 (528604) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from ANDREWS 6 (528604) 230 kV Bus to ANDREWS 3 (528602) 115 kV Bus to ANDREWS_TR21 (528600) 13.2 kV Bus CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | Group5_Fault_0242_P1 | 3 phase fault on ANDREWS 6 (528604) 230 kV Bus a. Apply Fault at the ANDREWS 6 (528604) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from ANDREWS 6 (528604) 230 kV Bus to ANDREWS 3 (528602) 115 kV Bus to ANDREWS_TR11 (528601) 13.2 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | Group5_Fault_0243_P1 | 3 phase fault on POTASH_JCT 6 (527963) 230 kV Bus a. Apply Fault at the POTASH_JCT 6 (527963) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from POTASH_JCT 6 (527963) 230 kV Bus to PECOS 6 (528179) 230 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | No | No | No | No | Yes | No | No | Out Of Step Generators and damping issues observed | Potter to Tolk 345 kV Double Circuit Line Build Potter to Chisholm 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer Potter to Tolk 345 kV | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000], 763397 [G18-124-GEN1], 763309 [G18-112-GEN1]
05 - Southwest | 25W | Transfer | Group5_Fault_0244_P1 | 3 phase fault on POTASH_JCT 6 (527963) 230 kV Bus a. Apply Fault at the POTASH_JCT 6 (527963) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from POTASH_JCT 6 (527963) 230 kV Bus to CUNNIGHM_N 6 (527865) 230 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | No | No | No | No | Yes | No | No | Out Of Step Generators and damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25W | Transfer | Group5_Fault_0245_P1 | 3 phase fault on CARLISLE 3 (526160) 115 kV Bus a. Apply Fault at the CARLISLE 3 (526160) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from CARLISLE 3 (526160) 115 kV Bus to LP-DOUD_TP 3 (526162) 115 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 763309 [G18-112-GEN10.6600]
05 - Southwest | 25W | Transfer | Group5_Fault_0246_P1 | 3 phase fault on HITCHLAND 7 (523097) 345 kV Bus a. Apply Fault at the HITCHLAND 7 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from HITCHLAND 7 (523097) 345 kV Bus to CARPENTER 7 (523823) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | No | No | No | No | Yes | No | No | Out Of Step Generators and damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25W | Transfer | Group5_Fault_0247_P1 | 3 phase fault on RDRUNNER 3 (528025) 115 kV Bus a. Apply Fault at the RDRUNNER 3 (528025) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from RDRUNNER 3 (528025) 115 kV Bus to AGAVE_RHILL3 (528230) 115 kV Bus CKT 1 b. 2. Trip branch from AGAVE_RHILL3 (528230) 115 kV Bus to OCHOA 3 (528232) 115 kV Bus CKT 1 b. 3. Drop Load 1 at AGAVE_RHILL3 (528230) 115 kV Bus b. 4. Drop Load 1 at OCHOA 3 (528232) 115 kV Bus b. 5. Drop Load 1* at OCHOA 3 (528232) 115 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | No | No | No | Yes | No | No | No | Out Of Step Generators and damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25W | Transfer | Group5_Fault_0248_P1 | 3 phase fault on RDRUNNER 3 (528025) 115 kV Bus a. Apply Fault at the RDRUNNER 3 (528025) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from RDRUNNER 3 (528025) 115 kV Bus to AGAVE_RHIL23 (528231) 115 kV Bus CKT 1 b. 2. Drop Load 1 at AGAVE_RHIL23 (528231) 115 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | No | No | No | No | Yes | No | No | Out Of Step Generators and damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25W | Transfer | Group5_Fault_0249_P1 | 3 phase fault on RDRUNNER 3 (528025) 115 kV Bus a. Apply Fault at the RDRUNNER 3 (528025) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from RDRUNNER 3 (528025) 115 kV Bus to RR_SVC_HV 3 (528024) 115 kV Bus CKT Z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25W | Transfer | Group5_Fault_0250_P1 | 3 phase fault on NORTH_LOVNG3 (528182) 115 kV Bus a. Apply Fault at the NORTH_LOVNG3 (528182) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from NORTH_LOVNG3 (528182) 115 kV Bus to BLACKRIVER 3 (528193) 115 kV Bus CKT 1 b. 2. Trip branch from BLACKRIVER 3 (528193) 115 kV Bus to SENDERO +3 (528184) 115 kV Bus CKT 1 b. 3. Trip branch from SENDERO +3 (528184) 115 kV Bus to BLCKRVR_DST3 (528206) 115 kV Bus CKT 1 b. 4. Trip branch from BLCKRVR_DST3 (528206) 115 kV Bus to CHINA_DRAW 3 (528222) 115 kV Bus CKT 1 b. 5. Drop Load 1 at NORTH_LOVNG3 (528182) 115 kV Bus b. 6. Drop Load 1 at BLACKRIVER 3 (528193) 115 kV Bus b. 7. Drop Load 1 at SENDERO +3 (528184) 115 kV Bus b. 8. Drop Load 2 at SENDERO +3 (528184) 115 kV Bus b. 9. Drop Load 1 at BLCKRVR_DST3 (528206) 115 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | No | No | No | No | No | No | No | Out Of Step Generators and damping issues observed | Potter to Tolk 345 kV Double Circuit Line Build Potter to Chisholm 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer Potter to Tolk 345 kV | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000], 763397 [G18-124-GEN1], 763309 [G18-112-GEN1]
05 - Southwest | 25W | Transfer | Group5_Fault_0251_P1 | 3 phase fault on ANDREWS 3 (528602) 115 kV Bus a. Apply Fault at the ANDREWS 3 (528602) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from ANDREWS 3 (528602) 115 kV Bus to NA_ENRICH 3 (528603) 115 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | Group5_Fault_0252_P1 | 3 phase fault on ALRDCRTZ_TP3 (527030) 115 kV Bus a. Apply Fault at the ALRDCRTZ_TP3 (527030) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from ALRDCRTZ_TP3 (527030) 115 kV Bus to ALLRED_SUB 3 (527024) 115 kV Bus CKT 1 b. 2. Trip branch from ALLRED_SUB 3 (527024) 115 kV Bus to APACHE_ROB 3 (527022) 115 kV Bus CKT 1 b. 3. Trip branch from APACHE_ROB 3 (527022) 115 kV Bus to CORTEZ 3 (527021) 115 kV Bus CKT 1 b. 4. Drop Load 1 at ALLRED_SUB 3 (527024) 115 kV Bus b. 5. Drop Load 1 at APACHE_ROB 3 (527022) 115 kV Bus b. 6. Drop Load 1 at CORTEZ 3 (527021) 115 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | Group5_Fault_0253_P1 | 3 phase fault on ALRDCRTZ_TP3 (527030) 115 kV Bus a. Apply Fault at the ALRDCRTZ_TP3 (527030) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from ALRDCRTZ_TP3 (527030) 115 kV Bus to XTO_CORNEL+3 (527033) 115 kV Bus CKT 1 b. 2. Trip branch from XTO_CORNEL+3 (527033) 115 kV Bus to SHELLC3_TP 3 (527068) 115 kV Bus CKT 1 b. 3. Drop Load 1 at XTO_CORNEL+3 (527033) 115 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | Group5_Fault_0254_P1 | 3 phase fault on LP-DOUD_TP 3 (526162) 115 kV Bus a. Apply Fault at the LP-DOUD_TP 3 (526162) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from LP-DOUD_TP 3 (526162) 115 kV Bus to SP-WOLF_TP 3 (526481) 115 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | No | Yes | Damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer
05 - Southwest | 25W | Transfer | Group5_Fault_0255_P1 | 3 phase fault on NA_ENRICH 3 (528603) 115 kV Bus a. Apply Fault at the NA_ENRICH 3 (528603) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from NA_ENRICH 3 (528603) 115 kV Bus to DRINKARD 3 (528589) 115 kV Bus CKT 1 b. 2. Trip branch from DRINKARD 3 (528589) 115 kV Bus to DRINKARD_TP3 (528533) 115 kV Bus CKT 1 b. 3. Drop Load 1 at NA_ENRICH 3 (528603) 115 kV Bus b. 4. Drop Load 5* at NA_ENRICH 3 (528603) 115 kV Bus b. 5. Drop Load 1 at DRINKARD 3 (528589) 115 kV Bus b. 6. Drop Load 1* at DRINKARD 3 (528589) 115 kV Bus b. 7. Drop Shunt 1 at NA_ENRICH 3 (528603) 115 kV Bus b. 8. Drop Shunt 1 at DRINKARD 3 (528589) 115 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | Group5_Fault_0256_P1 | 3 phase fault on NA_ENRICH 3 (528603) 115 kV Bus a. Apply Fault at the NA_ENRICH 3 (528603) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from NA_ENRICH 3 (528603) 115 kV Bus to TARGA 3 (528605) 115 kV Bus CKT 1 b. 2. Trip branch from TARGA 3 (528605) 115 kV Bus to CARDINAL 3 (528596) 115 kV Bus CKT 1 b. 3. Drop Load 1 at NA_ENRICH 3 (528603) 115 kV Bus b. 4. Drop Load 5* at NA_ENRICH 3 (528603) 115 kV Bus b. 5. Drop Load 1 at TARGA 3 (528605) 115 kV Bus b. 6. Drop Shunt 1 at NA_ENRICH 3 (528603) 115 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | Group5_Fault_0257_P1 | 3 phase fault on SHELLC3_TP 3 (527068) 115 kV Bus a. Apply Fault at the SHELLC3_TP 3 (527068) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from SHELLC3_TP 3 (527068) 115 kV Bus to SHELL_C2 3 (527036) 115 kV Bus CKT 1 b. 2. Trip branch from SHELL_C2 3 (527036) 115 kV Bus to DENVER_S 3 (527136) 115 kV Bus CKT 1 b. 3. Drop Load 1 at SHELL_C2 3 (527036) 115 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25W | Transfer | Group5_Fault_0258_P1 | 3 phase fault on SHELLC3_TP 3 (527068) 115 kV Bus a. Apply Fault at the SHELLC3_TP 3 (527068) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from SHELLC3_TP 3 (527068) 115 kV Bus to SHELLC3 3 (527074) 115 kV Bus CKT 1 b. 2. Drop Load 1 at SHELLC3 3 (527074) 115 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25W | Transfer | Group5_Fault_0259_P1 | 3 phase fault on TUCO_INT 6 (525830) 230 kV Bus a. Apply Fault at the TUCO_INT 6 (525830) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from TUCO_INT 6 (525830) 230 kV Bus to JONES 6 (526337) 230 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 763084 [G18-073-GEN20.6600]
05 - Southwest | 25W | Transfer | Group5_Fault_0260_P1 | 3 phase fault on TUCO_INT 6 (525830) 230 kV Bus a. Apply Fault at the TUCO_INT 6 (525830) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from TUCO_INT 6 (525830) 230 kV Bus to ANTELOPE_1 6 (525840) 230 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  | Generator relays were disabled for the following generators: 763084 [G18-073-GEN20.6600]
05 - Southwest | 25W | Transfer | Group5_Fault_0261_P1 | 3 phase fault on TUCO_INT 6 (525830) 230 kV Bus a. Apply Fault at the TUCO_INT 6 (525830) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from TUCO_INT 6 (525830) 230 kV Bus to CARLISLE 6 (526161) 230 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 763084 [G18-073-GEN20.6600]
05 - Southwest | 25W | Transfer | Group5_Fault_0262_P1 | 3 phase fault on TUCO_INT 6 (525830) 230 kV Bus a. Apply Fault at the TUCO_INT 6 (525830) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from TUCO_INT 6 (525830) 230 kV Bus to SWISHER 6 (525213) 230 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | No | No | No | Yes | No | No | No | Out Of Step Generators and damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25W | Transfer | Group5_Fault_0263_P1 | 3 phase fault on HOBBS_INT 7 (527896) 345 kV Bus a. Apply Fault at the HOBBS_INT 7 (527896) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from HOBBS_INT 7 (527896) 345 kV Bus to KIOWA 7 (527965) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | No | No | No | No | No | No | No | Out Of Step Generators and damping issues observed | Potter to Tolk 345 kV Double Circuit Line Build Potter to Chisholm 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer Potter to Tolk 345 kV | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000], 763397 [G18-124-GEN1], 763309 [G18-112-GEN1]
05 - Southwest | 25W | Transfer | Group5_Fault_0264_P1 | 3 phase fault on CARLISLE 6 (526161) 230 kV Bus a. Apply Fault at the CARLISLE 6 (526161) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from CARLISLE 6 (526161) 230 kV Bus to WOLFFORTH 6 (526525) 230 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Low voltage ride through fails due to the tripping of G18-115-GEN10 and G18-115-GEN20 units. No cascading was observed and the issue was localised. Model tuning is recommended.
05 - Southwest | 25W | Transfer | Group5_Fault_0265_P1 | 3 phase fault on CARPENTER 7 (523823) 345 kV Bus a. Apply Fault at the CARPENTER 7 (523823) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from CARPENTER 7 (523823) 345 kV Bus to HARBNGR7 (531512) 345 kV Bus CKT Z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | Group5_Fault_0266_P1 | 3 phase fault on G18-092-TAP (763215) 345 kV Bus a. Apply Fault at the G18-092-TAP (763215) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from G18-092-TAP (763215) 345 kV Bus to O.K.U.-7 (511456) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | No | No | No | No | No | No | No | Out Of Step Generators and damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25W | Transfer | Group5_Fault_0267_P1 | 3 phase fault on HOBBS_INT 3 (527891) 115 kV Bus a. Apply Fault at the HOBBS_INT 3 (527891) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from HOBBS_INT 3 (527891) 115 kV Bus to CUNNINHAM 3 (527864) 115 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | No | No | No | No | Yes | No | No | Out Of Step Generators and damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25W | Transfer | Group5_Fault_0268_P1 | 3 phase fault on HOBBS_INT 3 (527891) 115 kV Bus a. Apply Fault at the HOBBS_INT 3 (527891) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from HOBBS_INT 3 (527891) 115 kV Bus to CUNNINHAM 3 (527864) 115 kV Bus CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | No | No | No | No | Yes | No | No | Out Of Step Generators and damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25W | Transfer | Group5_Fault_0269_P1 | 3 phase fault on HOBBS_INT 3 (527891) 115 kV Bus a. Apply Fault at the HOBBS_INT 3 (527891) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from HOBBS_INT 3 (527891) 115 kV Bus to BENSING 3 (528433) 115 kV Bus CKT 1 b. 2. Trip branch from BENSING 3 (528433) 115 kV Bus to HIGG 3 (527363) 115 kV Bus CKT 1 b. 3. Drop Load 1 at BENSING 3 (528433) 115 kV Bus b. 4. Drop Load 1* at BENSING 3 (528433) 115 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | No | No | No | Yes | No | No | No | Out Of Step Generators and damping issues observed | Potter to Tolk 345 kV Double Circuit Line Build Potter to Chisholm 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer Potter to Tolk 345 kV | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000], 763397 [G18-124-GEN1], 763309 [G18-112-GEN1]
05 - Southwest | 25W | Transfer | Group5_Fault_0270_P1 | 3 phase fault on HOBBS_INT 3 (527891) 115 kV Bus a. Apply Fault at the HOBBS_INT 3 (527891) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from HOBBS_INT 3 (527891) 115 kV Bus to MILLEN_TPW 3 (528434) 115 kV Bus CKT 1 b. 2. Trip branch from MILLEN_TPW 3 (528434) 115 kV Bus to MILLEN 3 (528435) 115 kV Bus CKT *1 b. 3. Trip branch from MILLEN 3 (528435) 115 kV Bus to MILLEN_TPE 3 (528436) 115 kV Bus CKT *1 b. 4. Trip branch from MILLEN_TPE 3 (528436) 115 kV Bus to NE_HOBBS 3 (528442) 115 kV Bus CKT 1 b. 5. Trip branch from NE_HOBBS 3 (528442) 115 kV Bus to TAYLOR 3 (528413) 115 kV Bus CKT 1 b. 6. Drop Load 1 at MILLEN 3 (528435) 115 kV Bus b. 7. Drop Load 1* at MILLEN 3 (528435) 115 kV Bus b. 8. Drop Load 1 at NE_HOBBS 3 (528442) 115 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | No | No | No | No | Yes | No | No | Out Of Step Generators and damping issues observed | Potter to Tolk 345 kV Double Circuit Line Build Potter to Chisholm 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer Potter to Tolk 345 kV | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000], 763397 [G18-124-GEN1], 763309 [G18-112-GEN1]
05 - Southwest | 25W | Transfer | Group5_Fault_0271_P1 | 3 phase fault on HOBBS_INT 3 (527891) 115 kV Bus a. Apply Fault at the HOBBS_INT 3 (527891) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from HOBBS_INT 3 (527891) 115 kV Bus to LE-WEST_SUB3 (528333) 115 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | No | No | No | No | Yes | No | No | Out Of Step Generators and damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25W | Transfer | Group5_Fault_0272_P1 | 3 phase fault on HOBBS_INT 3 (527891) 115 kV Bus a. Apply Fault at the HOBBS_INT 3 (527891) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from HOBBS_INT 3 (527891) 115 kV Bus to MADDOX 3 (528355) 115 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | No | No | No | No | Yes | No | No | Out Of Step Generators and damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25W | Transfer | Group5_Fault_0273_P1 | 3 phase fault on HOBBS_INT 3 (527891) 115 kV Bus a. Apply Fault at the HOBBS_INT 3 (527891) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from HOBBS_INT 3 (527891) 115 kV Bus to BENSING 3 (528433) 115 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | No | No | No | No | Yes | No | No | Out Of Step Generators and damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25W | Transfer | Group5_Fault_0274_P1 | 3 phase fault on CUNNINHAM 3 (527864) 115 kV Bus a. Apply Fault at the CUNNINHAM 3 (527864) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from CUNNINHAM 3 (527864) 115 kV Bus to BUCKEYE_TP 3 (528348) 115 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | No | No | No | No | No | No | No | Out Of Step Generators and damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25W | Transfer | Group5_Fault_0275_P1 | 3 phase fault on CUNNINHAM 3 (527864) 115 kV Bus a. Apply Fault at the CUNNINHAM 3 (527864) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from CUNNINHAM 3 (527864) 115 kV Bus to MADDOX 3 (528355) 115 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | No | No | No | Yes | No | No | No | Out Of Step Generators and damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25W | Transfer | Group5_Fault_0276_P1 | 3 phase fault on CUNNINHAM 3 (527864) 115 kV Bus a. Apply Fault at the CUNNINHAM 3 (527864) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from CUNNINHAM 3 (527864) 115 kV Bus to QUAHADA 3 (528394) 115 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | No | No | No | No | Yes | No | No | Out Of Step Generators and damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25W | Transfer | Group5_Fault_0277_P1 | 3 phase fault on CUNNINHAM 3 (527864) 115 kV Bus a. Apply Fault at the CUNNINHAM 3 (527864) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from CUNNINHAM 3 (527864) 115 kV Bus to MONUMNT_TP 3 (528568) 115 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | No | No | No | No | Yes | No | No | Out Of Step Generators and damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25W | Transfer | Group5_Fault_0278_P1 | 3 phase fault on CUNNINHAM 3 (527864) 115 kV Bus a. Apply Fault at the CUNNINHAM 3 (527864) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from CUNNINHAM 3 (527864) 115 kV Bus to CUNNIGHM_S 6 (527867) 230 kV Bus to CUNNHM_TR1 1 (527863) 13.2 kV Bus CKT 1 | P1 | No | No | No | No | Yes | No | No | Out Of Step Generators and damping issues observed | Potter to Tolk 345 kV Double Circuit Line Build Potter to Chisholm 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer Potter to Tolk 345 kV | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000], 763397 [G18-124-GEN1], 763309 [G18-112-GEN1]
05 - Southwest | 25W | Transfer | Group5_Fault_0279_P1 | 3 phase fault on LE-WEST_SUB3 (528333) 115 kV Bus a. Apply Fault at the LE-WEST_SUB3 (528333) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from LE-WEST_SUB3 (528333) 115 kV Bus to LE-NRTH_INT3 (528334) 115 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | Group5_Fault_0280_P1 | 3 phase fault on MADDOX 3 (528355) 115 kV Bus a. Apply Fault at the MADDOX 3 (528355) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from MADDOX 3 (528355) 115 kV Bus to MONUMENT 3 (528491) 115 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | No | No | No | No | Yes | No | No | Out Of Step Generators and damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25W | Transfer | Group5_Fault_0281_P1 | 3 phase fault on MADDOX 3 (528355) 115 kV Bus a. Apply Fault at the MADDOX 3 (528355) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from MADDOX 3 (528355) 115 kV Bus to G18-004-TAP (762442) 115 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | No | No | No | No | Yes | No | No | Out Of Step Generators and damping issues observed | Potter to Tolk 345 kV Double Circuit Line Build Potter to Chisholm 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer Potter to Tolk 345 kV | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000], 763397 [G18-124-GEN1], 763309 [G18-112-GEN1]
05 - Southwest | 25W | Transfer | Group5_Fault_0282_P1 | 3 phase fault on MADDOX 3 (528355) 115 kV Bus a. Apply Fault at the MADDOX 3 (528355) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from MADDOX 3 (528355) 115 kV Bus to PEARLE 3 (528392) 115 kV Bus CKT 1 b. 2. Trip branch from PEARLE 3 (528392) 115 kV Bus to ENRON_TP 3 (528317) 115 kV Bus CKT 1 b. 3. Drop Load 1 at PEARLE 3 (528392) 115 kV Bus b. 4. Drop Load 1* at PEARLE 3 (528392) 115 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | No | No | No | No | No | No | No | Out Of Step Generators and damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25W | Transfer | Group5_Fault_0283_P1 | 3 phase fault on HIGG 3 (527363) 115 kV Bus a. Apply Fault at the HIGG 3 (527363) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from HIGG 3 (527363) 115 kV Bus to HIGGEAST 3 (527286) 115 kV Bus CKT 1 b. 2. Trip branch from HIGGEAST 3 (527286) 115 kV Bus to DENVER_N 3 (527130) 115 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | Group5_Fault_0284_P1 | 3 phase fault on HIGG 3 (527363) 115 kV Bus a. Apply Fault at the HIGG 3 (527363) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from HIGG 3 (527363) 115 kV Bus to JOHNSON_DRW3 (527362) 115 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | Group5_Fault_0285_P1 | 3 phase fault on HIGG 3 (527363) 115 kV Bus a. Apply Fault at the HIGG 3 (527363) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from HIGG 3 (527363) 115 kV Bus to RUSSELL 3 (527284) 115 kV Bus CKT 1 b. 2. Drop Load 1 at RUSSELL 3 (527284) 115 kV Bus b. 3. Drop Load 2 at RUSSELL 3 (527284) 115 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | Group5_Fault_0286_P1 | 3 phase fault on INK_BASIN 6 (527028) 230 kV Bus a. Apply Fault at the INK_BASIN 6 (527028) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from INK_BASIN 6 (527028) 230 kV Bus to INK_BASIN 3 (527027) 115 kV Bus to INKBASN_TR 1 (527026) 13.2 kV Bus CKT 1 | P1 | Yes | No | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25W | Transfer | Group5_Fault_0287_P1 | 3 phase fault on CUNNIGHM_S 6 (527867) 230 kV Bus a. Apply Fault at the CUNNIGHM_S 6 (527867) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from CUNNIGHM_S 6 (527867) 230 kV Bus to CUNNIGHM_N 6 (527865) 230 kV Bus CKT *1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | No | No | No | No | Yes | No | No | Out Of Step Generators and damping issues observed | Potter to Tolk 345 kV Double Circuit Line Build Potter to Chisholm 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer Potter to Tolk 345 kV | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000], 763397 [G18-124-GEN1], 763309 [G18-112-GEN1]
05 - Southwest | 25W | Transfer | Group5_Fault_0288_P1 | 3 phase fault on ANDREWS 6 (528604) 230 kV Bus a. Apply Fault at the ANDREWS 6 (528604) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from ANDREWS 6 (528604) 230 kV Bus to ANDREWS 3 (528602) 115 kV Bus to ANDREWS_TR21 (528600) 13.2 kV Bus CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | Group5_Fault_0289_P1 | 3 phase fault on ANDREWS 6 (528604) 230 kV Bus a. Apply Fault at the ANDREWS 6 (528604) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from ANDREWS 6 (528604) 230 kV Bus to ANDREWS 3 (528602) 115 kV Bus to ANDREWS_TR11 (528601) 13.2 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | Group5_Fault_0290_P1 | 3 phase fault on TAYLOR 3 (528413) 115 kV Bus a. Apply Fault at the TAYLOR 3 (528413) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from TAYLOR 3 (528413) 115 kV Bus to JOHNSON_DRW3 (527362) 115 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | Group5_Fault_0291_P1 | 3 phase fault on TAYLOR 3 (528413) 115 kV Bus a. Apply Fault at the TAYLOR 3 (528413) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from TAYLOR 3 (528413) 115 kV Bus to W_BENDER 3 (528449) 115 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | Group5_Fault_0292_P1 | 3 phase fault on TAYLOR 3 (528413) 115 kV Bus a. Apply Fault at the TAYLOR 3 (528413) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from TAYLOR 3 (528413) 115 kV Bus to E_SANGER 3 (528470) 115 kV Bus CKT 1 b. 2. Trip branch from E_SANGER 3 (528470) 115 kV Bus to S_HOBBS 3 (528477) 115 kV Bus CKT 1 b. 3. Trip branch from S_HOBBS 3 (528477) 115 kV Bus to OXY_S_HOBBS3 (528480) 115 kV Bus CKT 1 b. 4. Trip branch from OXY_S_HOBBS3 (528480) 115 kV Bus to SW_4J44 3 (528484) 115 kV Bus CKT 1 b. 5. Trip branch from SW_4J44 3 (528484) 115 kV Bus to W_HOBBS 3 (528498) 115 kV Bus CKT 1 b. 6. Drop Load 1 at E_SANGER 3 (528470) 115 kV Bus b. 7. Drop Load 1 at S_HOBBS 3 (528477) 115 kV Bus b. 8. Drop Load 2 at S_HOBBS 3 (528477) 115 kV Bus b. 9. Drop Load 1 at OXY_S_HOBBS3 (528480) 115 kV Bus b. 10. Drop Load 2 at OXY_S_HOBBS3 (528480) 115 kV Bus b. 11. Drop Load 3 at OXY_S_HOBBS3 (528480) 115 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25W | Transfer | Group5_Fault_0293_P1 | 3 phase fault on LE-WAITS 3 (528325) 115 kV Bus a. Apply Fault at the LE-WAITS 3 (528325) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from LE-WAITS 3 (528325) 115 kV Bus to LE-NRTH_INT3 (528334) 115 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | Group5_Fault_0294_P1 | 3 phase fault on LE-LOVINTON2 (528618) 69 kV Bus a. Apply Fault at the LE-LOVINTON2 (528618) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from LE-LOVINTON2 (528618) 69 kV Bus to LE-NRTH_INT3 (528334) 115 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | Group5_Fault_0295_P1 | 3 phase fault on W_BENDER 3 (528449) 115 kV Bus a. Apply Fault at the W_BENDER 3 (528449) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from W_BENDER 3 (528449) 115 kV Bus to OXY_NHU_RCF3 (528574) 115 kV Bus CKT 1 b. 2. Trip branch from OXY_NHU_RCF3 (528574) 115 kV Bus to OXYPERMIAN 3 (528575) 115 kV Bus CKT 1 b. 3. Trip branch from OXYPERMIAN 3 (528575) 115 kV Bus to SANGER_SW 3 (528463) 115 kV Bus CKT 1 b. 4. Drop Load 1 at OXY_NHU_RCF3 (528574) 115 kV Bus b. 5. Drop Load 2 at OXY_NHU_RCF3 (528574) 115 kV Bus b. 6. Drop Load 2 at OXYPERMIAN 3 (528575) 115 kV Bus b. 7. Drop Load 1 at OXYPERMIAN 3 (528575) 115 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25W | Transfer | Group5_Fault_0296_P1 | 3 phase fault on W_BENDER 3 (528449) 115 kV Bus a. Apply Fault at the W_BENDER 3 (528449) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from W_BENDER 3 (528449) 115 kV Bus to N_HOBBS 3 (528456) 115 kV Bus CKT 1 b. 2. Drop Load 1 at N_HOBBS 3 (528456) 115 kV Bus b. 3. Drop Load 2 at N_HOBBS 3 (528456) 115 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25W | Transfer | Group5_Fault_0297_P1 | 3 phase fault on SANGER_SW 3 (528463) 115 kV Bus a. Apply Fault at the SANGER_SW 3 (528463) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from SANGER_SW 3 (528463) 115 kV Bus to G18-004-TAP (762442) 115 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | No | Yes | Damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer
05 - Southwest | 25W | Transfer | Group5_Fault_0298_P1 | 3 phase fault on MONUMENT 3 (528491) 115 kV Bus a. Apply Fault at the MONUMENT 3 (528491) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from MONUMENT 3 (528491) 115 kV Bus to W_HOBBS 3 (528498) 115 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25W | Transfer | Group5_Fault_0299_P1 | 3 phase fault on W_HOBBS 3 (528498) 115 kV Bus a. Apply Fault at the W_HOBBS 3 (528498) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from W_HOBBS 3 (528498) 115 kV Bus to DRINKARD_TP3 (528533) 115 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | Group5_Fault_0300_P1 | 3 phase fault on DRINKARD_TP3 (528533) 115 kV Bus a. Apply Fault at the DRINKARD_TP3 (528533) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from DRINKARD_TP3 (528533) 115 kV Bus to EUNICE 3 (528512) 115 kV Bus CKT 1 b. 2. Drop Load 1 at EUNICE 3 (528512) 115 kV Bus b. 3. Drop Load 1* at EUNICE 3 (528512) 115 kV Bus b. 4. Drop Shunt 1 at EUNICE 3 (528512) 115 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | Group5_Fault_0301_P1 | 3 phase fault on MONUMNT_TP 3 (528568) 115 kV Bus a. Apply Fault at the MONUMNT_TP 3 (528568) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from MONUMNT_TP 3 (528568) 115 kV Bus to BYRD_TP 3 (528581) 115 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | Group5_Fault_0302_P1 | 3 phase fault on JOHNSON_DRW3 (527362) 115 kV Bus a. Apply Fault at the JOHNSON_DRW3 (527362) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from JOHNSON_DRW3 (527362) 115 kV Bus to OXY_WSEM_TP3 (527325) 115 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | Group5_Fault_0303_P1 | 3 phase fault on JOHNSON_DRW3 (527362) 115 kV Bus a. Apply Fault at the JOHNSON_DRW3 (527362) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from JOHNSON_DRW3 (527362) 115 kV Bus to LE-ERF 3 (528775) 115 kV Bus CKT "@1" c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | Group5_Fault_0304_P1 | 3 phase fault on JOHNSON_DRW3 (527362) 115 kV Bus a. Apply Fault at the JOHNSON_DRW3 (527362) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from JOHNSON_DRW3 (527362) 115 kV Bus to MAPCO 3 (527360) 115 kV Bus CKT 1 b. 2. Trip branch from MAPCO 3 (527360) 115 kV Bus to AM_FRAC 3 (527300) 115 kV Bus CKT 1 b. 3. Drop Load 1 at MAPCO 3 (527360) 115 kV Bus b. 4. Drop Load 1 at AM_FRAC 3 (527300) 115 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | Group5_Fault_0305_P1 | 3 phase fault on INK_BASIN 3 (527027) 115 kV Bus a. Apply Fault at the INK_BASIN 3 (527027) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from INK_BASIN 3 (527027) 115 kV Bus to ALRDCRTZ_TP3 (527030) 115 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | Group5_Fault_0306_P1 | 3 phase fault on LE-WAITS 3 (528325) 115 kV Bus a. Apply Fault at the LE-WAITS 3 (528325) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from LE-WAITS 3 (528325) 115 kV Bus to LE-WAITS 2 (528617) 69 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | Group5_Fault_0307_P1 | 3 phase fault on LE-LOVINTON2 (528618) 69 kV Bus a. Apply Fault at the LE-LOVINTON2 (528618) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from LE-LOVINTON2 (528618) 69 kV Bus to LE-DSYSRPOI2 (528677) 69 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | Group5_Fault_0308_P1 | 3 phase fault on LE-LOVINTON2 (528618) 69 kV Bus a. Apply Fault at the LE-LOVINTON2 (528618) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from LE-LOVINTON2 (528618) 69 kV Bus to LE-TATMGOAB2 (528679) 69 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | Group5_Fault_0309_P1 | 3 phase fault on DENVER_N 3 (527130) 115 kV Bus a. Apply Fault at the DENVER_N 3 (527130) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from DENVER_N 3 (527130) 115 kV Bus to DENVER_S 3 (527136) 115 kV Bus CKT @1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | No | No | No | No | Yes | No | Yes | Out Of Step Generators and damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer
05 - Southwest | 25W | Transfer | Group5_Fault_0310_P1 | 3 phase fault on DENVER_N 3 (527130) 115 kV Bus a. Apply Fault at the DENVER_N 3 (527130) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from DENVER_N 3 (527130) 115 kV Bus to MUSTANG 3 (527146) 115 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | No | No | No | No | Yes | No | Yes | Out Of Step Generators and damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer
05 - Southwest | 25W | Transfer | Group5_Fault_0311_P1 | 3 phase fault on DENVER_N 3 (527130) 115 kV Bus a. Apply Fault at the DENVER_N 3 (527130) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from DENVER_N 3 (527130) 115 kV Bus to DENVER_CTY 2 (527125) 69 kV Bus to DNVER_N_TR11 (527122) 13.2 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 763309 [G18-112-GEN10.6600]
05 - Southwest | 25W | Transfer | Group5_Fault_0312_P1 | 3 phase fault on BYRD_TP 3 (528581) 115 kV Bus a. Apply Fault at the BYRD_TP 3 (528581) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from BYRD_TP 3 (528581) 115 kV Bus to BYRD 3 (528582) 115 kV Bus CKT 1 b. 2. Drop Load 1 at BYRD 3 (528582) 115 kV Bus b. 3. Drop Load 1* at BYRD 3 (528582) 115 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | Group5_Fault_0313_P1 | 3 phase fault on BYRD_TP 3 (528581) 115 kV Bus a. Apply Fault at the BYRD_TP 3 (528581) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from BYRD_TP 3 (528581) 115 kV Bus to COOPER_RNCH3 (528554) 115 kV Bus CKT 1 b. 2. Trip branch from COOPER_RNCH3 (528554) 115 kV Bus to OIL_CENTER 3 (528552) 115 kV Bus CKT 1 b. 3. Trip branch from OIL_CENTER 3 (528552) 115 kV Bus to LEA_ROAD 3 (528505) 115 kV Bus CKT 1 b. 4. Drop Load 1 at COOPER_RNCH3 (528554) 115 kV Bus b. 5. Drop Load 1 at OIL_CENTER 3 (528552) 115 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | Group5_Fault_0314_P1 | 3 phase fault on OXY_WSEM_TP3 (527325) 115 kV Bus a. Apply Fault at the OXY_WSEM_TP3 (527325) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from OXY_WSEM_TP3 (527325) 115 kV Bus to OXY_WSTSEM 3 (527323) 115 kV Bus CKT 1 b. 2. Drop Load 1 at OXY_WSTSEM 3 (527323) 115 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | Group5_Fault_0315_P1 | 3 phase fault on OXY_WSEM_TP3 (527325) 115 kV Bus a. Apply Fault at the OXY_WSEM_TP3 (527325) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from OXY_WSEM_TP3 (527325) 115 kV Bus to GAINES 3 (527322) 115 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | Group5_Fault_0316_P1 | 3 phase fault on LE-ERF 3 (528775) 115 kV Bus a. Apply Fault at the LE-ERF 3 (528775) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from LE-ERF 3 (528775) 115 kV Bus to LE-TALLCOTN3 (528779) 115 kV Bus CKT 1 b. 2. Trip branch from LE-TALLCOTN3 (528779) 115 kV Bus to LE-KCM 3 (527292) 115 kV Bus CKT 1 b. 3. Drop Load 1 at LE-TALLCOTN3 (528779) 115 kV Bus b. 4. Drop Load 1 at LE-KCM 3 (527292) 115 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | Group5_Fault_0317_P1 | 3 phase fault on LE-ERF 3 (528775) 115 kV Bus a. Apply Fault at the LE-ERF 3 (528775) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from LE-ERF 3 (528775) 115 kV Bus to LE-ERF 2 (528774) 69 kV Bus to LE-ERF_TR 1 (528773) 12.47 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | Group5_Fault_0318_P1 | 3 phase fault on POTASH_JCT 3 (527962) 115 kV Bus a. Apply Fault at the POTASH_JCT 3 (527962) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from POTASH_JCT 3 (527962) 115 kV Bus to PCA 3 (527930) 115 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | No | No | No | Yes | No | No | No | Out Of Step Generators and damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25W | Transfer | Group5_Fault_0319_P1 | 3 phase fault on CARDINAL 3 (528596) 115 kV Bus a. Apply Fault at the CARDINAL 3 (528596) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from CARDINAL 3 (528596) 115 kV Bus to TEAGUE 3 (528526) 115 kV Bus CKT 1 b. 2. Trip branch from TEAGUE 3 (528526) 115 kV Bus to S_JAL 3 (528547) 115 kV Bus CKT 1 b. 3. Drop Load 1 at TEAGUE 3 (528526) 115 kV Bus b. 4. Drop Load 1* at TEAGUE 3 (528526) 115 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | Group5_Fault_0320_P1 | 3 phase fault on CARDINAL 3 (528596) 115 kV Bus a. Apply Fault at the CARDINAL 3 (528596) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from CARDINAL 3 (528596) 115 kV Bus to SAGE_BRUSH 3 (527955) 115 kV Bus CKT 1 b. 2. Trip branch from SAGE_BRUSH 3 (527955) 115 kV Bus to MEDANOS 3 (527954) 115 kV Bus CKT 1 b. 3. Trip branch from MEDANOS 3 (527954) 115 kV Bus to LIVSTNRIDGE3 (527953) 115 kV Bus CKT 1 b. 4. Drop Load 1 at SAGE_BRUSH 3 (527955) 115 kV Bus b. 5. Drop Load 1* at SAGE_BRUSH 3 (527955) 115 kV Bus b. 6. Drop Load 1 at TEAGUE 3 (528526) 115 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | Group5_Fault_0321_P1 | 3 phase fault on GAINES 3 (527322) 115 kV Bus a. Apply Fault at the GAINES 3 (527322) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from GAINES 3 (527322) 115 kV Bus to SEMINOLE 3 (527275) 115 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | Group5_Fault_0322_P1 | 3 phase fault on GAINES 3 (527322) 115 kV Bus a. Apply Fault at the GAINES 3 (527322) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from GAINES 3 (527322) 115 kV Bus to LEGACY 3 (527346) 115 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | Group5_Fault_0323_P1 | 3 phase fault on GAINES 3 (527322) 115 kV Bus a. Apply Fault at the GAINES 3 (527322) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from GAINES 3 (527322) 115 kV Bus to GAINES 2 (527321) 69 kV Bus to GAINES_TR1 1 (527319) 13.2 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | Group5_Fault_0324_P1 | 3 phase fault on GAINES 3 (527322) 115 kV Bus a. Apply Fault at the GAINES 3 (527322) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from GAINES 3 (527322) 115 kV Bus to GAINES 2 (527321) 69 kV Bus to GAINES_TR2 1 (527320) 13.2 kV Bus CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | Group5_Fault_0325_P1 | 3 phase fault on SEMINOLE 3 (527275) 115 kV Bus a. Apply Fault at the SEMINOLE 3 (527275) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from SEMINOLE 3 (527275) 115 kV Bus to SAN_ANDS_TP3 (527105) 115 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | Group5_Fault_0326_P1 | 3 phase fault on SEMINOLE 3 (527275) 115 kV Bus a. Apply Fault at the SEMINOLE 3 (527275) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from SEMINOLE 3 (527275) 115 kV Bus to SEMINOLE 6 (527276) 230 kV Bus to SEMINLE_TR21 (527274) 13.2 kV Bus CKT 2 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25W | Transfer | Group5_Fault_0327_P1 | 3 phase fault on SEMINOLE 3 (527275) 115 kV Bus a. Apply Fault at the SEMINOLE 3 (527275) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from SEMINOLE 3 (527275) 115 kV Bus to SEMINOLE 6 (527276) 230 kV Bus to SEMINLE_TR11 (527273) 13.2 kV Bus CKT 1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25W | Transfer | Group5_Fault_0328_P1 | 3 phase fault on GAINES 2 (527321) 69 kV Bus a. Apply Fault at the GAINES 2 (527321) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from GAINES 2 (527321) 69 kV Bus to RILEY_TP 2 (527228) 69 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | Group5_Fault_0329_P1 | 3 phase fault on SAN_ANDS_TP3 (527105) 115 kV Bus a. Apply Fault at the SAN_ANDS_TP3 (527105) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from SAN_ANDS_TP3 (527105) 115 kV Bus to DENVER_S 3 (527136) 115 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | No | No | No | No | Yes | No | Yes | Out Of Step Generators and damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer
05 - Southwest | 25W | Transfer | Group5_Fault_0330_P1 | 3 phase fault on RILEY_TP 2 (527228) 69 kV Bus a. Apply Fault at the RILEY_TP 2 (527228) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from RILEY_TP 2 (527228) 69 kV Bus to RILEY 2 (527331) 69 kV Bus CKT 1 b. 2. Drop Load 1 at RILEY 2 (527331) 69 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | Group5_Fault_0331_P4 | a. Apply single phase fault at O.K.U.-7 (511456) 345 kV CB 3409A Stuck b. Clear Fault after 16 cycles: b. 1. Trip branch from O.K.U.-7 (511456) 345 kV to L.E.S.-7 (511468) 345 kV CKT 1 b. 2. Trip branch from O.K.U.-7 (511456) 345 kV to G18-092-TAP (763215) 345 kV CKT 1 | P4 | No | No | No | No | No | No | No | Out Of Step Generators and damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25W | Transfer | Group5_Fault_0332_P4 | a. Apply single phase fault at L.E.S.-7 (511468) 345 kV CB 3429B Stuck b. Clear Fault after 16 cycles: b. 1. Trip branch from O.K.U.-7 (511456) 345 kV to L.E.S.-7 (511468) 345 kV CKT 1 b. 2. Trip three winding transformer from LES#5-1 (511411) 13.8 kV to L.E.S.-4 (511467) kV to L.E.S.-7 (511468) 345 kV CKT2 | P4 | No | No | No | Yes | No | No | No | Out Of Step Generators and damping issues observed | Lawton Eastside 345 kV Substation Upgrade to Double-Bus-Double-Breaker Configuration | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25W | Transfer | Group5_Fault_0333_P4 | a. Apply single phase fault at L.E.S.-7 (511468) 345 kV CB 3433A Stuck b. Clear Fault after 16 cycles: b. 1. Trip branch from L.E.S.-7 (511468) 345 kV to O.K.U.-7 (511456) 345 kV CKT 1 b. 2. Trip branch from L.E.S.-7 (511468) 345 kV to G17-171-TAP (760938) 345 kV CKT 1 | P4 | No | No | No | No | No | No | No | Out Of Step Generators and damping issues observed | Lawton Eastside 345 kV Substation Upgrade to Double-Bus-Double-Breaker Configuration | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25W | Transfer | Group5_Fault_0334_P4 | a. Apply single phase fault at BVRCNTY7 (515554) 345 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from BVRCNTY7 (515554) 345 kV to HITCHLAND 7 (523097) 345 kV CKT 1 b. 2. Trip branch from BVRCNTY7 (515554) 345 kV to HITCHLAND 7 (523097) 345 kV CKT 2 | P4 | No | No | No | No | No | No | No | Out Of Step Generators and damping issues observed | Potter to Tolk 345 kV Double Circuit Line Build Potter to Chisholm 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer Potter to Tolk 345 kV | Generator relays were disabled for the following generators: 523121 [GRPLNS-WT4-10.5750], 763397 [G18-124-GEN1], 763309 [G18-112-GEN1]
05 - Southwest | 25W | Transfer | Group5_Fault_0335_P4 | a. Apply single phase fault at CARPENTER 7 (523823) 345 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from CARPENTER 7 (523823) 345 kV to FINNEY 7 (523853) 345 kV CKT 1 b. 2. Disconnect Bus CARPENTER 7 (523823) 345 kV | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25W | Transfer | Group5_Fault_0336_P4 | a. Apply single phase fault at CROSSROADS 7 (527656) 345 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from CROSSROADS 7 (527656) 345 kV to EDDY_CNTY 7 (527802) 345 kV CKT 1 b. 2. Trip branch from CROSSROADS 7 (527656) 345 kV to TOLK 7 (525549) 345 kV CKT 1 b. 3. Trip branch from CROSSROADS 7 (527656) 345 kV to RSVLT_CC_E 7 (527655) 345 kV CKT 1 b. 4. Disconnect Bus RSVLT_CC_E 7 (527655) 345 kV b. 5. Disconnect Bus MILO_WIND 1 (527653) 0.7 kV b. 6. Disconnect Bus RSVLT_GEN1 1 (527651) 0.69 kV b. 7. Disconnect Bus RSVLT_GEN2 1 (527652) 0.69 kV b. 8. Disconnect Bus RSVLT_CC_W 7 (527654) 345 kV b. 9. Disconnect Bus CROSSROADS 7 (527656) 345 kV | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer
05 - Southwest | 25W | Transfer | Group5_Fault_0337_P4 | a. Apply single phase fault at EDDY_CNTY 7 (527802) 345 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from EDDY_CNTY 7 (527802) 345 kV to KIOWA 7 (527965) 345 kV CKT 1 b. 2. Trip branch from EDDY_CNTY 7 (527802) 345 kV to CROSSROADS 7 (527656) 345 kV CKT 1 b. 3. Trip three winding transformer from EDDY_TR 1 (527796) 13.2 kV to EDDY_NORTH 6 (527799) kV to EDDY_CNTY 7 (527802) 345 kV CKT1 b. 4. Disconnect Bus EDDY_TR 1 (527796) 13.2 kV b. 5. Disconnect Bus EDDY_CNTY 7 (527802) 345 kV | P4 | No | No | No | No | Yes | No | Yes | Out Of Step Generators and damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer
05 - Southwest | 25W | Transfer | Group5_Fault_0338_P4 | a. Apply single phase fault at FINNEY 7 (523853) 345 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from FINNEY 7 (523853) 345 kV to CARPENTER 7 (523823) 345 kV CKT 1 b. 2. Trip branch from FINNEY 7 (523853) 345 kV to HOLCOMB7 (531449) 345 kV CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | Group5_Fault_0339_P4 | a. Apply single phase fault at HITCHLAND 7 (523097) 345 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from HITCHLAND 7 (523097) 345 kV to BVRCNTY7 (515554) 345 kV CKT 2 b. 2. Disconnect Bus NOVUS_WND 1 (523107) 4.16 kV b. 3. Disconnect Bus NOVUS1 1 (523109) 34.5 kV b. 4. Disconnect Bus NOVUS1 3 (523111) 115 kV b. 5. Disconnect Bus NOVUS1_TR1 1 (523110) 13.8 kV | P4 | Yes | Yes | Yes | No | Yes | No | No | Damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25W | Transfer | Group5_Fault_0340_P4 | a. Apply single phase fault at HITCHLAND 7 (523097) 345 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from HITCHLAND 7 (523097) 345 kV to CARPENTER 7 (523823) 345 kV CKT 1 b. 2. Drop Shunt HITCHLAND 7 (523097) 345 kV b. 3. Trip three winding transformer from HITCHLD_TR21 (523094) 13.2 kV to HITCHLAND 6 (523095) kV to HITCHLAND 7 (523097) 345 kV CKT2 | P4 | Yes | No | Yes | No | Yes | Yes | No | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points) |  | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25W | Transfer | Group5_Fault_0341_P4 | a. Apply single phase fault at HITCHLAND 7 (523097) 345 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from HITCHLAND 7 (523097) 345 kV to POTTER_CO 7 (523961) 345 kV CKT 1 b. 2. Disconnect Bus NOBLE_TR 1 (523102) 13.8 kV b. 3. Disconnect Bus NOBLE_WND 3 (523103) 115 kV b. 4. Disconnect Bus GRPLNS-HV4-3 (523130) 115 kV b. 5. Disconnect Bus GRPLNS-HV2-3 (523131) 115 kV b. 6. Disconnect Bus GRPLNS-LV4-1 (523127) 34.5 kV b. 7. Disconnect Bus GRPLNS-LV2-1 (523129) 34.5 kV b. 8. Disconnect Bus GRPLNS-CB4-1 (523124) 34.5 kV b. 9. Disconnect Bus GRPLNS-CB2-1 (523126) 34.5 kV b. 10. Disconnect Bus GRPLNS-WT4-1 (523121) 0.575 kV b. 11. Disconnect Bus GRPLNS-WT2-1 (523123) 0.575 kV | P4 | No | No | No | Yes | No | No | No | Out Of Step Generators and damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523122 [NBLWND-WTG110.7000]
05 - Southwest | 25W | Transfer | Group5_Fault_0342_P4 | a. Apply single phase fault at HOBBS_INT 7 (527896) 345 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from HOBBS_INT 7 (527896) 345 kV to KIOWA 7 (527965) 345 kV CKT 1 b. 2. Disconnect Bus HOBBS_TR3 1 (527895) 13.2 kV | P4 | No | No | No | No | Yes | No | No | Out Of Step Generators and damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25W | Transfer | Group5_Fault_0343_P4 | a. Apply single phase fault at N_LOVING 7 (528185) 345 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from N_LOVING 7 (528185) 345 kV to CHINA_DRAW 7 (528223) 345 kV CKT 1 b. 2. Trip branch from N_LOVING 7 (528185) 345 kV to KIOWA 7 (527965) 345 kV CKT 1 b. 3. Trip three winding transformer from NORTH_LOVNG3 (528182) 115 kV to N_LOVING 7 (528185) kV to N_LOVING TR1 (528186) 13.2 kV CKT1 b. 4. Disconnect Bus N_LOVING TR1 (528186) 13.2 kV b. 5. Disconnect Bus N_LOVING 7 (528185) 345 kV | P4 | No | No | No | Yes | No | No | Yes | Out Of Step Generators and damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer
05 - Southwest | 25W | Transfer | Group5_Fault_0344_P4 | a. Apply single phase fault at POTTER_CO 7 (523961) 345 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from POTTER_CO 7 (523961) 345 kV to HITCHLAND 7 (523097) 345 kV CKT 1 b. 2. Trip three winding transformer from POTTER_TR 1 (523957) 13.2 kV to POTTER_CO 6 (523959) kV to POTTER_CO 7 (523961) 345 kV CKT1 b. 3. Disconnect Bus POTTER_CO 7 (523961) 345 kV b. 4. Disconnect Bus SPNSPUR_WND7 (524296) 345 kV b. 5. Disconnect Bus SPNSPUR_GEN1 (524295) 0.69 kV | P4 | No | No | No | No | No | No | No | Out Of Step Generators and damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25W | Transfer | Group5_Fault_0345_P4 | a. Apply single phase fault at YOAKUM_345 (526936) 345 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from YOAKUM_345 (526936) 345 kV to TUCO_INT 7 (525832) 345 kV CKT 1 b. 2. Trip branch from YOAKUM_345 (526936) 345 kV to HOBBS_INT 7 (527896) 345 kV CKT 1 b. 3. Trip three winding transformer from YOAKUM 6 (526935) 230 kV to YOAKUM_345 (526936) kV to YOAKUM_TR1 (526937) 13.2 kV CKT1 b. 4. Disconnect Bus YOAKUM_TR1 (526937) 13.2 kV b. 5. Disconnect Bus YOAKUM_345 (526936) 345 kV | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer
05 - Southwest | 25W | Transfer | Group5_Fault_0346_P4 | a. Apply single phase fault at TUCO_INT 7 (525832) 345 kV b. Clear Fault after 16 cycles: b. 1. Disconnect Bus TUCO_TR1 1 (525824) 13.2 kV b. 2. Trip branch from TUCO_INT 7 (525832) 345 kV to CRAWFISH_DR (560022) 345 kV CKT | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 763309 [G18-112-GEN10.6600]
05 - Southwest | 25W | Transfer | Group5_Fault_0347_P4 | a. Apply single phase fault at TUCO_INT 7 (525832) 345 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from TUCO_INT 7 (525832) 345 kV to YOAKUM_345 (526936) 345 kV CKT 1 b. 2. Disconnect Bus ELK_CT1 (525850) 345 kV b. 3. Disconnect Bus ELK_1 1 (525844) 18 kV b. 4. Disconnect Bus ELK_2 1 (525845) 18 kV | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 763309 [G18-112-GEN10.6600]
05 - Southwest | 25W | Transfer | Group5_Fault_0348_P4 | a. Apply single phase fault at EDDY_CNTY 7 (527802) 345 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from EDDY_CNTY 7 (527802) 345 kV to KIOWA 7 (527965) 345 kV CKT 1 b. 2. Trip branch from EDDY_CNTY 7 (527802) 345 kV to CROSSROADS 7 (527656) 345 kV CKT 1 b. 3. Disconnect Bus EDDY_TR 1 (527796) 13.2 kV b. 4. Disconnect Bus EDDY_CNTY 7 (527802) 345 kV | P4 | No | No | No | No | Yes | No | Yes | Out Of Step Generators and damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer
05 - Southwest | 25W | Transfer | Group5_Fault_0349_P4 | a. Apply single phase fault at HOBBS_INT 7 (527896) 345 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from HOBBS_INT 7 (527896) 345 kV to KIOWA 7 (527965) 345 kV CKT 1 b. 2. Disconnect Bus HOBBS_TR3 1 (527895) 13.2 kV | P4 | No | No | No | No | Yes | No | No | Out Of Step Generators and damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25W | Transfer | Group5_Fault_0350_P4 | a. Apply single phase fault at YOAKUM_345 (526936) 345 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from YOAKUM_345 (526936) 345 kV to TUCO_INT 7 (525832) 345 kV CKT 1 b. 2. Trip branch from YOAKUM_345 (526936) 345 kV to HOBBS_INT 7 (527896) 345 kV CKT 1 b. 3. Disconnect Bus YOAKUM_TR1 (526937) 13.2 kV b. 4. Disconnect Bus YOAKUM_345 (526936) 345 kV | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer
05 - Southwest | 25W | Transfer | Group5_Fault_0351_P4 | a. Apply single phase fault at N_LOVING 7 (528185) 345 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from N_LOVING 7 (528185) 345 kV to CHINA_DRAW 7 (528223) 345 kV CKT 1 b. 2. Trip branch from N_LOVING 7 (528185) 345 kV to KIOWA 7 (527965) 345 kV CKT 1 b. 3. Disconnect Bus N_LOVING TR1 (528186) 13.2 kV b. 4. Disconnect Bus N_LOVING 7 (528185) 345 kV | P4 | No | No | No | Yes | No | No | Yes | Out Of Step Generators and damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer
05 - Southwest | 25W | Transfer | Group5_Fault_0352_P4 | a. Apply single phase fault at CHINA_DRAW 7 (528223) 345 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from CHINA_DRAW 7 (528223) 345 kV to PHANTOM 7 (528015) 345 kV CKT 1 b. 2. Trip branch from CHINA_DRAW 7 (528223) 345 kV to N_LOVING 7 (528185) 345 kV CKT 1 b. 3. Disconnect Bus CHINA_DRAW 1 (528219) 13.2 kV b. 4. Disconnect Bus CHINA_DRAW 7 (528223) 345 kV | P4 | No | No | No | Yes | No | No | Yes | Out Of Step Generators and damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer
05 - Southwest | 25W | Transfer | Group5_Fault_0353_P4 | a. Apply single phase fault at RDRUNNER 7 (528027) 345 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from RDRUNNER 7 (528027) 345 kV to PHANTOM 7 (528015) 345 kV CKT 1 b. 2. Trip branch from RDRUNNER 7 (528027) 345 kV to KIOWA 7 (527965) 345 kV CKT 1 b. 3. Disconnect Bus RDRNNER_TR11 (528023) 13.2 kV b. 4. Disconnect Bus RDRUNNER 7 (528027) 345 kV | P4 | No | No | No | No | Yes | No | No | Out Of Step Generators and damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25W | Transfer | Group5_Fault_0354_P4 | a. Apply single phase fault at PHANTOM 7 (528015) 345 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from PHANTOM 7 (528015) 345 kV to CHINA_DRAW 7 (528223) 345 kV CKT 1 b. 2. Disconnect Bus PHANTOM TR21 (528012) 13.2 kV | P4 | No | No | No | Yes | No | No | Yes | Out Of Step Generators and damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer
05 - Southwest | 25W | Transfer | Group5_Fault_0355_P4 | a. Apply single phase fault at PHANTOM 7 (528015) 345 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from PHANTOM 7 (528015) 345 kV to RDRUNNER 7 (528027) 345 kV CKT 1 b. 2. Disconnect Bus PHANTOM TR11 (528011) 13.2 kV | P4 | No | No | No | No | Yes | No | Yes | Out Of Step Generators and damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer
05 - Southwest | 25W | Transfer | Group5_Fault_0356_P4 | a. Apply single phase fault at SUNDOWN 6 (526435) 230 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from SUNDOWN 6 (526435) 230 kV to AMOCO_SS 6 (526460) kV CKT 1 b. 2. Disconnect Bus AMOCO_SS 6 (526460) 230 kV | P4 | Yes | Yes | Yes | No | Yes | Yes | No | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points) |  | Generator relays were disabled for the following generators: 763309 [G18-112-GEN10.6600]
05 - Southwest | 25W | Transfer | Group5_Fault_0357_P4 | a. Apply single phase fault at BORDER 7 (515458) 345 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from BORDER 7 (515458) 345 kV to CRAWFISH_DR (560022) 345 kV CKT 1 b. 2. Trip branch from BORDER 7 (515458) 345 kV to WWDBORDT (755000) 345 kV CKT 1 | P4 | No | No | No | No | Yes | No | No | Out Of Step Generators and damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25W | Transfer | Group5_Fault_0358_P4 | a. Apply single phase fault at WWRDEHV7 (515375) 345 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from WWRDEHV7 (515375) 345 kV to WWDBORDT (755000) 345 kV CKT 1 b. 2. Trip branch from WWRDEHV7 (515375) 345 kV to TATONGA7 (515407) 345 kV CKT 1 b. 3. Trip three winding transformer from WWRDEHV7 (515375) 345 kV to WWRDEHV4 (515376) kV to WWDEHV21 (515799) 13.8 kV CKT2 b. 4. Drop Shunt 1 WWDEHV21 (515799) 13.8 kV | P4 | No | No | No | Yes | No | No | No | Out Of Step Generators and damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25W | Transfer | Group5_Fault_0359_P4 | a. Apply single phase fault at SWEETWT6 (511541) 230 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from SWEETWT6 (511541) 230 kV to CHISHOLM6 (511557) 230 kV CKT 1 b. 2. Trip branch from SWEETWT6 (511541) 230 kV to STLN-DEMARC6 (523779) 230 kV CKT 1 b. 3. Trip branch from STLN-DEMARC6 (523779) 230 kV to WHEELER 6 (523777) 230 kV CKT 1 | P4 | No | Yes | Yes | Yes | Yes | No | Yes | Out Of Step Generators and damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 511967 [BUFFCK0 0.6900]
05 - Southwest | 25W | Transfer | Group5_Fault_0360_P4 | a. Apply single phase fault at TUCO_INT 6 (525830) 230 kV b. Clear Fault after 16 cycles: b. 1. Trip three winding transformer from TUCO_INT 6 (525830) 230 kV to TUCO_INT 3 (525828) kV to TUCO_TR4 1 (525821) 13.2 kV CKT1 b. 2. Trip three winding transformer from TUCO_INT 6 (525830) 230 kV to TUCO_INT 7 (525832) kV to TUCO_TR2 1 (525825) 13.2 kV CKT2 | P4 | Yes | Yes | Yes | No | Yes | No | Yes | Damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer
05 - Southwest | 25W | Transfer | Group5_Fault_0361_P4 | a. Apply single phase fault at PLANT_X 6 (525481) 230 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from PLANT_X 6 (525481) 230 kV to SUNDOWN 6 (526435) 230 kV CKT 1 b. 2. Trip branch from PLANT_X 6 (525481) 230 kV to TOLK 6 (525531) 230 kV CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | Group5_Fault_0362_P4 | a. Apply single phase fault at NEWHART 6 (525461) 230 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from NEWHART 6 (525461) 230 kV to POTTER_CO 6 (523959) 230 kV CKT 1 b. 2. Trip three winding transformer from NEWHART 6 (525461) 230 kV to NEWHART 3 (525460) kV to NEWHART_TR11 (525459) 13.2 kV CKT1 | P4 | Yes | Yes | Yes | No | Yes | Yes | No | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points) |  | Generator relays were disabled for the following generators: 763309 [G18-112-GEN10.6600]
05 - Southwest | 25W | Transfer | Group5_Fault_0363_P4 | a. Apply single phase fault at TOLK 6 (525531) 230 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from TOLK 6 (525531) 230 kV to ROOSEVELT 6 (524909) 230 kV CKT 1 b. 2. Trip three winding transformer from TOLK 7 (525549) 345 kV to TOLK 6 (525531) kV to TOLK_TR 1 (525537) 13.2 kV CKT1 b. 3. Drop Shunt 1 TOLK_TR 1 (525537) 13.2 kV | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25W | Transfer | Group5_Fault_0364_P4 | a. Apply single phase fault at PLANT_X 3 (525480) 115 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from PLANT_X 3 (525480) 115 kV to MULSHVLY_TP3 (525019) 115 kV CKT 1 b. 2. Trip branch from MULSHVLY_TP3 (525019) 115 kV to MULESHVALLY3 (525018) 115 kV CKT 1 b. 3. Trip branch from MULSHVLY_TP3 (525019) 115 kV to BAILEYCO 3 (525028) 115 kV CKT 1 b. 4. Drop Load 1 MULESHVALLY3 (525018) 115 kV b. 5. Drop Load 2 MULESHVALLY3 (525018) 115 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | Group5_Fault_0365_P4 | a. Apply single phase fault at ROOSEVELT 6 (524909) 230 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from ROOSEVELT 6 (524909) 230 kV to OASIS 6 (524875) 230 kV CKT 1 b. 2. Trip branch from ROOSEVELT 6 (524909) 230 kV to TOLK 6 (525531) 230 kV CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 763309 [G18-112-GEN10.6600]
05 - Southwest | 25W | Transfer | Group5_Fault_0366_P4 | a. Apply single phase fault at LAMB_CNTY 3 (525636) 115 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from LAMB_CNTY 3 (525636) 115 kV to HOCKLEY 3 (526020) 115 kV CKT 1 b. 2. Trip three winding transformer from LAMB_CNTY 6 (525637) 230 kV to LAMB_CNTY 3 (525636) kV to LAMB_TR3 1 (525633) 13.2 kV CKT1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | Group5_Fault_0367_P4 | a. Apply single phase fault at CASTRO_CNTY3 (524746) 115 kV b. Clear Fault after 16 cycles: b. 1. Trip three winding transformer from CASTRO_CNTY3 (524746) 115 kV to CASTRO_CNTY2 (524745) kV to CASTRO_TR1 1 (524744) 13.2 kV CKT1 b. 2. Trip branch from CASTRO_CNTY3 (524746) 115 kV to DS-#21 3 (524734) 115 kV CKT 1 b. 3. Trip branch from DS-#21 3 (524734) 115 kV to TIERABLANCA3 (524630) 115 kV CKT 1 b. 4. Drop Load 1 DS-#21 3 (524734) 115 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | Group5_Fault_0368_P4 | a. Apply single phase fault at TUCO_INT 3 (525828) 115 kV b. Clear Fault after 16 cycles: b. 1. Trip three winding transformer from TUCO_INT 3 (525828) 115 kV to TUCO_INT 6 (525830) kV to TUCO_TR4 1 (525821) 13.2 kV CKT1 b. 2. Trip branch from TUCO_INT 3 (525828) 115 kV to FLOYD_CNTY 3 (525780) 115 kV CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer
05 - Southwest | 25W | Transfer | Group5_Fault_0369_P4 | a. Apply single phase fault at KRESS_INT 3 (525192) 115 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from KRESS_INT 3 (525192) 115 kV to KRS_RURL_TP3 (525226) 115 kV CKT 1 b. 2. Trip three winding transformer from KRESS_INT 3 (525192) 115 kV to KRESS_INT 2 (525191) kV to KRESS_TR1 1 (525190) 13.2 kV CKT1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | Group5_Fault_0370_P4 | a. Apply single phase fault at LUBBCK_STH 6 (526269) 230 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from WOLFFORTH 6 (526525) 230 kV to LUBBCK_STH 6 (526269) 230 kV CKT 1 b. 2. Trip branch from JONES 6 (526337) 230 kV to LUBBCK_STH 6 (526269) 230 kV CKT 1 | P4 | Yes | Yes | Yes | No | Yes | No | No | Damping issues observed. Low voltage ride through fails due to the tripping of G18-115-GEN10 and G18-115-GEN20 units. No cascading was observed and the issue was localised. Model tuning is recommended. | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 763309 [G18-112-GEN10.6600]
05 - Southwest | 25W | Transfer | Group5_Fault_0371_P4 | a. Apply single phase fault at YOAKUM 6 (526935) 230 kV b. Clear Fault after 16 cycles: b. 1. Trip three winding transformer from YOAKUM 6 (526935) 230 kV to YOAKUM 3 (526934) kV to YOAKUM_TR1 1 (526931) 13.2 kV CKT1 b. 2. Trip branch from YOAKUM 3 (526934) 115 kV to PLAINS_INT 3 (526928) 115 kV CKT 1 | P4 | No | No | No | No | Yes | No | Yes | Out Of Step Generators and damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer
05 - Southwest | 25W | Transfer | Group5_Fault_0372_P4 | a. Apply single phase fault at TERRY_CNTY 3 (526736) 115 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from TERRY_CNTY 3 (526736) 115 kV to WOLFFORTH 3 (526524) 115 kV CKT 1 b. 2. Trip three winding transformer from TERRY_CNTY 3 (526736) 115 kV to TERRY_CNTY 2 (526735) kV to TERRY_TR1 1 (526733) 13.2 kV CKT1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | Group5_Fault_0373_P4 | a. Apply single phase fault at TIERABLANCA3 (524630) 115 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from TIERABLANCA3 (524630) 115 kV to DFSMTH_EST 3 (524619) 115 kV CKT 1 b. 2. Trip three winding transformer from DEAFSMITH 6 (524623) 230 kV to DFSMTH_EST 3 (524619) kV to DEFSMTH_TR21 (524621) 13.8 kV CKT2 b. 3. Trip branch from TIERABLANCA3 (524630) 115 kV to NE_HEREFORD3 (524567) 115 kV CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | Group5_Fault_0374_P4 | a. Apply single phase fault at ROLLHILLS 3 (524007) 115 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from ROLLHILLS 3 (524007) 115 kV to NORTHWEST 3 (524106) 115 kV CKT 1 b. 2. Drop Shunt 1 ROLLHILLS 3 (524007) 115 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25W | Transfer | Group5_Fault_0375_P4 | a. Apply single phase fault at AMA_SOUTH 3 (524414) 115 kV b. Clear Fault after 16 cycles: b. 1. Trip three winding transformer from AMA_SOUTH 3 (524414) 115 kV to AMA_SOUTH 6 (524415) kV to AMA_SO_TR1 1 (524410) 13.2 kV CKT1 b. 2. Trip branch from AMA_SOUTH 3 (524414) 115 kV to OWENSCORN 3 (524404) 115 kV CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25W | Transfer | Group5_Fault_0376_P4 | a. Apply single phase fault at HITCHLAND 6 (523095) 230 kV b. Clear Fault after 16 cycles: b. 1. Trip three winding transformer from HITCHLAND 6 (523095) 230 kV to HITCHLAND 7 (523097) kV to HITCHLD_TR21 (523094) 13.2 kV CKT2 b. 2. Trip branch from HITCHLAND 6 (523095) 230 kV to MOORE_CNTY 6 (523309) 230 kV CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | No | No | Damping issues observed. Low voltage ride through fails due to the tripping of G18-115-GEN10 and G18-115-GEN20 units. No cascading was observed and the issue was localised. Model tuning is recommended. | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer
05 - Southwest | 25W | Transfer | Group5_Fault_0377_P4 | a. Apply single phase fault at L.E.S.-4 (511467) 138 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from L.E.S.-4 (511467) 138 kV to SHERID4 (511474) 138 kV CKT 1 b. 2. Trip branch from SHERID4 (511474) 138 kV to ARTVLTP4 (511537) 138 kV CKT 1 b. 3. Trip branch from 53CACHE4 (511509) 138 kV to ARTVLTP4 (511537) 138 kV CKT 1 b. 4. Trip branch from ARTVLTP4 (511537) 138 kV to ARTVILL4 (511538) 138 kV CKT 1 b. 5. Trip branch from LWS-NTP4 (511471) 138 kV to 53CACHE4 (511509) 138 kV CKT 1 b. 6. Trip branch from LWS N4 (511430) 138 kV to LWS-NTP4 (511471) 138 kV CKT 1 b. 7. Drop Load 1 SHERID4 (511474) 138 kV b. 8. Drop Load 1 ARTVILL4 (511538) 138 kV b. 9. Drop Load 1 53CACHE4 (511509) 138 kV b. 10. Drop Load 1 LWS N4 (511430) 138 kV b. 11. Drop Shunt 1 ARTVILL4 (511538) 138 kV b. 12. Drop Shunt 1 LWS N4 (511430) 138 kV b. 13. Trip three winding transformer from L.E.S.-4 (511467) 138 kV to L.E.S.-7 (511468) kV to LES#5-1 (511411) 13.8 kV CKT2 b. 14. Drop Shunt 1 LES#5-1 (511411) 13.8 kV | P4 | Yes | Yes | Yes | No | Yes | No | No | Damping issues observed. Low voltage ride through fails due to the tripping of G18-115-GEN10 and G18-115-GEN20 units. No cascading was observed and the issue was localised. Model tuning is recommended. | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer
05 - Southwest | 25W | Transfer | Group5_Fault_0378_P4 | a. Apply single phase fault at PLSNT_HILL 3 (524768) 115 kV b. Clear Fault after 16 cycles: b. 1. Trip three winding transformer from PLSNT_HILL 6 (524770) 230 kV to PLSNT_HILL 3 (524768) kV to PLSNHIL_TR11 (524767) 13.2 kV CKT1 b. 2. Trip branch from PLSNT_HILL 3 (524768) 115 kV to N_CLOVIS_TP3 (524776) 115 kV CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | Group5_Fault_0379_P4 | a. Apply single phase fault at CURRY 3 (524822) 115 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from CURRY 3 (524822) 115 kV to ROOSEVELT 3 (524908) 115 kV CKT 2 b. 2. Trip branch from CURRY 3 (524822) 115 kV to NORRIS_TP 3 (524764) 115 kV CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | Group5_Fault_0380_P4 | a. Apply single phase fault at PORTALES 3 (524924) 115 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from ROOSEVELT 3 (524908) 115 kV to PORTALES 3 (524924) 115 kV CKT 1 b. 2. Trip branch from OASIS 3 (524874) 115 kV to PORTALES 3 (524924) 115 kV CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | Group5_Fault_0381_P4 | a. Apply single phase fault at NEWHART 3 (525460) 115 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from CASTRO_CNTY3 (524746) 115 kV to NEWHART 3 (525460) 115 kV CKT 1 b. 2. Trip three winding transformer from NEWHART 6 (525461) 230 kV to NEWHART 3 (525460) kV to NEWHART_TR21 (525458) 13.2 kV CKT2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | Group5_Fault_0382_P4 | a. Apply single phase fault at YOAKUM 3 (526934) 115 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from PLAINS_INT 3 (526928) 115 kV to YOAKUM 3 (526934) 115 kV CKT 1 b. 2. Trip three winding transformer from YOAKUM 6 (526935) 230 kV to YOAKUM 3 (526934) kV to YOAKUM_TR1 1 (526931) 13.2 kV CKT1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | Group5_Fault_0383_P4 | a. Apply single phase fault at LAMB_CNTY 2 (525635) 69 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from W_LITTLFLD 2 (525613) 69 kV to LAMB_CNTY 2 (525635) 69 kV CKT 1 b. 2. Trip branch from AMHERST 2 (525606) 69 kV to W_LITTLFLD 2 (525613) 69 kV CKT 1 b. 3. Trip branch from LC-SANDHLL+2 (525599) 69 kV to AMHERST 2 (525606) 69 kV CKT 1 b. 4. Trip branch from SUDANRURAL 2 (525592) 69 kV to LC-SANDHLL+2 (525599) 69 kV CKT 1 b. 5. Drop Load 1 W_LITTLFLD 2 (525613) 69 kV b. 6. Drop Load 1 AMHERST 2 (525606) 69 kV b. 7. Drop Load 1 LC-SANDHLL+2 (525599) 69 kV b. 8. Drop Load 2 LC-SANDHLL+2 (525599) 69 kV b. 9. Drop Load 1 SUDANRURAL 2 (525592) 69 kV b. 10. Trip three winding transformer from LAMB_CNTY 3 (525636) 115 kV to LAMB_CNTY 2 (525635) kV to LAMB_TR1 1 (525631) 13.2 kV CKT1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | Group5_Fault_0384_P4 | a. Apply single phase fault at CARLISLE 3 (526160) 115 kV b. Clear Fault after 16 cycles: b. 1. Trip three winding transformer from CARLISLE 6 (526161) 230 kV to CARLISLE 3 (526160) kV to CRLSLE_TR1 1 (526157) 13.2 kV CKT1 b. 2. Trip branch from CARLISLE 3 (526160) 115 kV to MURPHY 3 (526192) 115 kV CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | Group5_Fault_0385_P4 | a. Apply single phase fault at FLOYD_CNTY 3 (525780) 115 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from FLOYD_CNTY 3 (525780) 115 kV to TUCO_INT 3 (525828) 115 kV CKT 1 b. 2. Trip three winding transformer from FLOYD_CNTY 3 (525780) 115 kV to FLOYD_CNTY 2 (525779) kV to FLOYD_TR1 1 (525777) 13.2 kV CKT1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | Group5_Fault_0386_P4 | a. Apply single phase fault at TUCO_INT 2 (525826) 69 kV b. Clear Fault after 16 cycles: b. 1. Trip three winding transformer from TUCO_INT 3 (525828) 115 kV to TUCO_INT 2 (525826) kV to TUCO_TR6 1 (525823) 13.2 kV CKT1 b. 2. Trip branch from TUCO_INT 2 (525826) 69 kV to SP-NEWDEAL 2 (525885) 69 kV CKT 1 b. 3. Trip branch from SP-NEWDEAL 2 (525885) 69 kV to MONROE 2 (525892) 69 kV CKT 1 b. 4. Trip branch from WHITEHEAD 2 (525891) 69 kV to MONROE 2 (525892) 69 kV CKT 1 b. 5. Trip branch from WHITEHEAD 2 (525891) 69 kV to SP-SHALLWTR2 (525899) 69 kV CKT 1 b. 6. Trip branch from SP-SHALLWTR2 (525899) 69 kV to STANTON_N 2 (526073) 69 kV CKT 1 b. 7. Drop Load 1 SP-NEWDEAL 2 (525885) 69 kV b. 8. Drop Load 1 MONROE 2 (525892) 69 kV b. 9. Drop Load 1 WHITEHEAD 2 (525891) 69 kV b. 10. Drop Load SP-SHALLWTR2 (525899) 69 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | Group5_Fault_0387_P4 | a. Apply single phase fault at POTTER_CO 7 (523961) 345 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from POTTER_CO 7 (523961) 345 kV to TOLK 7 (525549) 345 kV CKT 1 b. 2. Trip branch from POTTER_CO 7 (523961) 345 kV to GRAPEVINE (560035) 345 kV CKT 1 b. 3. Trip branch from CHISHOLM7 (511553) 345 kV to GRAPEVINE (560035) 345 kV CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | Group5_Fault_0388_P4 | a. Apply single phase fault at CROSSROADS 7 (527656) 345 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from TOLK 7 (525549) 345 kV to CROSSROADS 7 (527656) 345 kV CKT 1 b. 2. Trip branch from CROSSROADS 7 (527656) 345 kV to EDDY_CNTY 7 (527802) 345 kV CKT 1 | P4 | No | No | No | No | Yes | No | Yes | Out Of Step Generators and damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer
05 - Southwest | 25W | Transfer | Group5_Fault_0389_P4 | a. Apply single phase fault at TUCO_INT 7 (525832) 345 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from TUCO_INT 7 (525832) 345 kV to YOAKUM_345 (526936) 345 kV CKT 1 b. 2. Trip three winding transformer from TUCO_INT 7 (525832) 345 kV to TUCO_INT 6 (525830) kV to TUCO_TR1 1 (525824) 13.2 kV CKT1 b. 3. Drop Shunt 1 TUCO_TR1 1 (525824) 13.2 kV | P4 | Yes | Yes | Yes | No | Yes | No | No | Damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 763309 [G18-112-GEN10.6600]
05 - Southwest | 25W | Transfer | Group5_Fault_0390_P4 | a. Apply single phase fault at HITCHLAND 7 (523097) 345 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from HITCHLAND 7 (523097) 345 kV to CARPENTER 7 (523823) 345 kV CKT 1 b. 2. Trip branch from BVRCNTY7 (515554) 345 kV to HITCHLAND 7 (523097) 345 kV CKT 1 | P4 | No | No | No | Yes | No | No | Yes | Out Of Step Generators and damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer
05 - Southwest | 25W | Transfer | Group5_Fault_0391_P4 | a. Apply single phase fault at POTTER_CO 6 (523959) 230 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from POTTER_CO 6 (523959) 230 kV to HARRNG_EST 6 (523979) 230 kV CKT 1 b. 2. Trip branch from POTTER_CO 6 (523959) 230 kV to ROLLHILLS 6 (524010) 230 kV CKT 1 | P4 | No | No | No | Yes | No | No | No | Out Of Step Generators and damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25W | Transfer | Group5_Fault_0392_P4 | a. Apply single phase fault at YOAKUM_345 (526936) 345 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from YOAKUM_345 (526936) 345 kV to HOBBS_INT 7 (527896) 345 kV CKT 1 b. 2. Trip branch from TUCO_INT 7 (525832) 345 kV to YOAKUM_345 (526936) 345 kV CKT 1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25W | Transfer | Group5_Fault_0393_P4 | a. Apply single phase fault at HOBBS_INT 3 (527891) 115 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from HOBBS_INT 3 (527891) 115 kV to MADDOX 3 (528355) 115 kV CKT 1 b. 2. Trip branch from HOBBS_INT 3 (527891) 115 kV to MILLEN_TPW 3 (528434) 115 kV CKT 1 b. 3. Trip branch from MILLEN_TPW 3 (528434) 115 kV to MILLEN 3 (528435) 115 kV CKT *1 b. 4. Trip branch from MILLEN 3 (528435) 115 kV to MILLEN_TPE 3 (528436) 115 kV CKT *1 b. 5. Trip branch from MILLEN_TPE 3 (528436) 115 kV to NE_HOBBS 3 (528442) 115 kV CKT 1 b. 6. Trip branch from NE_HOBBS 3 (528442) 115 kV to TAYLOR 3 (528413) 115 kV CKT 1 b. 7. Drop Load 1 MILLEN 3 (528435) 115 kV b. 8. Drop Load 1* MILLEN 3 (528435) 115 kV b. 9. Drop Load 1 NE_HOBBS 3 (528442) 115 kV | P4 | Yes | No | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25W | Transfer | Group5_Fault_0394_P4 | a. Apply single phase fault at CUNNINHAM 3 (527864) 115 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from CUNNINHAM 3 (527864) 115 kV to BUCKEYE_TP 3 (528348) 115 kV CKT 1 b. 2. Trip branch from CUNNINHAM 3 (527864) 115 kV to QUAHADA 3 (528394) 115 kV CKT 1 | P4 | Yes | Yes | Yes | No | Yes | No | No | Damping issues observed. Low voltage ride through fails due to the tripping of G18-115-GEN10 and G18-115-GEN20 units. No cascading was observed and the issue was localised. Model tuning is recommended. | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer
05 - Southwest | 25W | Transfer | Group5_Fault_0395_P4 | a. Apply single phase fault at MADDOX 3 (528355) 115 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from HOBBS_INT 3 (527891) 115 kV to MADDOX 3 (528355) 115 kV CKT 1 b. 2. Trip branch from MADDOX 3 (528355) 115 kV to G18-004-TAP (762442) 115 kV CKT 1 | P4 | Yes | Yes | Yes | No | Yes | No | Yes | Damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer
05 - Southwest | 25W | Transfer | Group5_Fault_0396_P4 | a. Apply single phase fault at JOHNSON_DRW3 (527362) 115 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from JOHNSON_DRW3 (527362) 115 kV to LE-ERF 3 (528775) 115 kV CKT @1 b. 2. Trip branch from JOHNSON_DRW3 (527362) 115 kV to HIGG 3 (527363) 115 kV CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | Group5_Fault_0397_P4 | a. Apply single phase fault at LE-LOVINTON2 (528618) 69 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from LE-LOVINTON2 (528618) 69 kV to LE-NRTH_INT3 (528334) 115 kV CKT 1 b. 2. Trip branch from LE-LOVINTON2 (528618) 69 kV to LE-DSYSRPOI2 (528677) 69 kV CKT 1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25W | Transfer | Group5_Fault_0398_P4 | a. Apply single phase fault at DENVER_N 3 (527130) 115 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from DENVER_N 3 (527130) 115 kV to MUSTANG 3 (527146) 115 kV CKT 1 b. 2. Trip branch from DENVER_N 3 (527130) 115 kV to HIGGEAST 3 (527286) 115 kV CKT 1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25W | Transfer | Group5_Fault_0399_P4 | a. Apply single phase fault at EDDY_NORTH 6 (527799) 230 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from EDDY_NORTH 6 (527799) 230 kV to CUNNIGHM_N 6 (527865) 230 kV CKT 1 b. 2. Trip three winding transformer from EDDY_CNTY 7 (527802) 345 kV to EDDY_NORTH 6 (527799) kV to EDDY_TR 1 (527796) 13.2 kV CKT1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | Group5_Fault_0400_P4 | a. Apply single phase fault at POTASH_JCT 3 (527962) 115 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from POTASH_JCT 3 (527962) 115 kV to KIOWA 3 (527966) 115 kV CKT 1 b. 2. Trip three winding transformer from KIOWA 7 (527965) 345 kV to KIOWA 3 (527966) kV to KIOWA_TR1 1 (527964) 13.2 kV CKT1 b. 3. Trip three winding transformer from POTASH_JCT 6 (527963) 230 kV to POTASH_JCT 3 (527962) kV to POTASH_TR1 1 (527958) 13.2 kV CKT1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25W | Transfer | Group5_Fault_0401_P4 | a. Apply single phase fault at GAINES 3 (527322) 115 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from SEMINOLE 3 (527275) 115 kV to GAINES 3 (527322) 115 kV CKT 1 b. 2. Trip branch from GAINES 3 (527322) 115 kV to OXY_WSEM_TP3 (527325) 115 kV CKT 1 b. 3. Trip branch from OXY_WSTSEM 3 (527323) 115 kV to OXY_WSEM_TP3 (527325) 115 kV CKT 1 b. 4. Drop Load 1 OXY_WSTSEM 3 (527323) 115 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | Group5_Fault_0402_P4 | a. Apply single phase fault at HOBBS_INT 6 (527894) 230 kV b. Clear Fault after 16 cycles: b. 1. Trip three winding transformer from HOBBS_INT 7 (527896) 345 kV to HOBBS_INT 6 (527894) kV to HOBBS_TR3 1 (527895) 13.2 kV CKT1 b. 2. Trip branch from HOBBS_INT 6 (527894) 230 kV to ANDREWS 6 (528604) 230 kV CKT 1 | P4 | No | No | No | No | Yes | No | No | Out Of Step Generators and damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25W | Transfer | Group5_Fault_0403_P4 | a. Apply single phase fault at RANDALL 3 (524364) 115 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from GEORGIA 3 (524322) 115 kV to RANDALL 3 (524364) 115 kV CKT 1 b. 2. Trip three winding transformer from RANDALL 6 (524365) 230 kV to RANDALL 3 (524364) kV to RANDAL_TR1 1 (524361) 13.2 kV CKT1 | P4 | Yes | Yes | Yes | No | Yes | Yes | No | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points) |  | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25W | Transfer | Group5_Fault_0404_P4 | a. Apply single phase fault at COULTER 3 (524306) 115 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from 34TH_ST_TP 3 (524281) 115 kV to COULTER 3 (524306) 115 kV CKT 1 b. 2. Trip branch from COULTER 3 (524306) 115 kV to PUCKETT 3 (524256) 115 kV CKT 1 b. 3. Trip branch from PUCKETT 3 (524256) 115 kV to SONCY_TP 3 (524252) 115 kV CKT 1 b. 4. Drop Load 1 PUCKETT 3 (524256) 115 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25W | Transfer | Group5_Fault_0405_P4 | a. Apply single phase fault at EAST_PLANT 3 (524162) 115 kV b. Clear Fault after 16 cycles: b. 1. Trip three winding transformer from EAST_PLANT 6 (524163) 230 kV to EAST_PLANT 3 (524162) kV to EPLANT_TR3 1 (524160) 13.2 kV CKT1 b. 2. Trip branch from HARRNG_WST 6 (523977) 230 kV to EAST_PLANT 6 (524163) 230 kV CKT 1 b. 3. Trip branch from EAST_PLANT 3 (524162) 115 kV to PIERCE_TP 3 (524185) 115 kV CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25W | Transfer | Group5_Fault_0406_P4 | a. Apply single phase fault at NICHOLS 3 (524043) 115 kV b. Clear Fault after 16 cycles: b. 1. Trip three winding transformer from NICHOLS 6 (524044) 230 kV to NICHOLS 3 (524043) kV to NICHOLS_TR11 (524041) 13.2 kV CKT1 b. 2. Trip branch from NICHOLS 3 (524043) 115 kV to WHITAKER 3 (524058) 115 kV CKT 1 b. 3. Trip branch from WHITAKER 3 (524058) 115 kV to EAST_PLANT 3 (524162) 115 kV CKT 1 | P4 | No | No | No | No | No | No | No | Out Of Step Generators and damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25W | Transfer | Group5_Fault_0407_P4 | a. Apply single-phase fault at BVRCNTY7 (515554) 345 kV Bus CB 307 Stuck b. Clear Fault after 16 cycles: b. 1. Trip branch from BVRCNTY7 (515554) 345 kV Bus TO BADGER 7 (515677) 345 kV Bus CKT 1 b. 2. Trip branch from BVRCNTY7 (515554) 345 kV Bus TO BADGER 7 (515677) 345 kV Bus CKT 2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | Group5_Fault_0408_P4 | a. Apply single-phase fault at WWDBORDT (755000) 345 kV Bus CB 384 Stuck b. Clear Fault after 16 cycles: b. 1. Trip branch from WWDBORDT (755000) 345 kV Bus TO BORDER 7 (515458) 345 kV Bus CKT 1 b. 2. Trip branch from BORDER 7 (515458) 345 kV Bus TO CRAWFISH_DR (560022) 345 kV Bus CKT 1 | P4 | No | No | No | No | No | No | No | Out Of Step Generators and damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25W | Transfer | Group5_Fault_0409_P4 | a. Apply single-phase fault at CARPENTER 7 (523823) 345 kV Bus CB OR335 Stuck b. Clear Fault after 21 cycles: b. 1. Trip branch from CARPENTER 7 (523823) 345 kV Bus TO FINNEY 7 (523853) 345 kV Bus CKT 1 b. 2. Clear fault and Disconnect CARPENTER 7 (523823) 345 kV Bus | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25W | Transfer | Group5_Fault_0410_P4 | a. Apply single-phase fault at CROSSROADS 7 (527656) 345 kV CB 6R30 Stuck b. Clear Fault after 21 cycles: b. 1. Trip branch from EDDY_CNTY 7 (527802) 345 kV Bus TO CROSSROADS 7 (527656) 345 kV Bus CKT 1 b. 2. Trip branch from TOLK 7 (525549) 345 kV Bus TO CROSSROADS 7 (527656) 345 kV Bus CKT 1 b. 3. Disconnect Bus RSVLT_CC_E 7 (527655) 345 kV b. 4. Disconnect Bus MILO_WIND 1 (527653) 0.70 kV b. 5. Disconnect Bus RSVLT_GEN1 1 (527651) 0.69 kV b. 6. Disconnect Bus RSVLT_GEN2 1 (527652) 0.69 kV b. 7. Disconnect Bus RSVLT_CC_W 7 (527654) 345 kV b. 8. Drop Generator 1 Bus SAGSFT3_2.21 (527605) 0.70 kV b. 9. Drop Generator 1 Bus SAGSFT4_2.21 (527607) 0.70 kV b. 10. Drop Generator 1 Bus SAGSFT1_2.21 (527614) 0.70 kV b. 11. Drop Generator 1 Bus SAGSFT1_2.01 (527615) 0.70 kV b. 12. Drop Generator 1 Bus SAGSFT2_2.21 (527617) 0.70 kV b. 13. Drop Generator 1 Bus SAGSFT2_2.01 (527618) 0.70 kV b. 14. Drop Load 1 Bus SAGA_SCOL 7 (527610) 345 kV b. 15. Drop Load 2 Bus SAGA_SCOL 7 (527610) 345 kV b. 16. Disconnect Bus SAGA_NDCOL 7 (527598) 345 kV b. 17. Disconnect Bus SAGA_SDCOL 7 (527599) 345 kV b. 18. Disconnect Bus SAGA_SMEAS 7 (527600) 345 kV b. 19. Disconnect Bus SAGA_NCOL 7 (527601) 345 kV b. 20. Disconnect Bus SAGANCOL1 1 (527602) 34.5 kV b. 21. Disconnect Bus SAGANCOL2 1 (527603) 34.5 kV b. 22. Disconnect Bus GRDXFR3 1 (527604) 0.50 kV b. 23. Disconnect Bus SAGSFT3_2.21 (527605) 0.70 kV b. 24. Disconnect Bus GRDXFR4 1 (527606) 0.50 kV b. 25. Disconnect Bus SAGSFT4_2.21 (527607) 0.70 kV b. 26. Disconnect Bus SUB BUS #3 1 (527608) 34.5 kV b. 27. Disconnect Bus SUB BUS #4 1 (527609) 34.5 kV b. 28. Disconnect Bus SAGA_SCOL 7 (527610) 345 kV b. 29. Disconnect Bus SAGASCOL1 1 (527611) 34.5 kV b. 30. Disconnect Bus SAGASCOL2 1 (527612) 34.5 kV b. 31. Disconnect Bus GRDXFR1 1 (527613) 0.50 kV b. 32. Disconnect Bus SAGSFT1_2.21 (527614) 0.70 kV b. 33.Disconnect Bus SAGSFT1_2.01 (527615) 0.70 kV b. 34. Disconnect Bus GRDXFR2 1 (527616) 0.50 kV b. 35. Disconnect Bus SAGSFT2_2.21 (527617) 0.70 kV b. 36. Disconnect Bus SAGSFT2_2.01 (527618) 0.70 kV b. 37. Disconnect Bus SAGA_NCLTR31 (527621) 13.8 kV b. 38. Disconnect Bus SAGA_NCLTR41 (527622) 13.8 kV b. 39. Disconnect Bus SAGA_SCLTR11 (527623) 13.8 kV b. 40. Disconnect Bus SAGA_SCLTR21 (527624) 13.8 kV b. 41. Disconnect Bus SUB BUS #1 (527628) 34.5 kV b. 42. Disconnect Bus SUB BUS #2 (527629) 34.5 kV b. 43. Disconnect Bus CROSSROADS 7 (527656) 345 kV b. 44. Disconnect Bus RSVLT_WIND11 (527658) 34.5 kV b. 45. Disconnect Bus RSVLT_WIND21 (527659) 34.5 kV b. 46. Disconnect Bus RSVLT_COL1 1 (527660) 34.5 kV b. 47. Disconnect Bus RSVLT_COL2 1 (527661) 34.5 kV b. 48. Disconnect Bus RSVLT_TR1 1 (527662) 13.2 kV b. 49. Disconnect Bus RSVLT_TR2 1 (527663) 13.2 kV b. 50. Disconnect Bus RSVLT_COL1 7 (527666) 345 kV b. 51. Disconnect Bus RSVLT_COL2 7 (527667) 345 kV b. 52. Disconnect Bus MILO_CB (577120) 34.5 kV b. 53. Disconnect Bus MILO_WND (577121) 34.5 kV | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer
05 - Southwest | 25W | Transfer | Group5_Fault_0411_P4 | Apply single-phase fault at CROSSROADS 7 (527656) 345 kV Bus CB 6R45 Stuck b. Run for 21 cycles: b. 1. Trip branch from CROSSROADS 7 (527656) 345 kV Bus TO TOLK 7 (525549) 345 kV Bus CKT 1 b. 2. Trip branch from CROSSROADS 7 (527656) 345 kV Bus TO SAGA_SCOL 7 (527610) 345 kV Bus CKT 1 b. 3. Disconnect Bus SAGSFT3_2.21 (527605) 0.70 kV b. 4. Disconnect Bus GRDXFR4 1 (527606) 0.50 kV b. 5. Disconnect Bus SAGSFT4_2.21 (527607) 0.70 kV b. 6. Disconnect Bus SUB BUS #3 1 (527608) 34.5 kV b. 7. Disconnect Bus SUB BUS #4 1 (527609) 34.5 kV b. 8. Disconnect Bus GRDXFR1 1 (527613) 0.5 kV b. 9. Disconnect Bus SAGSFT1_2.21 (527614) 0.70 kV b. 10. Disconnect Bus SAGSFT1_2.01 (527615) 0.70 kV b. 11. Disconnect Bus GRDXFR2 1 (527616) 0.5 kV b. 12. Disconnect Bus SAGSFT2_2.21 (527617) 0.70 kV b. 13. Disconnect Bus SAGSFT2_2.01 (527618) 0.70 kV b. 14. Clear fault at Bus CROSSROADS 7 (527656) 345 kV b. 15. Drop Load 1 Bus SAGA_SCOL 7 (527610) 345 kV b. 16. Drop Load 2 Bus SAGA_SCOL 7 (527610) 345 kV b. 17. Disconnect Bus SAGA_NDCOL 7 (527598) 345 kV b. 18. Disconnect Bus SAGA_SDCOL 7 (527599) 345 kV b. 19. Disconnect Bus SAGA_SMEAS 7 (527600) 345 kV b. 20. Disconnect Bus SAGA_NCOL 7 (527601) 345 kV b. 21. Disconnect Bus SAGANCOL1 1 (527602) 34.5 kV b. 22. Disconnect Bus SAGANCOL2 1 (527603) 34.5 kV b. 23. Disconnect Bus GRDXFR3 1 (527604) 0.50 kV b. 24. Disconnect Bus SAGA_SCOL 7 (527610) 345 kV b. 25. Disconnect Bus SAGASCOL1 1 (527611) 34.5 kV b. 26. Disconnect Bus SAGASCOL2 1 (527612) 34.5 kV b. 27. Disconnect Bus SAGA_NCLTR31 (527621) 13.8 kV b. 28. Disconnect Bus SAGA_NCLTR41 (527622) 13.8 kV b. 29. Disconnect Bus SAGA_SCLTR11 (527623) 13.8 kV b. 30. Disconnect Bus SAGA_SCLTR21 (527624) 13.8 kV b. 31. Disconnect Bus SUB BUS #1 (527628) 34.5 kV b. 32. Disconnect Bus SUB BUS #2 (527629) 34.5 kV | P4 | No | Yes | Yes | Yes | No | No | Yes | Out Of Step Generators and damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer
05 - Southwest | 25W | Transfer | Group5_Fault_0412_P4 | a. Apply single-phase fault at CHINA_DRAW 7 (528223) 345 kV Bus CB 4T805 Stuck b. Clear Fault after 16 cycles: b. 1. Trip branch from CHINA_DRAW 7 (528223) 345 kV Bus TO PHANTOM 7 (528015) 345 kV Bus CKT 1 b. 2. Disconnect Bus CHINA_DRAW 1 (528219) 13.2 kV b. 3. Disconnect Bus CARPENTER 7 (523823) 345 kV | P4 | No | No | No | Yes | No | No | No | Out Of Step Generators and damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25W | Transfer | Group5_Fault_0413_P4 | a. Apply single-phase fault at CHINA_DRAW 7 (528223) 345 kV Bus CB TF#### Stuck b. 1. Run for 5 cycles, Disconnect Bus CHINA_DRAW 1 (528219) 13.2 kV b. 2. Run for 11 cycles, Trip branch from CHINA_DRAW 7 (528223) 345 kV Bus TO N_LOVING 7 (528185) 345 kV Bus CKT 1 b. 3. Clear fault and run for 5 cycles, Trip branch from CHINA_DRAW 7 (528223) 345 kV Bus TO PHANTOM 7 (528015) 345 kV Bus CKT 1 b. 4. Disconnect Bus CHINA_DRAW 1 (528219) 13.2 kV b. 5. Disconnect Bus CARPENTER 7 (523823) 345 kV | P4 | No | No | No | Yes | No | No | No | Out Of Step Generators and damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523936 [PANTEX_WIND10.6900]
05 - Southwest | 25W | Transfer | Group5_Fault_0414_P4 | a. Apply single-phase fault at CHINA_DRAW 7 (528223) 345 kV Bus CB J27#### Stuck b. 1. Run for 16 cycles, Disconnect Bus CHINA_DRAW 1 (528219) 13.2 kV b. 2. Clear fault and run for 5 cycles: b. 3. Trip branch from CHINA_DRAW 7 (528223) 345 kV Bus TO N_LOVING 7 (528185) 345 kV Bus CKT 1 b. 4. Trip branch from CHINA_DRAW 7 (528223) 345 kV Bus TO PHANTOM 7 (528015) 345 kV Bus CKT 1 b. 5. Disconnect Bus CHINA_DRAW 1 (528219) 13.2 kV b. 6. Disconnect Bus CARPENTER 7 (523823) 345 kV | P4 | No | No | No | Yes | No | No | No | Out Of Step Generators and damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25W | Transfer | Group5_Fault_0415_P4 | a. Apply single-phase fault at EDDY_CNTY 7 (527802) 345 kV Bus CB 4R00 Stuck b. 1. Run for 16 cycles, Trip branch from EDDY_CNTY 7 (527802) 345 kV Bus TO KIOWA 7 (527965) 345 kV Bus CKT 1 b. 2. Clear fault and run for 5 cycles, Trip branch from EDDY_CNTY 7 (527802) 345 kV Bus TO CROSSROADS 7 (527656) 345 kV Bus CKT 1 b. 3. Disconnect Bus EDDY_TR 1 (527796) 13.2 kV b. 4. Disconnect Bus EDDY_CNTY 7 (527802) 345 kV | P4 | No | No | No | No | No | No | No | Out Of Step Generators and damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25W | Transfer | Group5_Fault_0416_P4 | a. Apply single-phase fault at EDDY_CNTY 7 (527802) 345 kV Bus CB J24#### Stuck b. 1. Run for 16 cycles, Disconnect Bus EDDY_TR 1 (527796) 13.2 kV b. 2. Clear fault and run for 5 cycles: b. 3. Trip branch from EDDY_CNTY 7 (527802) 345 kV Bus TO CROSSROADS 7 (527656) 345 kV Bus CKT 1 b. 4. Trip branch from EDDY_CNTY 7 (527802) 345 kV Bus TO KIOWA 7 (527965) 345 kV Bus CKT 1 b. 5. Disconnect Bus EDDY_TR 1 (527796) 13.2 kV b. 6. Disconnect Bus EDDY_CNTY 7 (527802) 345 kV | P4 | No | No | No | No | Yes | No | No | Out Of Step Generators and damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25W | Transfer | Group5_Fault_0417_P4 | a. Apply single-phase fault at EDDY_CNTY 7 (527802) 345 kV Bus CB TF#### Stuck b. 1. Run for 5 cycles, Disconnect Bus EDDY_TR 1 (527796) 13.2 kV b. 2. Run for 11 cycles, Trip branch from EDDY_CNTY 7 (527802) 345 kV Bus TO CROSSROADS 7 (527656) 345 kV Bus CKT 1 b. 3. Clear fault and run for 5 cycles, Trip branch from EDDY_CNTY 7 (527802) 345 kV Bus TO KIOWA 7 (527965) 345 kV Bus CKT 1 b. 4. Disconnect Bus EDDY_TR 1 (527796) 13.2 kV b. 5. Disconnect Bus EDDY_CNTY 7 (527802) 345 kV | P4 | No | No | No | No | Yes | No | Yes | Out Of Step Generators and damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer
05 - Southwest | 25W | Transfer | Group5_Fault_0418_P4 | a. Apply single-phase fault at FINNEY 7 (523853) 345 kV Bus CB OR70 Stuck b. Clear Fault after 21 cycles: b. 1. Trip branch from HOLCOMB7 (531449) 345 kV Bus TO FINNEY 7 (523853) 345 kV Bus CKT 1 b. 2. Trip branch from CARPENTER 7 (523823) 345 kV TO FINNEY 7 (523853) 345 kV Bus CKT 1 b. 3. Disconnect Bus 523853 b. 4. Disconnect Bus 599950 b. 5. Disconnect Bus 599951 b. 6. Disconnect Bus 523118 b. 7. Disconnect Bus 523114 b. 8. Disconnect Bus 523115 b. 9. Disconnect Bus 523116 b. 10. Disconnect Bus 523117 b. 11. Drop Generator 1 Bus 523061 b. 12. Drop Generator 1 Bus 523062 b. 13. Disconnect Bus 523061 b. 14. Disconnect Bus 523062 b. 15. Disconnect Bus 523063 b. 16. Disconnect Bus 523064 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | Group5_Fault_0419_P4 | a. Apply single-phase fault at HITCHLAND 7 (523097) 345 kV Bus CB 1R75 Stuck b. Clear Fault after 21 cycles: b. 1. Trip branch from HITCHLAND 7 (523097) 345 kV Bus TO BVRCNTY7 (515554) 345 kV Bus CKT 2 b. 2. Disconnect Bus 523112 b. 3. Disconnect Bus 523111 b. 4. Disconnect Bus 523109 b. 5. Disconnect Bus 523107 b. 6. Disconnect Bus 523110 b. 7. Drop Generator 1 Bus 523107 b. 8. Drop Load A1 Bus 523107 b. 9. Drop Generator 1 Bus 560585 b. 10. Drop Generator 1 Bus 560586 b. 11. Disconnect Bus 560577 b. 12. Disconnect Bus 560582 b. 13. Disconnect Bus 560585 b. 14. Disconnect Bus 560583 b. 15. Disconnect Bus 560586 b. 16. Disconnect Bus 560578 | P4 | Yes | Yes | Yes | No | Yes | Yes | No | Low voltage ride through fails due to the tripping of G18-115-GEN10 and G18-115-GEN20 units. No cascading was observed and the issue was localised. Model tuning is recommended.
05 - Southwest | 25W | Transfer | Group5_Fault_0420_P4 | a. Apply single-phase fault at HOBBS_INT 7 (527896) 345 kV Bus CB 4R240 Stuck b. Clear Fault after 21 cycles: b. 1. Trip branch from HOBBS_INT 7 (527896) 345 kV Bus TO KIOWA 7 (527965) 345 kV Bus CKT 1 b. 2. Trip branch from HOBBS_INT 7 (527896) 345 kV Bus TO YOAKUM_345 (526936) 345 kV Bus CKT 1 b. 3. Disconnect Bus HOBBS_TR3 1 (527895) 13.2 kV b. 4. Disconnect Bus HOBBS_INT 7 (527896) 345 kV | P4 | Yes | No | Yes | No | Yes | Yes | No | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points) |  | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25W | Transfer | Group5_Fault_0421_P4 | a. Apply single-phase fault at KIOWA 7 (527965) 345 kV Bus CB TF#### Stuck b. 1. Run for 5 cycles, Disconnect Bus KIOWA_TR1 1 (527964) 13.2 kV b. 2. Clear fault and run for 16 cycles, Trip branch from KIOWA 7 (527965) 345 kV TO RDRUNNER 7 (528027) Bus CKT 1 b. 3. Disconnect Bus KIOWA_TR1 1 (527964) 13.2 kV | P4 | No | No | No | Yes | No | No | No | Out Of Step Generators and damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25W | Transfer | Group5_Fault_0422_P4 | a. Apply single-phase fault at KIOWA 7 (527965) 345 kV Bus CB J23#### Stuck b. 1. Clear fault and run for 16 cycles, Trip branch from KIOWA 7 (527965) 345 kV TO RDRUNNER 7 (528027) Bus CKT 1 b. 2. Disconnect Bus KIOWA_TR1 1 (527964) 13.2 kV | P4 | No | No | No | No | Yes | No | No | Out Of Step Generators and damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25W | Transfer | Group5_Fault_0423_P4 | a. Apply single-phase fault at N_LOVING (528185) 345 kV Bus CB 4S120 Stuck b. 1. Run for 16 cycles, Trip branch from N_LOVING (528185) 345 kV TO CHINA_DRAW 7 (528223) 345 kV Bus CKT 1 b. 2. Clear fault and run for 5 cycles, Trip branch from N_LOVING (528185) 345 kV TO KIOWA 7 (527965) 345 kV CKT 1 b. 3. Disconnect Bus N_LOVING TR1 (528186) 13.2 kV b. 4. Disconnect Bus N_LOVING (528185) 345 kV | P4 | No | No | No | No | No | No | Yes | Out Of Step Generators and damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer
05 - Southwest | 25W | Transfer | Group5_Fault_0424_P4 | a. Apply single-phase fault at N_LOVING (528185) 345 kV Bus CB 4S110 Stuck b. 1. Run for 5 cycles, Disconnect Bus N_LOVING TR1 (528186) 13.2 kV b. 2. Run for 11 cycles, Trip branch from N_LOVING (528185) 345 kV TO KIOWA 7 (527965) 345 kV CKT 1 b. 3. Clear fault and run for 5 cycles, Trip branch from N_LOVING (528185) 345 kV TO CHINA_DRAW 7 (528223) 345 kV Bus CKT 1 b. 4. Disconnect Bus N_LOVING (528185) 345 kV | P4 | No | No | No | Yes | No | No | No | Out Of Step Generators and damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25W | Transfer | Group5_Fault_0425_P4 | a. Apply single-phase fault at N_LOVING (528185) 345 kV Bus CB 4S110 Stuck b. 1. Run for 16 cycles, Disconnect Bus N_LOVING TR1 (528186) 13.2 kV b. 2. Clear fault and run for 5 cycles: b. 3. Trip branch from N_LOVING (528185) 345 kV TO CHINA_DRAW 7 (528223) 345 kV Bus CKT 1 b. 4. Trip branch from N_LOVING (528185) 345 kV TO KIOWA 7 (527965) 345 kV CKT 1 b. 5. Disconnect Bus N_LOVING TR1 (528186) 13.2 kV b. 6. Disconnect Bus N_LOVING (528185) 345 kV | P4 | No | No | No | No | No | No | No | Out Of Step Generators and damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 763397 [G18-124-GEN10.6600]
05 - Southwest | 25W | Transfer | Group5_Fault_0426_P4 | a. Apply single-phase fault at POTTER_CO 7 (523961) 345 kV Bus CB 2R05 Stuck b. Clear Fault after 21 cycles: b. 1. Trip branch from HITCHLAND 7 (523097) 345 kV Bus TO POTTER_CO 7 (523961) 345 kV Bus CKT 1 b. 2. Disconnect bus 523957 b. 3. Disconnect bus 523957 b. 4. Disconnect bus 523961 b. 5. Disconnect bus 524296 b. 6. Disconnect bus 524299 b. 7. Disconnect bus 524298 b. 8. Disconnect bus 524294 b. 9. Disconnect bus 524295 b. 10. Disconnect bus 524297 | P4 | No | No | No | Yes | No | No | No | Out Of Step Generators and damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25W | Transfer | Group5_Fault_0427_P4 | a. Apply single-phase fault at RDRUNNER 7 (528027) 345 kV Bus CB J23#### Stuck b. 1. Run for 16 cycles, Trip branch from RDRUNNER 7(528027) 345 kV TO PHANTOM 7 (528015) 345 kV Bus CKT 1 b. 2. Clear fault and run for 5 cycles, Trip branch from KIOWA 7 (527965) 345 kV TO RDRUNNER 7 (528027) Bus CKT 1 b. 3. Disconnect Bus RDRNNER_TR11 (528023) 13.2 kV b. 4. Disconnect Bus RDRUNNER 7(528027) 345 kV | P4 | No | No | No | No | Yes | No | No | Out Of Step Generators and damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25W | Transfer | Group5_Fault_0428_P4 | a. Apply single-phase fault at RDRUNNER 7 (528027) 345 kV Bus CB #### Stuck b. 1. Run for 5 cycles, Disconnect Bus RDRNNER_TR11 (528023) 13.2 kV b. 2. Run for 11 cycles, Trip branch from KIOWA 7 (527965) 345 kV TO RDRUNNER 7 (528027) Bus CKT 1 b. 3. Clear fault and run for 5 cycles, Trip branch from RDRUNNER 7(528027) 345 kV TO PHANTOM 7 (528015) 345 kV Bus CKT 1 b. 4. Disconnect Bus RDRUNNER 7(528027) 345 kV | P4 | No | No | No | Yes | No | No | No | Out Of Step Generators and damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25W | Transfer | Group5_Fault_0429_P4 | a. Apply single-phase fault at RDRUNNER 7 (528027) 345 kV Bus CB J22#### Stuck b. 1. Run for 16 cycles, Disconnect Bus RDRNNER_TR11 (528023) 13.2 kV b. 2. Clear fault and run for 5 cycles: b. 3. Trip branch from RDRUNNER 7(528027) 345 kV TO PHANTOM 7 (528015) 345 kV Bus CKT 1 b. 4. Trip branch from KIOWA 7 (527965) 345 kV TO RDRUNNER 7 (528027) Bus CKT 1 b. 5. Disconnect Bus RDRUNNER 7(528027) 345 kV | P4 | No | No | No | Yes | No | No | No | Out Of Step Generators and damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25W | Transfer | Group5_Fault_0430_P4 | a. Apply single-phase fault at YOAKUM_345 (526936) 345 kV Bus CB J18#### Stuck b. 1. Run for 16 cycles, Trip branch from YOAKUM_345 (526936) 345 kV Bus TO TUCO_INT 7 (525832) 345 kV Bus CKT 1 b. 2. Clear fault and run for 5 cycles, Tri branch from YOAKUM_345 (526936) 345 kV Bus TO HOBBS_INT 7 (527896) 345 kV Bus CKT 1 b. 3. Disconnect Bus YOAKUM_TR1 (526937) 13.2 kV b. 4. Disconnect Bus YOAKUM_345 (526936) 345 kV | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer
05 - Southwest | 25W | Transfer | Group5_Fault_0431_P4 | a. Apply single-phase fault at YOAKUM_345 (526936) 345 kV Bus CB TF##### Stuck b. 1. Run for 5 cycles, Disconnect Bus YOAKUM_TR1 (526937) 13.2 kV b. 2. Run for 11 cycles, Trip branch from YOAKUM_345 (526936) 345 kV Bus TO HOBBS_INT 7 (527896) 345 kV Bus CKT 1 b. 3. Clear fault and run for 5 cycles, Trip branch from YOAKUM_345 (526936) 345 kV Bus TO TUCO_INT 7 (525832) 345 kV Bus CKT 1 b. 4. Disconnect Bus YOAKUM_345 (526936) 345 kV | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer
05 - Southwest | 25W | Transfer | Group5_Fault_0432_P4 | a. Apply single-phase fault at YOAKUM_345 (526936) 345 kV Bus CB J17#### Stuck b. 1. Run for 16 cycles, Disconnect Bus YOAKUM_TR1 (526937) 13.2 kV b. 2. Clear fault and run for 5 cycles: b. 3. Trip branch from YOAKUM_345 (526936) 345 kV Bus TO TUCO_INT 7 (525832) 345 kV Bus CKT 1 b. 4. Trip branch from YOAKUM_345 (526936) 345 kV Bus TO HOBBS_INT 7 (527896) 345 kV Bus CKT 1 b. 5. Disconnect Bus YOAKUM_345 (526936) 345 kV | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer
05 - Southwest | 25W | Transfer | Group5_Fault_0433_P4 | a. Apply single-phase fault at TUCO_INT 7 (525832) 345 kV Bus CB NR20 Stuck b. 1. Run for 5 cycles, Disconnect Bus TUCO_TR1 1 (525824) 13.2 kV b. 2. Clear fault and run for 11 cycles, Trip branch from TUCO_INT 7 (525832) 345 kV Bus TO CRAWFISH_DR (560022) 345 kV Bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 763309 [G18-112-GEN10.6600]
05 - Southwest | 25W | Transfer | Group5_Fault_0434_P4 | a. Apply single-phase fault at MUSTANG 3 (527146) 115 kV Bus b. 1. Run for 5 cycles, Disconnect Bus MUSTANG_2 1 (527162) 13.2 kV b. 2. Clear fault and run for 11 cycles, Trip branch from SEAGRAVES 3 (527202) 115 kV Bus TO MUSTANG 3 (527146) 115 kV Bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer
05 - Southwest | 25W | Transfer | Group5_Fault_0435_P4 | a. Apply SLG fault at NICHOLS 6 (524044) 230 kV Bus b. Clear Fault after 21 cycles: b. 1. Trip branch from NICHOLS (523978) 230 kV Bus TO NICHOLS 6 (524044) 230 kV Bus CKT 2 b. 2. Trip branch from HUTCHISON 6 (523551) 230 kV Bus TO NICHOLS 6 (524044) 230 kV Bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25W | Transfer | Group5_Fault_0436_P4 | a. Apply single-phase fault at NICHOLS 6 (524044) 230 kV Bus b. 1. Run for 5 cycles, Disconnect Bus NICHOLS_TR11 (524041) 13.2 kV b. 2. Clear fault and run for 11 cycles, Disconnect Bus from NICHOLS_3 1 (524023) 22 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25W | Transfer | Group5_Fault_0437_P4 | a. Apply single-phase fault at POTTER_CO 6 (523959) 230 kV Bus b. Clear Fault after 21 cycles: b. 1. Trip branch from POTTER_CO 6 (523959) 230 kV Bus TO BUSHLAND 6 (524267) 230 kV Bus CKT 1 b. 2. Trip branch from POTTER_CO 6 (523959) 230 kV Bus TO ROLLHILLS 6 (524010) 230 kV Bus CKT 1 | P4 | No | No | No | No | Yes | No | No | Out Of Step Generators and damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25W | Transfer | Group5_Fault_0438_P4 | a. Apply single-phase fault at YOAKUM 6 (526935) 230 kV Bus b. 1. Run for 5 cycles, Disconnect Bus YOAKUM_TR1 1 (526931) 13.2 kV b. 2. Clear fault and run for 11 cycles, Trip branch from YOAKUM 6 (526935) 230 kV Bus TO NEEDMORE 6 (525586) 230 kV Bus CKT 1 | P4 | No | No | No | Yes | No | No | Yes | Out Of Step Generators and damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer
05 - Southwest | 25W | Transfer | Group5_Fault_0439_P4 | a. Apply single-phase fault at TUCO_INT 7 (525832) 345 kV Bus b. Clear Fault after 21 cycles: b. 1. Trip branch from TUCO_INT 7 (525832) 345 kV Bus TO CRAWFISH_DR (560022) 345 kV Bus CKT 1 b. 2. Disconnect Bus TUCO_TR1 1 (525824) 13.2 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 763084 [G18-073-GEN20.6600]
05 - Southwest | 25W | Transfer | Group5_Fault_0440_P4 | a. Apply single-phase fault at TUCO_INT 7 (525832) 345 kV Bus b. Clear Fault after 21 cycles: b. 1. Trip branch from TUCO_INT 7 (525832) 345 kV Bus TO CRAWFISH_DR (560022) 345 kV Bus CKT 1 b. 2. Disconnect Bus TUCO_TR2 1 (525825) 13.2 kV | P4 | Yes | Yes | Yes | Yes | Yes | No | No | Damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 763084 [G18-073-GEN20.6600]
05 - Southwest | 25W | Transfer | Group5_Fault_0441_P4 | a. Apply single-phase fault at TUCO_INT 7 (525832) 345 kV Bus b. 1. Run for 5 cycles, Disconnect Bus TUCO_TR2 1 (525825) 13.2 kV b. 2. Clear fault and run for 11 cycles, Trip branch from TUCO_INT 7 (525832) 345 kV Bus TO CRAWFISH_DR (560022) 345 kV Bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer
05 - Southwest | 25W | Transfer | Group5_Fault_0442_P4 | a. Apply single-phase fault at HITCHLAND 7 (523097) 345 kV Bus b. 1. Run for 5 cycles, Disconnect Bus HITCHLD_TR01 (523091) 13.2 kV b. 2. Clear fault and run for 11 cycles, Disconnect Bus HITCHLD_TR01 (523091) 13.2 kV | P4 | Yes | Yes | Yes | No | Yes | No | No | Damping issues observed. Low voltage ride through fails due to the tripping of G18-115-GEN10 and G18-115-GEN20 units. No cascading was observed and the issue was localised. Model tuning is recommended. | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25W | Transfer | Group5_Fault_0443_P4 | a. Apply single-phase fault at POTTER_CO 7 (523961) 345 kV Bus b. 1. Run for 5 cycles, Disconnect Bus POTTER_TR 1 (523957) 13.2 kV b. 2. Clear fault and run for 11 cycles, Disconnect Bus POTTER_TR 1 (523957) 13.2 kV b. 3. Run for 5 cycles: b. 4. Trip branch from HITCHLAND 7 (523097) 345 kV Bus TO POTTER_CO 7 (523961) 345 kV Bus CKT 1 b. 5. Disconnect bus 523957 b. 6. Disconnect bus 523961 b. 7. Disconnect bus 524296 b. 8. Disconnect bus 524299 b. 9. Disconnect bus 524298 b. 10. Disconnect bus 524294 b. 11. Disconnect bus 524295 b. 12. Disconnect bus 524297 | P4 | No | No | No | No | No | No | No | Out Of Step Generators and damping issues observed | Potter to Tolk 345 kV Double Circuit Line Build Potter to Chisholm 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer Potter to Tolk 345 kV | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000], 763397 [G18-124-GEN1], 763309 [G18-112-GEN1]
05 - Southwest | 25W | Transfer | Group5_Fault_0444_P4 | a. Apply single-phase fault at BUSHLAND 6 (524267) 230 kV Bus b. 1. Run for 5 cycles, Drop Shunt 1 BUSHLAND 6 (524267) 230 kV Bus b. 2. Run for 11 cycles, Disconnect Bus BUSHLAND 6 (524267) 230 kV b. 3. Disconnect Bus WILDORA_GEN1 (524285) 0.69 kV b. 4. Disconnect Bus GS-PHWD_GEN1 (524287) 0.69 kV b. 5. Clear fault at BUSHLAND 6 (524267) 230 kV b. 6. Disconnect Bus BSHLND_TR1 1 (524263) 13.2 kV b. 7. Disconnect Bus WILDOR_WND 1 (524275) 34.5 kV b. 8. Disconnect Bus WILDOR_WND 6 (524276) 230 kV b. 9. Disconnect Bus GS-PHWDRNCH1 (524289) 34.5 kV b. 10. Disconnect Bus WILDOR2_JUS6 (524290) 230 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25W | Transfer | Group5_Fault_0445_P4 | a. Apply single-phase fault at SWISHER 6 (525213) 230 kV b. 1. Run for 5 cycles, Drop Shunt 1 SWISHER 6 (525213) 230 kV b. 2. Clear fault and run for 11 cycles, Trip branch from SWISHER 6 (525213) 230 kV Bus TO TUCO_INT 6 (525830) 230 kV Bus CKT 1 | P4 | Yes | Yes | Yes | No | Yes | No | No | Damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 763309 [G18-112-GEN10.6600]
05 - Southwest | 25W | Transfer | Group5_Fault_0446_P4 | a. Apply single-phase fault at TUCO_INT 6 (525830) 230 kV b. 1. Run for 5 cycles, Drop Shunt 1 TUCO_INT 6 (525830) 230 kV b. 2. Clear fault and run for 11 cycles, Disconnect BusTUCO_TR3 1 (525819) 13.2 kV | P4 | Yes | Yes | Yes | No | Yes | No | No | Damping issues observed. Low voltage ride through fails due to the tripping of G18-115-GEN10 and G18-115-GEN20 units. No cascading was observed and the issue was localised. Model tuning is recommended. | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer
05 - Southwest | 25W | Transfer | Group5_Fault_0447_P4 | a. Apply single-phase fault at BUSHLAND 6 (524267) 230 kV Bus b. Clear Fault after 5 cycles: b. 1. Trip branch from BUSHLAND 6 (524267) 230 kV Bus TO WILDOR2_JUS6 (524290) 230 kV Bus CKT 1 b. 2. Drop Shunt 1 BUSHLAND 6 (524267) 230 kV Bus b. 3. Disconnect Bus BSHLND_TR1 1 (524263) 13.2 kV b. 4. Disconnect Bus WILDORA_GEN1 (524285) 0.69 kV b. 5. Disconnect Bus GS-PHWD_GEN1 (524287) 0.69 kV b. 6. Trip branch from BUSHLAND 6 (524267) 230 kV Bus TO POTTER_CO 6 (523959) 230 kV Bus CKT 1 b. 7. Clear Fault after 16 cycles: b. 8. Trip branch from BUSHLAND 6 (524267) 230 kV Bus TO DEAFSMITH 6 (524623) 230 kV Bus CKT 1 b. 9. Disconnect Bus WILDOR_WND 1 (524275) 34.5 kV b. 10. Disconnect Bus WILDOR_WND 6 (524276) 230 kV b. 11. Disconnect Bus GS-PHWDRNCH1 (524289) 34.5 kV b. 12. Disconnect Bus WILDOR2_JUS6 (524290) 230 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | Group5_Fault_0448_P4 | a. Apply single-phase fault at HARRNG_WST 6 (523977) 230 kV Bus b. Clear Fault after 16 cycles: b. 1. Trip branch from HARRNG_WST 6 (523977) 230 kV Bus TO ROLLHILLS 6 (524010) 230 kV Bus CKT 1 b. 2. Trip branch from HARRNG_WST 6 (523977) 230 kV Bus TO EAST_PLANT 6 (524163) 230 kV Bus CKT 1 b. 3. Trip branch from HARRNG_WST 6 (523977) 230 kV Bus TO NICHOLS 6 (524044) 230 kV Bus CKT 1 b. 4. Disconnect Bus HARRNG_WST 6 (523977) 230 kV b. 5. Disconnect Bus HARRNGTON1 1 (523971) 24 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25W | Transfer | Group5_Fault_0449_P4 | a. Apply single-phase fault at HARRNG_MID 6 (523978) 230 kV Bus b. Clear Fault after 16 cycles: b. 1. Trip branch from HARRNG_MID 6 (523978) 230 kV Bus TO RANDALL 6 (524365) 230 kV Bus CKT 1 b. 2. Trip branch from HARRNG_MID 6 (523978) 230 kV Bus TO NICHOLS 6 (524044) 230 kV Bus CKT 2 b. 3. Disconnect Bus HARRNG_MID 6 (523978) 230 kV b. 4. Disconnect Bus HARRNGTON2 1 (523972) 24 kV | P4 | No | Yes | Yes | Yes | Yes | No | Yes | Out Of Step Generators and damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25W | Transfer | Group5_Fault_0450_P4 | a. Apply single-phase fault at HARRNG_EST 6 (523979) 230 kV Bus b. Clear Fault after 16 cycles: b. 1. Trip branch from HARRNG_EST 6 (523979) 230 kV Bus TO PRINGLE 6 (523267) 230 kV Bus CKT 1 b. 2. Trip branch from HARRNG_EST 6 (523979) 230 kV Bus TO POTTER_CO 6 (523959) 230 kV Bus CKT 1 b. 3. Disconnect Bus HARRNG_EST 6 (523979) 230 kV b. 4. Disconnect Bus HARRNGTON3 1 (523973) 24 kV | P4 | No | Yes | Yes | Yes | Yes | No | Yes | Out Of Step Generators and damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25W | Transfer | Group5_Fault_0451_P4 | a. Apply single-phase fault at JONES 6 (526337) 230 kV b. 1. Clear fault and run for 18 cycles, Disconnect Bus from JONES 6 (526337) 230 kV b. 2. Disconnect Bus from JONES_1 1 (526331) 22 kV | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer
05 - Southwest | 25W | Transfer | Group5_Fault_0452_P4 | a. Apply single-phase fault at HARRNG_MID 6 (523978) 230 kV b. 1. Clear fault and run for 5 cycles, Disconnect Bus from HARRNG_MID 6 (523978) 230 kV b. 2. Drop Generator 1 Bus 523972 b. 3. Drop Load S1 Bus 523972 b. 4. Disconnect Bus 523972 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25W | Transfer | Group5_Fault_0453_P4 | a. Apply single-phase fault at MOORE_E 3 (523308) 115 kV b. 1. Clear fault and run for 5 cycles, Disconnect Bus from MOORE_E 3 (523308) 115 kV b. 2. Drop Generator 1 Bus 523297 b. 3. Drop Generator 3 Bus 523301 b. 4. Drop Load F1 Bus 523297 b. 5. Drop Load 1 Bus 523301 b. 6. Drop Load A3 Bus 523301 b. 7. Disconnect Bus 523294 b. 8. Disconnect Bus 523295 b. 9. Disconnect Bus 523296 b. 10. Disconnect Bus 523297 b. 11. Disconnect Bus 523301 b. 12. Disconnect Bus 523302 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | Group5_Fault_0454_P4 | a. Apply single-phase fault at O.K.U.-7 (762467) 345 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from G18-092 TAP (763215) 345 kV Bus TO G18-015 TAP (762467) 345 kV Bus Ckt 1 b. 2. Trip branch from G17-151 (762216) 345 kV Bus TO G18-015 TAP (762467) 345 kV Bus Ckt 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes

## Short Circuit Analysis
Gen Number | Group | Bus Number | Bus Name | Bus Voltage (kV) | Request Not In Service 25SP Fault Current 3-Phase (kA) | Request In Service 25SP Fault Current 3-Phase (kA) | Change in Fault Current (kA) | Circuit Breakers Exceeding Capacity | Facilities Required to Interconnect
GEN-2015-089_GEN-2018-070 | 01 NORTH | 652526 | UTICAJC4 | 230 | 8.4184 | 8.0469 | 0.3715
GEN-2015-089_GEN-2018-070 | 01 NORTH | 652509 | FTRANDL4 | 230 | 12.1336 | 12.0707 | 0.0629
GEN-2015-089_GEN-2018-070 | 01 NORTH | 652626 | UTICAJC7 | 115 | 8.7387 | 8.6376 | 0.1011
GEN-2015-089_GEN-2018-070 | 01 NORTH | 654457 | PRVLNG16 | 230 | 8.3621 | 7.9905 | 0.3716
GEN-2015-089_GEN-2018-070 | 01 NORTH | 655484 | RASMUSN-ER4 | 230 | 6.7272 | 6.6736 | 0.0536
GEN-2015-089_GEN-2018-070 | 01 NORTH | 762237 | G17-175TAP | 230 | 7.2707 | 7.1128 | 0.1579
GEN-2015-089_GEN-2018-070 | 01 NORTH | 640540 | MEADOWGROVE4 | 230 | 5.0998 | 5.0979 | 0.0019
GEN-2015-089_GEN-2018-070 | 01 NORTH | 652398 | VFODNES4 | 230 | 7.3557 | 7.2819 | 0.0738
GEN-2015-089_GEN-2018-070 | 01 NORTH | 652507 | FTTHOMP4 | 230 | 19.8146 | 19.7901 | 0.0245
GEN-2015-089_GEN-2018-070 | 01 NORTH | 652510 | FTRANDL7 | 115 | 12.7749 | 12.7486 | 0.0263
GEN-2015-089_GEN-2018-070 | 01 NORTH | 652565 | SIOUXCY4 | 230 | 20.341 | 20.2869 | 0.0541
GEN-2015-089_GEN-2018-070 | 01 NORTH | 654455 | PRVLNG23 | 115 | 6.3384 | 5.541 | 0.7974
GEN-2015-089_GEN-2018-070 | 01 NORTH | 655418 | FREEMAN-ER7 | 115 | 2.5595 | 2.5509 | 0.0086
GEN-2015-089_GEN-2018-070 | 01 NORTH | 655475 | LAKPLAT-ER4 | 230 | 5.5515 | 5.5452 | 0.0063
GEN-2015-089_GEN-2018-070 | 01 NORTH | 655485 | RASMUSN-ER8 | 69 | 3.1695 | 3.1658 | 0.0037
GEN-2015-089_GEN-2018-070 | 01 NORTH | 660007 | MENNO JCT 7 | 115 | 6.4875 | 6.438 | 0.0495
GEN-2015-089_GEN-2018-070 | 01 NORTH | 660026 | NAPA JCT 7 | 115 | 7.6491 | 7.6138 | 0.0353
GEN-2015-089_GEN-2018-070 | 01 NORTH | 762238 | GEN-2017-175 | 230 | 7.041 | 6.894 | 0.147
GEN-2015-089_GEN-2018-070 | 01 NORTH | 587764 | G16-094-TAP | 230 | 8.8873 | 8.8836 | 0.0037
GEN-2015-089_GEN-2018-070 | 01 NORTH | 589324 | G17-094-TAP | 230 | 7.6985 | 7.6965 | 0.002
GEN-2015-089_GEN-2018-070 | 01 NORTH | 640133 | COLMBUS4 | 230 | 11.4877 | 11.4859 | 0.0018
GEN-2015-089_GEN-2018-070 | 01 NORTH | 640349 | SPENCER7 | 115 | 4.7744 | 4.7719 | 0.0025
GEN-2015-089_GEN-2018-070 | 01 NORTH | 640386 | TWIN CH4 | 230 | 8.9225 | 8.9165 | 0.006
GEN-2015-089_GEN-2018-070 | 01 NORTH | 648506 | PR BRZ 4 | 230 | 3.5115 | 3.5108 | 0.0007
GEN-2015-089_GEN-2018-070 | 01 NORTH | 652276 | FTTHOMP8 | 69 | 3.6054 | 3.6052 | 0.0002
GEN-2015-089_GEN-2018-070 | 01 NORTH | 652475 | BONESTL7 | 115 | 3.5176 | 3.5161 | 0.0015
GEN-2015-089_GEN-2018-070 | 01 NORTH | 652501 | ARMOUR 7 | 115 | 4.124 | 4.1221 | 0.0019
GEN-2015-089_GEN-2018-070 | 01 NORTH | 652506 | FTTHOMP3 | 345 | 10.4278 | 10.4198 | 0.008
GEN-2015-089_GEN-2018-070 | 01 NORTH | 652514 | HURON 4 | 230 | 11.0547 | 11.0517 | 0.003
GEN-2015-089_GEN-2018-070 | 01 NORTH | 652519 | OAHE 4 | 230 | 11.9528 | 11.9485 | 0.0043
GEN-2015-089_GEN-2018-070 | 01 NORTH | 652523 | SIOUXFL4 | 230 | 13.6104 | 13.5561 | 0.0543
GEN-2015-089_GEN-2018-070 | 01 NORTH | 652540 | BIGBND14 | 230 | 11.7244 | 11.7169 | 0.0075
GEN-2015-089_GEN-2018-070 | 01 NORTH | 652541 | BIGBND24 | 230 | 11.6429 | 11.6355 | 0.0074
GEN-2015-089_GEN-2018-070 | 01 NORTH | 652552 | SIOUXCY2 | 230 | 20.341 | 20.2869 | 0.0541
GEN-2015-089_GEN-2018-070 | 01 NORTH | 652566 | SIOUXCY5 | 161 | 20.956 | 20.9328 | 0.0232
GEN-2015-089_GEN-2018-070 | 01 NORTH | 652567 | DENISON4 | 230 | 5.1544 | 5.1535 | 0.0009
GEN-2015-089_GEN-2018-070 | 01 NORTH | 652606 | LETCHER4 | 230 | 4.7237 | 4.7195 | 0.0042
GEN-2015-089_GEN-2018-070 | 01 NORTH | 652607 | WESSINGTON 4 | 230 | 5.7229 | 5.7199 | 0.003
GEN-2015-089_GEN-2018-070 | 01 NORTH | 654454 | PRVLNG13 | 115 | 3.263 | 2.2519 | 1.0111
GEN-2015-089_GEN-2018-070 | 01 NORTH | 655145 | SW870-ER8 | 69 | 2.758 | 2.7553 | 0.0027
GEN-2015-089_GEN-2018-070 | 01 NORTH | 655146 | SW873-ER8 | 69 | 2.7568 | 2.754 | 0.0028
GEN-2015-089_GEN-2018-070 | 01 NORTH | 655147 | MOS-JEFF-ER8 | 69 | 2.4256 | 2.4235 | 0.0021
GEN-2015-089_GEN-2018-070 | 01 NORTH | 655468 | VFODNES-ER7 | 115 | 5.0474 | 5.0298 | 0.0176
GEN-2015-089_GEN-2018-070 | 01 NORTH | 655469 | VFODNES-ER8 | 69 | 4.2362 | 4.2287 | 0.0075
GEN-2015-089_GEN-2018-070 | 01 NORTH | 655476 | LAKPLAT-ER8 | 69 | 4.0077 | 4.0067 | 0.001
GEN-2015-089_GEN-2018-070 | 01 NORTH | 655490 | WHTSWAN-ER7 | 115 | 12.4458 | 12.4207 | 0.0251
GEN-2015-089_GEN-2018-070 | 01 NORTH | 660005 | TRIPP JCT 7 | 115 | 3.9571 | 3.9475 | 0.0096
GEN-2015-089_GEN-2018-070 | 01 NORTH | 660006 | YANKTON JCT7 | 115 | 7.9557 | 7.9246 | 0.0311
GEN-2015-089_GEN-2018-070 | 01 NORTH | 660036 | YANKTONEAST7 | 115 | 3.9429 | 3.9335 | 0.0094
GEN-2015-089_GEN-2018-070 | 01 NORTH | 587760 | GEN-2016-094 | 230 | 8.7366 | 8.733 | 0.0036
GEN-2015-089_GEN-2018-070 | 01 NORTH | 589320 | GEN-2017-094 | 230 | 6.1877 | 6.1865 | 0.0012
GEN-2015-089_GEN-2018-070 | 01 NORTH | 602004 | SPLT RK4 | 230 | 13.1508 | 13.1022 | 0.0486
GEN-2015-089_GEN-2018-070 | 01 NORTH | 635223 | PLYMOTH5 | 161 | 20.4785 | 20.4582 | 0.0203
GEN-2015-089_GEN-2018-070 | 01 NORTH | 640126 | E.COL. 4 | 230 | 10.0667 | 10.0654 | 0.0013
GEN-2015-089_GEN-2018-070 | 01 NORTH | 640131 | COLMB.W4 | 230 | 9.8308 | 9.8296 | 0.0012
GEN-2015-089_GEN-2018-070 | 01 NORTH | 640134 | KELLY 7 | 115 | 17.6974 | 17.696 | 0.0014
GEN-2015-089_GEN-2018-070 | 01 NORTH | 640305 | ONEILL 7 | 115 | 3.9336 | 3.9328 | 0.0008
GEN-2015-089_GEN-2018-070 | 01 NORTH | 640343 | SHELCRK4 | 230 | 10.8729 | 10.8715 | 0.0014
GEN-2015-089_GEN-2018-070 | 01 NORTH | 640387 | TWIN CH7 | 115 | 10.7822 | 10.7777 | 0.0045
GEN-2015-089_GEN-2018-070 | 01 NORTH | 640560 | WAKEFIELD 4 | 230 | 7.9675 | 7.9649 | 0.0026
GEN-2015-089_GEN-2018-070 | 01 NORTH | 652249 | ARMOUR 8 | 69 | 2.4299 | 2.4295 | 0.0004
GEN-2015-089_GEN-2018-070 | 01 NORTH | 652478 | GREGORY7 | 115 | 2.1571 | 2.1567 | 0.0004
GEN-2015-089_GEN-2018-070 | 01 NORTH | 652511 | GAVINS 7 | 115 | 8.4307 | 8.4097 | 0.021
GEN-2015-089_GEN-2018-070 | 01 NORTH | 652513 | HANLON 4 | 230 | 5.5672 | 5.5602 | 0.007
GEN-2015-089_GEN-2018-070 | 01 NORTH | 652515 | HURON 7 | 115 | 15.0903 | 15.087 | 0.0033
GEN-2015-089_GEN-2018-070 | 01 NORTH | 652518 | MTVERN 7 | 115 | 4.2008 | 4.1996 | 0.0012
GEN-2015-089_GEN-2018-070 | 01 NORTH | 652520 | OAHE 7 | 115 | 10.0527 | 10.0516 | 0.0011
GEN-2015-089_GEN-2018-070 | 01 NORTH | 652524 | SIOUXFL7 | 115 | 26.9963 | 26.9467 | 0.0496
GEN-2015-089_GEN-2018-070 | 01 NORTH | 652525 | TYNDALL7 | 115 | 3.7466 | 3.7419 | 0.0047
GEN-2015-089_GEN-2018-070 | 01 NORTH | 652530 | WATERTN4 | 230 | 14.4494 | 14.4481 | 0.0013
GEN-2015-089_GEN-2018-070 | 01 NORTH | 652561 | DENISON5 | 161 | 6.1701 | 6.1693 | 0.0008
GEN-2015-089_GEN-2018-070 | 01 NORTH | 652563 | SPENCER5 | 161 | 10.0544 | 10.0539 | 0.0005
GEN-2015-089_GEN-2018-070 | 01 NORTH | 652564 | SIOUXCY3 | 345 | 15.3816 | 15.3616 | 0.02
GEN-2015-089_GEN-2018-070 | 01 NORTH | 652574 | SIOUXCY8 | 69 | 18.4952 | 18.489 | 0.0062
GEN-2015-089_GEN-2018-070 | 01 NORTH | 652583 | DENISON8 | 69 | 11.9688 | 11.9676 | 0.0012
GEN-2015-089_GEN-2018-070 | 01 NORTH | 652609 | LETCHER7 | 115 | 6.0091 | 6.0051 | 0.004
GEN-2015-089_GEN-2018-070 | 01 NORTH | 652614 | CARPENTER 4 | 230 | 6.9031 | 6.9022 | 0.0009
GEN-2015-089_GEN-2018-070 | 01 NORTH | 652806 | FTTHOM1-LNX3 | 345 | 10.3307 | 10.3229 | 0.0078
GEN-2015-089_GEN-2018-070 | 01 NORTH | 652807 | FTTHOM2-LNX3 | 345 | 10.4278 | 10.4198 | 0.008
GEN-2015-089_GEN-2018-070 | 01 NORTH | 655126 | MOS-VERM-ER8 | 69 | 1.9286 | 1.9273 | 0.0013
GEN-2015-089_GEN-2018-070 | 01 NORTH | 655130 | SW808-ER8 | 69 | 2.4249 | 2.4229 | 0.002
GEN-2015-089_GEN-2018-070 | 01 NORTH | 655136 | SW832-ER8 | 69 | 2.5038 | 2.5015 | 0.0023
GEN-2015-089_GEN-2018-070 | 01 NORTH | 655137 | SW833-ER8 | 69 | 1.9982 | 1.9968 | 0.0014
GEN-2015-089_GEN-2018-070 | 01 NORTH | 655143 | MOS-PARK-ER8 | 69 | 1.6133 | 1.6131 | 0.0002
GEN-2015-089_GEN-2018-070 | 01 NORTH | 655153 | MOS-AMES-ER8 | 69 | 3.5356 | 3.5354 | 0.0002
GEN-2015-089_GEN-2018-070 | 01 NORTH | 655250 | CHMBRLAN-ER8 | 69 | 1.5802 | 1.58 | 0.0002
GEN-2015-089_GEN-2018-070 | 01 NORTH | 655322 | TEA-ER8 | 69 | 1.3411 | 1.341 | 0.0001
GEN-2015-089_GEN-2018-070 | 01 NORTH | 655385 | MOS-LKPL-ER8 | 69 | 3.9932 | 3.9922 | 0.001
GEN-2015-089_GEN-2018-070 | 01 NORTH | 655408 | SXFCHCLR-ER7 | 115 | 3.3252 | 3.3176 | 0.0076
GEN-2015-089_GEN-2018-070 | 01 NORTH | 655441 | BUCKSNRT-ER7 | 115 | 3.8331 | 3.823 | 0.0101
GEN-2015-089_GEN-2018-070 | 01 NORTH | 655446 | SW1109-ER7 | 115 | 3.7016 | 3.6922 | 0.0094
GEN-2015-089_GEN-2018-070 | 01 NORTH | 655487 | SULLYBT-ER4 | 230 | 5.8952 | 5.8944 | 0.0008
GEN-2015-089_GEN-2018-070 | 01 NORTH | 655518 | DAYTON__-ER7 | 115 | 3.4976 | 3.4893 | 0.0083
GEN-2015-089_GEN-2018-070 | 01 NORTH | 659122 | STORLA__-BE4 | 230 | 5.3706 | 5.3676 | 0.003
GEN-2015-089_GEN-2018-070 | 01 NORTH | 659188 | PHILIP_T-BE4 | 230 | 4.311 | 4.3108 | 0.0002
GEN-2015-089_GEN-2018-070 | 01 NORTH | 659205 | BROADLND-BE4 | 230 | 10.0163 | 10.0139 | 0.0024
GEN-2015-089_GEN-2018-070 | 01 NORTH | 659295 | SD.PW1__-BE4 | 230 | 4.4278 | 4.4262 | 0.0016
GEN-2015-089_GEN-2018-070 | 01 NORTH | 659311 | PAHOJA__-BE4 | 230 | 7.4254 | 7.4127 | 0.0127
GEN-2015-089_GEN-2018-070 | 01 NORTH | 659900 | EAGLE___-NI4 | 230 | 7.3012 | 7.2922 | 0.009
GEN-2015-089_GEN-2018-070 | 01 NORTH | 660004 | MITCHELL 7 | 115 | 5.787 | 5.7825 | 0.0045
GEN-2015-089_GEN-2018-070 | 01 NORTH | 660018 | SCHROEDER 7 | 115 | 3.2671 | 3.2609 | 0.0062
GEN-2015-089_GEN-2018-070 | 01 NORTH | 760515 | GEN-2017-222 | 230 | 3.8535 | 3.8531 | 0.0004
GEN-2015-089_GEN-2018-070 | 01 NORTH | 588590 | GEN-2017-014 | 230 | 4.311 | 4.3108 | 0.0002
GEN-2015-089_GEN-2018-070 | 01 NORTH | 603009 | GRANT 7 | 115 | 4.4844 | 4.4832 | 0.0012
GEN-2015-089_GEN-2018-070 | 01 NORTH | 603012 | LAWRENC7 | 115 | 30.6656 | 30.6139 | 0.0517
GEN-2015-089_GEN-2018-070 | 01 NORTH | 603016 | SPLT RK7 | 115 | 39.3911 | 39.3248 | 0.0663
GEN-2015-089_GEN-2018-070 | 01 NORTH | 635200 | RAUN 3 | 345 | 27.0138 | 26.9973 | 0.0165
GEN-2015-089_GEN-2018-070 | 01 NORTH | 635224 | PLYMOTH8 | 69 | 21.403 | 21.3947 | 0.0083
GEN-2015-089_GEN-2018-070 | 01 NORTH | 635225 | MORNSD 5 | 161 | 10.845 | 10.841 | 0.004
GEN-2015-089_GEN-2018-070 | 01 NORTH | 635226 | LEEDS 5 | 161 | 15.8452 | 15.8367 | 0.0085
GEN-2015-089_GEN-2018-070 | 01 NORTH | 635260 | LEMARST5 | 161 | 9.7975 | 9.7937 | 0.0038
GEN-2015-089_GEN-2018-070 | 01 NORTH | 640080 | BELDEN 7 | 115 | 5.9733 | 5.9705 | 0.0028
GEN-2015-089_GEN-2018-070 | 01 NORTH | 640084 | BLMFLD 7 | 115 | 5.1275 | 5.1236 | 0.0039
GEN-2015-089_GEN-2018-070 | 01 NORTH | 640113 | CLRWATR7 | 115 | 5.1516 | 5.151 | 0.0006
GEN-2015-089_GEN-2018-070 | 01 NORTH | 640127 | COLMB.E7 | 115 | 22.1185 | 22.1164 | 0.0021
GEN-2015-089_GEN-2018-070 | 01 NORTH | 640136 | COLMBUS7 | 115 | 19.1401 | 19.1384 | 0.0017
GEN-2015-089_GEN-2018-070 | 01 NORTH | 640163 | EMERSON7 | 115 | 5.4485 | 5.4477 | 0.0008
GEN-2015-089_GEN-2018-070 | 01 NORTH | 640200 | GR ISLD4 | 230 | 16.413 | 16.4126 | 0.0004
GEN-2015-089_GEN-2018-070 | 01 NORTH | 640212 | HARTGTN7 | 115 | 5.1832 | 5.1793 | 0.0039
GEN-2015-089_GEN-2018-070 | 01 NORTH | 640227 | HOSKINS4 | 230 | 10.0896 | 10.0873 | 0.0023
GEN-2015-089_GEN-2018-070 | 01 NORTH | 640306 | ONEILL 8 | 69 | 4.2323 | 4.2318 | 0.0005
GEN-2015-089_GEN-2018-070 | 01 NORTH | 640342 | SHELCRK3 | 345 | 10.533 | 10.5314 | 0.0016
GEN-2015-089_GEN-2018-070 | 01 NORTH | 640388 | TWIN CH8 | 69 | 7.7842 | 7.7828 | 0.0014
GEN-2015-089_GEN-2018-070 | 01 NORTH | 640424 | S.SIOUXCITY7 | 115 | 7.3706 | 7.3685 | 0.0021
GEN-2015-089_GEN-2018-070 | 01 NORTH | 640465 | EAGLECREEK 7 | 115 | 3.0176 | 3.0172 | 0.0004
GEN-2015-089_GEN-2018-070 | 01 NORTH | 640561 | RTLSNAKE.W 4 | 230 | 7.1132 | 7.1114 | 0.0018
GEN-2015-089_GEN-2018-070 | 01 NORTH | 652235 | SIOUXFL8 | 69 | 3.8995 | 3.8988 | 0.0007
GEN-2015-089_GEN-2018-070 | 01 NORTH | 652251 | MTVERNS8 | 69 | 2.2374 | 2.2372 | 0.0002
GEN-2015-089_GEN-2018-070 | 01 NORTH | 652284 | HURON 8 | 69 | 4.1917 | 4.1916 | 0.0001
GEN-2015-089_GEN-2018-070 | 01 NORTH | 652286 | TYNDALL8 | 69 | 2.4871 | 2.4858 | 0.0013
GEN-2015-089_GEN-2018-070 | 01 NORTH | 652476 | EAGLEBT7 | 115 | 1.8836 | 1.8836 | 0
GEN-2015-089_GEN-2018-070 | 01 NORTH | 652484 | NUNDRWD4 | 230 | 3.5581 | 3.558 | 0.0001
GEN-2015-089_GEN-2018-070 | 01 NORTH | 652494 | WINNER 7 | 115 | 1.882 | 1.8818 | 0.0002
GEN-2015-089_GEN-2018-070 | 01 NORTH | 652502 | BERSFRD7 | 115 | 3.8486 | 3.8476 | 0.001
GEN-2015-089_GEN-2018-070 | 01 NORTH | 652505 | FLANDRU7 | 115 | 4.2781 | 4.2776 | 0.0005
GEN-2015-089_GEN-2018-070 | 01 NORTH | 652528 | WOONSKT7 | 115 | 5.1717 | 5.1707 | 0.001
GEN-2015-089_GEN-2018-070 | 01 NORTH | 652529 | WATERTN3 | 345 | 10.2735 | 10.2726 | 0.0009
GEN-2015-089_GEN-2018-070 | 01 NORTH | 652531 | WATERTN7 | 115 | 13.6622 | 13.6617 | 0.0005
GEN-2015-089_GEN-2018-070 | 01 NORTH | 652581 | SPENCER8 | 69 | 15.0604 | 15.06 | 0.0004
GEN-2015-089_GEN-2018-070 | 01 NORTH | 652582 | APPLEDORN 4 | 230 | 7.0997 | 7.0996 | 0.0001
GEN-2015-089_GEN-2018-070 | 01 NORTH | 652600 | ASH TAP | 115 | 7.7953 | 7.7946 | 0.0007
GEN-2015-089_GEN-2018-070 | 01 NORTH | 652603 | EXIRA 5 | 161 | 7.0877 | 7.0876 | 0.0001
GEN-2015-089_GEN-2018-070 | 01 NORTH | 652630 | WATERTNCAP 4 | 230 | 14.2782 | 14.277 | 0.0012
GEN-2015-089_GEN-2018-070 | 01 NORTH | 652833 | GRPRAR2-LNX3 | 345 | 7.4489 | 7.4483 | 0.0006
GEN-2015-089_GEN-2018-070 | 01 NORTH | 652864 | SIOUXCY-LNX3 | 345 | 15.1969 | 15.1774 | 0.0195
GEN-2015-089_GEN-2018-070 | 01 NORTH | 655079 | MOS-KLKP-ER8 | 69 | 0.7678 | 0.7677 | 0.0001
GEN-2015-089_GEN-2018-070 | 01 NORTH | 655080 | MOS-HLTP-ER8 | 69 | 1.3053 | 1.3052 | 0.0001
GEN-2015-089_GEN-2018-070 | 01 NORTH | 655091 | MOS-AMR1-ER8 | 69 | 2.1516 | 2.1513 | 0.0003
GEN-2015-089_GEN-2018-070 | 01 NORTH | 655105 | MOS-HRLM-ER8 | 69 | 1.0208 | 1.0207 | 0.0001
GEN-2015-089_GEN-2018-070 | 01 NORTH | 655133 | SW822-ER8 | 69 | 2.0949 | 2.0934 | 0.0015
GEN-2015-089_GEN-2018-070 | 01 NORTH | 655142 | MOS-CNTN-ER8 | 69 | 1.7341 | 1.734 | 0.0001
GEN-2015-089_GEN-2018-070 | 01 NORTH | 655158 | MOS-HYDE-ER8 | 69 | 2.1093 | 2.1093 | 0
GEN-2015-089_GEN-2018-070 | 01 NORTH | 655169 | MOS-PRRI-ER8 | 69 | 2.1789 | 2.1787 | 0.0002
GEN-2015-089_GEN-2018-070 | 01 NORTH | 655192 | PARKER-ER8 | 69 | 1.6443 | 1.6441 | 0.0002
GEN-2015-089_GEN-2018-070 | 01 NORTH | 655313 | RICHLAND-ER8 | 69 | 2.417 | 2.4149 | 0.0021
GEN-2015-089_GEN-2018-070 | 01 NORTH | 655314 | ELKPNTCY-ER8 | 69 | 1.8492 | 1.8481 | 0.0011
GEN-2015-089_GEN-2018-070 | 01 NORTH | 655316 | BURBANK-ER8 | 69 | 1.7938 | 1.7927 | 0.0011
GEN-2015-089_GEN-2018-070 | 01 NORTH | 655328 | BIGBEND-ER8 | 69 | 2.7715 | 2.7714 | 0.0001
GEN-2015-089_GEN-2018-070 | 01 NORTH | 655352 | AMES-ER8 | 69 | 1.2591 | 1.2591 | 0
GEN-2015-089_GEN-2018-070 | 01 NORTH | 655359 | JEFERSON-ER8 | 69 | 1.6099 | 1.609 | 0.0009
GEN-2015-089_GEN-2018-070 | 01 NORTH | 655376 | MOS-AMR2-ER8 | 69 | 2.2305 | 2.2302 | 0.0003
GEN-2015-089_GEN-2018-070 | 01 NORTH | 655377 | SW1145-ER7 | 115 | 25.6249 | 25.5803 | 0.0446
GEN-2015-089_GEN-2018-070 | 01 NORTH | 655386 | MOS-RVR1-ER8 | 69 | 2.0839 | 2.0837 | 0.0002
GEN-2015-089_GEN-2018-070 | 01 NORTH | 655404 | HRRISBRG-ER7 | 115 | 3.2445 | 3.2374 | 0.0071
GEN-2015-089_GEN-2018-070 | 01 NORTH | 655417 | ROSWELL-ER7 | 115 | 2.5983 | 2.5976 | 0.0007
GEN-2015-089_GEN-2018-070 | 01 NORTH | 655444 | DELAPRE-ER7 | 115 | 3.5343 | 3.5257 | 0.0086
GEN-2015-089_GEN-2018-070 | 01 NORTH | 655445 | SUNDOWN-ER7 | 115 | 3.6445 | 3.6354 | 0.0091
GEN-2015-089_GEN-2018-070 | 01 NORTH | 655447 | WALLLK-ER7 | 115 | 1.8834 | 1.883 | 0.0004
GEN-2015-089_GEN-2018-070 | 01 NORTH | 655448 | WILOWCRK-ER7 | 115 | 3.3551 | 3.3474 | 0.0077
GEN-2015-089_GEN-2018-070 | 01 NORTH | 655465 | BLAIR-ER4 | 230 | 9.8277 | 9.8274 | 0.0003
GEN-2015-089_GEN-2018-070 | 01 NORTH | 655481 | REDFELD-ER7 | 115 | 4.0937 | 4.0936 | 0.0001
GEN-2015-089_GEN-2018-070 | 01 NORTH | 655488 | SULLYBT-ER8 | 69 | 2.3518 | 2.3517 | 0.0001
GEN-2015-089_GEN-2018-070 | 01 NORTH | 655493 | HANLON-ER7 | 115 | 3.8464 | 3.8447 | 0.0017
GEN-2015-089_GEN-2018-070 | 01 NORTH | 655494 | HANLON1-ER8 | 69 | 5.1403 | 5.1385 | 0.0018
GEN-2015-089_GEN-2018-070 | 01 NORTH | 655495 | HANLON2-ER8 | 69 | 5.1403 | 5.1385 | 0.0018
GEN-2015-089_GEN-2018-070 | 01 NORTH | 655499 | CARPENTR-ER8 | 69 | 3.1739 | 3.1739 | 0
GEN-2015-089_GEN-2018-070 | 01 NORTH | 655510 | SB.LS-WK-ER4 | 230 | 5.8952 | 5.8944 | 0.0008
GEN-2015-089_GEN-2018-070 | 01 NORTH | 656267 | MANNINGTAP 8 | 69 | 4.4766 | 4.4765 | 0.0001
GEN-2015-089_GEN-2018-070 | 01 NORTH | 656570 | WISDOM5 | 161 | 10.2621 | 10.2616 | 0.0005
GEN-2015-089_GEN-2018-070 | 01 NORTH | 658030 | DENISONWEST8 | 69 | 6.6947 | 6.6943 | 0.0004
GEN-2015-089_GEN-2018-070 | 01 NORTH | 658031 | DENSOUMAIN8 | 69 | 6.86 | 6.8596 | 0.0004
GEN-2015-089_GEN-2018-070 | 01 NORTH | 658174 | IRVSIMM7 | 115 | 7.3976 | 7.397 | 0.0006
GEN-2015-089_GEN-2018-070 | 01 NORTH | 659120 | BROADLND-BE3 | 345 | 4.5977 | 4.5971 | 0.0006
GEN-2015-089_GEN-2018-070 | 01 NORTH | 659121 | SPIRIT_M-BE7 | 115 | 5.9966 | 5.9941 | 0.0025
GEN-2015-089_GEN-2018-070 | 01 NORTH | 659123 | STORLA__-BE7 | 115 | 6.3723 | 6.3703 | 0.002
GEN-2015-089_GEN-2018-070 | 01 NORTH | 659130 | CHAPELLE-BE3 | 345 | 6.7447 | 6.742 | 0.0027
GEN-2015-089_GEN-2018-070 | 01 NORTH | 659192 | PHILIP__-BE4 | 230 | 3.4792 | 3.4791 | 0.0001
GEN-2015-089_GEN-2018-070 | 01 NORTH | 659716 | MAPLETAP-LO7 | 115 | 12.7753 | 12.7646 | 0.0107
GEN-2015-089_GEN-2018-070 | 01 NORTH | 659735 | CLEVELND-LO4 | 230 | 4.9229 | 4.9173 | 0.0056
GEN-2015-089_GEN-2018-070 | 01 NORTH | 659901 | EAGLE___-NI8 | 69 | 14.0991 | 14.0906 | 0.0085
GEN-2015-089_GEN-2018-070 | 01 NORTH | 659912 | J6BOYER_-NI8 | 69 | 9.7909 | 9.7902 | 0.0007
GEN-2015-089_GEN-2018-070 | 01 NORTH | 659946 | K216LIBE-NI8 | 69 | 7.566 | 7.5648 | 0.0012
GEN-2015-089_GEN-2018-070 | 01 NORTH | 659953 | K412HTNM-NI8 | 69 | 11.9214 | 11.919 | 0.0024
GEN-2015-089_GEN-2018-070 | 01 NORTH | 659971 | K301HINT-NI8 | 69 | 10.2335 | 10.2317 | 0.0018
GEN-2015-089_GEN-2018-070 | 01 NORTH | 659980 | K135CONC-NI8 | 69 | 6.665 | 6.6643 | 0.0007
GEN-2015-089_GEN-2018-070 | 01 NORTH | 660003 | HURON WPARK7 | 115 | 9.4672 | 9.4656 | 0.0016
GEN-2015-089_GEN-2018-070 | 01 NORTH | 660008 | MITCHELL NW7 | 115 | 5.3924 | 5.3887 | 0.0037
GEN-2015-089_GEN-2018-070 | 01 NORTH | 660009 | HURON BTAP 7 | 115 | 14.6404 | 14.6373 | 0.0031
GEN-2015-089_GEN-2018-070 | 01 NORTH | 660252 | MT VERNON 8 | 69 | 2.8114 | 2.8111 | 0.0003
GEN-2015-089_GEN-2018-070 | 01 NORTH | 763098 | GEN-2018-074 | 230 | 3.6096 | 3.6091 | 0.0005
GEN-2018-067 | 01 NORTH | 655941 | STRNDAHL-MW7 | 115 | 7.071 | 5.5809 | 1.4901
GEN-2018-067 | 01 NORTH | 655915 | BARRBUTE-MW7 | 115 | 4.7637 | 4.2509 | 0.5128
GEN-2018-067 | 01 NORTH | 655940 | MONT -MW7 | 115 | 14.8393 | 13.7847 | 1.0546
GEN-2018-067 | 01 NORTH | 763021 | GEN-2018-067 | 115 | 7.071 | 5.5809 | 1.4901
GEN-2018-067 | 01 NORTH | 652391 | WILLISTON27 | 115 | 18.5279 | 17.9187 | 0.6092
GEN-2018-067 | 01 NORTH | 655924 | STATELIN-MW7 | 115 | 15.094 | 14.5465 | 0.5475
GEN-2018-067 | 01 NORTH | 655933 | N.MISRDG-MW7 | 115 | 14.3984 | 13.948 | 0.4504
GEN-2018-067 | 01 NORTH | 659145 | GRENORA_-UM7 | 115 | 4.6537 | 4.1916 | 0.4621
GEN-2018-067 | 01 NORTH | 652400 | WILISTN4 | 230 | 11.1567 | 10.9844 | 0.1723
GEN-2018-067 | 01 NORTH | 652421 | WILISTN7 | 115 | 18.5165 | 17.9095 | 0.607
GEN-2018-067 | 01 NORTH | 655776 | ALKABO -SH7 | 115 | 2.213 | 2.1029 | 0.1101
GEN-2018-067 | 01 NORTH | 655778 | SNAKEBTT-SH7 | 115 | 7.6372 | 7.3817 | 0.2555
GEN-2018-067 | 01 NORTH | 655925 | JUDSON -MW7 | 115 | 14.5441 | 14.1503 | 0.3938
GEN-2018-067 | 01 NORTH | 655934 | N.WLST_T-MW7 | 115 | 13.1858 | 12.8658 | 0.32
GEN-2018-067 | 01 NORTH | 655935 | NW.WLSTN-MW7 | 115 | 11.7789 | 11.5248 | 0.2541
GEN-2018-067 | 01 NORTH | 655957 | EASTFORK-MW7 | 115 | 15.8907 | 15.5532 | 0.3375
GEN-2018-067 | 01 NORTH | 659347 | PIONEER1-BE7 | 115 | 15.094 | 14.5465 | 0.5475
GEN-2018-067 | 01 NORTH | 659430 | PIONEER2-BE7 | 115 | 14.4519 | 13.9513 | 0.5006
GEN-2018-067 | 01 NORTH | 661077 | PLNTYWD7 | 115 | 1.6921 | 1.6267 | 0.0654
GEN-2018-067 | 01 NORTH | 661089 | LTLMUDY7 | 115 | 6.7679 | 6.7076 | 0.0603
GEN-2018-067 | 01 NORTH | 652216 | WATFORD4 | 230 | 6.5544 | 6.5311 | 0.0233
GEN-2018-067 | 01 NORTH | 652651 | FAIRVIEW 7 | 115 | 4.826 | 4.8125 | 0.0135
GEN-2018-067 | 01 NORTH | 655777 | FORTUNA -SH7 | 115 | 1.7511 | 1.6814 | 0.0697
GEN-2018-067 | 01 NORTH | 655779 | REDBANK -SH7 | 115 | 4.5295 | 4.4384 | 0.0911
GEN-2018-067 | 01 NORTH | 655793 | MARLEY -LY7 | 115 | 6.4767 | 6.4009 | 0.0758
GEN-2018-067 | 01 NORTH | 655926 | SW.WLSTN-MW7 | 115 | 8.2618 | 8.1334 | 0.1284
GEN-2018-067 | 01 NORTH | 655936 | N.WILSTN-MW7 | 115 | 12.8828 | 12.5823 | 0.3005
GEN-2018-067 | 01 NORTH | 655956 | TYRONE -MW7 | 115 | 9.946 | 9.8204 | 0.1256
GEN-2018-067 | 01 NORTH | 655958 | FOLVAG -MW7 | 115 | 12.9354 | 12.6997 | 0.2357
GEN-2018-067 | 01 NORTH | 659262 | CULBSN.E-BE7 | 115 | 7.8791 | 7.7607 | 0.1184
GEN-2018-067 | 01 NORTH | 659334 | JUDSON__-BE4 | 230 | 11.0806 | 10.9202 | 0.1604
GEN-2018-067 | 01 NORTH | 659362 | WHEELOCK-BE4 | 230 | 7.5903 | 7.5359 | 0.0544
GEN-2018-067 | 01 NORTH | 659600 | EFORK_-BE334 | 345 | 7.6977 | 7.5919 | 0.1058
GEN-2018-067 | 01 NORTH | 661087 | RAY JCT7 | 115 | 5.6142 | 5.5933 | 0.0209
GEN-2018-067 | 01 NORTH | 652408 | WATFORD7 | 115 | 8.2975 | 8.2833 | 0.0142
GEN-2018-067 | 01 NORTH | 655784 | AMBROSE -BD7 | 115 | 1.1912 | 1.1909 | 0.0003
GEN-2018-067 | 01 NORTH | 655791 | SPRINGLK-LY7 | 115 | 1.8952 | 1.8931 | 0.0021
GEN-2018-067 | 01 NORTH | 655792 | NOHLEY -LY7 | 115 | 3.4151 | 3.4083 | 0.0068
GEN-2018-067 | 01 NORTH | 655794 | SANDRSON-LY7 | 115 | 3.3403 | 3.32 | 0.0203
GEN-2018-067 | 01 NORTH | 655931 | BLKTLTAP-MW7 | 115 | 7.4933 | 7.4264 | 0.0669
GEN-2018-067 | 01 NORTH | 655937 | NE.WLSTN-MW7 | 115 | 11.9889 | 11.755 | 0.2339
GEN-2018-067 | 01 NORTH | 659112 | CULBRTSN-UM7 | 115 | 5.3339 | 5.2854 | 0.0485
GEN-2018-067 | 01 NORTH | 659151 | RICHLAND-BE7 | 115 | 5.5253 | 5.5164 | 0.0089
GEN-2018-067 | 01 NORTH | 659269 | CULB_GEN-BE7 | 115 | 7.1776 | 7.0952 | 0.0824
GEN-2018-067 | 01 NORTH | 659302 | CHARL_CK-BE4 | 230 | 11.3272 | 11.2941 | 0.0331
GEN-2018-067 | 01 NORTH | 659333 | JUDSON__-BE3 | 345 | 8.3923 | 8.2852 | 0.1071
GEN-2018-067 | 01 NORTH | 659363 | WHEELOCK-BE7 | 115 | 8.8864 | 8.8296 | 0.0568
GEN-2018-067 | 01 NORTH | 659427 | TN.LS-JD-BE3 | 345 | 8.6936 | 8.6367 | 0.0569
GEN-2018-067 | 01 NORTH | 661003 | WATFRDSOUTH4 | 230 | 6.4853 | 6.4625 | 0.0228
GEN-2018-067 | 01 NORTH | 661084 | TIOGA4 4 | 230 | 12.8663 | 12.79 | 0.0763
GEN-2018-067 | 01 NORTH | 661086 | TIOGA7 7 | 115 | 9.9525 | 9.9171 | 0.0354
GEN-2018-069 | 01 NORTH | 652616 | MINGUSVILLE4 | 230 | 4.3407 | 3.9852 | 0.3555
GEN-2018-069 | 01 NORTH | 652403 | DAWSONC4 | 230 | 4.2911 | 4.1167 | 0.1744
GEN-2018-069 | 01 NORTH | 659247 | MEDORA__-UM4 | 230 | 5.2368 | 5.0893 | 0.1475
GEN-2018-069 | 01 NORTH | 659535 | BEAVRHIL-GW4 | 230 | 4.3407 | 3.9852 | 0.3555
GEN-2018-069 | 01 NORTH | 763043 | GEN-2018-069 | 230 | 4.2714 | 3.9133 | 0.3581
GEN-2018-069 | 01 NORTH | 652404 | DAWSONC7 | 115 | 7.6808 | 7.4971 | 0.1837
GEN-2018-069 | 01 NORTH | 652405 | FTPECK 4 | 230 | 2.094 | 2.0756 | 0.0184
GEN-2018-069 | 01 NORTH | 652411 | MI CTYE4 | 230 | 2.7429 | 2.703 | 0.0399
GEN-2018-069 | 01 NORTH | 652425 | BELFELD4 | 230 | 9.3261 | 9.2031 | 0.123
GEN-2018-069 | 01 NORTH | 659536 | BEAVRHIL-GW7 | 115 | 3.5043 | 3.383 | 0.1213
GEN-2018-069 | 01 NORTH | 652200 | GLENDIVE7 | 115 | 6.9146 | 6.7804 | 0.1342
GEN-2018-069 | 01 NORTH | 652212 | GLENDIVEP2T7 | 115 | 4.1788 | 4.1258 | 0.053
GEN-2018-069 | 01 NORTH | 652401 | CIRCLE 7 | 115 | 2.1157 | 2.1064 | 0.0093
GEN-2018-069 | 01 NORTH | 652406 | FTPECK 7 | 115 | 2.9033 | 2.8896 | 0.0137
GEN-2018-069 | 01 NORTH | 652412 | MI CTYE7 | 115 | 3.7233 | 3.6894 | 0.0339
GEN-2018-069 | 01 NORTH | 652424 | BELFELD3 | 345 | 6.628 | 6.5736 | 0.0544
GEN-2018-069 | 01 NORTH | 659124 | DICKINSN-BE4 | 230 | 6.9327 | 6.8878 | 0.0449
GEN-2018-069 | 01 NORTH | 659309 | S.HEART_-RR4 | 230 | 9.3261 | 9.2031 | 0.123
GEN-2018-069 | 01 NORTH | 659448 | DAGLUM__-BE4 | 230 | 6.3542 | 6.3026 | 0.0516
GEN-2018-069 | 01 NORTH | 661004 | BAKER 4 | 230 | 3.1917 | 3.1665 | 0.0252
GEN-2018-069 | 01 NORTH | 661056 | LEWIS 7 | 115 | 5.5853 | 5.5751 | 0.0102
GEN-2018-069 | 01 NORTH | 652395 | SHIRLEY TAP | 115 | 2.9196 | 2.8974 | 0.0222
GEN-2018-069 | 01 NORTH | 652407 | FALLON 7 | 115 | 3.075 | 3.0476 | 0.0274
GEN-2018-069 | 01 NORTH | 652409 | WOLFPT 7 | 115 | 2.926 | 2.9149 | 0.0111
GEN-2018-069 | 01 NORTH | 652468 | HEBRON 4 | 230 | 5.5473 | 5.5352 | 0.0121
GEN-2018-069 | 01 NORTH | 659125 | DICKINSN-BE7 | 115 | 9.0705 | 9.0367 | 0.0338
GEN-2018-069 | 01 NORTH | 659151 | RICHLAND-BE7 | 115 | 5.5253 | 5.5165 | 0.0088
GEN-2018-069 | 01 NORTH | 659183 | CHARL_CK-BE3 | 345 | 10.581 | 10.5447 | 0.0363
GEN-2018-069 | 01 NORTH | 659195 | DICKINS2-BE7 | 115 | 9.0358 | 9.0023 | 0.0335
GEN-2018-069 | 01 NORTH | 659265 | LITTL_MS-BE4 | 230 | 3.4157 | 3.3919 | 0.0238
GEN-2018-069 | 01 NORTH | 659266 | RHAME___-BE4 | 230 | 4.3675 | 4.3413 | 0.0262
GEN-2018-069 | 01 NORTH | 659306 | S.HEART_-RR7 | 115 | 2.2025 | 2.1991 | 0.0034
GEN-2018-069 | 01 NORTH | 659450 | BRADYWND 4 | 230 | 3.4656 | 3.4542 | 0.0114
GEN-2018-069 | 01 NORTH | 659542 | REDWATER-MC7 | 115 | 2.1157 | 2.1064 | 0.0093
GEN-2018-069 | 01 NORTH | 661005 | BAKER 7 | 115 | 3.3994 | 3.383 | 0.0164
GEN-2018-069 | 01 NORTH | 661032 | GLENDCT7 | 115 | 6.257 | 6.1641 | 0.0929
GEN-2018-069 | 01 NORTH | 588550 | GEN-2017-010 | 230 | 4.292 | 4.2668 | 0.0252
GEN-2018-069 | 01 NORTH | 652213 | FALLON 8 | 69 | 1.0345 | 1.0327 | 0.0018
GEN-2018-069 | 01 NORTH | 652394 | TERRY TAP | 115 | 2.785 | 2.7634 | 0.0216
GEN-2018-069 | 01 NORTH | 652651 | FAIRVIEW 7 | 115 | 4.826 | 4.8215 | 0.0045
GEN-2018-069 | 01 NORTH | 655790 | HELMUT -LY7 | 115 | 5.4862 | 5.4775 | 0.0087
GEN-2018-069 | 01 NORTH | 659101 | ANTELOPE-BE3 | 345 | 19.5131 | 19.4984 | 0.0147
GEN-2018-069 | 01 NORTH | 659182 | CHARL_CK-BE7 | 115 | 13.6018 | 13.582 | 0.0198
GEN-2018-069 | 01 NORTH | 659186 | E.SIDNEY-LY7 | 115 | 4.0995 | 4.0951 | 0.0044
GEN-2018-069 | 01 NORTH | 659259 | HEADRESS-CM7 | 115 | 2.9204 | 2.9093 | 0.0111
GEN-2018-069 | 01 NORTH | 659263 | LITTL_MS-BE7 | 115 | 2.8884 | 2.8798 | 0.0086
GEN-2018-069 | 01 NORTH | 659267 | RHAME___-BE7 | 115 | 1.943 | 1.9404 | 0.0026
GEN-2018-069 | 01 NORTH | 659302 | CHARL_CK-BE4 | 230 | 11.3272 | 11.3017 | 0.0255
GEN-2018-069 | 01 NORTH | 659339 | BOWMAN__-BE4 | 230 | 3.6806 | 3.6653 | 0.0153
GEN-2018-069 | 01 NORTH | 659384 | ROUNDUP_-BE3 | 345 | 9.5729 | 9.555 | 0.0179
GEN-2018-069 | 01 NORTH | 659390 | PATENTGT-BE3 | 345 | 8.6996 | 8.6869 | 0.0127
GEN-2018-069 | 01 NORTH | 659400 | ND.SUN._-PP4 | 230 | 5.0211 | 5.0116 | 0.0095
GEN-2018-069 | 01 NORTH | 659442 | 32STREET-RR7 | 115 | 1.8456 | 1.8431 | 0.0025
GEN-2018-069 | 01 NORTH | 659544 | PRNGHORN-RR7 | 115 | 1.8456 | 1.8431 | 0.0025
GEN-2018-069 | 01 NORTH | 659550 | LNGBUTTE-RR4 | 230 | 5.4118 | 5.4003 | 0.0115
GEN-2018-069 | 01 NORTH | 661019 | MATHSON7 | 115 | 8.034 | 8.0085 | 0.0255
GEN-2018-069 | 01 NORTH | 661024 | WDICKSN7 | 115 | 6.4036 | 6.3873 | 0.0163
GEN-2018-069 | 01 NORTH | 661033 | CABINCR7 | 115 | 3.0509 | 3.035 | 0.0159
GEN-2018-069 | 01 NORTH | 661034 | KEYXLPS14 7 | 115 | 3.121 | 3.1058 | 0.0152
GEN-2018-069 | 01 NORTH | 661053 | MANDAN 4 | 230 | 15.7601 | 15.7558 | 0.0043
GEN-2018-069 | 01 NORTH | 661070 | N ENGLN7 | 115 | 3.6534 | 3.6481 | 0.0053
GEN-2018-074 | 01 NORTH | 652567 | DENISON4 | 230 | 5.1544 | 4.9366 | 0.2178
GEN-2018-074 | 01 NORTH | 652561 | DENISON5 | 161 | 6.1701 | 5.9871 | 0.183
GEN-2018-074 | 01 NORTH | 652565 | SIOUXCY4 | 230 | 20.341 | 20.2786 | 0.0624
GEN-2018-074 | 01 NORTH | 652583 | DENISON8 | 69 | 11.9688 | 11.7338 | 0.235
GEN-2018-074 | 01 NORTH | 760515 | GEN-2017-222 | 230 | 3.8535 | 3.611 | 0.2425
GEN-2018-074 | 01 NORTH | 640386 | TWIN CH4 | 230 | 8.9225 | 8.917 | 0.0055
GEN-2018-074 | 01 NORTH | 652509 | FTRANDL4 | 230 | 12.1336 | 12.1325 | 0.0011
GEN-2018-074 | 01 NORTH | 652552 | SIOUXCY2 | 230 | 20.341 | 20.2786 | 0.0624
GEN-2018-074 | 01 NORTH | 652566 | SIOUXCY5 | 161 | 20.956 | 20.9268 | 0.0292
GEN-2018-074 | 01 NORTH | 652603 | EXIRA 5 | 161 | 7.0877 | 7.0588 | 0.0289
GEN-2018-074 | 01 NORTH | 655484 | RASMUSN-ER4 | 230 | 6.7272 | 6.7231 | 0.0041
GEN-2018-074 | 01 NORTH | 656267 | MANNINGTAP 8 | 69 | 4.4766 | 4.465 | 0.0116
GEN-2018-074 | 01 NORTH | 658030 | DENISONWEST8 | 69 | 6.6947 | 6.6199 | 0.0748
GEN-2018-074 | 01 NORTH | 658031 | DENSOUMAIN8 | 69 | 6.86 | 6.7815 | 0.0785
GEN-2018-074 | 01 NORTH | 659912 | J6BOYER_-NI8 | 69 | 9.7909 | 9.6821 | 0.1088
GEN-2018-074 | 01 NORTH | 763098 | GEN-2018-074 | 230 | 3.6096 | 3.3659 | 0.2437
GEN-2018-074 | 01 NORTH | 631069 | ANTA TP5 | 161 | 7.1269 | 7.1056 | 0.0213
GEN-2018-074 | 01 NORTH | 635223 | PLYMOTH5 | 161 | 20.4785 | 20.4523 | 0.0262
GEN-2018-074 | 01 NORTH | 640387 | TWIN CH7 | 115 | 10.7822 | 10.7789 | 0.0033
GEN-2018-074 | 01 NORTH | 640540 | MEADOWGROVE4 | 230 | 5.0998 | 5.0997 | 0.0001
GEN-2018-074 | 01 NORTH | 640560 | WAKEFIELD 4 | 230 | 7.9675 | 7.9654 | 0.0021
GEN-2018-074 | 01 NORTH | 652507 | FTTHOMP4 | 230 | 19.8146 | 19.814 | 0.0006
GEN-2018-074 | 01 NORTH | 652510 | FTRANDL7 | 115 | 12.7749 | 12.7744 | 0.0005
GEN-2018-074 | 01 NORTH | 652526 | UTICAJC4 | 230 | 8.4184 | 8.4168 | 0.0016
GEN-2018-074 | 01 NORTH | 652563 | SPENCER5 | 161 | 10.0544 | 10.0537 | 0.0007
GEN-2018-074 | 01 NORTH | 652564 | SIOUXCY3 | 345 | 15.3816 | 15.3622 | 0.0194
GEN-2018-074 | 01 NORTH | 652574 | SIOUXCY8 | 69 | 18.4952 | 18.4856 | 0.0096
GEN-2018-074 | 01 NORTH | 655475 | LAKPLAT-ER4 | 230 | 5.5515 | 5.5513 | 0.0002
GEN-2018-074 | 01 NORTH | 655485 | RASMUSN-ER8 | 69 | 3.1695 | 3.1692 | 0.0003
GEN-2018-074 | 01 NORTH | 656247 | TEMPLTON8 | 69 | 6.1067 | 6.0993 | 0.0074
GEN-2018-074 | 01 NORTH | 659854 | K335AMAI-NI8 | 69 | 8.7723 | 8.687 | 0.0853
GEN-2018-074 | 01 NORTH | 659862 | K307DENI-NI8 | 69 | 6.3923 | 6.3495 | 0.0428
GEN-2018-074 | 01 NORTH | 659868 | L9 MANNI-NI8 | 69 | 2.5655 | 2.5619 | 0.0036
GEN-2018-074 | 01 NORTH | 659885 | K306SCHL-NI8 | 69 | 4.2296 | 4.2155 | 0.0141
GEN-2018-074 | 01 NORTH | 659900 | EAGLE___-NI4 | 230 | 7.3012 | 7.2975 | 0.0037
GEN-2018-074 | 01 NORTH | 659918 | J12_____-NI8 | 69 | 5.1944 | 5.1794 | 0.015
GEN-2018-074 | 01 NORTH | 587764 | G16-094-TAP | 230 | 8.8873 | 8.8872 | 0.0001
GEN-2018-074 | 01 NORTH | 589324 | G17-094-TAP | 230 | 7.6985 | 7.6984 | 0.0001
GEN-2018-074 | 01 NORTH | 631070 | ANITA 5 | 161 | 6.3452 | 6.3304 | 0.0148
GEN-2018-074 | 01 NORTH | 635200 | RAUN 3 | 345 | 27.0138 | 26.9962 | 0.0176
GEN-2018-074 | 01 NORTH | 635224 | PLYMOTH8 | 69 | 21.403 | 21.391 | 0.012
GEN-2018-074 | 01 NORTH | 635225 | MORNSD 5 | 161 | 10.845 | 10.8392 | 0.0058
GEN-2018-074 | 01 NORTH | 635226 | LEEDS 5 | 161 | 15.8452 | 15.8337 | 0.0115
GEN-2018-074 | 01 NORTH | 635260 | LEMARST5 | 161 | 9.7975 | 9.7921 | 0.0054
GEN-2018-074 | 01 NORTH | 640080 | BELDEN 7 | 115 | 5.9733 | 5.973 | 0.0003
GEN-2018-074 | 01 NORTH | 640133 | COLMBUS4 | 230 | 11.4877 | 11.4874 | 0.0003
GEN-2018-074 | 01 NORTH | 640163 | EMERSON7 | 115 | 5.4485 | 5.4479 | 0.0006
GEN-2018-074 | 01 NORTH | 640227 | HOSKINS4 | 230 | 10.0896 | 10.0884 | 0.0012
GEN-2018-074 | 01 NORTH | 640349 | SPENCER7 | 115 | 4.7744 | 4.7744 | 0
GEN-2018-074 | 01 NORTH | 640388 | TWIN CH8 | 69 | 7.7842 | 7.7832 | 0.001
GEN-2018-074 | 01 NORTH | 640424 | S.SIOUXCITY7 | 115 | 7.3706 | 7.3691 | 0.0015
GEN-2018-074 | 01 NORTH | 640561 | RTLSNAKE.W 4 | 230 | 7.1132 | 7.1117 | 0.0015
GEN-2018-074 | 01 NORTH | 648506 | PR BRZ 4 | 230 | 3.5115 | 3.5115 | 0
GEN-2018-074 | 01 NORTH | 652276 | FTTHOMP8 | 69 | 3.6054 | 3.6054 | 0
GEN-2018-074 | 01 NORTH | 652475 | BONESTL7 | 115 | 3.5176 | 3.5176 | 0
GEN-2018-074 | 01 NORTH | 652501 | ARMOUR 7 | 115 | 4.124 | 4.1239 | 0.0001
GEN-2018-074 | 01 NORTH | 652506 | FTTHOMP3 | 345 | 10.4278 | 10.4276 | 0.0002
GEN-2018-074 | 01 NORTH | 652514 | HURON 4 | 230 | 11.0547 | 11.0547 | 0
GEN-2018-074 | 01 NORTH | 652519 | OAHE 4 | 230 | 11.9528 | 11.9527 | 0.0001
GEN-2018-074 | 01 NORTH | 652540 | BIGBND14 | 230 | 11.7244 | 11.7242 | 0.0002
GEN-2018-074 | 01 NORTH | 652541 | BIGBND24 | 230 | 11.6429 | 11.6427 | 0.0002
GEN-2018-074 | 01 NORTH | 652560 | CRESTON5 | 161 | 9.7302 | 9.7262 | 0.004
GEN-2018-074 | 01 NORTH | 652581 | SPENCER8 | 69 | 15.0604 | 15.06 | 0.0004
GEN-2018-074 | 01 NORTH | 652606 | LETCHER4 | 230 | 4.7237 | 4.7236 | 0.0001
GEN-2018-074 | 01 NORTH | 652607 | WESSINGTON 4 | 230 | 5.7229 | 5.7228 | 0.0001
GEN-2018-074 | 01 NORTH | 652626 | UTICAJC7 | 115 | 8.7387 | 8.7382 | 0.0005
GEN-2018-074 | 01 NORTH | 652864 | SIOUXCY-LNX3 | 345 | 15.1969 | 15.178 | 0.0189
GEN-2018-074 | 01 NORTH | 654457 | PRVLNG16 | 230 | 8.3621 | 8.3606 | 0.0015
GEN-2018-074 | 01 NORTH | 655145 | SW870-ER8 | 69 | 2.758 | 2.7578 | 0.0002
GEN-2018-074 | 01 NORTH | 655146 | SW873-ER8 | 69 | 2.7568 | 2.7566 | 0.0002
GEN-2018-074 | 01 NORTH | 655147 | MOS-JEFF-ER8 | 69 | 2.4256 | 2.4254 | 0.0002
GEN-2018-074 | 01 NORTH | 655476 | LAKPLAT-ER8 | 69 | 4.0077 | 4.0077 | 0
GEN-2018-074 | 01 NORTH | 655490 | WHTSWAN-ER7 | 115 | 12.4458 | 12.4454 | 0.0004
GEN-2018-074 | 01 NORTH | 656249 | TOYNE8 | 69 | 6.6812 | 6.6738 | 0.0074
GEN-2018-074 | 01 NORTH | 656570 | WISDOM5 | 161 | 10.2621 | 10.2614 | 0.0007
GEN-2018-074 | 01 NORTH | 659311 | PAHOJA__-BE4 | 230 | 7.4254 | 7.4235 | 0.0019
GEN-2018-074 | 01 NORTH | 659853 | K125DUNL-NI8 | 69 | 3.8742 | 3.868 | 0.0062
GEN-2018-074 | 01 NORTH | 659863 | K313HALB-NI8 | 69 | 3.5491 | 3.54 | 0.0091
GEN-2018-074 | 01 NORTH | 659867 | K319EWOL-NI8 | 69 | 2.6382 | 2.6344 | 0.0038
GEN-2018-074 | 01 NORTH | 659886 | K326OTTE-NI8 | 69 | 4.0815 | 4.069 | 0.0125
GEN-2018-074 | 01 NORTH | 659897 | K338WTCT-NI8 | 69 | 8.3685 | 8.2919 | 0.0766
GEN-2018-074 | 01 NORTH | 659901 | EAGLE___-NI8 | 69 | 14.0991 | 14.0953 | 0.0038
GEN-2018-074 | 01 NORTH | 659946 | K216LIBE-NI8 | 69 | 7.566 | 7.5645 | 0.0015
GEN-2018-074 | 01 NORTH | 659953 | K412HTNM-NI8 | 69 | 11.9214 | 11.9174 | 0.004
GEN-2018-074 | 01 NORTH | 659971 | K301HINT-NI8 | 69 | 10.2335 | 10.2302 | 0.0033
GEN-2018-074 | 01 NORTH | 659980 | K135CONC-NI8 | 69 | 6.665 | 6.6638 | 0.0012
GEN-2018-074 | 01 NORTH | 659999 | K106CHAR-NI8 | 69 | 4.9361 | 4.9232 | 0.0129
GEN-2018-074 | 01 NORTH | 762237 | G17-175TAP | 230 | 7.2707 | 7.2698 | 0.0009
GEN-2018-074 | 01 NORTH | 87487 | J748POI | 345 | 15.0615 | 15.0588 | 0.0027
GEN-2018-074 | 01 NORTH | 300097 | 5MARYVB2 | 161 | 10.6287 | 10.6283 | 0.0004
GEN-2018-074 | 01 NORTH | 587760 | GEN-2016-094 | 230 | 8.7366 | 8.7366 | 0
GEN-2018-074 | 01 NORTH | 589320 | GEN-2017-094 | 230 | 6.1877 | 6.1877 | 0
GEN-2018-074 | 01 NORTH | 601006 | SPLT RK3 | 345 | 14.9416 | 14.9392 | 0.0024
GEN-2018-074 | 01 NORTH | 628910 | HD WIND 5 | 161 | 5.2739 | 5.2659 | 0.008
GEN-2018-074 | 01 NORTH | 630009 | ANITA 8 | 69 | 7.4667 | 7.4591 | 0.0076
GEN-2018-074 | 01 NORTH | 630028 | EVERLYN8 | 69 | 7.1136 | 7.1135 | 0.0001
GEN-2018-074 | 01 NORTH | 631183 | CAYLER5 | 161 | 9.9229 | 9.9226 | 0.0003
GEN-2018-074 | 01 NORTH | 635056 | ADAMS 5 | 161 | 5.7686 | 5.7679 | 0.0007
GEN-2018-074 | 01 NORTH | 635201 | RAUN 5 | 161 | 27.0927 | 27.0747 | 0.018
GEN-2018-074 | 01 NORTH | 635221 | KELLOGG5 | 161 | 17.1226 | 17.1115 | 0.0111
GEN-2018-074 | 01 NORTH | 635235 | SALIX 5 | 161 | 14.6126 | 14.605 | 0.0076
GEN-2018-074 | 01 NORTH | 635248 | JAMES 8 | 69 | 13.7585 | 13.7539 | 0.0046
GEN-2018-074 | 01 NORTH | 635252 | J412 POI 3 | 345 | 9.6628 | 9.6617 | 0.0011
GEN-2018-074 | 01 NORTH | 635261 | LEMARS S 5 | 161 | 5.9001 | 5.8981 | 0.002
GEN-2018-074 | 01 NORTH | 635265 | LEMARSINDT 8 | 69 | 7.4579 | 7.4565 | 0.0014
GEN-2018-074 | 01 NORTH | 635280 | BVISTA 5 | 161 | 8.1852 | 8.1846 | 0.0006
GEN-2018-074 | 01 NORTH | 635322 | CAROL S8 | 69 | 7.7308 | 7.7266 | 0.0042
GEN-2018-074 | 01 NORTH | 635325 | TEMPLTN8 | 69 | 6.1548 | 6.1485 | 0.0063
GEN-2018-074 | 01 NORTH | 635360 | LTL SIOUX 5 | 161 | 6.5258 | 6.5242 | 0.0016
GEN-2018-074 | 01 NORTH | 635385 | HUDSON 8 | 69 | 6.0247 | 6.024 | 0.0007
GEN-2018-074 | 01 NORTH | 635391 | IRETONT8 | 69 | 5.8592 | 5.8585 | 0.0007
GEN-2018-074 | 01 NORTH | 635393 | MERRIL 8 | 69 | 5.8453 | 5.8445 | 0.0008
GEN-2018-074 | 01 NORTH | 635398 | REMSEN 3 | 345 | 14.4843 | 14.4816 | 0.0027
GEN-2018-074 | 01 NORTH | 635645 | MCKSBRG 5 | 161 | 7.9779 | 7.9764 | 0.0015
GEN-2018-074 | 01 NORTH | 640070 | BANCRFT7 | 115 | 5.0416 | 5.0413 | 0.0003
GEN-2018-074 | 01 NORTH | 640081 | BELDEN 8 | 69 | 3.6996 | 3.6995 | 0.0001
GEN-2018-074 | 01 NORTH | 640126 | E.COL. 4 | 230 | 10.0667 | 10.0664 | 0.0003
GEN-2018-074 | 01 NORTH | 640131 | COLMB.W4 | 230 | 9.8308 | 9.8306 | 0.0002
GEN-2018-074 | 01 NORTH | 640134 | KELLY 7 | 115 | 17.6974 | 17.6971 | 0.0003
GEN-2018-074 | 01 NORTH | 640164 | EMERSONG | 69 | 3.7543 | 3.7541 | 0.0002
GEN-2018-074 | 01 NORTH | 640212 | HARTGTN7 | 115 | 5.1832 | 5.183 | 0.0002
GEN-2018-074 | 01 NORTH | 640226 | HOSKINS3 | 345 | 13.0113 | 13.0096 | 0.0017
GEN-2018-074 | 01 NORTH | 640228 | HOSKINS7 | 115 | 18.0994 | 18.098 | 0.0014
GEN-2018-074 | 01 NORTH | 640305 | ONEILL 7 | 115 | 3.9336 | 3.9336 | 0
GEN-2018-074 | 01 NORTH | 640343 | SHELCRK4 | 230 | 10.8729 | 10.8726 | 0.0003
GEN-2018-074 | 01 NORTH | 640425 | S.SIOUXCITY8 | 69 | 4.497 | 4.4966 | 0.0004
GEN-2018-074 | 01 NORTH | 652249 | ARMOUR 8 | 69 | 2.4299 | 2.4299 | 0
GEN-2018-074 | 01 NORTH | 652398 | VFODNES4 | 230 | 7.3557 | 7.3549 | 0.0008
GEN-2018-074 | 01 NORTH | 652478 | GREGORY7 | 115 | 2.1571 | 2.1571 | 0
GEN-2018-074 | 01 NORTH | 652515 | HURON 7 | 115 | 15.0903 | 15.0902 | 0.0001
GEN-2018-074 | 01 NORTH | 652518 | MTVERN 7 | 115 | 4.2008 | 4.2007 | 0.0001
GEN-2018-074 | 01 NORTH | 652520 | OAHE 7 | 115 | 10.0527 | 10.0527 | 0
GEN-2018-074 | 01 NORTH | 652523 | SIOUXFL4 | 230 | 13.6104 | 13.6081 | 0.0023
GEN-2018-074 | 01 NORTH | 652525 | TYNDALL7 | 115 | 3.7466 | 3.7465 | 0.0001
GEN-2018-074 | 01 NORTH | 652530 | WATERTN4 | 230 | 14.4494 | 14.4493 | 0.0001
GEN-2018-074 | 01 NORTH | 652569 | CRESTON8 | 69 | 16.0633 | 16.0599 | 0.0034
GEN-2018-074 | 01 NORTH | 652609 | LETCHER7 | 115 | 6.0091 | 6.009 | 0.0001
GEN-2018-074 | 01 NORTH | 652614 | CARPENTER 4 | 230 | 6.9031 | 6.9031 | 0
GEN-2018-074 | 01 NORTH | 652806 | FTTHOM1-LNX3 | 345 | 10.3307 | 10.3306 | 0.0001
GEN-2018-074 | 01 NORTH | 652807 | FTTHOM2-LNX3 | 345 | 10.4278 | 10.4276 | 0.0002
GEN-2018-074 | 01 NORTH | 654455 | PRVLNG23 | 115 | 6.3384 | 6.3381 | 0.0003
GEN-2018-074 | 01 NORTH | 655126 | MOS-VERM-ER8 | 69 | 1.9286 | 1.9285 | 0.0001
GEN-2018-074 | 01 NORTH | 655130 | SW808-ER8 | 69 | 2.4249 | 2.4248 | 0.0001
GEN-2018-074 | 01 NORTH | 655136 | SW832-ER8 | 69 | 2.5038 | 2.5036 | 0.0002
GEN-2018-074 | 01 NORTH | 655137 | SW833-ER8 | 69 | 1.9982 | 1.9981 | 0.0001
GEN-2018-074 | 01 NORTH | 655153 | MOS-AMES-ER8 | 69 | 3.5356 | 3.5356 | 0
GEN-2018-074 | 01 NORTH | 655250 | CHMBRLAN-ER8 | 69 | 1.5802 | 1.5802 | 0
GEN-2018-074 | 01 NORTH | 655385 | MOS-LKPL-ER8 | 69 | 3.9932 | 3.9932 | 0
GEN-2018-074 | 01 NORTH | 655418 | FREEMAN-ER7 | 115 | 2.5595 | 2.5595 | 0
GEN-2018-074 | 01 NORTH | 655487 | SULLYBT-ER4 | 230 | 5.8952 | 5.8951 | 0.0001
GEN-2018-074 | 01 NORTH | 656233 | CAROLTON8 | 69 | 5.0236 | 5.0212 | 0.0024
GEN-2018-074 | 01 NORTH | 656527 | OSGOOD5 | 161 | 5.7271 | 5.727 | 0.0001
GEN-2018-074 | 01 NORTH | 656555 | SPNCRSJCT8 | 69 | 8.7543 | 8.7542 | 0.0001
GEN-2018-074 | 01 NORTH | 656573 | WISDOM G | 69 | 15.1844 | 15.184 | 0.0004
GEN-2018-074 | 01 NORTH | 659122 | STORLA__-BE4 | 230 | 5.3706 | 5.3705 | 0.0001
GEN-2018-074 | 01 NORTH | 659188 | PHILIP_T-BE4 | 230 | 4.311 | 4.311 | 0
GEN-2018-074 | 01 NORTH | 659205 | BROADLND-BE4 | 230 | 10.0163 | 10.0163 | 0
GEN-2018-074 | 01 NORTH | 659295 | SD.PW1__-BE4 | 230 | 4.4278 | 4.4278 | 0
GEN-2018-074 | 01 NORTH | 659700 | LAKPRKTP-LO8 | 69 | 2.0299 | 2.0299 | 0
GEN-2018-074 | 01 NORTH | 659735 | CLEVELND-LO4 | 230 | 4.9229 | 4.9221 | 0.0008
GEN-2018-074 | 01 NORTH | 659852 | K126MEC -NI8 | 69 | 3.7592 | 3.754 | 0.0052
GEN-2018-074 | 01 NORTH | 659855 | K318MEC -NI8 | 69 | 5.1171 | 5.0952 | 0.0219
GEN-2018-074 | 01 NORTH | 659887 | K333SCHL-NI8 | 69 | 3.9518 | 3.9406 | 0.0112
GEN-2018-074 | 01 NORTH | 659895 | PERRY___-NI8 | 69 | 10.5252 | 10.5225 | 0.0027
GEN-2018-074 | 01 NORTH | 659899 | K225ADAV-NI8 | 69 | 5.7554 | 5.7546 | 0.0008
GEN-2018-074 | 01 NORTH | 659906 | K317MANN-NI8 | 69 | 3.2123 | 3.2067 | 0.0056
GEN-2018-074 | 01 NORTH | 659907 | J1CENTER-NI8 | 69 | 9.5838 | 9.5821 | 0.0017
GEN-2018-074 | 01 NORTH | 659921 | J15_____-NI8 | 69 | 7.0376 | 7.0368 | 0.0008
GEN-2018-074 | 01 NORTH | 659942 | K217HWDN-NI8 | 69 | 8.2734 | 8.2721 | 0.0013
GEN-2018-074 | 01 NORTH | 659954 | K401UNIO-NI8 | 69 | 7.4163 | 7.4147 | 0.0016
GEN-2018-074 | 01 NORTH | 659972 | K334KING-NI8 | 69 | 2.8351 | 2.8346 | 0.0005
GEN-2018-074 | 01 NORTH | 659979 | K144LWTN-NI8 | 69 | 6.4764 | 6.4753 | 0.0011
GEN-2018-074 | 01 NORTH | 659998 | K105UTE_-NI8 | 69 | 4.2643 | 4.2573 | 0.007
GEN-2018-074 | 01 NORTH | 660007 | MENNO JCT 7 | 115 | 6.4875 | 6.4873 | 0.0002
GEN-2018-074 | 01 NORTH | 660026 | NAPA JCT 7 | 115 | 7.6491 | 7.6488 | 0.0003
GEN-2018-074 | 01 NORTH | 762238 | GEN-2017-175 | 230 | 7.041 | 7.0401 | 0.0009
GEN-2018-074 | 01 NORTH | 762779 | G18-043-TAP | 345 | 15.621 | 15.6194 | 0.0016
GEN-2019-019 | 01 NORTH | 659921 | J15_____-NI8 | 69 | 7.0376 | 6.6118 | 0.4258
GEN-2019-019 | 01 NORTH | 658900 | L4SXCTNMUNI8 | 69 | 6.6105 | 6.2712 | 0.3393
GEN-2019-019 | 01 NORTH | 658902 | L5SXCTWMUNI8 | 69 | 6.3538 | 6.0694 | 0.2844
GEN-2019-019 | 01 NORTH | 659901 | EAGLE___-NI8 | 69 | 14.0991 | 13.7992 | 0.2999
GEN-2019-019 | 01 NORTH | 763593 | GEN-2019-019 | 69 | 1.3293 | 1.0392 | 0.2901
GEN-2019-019 | 01 NORTH | 635385 | HUDSON 8 | 69 | 6.0247 | 5.9671 | 0.0576
GEN-2019-019 | 01 NORTH | 635391 | IRETONT8 | 69 | 5.8592 | 5.8053 | 0.0539
GEN-2019-019 | 01 NORTH | 659900 | EAGLE___-NI4 | 230 | 7.3012 | 7.2293 | 0.0719
GEN-2019-019 | 01 NORTH | 659907 | J1CENTER-NI8 | 69 | 9.5838 | 9.371 | 0.2128
GEN-2019-019 | 01 NORTH | 659940 | K223SIOU-NI8 | 69 | 6.4066 | 6.2117 | 0.1949
GEN-2019-019 | 01 NORTH | 659941 | K222HULL-NI8 | 69 | 6.1824 | 5.9581 | 0.2243
GEN-2019-019 | 01 NORTH | 659942 | K217HWDN-NI8 | 69 | 8.2734 | 8.1541 | 0.1193
GEN-2019-019 | 01 NORTH | 635380 | RCKVALY8 | 69 | 6.2826 | 6.2144 | 0.0682
GEN-2019-019 | 01 NORTH | 635383 | INWOODT8 | 69 | 5.6623 | 5.6109 | 0.0514
GEN-2019-019 | 01 NORTH | 635386 | SXRIVER8 | 69 | 3.2708 | 3.255 | 0.0158
GEN-2019-019 | 01 NORTH | 635390 | IRETON 8 | 69 | 2.7741 | 2.763 | 0.0111
GEN-2019-019 | 01 NORTH | 652552 | SIOUXCY2 | 230 | 20.341 | 20.2994 | 0.0416
GEN-2019-019 | 01 NORTH | 659311 | PAHOJA__-BE4 | 230 | 7.4254 | 7.3973 | 0.0281
GEN-2019-019 | 01 NORTH | 659902 | L1______-NI8 | 69 | 6.3975 | 6.2241 | 0.1734
GEN-2019-019 | 01 NORTH | 659904 | L3______-NI8 | 69 | 8.7972 | 8.653 | 0.1442
GEN-2019-019 | 01 NORTH | 659977 | K218ROCK-NI8 | 69 | 5.4792 | 5.4216 | 0.0576
GEN-2019-019 | 01 NORTH | 635377 | DOONTAP8 | 69 | 5.6209 | 5.5663 | 0.0546
GEN-2019-019 | 01 NORTH | 635381 | RKVALTT8 | 69 | 5.5511 | 5.4942 | 0.0569
GEN-2019-019 | 01 NORTH | 635387 | ALCESTR8 | 69 | 1.594 | 1.5906 | 0.0034
GEN-2019-019 | 01 NORTH | 635392 | CRAIG 8 | 69 | 1.9056 | 1.9006 | 0.005
GEN-2019-019 | 01 NORTH | 652523 | SIOUXFL4 | 230 | 13.6104 | 13.5916 | 0.0188
GEN-2019-019 | 01 NORTH | 652564 | SIOUXCY3 | 345 | 15.3816 | 15.3669 | 0.0147
GEN-2019-019 | 01 NORTH | 652565 | SIOUXCY4 | 230 | 20.341 | 20.2994 | 0.0416
GEN-2019-019 | 01 NORTH | 659735 | CLEVELND-LO4 | 230 | 4.9229 | 4.9105 | 0.0124
GEN-2019-019 | 01 NORTH | 659894 | NORTHWST-NI8 | 69 | 4.0821 | 4.056 | 0.0261
GEN-2019-019 | 01 NORTH | 659896 | K228WSTB-NI8 | 69 | 5.7243 | 5.6382 | 0.0861
GEN-2019-019 | 01 NORTH | 659943 | K207OC N-NI8 | 69 | 6.0861 | 5.9543 | 0.1318
GEN-2019-019 | 01 NORTH | 659944 | K202PRES-NI8 | 69 | 5.4683 | 5.4407 | 0.0276
GEN-2019-019 | 01 NORTH | 659955 | K213HOSP-NI8 | 69 | 5.1025 | 5.0196 | 0.0829
GEN-2019-019 | 01 NORTH | 602004 | SPLT RK4 | 230 | 13.1508 | 13.134 | 0.0168
GEN-2019-019 | 01 NORTH | 635200 | RAUN 3 | 345 | 27.0138 | 27.0003 | 0.0135
GEN-2019-019 | 01 NORTH | 635371 | HOSPERS8 | 69 | 4.911 | 4.8566 | 0.0544
GEN-2019-019 | 01 NORTH | 635382 | RCKVALT8 | 69 | 5.3779 | 5.3245 | 0.0534
GEN-2019-019 | 01 NORTH | 635384 | INWOOD 8 | 69 | 2.2005 | 2.1932 | 0.0073
GEN-2019-019 | 01 NORTH | 635394 | MERRILN8 | 69 | 5.7709 | 5.7696 | 0.0013
GEN-2019-019 | 01 NORTH | 640386 | TWIN CH4 | 230 | 8.9225 | 8.9188 | 0.0037
GEN-2019-019 | 01 NORTH | 652398 | VFODNES4 | 230 | 7.3557 | 7.3519 | 0.0038
GEN-2019-019 | 01 NORTH | 652509 | FTRANDL4 | 230 | 12.1336 | 12.1321 | 0.0015
GEN-2019-019 | 01 NORTH | 652513 | HANLON 4 | 230 | 5.5672 | 5.5651 | 0.0021
GEN-2019-019 | 01 NORTH | 652524 | SIOUXFL7 | 115 | 26.9963 | 26.9793 | 0.017
GEN-2019-019 | 01 NORTH | 652566 | SIOUXCY5 | 161 | 20.956 | 20.9267 | 0.0293
GEN-2019-019 | 01 NORTH | 652567 | DENISON4 | 230 | 5.1544 | 5.1536 | 0.0008
GEN-2019-019 | 01 NORTH | 652606 | LETCHER4 | 230 | 4.7237 | 4.723 | 0.0007
GEN-2019-019 | 01 NORTH | 652864 | SIOUXCY-LNX3 | 345 | 15.1969 | 15.1826 | 0.0143
GEN-2019-019 | 01 NORTH | 655484 | RASMUSN-ER4 | 230 | 6.7272 | 6.7239 | 0.0033
GEN-2019-019 | 01 NORTH | 659736 | CLEVELND-LO8 | 69 | 4.2477 | 4.2449 | 0.0028
GEN-2019-019 | 01 NORTH | 659905 | L8______-NI8 | 69 | 6.0909 | 5.9731 | 0.1178
GEN-2019-019 | 01 NORTH | 659920 | J14PRKNS-NI8 | 69 | 4.7883 | 4.7487 | 0.0396
GEN-2019-019 | 01 NORTH | 659945 | K226MERR-NI8 | 69 | 5.6994 | 5.681 | 0.0184
GEN-2019-023 | 01 NORTH | 652616 | MINGUSVILLE4 | 230 | 4.3407 | 3.9054 | 0.4353
GEN-2019-023 | 01 NORTH | 652403 | DAWSONC4 | 230 | 4.2911 | 4.0754 | 0.2157
GEN-2019-023 | 01 NORTH | 659247 | MEDORA__-UM4 | 230 | 5.2368 | 5.0538 | 0.183
GEN-2019-023 | 01 NORTH | 659535 | BEAVRHIL-GW4 | 230 | 4.3407 | 3.9054 | 0.4353
GEN-2019-023 | 01 NORTH | 763043 | GEN-2018-069 | 230 | 4.2714 | 3.8332 | 0.4382
GEN-2019-023 | 01 NORTH | 652404 | DAWSONC7 | 115 | 7.6808 | 7.4527 | 0.2281
GEN-2019-023 | 01 NORTH | 652405 | FTPECK 4 | 230 | 2.094 | 2.0711 | 0.0229
GEN-2019-023 | 01 NORTH | 652411 | MI CTYE4 | 230 | 2.7429 | 2.6932 | 0.0497
GEN-2019-023 | 01 NORTH | 652425 | BELFELD4 | 230 | 9.3261 | 9.1728 | 0.1533
GEN-2019-023 | 01 NORTH | 659536 | BEAVRHIL-GW7 | 115 | 3.5043 | 3.3541 | 0.1502
GEN-2019-023 | 01 NORTH | 652200 | GLENDIVE7 | 115 | 6.9146 | 6.7477 | 0.1669
GEN-2019-023 | 01 NORTH | 652212 | GLENDIVEP2T7 | 115 | 4.1788 | 4.1127 | 0.0661
GEN-2019-023 | 01 NORTH | 652401 | CIRCLE 7 | 115 | 2.1157 | 2.1041 | 0.0116
GEN-2019-023 | 01 NORTH | 652406 | FTPECK 7 | 115 | 2.9033 | 2.8862 | 0.0171
GEN-2019-023 | 01 NORTH | 652412 | MI CTYE7 | 115 | 3.7233 | 3.681 | 0.0423
GEN-2019-023 | 01 NORTH | 652424 | BELFELD3 | 345 | 6.628 | 6.5602 | 0.0678
GEN-2019-023 | 01 NORTH | 659124 | DICKINSN-BE4 | 230 | 6.9327 | 6.8766 | 0.0561
GEN-2019-023 | 01 NORTH | 659309 | S.HEART_-RR4 | 230 | 9.3261 | 9.1728 | 0.1533
GEN-2019-023 | 01 NORTH | 659448 | DAGLUM__-BE4 | 230 | 6.3542 | 6.2898 | 0.0644
GEN-2019-023 | 01 NORTH | 661004 | BAKER 4 | 230 | 3.1917 | 3.1603 | 0.0314
GEN-2019-023 | 01 NORTH | 661056 | LEWIS 7 | 115 | 5.5853 | 5.5726 | 0.0127
GEN-2019-023 | 01 NORTH | 652395 | SHIRLEY TAP | 115 | 2.9196 | 2.8919 | 0.0277
GEN-2019-023 | 01 NORTH | 652407 | FALLON 7 | 115 | 3.075 | 3.0408 | 0.0342
GEN-2019-023 | 01 NORTH | 652409 | WOLFPT 7 | 115 | 2.926 | 2.9121 | 0.0139
GEN-2019-023 | 01 NORTH | 652468 | HEBRON 4 | 230 | 5.5473 | 5.5322 | 0.0151
GEN-2019-023 | 01 NORTH | 659125 | DICKINSN-BE7 | 115 | 9.0705 | 9.0283 | 0.0422
GEN-2019-023 | 01 NORTH | 659151 | RICHLAND-BE7 | 115 | 5.5253 | 5.5142 | 0.0111
GEN-2019-023 | 01 NORTH | 659183 | CHARL_CK-BE3 | 345 | 10.581 | 10.5357 | 0.0453
GEN-2019-023 | 01 NORTH | 659195 | DICKINS2-BE7 | 115 | 9.0358 | 8.994 | 0.0418
GEN-2019-023 | 01 NORTH | 659265 | LITTL_MS-BE4 | 230 | 3.4157 | 3.3859 | 0.0298
GEN-2019-023 | 01 NORTH | 659266 | RHAME___-BE4 | 230 | 4.3675 | 4.3348 | 0.0327
GEN-2019-023 | 01 NORTH | 659306 | S.HEART_-RR7 | 115 | 2.2025 | 2.1982 | 0.0043
GEN-2019-023 | 01 NORTH | 659450 | BRADYWND 4 | 230 | 3.4656 | 3.4513 | 0.0143
GEN-2019-023 | 01 NORTH | 659542 | REDWATER-MC7 | 115 | 2.1157 | 2.1041 | 0.0116
GEN-2019-023 | 01 NORTH | 661005 | BAKER 7 | 115 | 3.3994 | 3.3789 | 0.0205
GEN-2019-023 | 01 NORTH | 661032 | GLENDCT7 | 115 | 6.257 | 6.1413 | 0.1157
GEN-2019-023 | 01 NORTH | 588550 | GEN-2017-010 | 230 | 4.292 | 4.2606 | 0.0314
GEN-2019-023 | 01 NORTH | 652213 | FALLON 8 | 69 | 1.0345 | 1.0322 | 0.0023
GEN-2019-023 | 01 NORTH | 652394 | TERRY TAP | 115 | 2.785 | 2.758 | 0.027
GEN-2019-023 | 01 NORTH | 652651 | FAIRVIEW 7 | 115 | 4.826 | 4.8204 | 0.0056
GEN-2019-023 | 01 NORTH | 655790 | HELMUT -LY7 | 115 | 5.4862 | 5.4753 | 0.0109
GEN-2019-023 | 01 NORTH | 659101 | ANTELOPE-BE3 | 345 | 19.5131 | 19.4947 | 0.0184
GEN-2019-023 | 01 NORTH | 659182 | CHARL_CK-BE7 | 115 | 13.6018 | 13.5771 | 0.0247
GEN-2019-023 | 01 NORTH | 659186 | E.SIDNEY-LY7 | 115 | 4.0995 | 4.094 | 0.0055
GEN-2019-023 | 01 NORTH | 659259 | HEADRESS-CM7 | 115 | 2.9204 | 2.9066 | 0.0138
GEN-2019-023 | 01 NORTH | 659263 | LITTL_MS-BE7 | 115 | 2.8884 | 2.8777 | 0.0107
GEN-2019-023 | 01 NORTH | 659267 | RHAME___-BE7 | 115 | 1.943 | 1.9397 | 0.0033
GEN-2019-023 | 01 NORTH | 659302 | CHARL_CK-BE4 | 230 | 11.3272 | 11.2953 | 0.0319
GEN-2019-023 | 01 NORTH | 659339 | BOWMAN__-BE4 | 230 | 3.6806 | 3.6615 | 0.0191
GEN-2019-023 | 01 NORTH | 659384 | ROUNDUP_-BE3 | 345 | 9.5729 | 9.5505 | 0.0224
GEN-2019-023 | 01 NORTH | 659390 | PATENTGT-BE3 | 345 | 8.6996 | 8.6837 | 0.0159
GEN-2019-023 | 01 NORTH | 659400 | ND.SUN._-PP4 | 230 | 5.0211 | 5.0092 | 0.0119
GEN-2019-023 | 01 NORTH | 659442 | 32STREET-RR7 | 115 | 1.8456 | 1.8425 | 0.0031
GEN-2019-023 | 01 NORTH | 659544 | PRNGHORN-RR7 | 115 | 1.8456 | 1.8425 | 0.0031
GEN-2019-023 | 01 NORTH | 659550 | LNGBUTTE-RR4 | 230 | 5.4118 | 5.3974 | 0.0144
GEN-2019-023 | 01 NORTH | 661019 | MATHSON7 | 115 | 8.034 | 8.0021 | 0.0319
GEN-2019-023 | 01 NORTH | 661024 | WDICKSN7 | 115 | 6.4036 | 6.3832 | 0.0204
GEN-2019-023 | 01 NORTH | 661033 | CABINCR7 | 115 | 3.0509 | 3.0311 | 0.0198
GEN-2019-023 | 01 NORTH | 661034 | KEYXLPS14 7 | 115 | 3.121 | 3.102 | 0.019
GEN-2019-023 | 01 NORTH | 661053 | MANDAN 4 | 230 | 15.7601 | 15.7548 | 0.0053
GEN-2019-023 | 01 NORTH | 661070 | N ENGLN7 | 115 | 3.6534 | 3.6468 | 0.0066
GEN-2019-037 | 01 NORTH | 659105 | LELAND_O-BE3 | 345 | 19.2093 | 18.9213 | 0.288
GEN-2019-037 | 01 NORTH | 588210 | GEN-2016-130 | 345 | 12.4165 | 12.2981 | 0.1184
GEN-2019-037 | 01 NORTH | 659060 | FINSTAD345 | 345 | 7.107 | 7.0983 | 0.0087
GEN-2019-037 | 01 NORTH | 659101 | ANTELOPE-BE3 | 345 | 19.5131 | 19.4075 | 0.1056
GEN-2019-037 | 01 NORTH | 659106 | LELAND_O-BE4 | 230 | 24.735 | 24.5325 | 0.2025
GEN-2019-037 | 01 NORTH | 659422 | LO.LS-GR-BE3 | 345 | 19.2093 | 18.9213 | 0.288
GEN-2019-037 | 01 NORTH | 659424 | LO.LS-FT-BE3 | 345 | 19.2093 | 18.9213 | 0.288
GEN-2019-037 | 01 NORTH | 763703 | GEN-2019-037 | 345 | 11.6051 | 11.3174 | 0.2877
GEN-2019-037 | 01 NORTH | 615901 | GRE-STANTON4 | 230 | 17.7108 | 17.7053 | 0.0055
GEN-2019-037 | 01 NORTH | 652441 | GARRISN4 | 230 | 11.6312 | 11.6212 | 0.01
GEN-2019-037 | 01 NORTH | 652456 | WASHBRN4 | 230 | 10.2876 | 10.2641 | 0.0235
GEN-2019-037 | 01 NORTH | 655906 | FINSTAD -MW7 | 115 | 19.8346 | 19.813 | 0.0216
GEN-2019-037 | 01 NORTH | 659108 | LOGAN___-BE4 | 230 | 6.5905 | 6.5865 | 0.004
GEN-2019-037 | 01 NORTH | 659183 | CHARL_CK-BE3 | 345 | 10.581 | 10.5672 | 0.0138
GEN-2019-037 | 01 NORTH | 659199 | BASIN___-BE4 | 230 | 22.3804 | 22.2152 | 0.1652
GEN-2019-037 | 01 NORTH | 659212 | DGC_____-BE3 | 345 | 18.4352 | 18.3409 | 0.0943
GEN-2019-037 | 01 NORTH | 659218 | COTEAU__-RR3 | 345 | 19.5131 | 19.4075 | 0.1056
GEN-2019-037 | 01 NORTH | 659336 | TANDE___-BE3 | 345 | 8.6936 | 8.6869 | 0.0067
GEN-2019-037 | 01 NORTH | 659384 | ROUNDUP_-BE3 | 345 | 9.5729 | 9.5592 | 0.0137
GEN-2019-037 | 01 NORTH | 659420 | AV.LS-BD-BE3 | 345 | 19.5131 | 19.4075 | 0.1056
GEN-2019-037 | 01 NORTH | 659428 | CC.LS-LO-BE3 | 345 | 6.7075 | 6.706 | 0.0015
GEN-2019-037 | 01 NORTH | 659576 | BEPCPRXCC1 3 | 345 | 18.6794 | 18.5853 | 0.0941
GEN-2019-037 | 01 NORTH | 762544 | G18-008-TAP | 345 | 4.2884 | 4.2847 | 0.0037
GEN-2019-037 | 01 NORTH | 587030 | GEN-2016-004 | 230 | 7.3122 | 7.2964 | 0.0158
GEN-2019-037 | 01 NORTH | 615600 | GRE-COAL CR4 | 230 | 18.9494 | 18.9463 | 0.0031
GEN-2019-037 | 01 NORTH | 615900 | GRE-COAL TP4 | 230 | 16.0152 | 16.0124 | 0.0028
GEN-2019-037 | 01 NORTH | 652424 | BELFELD3 | 345 | 6.628 | 6.6245 | 0.0035
GEN-2019-037 | 01 NORTH | 652426 | BISMARK4 | 230 | 14.3162 | 14.3089 | 0.0073
GEN-2019-037 | 01 NORTH | 652442 | GARRISN7 | 115 | 15.0699 | 15.0647 | 0.0052
GEN-2019-037 | 01 NORTH | 652444 | JAMESTN4 | 230 | 8.2619 | 8.2609 | 0.001
GEN-2019-037 | 01 NORTH | 652466 | HILKEN 4 | 230 | 7.8973 | 7.8947 | 0.0026
GEN-2019-037 | 01 NORTH | 655905 | RBNSNLAK-MW7 | 115 | 10.0829 | 10.0786 | 0.0043
GEN-2019-037 | 01 NORTH | 655919 | OSBORN -MW7 | 115 | 11.6878 | 11.6815 | 0.0063
GEN-2019-037 | 01 NORTH | 655920 | VANHOOK -MW7 | 115 | 13.0464 | 13.038 | 0.0084
GEN-2019-037 | 01 NORTH | 657756 | SQBUTTE4 | 230 | 23.1894 | 23.1858 | 0.0036
GEN-2019-037 | 01 NORTH | 659109 | BASIN___-BE7 | 115 | 5.1737 | 5.1693 | 0.0044
GEN-2019-037 | 01 NORTH | 659130 | CHAPELLE-BE3 | 345 | 6.7447 | 6.7431 | 0.0016
GEN-2019-037 | 01 NORTH | 659143 | BLAISDEL-BE4 | 230 | 6.059 | 6.0567 | 0.0023
GEN-2019-037 | 01 NORTH | 659155 | LOGAN___-BE7 | 115 | 11.2842 | 11.2805 | 0.0037
GEN-2019-037 | 01 NORTH | 659182 | CHARL_CK-BE7 | 115 | 13.6018 | 13.5951 | 0.0067
GEN-2019-037 | 01 NORTH | 659222 | COTEAU_1-RR8 | 69 | 9.4106 | 9.4056 | 0.005
GEN-2019-037 | 01 NORTH | 659233 | DGC_____-BE4 | 230 | 7.3407 | 7.3307 | 0.01
GEN-2019-037 | 01 NORTH | 659302 | CHARL_CK-BE4 | 230 | 11.3272 | 11.3173 | 0.0099
GEN-2019-037 | 01 NORTH | 659337 | TANDE___-BE4 | 230 | 12.6699 | 12.6624 | 0.0075
GEN-2019-037 | 01 NORTH | 659385 | ROUNDUP_-MK7 | 115 | 11.5156 | 11.509 | 0.0066
GEN-2019-037 | 01 NORTH | 659387 | KUMMERDG-BE3 | 345 | 7.2268 | 7.2203 | 0.0065
GEN-2019-037 | 01 NORTH | 659390 | PATENTGT-BE3 | 345 | 8.6996 | 8.6923 | 0.0073
GEN-2019-037 | 01 NORTH | 659404 | BURKE___-PP3 | 345 | 4.6884 | 4.6865 | 0.0019
GEN-2019-037 | 01 NORTH | 659421 | BD.LS-AV-BE3 | 345 | 4.5977 | 4.597 | 0.0007
GEN-2019-037 | 01 NORTH | 659423 | GR.LS-LO-BE3 | 345 | 6.6232 | 6.6219 | 0.0013
GEN-2019-037 | 01 NORTH | 659427 | TN.LS-JD-BE3 | 345 | 8.6936 | 8.6869 | 0.0067
GEN-2019-037 | 01 NORTH | 659479 | TRADEWND-UA3 | 345 | 6.1731 | 6.1699 | 0.0032
GEN-2019-037 | 01 NORTH | 760998 | GEN-2017-214 | 230 | 3.3734 | 3.3726 | 0.0008
GEN-2019-037 | 01 NORTH | 762537 | GEN-2018-008 | 345 | 4.2841 | 4.2804 | 0.0037
GEN-2019-037 | 01 NORTH | 47544 | J1754 POI | 230 | 7.2374 | 7.2369 | 0.0005
GEN-2019-037 | 01 NORTH | 67030 | MPC04000MPT | 230 | 10.7253 | 10.7246 | 0.0007
GEN-2019-037 | 01 NORTH | 603023 | MALLARD7 | 115 | 11.3208 | 11.3179 | 0.0029
GEN-2019-037 | 01 NORTH | 608602 | SQBEAST4 | 230 | 23.1894 | 23.1858 | 0.0036
GEN-2019-037 | 01 NORTH | 615601 | GRE-COAL FM8 | 69 | 8.6546 | 8.6545 | 0.0001
GEN-2019-037 | 01 NORTH | 615604 | GRE-COALFB14 | 230 | 18.9494 | 18.9463 | 0.0031
GEN-2019-037 | 01 NORTH | 615605 | GRE-COALFB24 | 230 | 18.9494 | 18.9463 | 0.0031
GEN-2019-037 | 01 NORTH | 615606 | GRE-COALFB34 | 230 | 18.9494 | 18.9463 | 0.0031
GEN-2019-037 | 01 NORTH | 620381 | UNDERWD4 | 230 | 14.8822 | 14.8803 | 0.0019
GEN-2019-037 | 01 NORTH | 652216 | WATFORD4 | 230 | 6.5544 | 6.5522 | 0.0022
GEN-2019-037 | 01 NORTH | 652296 | WARD 4 | 230 | 14.095 | 14.0899 | 0.0051
GEN-2019-037 | 01 NORTH | 652419 | KILDEER7 | 115 | 4.8314 | 4.8307 | 0.0007
GEN-2019-037 | 01 NORTH | 652425 | BELFELD4 | 230 | 9.3261 | 9.3228 | 0.0033
GEN-2019-037 | 01 NORTH | 652427 | BISMARK7 | 115 | 15.6389 | 15.6356 | 0.0033
GEN-2019-037 | 01 NORTH | 652435 | FARGO 4 | 230 | 10.1913 | 10.191 | 0.0003
GEN-2019-037 | 01 NORTH | 652445 | JAMESTN7 | 115 | 9.656 | 9.6554 | 0.0006
GEN-2019-037 | 01 NORTH | 652496 | WINCHESTER4 | 230 | 4.3543 | 4.3539 | 0.0004
GEN-2019-037 | 01 NORTH | 652590 | SNAKECR7 | 115 | 5.572 | 5.5712 | 0.0008
GEN-2019-037 | 01 NORTH | 652806 | FTTHOM1-LNX3 | 345 | 10.3307 | 10.3292 | 0.0015
GEN-2019-037 | 01 NORTH | 655643 | VOLTAIR -CP7 | 115 | 8.4725 | 8.4718 | 0.0007
GEN-2019-037 | 01 NORTH | 655657 | SW.MINOT-CP7 | 115 | 8.0129 | 8.0112 | 0.0017
GEN-2019-037 | 01 NORTH | 655690 | MAX_____-CP7 | 115 | 5.9234 | 5.9227 | 0.0007
GEN-2019-037 | 01 NORTH | 655752 | NWMDNTAP-MG7 | 115 | 1.4782 | 1.4778 | 0.0004
GEN-2019-037 | 01 NORTH | 655833 | GRSYBTTP-MK7 | 115 | 13.4843 | 13.4777 | 0.0066
GEN-2019-037 | 01 NORTH | 655853 | BEARCREK-MK7 | 115 | 8.0095 | 8.0063 | 0.0032
GEN-2019-037 | 01 NORTH | 655893 | DUNNCNTR-MK7 | 115 | 5.9828 | 5.981 | 0.0018
GEN-2019-037 | 01 NORTH | 655904 | BELDEN -MW7 | 115 | 9.66 | 9.6572 | 0.0028
GEN-2019-037 | 01 NORTH | 655907 | E.NEWTWN-MW7 | 115 | 11.8866 | 11.8804 | 0.0062
GEN-2019-037 | 01 NORTH | 655908 | PARSHALL-MW7 | 115 | 8.0727 | 8.0698 | 0.0029
GEN-2019-037 | 01 NORTH | 657751 | CENTER 4 | 230 | 20.3565 | 20.3535 | 0.003
GEN-2019-037 | 01 NORTH | 657759 | PICKERT4 | 230 | 4.3291 | 4.329 | 0.0001
GEN-2019-037 | 01 NORTH | 657791 | CENTER 3 | 345 | 12.3703 | 12.369 | 0.0013
GEN-2019-037 | 01 NORTH | 657848 | YNG2 4 | 230 | 18.6993 | 18.6972 | 0.0021
GEN-2019-037 | 01 NORTH | 659120 | BROADLND-BE3 | 345 | 4.5977 | 4.597 | 0.0007
GEN-2019-037 | 01 NORTH | 659128 | HERBERTW-KM4 | 230 | 4.8639 | 4.8632 | 0.0007
GEN-2019-037 | 01 NORTH | 659138 | NESET___-BE4 | 230 | 12.8663 | 12.8587 | 0.0076
GEN-2019-037 | 01 NORTH | 659144 | BLAISDEL-BE7 | 115 | 8.9956 | 8.9931 | 0.0025
GEN-2019-037 | 01 NORTH | 659160 | GROTON__-BE3 | 345 | 6.6232 | 6.6219 | 0.0013
GEN-2019-037 | 01 NORTH | 659184 | ROUGHRDR-BE7 | 115 | 4.2092 | 4.2087 | 0.0005
GEN-2019-037 | 01 NORTH | 659185 | FOUREYES-RR7 | 115 | 3.5664 | 3.566 | 0.0004
GEN-2019-037 | 01 NORTH | 659236 | DGC UREA-BE8 | 69 | 7.0553 | 7.0525 | 0.0028
GEN-2019-037 | 01 NORTH | 659300 | STANTN.T-BE7 | 115 | 7.5309 | 7.53 | 0.0009
GEN-2019-037 | 01 NORTH | 659333 | JUDSON__-BE3 | 345 | 8.3923 | 8.3867 | 0.0056
GEN-2019-037 | 01 NORTH | 659365 | BALDWIN_-PP4 | 230 | 6.7552 | 6.7533 | 0.0019
GEN-2019-037 | 01 NORTH | 659388 | KUMMERDG-MK7 | 115 | 13.8646 | 13.8567 | 0.0079
GEN-2019-037 | 01 NORTH | 659433 | TRIPLEH__UA3 | 345 | 6.6721 | 6.6706 | 0.0015
GEN-2019-037 | 01 NORTH | 659466 | PG.KU17A-BE7 | 115 | 17.3028 | 17.2944 | 0.0084
GEN-2019-037 | 01 NORTH | 659467 | PG.KU19A-BE7 | 115 | 17.3139 | 17.3056 | 0.0083
GEN-2019-037 | 01 NORTH | 659543 | PICKCITY-RR7 | 115 | 9.7067 | 9.7049 | 0.0018
GEN-2019-037 | 01 NORTH | 659600 | EFORK_-BE334 | 345 | 7.6977 | 7.6932 | 0.0045
GEN-2019-037 | 01 NORTH | 661084 | TIOGA4 4 | 230 | 12.8663 | 12.8587 | 0.0076
GEN-2019-037 | 01 NORTH | 44568 | J1456 POI | 230 | 5.1844 | 5.1842 | 0.0002
GEN-2019-037 | 01 NORTH | 47543 | J1754 SUB | 230 | 5.7457 | 5.7454 | 0.0003
GEN-2019-037 | 01 NORTH | 588870 | GEN-2017-048 | 230 | 9.6825 | 9.6785 | 0.004
GEN-2019-037 | 01 NORTH | 602006 | SHEYNNE4 | 230 | 11.1365 | 11.1362 | 0.0003
GEN-2019-037 | 01 NORTH | 603022 | SOURIS 7 | 115 | 8.9561 | 8.9547 | 0.0014
GEN-2019-037 | 01 NORTH | 608597 | SQBP1DC4 | 230 | 23.1894 | 23.1858 | 0.0036
GEN-2019-037 | 01 NORTH | 608599 | SQBP2DC4 | 230 | 23.1894 | 23.1858 | 0.0036
GEN-2019-037 | 01 NORTH | 608600 | BISONMP4 | 230 | 7.8057 | 7.8054 | 0.0003
GEN-2019-037 | 01 NORTH | 615347 | GRE-MCHENRY4 | 230 | 7.0405 | 7.0399 | 0.0006
GEN-2019-037 | 01 NORTH | 615348 | GRE-MCHENRY7 | 115 | 8.5387 | 8.538 | 0.0007
GEN-2019-037 | 01 NORTH | 620369 | JAMESTN3 | 345 | 5.6031 | 5.603 | 0.0001
GEN-2019-037 | 01 NORTH | 652400 | WILISTN4 | 230 | 11.1567 | 11.1511 | 0.0056
GEN-2019-037 | 01 NORTH | 652408 | WATFORD7 | 115 | 8.2975 | 8.2962 | 0.0013
GEN-2019-037 | 01 NORTH | 652428 | CARNGTN7 | 115 | 2.5992 | 2.5991 | 0.0001
GEN-2019-037 | 01 NORTH | 652432 | EDGELEY7 | 115 | 3.6857 | 3.6856 | 0.0001
GEN-2019-037 | 01 NORTH | 652436 | FARGO 7 | 115 | 10.9806 | 10.9804 | 0.0002
GEN-2019-037 | 01 NORTH | 652437 | GRNDFKS4 | 230 | 7.5835 | 7.5833 | 0.0002
GEN-2019-037 | 01 NORTH | 652440 | NELSON 7 | 115 | 7.2475 | 7.2464 | 0.0011
GEN-2019-037 | 01 NORTH | 652452 | RUGBY 7 | 115 | 8.0908 | 8.0905 | 0.0003
GEN-2019-037 | 01 NORTH | 652454 | VALLEYC7 | 115 | 3.3812 | 3.3811 | 0.0001
GEN-2019-037 | 01 NORTH | 652464 | DENBIGH TAP7 | 115 | 4.4708 | 4.4706 | 0.0002
GEN-2019-037 | 01 NORTH | 652499 | CAMPBELL 4 | 230 | 3.8434 | 3.8432 | 0.0002
GEN-2019-037 | 01 NORTH | 652506 | FTTHOMP3 | 345 | 10.4278 | 10.4262 | 0.0016
GEN-2019-037 | 01 NORTH | 655641 | BERTHOLD-CP7 | 115 | 6.1489 | 6.1478 | 0.0011
GEN-2019-037 | 01 NORTH | 655647 | WARD -CP7 | 115 | 8.0111 | 8.0102 | 0.0009
GEN-2019-037 | 01 NORTH | 655652 | E.BISMRK-CP7 | 115 | 15.1847 | 15.1815 | 0.0032
GEN-2019-037 | 01 NORTH | 655655 | E.RUTHVL-CP7 | 115 | 6.6648 | 6.6638 | 0.001
GEN-2019-037 | 01 NORTH | 655661 | DOUGLS.C-CP7 | 115 | 3.9206 | 3.9201 | 0.0005
GEN-2019-037 | 01 NORTH | 655693 | WARD_SPR-CP7 | 115 | 2.9928 | 2.9926 | 0.0002
GEN-2019-037 | 01 NORTH | 655748 | NEWSALEM-MG7 | 115 | 1.4422 | 1.4419 | 0.0003
GEN-2019-037 | 01 NORTH | 655749 | MANSWTCH-MG7 | 115 | 0.9748 | 0.9746 | 0.0002
GEN-2019-037 | 01 NORTH | 655834 | GRASSYBT-MK7 | 115 | 6.6236 | 6.622 | 0.0016
GEN-2019-037 | 01 NORTH | 655835 | LITTLKNF-MK7 | 115 | 2.981 | 2.9806 | 0.0004
GEN-2019-037 | 01 NORTH | 655836 | OAKDALE -MK7 | 115 | 5.2967 | 5.2953 | 0.0014
GEN-2019-037 | 01 NORTH | 655849 | VEEDER -MK7 | 115 | 9.376 | 9.3723 | 0.0037
GEN-2019-037 | 01 NORTH | 655873 | BBCOMPTP-MK7 | 115 | 6.6385 | 6.6367 | 0.0018
GEN-2019-037 | 01 NORTH | 655881 | DAP_____-MK7 | 115 | 12.4963 | 12.4899 | 0.0064
GEN-2019-037 | 01 NORTH | 655882 | GALAXYTP-MK7 | 115 | 9.4233 | 9.4196 | 0.0037
GEN-2019-037 | 01 NORTH | 655891 | KILLDEER-MK7 | 115 | 4.6672 | 4.6666 | 0.0006
GEN-2019-037 | 01 NORTH | 655894 | HALLIDAY-MK7 | 115 | 3.3862 | 3.3856 | 0.0006
GEN-2019-037 | 01 NORTH | 655899 | FNCYBTAP-MK7 | 115 | 6.1012 | 6.0997 | 0.0015
GEN-2019-037 | 01 NORTH | 655901 | BROOKBNK-MW7 | 115 | 10.5326 | 10.5304 | 0.0022
GEN-2019-037 | 01 NORTH | 655912 | AUSTIN -MW7 | 115 | 6.4179 | 6.4166 | 0.0013
GEN-2019-037 | 01 NORTH | 655916 | PALERMO -MW7 | 115 | 7.1022 | 7.1006 | 0.0016
GEN-2019-037 | 01 NORTH | 655917 | STANLEY -MW7 | 115 | 6.8701 | 6.8686 | 0.0015
GEN-2019-037 | 01 NORTH | 655944 | PLAZA -MW7 | 115 | 6.6947 | 6.6929 | 0.0018
GEN-2019-037 | 01 NORTH | 655949 | BLAISDEL-MW7 | 115 | 8.6932 | 8.6908 | 0.0024
GEN-2019-037 | 01 NORTH | 655957 | EASTFORK-MW7 | 115 | 15.8907 | 15.8857 | 0.005
GEN-2019-037 | 01 NORTH | 655960 | BIGBEND -MW7 | 115 | 5.2991 | 5.2979 | 0.0012
GEN-2019-037 | 01 NORTH | 655967 | SATTER -MW7 | 115 | 9.2228 | 9.2201 | 0.0027
GEN-2019-037 | 01 NORTH | 657741 | ROUGHRIDER 4 | 230 | 15.5165 | 15.5141 | 0.0024
GEN-2019-037 | 01 NORTH | 657923 | PICKERT8 | 69 | 3.1341 | 3.1341 | 0
GEN-2019-037 | 01 NORTH | 657951 | CNTSHNT3 | 345 | 12.3703 | 12.369 | 0.0013
GEN-2019-037 | 01 NORTH | 658209 | MOORHDW4 | 230 | 6.9412 | 6.9411 | 0.0001
GEN-2019-037 | 01 NORTH | 659124 | DICKINSN-BE4 | 230 | 6.9327 | 6.9313 | 0.0014
GEN-2019-037 | 01 NORTH | 659139 | NESET___-BE7 | 115 | 13.106 | 13.1027 | 0.0033
GEN-2019-037 | 01 NORTH | 659140 | NRTSHORE-BE4 | 230 | 5.8229 | 5.8216 | 0.0013
GEN-2019-037 | 01 NORTH | 659165 | CROCKER_-BE3 | 345 | 6.5153 | 6.5145 | 0.0008
GEN-2019-037 | 01 NORTH | 659181 | BICNTNIL-BE7 | 115 | 3.272 | 3.2718 | 0.0002
GEN-2019-037 | 01 NORTH | 659187 | GROTON__-BE7 | 115 | 19.0821 | 19.0795 | 0.0026
GEN-2019-037 | 01 NORTH | 659198 | GROTON__-BE8 | 115 | 10.114 | 10.113 | 0.001
GEN-2019-037 | 01 NORTH | 659205 | BROADLND-BE4 | 230 | 10.0163 | 10.015 | 0.0013
GEN-2019-037 | 01 NORTH | 659247 | MEDORA__-UM4 | 230 | 5.2368 | 5.236 | 0.0008
GEN-2019-037 | 01 NORTH | 659248 | HALLIDAY-UM7 | 115 | 3.9641 | 3.9638 | 0.0003
GEN-2019-037 | 01 NORTH | 659284 | ECKLUND_-PP4 | 230 | 6.7552 | 6.7533 | 0.0019
GEN-2019-037 | 01 NORTH | 659309 | S.HEART_-RR4 | 230 | 9.3261 | 9.3228 | 0.0033
GEN-2019-037 | 01 NORTH | 659334 | JUDSON__-BE4 | 230 | 11.0806 | 11.0749 | 0.0057
GEN-2019-037 | 01 NORTH | 659362 | WHEELOCK-BE4 | 230 | 7.5903 | 7.5877 | 0.0026
GEN-2019-037 | 01 NORTH | 659391 | PATENTGT-MK7 | 115 | 17.3966 | 17.3882 | 0.0084
GEN-2019-037 | 01 NORTH | 659448 | DAGLUM__-BE4 | 230 | 6.3542 | 6.353 | 0.0012
GEN-2019-037 | 01 NORTH | 659584 | BEPCPRXCC3 7 | 115 | 13.6262 | 13.6186 | 0.0076
GEN-2019-037 | 01 NORTH | 661003 | WATFRDSOUTH4 | 230 | 6.4853 | 6.4832 | 0.0021
GEN-2019-037 | 01 NORTH | 661011 | BEULAH27 | 115 | 9.0606 | 9.0597 | 0.0009
GEN-2019-037 | 01 NORTH | 661016 | COYOTE 3 | 345 | 8.2674 | 8.2669 | 0.0005
GEN-2019-037 | 01 NORTH | 661029 | ESTBMRK7 | 115 | 15.612 | 15.6087 | 0.0033
GEN-2019-037 | 01 NORTH | 661053 | MANDAN 4 | 230 | 15.7601 | 15.7553 | 0.0048
GEN-2019-037 | 01 NORTH | 661085 | TIOGA4 7 | 115 | 13.0515 | 13.0482 | 0.0033
GEN-2019-037 | 01 NORTH | 672603 | BDV 4 | 230 | 4.8118 | 4.8115 | 0.0003
GEN-2018-065 | 02 NEBRASKA | 640520 | ANTELOPE 3 | 345 | 6.9888 | 6.9518 | 0.037
GEN-2018-065 | 02 NEBRASKA | 640226 | HOSKINS3 | 345 | 13.0113 | 12.9851 | 0.0262
GEN-2018-065 | 02 NEBRASKA | 640521 | ANTELOPE 7 | 115 | 14.1104 | 14.0826 | 0.0278
GEN-2018-065 | 02 NEBRASKA | 763032 | GEN-2018-068 | 345 | 5.9447 | 5.906 | 0.0387
GEN-2018-065 | 02 NEBRASKA | 763439 | GEN-2018-131 | 345 | 6.9826 | 6.9457 | 0.0369
GEN-2018-065 | 02 NEBRASKA | 635200 | RAUN 3 | 345 | 27.0138 | 27.0091 | 0.0047
GEN-2018-065 | 02 NEBRASKA | 640115 | CO.LINE7 | 115 | 7.2295 | 7.2242 | 0.0053
GEN-2018-065 | 02 NEBRASKA | 640149 | CREITON7 | 115 | 4.7116 | 4.7101 | 0.0015
GEN-2018-065 | 02 NEBRASKA | 640227 | HOSKINS4 | 230 | 10.0896 | 10.082 | 0.0076
GEN-2018-065 | 02 NEBRASKA | 640228 | HOSKINS7 | 115 | 18.0994 | 18.0856 | 0.0138
GEN-2018-065 | 02 NEBRASKA | 640293 | NELIGH 7 | 115 | 9.9449 | 9.934 | 0.0109
GEN-2018-065 | 02 NEBRASKA | 640522 | ANTELOPE 8 | 69 | 5.119 | 5.1168 | 0.0022
GEN-2018-065 | 02 NEBRASKA | 640588 | TURTLE.CRK 3 | 345 | 11.1479 | 11.1298 | 0.0181
GEN-2018-065 | 02 NEBRASKA | 643254 | UPSTREAM.W 7 | 115 | 13.3751 | 13.3504 | 0.0247
GEN-2018-065 | 02 NEBRASKA | 763450 | GEN-2018-132 | 345 | 6.6695 | 6.6358 | 0.0337
GEN-2018-065 | 02 NEBRASKA | 763982 | G19-069-TAP | 345 | 11.2849 | 11.2711 | 0.0138
GEN-2018-065 | 02 NEBRASKA | 87487 | J748POI | 345 | 15.0615 | 15.0608 | 0.0007
GEN-2018-065 | 02 NEBRASKA | 635201 | RAUN 5 | 161 | 27.0927 | 27.0908 | 0.0019
GEN-2018-065 | 02 NEBRASKA | 635252 | J412 POI 3 | 345 | 9.6628 | 9.6626 | 0.0002
GEN-2018-065 | 02 NEBRASKA | 635398 | REMSEN 3 | 345 | 14.4843 | 14.4837 | 0.0006
GEN-2018-065 | 02 NEBRASKA | 640072 | BATTLCR7 | 115 | 7.3087 | 7.3049 | 0.0038
GEN-2018-065 | 02 NEBRASKA | 640080 | BELDEN 7 | 115 | 5.9733 | 5.9727 | 0.0006
GEN-2018-065 | 02 NEBRASKA | 640084 | BLMFLD 7 | 115 | 5.1275 | 5.1269 | 0.0006
GEN-2018-065 | 02 NEBRASKA | 640113 | CLRWATR7 | 115 | 5.1516 | 5.1494 | 0.0022
GEN-2018-065 | 02 NEBRASKA | 640150 | CREITON8 | 69 | 4.3586 | 4.3578 | 0.0008
GEN-2018-065 | 02 NEBRASKA | 640294 | NELIGH 8 | 69 | 5.8977 | 5.8954 | 0.0023
GEN-2018-065 | 02 NEBRASKA | 640296 | NORFK.N7 | 115 | 13.1793 | 13.1713 | 0.008
GEN-2018-065 | 02 NEBRASKA | 640298 | NORFOLK7 | 115 | 12.385 | 12.3785 | 0.0065
GEN-2018-065 | 02 NEBRASKA | 640342 | SHELCRK3 | 345 | 10.533 | 10.5269 | 0.0061
GEN-2018-065 | 02 NEBRASKA | 640363 | STNTN.N7 | 115 | 6.977 | 6.9753 | 0.0017
GEN-2018-065 | 02 NEBRASKA | 640444 | PETERSBRG.N7 | 115 | 5.4317 | 5.4303 | 0.0014
GEN-2018-065 | 02 NEBRASKA | 640560 | WAKEFIELD 4 | 230 | 7.9675 | 7.9661 | 0.0014
GEN-2018-065 | 02 NEBRASKA | 640589 | SHOLES.W 3 | 345 | 9.0182 | 9.0067 | 0.0115
GEN-2018-065 | 02 NEBRASKA | 640598 | HAYSTACK.WD3 | 345 | 8.6554 | 8.6452 | 0.0102
GEN-2018-065 | 02 NEBRASKA | 643271 | PLUMBCR.W 3 | 345 | 10.8968 | 10.8795 | 0.0173
GEN-2018-065 | 02 NEBRASKA | 652564 | SIOUXCY3 | 345 | 15.3816 | 15.3804 | 0.0012
GEN-2018-065 | 02 NEBRASKA | 762779 | G18-043-TAP | 345 | 15.621 | 15.6206 | 0.0004
GEN-2018-065 | 02 NEBRASKA | 763142 | GEN-2018-083 | 345 | 2.1648 | 2.1645 | 0.0003
GEN-2018-065 | 02 NEBRASKA | 763978 | GEN-2019-069 | 345 | 11.2497 | 11.236 | 0.0137
GEN-2018-065 | 02 NEBRASKA | 45906 | J1590 SUB | 345 | 14.2602 | 14.2595 | 0.0007
GEN-2018-065 | 02 NEBRASKA | 87486 | J748GENTIE | 345 | 13.2728 | 13.2722 | 0.0006
GEN-2018-065 | 02 NEBRASKA | 635202 | NEAL S 5 | 161 | 22.3496 | 22.3483 | 0.0013
GEN-2018-065 | 02 NEBRASKA | 635203 | NEAL N 5 | 161 | 25.6073 | 25.6056 | 0.0017
GEN-2018-065 | 02 NEBRASKA | 635206 | IDA CO 3 | 345 | 9.3103 | 9.3101 | 0.0002
GEN-2018-065 | 02 NEBRASKA | 635220 | INTCHG 5 | 161 | 14.526 | 14.5254 | 0.0006
GEN-2018-065 | 02 NEBRASKA | 635230 | LIBERTY5 | 161 | 24.9266 | 24.925 | 0.0016
GEN-2018-065 | 02 NEBRASKA | 635399 | CHEROKEE 3 | 345 | 15.9186 | 15.9178 | 0.0008
GEN-2018-065 | 02 NEBRASKA | 640073 | BATTLCR8 | 69 | 3.8906 | 3.8899 | 0.0007
GEN-2018-065 | 02 NEBRASKA | 640081 | BELDEN 8 | 69 | 3.6996 | 3.6995 | 0.0001
GEN-2018-065 | 02 NEBRASKA | 640085 | BLMFLD 8 | 69 | 3.7238 | 3.7236 | 0.0002
GEN-2018-065 | 02 NEBRASKA | 640125 | COLMB.E3 | 345 | 10.209 | 10.2046 | 0.0044
GEN-2018-065 | 02 NEBRASKA | 640212 | HARTGTN7 | 115 | 5.1832 | 5.1828 | 0.0004
GEN-2018-065 | 02 NEBRASKA | 640263 | MADISON7 | 115 | 6.1678 | 6.1667 | 0.0011
GEN-2018-065 | 02 NEBRASKA | 640305 | ONEILL 7 | 115 | 3.9336 | 3.9333 | 0.0003
GEN-2018-065 | 02 NEBRASKA | 640318 | PETRSBG7 | 115 | 5.4269 | 5.4255 | 0.0014
GEN-2018-065 | 02 NEBRASKA | 640343 | SHELCRK4 | 230 | 10.8729 | 10.8703 | 0.0026
GEN-2018-065 | 02 NEBRASKA | 640357 | STANTON7 | 115 | 5.115 | 5.1143 | 0.0007
GEN-2018-065 | 02 NEBRASKA | 640386 | TWIN CH4 | 230 | 8.9225 | 8.9215 | 0.001
GEN-2018-065 | 02 NEBRASKA | 640387 | TWIN CH7 | 115 | 10.7822 | 10.7814 | 0.0008
GEN-2018-065 | 02 NEBRASKA | 640561 | RTLSNAKE.W 4 | 230 | 7.1132 | 7.1122 | 0.001
GEN-2018-065 | 02 NEBRASKA | 645451 | S3451 3 | 345 | 21.3318 | 21.3313 | 0.0005
GEN-2018-065 | 02 NEBRASKA | 652511 | GAVINS 7 | 115 | 8.4307 | 8.43 | 0.0007
GEN-2018-065 | 02 NEBRASKA | 652552 | SIOUXCY2 | 230 | 20.341 | 20.3393 | 0.0017
GEN-2018-065 | 02 NEBRASKA | 652864 | SIOUXCY-LNX3 | 345 | 15.1969 | 15.1957 | 0.0012
GEN-2018-065 | 02 NEBRASKA | 760788 | GEN-2017-201 | 345 | 8.2239 | 8.2145 | 0.0094
GEN-2018-065 | 02 NEBRASKA | 762069 | G17-105TAP | 161 | 8.3472 | 8.3471 | 0.0001
GEN-2018-065 | 02 NEBRASKA | 762780 | GEN-2018-043 | 345 | 12.7205 | 12.7202 | 0.0003
GEN-2018-065 | 02 NEBRASKA | 601006 | SPLT RK3 | 345 | 14.9416 | 14.9414 | 0.0002
GEN-2018-065 | 02 NEBRASKA | 635204 | NEAL N 8 | 69 | 9.7689 | 9.7688 | 0.0001
GEN-2018-065 | 02 NEBRASKA | 635219 | GARD AVE 3 | 345 | 8.9677 | 8.9675 | 0.0002
GEN-2018-065 | 02 NEBRASKA | 635221 | KELLOGG5 | 161 | 17.1226 | 17.1219 | 0.0007
GEN-2018-065 | 02 NEBRASKA | 635229 | AIRPORT 5 | 161 | 16.9835 | 16.9828 | 0.0007
GEN-2018-065 | 02 NEBRASKA | 635235 | SALIX 5 | 161 | 14.6126 | 14.6121 | 0.0005
GEN-2018-065 | 02 NEBRASKA | 635300 | MONONA 5 | 161 | 5.4609 | 5.4609 | 0
GEN-2018-065 | 02 NEBRASKA | 635400 | HIGHLND 3 | 345 | 14.5121 | 14.5118 | 0.0003
GEN-2018-065 | 02 NEBRASKA | 637009 | GLACIAL EDGE | 345 | 15.6443 | 15.6436 | 0.0007
GEN-2018-065 | 02 NEBRASKA | 640054 | ALBION 7 | 115 | 5.1766 | 5.1758 | 0.0008
GEN-2018-065 | 02 NEBRASKA | 640078 | BEEMER 7 | 115 | 4.396 | 4.3957 | 0.0003
GEN-2018-065 | 02 NEBRASKA | 640127 | COLMB.E7 | 115 | 22.1185 | 22.1138 | 0.0047
GEN-2018-065 | 02 NEBRASKA | 640133 | COLMBUS4 | 230 | 11.4877 | 11.4851 | 0.0026
GEN-2018-065 | 02 NEBRASKA | 640151 | CRESTON7 | 115 | 5.9927 | 5.9919 | 0.0008
GEN-2018-065 | 02 NEBRASKA | 640163 | EMERSON7 | 115 | 5.4485 | 5.4483 | 0.0002
GEN-2018-065 | 02 NEBRASKA | 640213 | HARTGTN8 | 69 | 3.4988 | 3.4987 | 0.0001
GEN-2018-065 | 02 NEBRASKA | 640306 | ONEILL 8 | 69 | 4.2323 | 4.2321 | 0.0002
GEN-2018-065 | 02 NEBRASKA | 640349 | SPENCER7 | 115 | 4.7744 | 4.7742 | 0.0002
GEN-2018-065 | 02 NEBRASKA | 640377 | TEKAMAH5 | 161 | 8.8894 | 8.8893 | 0.0001
GEN-2018-065 | 02 NEBRASKA | 640388 | TWIN CH8 | 69 | 7.7842 | 7.7839 | 0.0003
GEN-2018-065 | 02 NEBRASKA | 640424 | S.SIOUXCITY7 | 115 | 7.3706 | 7.3702 | 0.0004
GEN-2018-065 | 02 NEBRASKA | 640465 | EAGLECREEK 7 | 115 | 3.0176 | 3.0174 | 0.0002
GEN-2018-065 | 02 NEBRASKA | 645454 | S3454 3 | 345 | 27.4247 | 27.4242 | 0.0005
GEN-2018-065 | 02 NEBRASKA | 645459 | S3459 3 | 345 | 24.0005 | 24.0001 | 0.0004
GEN-2018-065 | 02 NEBRASKA | 646251 | S1251 5 | 161 | 30.7514 | 30.751 | 0.0004
GEN-2018-065 | 02 NEBRASKA | 650114 | NW68HOLDRG3 | 345 | 16.8066 | 16.8054 | 0.0012
GEN-2018-065 | 02 NEBRASKA | 652565 | SIOUXCY4 | 230 | 20.341 | 20.3393 | 0.0017
GEN-2018-065 | 02 NEBRASKA | 659121 | SPIRIT_M-BE7 | 115 | 5.9966 | 5.9965 | 0.0001
GEN-2018-065 | 02 NEBRASKA | 659900 | EAGLE___-NI4 | 230 | 7.3012 | 7.3011 | 0.0001
GEN-2018-065 | 02 NEBRASKA | 660006 | YANKTON JCT7 | 115 | 7.9557 | 7.9553 | 0.0004
GEN-2018-065 | 02 NEBRASKA | 762070 | GEN-2017-105 | 161 | 8.3472 | 8.3471 | 0.0001
GEN-2018-065 | 02 NEBRASKA | 762603 | GEN-2018-025 | 345 | 20.4121 | 20.4116 | 0.0005
GEN-2018-068 | 02 NEBRASKA | 640520 | ANTELOPE 3 | 345 | 6.9888 | 6.4396 | 0.5492
GEN-2018-068 | 02 NEBRASKA | 640226 | HOSKINS3 | 345 | 13.0113 | 12.6032 | 0.4081
GEN-2018-068 | 02 NEBRASKA | 640521 | ANTELOPE 7 | 115 | 14.1104 | 13.6791 | 0.4313
GEN-2018-068 | 02 NEBRASKA | 763032 | GEN-2018-068 | 345 | 5.9447 | 5.3793 | 0.5654
GEN-2018-068 | 02 NEBRASKA | 763439 | GEN-2018-131 | 345 | 6.9826 | 6.4344 | 0.5482
GEN-2018-068 | 02 NEBRASKA | 635200 | RAUN 3 | 345 | 27.0138 | 26.9391 | 0.0747
GEN-2018-068 | 02 NEBRASKA | 640115 | CO.LINE7 | 115 | 7.2295 | 7.1454 | 0.0841
GEN-2018-068 | 02 NEBRASKA | 640149 | CREITON7 | 115 | 4.7116 | 4.6871 | 0.0245
GEN-2018-068 | 02 NEBRASKA | 640227 | HOSKINS4 | 230 | 10.0896 | 9.9701 | 0.1195
GEN-2018-068 | 02 NEBRASKA | 640228 | HOSKINS7 | 115 | 18.0994 | 17.8808 | 0.2186
GEN-2018-068 | 02 NEBRASKA | 640293 | NELIGH 7 | 115 | 9.9449 | 9.7721 | 0.1728
GEN-2018-068 | 02 NEBRASKA | 640522 | ANTELOPE 8 | 69 | 5.119 | 5.0845 | 0.0345
GEN-2018-068 | 02 NEBRASKA | 640588 | TURTLE.CRK 3 | 345 | 11.1479 | 10.8645 | 0.2834
GEN-2018-068 | 02 NEBRASKA | 643254 | UPSTREAM.W 7 | 115 | 13.3751 | 12.9909 | 0.3842
GEN-2018-068 | 02 NEBRASKA | 763450 | GEN-2018-132 | 345 | 6.6695 | 6.1675 | 0.502
GEN-2018-068 | 02 NEBRASKA | 763982 | G19-069-TAP | 345 | 11.2849 | 11.0674 | 0.2175
GEN-2018-068 | 02 NEBRASKA | 87487 | J748POI | 345 | 15.0615 | 15.0505 | 0.011
GEN-2018-068 | 02 NEBRASKA | 635201 | RAUN 5 | 161 | 27.0927 | 27.0623 | 0.0304
GEN-2018-068 | 02 NEBRASKA | 635252 | J412 POI 3 | 345 | 9.6628 | 9.6586 | 0.0042
GEN-2018-068 | 02 NEBRASKA | 635398 | REMSEN 3 | 345 | 14.4843 | 14.4735 | 0.0108
GEN-2018-068 | 02 NEBRASKA | 640072 | BATTLCR7 | 115 | 7.3087 | 7.2489 | 0.0598
GEN-2018-068 | 02 NEBRASKA | 640080 | BELDEN 7 | 115 | 5.9733 | 5.9631 | 0.0102
GEN-2018-068 | 02 NEBRASKA | 640084 | BLMFLD 7 | 115 | 5.1275 | 5.1168 | 0.0107
GEN-2018-068 | 02 NEBRASKA | 640113 | CLRWATR7 | 115 | 5.1516 | 5.1169 | 0.0347
GEN-2018-068 | 02 NEBRASKA | 640150 | CREITON8 | 69 | 4.3586 | 4.3461 | 0.0125
GEN-2018-068 | 02 NEBRASKA | 640294 | NELIGH 8 | 69 | 5.8977 | 5.8613 | 0.0364
GEN-2018-068 | 02 NEBRASKA | 640296 | NORFK.N7 | 115 | 13.1793 | 13.0524 | 0.1269
GEN-2018-068 | 02 NEBRASKA | 640298 | NORFOLK7 | 115 | 12.385 | 12.2825 | 0.1025
GEN-2018-068 | 02 NEBRASKA | 640342 | SHELCRK3 | 345 | 10.533 | 10.4362 | 0.0968
GEN-2018-068 | 02 NEBRASKA | 640363 | STNTN.N7 | 115 | 6.977 | 6.9507 | 0.0263
GEN-2018-068 | 02 NEBRASKA | 640444 | PETERSBRG.N7 | 115 | 5.4317 | 5.4087 | 0.023
GEN-2018-068 | 02 NEBRASKA | 640560 | WAKEFIELD 4 | 230 | 7.9675 | 7.944 | 0.0235
GEN-2018-068 | 02 NEBRASKA | 640589 | SHOLES.W 3 | 345 | 9.0182 | 8.8381 | 0.1801
GEN-2018-068 | 02 NEBRASKA | 640598 | HAYSTACK.WD3 | 345 | 8.6554 | 8.4949 | 0.1605
GEN-2018-068 | 02 NEBRASKA | 643271 | PLUMBCR.W 3 | 345 | 10.8968 | 10.6258 | 0.271
GEN-2018-068 | 02 NEBRASKA | 652564 | SIOUXCY3 | 345 | 15.3816 | 15.3619 | 0.0197
GEN-2018-068 | 02 NEBRASKA | 762779 | G18-043-TAP | 345 | 15.621 | 15.6142 | 0.0068
GEN-2018-068 | 02 NEBRASKA | 763142 | GEN-2018-083 | 345 | 2.1648 | 2.1596 | 0.0052
GEN-2018-068 | 02 NEBRASKA | 763978 | GEN-2019-069 | 345 | 11.2497 | 11.0336 | 0.2161
GEN-2018-068 | 02 NEBRASKA | 45906 | J1590 SUB | 345 | 14.2602 | 14.2497 | 0.0105
GEN-2018-068 | 02 NEBRASKA | 87486 | J748GENTIE | 345 | 13.2728 | 13.2643 | 0.0085
GEN-2018-068 | 02 NEBRASKA | 635202 | NEAL S 5 | 161 | 22.3496 | 22.3296 | 0.02
GEN-2018-068 | 02 NEBRASKA | 635203 | NEAL N 5 | 161 | 25.6073 | 25.5802 | 0.0271
GEN-2018-068 | 02 NEBRASKA | 635206 | IDA CO 3 | 345 | 9.3103 | 9.3069 | 0.0034
GEN-2018-068 | 02 NEBRASKA | 635220 | INTCHG 5 | 161 | 14.526 | 14.5175 | 0.0085
GEN-2018-068 | 02 NEBRASKA | 635230 | LIBERTY5 | 161 | 24.9266 | 24.9009 | 0.0257
GEN-2018-068 | 02 NEBRASKA | 635399 | CHEROKEE 3 | 345 | 15.9186 | 15.907 | 0.0116
GEN-2018-068 | 02 NEBRASKA | 640073 | BATTLCR8 | 69 | 3.8906 | 3.8804 | 0.0102
GEN-2018-068 | 02 NEBRASKA | 640081 | BELDEN 8 | 69 | 3.6996 | 3.6972 | 0.0024
GEN-2018-068 | 02 NEBRASKA | 640085 | BLMFLD 8 | 69 | 3.7238 | 3.7204 | 0.0034
GEN-2018-068 | 02 NEBRASKA | 640125 | COLMB.E3 | 345 | 10.209 | 10.1392 | 0.0698
GEN-2018-068 | 02 NEBRASKA | 640212 | HARTGTN7 | 115 | 5.1832 | 5.177 | 0.0062
GEN-2018-068 | 02 NEBRASKA | 640263 | MADISON7 | 115 | 6.1678 | 6.1505 | 0.0173
GEN-2018-068 | 02 NEBRASKA | 640305 | ONEILL 7 | 115 | 3.9336 | 3.9278 | 0.0058
GEN-2018-068 | 02 NEBRASKA | 640318 | PETRSBG7 | 115 | 5.4269 | 5.404 | 0.0229
GEN-2018-068 | 02 NEBRASKA | 640343 | SHELCRK4 | 230 | 10.8729 | 10.8305 | 0.0424
GEN-2018-068 | 02 NEBRASKA | 640357 | STANTON7 | 115 | 5.115 | 5.1038 | 0.0112
GEN-2018-068 | 02 NEBRASKA | 640386 | TWIN CH4 | 230 | 8.9225 | 8.9058 | 0.0167
GEN-2018-068 | 02 NEBRASKA | 640387 | TWIN CH7 | 115 | 10.7822 | 10.7686 | 0.0136
GEN-2018-068 | 02 NEBRASKA | 640561 | RTLSNAKE.W 4 | 230 | 7.1132 | 7.0963 | 0.0169
GEN-2018-068 | 02 NEBRASKA | 645451 | S3451 3 | 345 | 21.3318 | 21.324 | 0.0078
GEN-2018-068 | 02 NEBRASKA | 652511 | GAVINS 7 | 115 | 8.4307 | 8.4203 | 0.0104
GEN-2018-068 | 02 NEBRASKA | 652552 | SIOUXCY2 | 230 | 20.341 | 20.3147 | 0.0263
GEN-2018-068 | 02 NEBRASKA | 652864 | SIOUXCY-LNX3 | 345 | 15.1969 | 15.1777 | 0.0192
GEN-2018-068 | 02 NEBRASKA | 760788 | GEN-2017-201 | 345 | 8.2239 | 8.0755 | 0.1484
GEN-2018-068 | 02 NEBRASKA | 762069 | G17-105TAP | 161 | 8.3472 | 8.3447 | 0.0025
GEN-2018-068 | 02 NEBRASKA | 762780 | GEN-2018-043 | 345 | 12.7205 | 12.7162 | 0.0043
GEN-2018-068 | 02 NEBRASKA | 601006 | SPLT RK3 | 345 | 14.9416 | 14.9388 | 0.0028
GEN-2018-068 | 02 NEBRASKA | 635204 | NEAL N 8 | 69 | 9.7689 | 9.7672 | 0.0017
GEN-2018-068 | 02 NEBRASKA | 635219 | GARD AVE 3 | 345 | 8.9677 | 8.965 | 0.0027
GEN-2018-068 | 02 NEBRASKA | 635221 | KELLOGG5 | 161 | 17.1226 | 17.111 | 0.0116
GEN-2018-068 | 02 NEBRASKA | 635229 | AIRPORT 5 | 161 | 16.9835 | 16.9719 | 0.0116
GEN-2018-068 | 02 NEBRASKA | 635235 | SALIX 5 | 161 | 14.6126 | 14.6043 | 0.0083
GEN-2018-068 | 02 NEBRASKA | 635300 | MONONA 5 | 161 | 5.4609 | 5.4604 | 0.0005
GEN-2018-068 | 02 NEBRASKA | 635400 | HIGHLND 3 | 345 | 14.5121 | 14.5066 | 0.0055
GEN-2018-068 | 02 NEBRASKA | 637009 | GLACIAL EDGE | 345 | 15.6443 | 15.6331 | 0.0112
GEN-2018-068 | 02 NEBRASKA | 640054 | ALBION 7 | 115 | 5.1766 | 5.1643 | 0.0123
GEN-2018-068 | 02 NEBRASKA | 640078 | BEEMER 7 | 115 | 4.396 | 4.3916 | 0.0044
GEN-2018-068 | 02 NEBRASKA | 640127 | COLMB.E7 | 115 | 22.1185 | 22.0426 | 0.0759
GEN-2018-068 | 02 NEBRASKA | 640133 | COLMBUS4 | 230 | 11.4877 | 11.4471 | 0.0406
GEN-2018-068 | 02 NEBRASKA | 640151 | CRESTON7 | 115 | 5.9927 | 5.9797 | 0.013
GEN-2018-068 | 02 NEBRASKA | 640163 | EMERSON7 | 115 | 5.4485 | 5.4453 | 0.0032
GEN-2018-068 | 02 NEBRASKA | 640213 | HARTGTN8 | 69 | 3.4988 | 3.4971 | 0.0017
GEN-2018-068 | 02 NEBRASKA | 640306 | ONEILL 8 | 69 | 4.2323 | 4.2282 | 0.0041
GEN-2018-068 | 02 NEBRASKA | 640349 | SPENCER7 | 115 | 4.7744 | 4.7717 | 0.0027
GEN-2018-068 | 02 NEBRASKA | 640377 | TEKAMAH5 | 161 | 8.8894 | 8.8866 | 0.0028
GEN-2018-068 | 02 NEBRASKA | 640388 | TWIN CH8 | 69 | 7.7842 | 7.7799 | 0.0043
GEN-2018-068 | 02 NEBRASKA | 640424 | S.SIOUXCITY7 | 115 | 7.3706 | 7.3642 | 0.0064
GEN-2018-068 | 02 NEBRASKA | 640465 | EAGLECREEK 7 | 115 | 3.0176 | 3.0149 | 0.0027
GEN-2018-068 | 02 NEBRASKA | 645454 | S3454 3 | 345 | 27.4247 | 27.416 | 0.0087
GEN-2018-068 | 02 NEBRASKA | 645459 | S3459 3 | 345 | 24.0005 | 23.9945 | 0.006
GEN-2018-068 | 02 NEBRASKA | 646251 | S1251 5 | 161 | 30.7514 | 30.7438 | 0.0076
GEN-2018-068 | 02 NEBRASKA | 650114 | NW68HOLDRG3 | 345 | 16.8066 | 16.7873 | 0.0193
GEN-2018-068 | 02 NEBRASKA | 652565 | SIOUXCY4 | 230 | 20.341 | 20.3147 | 0.0263
GEN-2018-068 | 02 NEBRASKA | 659121 | SPIRIT_M-BE7 | 115 | 5.9966 | 5.9956 | 0.001
GEN-2018-068 | 02 NEBRASKA | 659900 | EAGLE___-NI4 | 230 | 7.3012 | 7.2993 | 0.0019
GEN-2018-068 | 02 NEBRASKA | 660006 | YANKTON JCT7 | 115 | 7.9557 | 7.949 | 0.0067
GEN-2018-068 | 02 NEBRASKA | 762070 | GEN-2017-105 | 161 | 8.3472 | 8.3447 | 0.0025
GEN-2018-068 | 02 NEBRASKA | 762603 | GEN-2018-025 | 345 | 20.4121 | 20.4049 | 0.0072
GEN-2018-083 | 02 NEBRASKA | 763982 | G19-069-TAP | 345 | 11.2849 | 10.8886 | 0.3963
GEN-2018-083 | 02 NEBRASKA | 640226 | HOSKINS3 | 345 | 13.0113 | 12.733 | 0.2783
GEN-2018-083 | 02 NEBRASKA | 640342 | SHELCRK3 | 345 | 10.533 | 10.3664 | 0.1666
GEN-2018-083 | 02 NEBRASKA | 763142 | GEN-2018-083 | 345 | 2.1648 | 1.6704 | 0.4944
GEN-2018-083 | 02 NEBRASKA | 763978 | GEN-2019-069 | 345 | 11.2497 | 10.856 | 0.3937
GEN-2018-083 | 02 NEBRASKA | 635200 | RAUN 3 | 345 | 27.0138 | 26.9631 | 0.0507
GEN-2018-083 | 02 NEBRASKA | 640125 | COLMB.E3 | 345 | 10.209 | 10.0915 | 0.1175
GEN-2018-083 | 02 NEBRASKA | 640227 | HOSKINS4 | 230 | 10.0896 | 10.0126 | 0.077
GEN-2018-083 | 02 NEBRASKA | 640228 | HOSKINS7 | 115 | 18.0994 | 17.9754 | 0.124
GEN-2018-083 | 02 NEBRASKA | 640343 | SHELCRK4 | 230 | 10.8729 | 10.8068 | 0.0661
GEN-2018-083 | 02 NEBRASKA | 640520 | ANTELOPE 3 | 345 | 6.9888 | 6.9306 | 0.0582
GEN-2018-083 | 02 NEBRASKA | 640588 | TURTLE.CRK 3 | 345 | 11.1479 | 10.9551 | 0.1928
GEN-2018-083 | 02 NEBRASKA | 87487 | J748POI | 345 | 15.0615 | 15.0541 | 0.0074
GEN-2018-083 | 02 NEBRASKA | 635201 | RAUN 5 | 161 | 27.0927 | 27.0723 | 0.0204
GEN-2018-083 | 02 NEBRASKA | 635252 | J412 POI 3 | 345 | 9.6628 | 9.6599 | 0.0029
GEN-2018-083 | 02 NEBRASKA | 635398 | REMSEN 3 | 345 | 14.4843 | 14.477 | 0.0073
GEN-2018-083 | 02 NEBRASKA | 640080 | BELDEN 7 | 115 | 5.9733 | 5.9684 | 0.0049
GEN-2018-083 | 02 NEBRASKA | 640127 | COLMB.E7 | 115 | 22.1185 | 22.0141 | 0.1044
GEN-2018-083 | 02 NEBRASKA | 640133 | COLMBUS4 | 230 | 11.4877 | 11.427 | 0.0607
GEN-2018-083 | 02 NEBRASKA | 640296 | NORFK.N7 | 115 | 13.1793 | 13.1157 | 0.0636
GEN-2018-083 | 02 NEBRASKA | 640298 | NORFOLK7 | 115 | 12.385 | 12.3294 | 0.0556
GEN-2018-083 | 02 NEBRASKA | 640363 | STNTN.N7 | 115 | 6.977 | 6.962 | 0.015
GEN-2018-083 | 02 NEBRASKA | 640521 | ANTELOPE 7 | 115 | 14.1104 | 14.0562 | 0.0542
GEN-2018-083 | 02 NEBRASKA | 640560 | WAKEFIELD 4 | 230 | 7.9675 | 7.9527 | 0.0148
GEN-2018-083 | 02 NEBRASKA | 640589 | SHOLES.W 3 | 345 | 9.0182 | 8.8958 | 0.1224
GEN-2018-083 | 02 NEBRASKA | 640598 | HAYSTACK.WD3 | 345 | 8.6554 | 8.5464 | 0.109
GEN-2018-083 | 02 NEBRASKA | 643271 | PLUMBCR.W 3 | 345 | 10.8968 | 10.7124 | 0.1844
GEN-2018-083 | 02 NEBRASKA | 650114 | NW68HOLDRG3 | 345 | 16.8066 | 16.7767 | 0.0299
GEN-2018-083 | 02 NEBRASKA | 652564 | SIOUXCY3 | 345 | 15.3816 | 15.3687 | 0.0129
GEN-2018-083 | 02 NEBRASKA | 762779 | G18-043-TAP | 345 | 15.621 | 15.6155 | 0.0055
GEN-2018-083 | 02 NEBRASKA | 763032 | GEN-2018-068 | 345 | 5.9447 | 5.9045 | 0.0402
GEN-2018-083 | 02 NEBRASKA | 763439 | GEN-2018-131 | 345 | 6.9826 | 6.9246 | 0.058
GEN-2018-083 | 02 NEBRASKA | 45906 | J1590 SUB | 345 | 14.2602 | 14.2531 | 0.0071
GEN-2018-083 | 02 NEBRASKA | 87486 | J748GENTIE | 345 | 13.2728 | 13.267 | 0.0058
GEN-2018-083 | 02 NEBRASKA | 635202 | NEAL S 5 | 161 | 22.3496 | 22.3361 | 0.0135
GEN-2018-083 | 02 NEBRASKA | 635203 | NEAL N 5 | 161 | 25.6073 | 25.589 | 0.0183
GEN-2018-083 | 02 NEBRASKA | 635206 | IDA CO 3 | 345 | 9.3103 | 9.308 | 0.0023
GEN-2018-083 | 02 NEBRASKA | 635220 | INTCHG 5 | 161 | 14.526 | 14.5203 | 0.0057
GEN-2018-083 | 02 NEBRASKA | 635230 | LIBERTY5 | 161 | 24.9266 | 24.9093 | 0.0173
GEN-2018-083 | 02 NEBRASKA | 635399 | CHEROKEE 3 | 345 | 15.9186 | 15.9107 | 0.0079
GEN-2018-083 | 02 NEBRASKA | 640072 | BATTLCR7 | 115 | 7.3087 | 7.2907 | 0.018
GEN-2018-083 | 02 NEBRASKA | 640081 | BELDEN 8 | 69 | 3.6996 | 3.6984 | 0.0012
GEN-2018-083 | 02 NEBRASKA | 640115 | CO.LINE7 | 115 | 7.2295 | 7.2136 | 0.0159
GEN-2018-083 | 02 NEBRASKA | 640119 | COL.COG7 | 115 | 19.5195 | 19.4431 | 0.0764
GEN-2018-083 | 02 NEBRASKA | 640126 | E.COL. 4 | 230 | 10.0667 | 10.0207 | 0.046
GEN-2018-083 | 02 NEBRASKA | 640131 | COLMB.W4 | 230 | 9.8308 | 9.7905 | 0.0403
GEN-2018-083 | 02 NEBRASKA | 640134 | KELLY 7 | 115 | 17.6974 | 17.637 | 0.0604
GEN-2018-083 | 02 NEBRASKA | 640136 | COLMBUS7 | 115 | 19.1401 | 19.07 | 0.0701
GEN-2018-083 | 02 NEBRASKA | 640149 | CREITON7 | 115 | 4.7116 | 4.7082 | 0.0034
GEN-2018-083 | 02 NEBRASKA | 640157 | DAVIDCY7 | 115 | 5.6545 | 5.6504 | 0.0041
GEN-2018-083 | 02 NEBRASKA | 640212 | HARTGTN7 | 115 | 5.1832 | 5.1806 | 0.0026
GEN-2018-083 | 02 NEBRASKA | 640263 | MADISON7 | 115 | 6.1678 | 6.1565 | 0.0113
GEN-2018-083 | 02 NEBRASKA | 640277 | MOORE 3 | 345 | 22.4804 | 22.459 | 0.0214
GEN-2018-083 | 02 NEBRASKA | 640293 | NELIGH 7 | 115 | 9.9449 | 9.9223 | 0.0226
GEN-2018-083 | 02 NEBRASKA | 640357 | STANTON7 | 115 | 5.115 | 5.1085 | 0.0065
GEN-2018-083 | 02 NEBRASKA | 640386 | TWIN CH4 | 230 | 8.9225 | 8.9121 | 0.0104
GEN-2018-083 | 02 NEBRASKA | 640387 | TWIN CH7 | 115 | 10.7822 | 10.774 | 0.0082
GEN-2018-083 | 02 NEBRASKA | 640522 | ANTELOPE 8 | 69 | 5.119 | 5.1147 | 0.0043
GEN-2018-083 | 02 NEBRASKA | 640540 | MEADOWGROVE4 | 230 | 5.0998 | 5.0948 | 0.005
GEN-2018-083 | 02 NEBRASKA | 640561 | RTLSNAKE.W 4 | 230 | 7.1132 | 7.1025 | 0.0107
GEN-2018-083 | 02 NEBRASKA | 643254 | UPSTREAM.W 7 | 115 | 13.3751 | 13.3269 | 0.0482
GEN-2018-083 | 02 NEBRASKA | 645451 | S3451 3 | 345 | 21.3318 | 21.3247 | 0.0071
GEN-2018-083 | 02 NEBRASKA | 650185 | WAGENER 3 | 345 | 20.0853 | 20.0673 | 0.018
GEN-2018-083 | 02 NEBRASKA | 650214 | NW68HOLDRG7 | 115 | 24.3952 | 24.3825 | 0.0127
GEN-2018-083 | 02 NEBRASKA | 652552 | SIOUXCY2 | 230 | 20.341 | 20.3243 | 0.0167
GEN-2018-083 | 02 NEBRASKA | 652864 | SIOUXCY-LNX3 | 345 | 15.1969 | 15.1843 | 0.0126
GEN-2018-083 | 02 NEBRASKA | 760788 | GEN-2017-201 | 345 | 8.2239 | 8.1231 | 0.1008
GEN-2018-083 | 02 NEBRASKA | 762069 | G17-105TAP | 161 | 8.3472 | 8.3455 | 0.0017
GEN-2018-083 | 02 NEBRASKA | 762780 | GEN-2018-043 | 345 | 12.7205 | 12.717 | 0.0035
GEN-2018-083 | 02 NEBRASKA | 763450 | GEN-2018-132 | 345 | 6.6695 | 6.6165 | 0.053
GEN-2018-083 | 02 NEBRASKA | 601006 | SPLT RK3 | 345 | 14.9416 | 14.9399 | 0.0017
GEN-2018-083 | 02 NEBRASKA | 635204 | NEAL N 8 | 69 | 9.7689 | 9.7678 | 0.0011
GEN-2018-083 | 02 NEBRASKA | 635219 | GARD AVE 3 | 345 | 8.9677 | 8.9658 | 0.0019
GEN-2018-083 | 02 NEBRASKA | 635221 | KELLOGG5 | 161 | 17.1226 | 17.1149 | 0.0077
GEN-2018-083 | 02 NEBRASKA | 635229 | AIRPORT 5 | 161 | 16.9835 | 16.9757 | 0.0078
GEN-2018-083 | 02 NEBRASKA | 635235 | SALIX 5 | 161 | 14.6126 | 14.607 | 0.0056
GEN-2018-083 | 02 NEBRASKA | 635300 | MONONA 5 | 161 | 5.4609 | 5.4605 | 0.0004
GEN-2018-083 | 02 NEBRASKA | 635400 | HIGHLND 3 | 345 | 14.5121 | 14.5084 | 0.0037
GEN-2018-083 | 02 NEBRASKA | 637009 | GLACIAL EDGE | 345 | 15.6443 | 15.6367 | 0.0076
GEN-2018-083 | 02 NEBRASKA | 640073 | BATTLCR8 | 69 | 3.8906 | 3.8875 | 0.0031
GEN-2018-083 | 02 NEBRASKA | 640078 | BEEMER 7 | 115 | 4.396 | 4.3933 | 0.0027
GEN-2018-083 | 02 NEBRASKA | 640084 | BLMFLD 7 | 115 | 5.1275 | 5.1257 | 0.0018
GEN-2018-083 | 02 NEBRASKA | 640113 | CLRWATR7 | 115 | 5.1516 | 5.147 | 0.0046
GEN-2018-083 | 02 NEBRASKA | 640122 | COL.DRY7 | 115 | 16.4842 | 16.4296 | 0.0546
GEN-2018-083 | 02 NEBRASKA | 640124 | COL.SE 7 | 115 | 16.6202 | 16.5672 | 0.053
GEN-2018-083 | 02 NEBRASKA | 640150 | CREITON8 | 69 | 4.3586 | 4.3569 | 0.0017
GEN-2018-083 | 02 NEBRASKA | 640151 | CRESTON7 | 115 | 5.9927 | 5.9831 | 0.0096
GEN-2018-083 | 02 NEBRASKA | 640163 | EMERSON7 | 115 | 5.4485 | 5.4465 | 0.002
GEN-2018-083 | 02 NEBRASKA | 640181 | GENOA 7 | 115 | 4.8706 | 4.867 | 0.0036
GEN-2018-083 | 02 NEBRASKA | 640200 | GR ISLD4 | 230 | 16.413 | 16.4045 | 0.0085
GEN-2018-083 | 02 NEBRASKA | 640213 | HARTGTN8 | 69 | 3.4988 | 3.4981 | 0.0007
GEN-2018-083 | 02 NEBRASKA | 640271 | MCCOOL 3 | 345 | 10.8752 | 10.871 | 0.0042
GEN-2018-083 | 02 NEBRASKA | 640278 | SHELDON7 | 115 | 42.1871 | 42.1692 | 0.0179
GEN-2018-083 | 02 NEBRASKA | 640294 | NELIGH 8 | 69 | 5.8977 | 5.893 | 0.0047
GEN-2018-083 | 02 NEBRASKA | 640316 | PAWNEEL7 | 115 | 11.1764 | 11.1731 | 0.0033
GEN-2018-083 | 02 NEBRASKA | 640336 | SCHUYLR7 | 115 | 5.8 | 5.7956 | 0.0044
GEN-2018-083 | 02 NEBRASKA | 640345 | SILVRCK7 | 115 | 4.5561 | 4.5538 | 0.0023
GEN-2018-083 | 02 NEBRASKA | 640377 | TEKAMAH5 | 161 | 8.8894 | 8.8874 | 0.002
GEN-2018-083 | 02 NEBRASKA | 640388 | TWIN CH8 | 69 | 7.7842 | 7.7816 | 0.0026
GEN-2018-083 | 02 NEBRASKA | 640402 | WAHOO 7 | 115 | 4.7578 | 4.7566 | 0.0012
GEN-2018-083 | 02 NEBRASKA | 640424 | S.SIOUXCITY7 | 115 | 7.3706 | 7.3668 | 0.0038
GEN-2018-083 | 02 NEBRASKA | 640444 | PETERSBRG.N7 | 115 | 5.4317 | 5.4276 | 0.0041
GEN-2018-083 | 02 NEBRASKA | 640525 | TOBIAS 3 | 345 | 11.6744 | 11.6703 | 0.0041
GEN-2018-083 | 02 NEBRASKA | 640590 | MONOLITH 3 | 345 | 21.9978 | 21.9777 | 0.0201
GEN-2018-083 | 02 NEBRASKA | 645454 | S3454 3 | 345 | 27.4247 | 27.4149 | 0.0098
GEN-2018-083 | 02 NEBRASKA | 645459 | S3459 3 | 345 | 24.0005 | 23.9946 | 0.0059
GEN-2018-083 | 02 NEBRASKA | 646251 | S1251 5 | 161 | 30.7514 | 30.7446 | 0.0068
GEN-2018-083 | 02 NEBRASKA | 648506 | PR BRZ 4 | 230 | 3.5115 | 3.5096 | 0.0019
GEN-2018-083 | 02 NEBRASKA | 650189 | 103&ROKEBY3 | 345 | 19.9772 | 19.9619 | 0.0153
GEN-2018-083 | 02 NEBRASKA | 650210 | NW70FAIRFD7 | 115 | 20.3803 | 20.3717 | 0.0086
GEN-2018-083 | 02 NEBRASKA | 650216 | SW27&F 7 | 115 | 21.0693 | 21.0613 | 0.008
GEN-2018-083 | 02 NEBRASKA | 650285 | WAGENER 7 | 115 | 30.6415 | 30.6278 | 0.0137
GEN-2018-083 | 02 NEBRASKA | 650290 | ROKEBY 7 | 115 | 24.4224 | 24.4136 | 0.0088
GEN-2018-083 | 02 NEBRASKA | 652509 | FTRANDL4 | 230 | 12.1336 | 12.1308 | 0.0028
GEN-2018-083 | 02 NEBRASKA | 652511 | GAVINS 7 | 115 | 8.4307 | 8.4279 | 0.0028
GEN-2018-083 | 02 NEBRASKA | 652565 | SIOUXCY4 | 230 | 20.341 | 20.3243 | 0.0167
GEN-2018-083 | 02 NEBRASKA | 659900 | EAGLE___-NI4 | 230 | 7.3012 | 7.3 | 0.0012
GEN-2018-083 | 02 NEBRASKA | 762070 | GEN-2017-105 | 161 | 8.3472 | 8.3455 | 0.0017
GEN-2018-083 | 02 NEBRASKA | 762603 | GEN-2018-025 | 345 | 20.4121 | 20.4056 | 0.0065
GEN-2018-090 | 02 NEBRASKA | 762779 | G18-043-TAP | 345 | 15.621 | 15.621 | 0
GEN-2018-090 | 02 NEBRASKA | 635200 | RAUN 3 | 345 | 27.0138 | 27.0138 | 0
GEN-2018-090 | 02 NEBRASKA | 645451 | S3451 3 | 345 | 21.3318 | 21.3318 | 0
GEN-2018-090 | 02 NEBRASKA | 762780 | GEN-2018-043 | 345 | 12.7205 | 12.7205 | 0
GEN-2018-090 | 02 NEBRASKA | 87487 | J748POI | 345 | 15.0615 | 15.0615 | 0
GEN-2018-090 | 02 NEBRASKA | 635201 | RAUN 5 | 161 | 27.0927 | 27.0927 | 0
GEN-2018-090 | 02 NEBRASKA | 635252 | J412 POI 3 | 345 | 9.6628 | 9.6628 | 0
GEN-2018-090 | 02 NEBRASKA | 635398 | REMSEN 3 | 345 | 14.4843 | 14.4843 | 0
GEN-2018-090 | 02 NEBRASKA | 640226 | HOSKINS3 | 345 | 13.0113 | 13.0113 | 0
GEN-2018-090 | 02 NEBRASKA | 645454 | S3454 3 | 345 | 27.4247 | 27.4247 | 0
GEN-2018-090 | 02 NEBRASKA | 645459 | S3459 3 | 345 | 24.0005 | 24.0005 | 0
GEN-2018-090 | 02 NEBRASKA | 646251 | S1251 5 | 161 | 30.7514 | 30.7514 | 0
GEN-2018-090 | 02 NEBRASKA | 652564 | SIOUXCY3 | 345 | 15.3816 | 15.3816 | 0
GEN-2018-090 | 02 NEBRASKA | 762603 | GEN-2018-025 | 345 | 20.4121 | 20.4121 | 0
GEN-2018-090 | 02 NEBRASKA | 45906 | J1590 SUB | 345 | 14.2602 | 14.2602 | 0
GEN-2018-090 | 02 NEBRASKA | 87486 | J748GENTIE | 345 | 13.2728 | 13.2728 | 0
GEN-2018-090 | 02 NEBRASKA | 635202 | NEAL S 5 | 161 | 22.3496 | 22.3496 | 0
GEN-2018-090 | 02 NEBRASKA | 635203 | NEAL N 5 | 161 | 25.6073 | 25.6073 | 0
GEN-2018-090 | 02 NEBRASKA | 635206 | IDA CO 3 | 345 | 9.3103 | 9.3103 | 0
GEN-2018-090 | 02 NEBRASKA | 635220 | INTCHG 5 | 161 | 14.526 | 14.526 | 0
GEN-2018-090 | 02 NEBRASKA | 635230 | LIBERTY5 | 161 | 24.9266 | 24.9266 | 0
GEN-2018-090 | 02 NEBRASKA | 635399 | CHEROKEE 3 | 345 | 15.9186 | 15.9186 | 0
GEN-2018-090 | 02 NEBRASKA | 640227 | HOSKINS4 | 230 | 10.0896 | 10.0896 | 0
GEN-2018-090 | 02 NEBRASKA | 640228 | HOSKINS7 | 115 | 18.0994 | 18.0994 | 0
GEN-2018-090 | 02 NEBRASKA | 640520 | ANTELOPE 3 | 345 | 6.9888 | 6.9888 | 0
GEN-2018-090 | 02 NEBRASKA | 640588 | TURTLE.CRK 3 | 345 | 11.1479 | 11.1479 | 0
GEN-2018-090 | 02 NEBRASKA | 645100 | FC1A 5 | 161 | 28.3016 | 28.3016 | 0
GEN-2018-090 | 02 NEBRASKA | 645455 | S3455 3 | 345 | 30.2346 | 30.2346 | 0
GEN-2018-090 | 02 NEBRASKA | 645456 | S3456 3 | 345 | 32.5395 | 32.5395 | 0
GEN-2018-090 | 02 NEBRASKA | 645740 | S3740 3 | 345 | 21.8202 | 21.8202 | 0
GEN-2018-090 | 02 NEBRASKA | 646209 | S1209 5 | 161 | 44.7955 | 44.7955 | 0
GEN-2018-090 | 02 NEBRASKA | 646254 | S1254 5 | 161 | 30.731 | 30.731 | 0
GEN-2018-090 | 02 NEBRASKA | 646297 | S1297 5 | 161 | 18.0655 | 18.0655 | 0
GEN-2018-090 | 02 NEBRASKA | 646298 | S1298 5 | 161 | 28.0648 | 28.0648 | 0
GEN-2018-090 | 02 NEBRASKA | 646341 | S1341 5 | 161 | 25.9906 | 25.9906 | 0
GEN-2018-090 | 02 NEBRASKA | 650185 | WAGENER 3 | 345 | 20.0853 | 20.0853 | 0
GEN-2018-090 | 02 NEBRASKA | 652552 | SIOUXCY2 | 230 | 20.341 | 20.341 | 0
GEN-2018-090 | 02 NEBRASKA | 652864 | SIOUXCY-LNX3 | 345 | 15.1969 | 15.1969 | 0
GEN-2018-090 | 02 NEBRASKA | 762069 | G17-105TAP | 161 | 8.3472 | 8.3472 | 0
GEN-2018-090 | 02 NEBRASKA | 763982 | G19-069-TAP | 345 | 11.2849 | 11.2849 | 0
GEN-2018-090 | 02 NEBRASKA | 601006 | SPLT RK3 | 345 | 14.9416 | 14.9416 | 0
GEN-2018-090 | 02 NEBRASKA | 635000 | CBLUFFS3 | 345 | 29.9866 | 29.9866 | 0
GEN-2018-090 | 02 NEBRASKA | 635204 | NEAL N 8 | 69 | 9.7689 | 9.7689 | 0
GEN-2018-090 | 02 NEBRASKA | 635219 | GARD AVE 3 | 345 | 8.9677 | 8.9677 | 0
GEN-2018-090 | 02 NEBRASKA | 635221 | KELLOGG5 | 161 | 17.1226 | 17.1226 | 0
GEN-2018-090 | 02 NEBRASKA | 635229 | AIRPORT 5 | 161 | 16.9835 | 16.9835 | 0
GEN-2018-090 | 02 NEBRASKA | 635235 | SALIX 5 | 161 | 14.6126 | 14.6126 | 0
GEN-2018-090 | 02 NEBRASKA | 635300 | MONONA 5 | 161 | 5.4609 | 5.4609 | 0
GEN-2018-090 | 02 NEBRASKA | 635400 | HIGHLND 3 | 345 | 14.5121 | 14.5121 | 0
GEN-2018-090 | 02 NEBRASKA | 637009 | GLACIAL EDGE | 345 | 15.6443 | 15.6443 | 0
GEN-2018-090 | 02 NEBRASKA | 640080 | BELDEN 7 | 115 | 5.9733 | 5.9733 | 0
GEN-2018-090 | 02 NEBRASKA | 640296 | NORFK.N7 | 115 | 13.1793 | 13.1793 | 0
GEN-2018-090 | 02 NEBRASKA | 640298 | NORFOLK7 | 115 | 12.385 | 12.385 | 0
GEN-2018-090 | 02 NEBRASKA | 640342 | SHELCRK3 | 345 | 10.533 | 10.533 | 0
GEN-2018-090 | 02 NEBRASKA | 640363 | STNTN.N7 | 115 | 6.977 | 6.977 | 0
GEN-2018-090 | 02 NEBRASKA | 640377 | TEKAMAH5 | 161 | 8.8894 | 8.8894 | 0
GEN-2018-090 | 02 NEBRASKA | 640521 | ANTELOPE 7 | 115 | 14.1104 | 14.1104 | 0
GEN-2018-090 | 02 NEBRASKA | 640560 | WAKEFIELD 4 | 230 | 7.9675 | 7.9675 | 0
GEN-2018-090 | 02 NEBRASKA | 640589 | SHOLES.W 3 | 345 | 9.0182 | 9.0182 | 0
GEN-2018-090 | 02 NEBRASKA | 640598 | HAYSTACK.WD3 | 345 | 8.6554 | 8.6554 | 0
GEN-2018-090 | 02 NEBRASKA | 643271 | PLUMBCR.W 3 | 345 | 10.8968 | 10.8968 | 0
GEN-2018-090 | 02 NEBRASKA | 645458 | S3458 3 | 345 | 28.556 | 28.556 | 0
GEN-2018-090 | 02 NEBRASKA | 645761 | S3761 3 | 345 | 21.7546 | 21.7546 | 0
GEN-2018-090 | 02 NEBRASKA | 646206 | S1206 5 | 161 | 41.6222 | 41.6222 | 0
GEN-2018-090 | 02 NEBRASKA | 646226 | S1226 5 | 161 | 23.7677 | 23.7677 | 0
GEN-2018-090 | 02 NEBRASKA | 646231 | S1231 5 | 161 | 41.6151 | 41.6151 | 0
GEN-2018-090 | 02 NEBRASKA | 646249 | S1249 5 | 161 | 23.8088 | 23.8088 | 0
GEN-2018-090 | 02 NEBRASKA | 646250 | S1250 5 | 161 | 33.2474 | 33.2474 | 0
GEN-2018-090 | 02 NEBRASKA | 646255 | S1255 5 | 161 | 45.855 | 45.855 | 0
GEN-2018-090 | 02 NEBRASKA | 646281 | S1281 5 | 161 | 33.0129 | 33.0129 | 0
GEN-2018-090 | 02 NEBRASKA | 646305 | S1305 5 | 161 | 26.7007 | 26.7007 | 0
GEN-2018-090 | 02 NEBRASKA | 646347 | S1347 5 | 161 | 31.0911 | 31.0911 | 0
GEN-2018-090 | 02 NEBRASKA | 647909 | S909 8 | 69 | 25.6436 | 25.6436 | 0
GEN-2018-090 | 02 NEBRASKA | 650114 | NW68HOLDRG3 | 345 | 16.8066 | 16.8066 | 0
GEN-2018-090 | 02 NEBRASKA | 650189 | 103&ROKEBY3 | 345 | 19.9772 | 19.9772 | 0
GEN-2018-090 | 02 NEBRASKA | 650285 | WAGENER 7 | 115 | 30.6415 | 30.6415 | 0
GEN-2018-090 | 02 NEBRASKA | 652565 | SIOUXCY4 | 230 | 20.341 | 20.341 | 0
GEN-2018-090 | 02 NEBRASKA | 659900 | EAGLE___-NI4 | 230 | 7.3012 | 7.3012 | 0
GEN-2018-090 | 02 NEBRASKA | 762070 | GEN-2017-105 | 161 | 8.3472 | 8.3472 | 0
GEN-2018-090 | 02 NEBRASKA | 762691 | GEN-2018-033 | 345 | 21.8188 | 21.8188 | 0
GEN-2018-090 | 02 NEBRASKA | 763032 | GEN-2018-068 | 345 | 5.9447 | 5.9447 | 0
GEN-2018-090 | 02 NEBRASKA | 763142 | GEN-2018-083 | 345 | 2.1648 | 2.1648 | 0
GEN-2018-090 | 02 NEBRASKA | 763439 | GEN-2018-131 | 345 | 6.9826 | 6.9826 | 0
GEN-2018-090 | 02 NEBRASKA | 763978 | GEN-2019-069 | 345 | 11.2497 | 11.2497 | 0
GEN-2018-090 | 02 NEBRASKA | 541510 | HOLT 7 | 345 | 17.6874 | 17.6874 | 0
GEN-2018-090 | 02 NEBRASKA | 601034 | NOBLES 3 | 345 | 11.9717 | 11.9717 | 0
GEN-2018-090 | 02 NEBRASKA | 603016 | SPLT RK7 | 115 | 39.3911 | 39.3911 | 0
GEN-2018-090 | 02 NEBRASKA | 635001 | CBLUFFS5 | 161 | 37.3755 | 37.3755 | 0
GEN-2018-090 | 02 NEBRASKA | 635013 | PNYCRK 3 | 345 | 27.339 | 27.339 | 0
GEN-2018-090 | 02 NEBRASKA | 635014 | OVRLND 3 | 345 | 25.6899 | 25.6899 | 0
GEN-2018-090 | 02 NEBRASKA | 635016 | STHLND 3 | 345 | 27.3067 | 27.3067 | 0
GEN-2018-090 | 02 NEBRASKA | 635222 | KELLOGG8 | 69 | 17.6906 | 17.6906 | 0
GEN-2018-090 | 02 NEBRASKA | 635225 | MORNSD 5 | 161 | 10.845 | 10.845 | 0
GEN-2018-090 | 02 NEBRASKA | 635226 | LEEDS 5 | 161 | 15.8452 | 15.8452 | 0
GEN-2018-090 | 02 NEBRASKA | 635227 | SBRIDGE T8 | 69 | 8.529 | 8.529 | 0
GEN-2018-090 | 02 NEBRASKA | 635236 | SALIX 8 | 69 | 13.2308 | 13.2308 | 0
GEN-2018-090 | 02 NEBRASKA | 635301 | MONONA 8 | 69 | 4.5034 | 4.5034 | 0
GEN-2018-090 | 02 NEBRASKA | 635330 | CRWFRD 5 | 161 | 4.8914 | 4.8914 | 0
GEN-2018-090 | 02 NEBRASKA | 635368 | OBRIEN 3 | 345 | 14.9575 | 14.9575 | 0
GEN-2018-090 | 02 NEBRASKA | 636010 | LEHIGH 3 | 345 | 12.7745 | 12.7745 | 0
GEN-2018-090 | 02 NEBRASKA | 637024 | RICHLAND W | 345 | 8.9018 | 8.9018 | 0
GEN-2018-090 | 02 NEBRASKA | 640072 | BATTLCR7 | 115 | 7.3087 | 7.3087 | 0
GEN-2018-090 | 02 NEBRASKA | 640081 | BELDEN 8 | 69 | 3.6996 | 3.6996 | 0
GEN-2018-090 | 02 NEBRASKA | 640115 | CO.LINE7 | 115 | 7.2295 | 7.2295 | 0
GEN-2018-090 | 02 NEBRASKA | 640125 | COLMB.E3 | 345 | 10.209 | 10.209 | 0
GEN-2018-090 | 02 NEBRASKA | 640139 | COOPER 3 | 345 | 27.7474 | 27.7474 | 0
GEN-2018-090 | 02 NEBRASKA | 640149 | CREITON7 | 115 | 4.7116 | 4.7116 | 0
GEN-2018-090 | 02 NEBRASKA | 640212 | HARTGTN7 | 115 | 5.1832 | 5.1832 | 0
GEN-2018-090 | 02 NEBRASKA | 640263 | MADISON7 | 115 | 6.1678 | 6.1678 | 0
GEN-2018-090 | 02 NEBRASKA | 640277 | MOORE 3 | 345 | 22.4804 | 22.4804 | 0
GEN-2018-090 | 02 NEBRASKA | 640293 | NELIGH 7 | 115 | 9.9449 | 9.9449 | 0
GEN-2018-090 | 02 NEBRASKA | 640343 | SHELCRK4 | 230 | 10.8729 | 10.8729 | 0
GEN-2018-090 | 02 NEBRASKA | 640357 | STANTON7 | 115 | 5.115 | 5.115 | 0
GEN-2018-090 | 02 NEBRASKA | 640378 | TEKAMAH7 | 115 | 8.1878 | 8.1878 | 0
GEN-2018-090 | 02 NEBRASKA | 640386 | TWIN CH4 | 230 | 8.9225 | 8.9225 | 0
GEN-2018-090 | 02 NEBRASKA | 640387 | TWIN CH7 | 115 | 10.7822 | 10.7822 | 0
GEN-2018-090 | 02 NEBRASKA | 640522 | ANTELOPE 8 | 69 | 5.119 | 5.119 | 0
GEN-2018-090 | 02 NEBRASKA | 640561 | RTLSNAKE.W 4 | 230 | 7.1132 | 7.1132 | 0
GEN-2018-090 | 02 NEBRASKA | 643254 | UPSTREAM.W 7 | 115 | 13.3751 | 13.3751 | 0
GEN-2018-090 | 02 NEBRASKA | 646201 | S1201 5 | 161 | 29.9366 | 29.9366 | 0
GEN-2018-090 | 02 NEBRASKA | 646211 | S1211 5 | 161 | 33.8753 | 33.8753 | 0
GEN-2018-090 | 02 NEBRASKA | 646216 | S1216 5 | 161 | 28.8927 | 28.8927 | 0
GEN-2018-090 | 02 NEBRASKA | 646221 | S1221 5 | 161 | 33.815 | 33.815 | 0
GEN-2018-090 | 02 NEBRASKA | 646227 | S1227 5 | 161 | 31.0599 | 31.0599 | 0
GEN-2018-090 | 02 NEBRASKA | 646232 | S1232 5 | 161 | 25.1486 | 25.1486 | 0
GEN-2018-090 | 02 NEBRASKA | 646233 | S1233 5 | 161 | 27.829 | 27.829 | 0
GEN-2018-090 | 02 NEBRASKA | 646235 | S1235 5 | 161 | 32.2136 | 32.2136 | 0
GEN-2018-090 | 02 NEBRASKA | 646237 | S1237 5 | 161 | 20.7657 | 20.7657 | 0
GEN-2018-090 | 02 NEBRASKA | 646244 | S1244 5 | 161 | 20.9436 | 20.9436 | 0
GEN-2018-090 | 02 NEBRASKA | 646252 | S1252 5 | 161 | 28.1188 | 28.1188 | 0
GEN-2018-090 | 02 NEBRASKA | 646256 | S1256 5 | 161 | 21.5926 | 21.5926 | 0
GEN-2018-090 | 02 NEBRASKA | 646259 | S1259 5 | 161 | 36.1798 | 36.1798 | 0
GEN-2018-090 | 02 NEBRASKA | 646287 | S1287 5 | 161 | 20.6221 | 20.6221 | 0
GEN-2018-090 | 02 NEBRASKA | 646291 | S1291 5 | 161 | 6.7525 | 6.7525 | 0
GEN-2018-090 | 02 NEBRASKA | 646361 | S1361 5 | 161 | 37.9507 | 37.9507 | 0
GEN-2018-090 | 02 NEBRASKA | 646363 | S1363 5 | 161 | 29.7537 | 29.7537 | 0
GEN-2018-090 | 02 NEBRASKA | 647006 | S906 N 8 | 69 | 30.5075 | 30.5075 | 0
GEN-2018-090 | 02 NEBRASKA | 647906 | S906 S 8 | 69 | 30.9225 | 30.9225 | 0
GEN-2018-090 | 02 NEBRASKA | 647918 | S918 8 | 69 | 21.7552 | 21.7552 | 0
GEN-2018-090 | 02 NEBRASKA | 647921 | S921 8 | 69 | 25.0819 | 25.0819 | 0
GEN-2018-090 | 02 NEBRASKA | 647937 | S937 8 | 69 | 8.5818 | 8.5818 | 0
GEN-2018-090 | 02 NEBRASKA | 647939 | S939 8 | 69 | 19.1025 | 19.1025 | 0
GEN-2018-090 | 02 NEBRASKA | 647950 | S950 8 | 69 | 19.3217 | 19.3217 | 0
GEN-2018-090 | 02 NEBRASKA | 650214 | NW68HOLDRG7 | 115 | 24.3952 | 24.3952 | 0
GEN-2018-090 | 02 NEBRASKA | 650267 | 84LEIGHTON7 | 115 | 28.0723 | 28.0723 | 0
GEN-2018-090 | 02 NEBRASKA | 650271 | 81&OCHENEY7 | 115 | 23.946 | 23.946 | 0
GEN-2018-090 | 02 NEBRASKA | 650279 | 120&ALVO 7 | 115 | 20.6658 | 20.6658 | 0
GEN-2018-090 | 02 NEBRASKA | 652509 | FTRANDL4 | 230 | 12.1336 | 12.1336 | 0
GEN-2018-090 | 02 NEBRASKA | 652537 | WHITE 3 | 345 | 18.2959 | 18.2959 | 0
GEN-2018-090 | 02 NEBRASKA | 652566 | SIOUXCY5 | 161 | 20.956 | 20.956 | 0
GEN-2018-090 | 02 NEBRASKA | 652567 | DENISON4 | 230 | 5.1544 | 5.1544 | 0
GEN-2018-090 | 02 NEBRASKA | 655484 | RASMUSN-ER4 | 230 | 6.7272 | 6.7272 | 0
GEN-2018-090 | 02 NEBRASKA | 659311 | PAHOJA__-BE4 | 230 | 7.4254 | 7.4254 | 0
GEN-2018-090 | 02 NEBRASKA | 659901 | EAGLE___-NI8 | 69 | 14.0991 | 14.0991 | 0
GEN-2018-090 | 02 NEBRASKA | 760788 | GEN-2017-201 | 345 | 8.2239 | 8.2239 | 0
GEN-2018-090 | 02 NEBRASKA | 763450 | GEN-2018-132 | 345 | 6.6695 | 6.6695 | 0
GEN-2018-125 | 02 NEBRASKA | 763410 | G18-125-TAP | 345 | 7.096 | 6.6853 | 0.4107
GEN-2018-125 | 02 NEBRASKA | 640183 | GENTLMN3 | 345 | 15.5779 | 15.3524 | 0.2255
GEN-2018-125 | 02 NEBRASKA | 640374 | SWEET W3 | 345 | 10.1673 | 9.999 | 0.1683
GEN-2018-125 | 02 NEBRASKA | 763406 | GEN-2018-125 | 345 | 6.7903 | 6.3785 | 0.4118
GEN-2018-125 | 02 NEBRASKA | 587680 | GEN-2016-074 | 345 | 5.9023 | 5.8479 | 0.0544
GEN-2018-125 | 02 NEBRASKA | 640065 | AXTELL 3 | 345 | 9.208 | 9.1593 | 0.0487
GEN-2018-125 | 02 NEBRASKA | 640184 | GENTLMN4 | 230 | 18.6782 | 18.5638 | 0.1144
GEN-2018-125 | 02 NEBRASKA | 640252 | KEYSTON3 | 345 | 9.0821 | 9.0317 | 0.0504
GEN-2018-125 | 02 NEBRASKA | 640325 | REDWILO3 | 345 | 6.1522 | 6.1367 | 0.0155
GEN-2018-125 | 02 NEBRASKA | 640500 | THEDFRD3 | 345 | 5.6561 | 5.6385 | 0.0176
GEN-2018-125 | 02 NEBRASKA | 653571 | GR ISLD3 | 345 | 12.2807 | 12.2345 | 0.0462
GEN-2018-125 | 02 NEBRASKA | 531451 | MINGO 7 | 345 | 6.0094 | 6.0048 | 0.0046
GEN-2018-125 | 02 NEBRASKA | 560082 | G16-050-TAP | 345 | 6.9512 | 6.9328 | 0.0184
GEN-2018-125 | 02 NEBRASKA | 640066 | AXTELL 7 | 115 | 14.0353 | 14.0075 | 0.0278
GEN-2018-125 | 02 NEBRASKA | 640200 | GR ISLD4 | 230 | 16.413 | 16.3696 | 0.0434
GEN-2018-125 | 02 NEBRASKA | 640253 | KEYSTON7 | 115 | 14.5686 | 14.5344 | 0.0342
GEN-2018-125 | 02 NEBRASKA | 640271 | MCCOOL 3 | 345 | 10.8752 | 10.8602 | 0.015
GEN-2018-125 | 02 NEBRASKA | 640286 | N.PLATT4 | 230 | 12.7581 | 12.7098 | 0.0483
GEN-2018-125 | 02 NEBRASKA | 640302 | OGALALA4 | 230 | 7.9617 | 7.9437 | 0.018
GEN-2018-125 | 02 NEBRASKA | 640312 | PAULINE3 | 345 | 7.8813 | 7.8653 | 0.016
GEN-2018-125 | 02 NEBRASKA | 640326 | REDWILO7 | 115 | 10.8676 | 10.8533 | 0.0143
GEN-2018-125 | 02 NEBRASKA | 640381 | THEDFRD7 | 115 | 9.0544 | 9.0415 | 0.0129
GEN-2018-125 | 02 NEBRASKA | 640510 | HOLT.CO3 | 345 | 7.9834 | 7.9733 | 0.0101
GEN-2018-125 | 02 NEBRASKA | 653871 | GR ISLD-LNX3 | 345 | 12.1609 | 12.1157 | 0.0452
GEN-2018-125 | 02 NEBRASKA | 763666 | G19-029 TAP | 345 | 7.5898 | 7.5628 | 0.027
GEN-2018-125 | 02 NEBRASKA | 530583 | POSTROCK7 | 345 | 7.7231 | 7.7192 | 0.0039
GEN-2018-125 | 02 NEBRASKA | 531429 | MINGO 3 | 115 | 12.2091 | 12.2036 | 0.0055
GEN-2018-125 | 02 NEBRASKA | 531465 | SETAB 7 | 345 | 6.866 | 6.8639 | 0.0021
GEN-2018-125 | 02 NEBRASKA | 531632 | GEN-2015-065 | 345 | 5.3136 | 5.3101 | 0.0035
GEN-2018-125 | 02 NEBRASKA | 584650 | GEN-2015-023 | 345 | 7.9179 | 7.9079 | 0.01
GEN-2018-125 | 02 NEBRASKA | 587350 | GEN-2016-050 | 345 | 5.8546 | 5.842 | 0.0126
GEN-2018-125 | 02 NEBRASKA | 640082 | BEVERLY7 | 115 | 4.6682 | 4.6655 | 0.0027
GEN-2018-125 | 02 NEBRASKA | 640093 | C.CREEK4 | 230 | 6.8775 | 6.8688 | 0.0087
GEN-2018-125 | 02 NEBRASKA | 640096 | CALAMS 7 | 115 | 3.3654 | 3.3647 | 0.0007
GEN-2018-125 | 02 NEBRASKA | 640131 | COLMB.W4 | 230 | 9.8308 | 9.8286 | 0.0022
GEN-2018-125 | 02 NEBRASKA | 640201 | GR ISLD7 | 115 | 22.4767 | 22.4446 | 0.0321
GEN-2018-125 | 02 NEBRASKA | 640214 | HASTING4 | 230 | 7.1952 | 7.1883 | 0.0069
GEN-2018-125 | 02 NEBRASKA | 640224 | HOLDREG7 | 115 | 5.9846 | 5.9809 | 0.0037
GEN-2018-125 | 02 NEBRASKA | 640250 | KEARNEY7 | 115 | 11.7457 | 11.7312 | 0.0145
GEN-2018-125 | 02 NEBRASKA | 640255 | KINGSLY7 | 115 | 8.9942 | 8.9821 | 0.0121
GEN-2018-125 | 02 NEBRASKA | 640269 | MCCOOK 7 | 115 | 8.2673 | 8.2599 | 0.0074
GEN-2018-125 | 02 NEBRASKA | 640272 | MCCOOL 7 | 115 | 14.0002 | 13.9932 | 0.007
GEN-2018-125 | 02 NEBRASKA | 640275 | MINDEN 7 | 115 | 7.0792 | 7.0732 | 0.006
GEN-2018-125 | 02 NEBRASKA | 640277 | MOORE 3 | 345 | 22.4804 | 22.4668 | 0.0136
GEN-2018-125 | 02 NEBRASKA | 640287 | N.PLATT7 | 115 | 17.9774 | 17.9331 | 0.0443
GEN-2018-125 | 02 NEBRASKA | 640304 | OGALALANPPD7 | 115 | 14.5859 | 14.5542 | 0.0317
GEN-2018-125 | 02 NEBRASKA | 640313 | PAULINE7 | 115 | 15.9334 | 15.917 | 0.0164
GEN-2018-125 | 02 NEBRASKA | 640330 | RIVERDL4 | 230 | 7.1483 | 7.1392 | 0.0091
GEN-2018-125 | 02 NEBRASKA | 640359 | STAPLETON 7 | 115 | 4.0511 | 4.0489 | 0.0022
GEN-2018-125 | 02 NEBRASKA | 640365 | STOCKVL7 | 115 | 4.448 | 4.4455 | 0.0025
GEN-2018-125 | 02 NEBRASKA | 640525 | TOBIAS 3 | 345 | 11.6744 | 11.6667 | 0.0077
GEN-2018-125 | 02 NEBRASKA | 652832 | GRPRAR1-LNX3 | 345 | 7.4489 | 7.4446 | 0.0043
GEN-2018-125 | 02 NEBRASKA | 659134 | SIDNEY___TS4 | 230 | 6.7958 | 6.7867 | 0.0091
GEN-2018-125 | 02 NEBRASKA | 659425 | SD.LS-KS-MB3 | 345 | 6.1743 | 6.1644 | 0.0099
GEN-2018-125 | 02 NEBRASKA | 760767 | GEN-2017-144 | 345 | 7.6478 | 7.6386 | 0.0092
GEN-2018-125 | 02 NEBRASKA | 761208 | GEN-2017-210 | 345 | 9.5276 | 9.5163 | 0.0113
GEN-2018-125 | 02 NEBRASKA | 763659 | GEN-2019-029 | 345 | 6.3464 | 6.3283 | 0.0181
GEN-2018-125 | 02 NEBRASKA | 763681 | GEN-2019-033 | 345 | 6.7099 | 6.6891 | 0.0208
GEN-2018-125 | 02 NEBRASKA | 530555 | COLBY 3 | 115 | 5.8396 | 5.8386 | 0.001
GEN-2018-125 | 02 NEBRASKA | 530559 | PH RUN 3 | 115 | 4.4815 | 4.4809 | 0.0006
GEN-2018-125 | 02 NEBRASKA | 530584 | POSTROCK6 | 230 | 10.7096 | 10.7065 | 0.0031
GEN-2018-125 | 02 NEBRASKA | 531351 | BREWSTR3 | 115 | 3.0791 | 3.0789 | 0.0002
GEN-2018-125 | 02 NEBRASKA | 531449 | HOLCOMB7 | 345 | 9.9438 | 9.942 | 0.0018
GEN-2018-125 | 02 NEBRASKA | 531464 | SETAB 3 | 115 | 10.1837 | 10.1825 | 0.0012
GEN-2018-125 | 02 NEBRASKA | 531469 | SPERVIL7 | 345 | 13.6098 | 13.6078 | 0.002
GEN-2018-125 | 02 NEBRASKA | 531623 | EASTFORK3 | 115 | 9.6776 | 9.6742 | 0.0034
GEN-2018-125 | 02 NEBRASKA | 585241 | GEN-2015-088 | 345 | 11.6744 | 11.6667 | 0.0077
GEN-2018-125 | 02 NEBRASKA | 640050 | AINSWND7 | 115 | 3.6224 | 3.622 | 0.0004
GEN-2018-125 | 02 NEBRASKA | 640063 | AURORA_7 | 115 | 6.9169 | 6.9144 | 0.0025
GEN-2018-125 | 02 NEBRASKA | 640083 | BEVERLY8 | 69 | 4.2595 | 4.2582 | 0.0013
GEN-2018-125 | 02 NEBRASKA | 640094 | C.CREEK7 | 115 | 7.0229 | 7.0187 | 0.0042
GEN-2018-125 | 02 NEBRASKA | 640100 | CAMBRIG7 | 115 | 4.084 | 4.0824 | 0.0016
GEN-2018-125 | 02 NEBRASKA | 640102 | CANADAY4 | 230 | 6.0066 | 6.0005 | 0.0061
GEN-2018-125 | 02 NEBRASKA | 640107 | CENCITY7 | 115 | 5.0369 | 5.0359 | 0.001
GEN-2018-125 | 02 NEBRASKA | 640133 | COLMBUS4 | 230 | 11.4877 | 11.4853 | 0.0024
GEN-2018-125 | 02 NEBRASKA | 640161 | ELMCRK_7 | 115 | 5.864 | 5.8609 | 0.0031
GEN-2018-125 | 02 NEBRASKA | 640167 | ENDERS 7 | 115 | 3.7071 | 3.7052 | 0.0019
GEN-2018-125 | 02 NEBRASKA | 640178 | GENEVA 7 | 115 | 9.4414 | 9.439 | 0.0024
GEN-2018-125 | 02 NEBRASKA | 640215 | HASTING7 | 115 | 18.5276 | 18.5113 | 0.0163
GEN-2018-125 | 02 NEBRASKA | 640222 | HILDRTH7 | 115 | 4.1758 | 4.1743 | 0.0015
GEN-2018-125 | 02 NEBRASKA | 640238 | JEFFREY7 | 115 | 5.9155 | 5.912 | 0.0035
GEN-2018-125 | 02 NEBRASKA | 640242 | JOHN.2 7 | 115 | 11.9994 | 11.9884 | 0.011
GEN-2018-125 | 02 NEBRASKA | 640248 | KEAR.NE7 | 115 | 9.2674 | 9.2588 | 0.0086
GEN-2018-125 | 02 NEBRASKA | 640261 | LOWELL 7 | 115 | 8.0123 | 8.0058 | 0.0065
GEN-2018-125 | 02 NEBRASKA | 640265 | MALONEY7 | 115 | 11.0487 | 11.0319 | 0.0168
GEN-2018-125 | 02 NEBRASKA | 640267 | MAXWELS7 | 115 | 6.5173 | 6.5121 | 0.0052
GEN-2018-125 | 02 NEBRASKA | 640270 | MCCOOK 8 | 69 | 4.3637 | 4.3624 | 0.0013
GEN-2018-125 | 02 NEBRASKA | 640273 | MCCOOL 8 | 69 | 5.4561 | 5.4555 | 0.0006
GEN-2018-125 | 02 NEBRASKA | 640278 | SHELDON7 | 115 | 42.1871 | 42.1769 | 0.0102
GEN-2018-125 | 02 NEBRASKA | 640288 | N.PLATT8 | 69 | 4.8849 | 4.8829 | 0.002
GEN-2018-125 | 02 NEBRASKA | 640310 | ORLEANS7 | 115 | 2.3445 | 2.3439 | 0.0006
GEN-2018-125 | 02 NEBRASKA | 640314 | PAULINE8 | 69 | 4.6974 | 4.6966 | 0.0008
GEN-2018-125 | 02 NEBRASKA | 640331 | RIVERDL7 | 115 | 12.6215 | 12.6069 | 0.0146
GEN-2018-125 | 02 NEBRASKA | 640353 | ST.LIB 7 | 115 | 9.4324 | 9.4275 | 0.0049
GEN-2018-125 | 02 NEBRASKA | 640360 | STAPLETON 8 | 69 | 3.3012 | 3.3003 | 0.0009
GEN-2018-125 | 02 NEBRASKA | 640366 | STOCKVL8 | 69 | 3.2437 | 3.2429 | 0.0008
GEN-2018-125 | 02 NEBRASKA | 640383 | TOWER 7 | 115 | 8.91 | 8.902 | 0.008
GEN-2018-125 | 02 NEBRASKA | 640413 | YORK SW7 | 115 | 7.9943 | 7.9921 | 0.0022
GEN-2018-125 | 02 NEBRASKA | 640448 | HOLDREGE 8 | 69 | 3.6461 | 3.6453 | 0.0008
GEN-2018-125 | 02 NEBRASKA | 640583 | ROSEMONT 7 | 115 | 6.4298 | 6.4278 | 0.002
GEN-2018-125 | 02 NEBRASKA | 640590 | MONOLITH 3 | 345 | 21.9978 | 21.9851 | 0.0127
GEN-2018-125 | 02 NEBRASKA | 641088 | HASTCTY7 | 115 | 18.5276 | 18.5113 | 0.0163
GEN-2018-125 | 02 NEBRASKA | 642071 | SUB-D 7 | 115 | 16.5948 | 16.5801 | 0.0147
GEN-2018-125 | 02 NEBRASKA | 642072 | SUB-E 7 | 115 | 16.2981 | 16.2828 | 0.0153
GEN-2018-125 | 02 NEBRASKA | 650114 | NW68HOLDRG3 | 345 | 16.8066 | 16.8013 | 0.0053
GEN-2018-125 | 02 NEBRASKA | 650189 | 103&ROKEBY3 | 345 | 19.9772 | 19.9713 | 0.0059
GEN-2018-125 | 02 NEBRASKA | 652532 | GR PRAIRIE 3 | 345 | 7.4489 | 7.4446 | 0.0043
GEN-2018-125 | 02 NEBRASKA | 653572 | SIDNEY 7 | 115 | 4.4251 | 4.4232 | 0.0019
GEN-2018-125 | 02 NEBRASKA | 659133 | SIDNEY__-MB3 | 345 | 6.1743 | 6.1644 | 0.0099
GEN-2018-125 | 02 NEBRASKA | 659210 | SIDNEY__-MB4 | 230 | 7.0467 | 7.0372 | 0.0095
GEN-2018-125 | 02 NEBRASKA | 659800 | GRANTNB_-TS7 | 115 | 6.2302 | 6.2246 | 0.0056
GEN-2018-125 | 02 NEBRASKA | 659801 | OGALALA_-TS7 | 115 | 14.5859 | 14.5542 | 0.0317
GEN-2018-125 | 02 NEBRASKA | 761292 | GEN-2017-181 | 345 | 6.6467 | 6.6445 | 0.0022
GEN-2018-131 | 02 NEBRASKA | 640520 | ANTELOPE 3 | 345 | 6.9888 | 6.9887 | 0.0001
GEN-2018-131 | 02 NEBRASKA | 640226 | HOSKINS3 | 345 | 13.0113 | 13.0113 | 0
GEN-2018-131 | 02 NEBRASKA | 640521 | ANTELOPE 7 | 115 | 14.1104 | 14.1103 | 0.0001
GEN-2018-131 | 02 NEBRASKA | 763032 | GEN-2018-068 | 345 | 5.9447 | 5.9447 | 0
GEN-2018-131 | 02 NEBRASKA | 763439 | GEN-2018-131 | 345 | 6.9826 | 6.9826 | 0
GEN-2018-131 | 02 NEBRASKA | 635200 | RAUN 3 | 345 | 27.0138 | 27.0138 | 0
GEN-2018-131 | 02 NEBRASKA | 640115 | CO.LINE7 | 115 | 7.2295 | 7.2295 | 0
GEN-2018-131 | 02 NEBRASKA | 640149 | CREITON7 | 115 | 4.7116 | 4.7116 | 0
GEN-2018-131 | 02 NEBRASKA | 640227 | HOSKINS4 | 230 | 10.0896 | 10.0896 | 0
GEN-2018-131 | 02 NEBRASKA | 640228 | HOSKINS7 | 115 | 18.0994 | 18.0994 | 0
GEN-2018-131 | 02 NEBRASKA | 640293 | NELIGH 7 | 115 | 9.9449 | 9.9449 | 0
GEN-2018-131 | 02 NEBRASKA | 640522 | ANTELOPE 8 | 69 | 5.119 | 5.119 | 0
GEN-2018-131 | 02 NEBRASKA | 640588 | TURTLE.CRK 3 | 345 | 11.1479 | 11.1479 | 0
GEN-2018-131 | 02 NEBRASKA | 643254 | UPSTREAM.W 7 | 115 | 13.3751 | 13.375 | 0.0001
GEN-2018-131 | 02 NEBRASKA | 763450 | GEN-2018-132 | 345 | 6.6695 | 6.6694 | 0.0001
GEN-2018-131 | 02 NEBRASKA | 763982 | G19-069-TAP | 345 | 11.2849 | 11.2849 | 0
GEN-2018-131 | 02 NEBRASKA | 87487 | J748POI | 345 | 15.0615 | 15.0615 | 0
GEN-2018-131 | 02 NEBRASKA | 635201 | RAUN 5 | 161 | 27.0927 | 27.0927 | 0
GEN-2018-131 | 02 NEBRASKA | 635252 | J412 POI 3 | 345 | 9.6628 | 9.6628 | 0
GEN-2018-131 | 02 NEBRASKA | 635398 | REMSEN 3 | 345 | 14.4843 | 14.4843 | 0
GEN-2018-131 | 02 NEBRASKA | 640072 | BATTLCR7 | 115 | 7.3087 | 7.3087 | 0
GEN-2018-131 | 02 NEBRASKA | 640080 | BELDEN 7 | 115 | 5.9733 | 5.9733 | 0
GEN-2018-131 | 02 NEBRASKA | 640084 | BLMFLD 7 | 115 | 5.1275 | 5.1275 | 0
GEN-2018-131 | 02 NEBRASKA | 640113 | CLRWATR7 | 115 | 5.1516 | 5.1515 | 0.0001
GEN-2018-131 | 02 NEBRASKA | 640150 | CREITON8 | 69 | 4.3586 | 4.3586 | 0
GEN-2018-131 | 02 NEBRASKA | 640294 | NELIGH 8 | 69 | 5.8977 | 5.8977 | 0
GEN-2018-131 | 02 NEBRASKA | 640296 | NORFK.N7 | 115 | 13.1793 | 13.1793 | 0
GEN-2018-131 | 02 NEBRASKA | 640298 | NORFOLK7 | 115 | 12.385 | 12.385 | 0
GEN-2018-131 | 02 NEBRASKA | 640342 | SHELCRK3 | 345 | 10.533 | 10.533 | 0
GEN-2018-131 | 02 NEBRASKA | 640363 | STNTN.N7 | 115 | 6.977 | 6.977 | 0
GEN-2018-131 | 02 NEBRASKA | 640444 | PETERSBRG.N7 | 115 | 5.4317 | 5.4317 | 0
GEN-2018-131 | 02 NEBRASKA | 640560 | WAKEFIELD 4 | 230 | 7.9675 | 7.9675 | 0
GEN-2018-131 | 02 NEBRASKA | 640589 | SHOLES.W 3 | 345 | 9.0182 | 9.0181 | 0.0001
GEN-2018-131 | 02 NEBRASKA | 640598 | HAYSTACK.WD3 | 345 | 8.6554 | 8.6554 | 0
GEN-2018-131 | 02 NEBRASKA | 643271 | PLUMBCR.W 3 | 345 | 10.8968 | 10.8968 | 0
GEN-2018-131 | 02 NEBRASKA | 652564 | SIOUXCY3 | 345 | 15.3816 | 15.3816 | 0
GEN-2018-131 | 02 NEBRASKA | 762779 | G18-043-TAP | 345 | 15.621 | 15.621 | 0
GEN-2018-131 | 02 NEBRASKA | 763142 | GEN-2018-083 | 345 | 2.1648 | 2.1648 | 0
GEN-2018-131 | 02 NEBRASKA | 763978 | GEN-2019-069 | 345 | 11.2497 | 11.2497 | 0
GEN-2018-131 | 02 NEBRASKA | 45906 | J1590 SUB | 345 | 14.2602 | 14.2602 | 0
GEN-2018-131 | 02 NEBRASKA | 87486 | J748GENTIE | 345 | 13.2728 | 13.2728 | 0
GEN-2018-131 | 02 NEBRASKA | 635202 | NEAL S 5 | 161 | 22.3496 | 22.3496 | 0
GEN-2018-131 | 02 NEBRASKA | 635203 | NEAL N 5 | 161 | 25.6073 | 25.6073 | 0
GEN-2018-131 | 02 NEBRASKA | 635206 | IDA CO 3 | 345 | 9.3103 | 9.3103 | 0
GEN-2018-131 | 02 NEBRASKA | 635220 | INTCHG 5 | 161 | 14.526 | 14.526 | 0
GEN-2018-131 | 02 NEBRASKA | 635230 | LIBERTY5 | 161 | 24.9266 | 24.9266 | 0
GEN-2018-131 | 02 NEBRASKA | 635399 | CHEROKEE 3 | 345 | 15.9186 | 15.9186 | 0
GEN-2018-131 | 02 NEBRASKA | 640073 | BATTLCR8 | 69 | 3.8906 | 3.8905 | 0.0001
GEN-2018-131 | 02 NEBRASKA | 640081 | BELDEN 8 | 69 | 3.6996 | 3.6996 | 0
GEN-2018-131 | 02 NEBRASKA | 640085 | BLMFLD 8 | 69 | 3.7238 | 3.7238 | 0
GEN-2018-131 | 02 NEBRASKA | 640125 | COLMB.E3 | 345 | 10.209 | 10.209 | 0
GEN-2018-131 | 02 NEBRASKA | 640212 | HARTGTN7 | 115 | 5.1832 | 5.1832 | 0
GEN-2018-131 | 02 NEBRASKA | 640263 | MADISON7 | 115 | 6.1678 | 6.1678 | 0
GEN-2018-131 | 02 NEBRASKA | 640305 | ONEILL 7 | 115 | 3.9336 | 3.9336 | 0
GEN-2018-131 | 02 NEBRASKA | 640318 | PETRSBG7 | 115 | 5.4269 | 5.4269 | 0
GEN-2018-131 | 02 NEBRASKA | 640343 | SHELCRK4 | 230 | 10.8729 | 10.8729 | 0
GEN-2018-131 | 02 NEBRASKA | 640357 | STANTON7 | 115 | 5.115 | 5.115 | 0
GEN-2018-131 | 02 NEBRASKA | 640386 | TWIN CH4 | 230 | 8.9225 | 8.9225 | 0
GEN-2018-131 | 02 NEBRASKA | 640387 | TWIN CH7 | 115 | 10.7822 | 10.7822 | 0
GEN-2018-131 | 02 NEBRASKA | 640561 | RTLSNAKE.W 4 | 230 | 7.1132 | 7.1132 | 0
GEN-2018-131 | 02 NEBRASKA | 645451 | S3451 3 | 345 | 21.3318 | 21.3318 | 0
GEN-2018-131 | 02 NEBRASKA | 652511 | GAVINS 7 | 115 | 8.4307 | 8.4307 | 0
GEN-2018-131 | 02 NEBRASKA | 652552 | SIOUXCY2 | 230 | 20.341 | 20.341 | 0
GEN-2018-131 | 02 NEBRASKA | 652864 | SIOUXCY-LNX3 | 345 | 15.1969 | 15.1969 | 0
GEN-2018-131 | 02 NEBRASKA | 760788 | GEN-2017-201 | 345 | 8.2239 | 8.2239 | 0
GEN-2018-131 | 02 NEBRASKA | 762069 | G17-105TAP | 161 | 8.3472 | 8.3472 | 0
GEN-2018-131 | 02 NEBRASKA | 762780 | GEN-2018-043 | 345 | 12.7205 | 12.7205 | 0
GEN-2018-131 | 02 NEBRASKA | 601006 | SPLT RK3 | 345 | 14.9416 | 14.9416 | 0
GEN-2018-131 | 02 NEBRASKA | 635204 | NEAL N 8 | 69 | 9.7689 | 9.7689 | 0
GEN-2018-131 | 02 NEBRASKA | 635219 | GARD AVE 3 | 345 | 8.9677 | 8.9677 | 0
GEN-2018-131 | 02 NEBRASKA | 635221 | KELLOGG5 | 161 | 17.1226 | 17.1226 | 0
GEN-2018-131 | 02 NEBRASKA | 635229 | AIRPORT 5 | 161 | 16.9835 | 16.9835 | 0
GEN-2018-131 | 02 NEBRASKA | 635235 | SALIX 5 | 161 | 14.6126 | 14.6126 | 0
GEN-2018-131 | 02 NEBRASKA | 635300 | MONONA 5 | 161 | 5.4609 | 5.4609 | 0
GEN-2018-131 | 02 NEBRASKA | 635400 | HIGHLND 3 | 345 | 14.5121 | 14.5121 | 0
GEN-2018-131 | 02 NEBRASKA | 637009 | GLACIAL EDGE | 345 | 15.6443 | 15.6443 | 0
GEN-2018-131 | 02 NEBRASKA | 640054 | ALBION 7 | 115 | 5.1766 | 5.1766 | 0
GEN-2018-131 | 02 NEBRASKA | 640078 | BEEMER 7 | 115 | 4.396 | 4.396 | 0
GEN-2018-131 | 02 NEBRASKA | 640127 | COLMB.E7 | 115 | 22.1185 | 22.1185 | 0
GEN-2018-131 | 02 NEBRASKA | 640133 | COLMBUS4 | 230 | 11.4877 | 11.4876 | 0.0001
GEN-2018-131 | 02 NEBRASKA | 640151 | CRESTON7 | 115 | 5.9927 | 5.9927 | 0
GEN-2018-131 | 02 NEBRASKA | 640163 | EMERSON7 | 115 | 5.4485 | 5.4485 | 0
GEN-2018-131 | 02 NEBRASKA | 640213 | HARTGTN8 | 69 | 3.4988 | 3.4988 | 0
GEN-2018-131 | 02 NEBRASKA | 640306 | ONEILL 8 | 69 | 4.2323 | 4.2323 | 0
GEN-2018-131 | 02 NEBRASKA | 640349 | SPENCER7 | 115 | 4.7744 | 4.7744 | 0
GEN-2018-131 | 02 NEBRASKA | 640377 | TEKAMAH5 | 161 | 8.8894 | 8.8894 | 0
GEN-2018-131 | 02 NEBRASKA | 640388 | TWIN CH8 | 69 | 7.7842 | 7.7842 | 0
GEN-2018-131 | 02 NEBRASKA | 640424 | S.SIOUXCITY7 | 115 | 7.3706 | 7.3706 | 0
GEN-2018-131 | 02 NEBRASKA | 640465 | EAGLECREEK 7 | 115 | 3.0176 | 3.0176 | 0
GEN-2018-131 | 02 NEBRASKA | 645454 | S3454 3 | 345 | 27.4247 | 27.4247 | 0
GEN-2018-131 | 02 NEBRASKA | 645459 | S3459 3 | 345 | 24.0005 | 24.0005 | 0
GEN-2018-131 | 02 NEBRASKA | 646251 | S1251 5 | 161 | 30.7514 | 30.7514 | 0
GEN-2018-131 | 02 NEBRASKA | 650114 | NW68HOLDRG3 | 345 | 16.8066 | 16.8066 | 0
GEN-2018-131 | 02 NEBRASKA | 652565 | SIOUXCY4 | 230 | 20.341 | 20.341 | 0
GEN-2018-131 | 02 NEBRASKA | 659121 | SPIRIT_M-BE7 | 115 | 5.9966 | 5.9966 | 0
GEN-2018-131 | 02 NEBRASKA | 659900 | EAGLE___-NI4 | 230 | 7.3012 | 7.3012 | 0
GEN-2018-131 | 02 NEBRASKA | 660006 | YANKTON JCT7 | 115 | 7.9557 | 7.9557 | 0
GEN-2018-131 | 02 NEBRASKA | 762070 | GEN-2017-105 | 161 | 8.3472 | 8.3472 | 0
GEN-2018-131 | 02 NEBRASKA | 762603 | GEN-2018-025 | 345 | 20.4121 | 20.4121 | 0
GEN-2018-132 | 02 NEBRASKA | 640520 | ANTELOPE 3 | 345 | 6.9888 | 6.9887 | 0.0001
GEN-2018-132 | 02 NEBRASKA | 640226 | HOSKINS3 | 345 | 13.0113 | 13.0113 | 0
GEN-2018-132 | 02 NEBRASKA | 640521 | ANTELOPE 7 | 115 | 14.1104 | 14.1103 | 0.0001
GEN-2018-132 | 02 NEBRASKA | 763032 | GEN-2018-068 | 345 | 5.9447 | 5.9447 | 0
GEN-2018-132 | 02 NEBRASKA | 763439 | GEN-2018-131 | 345 | 6.9826 | 6.9826 | 0
GEN-2018-132 | 02 NEBRASKA | 635200 | RAUN 3 | 345 | 27.0138 | 27.0138 | 0
GEN-2018-132 | 02 NEBRASKA | 640115 | CO.LINE7 | 115 | 7.2295 | 7.2295 | 0
GEN-2018-132 | 02 NEBRASKA | 640149 | CREITON7 | 115 | 4.7116 | 4.7116 | 0
GEN-2018-132 | 02 NEBRASKA | 640227 | HOSKINS4 | 230 | 10.0896 | 10.0896 | 0
GEN-2018-132 | 02 NEBRASKA | 640228 | HOSKINS7 | 115 | 18.0994 | 18.0994 | 0
GEN-2018-132 | 02 NEBRASKA | 640293 | NELIGH 7 | 115 | 9.9449 | 9.9449 | 0
GEN-2018-132 | 02 NEBRASKA | 640522 | ANTELOPE 8 | 69 | 5.119 | 5.119 | 0
GEN-2018-132 | 02 NEBRASKA | 640588 | TURTLE.CRK 3 | 345 | 11.1479 | 11.1479 | 0
GEN-2018-132 | 02 NEBRASKA | 643254 | UPSTREAM.W 7 | 115 | 13.3751 | 13.375 | 0.0001
GEN-2018-132 | 02 NEBRASKA | 763450 | GEN-2018-132 | 345 | 6.6695 | 6.6694 | 0.0001
GEN-2018-132 | 02 NEBRASKA | 763982 | G19-069-TAP | 345 | 11.2849 | 11.2849 | 0
GEN-2018-132 | 02 NEBRASKA | 87487 | J748POI | 345 | 15.0615 | 15.0615 | 0
GEN-2018-132 | 02 NEBRASKA | 635201 | RAUN 5 | 161 | 27.0927 | 27.0927 | 0
GEN-2018-132 | 02 NEBRASKA | 635252 | J412 POI 3 | 345 | 9.6628 | 9.6628 | 0
GEN-2018-132 | 02 NEBRASKA | 635398 | REMSEN 3 | 345 | 14.4843 | 14.4843 | 0
GEN-2018-132 | 02 NEBRASKA | 640072 | BATTLCR7 | 115 | 7.3087 | 7.3087 | 0
GEN-2018-132 | 02 NEBRASKA | 640080 | BELDEN 7 | 115 | 5.9733 | 5.9733 | 0
GEN-2018-132 | 02 NEBRASKA | 640084 | BLMFLD 7 | 115 | 5.1275 | 5.1275 | 0
GEN-2018-132 | 02 NEBRASKA | 640113 | CLRWATR7 | 115 | 5.1516 | 5.1516 | 0
GEN-2018-132 | 02 NEBRASKA | 640150 | CREITON8 | 69 | 4.3586 | 4.3586 | 0
GEN-2018-132 | 02 NEBRASKA | 640294 | NELIGH 8 | 69 | 5.8977 | 5.8977 | 0
GEN-2018-132 | 02 NEBRASKA | 640296 | NORFK.N7 | 115 | 13.1793 | 13.1793 | 0
GEN-2018-132 | 02 NEBRASKA | 640298 | NORFOLK7 | 115 | 12.385 | 12.385 | 0
GEN-2018-132 | 02 NEBRASKA | 640342 | SHELCRK3 | 345 | 10.533 | 10.533 | 0
GEN-2018-132 | 02 NEBRASKA | 640363 | STNTN.N7 | 115 | 6.977 | 6.977 | 0
GEN-2018-132 | 02 NEBRASKA | 640444 | PETERSBRG.N7 | 115 | 5.4317 | 5.4317 | 0
GEN-2018-132 | 02 NEBRASKA | 640560 | WAKEFIELD 4 | 230 | 7.9675 | 7.9675 | 0
GEN-2018-132 | 02 NEBRASKA | 640589 | SHOLES.W 3 | 345 | 9.0182 | 9.0181 | 0.0001
GEN-2018-132 | 02 NEBRASKA | 640598 | HAYSTACK.WD3 | 345 | 8.6554 | 8.6554 | 0
GEN-2018-132 | 02 NEBRASKA | 643271 | PLUMBCR.W 3 | 345 | 10.8968 | 10.8968 | 0
GEN-2018-132 | 02 NEBRASKA | 652564 | SIOUXCY3 | 345 | 15.3816 | 15.3816 | 0
GEN-2018-132 | 02 NEBRASKA | 762779 | G18-043-TAP | 345 | 15.621 | 15.621 | 0
GEN-2018-132 | 02 NEBRASKA | 763142 | GEN-2018-083 | 345 | 2.1648 | 2.1648 | 0
GEN-2018-132 | 02 NEBRASKA | 763978 | GEN-2019-069 | 345 | 11.2497 | 11.2497 | 0
GEN-2018-132 | 02 NEBRASKA | 45906 | J1590 SUB | 345 | 14.2602 | 14.2602 | 0
GEN-2018-132 | 02 NEBRASKA | 87486 | J748GENTIE | 345 | 13.2728 | 13.2728 | 0
GEN-2018-132 | 02 NEBRASKA | 635202 | NEAL S 5 | 161 | 22.3496 | 22.3496 | 0
GEN-2018-132 | 02 NEBRASKA | 635203 | NEAL N 5 | 161 | 25.6073 | 25.6073 | 0
GEN-2018-132 | 02 NEBRASKA | 635206 | IDA CO 3 | 345 | 9.3103 | 9.3103 | 0
GEN-2018-132 | 02 NEBRASKA | 635220 | INTCHG 5 | 161 | 14.526 | 14.526 | 0
GEN-2018-132 | 02 NEBRASKA | 635230 | LIBERTY5 | 161 | 24.9266 | 24.9266 | 0
GEN-2018-132 | 02 NEBRASKA | 635399 | CHEROKEE 3 | 345 | 15.9186 | 15.9186 | 0
GEN-2018-132 | 02 NEBRASKA | 640073 | BATTLCR8 | 69 | 3.8906 | 3.8905 | 0.0001
GEN-2018-132 | 02 NEBRASKA | 640081 | BELDEN 8 | 69 | 3.6996 | 3.6996 | 0
GEN-2018-132 | 02 NEBRASKA | 640085 | BLMFLD 8 | 69 | 3.7238 | 3.7238 | 0
GEN-2018-132 | 02 NEBRASKA | 640125 | COLMB.E3 | 345 | 10.209 | 10.209 | 0
GEN-2018-132 | 02 NEBRASKA | 640212 | HARTGTN7 | 115 | 5.1832 | 5.1832 | 0
GEN-2018-132 | 02 NEBRASKA | 640263 | MADISON7 | 115 | 6.1678 | 6.1678 | 0
GEN-2018-132 | 02 NEBRASKA | 640305 | ONEILL 7 | 115 | 3.9336 | 3.9336 | 0
GEN-2018-132 | 02 NEBRASKA | 640318 | PETRSBG7 | 115 | 5.4269 | 5.4269 | 0
GEN-2018-132 | 02 NEBRASKA | 640343 | SHELCRK4 | 230 | 10.8729 | 10.8729 | 0
GEN-2018-132 | 02 NEBRASKA | 640357 | STANTON7 | 115 | 5.115 | 5.115 | 0
GEN-2018-132 | 02 NEBRASKA | 640386 | TWIN CH4 | 230 | 8.9225 | 8.9225 | 0
GEN-2018-132 | 02 NEBRASKA | 640387 | TWIN CH7 | 115 | 10.7822 | 10.7822 | 0
GEN-2018-132 | 02 NEBRASKA | 640561 | RTLSNAKE.W 4 | 230 | 7.1132 | 7.1132 | 0
GEN-2018-132 | 02 NEBRASKA | 645451 | S3451 3 | 345 | 21.3318 | 21.3318 | 0
GEN-2018-132 | 02 NEBRASKA | 652511 | GAVINS 7 | 115 | 8.4307 | 8.4307 | 0
GEN-2018-132 | 02 NEBRASKA | 652552 | SIOUXCY2 | 230 | 20.341 | 20.341 | 0
GEN-2018-132 | 02 NEBRASKA | 652864 | SIOUXCY-LNX3 | 345 | 15.1969 | 15.1969 | 0
GEN-2018-132 | 02 NEBRASKA | 760788 | GEN-2017-201 | 345 | 8.2239 | 8.2239 | 0
GEN-2018-132 | 02 NEBRASKA | 762069 | G17-105TAP | 161 | 8.3472 | 8.3472 | 0
GEN-2018-132 | 02 NEBRASKA | 762780 | GEN-2018-043 | 345 | 12.7205 | 12.7205 | 0
GEN-2018-132 | 02 NEBRASKA | 601006 | SPLT RK3 | 345 | 14.9416 | 14.9416 | 0
GEN-2018-132 | 02 NEBRASKA | 635204 | NEAL N 8 | 69 | 9.7689 | 9.7689 | 0
GEN-2018-132 | 02 NEBRASKA | 635219 | GARD AVE 3 | 345 | 8.9677 | 8.9677 | 0
GEN-2018-132 | 02 NEBRASKA | 635221 | KELLOGG5 | 161 | 17.1226 | 17.1226 | 0
GEN-2018-132 | 02 NEBRASKA | 635229 | AIRPORT 5 | 161 | 16.9835 | 16.9835 | 0
GEN-2018-132 | 02 NEBRASKA | 635235 | SALIX 5 | 161 | 14.6126 | 14.6126 | 0
GEN-2018-132 | 02 NEBRASKA | 635300 | MONONA 5 | 161 | 5.4609 | 5.4609 | 0
GEN-2018-132 | 02 NEBRASKA | 635400 | HIGHLND 3 | 345 | 14.5121 | 14.5121 | 0
GEN-2018-132 | 02 NEBRASKA | 637009 | GLACIAL EDGE | 345 | 15.6443 | 15.6443 | 0
GEN-2018-132 | 02 NEBRASKA | 640054 | ALBION 7 | 115 | 5.1766 | 5.1766 | 0
GEN-2018-132 | 02 NEBRASKA | 640078 | BEEMER 7 | 115 | 4.396 | 4.396 | 0
GEN-2018-132 | 02 NEBRASKA | 640127 | COLMB.E7 | 115 | 22.1185 | 22.1185 | 0
GEN-2018-132 | 02 NEBRASKA | 640133 | COLMBUS4 | 230 | 11.4877 | 11.4876 | 0.0001
GEN-2018-132 | 02 NEBRASKA | 640151 | CRESTON7 | 115 | 5.9927 | 5.9927 | 0
GEN-2018-132 | 02 NEBRASKA | 640163 | EMERSON7 | 115 | 5.4485 | 5.4485 | 0
GEN-2018-132 | 02 NEBRASKA | 640213 | HARTGTN8 | 69 | 3.4988 | 3.4988 | 0
GEN-2018-132 | 02 NEBRASKA | 640306 | ONEILL 8 | 69 | 4.2323 | 4.2323 | 0
GEN-2018-132 | 02 NEBRASKA | 640349 | SPENCER7 | 115 | 4.7744 | 4.7744 | 0
GEN-2018-132 | 02 NEBRASKA | 640377 | TEKAMAH5 | 161 | 8.8894 | 8.8894 | 0
GEN-2018-132 | 02 NEBRASKA | 640388 | TWIN CH8 | 69 | 7.7842 | 7.7842 | 0
GEN-2018-132 | 02 NEBRASKA | 640424 | S.SIOUXCITY7 | 115 | 7.3706 | 7.3706 | 0
GEN-2018-132 | 02 NEBRASKA | 640465 | EAGLECREEK 7 | 115 | 3.0176 | 3.0176 | 0
GEN-2018-132 | 02 NEBRASKA | 645454 | S3454 3 | 345 | 27.4247 | 27.4247 | 0
GEN-2018-132 | 02 NEBRASKA | 645459 | S3459 3 | 345 | 24.0005 | 24.0005 | 0
GEN-2018-132 | 02 NEBRASKA | 646251 | S1251 5 | 161 | 30.7514 | 30.7514 | 0
GEN-2018-132 | 02 NEBRASKA | 650114 | NW68HOLDRG3 | 345 | 16.8066 | 16.8066 | 0
GEN-2018-132 | 02 NEBRASKA | 652565 | SIOUXCY4 | 230 | 20.341 | 20.341 | 0
GEN-2018-132 | 02 NEBRASKA | 659121 | SPIRIT_M-BE7 | 115 | 5.9966 | 5.9966 | 0
GEN-2018-132 | 02 NEBRASKA | 659900 | EAGLE___-NI4 | 230 | 7.3012 | 7.3012 | 0
GEN-2018-132 | 02 NEBRASKA | 660006 | YANKTON JCT7 | 115 | 7.9557 | 7.9557 | 0
GEN-2018-132 | 02 NEBRASKA | 762070 | GEN-2017-105 | 161 | 8.3472 | 8.3472 | 0
GEN-2018-132 | 02 NEBRASKA | 762603 | GEN-2018-025 | 345 | 20.4121 | 20.4121 | 0
GEN-2019-009 | 02 NEBRASKA | 646263 | S1263 5 | 161 | 8.0723 | 7.6451 | 0.4272
GEN-2019-009 | 02 NEBRASKA | 646258 | S1258 5 | 161 | 5.7477 | 5.6213 | 0.1264
GEN-2019-009 | 02 NEBRASKA | 646280 | S1280 5 | 161 | 9.9891 | 9.6801 | 0.309
GEN-2019-009 | 02 NEBRASKA | 647111 | W BROCK8 | 69 | 9.928 | 9.7405 | 0.1875
GEN-2019-009 | 02 NEBRASKA | 763505 | GEN-2019-009 | 161 | 7.7793 | 7.3523 | 0.427
GEN-2019-009 | 02 NEBRASKA | 640140 | COOPER 5 | 161 | 17.5768 | 17.4426 | 0.1342
GEN-2019-009 | 02 NEBRASKA | 640234 | HUMBOLT5 | 161 | 7.4773 | 7.368 | 0.1093
GEN-2019-009 | 02 NEBRASKA | 646366 | S1366 5 | 161 | 15.5031 | 15.4672 | 0.0359
GEN-2019-009 | 02 NEBRASKA | 647963 | S963 8 | 69 | 9.109 | 8.9602 | 0.1488
GEN-2019-009 | 02 NEBRASKA | 647967 | S967 8 | 69 | 4.6567 | 4.6296 | 0.0271
GEN-2019-009 | 02 NEBRASKA | 648600 | NC1HS 5 | 161 | 5.6282 | 5.5069 | 0.1213
GEN-2019-009 | 02 NEBRASKA | 648610 | NC2HS 5 | 161 | 5.6372 | 5.5155 | 0.1217
GEN-2019-009 | 02 NEBRASKA | 640139 | COOPER 3 | 345 | 27.7474 | 27.6884 | 0.059
GEN-2019-009 | 02 NEBRASKA | 640235 | HUMBOLT7 | 115 | 6.3901 | 6.344 | 0.0461
GEN-2019-009 | 02 NEBRASKA | 640446 | COOPER 8 | 69 | 4.5614 | 4.5575 | 0.0039
GEN-2019-009 | 02 NEBRASKA | 646244 | S1244 5 | 161 | 20.9436 | 20.9093 | 0.0343
GEN-2019-009 | 02 NEBRASKA | 646398 | S1398 5 | 161 | 6.4456 | 6.3847 | 0.0609
GEN-2019-009 | 02 NEBRASKA | 647101 | AUBRNT 8 | 69 | 5.5904 | 5.5417 | 0.0487
GEN-2019-009 | 02 NEBRASKA | 647866 | S6866 8 | 69 | 19.5754 | 19.5599 | 0.0155
GEN-2019-009 | 02 NEBRASKA | 647968 | S968 8 | 69 | 4.1188 | 4.1034 | 0.0154
GEN-2019-009 | 02 NEBRASKA | 647973 | S973 8 | 69 | 3.4857 | 3.4635 | 0.0222
GEN-2019-009 | 02 NEBRASKA | 647975 | S975 8 | 69 | 6.0101 | 5.9707 | 0.0394
GEN-2019-009 | 02 NEBRASKA | 647977 | S977 8 | 69 | 5.1816 | 5.1483 | 0.0333
GEN-2019-009 | 02 NEBRASKA | 300039 | 7FAIRPT | 345 | 12.385 | 12.3819 | 0.0031
GEN-2019-009 | 02 NEBRASKA | 541199 | ST JOE 7 | 345 | 19.8132 | 19.8081 | 0.0051
GEN-2019-009 | 02 NEBRASKA | 635017 | ATCHSN 3 | 345 | 21.5201 | 21.4986 | 0.0215
GEN-2019-009 | 02 NEBRASKA | 640062 | AUBURN 8 | 69 | 3.991 | 3.966 | 0.025
GEN-2019-009 | 02 NEBRASKA | 640141 | COOPER_ESST8 | 69 | 4.4681 | 4.4643 | 0.0038
GEN-2019-009 | 02 NEBRASKA | 640143 | COOPER_602 8 | 69 | 1.9188 | 1.912 | 0.0068
GEN-2019-009 | 02 NEBRASKA | 640361 | STEINER7 | 115 | 4.36 | 4.3495 | 0.0105
GEN-2019-009 | 02 NEBRASKA | 640590 | MONOLITH 3 | 345 | 21.9978 | 21.987 | 0.0108
GEN-2019-009 | 02 NEBRASKA | 645458 | S3458 3 | 345 | 28.556 | 28.5334 | 0.0226
GEN-2019-009 | 02 NEBRASKA | 646206 | S1206 5 | 161 | 41.6222 | 41.5766 | 0.0456
GEN-2019-009 | 02 NEBRASKA | 646399 | S1399 5 | 161 | 6.2054 | 6.1576 | 0.0478
GEN-2019-009 | 02 NEBRASKA | 647107 | SAC623 8 | 69 | 17.3196 | 17.3088 | 0.0108
GEN-2019-009 | 02 NEBRASKA | 647400 | TECUMSH8 | 69 | 2.7952 | 2.7883 | 0.0069
GEN-2019-009 | 02 NEBRASKA | 647401 | NCU903 8 | 69 | 4.5553 | 4.537 | 0.0183
GEN-2019-009 | 02 NEBRASKA | 647964 | S964 8 | 69 | 2.2676 | 2.262 | 0.0056
GEN-2019-009 | 02 NEBRASKA | 647965 | S965 8 | 69 | 4.7404 | 4.7157 | 0.0247
GEN-2019-009 | 02 NEBRASKA | 647969 | S969 8 | 69 | 4.1582 | 4.1493 | 0.0089
GEN-2019-009 | 02 NEBRASKA | 647994 | S994 8 | 69 | 11.9029 | 11.8985 | 0.0044
GEN-2019-009 | 02 NEBRASKA | 301559 | 5FAIRPTXF3 | 161 | 16.4955 | 16.4941 | 0.0014
GEN-2019-009 | 02 NEBRASKA | 532913 | KELLY 5 | 161 | 6.2219 | 6.201 | 0.0209
GEN-2019-009 | 02 NEBRASKA | 541253 | ST JOE 5 | 161 | 19.5554 | 19.5534 | 0.002
GEN-2019-009 | 02 NEBRASKA | 541400 | EASTOWN7 | 345 | 18.2958 | 18.2925 | 0.0033
GEN-2019-009 | 02 NEBRASKA | 541510 | HOLT 7 | 345 | 17.6874 | 17.677 | 0.0104
GEN-2019-009 | 02 NEBRASKA | 635001 | CBLUFFS5 | 161 | 37.3755 | 37.362 | 0.0135
GEN-2019-009 | 02 NEBRASKA | 635018 | WESTBORO 3 | 345 | 19.9458 | 19.9282 | 0.0176
GEN-2019-009 | 02 NEBRASKA | 640076 | BEATRCE7 | 115 | 12.5236 | 12.5185 | 0.0051
GEN-2019-009 | 02 NEBRASKA | 640277 | MOORE 3 | 345 | 22.4804 | 22.4695 | 0.0109
GEN-2019-009 | 02 NEBRASKA | 640591 | MONOLITH 7 | 115 | 41.1825 | 41.1662 | 0.0163
GEN-2019-009 | 02 NEBRASKA | 645456 | S3456 3 | 345 | 32.5395 | 32.5172 | 0.0223
GEN-2019-009 | 02 NEBRASKA | 645740 | S3740 3 | 345 | 21.8202 | 21.8108 | 0.0094
GEN-2019-009 | 02 NEBRASKA | 646201 | S1201 5 | 161 | 29.9366 | 29.9228 | 0.0138
GEN-2019-009 | 02 NEBRASKA | 646216 | S1216 5 | 161 | 28.8927 | 28.8764 | 0.0163
GEN-2019-009 | 02 NEBRASKA | 646232 | S1232 5 | 161 | 25.1486 | 25.1353 | 0.0133
GEN-2019-009 | 02 NEBRASKA | 647006 | S906 N 8 | 69 | 30.5075 | 30.4964 | 0.0111
GEN-2019-009 | 02 NEBRASKA | 647016 | 6815TP38 | 69 | 16.6478 | 16.6395 | 0.0083
GEN-2019-009 | 02 NEBRASKA | 647108 | SAC629 8 | 69 | 11.3501 | 11.3471 | 0.003
GEN-2019-009 | 02 NEBRASKA | 647109 | SAC SO 8 | 69 | 9.3054 | 9.3023 | 0.0031
GEN-2019-009 | 02 NEBRASKA | 647112 | MGLN TP8 | 69 | 1.8852 | 1.8813 | 0.0039
GEN-2019-009 | 02 NEBRASKA | 647906 | S906 S 8 | 69 | 30.9225 | 30.9055 | 0.017
GEN-2019-009 | 02 NEBRASKA | 647962 | S962 8 | 69 | 4.7865 | 4.7748 | 0.0117
GEN-2019-009 | 02 NEBRASKA | 647966 | S966 8 | 69 | 0.4691 | 0.469 | 0.0001
GEN-2019-009 | 02 NEBRASKA | 647974 | S974 8 | 69 | 5.5119 | 5.5039 | 0.008
GEN-2019-009 | 02 NEBRASKA | 647995 | S995 8 | 69 | 9.0211 | 9.02 | 0.0011
GEN-2019-009 | 02 NEBRASKA | 650189 | 103&ROKEBY3 | 345 | 19.9772 | 19.9686 | 0.0086
GEN-2019-009 | 02 NEBRASKA | 761383 | G17-183-TAP | 345 | 17.119 | 17.1172 | 0.0018
GEN-2019-029 | 02 NEBRASKA | 763666 | G19-029 TAP | 345 | 7.5898 | 6.9356 | 0.6542
GEN-2019-029 | 02 NEBRASKA | 640252 | KEYSTON3 | 345 | 9.0821 | 8.5825 | 0.4996
GEN-2019-029 | 02 NEBRASKA | 659425 | SD.LS-KS-MB3 | 345 | 6.1743 | 5.988 | 0.1863
GEN-2019-029 | 02 NEBRASKA | 763659 | GEN-2019-029 | 345 | 6.3464 | 5.6785 | 0.6679
GEN-2019-029 | 02 NEBRASKA | 763681 | GEN-2019-033 | 345 | 6.7099 | 6.1996 | 0.5103
GEN-2019-029 | 02 NEBRASKA | 640183 | GENTLMN3 | 345 | 15.5779 | 15.2312 | 0.3467
GEN-2019-029 | 02 NEBRASKA | 640253 | KEYSTON7 | 115 | 14.5686 | 14.2878 | 0.2808
GEN-2019-029 | 02 NEBRASKA | 659133 | SIDNEY__-MB3 | 345 | 6.1743 | 5.988 | 0.1863
GEN-2019-029 | 02 NEBRASKA | 640184 | GENTLMN4 | 230 | 18.6782 | 18.4486 | 0.2296
GEN-2019-029 | 02 NEBRASKA | 640255 | KINGSLY7 | 115 | 8.9942 | 8.8938 | 0.1004
GEN-2019-029 | 02 NEBRASKA | 640304 | OGALALANPPD7 | 115 | 14.5859 | 14.3642 | 0.2217
GEN-2019-029 | 02 NEBRASKA | 640325 | REDWILO3 | 345 | 6.1522 | 6.1266 | 0.0256
GEN-2019-029 | 02 NEBRASKA | 640374 | SWEET W3 | 345 | 10.1673 | 10.1304 | 0.0369
GEN-2019-029 | 02 NEBRASKA | 640500 | THEDFRD3 | 345 | 5.6561 | 5.6315 | 0.0246
GEN-2019-029 | 02 NEBRASKA | 659135 | STEGALL_-MB3 | 345 | 4.7987 | 4.7481 | 0.0506
GEN-2019-029 | 02 NEBRASKA | 659210 | SIDNEY__-MB4 | 230 | 7.0467 | 6.9035 | 0.1432
GEN-2019-029 | 02 NEBRASKA | 659426 | SD.LS-LR-MB3 | 345 | 6.1743 | 5.988 | 0.1863
GEN-2019-029 | 02 NEBRASKA | 763410 | G18-125-TAP | 345 | 7.096 | 7.0573 | 0.0387
GEN-2019-029 | 02 NEBRASKA | 531451 | MINGO 7 | 345 | 6.0094 | 6.0021 | 0.0073
GEN-2019-029 | 02 NEBRASKA | 587680 | GEN-2016-074 | 345 | 5.9023 | 5.8905 | 0.0118
GEN-2019-029 | 02 NEBRASKA | 640065 | AXTELL 3 | 345 | 9.208 | 9.1956 | 0.0124
GEN-2019-029 | 02 NEBRASKA | 640286 | N.PLATT4 | 230 | 12.7581 | 12.663 | 0.0951
GEN-2019-029 | 02 NEBRASKA | 640302 | OGALALA4 | 230 | 7.9617 | 7.8559 | 0.1058
GEN-2019-029 | 02 NEBRASKA | 640326 | REDWILO7 | 115 | 10.8676 | 10.8406 | 0.027
GEN-2019-029 | 02 NEBRASKA | 640381 | THEDFRD7 | 115 | 9.0544 | 9.0357 | 0.0187
GEN-2019-029 | 02 NEBRASKA | 640510 | HOLT.CO3 | 345 | 7.9834 | 7.9761 | 0.0073
GEN-2019-029 | 02 NEBRASKA | 640529 | BOBCAT.C 3 | 345 | 4.7987 | 4.7481 | 0.0506
GEN-2019-029 | 02 NEBRASKA | 653571 | GR ISLD3 | 345 | 12.2807 | 12.2653 | 0.0154
GEN-2019-029 | 02 NEBRASKA | 659131 | LARAMIE_-MB3 | 345 | 6.7811 | 6.73 | 0.0511
GEN-2019-029 | 02 NEBRASKA | 659134 | SIDNEY___TS4 | 230 | 6.7958 | 6.6666 | 0.1292
GEN-2019-029 | 02 NEBRASKA | 659206 | STEGALL_-MB4 | 230 | 5.3565 | 5.3177 | 0.0388
GEN-2019-029 | 02 NEBRASKA | 659800 | GRANTNB_-TS7 | 115 | 6.2302 | 6.1948 | 0.0354
GEN-2019-029 | 02 NEBRASKA | 659801 | OGALALA_-TS7 | 115 | 14.5859 | 14.3642 | 0.2217
GEN-2019-029 | 02 NEBRASKA | 763406 | GEN-2018-125 | 345 | 6.7903 | 6.7552 | 0.0351
GEN-2019-029 | 02 NEBRASKA | 531429 | MINGO 3 | 115 | 12.2091 | 12.2007 | 0.0084
GEN-2019-029 | 02 NEBRASKA | 531465 | SETAB 7 | 345 | 6.866 | 6.8629 | 0.0031
GEN-2019-029 | 02 NEBRASKA | 531632 | GEN-2015-065 | 345 | 5.3136 | 5.3081 | 0.0055
GEN-2019-029 | 02 NEBRASKA | 560082 | G16-050-TAP | 345 | 6.9512 | 6.9464 | 0.0048
GEN-2019-029 | 02 NEBRASKA | 584650 | GEN-2015-023 | 345 | 7.9179 | 7.9107 | 0.0072
GEN-2019-029 | 02 NEBRASKA | 640066 | AXTELL 7 | 115 | 14.0353 | 14.0257 | 0.0096
GEN-2019-029 | 02 NEBRASKA | 640082 | BEVERLY7 | 115 | 4.6682 | 4.6607 | 0.0075
GEN-2019-029 | 02 NEBRASKA | 640091 | BRULE 7 | 115 | 5.3754 | 5.3454 | 0.03
GEN-2019-029 | 02 NEBRASKA | 640093 | C.CREEK4 | 230 | 6.8775 | 6.8681 | 0.0094
GEN-2019-029 | 02 NEBRASKA | 640096 | CALAMS 7 | 115 | 3.3654 | 3.3643 | 0.0011
GEN-2019-029 | 02 NEBRASKA | 640167 | ENDERS 7 | 115 | 3.7071 | 3.6983 | 0.0088
GEN-2019-029 | 02 NEBRASKA | 640200 | GR ISLD4 | 230 | 16.413 | 16.3971 | 0.0159
GEN-2019-029 | 02 NEBRASKA | 640269 | MCCOOK 7 | 115 | 8.2673 | 8.2536 | 0.0137
GEN-2019-029 | 02 NEBRASKA | 640271 | MCCOOL 3 | 345 | 10.8752 | 10.8702 | 0.005
GEN-2019-029 | 02 NEBRASKA | 640287 | N.PLATT7 | 115 | 17.9774 | 17.8865 | 0.0909
GEN-2019-029 | 02 NEBRASKA | 640312 | PAULINE3 | 345 | 7.8813 | 7.877 | 0.0043
GEN-2019-029 | 02 NEBRASKA | 640359 | STAPLETON 7 | 115 | 4.0511 | 4.0474 | 0.0037
GEN-2019-029 | 02 NEBRASKA | 640365 | STOCKVL7 | 115 | 4.448 | 4.4432 | 0.0048
GEN-2019-029 | 02 NEBRASKA | 640530 | BOBCAT.C 7 | 115 | 8.4233 | 8.3726 | 0.0507
GEN-2019-029 | 02 NEBRASKA | 652573 | STEGALL4 | 230 | 5.116 | 5.0813 | 0.0347
GEN-2019-029 | 02 NEBRASKA | 652832 | GRPRAR1-LNX3 | 345 | 7.4489 | 7.4457 | 0.0032
GEN-2019-029 | 02 NEBRASKA | 653572 | SIDNEY 7 | 115 | 4.4251 | 4.4013 | 0.0238
GEN-2019-029 | 02 NEBRASKA | 653871 | GR ISLD-LNX3 | 345 | 12.1609 | 12.1458 | 0.0151
GEN-2019-029 | 02 NEBRASKA | 659809 | ROSCOE__-TS7 | 115 | 6.3148 | 6.2815 | 0.0333
GEN-2019-029 | 02 NEBRASKA | 659810 | SPCREEK_-TS7 | 115 | 4.3326 | 4.3162 | 0.0164
GEN-2019-029 | 02 NEBRASKA | 659824 | MCONGHY_-TS7 | 115 | 5.3378 | 5.308 | 0.0298
GEN-2019-029 | 02 NEBRASKA | 760767 | GEN-2017-144 | 345 | 7.6478 | 7.6412 | 0.0066
GEN-2019-033 | 02 NEBRASKA | 763666 | G19-029 TAP | 345 | 7.5898 | 7.2445 | 0.3453
GEN-2019-033 | 02 NEBRASKA | 640252 | KEYSTON3 | 345 | 9.0821 | 8.8225 | 0.2596
GEN-2019-033 | 02 NEBRASKA | 659425 | SD.LS-KS-MB3 | 345 | 6.1743 | 6.0787 | 0.0956
GEN-2019-033 | 02 NEBRASKA | 763659 | GEN-2019-029 | 345 | 6.3464 | 6.1128 | 0.2336
GEN-2019-033 | 02 NEBRASKA | 763681 | GEN-2019-033 | 345 | 6.7099 | 6.3623 | 0.3476
GEN-2019-033 | 02 NEBRASKA | 640183 | GENTLMN3 | 345 | 15.5779 | 15.4007 | 0.1772
GEN-2019-033 | 02 NEBRASKA | 640253 | KEYSTON7 | 115 | 14.5686 | 14.4254 | 0.1432
GEN-2019-033 | 02 NEBRASKA | 659133 | SIDNEY__-MB3 | 345 | 6.1743 | 6.0787 | 0.0956
GEN-2019-033 | 02 NEBRASKA | 640184 | GENTLMN4 | 230 | 18.6782 | 18.5614 | 0.1168
GEN-2019-033 | 02 NEBRASKA | 640255 | KINGSLY7 | 115 | 8.9942 | 8.9432 | 0.051
GEN-2019-033 | 02 NEBRASKA | 640304 | OGALALANPPD7 | 115 | 14.5859 | 14.473 | 0.1129
GEN-2019-033 | 02 NEBRASKA | 640325 | REDWILO3 | 345 | 6.1522 | 6.1392 | 0.013
GEN-2019-033 | 02 NEBRASKA | 640374 | SWEET W3 | 345 | 10.1673 | 10.1486 | 0.0187
GEN-2019-033 | 02 NEBRASKA | 640500 | THEDFRD3 | 345 | 5.6561 | 5.6436 | 0.0125
GEN-2019-033 | 02 NEBRASKA | 659135 | STEGALL_-MB3 | 345 | 4.7987 | 4.773 | 0.0257
GEN-2019-033 | 02 NEBRASKA | 659210 | SIDNEY__-MB4 | 230 | 7.0467 | 6.9736 | 0.0731
GEN-2019-033 | 02 NEBRASKA | 659426 | SD.LS-LR-MB3 | 345 | 6.1743 | 6.0787 | 0.0956
GEN-2019-033 | 02 NEBRASKA | 763410 | G18-125-TAP | 345 | 7.096 | 7.0764 | 0.0196
GEN-2019-033 | 02 NEBRASKA | 531451 | MINGO 7 | 345 | 6.0094 | 6.0057 | 0.0037
GEN-2019-033 | 02 NEBRASKA | 587680 | GEN-2016-074 | 345 | 5.9023 | 5.8963 | 0.006
GEN-2019-033 | 02 NEBRASKA | 640065 | AXTELL 3 | 345 | 9.208 | 9.2017 | 0.0063
GEN-2019-033 | 02 NEBRASKA | 640286 | N.PLATT4 | 230 | 12.7581 | 12.7098 | 0.0483
GEN-2019-033 | 02 NEBRASKA | 640302 | OGALALA4 | 230 | 7.9617 | 7.9078 | 0.0539
GEN-2019-033 | 02 NEBRASKA | 640326 | REDWILO7 | 115 | 10.8676 | 10.8539 | 0.0137
GEN-2019-033 | 02 NEBRASKA | 640381 | THEDFRD7 | 115 | 9.0544 | 9.045 | 0.0094
GEN-2019-033 | 02 NEBRASKA | 640510 | HOLT.CO3 | 345 | 7.9834 | 7.9797 | 0.0037
GEN-2019-033 | 02 NEBRASKA | 640529 | BOBCAT.C 3 | 345 | 4.7987 | 4.773 | 0.0257
GEN-2019-033 | 02 NEBRASKA | 653571 | GR ISLD3 | 345 | 12.2807 | 12.2729 | 0.0078
GEN-2019-033 | 02 NEBRASKA | 659131 | LARAMIE_-MB3 | 345 | 6.7811 | 6.7552 | 0.0259
GEN-2019-033 | 02 NEBRASKA | 659134 | SIDNEY___TS4 | 230 | 6.7958 | 6.7299 | 0.0659
GEN-2019-033 | 02 NEBRASKA | 659206 | STEGALL_-MB4 | 230 | 5.3565 | 5.3368 | 0.0197
GEN-2019-033 | 02 NEBRASKA | 659800 | GRANTNB_-TS7 | 115 | 6.2302 | 6.2123 | 0.0179
GEN-2019-033 | 02 NEBRASKA | 659801 | OGALALA_-TS7 | 115 | 14.5859 | 14.473 | 0.1129
GEN-2019-033 | 02 NEBRASKA | 763406 | GEN-2018-125 | 345 | 6.7903 | 6.7725 | 0.0178
GEN-2019-033 | 02 NEBRASKA | 531429 | MINGO 3 | 115 | 12.2091 | 12.2049 | 0.0042
GEN-2019-033 | 02 NEBRASKA | 531465 | SETAB 7 | 345 | 6.866 | 6.8645 | 0.0015
GEN-2019-033 | 02 NEBRASKA | 531632 | GEN-2015-065 | 345 | 5.3136 | 5.3108 | 0.0028
GEN-2019-033 | 02 NEBRASKA | 560082 | G16-050-TAP | 345 | 6.9512 | 6.9488 | 0.0024
GEN-2019-033 | 02 NEBRASKA | 584650 | GEN-2015-023 | 345 | 7.9179 | 7.9142 | 0.0037
GEN-2019-033 | 02 NEBRASKA | 640066 | AXTELL 7 | 115 | 14.0353 | 14.0305 | 0.0048
GEN-2019-033 | 02 NEBRASKA | 640082 | BEVERLY7 | 115 | 4.6682 | 4.6644 | 0.0038
GEN-2019-033 | 02 NEBRASKA | 640091 | BRULE 7 | 115 | 5.3754 | 5.3602 | 0.0152
GEN-2019-033 | 02 NEBRASKA | 640093 | C.CREEK4 | 230 | 6.8775 | 6.8727 | 0.0048
GEN-2019-033 | 02 NEBRASKA | 640096 | CALAMS 7 | 115 | 3.3654 | 3.3648 | 0.0006
GEN-2019-033 | 02 NEBRASKA | 640167 | ENDERS 7 | 115 | 3.7071 | 3.7027 | 0.0044
GEN-2019-033 | 02 NEBRASKA | 640200 | GR ISLD4 | 230 | 16.413 | 16.405 | 0.008
GEN-2019-033 | 02 NEBRASKA | 640269 | MCCOOK 7 | 115 | 8.2673 | 8.2604 | 0.0069
GEN-2019-033 | 02 NEBRASKA | 640271 | MCCOOL 3 | 345 | 10.8752 | 10.8727 | 0.0025
GEN-2019-033 | 02 NEBRASKA | 640287 | N.PLATT7 | 115 | 17.9774 | 17.9313 | 0.0461
GEN-2019-033 | 02 NEBRASKA | 640312 | PAULINE3 | 345 | 7.8813 | 7.8791 | 0.0022
GEN-2019-033 | 02 NEBRASKA | 640359 | STAPLETON 7 | 115 | 4.0511 | 4.0493 | 0.0018
GEN-2019-033 | 02 NEBRASKA | 640365 | STOCKVL7 | 115 | 4.448 | 4.4456 | 0.0024
GEN-2019-033 | 02 NEBRASKA | 640530 | BOBCAT.C 7 | 115 | 8.4233 | 8.3976 | 0.0257
GEN-2019-033 | 02 NEBRASKA | 652573 | STEGALL4 | 230 | 5.116 | 5.0984 | 0.0176
GEN-2019-033 | 02 NEBRASKA | 652832 | GRPRAR1-LNX3 | 345 | 7.4489 | 7.4473 | 0.0016
GEN-2019-033 | 02 NEBRASKA | 653572 | SIDNEY 7 | 115 | 4.4251 | 4.413 | 0.0121
GEN-2019-033 | 02 NEBRASKA | 653871 | GR ISLD-LNX3 | 345 | 12.1609 | 12.1532 | 0.0077
GEN-2019-033 | 02 NEBRASKA | 659809 | ROSCOE__-TS7 | 115 | 6.3148 | 6.2979 | 0.0169
GEN-2019-033 | 02 NEBRASKA | 659810 | SPCREEK_-TS7 | 115 | 4.3326 | 4.3243 | 0.0083
GEN-2019-033 | 02 NEBRASKA | 659824 | MCONGHY_-TS7 | 115 | 5.3378 | 5.3227 | 0.0151
GEN-2019-033 | 02 NEBRASKA | 760767 | GEN-2017-144 | 345 | 7.6478 | 7.6445 | 0.0033
GEN-2019-039 | 02 NEBRASKA | 763718 | G19-039-TAP | 115 | 8.1446 | 8.1445 | 0.0001
GEN-2019-039 | 02 NEBRASKA | 640124 | COL.SE 7 | 115 | 16.6202 | 16.6201 | 0.0001
GEN-2019-039 | 02 NEBRASKA | 640328 | RISNGCY7 | 115 | 5.9719 | 5.9719 | 0
GEN-2019-039 | 02 NEBRASKA | 763714 | GEN-2019-039 | 115 | 8.118 | 8.1179 | 0.0001
GEN-2019-039 | 02 NEBRASKA | 640119 | COL.COG7 | 115 | 19.5195 | 19.5195 | 0
GEN-2019-039 | 02 NEBRASKA | 640136 | COLMBUS7 | 115 | 19.1401 | 19.14 | 0.0001
GEN-2019-039 | 02 NEBRASKA | 640340 | SEWARD 7 | 115 | 7.3414 | 7.3414 | 0
GEN-2019-039 | 02 NEBRASKA | 640417 | RISNGCY8 | 69 | 3.6925 | 3.6925 | 0
GEN-2019-039 | 02 NEBRASKA | 640122 | COL.DRY7 | 115 | 16.4842 | 16.4841 | 0.0001
GEN-2019-039 | 02 NEBRASKA | 640127 | COLMB.E7 | 115 | 22.1185 | 22.1185 | 0
GEN-2019-039 | 02 NEBRASKA | 640134 | KELLY 7 | 115 | 17.6974 | 17.6974 | 0
GEN-2019-039 | 02 NEBRASKA | 640151 | CRESTON7 | 115 | 5.9927 | 5.9927 | 0
GEN-2019-039 | 02 NEBRASKA | 640181 | GENOA 7 | 115 | 4.8706 | 4.8706 | 0
GEN-2019-039 | 02 NEBRASKA | 640316 | PAWNEEL7 | 115 | 11.1764 | 11.1764 | 0
GEN-2019-039 | 02 NEBRASKA | 640336 | SCHUYLR7 | 115 | 5.8 | 5.8 | 0
GEN-2019-039 | 02 NEBRASKA | 640345 | SILVRCK7 | 115 | 4.5561 | 4.5561 | 0
GEN-2019-039 | 02 NEBRASKA | 640375 | TAMORA 7 | 115 | 5.8391 | 5.8391 | 0
GEN-2019-039 | 02 NEBRASKA | 640054 | ALBION 7 | 115 | 5.1766 | 5.1766 | 0
GEN-2019-039 | 02 NEBRASKA | 640107 | CENCITY7 | 115 | 5.0369 | 5.0369 | 0
GEN-2019-039 | 02 NEBRASKA | 640125 | COLMB.E3 | 345 | 10.209 | 10.209 | 0
GEN-2019-039 | 02 NEBRASKA | 640126 | E.COL. 4 | 230 | 10.0667 | 10.0666 | 0.0001
GEN-2019-039 | 02 NEBRASKA | 640133 | COLMBUS4 | 230 | 11.4877 | 11.4876 | 0.0001
GEN-2019-039 | 02 NEBRASKA | 640157 | DAVIDCY7 | 115 | 5.6545 | 5.6545 | 0
GEN-2019-039 | 02 NEBRASKA | 640263 | MADISON7 | 115 | 6.1678 | 6.1678 | 0
GEN-2019-039 | 02 NEBRASKA | 640281 | N.BEND 7 | 115 | 4.7168 | 4.7168 | 0
GEN-2019-039 | 02 NEBRASKA | 640346 | SILVRCK8 | 69 | 4.049 | 4.049 | 0
GEN-2019-039 | 02 NEBRASKA | 640411 | YORK 7 | 115 | 7.4827 | 7.4827 | 0
GEN-2019-039 | 02 NEBRASKA | 640468 | TAMORA 8 | 69 | 3.9346 | 3.9346 | 0
GEN-2019-039 | 02 NEBRASKA | 650214 | NW68HOLDRG7 | 115 | 24.3952 | 24.3952 | 0
GEN-2019-039 | 02 NEBRASKA | 640063 | AURORA_7 | 115 | 6.9169 | 6.9169 | 0
GEN-2019-039 | 02 NEBRASKA | 640131 | COLMB.W4 | 230 | 9.8308 | 9.8308 | 0
GEN-2019-039 | 02 NEBRASKA | 640173 | FREMONT7 | 115 | 5.9814 | 5.9814 | 0
GEN-2019-039 | 02 NEBRASKA | 640176 | FULERTN7 | 115 | 2.5435 | 2.5435 | 0
GEN-2019-039 | 02 NEBRASKA | 640201 | GR ISLD7 | 115 | 22.4767 | 22.4767 | 0
GEN-2019-039 | 02 NEBRASKA | 640298 | NORFOLK7 | 115 | 12.385 | 12.385 | 0
GEN-2019-039 | 02 NEBRASKA | 640318 | PETRSBG7 | 115 | 5.4269 | 5.4269 | 0
GEN-2019-039 | 02 NEBRASKA | 640342 | SHELCRK3 | 345 | 10.533 | 10.533 | 0
GEN-2019-039 | 02 NEBRASKA | 640343 | SHELCRK4 | 230 | 10.8729 | 10.8729 | 0
GEN-2019-039 | 02 NEBRASKA | 640347 | SPALDNG7 | 115 | 3.7496 | 3.7496 | 0
GEN-2019-039 | 02 NEBRASKA | 640402 | WAHOO 7 | 115 | 4.7578 | 4.7578 | 0
GEN-2019-039 | 02 NEBRASKA | 640413 | YORK SW7 | 115 | 7.9943 | 7.9943 | 0
GEN-2019-039 | 02 NEBRASKA | 640443 | YORK 8 | 69 | 2.5434 | 2.5434 | 0
GEN-2019-039 | 02 NEBRASKA | 640540 | MEADOWGROVE4 | 230 | 5.0998 | 5.0998 | 0
GEN-2019-039 | 02 NEBRASKA | 650114 | NW68HOLDRG3 | 345 | 16.8066 | 16.8066 | 0
GEN-2019-039 | 02 NEBRASKA | 650210 | NW70FAIRFD7 | 115 | 20.3803 | 20.3803 | 0
GEN-2019-039 | 02 NEBRASKA | 650216 | SW27&F 7 | 115 | 21.0693 | 21.0693 | 0
GEN-2019-039 | 02 NEBRASKA | 650290 | ROKEBY 7 | 115 | 24.4224 | 24.4224 | 0
GEN-2019-041 | 02 NEBRASKA | 640591 | MONOLITH 7 | 115 | 41.1825 | 40.7765 | 0.406
GEN-2019-041 | 02 NEBRASKA | 560746 | G13-002-TAP | 115 | 41.1825 | 40.7765 | 0.406
GEN-2019-041 | 02 NEBRASKA | 640171 | FIRTH 7 | 115 | 6.6769 | 6.6685 | 0.0084
GEN-2019-041 | 02 NEBRASKA | 640278 | SHELDON7 | 115 | 42.1871 | 41.8345 | 0.3526
GEN-2019-041 | 02 NEBRASKA | 640590 | MONOLITH 3 | 345 | 21.9978 | 21.9192 | 0.0786
GEN-2019-041 | 02 NEBRASKA | 763725 | GEN-2019-041 | 115 | 41.0813 | 40.6753 | 0.406
GEN-2019-041 | 02 NEBRASKA | 583700 | GEN-2013-019 | 115 | 18.2402 | 18.1634 | 0.0768
GEN-2019-041 | 02 NEBRASKA | 640088 | BPS SUB7 | 115 | 15.1625 | 15.1491 | 0.0134
GEN-2019-041 | 02 NEBRASKA | 640111 | CLATONA7 | 115 | 10.381 | 10.3694 | 0.0116
GEN-2019-041 | 02 NEBRASKA | 640139 | COOPER 3 | 345 | 27.7474 | 27.7372 | 0.0102
GEN-2019-041 | 02 NEBRASKA | 640153 | CRETE__7 | 115 | 8.0252 | 8.0158 | 0.0094
GEN-2019-041 | 02 NEBRASKA | 640277 | MOORE 3 | 345 | 22.4804 | 22.4015 | 0.0789
GEN-2019-041 | 02 NEBRASKA | 640362 | STERLNG7 | 115 | 4.4925 | 4.4894 | 0.0031
GEN-2019-041 | 02 NEBRASKA | 650242 | FOLSM&PHIL7 | 115 | 26.4375 | 26.3833 | 0.0542
GEN-2019-041 | 02 NEBRASKA | 650246 | SW7&BENNET7 | 115 | 22.2667 | 22.219 | 0.0477
GEN-2019-041 | 02 NEBRASKA | 300039 | 7FAIRPT | 345 | 12.385 | 12.3845 | 0.0005
GEN-2019-041 | 02 NEBRASKA | 541199 | ST JOE 7 | 345 | 19.8132 | 19.8124 | 0.0008
GEN-2019-041 | 02 NEBRASKA | 635017 | ATCHSN 3 | 345 | 21.5201 | 21.5159 | 0.0042
GEN-2019-041 | 02 NEBRASKA | 640076 | BEATRCE7 | 115 | 12.5236 | 12.5154 | 0.0082
GEN-2019-041 | 02 NEBRASKA | 640140 | COOPER 5 | 161 | 17.5768 | 17.5747 | 0.0021
GEN-2019-041 | 02 NEBRASKA | 640174 | FRIEND 7 | 115 | 5.4338 | 5.4315 | 0.0023
GEN-2019-041 | 02 NEBRASKA | 640271 | MCCOOL 3 | 345 | 10.8752 | 10.8671 | 0.0081
GEN-2019-041 | 02 NEBRASKA | 640525 | TOBIAS 3 | 345 | 11.6744 | 11.6607 | 0.0137
GEN-2019-041 | 02 NEBRASKA | 645458 | S3458 3 | 345 | 28.556 | 28.5442 | 0.0118
GEN-2019-041 | 02 NEBRASKA | 647974 | S974 8 | 69 | 5.5119 | 5.5103 | 0.0016
GEN-2019-041 | 02 NEBRASKA | 650114 | NW68HOLDRG3 | 345 | 16.8066 | 16.7762 | 0.0304
GEN-2019-041 | 02 NEBRASKA | 650189 | 103&ROKEBY3 | 345 | 19.9772 | 19.9408 | 0.0364
GEN-2019-041 | 02 NEBRASKA | 650238 | 20PIONEERS7 | 115 | 26.0355 | 25.994 | 0.0415
GEN-2019-041 | 02 NEBRASKA | 650247 | 40&BENNET 7 | 115 | 20.4322 | 20.3986 | 0.0336
GEN-2019-041 | 02 NEBRASKA | 650290 | ROKEBY 7 | 115 | 24.4224 | 24.3786 | 0.0438
GEN-2019-041 | 02 NEBRASKA | 301559 | 5FAIRPTXF3 | 161 | 16.4955 | 16.4953 | 0.0002
GEN-2019-041 | 02 NEBRASKA | 541253 | ST JOE 5 | 161 | 19.5554 | 19.5551 | 0.0003
GEN-2019-041 | 02 NEBRASKA | 541400 | EASTOWN7 | 345 | 18.2958 | 18.2954 | 0.0004
GEN-2019-041 | 02 NEBRASKA | 541510 | HOLT 7 | 345 | 17.6874 | 17.6849 | 0.0025
GEN-2019-041 | 02 NEBRASKA | 585241 | GEN-2015-088 | 345 | 11.6744 | 11.6607 | 0.0137
GEN-2019-041 | 02 NEBRASKA | 635018 | WESTBORO 3 | 345 | 19.9458 | 19.9423 | 0.0035
GEN-2019-041 | 02 NEBRASKA | 640074 | BEAT. S7 | 115 | 5.1213 | 5.12 | 0.0013
GEN-2019-041 | 02 NEBRASKA | 640125 | COLMB.E3 | 345 | 10.209 | 10.2059 | 0.0031
GEN-2019-041 | 02 NEBRASKA | 640178 | GENEVA 7 | 115 | 9.4414 | 9.4387 | 0.0027
GEN-2019-041 | 02 NEBRASKA | 640208 | HARBINE7 | 115 | 6.561 | 6.5597 | 0.0013
GEN-2019-041 | 02 NEBRASKA | 640272 | MCCOOL 7 | 115 | 14.0002 | 13.9954 | 0.0048
GEN-2019-041 | 02 NEBRASKA | 640312 | PAULINE3 | 345 | 7.8813 | 7.8789 | 0.0024
GEN-2019-041 | 02 NEBRASKA | 640361 | STEINER7 | 115 | 4.36 | 4.3596 | 0.0004
GEN-2019-041 | 02 NEBRASKA | 640446 | COOPER 8 | 69 | 4.5614 | 4.5614 | 0
GEN-2019-041 | 02 NEBRASKA | 645456 | S3456 3 | 345 | 32.5395 | 32.5309 | 0.0086
GEN-2019-041 | 02 NEBRASKA | 645740 | S3740 3 | 345 | 21.8202 | 21.8146 | 0.0056
GEN-2019-041 | 02 NEBRASKA | 646280 | S1280 5 | 161 | 9.9891 | 9.9883 | 0.0008
GEN-2019-041 | 02 NEBRASKA | 647102 | HYDCAP 8 | 69 | 4.2637 | 4.263 | 0.0007
GEN-2019-041 | 02 NEBRASKA | 647969 | S969 8 | 69 | 4.1582 | 4.1576 | 0.0006
GEN-2019-041 | 02 NEBRASKA | 650185 | WAGENER 3 | 345 | 20.0853 | 20.0523 | 0.033
GEN-2019-041 | 02 NEBRASKA | 650214 | NW68HOLDRG7 | 115 | 24.3952 | 24.366 | 0.0292
GEN-2019-041 | 02 NEBRASKA | 650218 | 3&VANDORN 7 | 115 | 20.8494 | 20.8246 | 0.0248
GEN-2019-041 | 02 NEBRASKA | 650229 | 27&PLR 7 | 115 | 19.6739 | 19.6451 | 0.0288
GEN-2019-041 | 02 NEBRASKA | 650230 | 2&N 7 | 115 | 24.6985 | 24.6662 | 0.0323
GEN-2019-041 | 02 NEBRASKA | 650250 | 40&ROKEBY 7 | 115 | 20.2736 | 20.2426 | 0.031
GEN-2019-041 | 02 NEBRASKA | 650258 | 40&GERTIE 7 | 115 | 22.2532 | 22.2246 | 0.0286
GEN-2019-041 | 02 NEBRASKA | 650270 | 70&CALVERT7 | 115 | 26.1393 | 26.1023 | 0.037
GEN-2019-041 | 02 NEBRASKA | 650276 | 76&ROKEBY 7 | 115 | 17.0025 | 16.9815 | 0.021
GEN-2019-041 | 02 NEBRASKA | 653571 | GR ISLD3 | 345 | 12.2807 | 12.2766 | 0.0041
GEN-2019-041 | 02 NEBRASKA | 761208 | GEN-2017-210 | 345 | 9.5276 | 9.5216 | 0.006
GEN-2019-041 | 02 NEBRASKA | 761292 | GEN-2017-181 | 345 | 6.6467 | 6.6428 | 0.0039
GEN-2019-041 | 02 NEBRASKA | 761383 | G17-183-TAP | 345 | 17.119 | 17.1187 | 0.0003
GEN-2019-041 | 02 NEBRASKA | 300076 | 5FAIRPTB2 | 161 | 16.4807 | 16.4805 | 0.0002
GEN-2019-041 | 02 NEBRASKA | 541147 | ST JOE_CAP5 | 161 | 17.4799 | 17.4796 | 0.0003
GEN-2019-041 | 02 NEBRASKA | 541197 | MULLNCR7 | 345 | 11.613 | 11.6122 | 0.0008
GEN-2019-041 | 02 NEBRASKA | 541257 | COOK 5 | 161 | 13.7678 | 13.7677 | 0.0001
GEN-2019-041 | 02 NEBRASKA | 541258 | WOODBIN5 | 161 | 16.5442 | 16.544 | 0.0002
GEN-2019-041 | 02 NEBRASKA | 541394 | AVENUECTY 5 | 161 | 8.4761 | 8.4761 | 0
GEN-2019-041 | 02 NEBRASKA | 541401 | EASTOWN5 | 161 | 17.049 | 17.0488 | 0.0002
GEN-2019-041 | 02 NEBRASKA | 541511 | ROCKCK7 | 345 | 10.5304 | 10.5296 | 0.0008
GEN-2019-041 | 02 NEBRASKA | 541517 | HOLT_REACT7 | 345 | 17.5016 | 17.4992 | 0.0024
GEN-2019-041 | 02 NEBRASKA | 542980 | NASHUA 7 | 345 | 22.9207 | 22.9204 | 0.0003
GEN-2019-041 | 02 NEBRASKA | 542982 | IATAN 7 | 345 | 30.6944 | 30.694 | 0.0004
GEN-2019-041 | 02 NEBRASKA | 635000 | CBLUFFS3 | 345 | 29.9866 | 29.9823 | 0.0043
GEN-2019-041 | 02 NEBRASKA | 635570 | ORIENT 3 | 345 | 16.8003 | 16.7997 | 0.0006
GEN-2019-041 | 02 NEBRASKA | 637084 | J476 SHENHLL | 345 | 19.8162 | 19.8128 | 0.0034
GEN-2019-041 | 02 NEBRASKA | 640065 | AXTELL 3 | 345 | 9.208 | 9.2066 | 0.0014
GEN-2019-041 | 02 NEBRASKA | 640105 | CARLJCT7 | 115 | 5.3682 | 5.3676 | 0.0006
GEN-2019-041 | 02 NEBRASKA | 640127 | COLMB.E7 | 115 | 22.1185 | 22.115 | 0.0035
GEN-2019-041 | 02 NEBRASKA | 640141 | COOPER_ESST8 | 69 | 4.4681 | 4.468 | 0.0001
GEN-2019-041 | 02 NEBRASKA | 640143 | COOPER_602 8 | 69 | 1.9188 | 1.9188 | 0
GEN-2019-041 | 02 NEBRASKA | 640169 | FAIRBRY7 | 115 | 4.8779 | 4.8773 | 0.0006
GEN-2019-041 | 02 NEBRASKA | 640179 | GENEVA 8 | 69 | 4.1038 | 4.1034 | 0.0004
GEN-2019-041 | 02 NEBRASKA | 640200 | GR ISLD4 | 230 | 16.413 | 16.4087 | 0.0043
GEN-2019-041 | 02 NEBRASKA | 640234 | HUMBOLT5 | 161 | 7.4773 | 7.4768 | 0.0005
GEN-2019-041 | 02 NEBRASKA | 640235 | HUMBOLT7 | 115 | 6.3901 | 6.3897 | 0.0004
GEN-2019-041 | 02 NEBRASKA | 640273 | MCCOOL 8 | 69 | 5.4561 | 5.4557 | 0.0004
GEN-2019-041 | 02 NEBRASKA | 640313 | PAULINE7 | 115 | 15.9334 | 15.9309 | 0.0025
GEN-2019-041 | 02 NEBRASKA | 640316 | PAWNEEL7 | 115 | 11.1764 | 11.1711 | 0.0053
GEN-2019-041 | 02 NEBRASKA | 640342 | SHELCRK3 | 345 | 10.533 | 10.5305 | 0.0025
GEN-2019-041 | 02 NEBRASKA | 640372 | SUTTON 7 | 115 | 6.202 | 6.2013 | 0.0007
GEN-2019-041 | 02 NEBRASKA | 640374 | SWEET W3 | 345 | 10.1673 | 10.166 | 0.0013
GEN-2019-041 | 02 NEBRASKA | 640413 | YORK SW7 | 115 | 7.9943 | 7.9928 | 0.0015
GEN-2019-041 | 02 NEBRASKA | 640426 | STEELEC7 | 115 | 4.866 | 4.8655 | 0.0005
GEN-2019-041 | 02 NEBRASKA | 645454 | S3454 3 | 345 | 27.4247 | 27.4136 | 0.0111
GEN-2019-041 | 02 NEBRASKA | 645455 | S3455 3 | 345 | 30.2346 | 30.2246 | 0.01
GEN-2019-041 | 02 NEBRASKA | 645459 | S3459 3 | 345 | 24.0005 | 23.9961 | 0.0044
GEN-2019-041 | 02 NEBRASKA | 646206 | S1206 5 | 161 | 41.6222 | 41.6168 | 0.0054
GEN-2019-041 | 02 NEBRASKA | 646263 | S1263 5 | 161 | 8.0723 | 8.0717 | 0.0006
GEN-2019-041 | 02 NEBRASKA | 647103 | ENRON 8 | 69 | 4.1173 | 4.1167 | 0.0006
GEN-2019-041 | 02 NEBRASKA | 647966 | S966 8 | 69 | 0.4691 | 0.4691 | 0
GEN-2019-041 | 02 NEBRASKA | 647968 | S968 8 | 69 | 4.1188 | 4.1184 | 0.0004
GEN-2019-041 | 02 NEBRASKA | 647970 | S970 8 | 69 | 4.0129 | 4.0125 | 0.0004
GEN-2019-041 | 02 NEBRASKA | 650208 | W LINCOLN 7 | 115 | 21.2912 | 21.2681 | 0.0231
GEN-2019-041 | 02 NEBRASKA | 650210 | NW70FAIRFD7 | 115 | 20.3803 | 20.3601 | 0.0202
GEN-2019-041 | 02 NEBRASKA | 650216 | SW27&F 7 | 115 | 21.0693 | 21.0463 | 0.023
GEN-2019-041 | 02 NEBRASKA | 650217 | 8&N 7 | 115 | 23.0792 | 23.0514 | 0.0278
GEN-2019-041 | 02 NEBRASKA | 650255 | 56&PLR 7 | 115 | 18.3158 | 18.2926 | 0.0232
GEN-2019-041 | 02 NEBRASKA | 650257 | 56&ELK TAP7 | 115 | 23.9974 | 23.9659 | 0.0315
GEN-2019-041 | 02 NEBRASKA | 650271 | 81&OCHENEY7 | 115 | 23.946 | 23.9136 | 0.0324
GEN-2019-041 | 02 NEBRASKA | 650272 | 91&A 7 | 115 | 20.8564 | 20.8348 | 0.0216
GEN-2019-041 | 02 NEBRASKA | 650273 | 93&O 7 | 115 | 21.5729 | 21.5508 | 0.0221
GEN-2019-041 | 02 NEBRASKA | 650274 | 91&HWY2 7 | 115 | 20.749 | 20.7212 | 0.0278
GEN-2019-041 | 02 NEBRASKA | 650285 | WAGENER 7 | 115 | 30.6415 | 30.6048 | 0.0367
GEN-2019-041 | 02 NEBRASKA | 653871 | GR ISLD-LNX3 | 345 | 12.1609 | 12.1568 | 0.0041
GEN-2019-041 | 02 NEBRASKA | 760746 | GEN-2017-115 | 345 | 12.1065 | 12.1054 | 0.0011
GEN-2019-041 | 02 NEBRASKA | 761313 | GEN-2017-182 | 345 | 5.5534 | 5.5507 | 0.0027
GEN-2019-041 | 02 NEBRASKA | 761376 | GEN-2017-183 | 345 | 8.5745 | 8.5744 | 0.0001
GEN-2019-041 | 02 NEBRASKA | 762691 | GEN-2018-033 | 345 | 21.8188 | 21.8132 | 0.0056
GEN-2019-069 | 02 NEBRASKA | 763982 | G19-069-TAP | 345 | 11.2849 | 11.0888 | 0.1961
GEN-2019-069 | 02 NEBRASKA | 640226 | HOSKINS3 | 345 | 13.0113 | 12.8746 | 0.1367
GEN-2019-069 | 02 NEBRASKA | 640342 | SHELCRK3 | 345 | 10.533 | 10.4514 | 0.0816
GEN-2019-069 | 02 NEBRASKA | 763142 | GEN-2018-083 | 345 | 2.1648 | 2.1601 | 0.0047
GEN-2019-069 | 02 NEBRASKA | 763978 | GEN-2019-069 | 345 | 11.2497 | 11.0536 | 0.1961
GEN-2019-069 | 02 NEBRASKA | 635200 | RAUN 3 | 345 | 27.0138 | 26.9891 | 0.0247
GEN-2019-069 | 02 NEBRASKA | 640125 | COLMB.E3 | 345 | 10.209 | 10.1516 | 0.0574
GEN-2019-069 | 02 NEBRASKA | 640227 | HOSKINS4 | 230 | 10.0896 | 10.0521 | 0.0375
GEN-2019-069 | 02 NEBRASKA | 640228 | HOSKINS7 | 115 | 18.0994 | 18.039 | 0.0604
GEN-2019-069 | 02 NEBRASKA | 640343 | SHELCRK4 | 230 | 10.8729 | 10.8407 | 0.0322
GEN-2019-069 | 02 NEBRASKA | 640520 | ANTELOPE 3 | 345 | 6.9888 | 6.9604 | 0.0284
GEN-2019-069 | 02 NEBRASKA | 640588 | TURTLE.CRK 3 | 345 | 11.1479 | 11.0534 | 0.0945
GEN-2019-069 | 02 NEBRASKA | 87487 | J748POI | 345 | 15.0615 | 15.0579 | 0.0036
GEN-2019-069 | 02 NEBRASKA | 635201 | RAUN 5 | 161 | 27.0927 | 27.0828 | 0.0099
GEN-2019-069 | 02 NEBRASKA | 635252 | J412 POI 3 | 345 | 9.6628 | 9.6614 | 0.0014
GEN-2019-069 | 02 NEBRASKA | 635398 | REMSEN 3 | 345 | 14.4843 | 14.4808 | 0.0035
GEN-2019-069 | 02 NEBRASKA | 640080 | BELDEN 7 | 115 | 5.9733 | 5.9709 | 0.0024
GEN-2019-069 | 02 NEBRASKA | 640127 | COLMB.E7 | 115 | 22.1185 | 22.0677 | 0.0508
GEN-2019-069 | 02 NEBRASKA | 640133 | COLMBUS4 | 230 | 11.4877 | 11.4582 | 0.0295
GEN-2019-069 | 02 NEBRASKA | 640296 | NORFK.N7 | 115 | 13.1793 | 13.1484 | 0.0309
GEN-2019-069 | 02 NEBRASKA | 640298 | NORFOLK7 | 115 | 12.385 | 12.3579 | 0.0271
GEN-2019-069 | 02 NEBRASKA | 640363 | STNTN.N7 | 115 | 6.977 | 6.9697 | 0.0073
GEN-2019-069 | 02 NEBRASKA | 640521 | ANTELOPE 7 | 115 | 14.1104 | 14.084 | 0.0264
GEN-2019-069 | 02 NEBRASKA | 640560 | WAKEFIELD 4 | 230 | 7.9675 | 7.9603 | 0.0072
GEN-2019-069 | 02 NEBRASKA | 640589 | SHOLES.W 3 | 345 | 9.0182 | 8.9583 | 0.0599
GEN-2019-069 | 02 NEBRASKA | 640598 | HAYSTACK.WD3 | 345 | 8.6554 | 8.6021 | 0.0533
GEN-2019-069 | 02 NEBRASKA | 643271 | PLUMBCR.W 3 | 345 | 10.8968 | 10.8064 | 0.0904
GEN-2019-069 | 02 NEBRASKA | 650114 | NW68HOLDRG3 | 345 | 16.8066 | 16.792 | 0.0146
GEN-2019-069 | 02 NEBRASKA | 652564 | SIOUXCY3 | 345 | 15.3816 | 15.3753 | 0.0063
GEN-2019-069 | 02 NEBRASKA | 762779 | G18-043-TAP | 345 | 15.621 | 15.6183 | 0.0027
GEN-2019-069 | 02 NEBRASKA | 763032 | GEN-2018-068 | 345 | 5.9447 | 5.9251 | 0.0196
GEN-2019-069 | 02 NEBRASKA | 763439 | GEN-2018-131 | 345 | 6.9826 | 6.9543 | 0.0283
GEN-2019-069 | 02 NEBRASKA | 45906 | J1590 SUB | 345 | 14.2602 | 14.2567 | 0.0035
GEN-2019-069 | 02 NEBRASKA | 87486 | J748GENTIE | 345 | 13.2728 | 13.27 | 0.0028
GEN-2019-069 | 02 NEBRASKA | 635202 | NEAL S 5 | 161 | 22.3496 | 22.343 | 0.0066
GEN-2019-069 | 02 NEBRASKA | 635203 | NEAL N 5 | 161 | 25.6073 | 25.5984 | 0.0089
GEN-2019-069 | 02 NEBRASKA | 635206 | IDA CO 3 | 345 | 9.3103 | 9.3092 | 0.0011
GEN-2019-069 | 02 NEBRASKA | 635220 | INTCHG 5 | 161 | 14.526 | 14.5232 | 0.0028
GEN-2019-069 | 02 NEBRASKA | 635230 | LIBERTY5 | 161 | 24.9266 | 24.9182 | 0.0084
GEN-2019-069 | 02 NEBRASKA | 635399 | CHEROKEE 3 | 345 | 15.9186 | 15.9148 | 0.0038
GEN-2019-069 | 02 NEBRASKA | 640072 | BATTLCR7 | 115 | 7.3087 | 7.2999 | 0.0088
GEN-2019-069 | 02 NEBRASKA | 640081 | BELDEN 8 | 69 | 3.6996 | 3.699 | 0.0006
GEN-2019-069 | 02 NEBRASKA | 640115 | CO.LINE7 | 115 | 7.2295 | 7.2218 | 0.0077
GEN-2019-069 | 02 NEBRASKA | 640119 | COL.COG7 | 115 | 19.5195 | 19.4824 | 0.0371
GEN-2019-069 | 02 NEBRASKA | 640126 | E.COL. 4 | 230 | 10.0667 | 10.0443 | 0.0224
GEN-2019-069 | 02 NEBRASKA | 640131 | COLMB.W4 | 230 | 9.8308 | 9.8112 | 0.0196
GEN-2019-069 | 02 NEBRASKA | 640134 | KELLY 7 | 115 | 17.6974 | 17.668 | 0.0294
GEN-2019-069 | 02 NEBRASKA | 640136 | COLMBUS7 | 115 | 19.1401 | 19.106 | 0.0341
GEN-2019-069 | 02 NEBRASKA | 640149 | CREITON7 | 115 | 4.7116 | 4.71 | 0.0016
GEN-2019-069 | 02 NEBRASKA | 640157 | DAVIDCY7 | 115 | 5.6545 | 5.6525 | 0.002
GEN-2019-069 | 02 NEBRASKA | 640212 | HARTGTN7 | 115 | 5.1832 | 5.1819 | 0.0013
GEN-2019-069 | 02 NEBRASKA | 640263 | MADISON7 | 115 | 6.1678 | 6.1623 | 0.0055
GEN-2019-069 | 02 NEBRASKA | 640277 | MOORE 3 | 345 | 22.4804 | 22.47 | 0.0104
GEN-2019-069 | 02 NEBRASKA | 640293 | NELIGH 7 | 115 | 9.9449 | 9.9339 | 0.011
GEN-2019-069 | 02 NEBRASKA | 640357 | STANTON7 | 115 | 5.115 | 5.1118 | 0.0032
GEN-2019-069 | 02 NEBRASKA | 640386 | TWIN CH4 | 230 | 8.9225 | 8.9175 | 0.005
GEN-2019-069 | 02 NEBRASKA | 640387 | TWIN CH7 | 115 | 10.7822 | 10.7782 | 0.004
GEN-2019-069 | 02 NEBRASKA | 640522 | ANTELOPE 8 | 69 | 5.119 | 5.1169 | 0.0021
GEN-2019-069 | 02 NEBRASKA | 640540 | MEADOWGROVE4 | 230 | 5.0998 | 5.0973 | 0.0025
GEN-2019-069 | 02 NEBRASKA | 640561 | RTLSNAKE.W 4 | 230 | 7.1132 | 7.108 | 0.0052
GEN-2019-069 | 02 NEBRASKA | 643254 | UPSTREAM.W 7 | 115 | 13.3751 | 13.3516 | 0.0235
GEN-2019-069 | 02 NEBRASKA | 645451 | S3451 3 | 345 | 21.3318 | 21.3284 | 0.0034
GEN-2019-069 | 02 NEBRASKA | 650185 | WAGENER 3 | 345 | 20.0853 | 20.0765 | 0.0088
GEN-2019-069 | 02 NEBRASKA | 650214 | NW68HOLDRG7 | 115 | 24.3952 | 24.389 | 0.0062
GEN-2019-069 | 02 NEBRASKA | 652552 | SIOUXCY2 | 230 | 20.341 | 20.3329 | 0.0081
GEN-2019-069 | 02 NEBRASKA | 652864 | SIOUXCY-LNX3 | 345 | 15.1969 | 15.1908 | 0.0061
GEN-2019-069 | 02 NEBRASKA | 760788 | GEN-2017-201 | 345 | 8.2239 | 8.1747 | 0.0492
GEN-2019-069 | 02 NEBRASKA | 762069 | G17-105TAP | 161 | 8.3472 | 8.3464 | 0.0008
GEN-2019-069 | 02 NEBRASKA | 762780 | GEN-2018-043 | 345 | 12.7205 | 12.7188 | 0.0017
GEN-2019-069 | 02 NEBRASKA | 763450 | GEN-2018-132 | 345 | 6.6695 | 6.6436 | 0.0259
GEN-2019-069 | 02 NEBRASKA | 601006 | SPLT RK3 | 345 | 14.9416 | 14.9407 | 0.0009
GEN-2019-069 | 02 NEBRASKA | 635204 | NEAL N 8 | 69 | 9.7689 | 9.7684 | 0.0005
GEN-2019-069 | 02 NEBRASKA | 635219 | GARD AVE 3 | 345 | 8.9677 | 8.9668 | 0.0009
GEN-2019-069 | 02 NEBRASKA | 635221 | KELLOGG5 | 161 | 17.1226 | 17.1189 | 0.0037
GEN-2019-069 | 02 NEBRASKA | 635229 | AIRPORT 5 | 161 | 16.9835 | 16.9797 | 0.0038
GEN-2019-069 | 02 NEBRASKA | 635235 | SALIX 5 | 161 | 14.6126 | 14.6099 | 0.0027
GEN-2019-069 | 02 NEBRASKA | 635300 | MONONA 5 | 161 | 5.4609 | 5.4607 | 0.0002
GEN-2019-069 | 02 NEBRASKA | 635400 | HIGHLND 3 | 345 | 14.5121 | 14.5103 | 0.0018
GEN-2019-069 | 02 NEBRASKA | 637009 | GLACIAL EDGE | 345 | 15.6443 | 15.6406 | 0.0037
GEN-2019-069 | 02 NEBRASKA | 640073 | BATTLCR8 | 69 | 3.8906 | 3.8891 | 0.0015
GEN-2019-069 | 02 NEBRASKA | 640078 | BEEMER 7 | 115 | 4.396 | 4.3947 | 0.0013
GEN-2019-069 | 02 NEBRASKA | 640084 | BLMFLD 7 | 115 | 5.1275 | 5.1266 | 0.0009
GEN-2019-069 | 02 NEBRASKA | 640113 | CLRWATR7 | 115 | 5.1516 | 5.1493 | 0.0023
GEN-2019-069 | 02 NEBRASKA | 640122 | COL.DRY7 | 115 | 16.4842 | 16.4576 | 0.0266
GEN-2019-069 | 02 NEBRASKA | 640124 | COL.SE 7 | 115 | 16.6202 | 16.5944 | 0.0258
GEN-2019-069 | 02 NEBRASKA | 640150 | CREITON8 | 69 | 4.3586 | 4.3578 | 0.0008
GEN-2019-069 | 02 NEBRASKA | 640151 | CRESTON7 | 115 | 5.9927 | 5.988 | 0.0047
GEN-2019-069 | 02 NEBRASKA | 640163 | EMERSON7 | 115 | 5.4485 | 5.4475 | 0.001
GEN-2019-069 | 02 NEBRASKA | 640181 | GENOA 7 | 115 | 4.8706 | 4.8688 | 0.0018
GEN-2019-069 | 02 NEBRASKA | 640200 | GR ISLD4 | 230 | 16.413 | 16.4088 | 0.0042
GEN-2019-069 | 02 NEBRASKA | 640213 | HARTGTN8 | 69 | 3.4988 | 3.4984 | 0.0004
GEN-2019-069 | 02 NEBRASKA | 640271 | MCCOOL 3 | 345 | 10.8752 | 10.8732 | 0.002
GEN-2019-069 | 02 NEBRASKA | 640278 | SHELDON7 | 115 | 42.1871 | 42.1784 | 0.0087
GEN-2019-069 | 02 NEBRASKA | 640294 | NELIGH 8 | 69 | 5.8977 | 5.8954 | 0.0023
GEN-2019-069 | 02 NEBRASKA | 640316 | PAWNEEL7 | 115 | 11.1764 | 11.1748 | 0.0016
GEN-2019-069 | 02 NEBRASKA | 640336 | SCHUYLR7 | 115 | 5.8 | 5.7978 | 0.0022
GEN-2019-069 | 02 NEBRASKA | 640345 | SILVRCK7 | 115 | 4.5561 | 4.555 | 0.0011
GEN-2019-069 | 02 NEBRASKA | 640377 | TEKAMAH5 | 161 | 8.8894 | 8.8884 | 0.001
GEN-2019-069 | 02 NEBRASKA | 640388 | TWIN CH8 | 69 | 7.7842 | 7.7829 | 0.0013
GEN-2019-069 | 02 NEBRASKA | 640402 | WAHOO 7 | 115 | 4.7578 | 4.7572 | 0.0006
GEN-2019-069 | 02 NEBRASKA | 640424 | S.SIOUXCITY7 | 115 | 7.3706 | 7.3687 | 0.0019
GEN-2019-069 | 02 NEBRASKA | 640444 | PETERSBRG.N7 | 115 | 5.4317 | 5.4297 | 0.002
GEN-2019-069 | 02 NEBRASKA | 640525 | TOBIAS 3 | 345 | 11.6744 | 11.6724 | 0.002
GEN-2019-069 | 02 NEBRASKA | 640590 | MONOLITH 3 | 345 | 21.9978 | 21.988 | 0.0098
GEN-2019-069 | 02 NEBRASKA | 645454 | S3454 3 | 345 | 27.4247 | 27.4199 | 0.0048
GEN-2019-069 | 02 NEBRASKA | 645459 | S3459 3 | 345 | 24.0005 | 23.9976 | 0.0029
GEN-2019-069 | 02 NEBRASKA | 646251 | S1251 5 | 161 | 30.7514 | 30.7481 | 0.0033
GEN-2019-069 | 02 NEBRASKA | 648506 | PR BRZ 4 | 230 | 3.5115 | 3.5106 | 0.0009
GEN-2019-069 | 02 NEBRASKA | 650189 | 103&ROKEBY3 | 345 | 19.9772 | 19.9697 | 0.0075
GEN-2019-069 | 02 NEBRASKA | 650210 | NW70FAIRFD7 | 115 | 20.3803 | 20.3761 | 0.0042
GEN-2019-069 | 02 NEBRASKA | 650216 | SW27&F 7 | 115 | 21.0693 | 21.0654 | 0.0039
GEN-2019-069 | 02 NEBRASKA | 650285 | WAGENER 7 | 115 | 30.6415 | 30.6348 | 0.0067
GEN-2019-069 | 02 NEBRASKA | 650290 | ROKEBY 7 | 115 | 24.4224 | 24.4181 | 0.0043
GEN-2019-069 | 02 NEBRASKA | 652509 | FTRANDL4 | 230 | 12.1336 | 12.1322 | 0.0014
GEN-2019-069 | 02 NEBRASKA | 652511 | GAVINS 7 | 115 | 8.4307 | 8.4293 | 0.0014
GEN-2019-069 | 02 NEBRASKA | 652565 | SIOUXCY4 | 230 | 20.341 | 20.3329 | 0.0081
GEN-2019-069 | 02 NEBRASKA | 659900 | EAGLE___-NI4 | 230 | 7.3012 | 7.3006 | 0.0006
GEN-2019-069 | 02 NEBRASKA | 762070 | GEN-2017-105 | 161 | 8.3472 | 8.3464 | 0.0008
GEN-2019-069 | 02 NEBRASKA | 762603 | GEN-2018-025 | 345 | 20.4121 | 20.4089 | 0.0032
GEN-2019-070 | 02 NEBRASKA | 763982 | G19-069-TAP | 345 | 11.2849 | 11.1983 | 0.0866
GEN-2019-070 | 02 NEBRASKA | 640226 | HOSKINS3 | 345 | 13.0113 | 12.9511 | 0.0602
GEN-2019-070 | 02 NEBRASKA | 640342 | SHELCRK3 | 345 | 10.533 | 10.4971 | 0.0359
GEN-2019-070 | 02 NEBRASKA | 763142 | GEN-2018-083 | 345 | 2.1648 | 2.1628 | 0.002
GEN-2019-070 | 02 NEBRASKA | 763978 | GEN-2019-069 | 345 | 11.2497 | 11.1631 | 0.0866
GEN-2019-070 | 02 NEBRASKA | 635200 | RAUN 3 | 345 | 27.0138 | 27.003 | 0.0108
GEN-2019-070 | 02 NEBRASKA | 640125 | COLMB.E3 | 345 | 10.209 | 10.1838 | 0.0252
GEN-2019-070 | 02 NEBRASKA | 640227 | HOSKINS4 | 230 | 10.0896 | 10.0731 | 0.0165
GEN-2019-070 | 02 NEBRASKA | 640228 | HOSKINS7 | 115 | 18.0994 | 18.0729 | 0.0265
GEN-2019-070 | 02 NEBRASKA | 640343 | SHELCRK4 | 230 | 10.8729 | 10.8588 | 0.0141
GEN-2019-070 | 02 NEBRASKA | 640520 | ANTELOPE 3 | 345 | 6.9888 | 6.9763 | 0.0125
GEN-2019-070 | 02 NEBRASKA | 640588 | TURTLE.CRK 3 | 345 | 11.1479 | 11.1064 | 0.0415
GEN-2019-070 | 02 NEBRASKA | 87487 | J748POI | 345 | 15.0615 | 15.0599 | 0.0016
GEN-2019-070 | 02 NEBRASKA | 635201 | RAUN 5 | 161 | 27.0927 | 27.0884 | 0.0043
GEN-2019-070 | 02 NEBRASKA | 635252 | J412 POI 3 | 345 | 9.6628 | 9.6622 | 0.0006
GEN-2019-070 | 02 NEBRASKA | 635398 | REMSEN 3 | 345 | 14.4843 | 14.4828 | 0.0015
GEN-2019-070 | 02 NEBRASKA | 640080 | BELDEN 7 | 115 | 5.9733 | 5.9723 | 0.001
GEN-2019-070 | 02 NEBRASKA | 640127 | COLMB.E7 | 115 | 22.1185 | 22.0963 | 0.0222
GEN-2019-070 | 02 NEBRASKA | 640133 | COLMBUS4 | 230 | 11.4877 | 11.4747 | 0.013
GEN-2019-070 | 02 NEBRASKA | 640296 | NORFK.N7 | 115 | 13.1793 | 13.1658 | 0.0135
GEN-2019-070 | 02 NEBRASKA | 640298 | NORFOLK7 | 115 | 12.385 | 12.3731 | 0.0119
GEN-2019-070 | 02 NEBRASKA | 640363 | STNTN.N7 | 115 | 6.977 | 6.9738 | 0.0032
GEN-2019-070 | 02 NEBRASKA | 640521 | ANTELOPE 7 | 115 | 14.1104 | 14.0988 | 0.0116
GEN-2019-070 | 02 NEBRASKA | 640560 | WAKEFIELD 4 | 230 | 7.9675 | 7.9644 | 0.0031
GEN-2019-070 | 02 NEBRASKA | 640589 | SHOLES.W 3 | 345 | 9.0182 | 8.9919 | 0.0263
GEN-2019-070 | 02 NEBRASKA | 640598 | HAYSTACK.WD3 | 345 | 8.6554 | 8.632 | 0.0234
GEN-2019-070 | 02 NEBRASKA | 643271 | PLUMBCR.W 3 | 345 | 10.8968 | 10.8571 | 0.0397
GEN-2019-070 | 02 NEBRASKA | 650114 | NW68HOLDRG3 | 345 | 16.8066 | 16.8002 | 0.0064
GEN-2019-070 | 02 NEBRASKA | 652564 | SIOUXCY3 | 345 | 15.3816 | 15.3789 | 0.0027
GEN-2019-070 | 02 NEBRASKA | 762779 | G18-043-TAP | 345 | 15.621 | 15.6198 | 0.0012
GEN-2019-070 | 02 NEBRASKA | 763032 | GEN-2018-068 | 345 | 5.9447 | 5.9361 | 0.0086
GEN-2019-070 | 02 NEBRASKA | 763439 | GEN-2018-131 | 345 | 6.9826 | 6.9702 | 0.0124
GEN-2019-070 | 02 NEBRASKA | 45906 | J1590 SUB | 345 | 14.2602 | 14.2587 | 0.0015
GEN-2019-070 | 02 NEBRASKA | 87486 | J748GENTIE | 345 | 13.2728 | 13.2715 | 0.0013
GEN-2019-070 | 02 NEBRASKA | 635202 | NEAL S 5 | 161 | 22.3496 | 22.3467 | 0.0029
GEN-2019-070 | 02 NEBRASKA | 635203 | NEAL N 5 | 161 | 25.6073 | 25.6034 | 0.0039
GEN-2019-070 | 02 NEBRASKA | 635206 | IDA CO 3 | 345 | 9.3103 | 9.3098 | 0.0005
GEN-2019-070 | 02 NEBRASKA | 635220 | INTCHG 5 | 161 | 14.526 | 14.5248 | 0.0012
GEN-2019-070 | 02 NEBRASKA | 635230 | LIBERTY5 | 161 | 24.9266 | 24.9229 | 0.0037
GEN-2019-070 | 02 NEBRASKA | 635399 | CHEROKEE 3 | 345 | 15.9186 | 15.9169 | 0.0017
GEN-2019-070 | 02 NEBRASKA | 640072 | BATTLCR7 | 115 | 7.3087 | 7.3049 | 0.0038
GEN-2019-070 | 02 NEBRASKA | 640081 | BELDEN 8 | 69 | 3.6996 | 3.6994 | 0.0002
GEN-2019-070 | 02 NEBRASKA | 640115 | CO.LINE7 | 115 | 7.2295 | 7.2261 | 0.0034
GEN-2019-070 | 02 NEBRASKA | 640119 | COL.COG7 | 115 | 19.5195 | 19.5033 | 0.0162
GEN-2019-070 | 02 NEBRASKA | 640126 | E.COL. 4 | 230 | 10.0667 | 10.0569 | 0.0098
GEN-2019-070 | 02 NEBRASKA | 640131 | COLMB.W4 | 230 | 9.8308 | 9.8222 | 0.0086
GEN-2019-070 | 02 NEBRASKA | 640134 | KELLY 7 | 115 | 17.6974 | 17.6846 | 0.0128
GEN-2019-070 | 02 NEBRASKA | 640136 | COLMBUS7 | 115 | 19.1401 | 19.1251 | 0.015
GEN-2019-070 | 02 NEBRASKA | 640149 | CREITON7 | 115 | 4.7116 | 4.7109 | 0.0007
GEN-2019-070 | 02 NEBRASKA | 640157 | DAVIDCY7 | 115 | 5.6545 | 5.6536 | 0.0009
GEN-2019-070 | 02 NEBRASKA | 640212 | HARTGTN7 | 115 | 5.1832 | 5.1826 | 0.0006
GEN-2019-070 | 02 NEBRASKA | 640263 | MADISON7 | 115 | 6.1678 | 6.1654 | 0.0024
GEN-2019-070 | 02 NEBRASKA | 640277 | MOORE 3 | 345 | 22.4804 | 22.4759 | 0.0045
GEN-2019-070 | 02 NEBRASKA | 640293 | NELIGH 7 | 115 | 9.9449 | 9.9401 | 0.0048
GEN-2019-070 | 02 NEBRASKA | 640357 | STANTON7 | 115 | 5.115 | 5.1136 | 0.0014
GEN-2019-070 | 02 NEBRASKA | 640386 | TWIN CH4 | 230 | 8.9225 | 8.9203 | 0.0022
GEN-2019-070 | 02 NEBRASKA | 640387 | TWIN CH7 | 115 | 10.7822 | 10.7805 | 0.0017
GEN-2019-070 | 02 NEBRASKA | 640522 | ANTELOPE 8 | 69 | 5.119 | 5.1181 | 0.0009
GEN-2019-070 | 02 NEBRASKA | 640540 | MEADOWGROVE4 | 230 | 5.0998 | 5.0987 | 0.0011
GEN-2019-070 | 02 NEBRASKA | 640561 | RTLSNAKE.W 4 | 230 | 7.1132 | 7.111 | 0.0022
GEN-2019-070 | 02 NEBRASKA | 643254 | UPSTREAM.W 7 | 115 | 13.3751 | 13.3648 | 0.0103
GEN-2019-070 | 02 NEBRASKA | 645451 | S3451 3 | 345 | 21.3318 | 21.3303 | 0.0015
GEN-2019-070 | 02 NEBRASKA | 650185 | WAGENER 3 | 345 | 20.0853 | 20.0815 | 0.0038
GEN-2019-070 | 02 NEBRASKA | 650214 | NW68HOLDRG7 | 115 | 24.3952 | 24.3925 | 0.0027
GEN-2019-070 | 02 NEBRASKA | 652552 | SIOUXCY2 | 230 | 20.341 | 20.3374 | 0.0036
GEN-2019-070 | 02 NEBRASKA | 652864 | SIOUXCY-LNX3 | 345 | 15.1969 | 15.1942 | 0.0027
GEN-2019-070 | 02 NEBRASKA | 760788 | GEN-2017-201 | 345 | 8.2239 | 8.2023 | 0.0216
GEN-2019-070 | 02 NEBRASKA | 762069 | G17-105TAP | 161 | 8.3472 | 8.3469 | 0.0003
GEN-2019-070 | 02 NEBRASKA | 762780 | GEN-2018-043 | 345 | 12.7205 | 12.7197 | 0.0008
GEN-2019-070 | 02 NEBRASKA | 763450 | GEN-2018-132 | 345 | 6.6695 | 6.6581 | 0.0114
GEN-2019-070 | 02 NEBRASKA | 601006 | SPLT RK3 | 345 | 14.9416 | 14.9412 | 0.0004
GEN-2019-070 | 02 NEBRASKA | 635204 | NEAL N 8 | 69 | 9.7689 | 9.7687 | 0.0002
GEN-2019-070 | 02 NEBRASKA | 635219 | GARD AVE 3 | 345 | 8.9677 | 8.9673 | 0.0004
GEN-2019-070 | 02 NEBRASKA | 635221 | KELLOGG5 | 161 | 17.1226 | 17.121 | 0.0016
GEN-2019-070 | 02 NEBRASKA | 635229 | AIRPORT 5 | 161 | 16.9835 | 16.9819 | 0.0016
GEN-2019-070 | 02 NEBRASKA | 635235 | SALIX 5 | 161 | 14.6126 | 14.6114 | 0.0012
GEN-2019-070 | 02 NEBRASKA | 635300 | MONONA 5 | 161 | 5.4609 | 5.4608 | 0.0001
GEN-2019-070 | 02 NEBRASKA | 635400 | HIGHLND 3 | 345 | 14.5121 | 14.5113 | 0.0008
GEN-2019-070 | 02 NEBRASKA | 637009 | GLACIAL EDGE | 345 | 15.6443 | 15.6427 | 0.0016
GEN-2019-070 | 02 NEBRASKA | 640073 | BATTLCR8 | 69 | 3.8906 | 3.8899 | 0.0007
GEN-2019-070 | 02 NEBRASKA | 640078 | BEEMER 7 | 115 | 4.396 | 4.3954 | 0.0006
GEN-2019-070 | 02 NEBRASKA | 640084 | BLMFLD 7 | 115 | 5.1275 | 5.1271 | 0.0004
GEN-2019-070 | 02 NEBRASKA | 640113 | CLRWATR7 | 115 | 5.1516 | 5.1506 | 0.001
GEN-2019-070 | 02 NEBRASKA | 640122 | COL.DRY7 | 115 | 16.4842 | 16.4726 | 0.0116
GEN-2019-070 | 02 NEBRASKA | 640124 | COL.SE 7 | 115 | 16.6202 | 16.6089 | 0.0113
GEN-2019-070 | 02 NEBRASKA | 640150 | CREITON8 | 69 | 4.3586 | 4.3582 | 0.0004
GEN-2019-070 | 02 NEBRASKA | 640151 | CRESTON7 | 115 | 5.9927 | 5.9907 | 0.002
GEN-2019-070 | 02 NEBRASKA | 640163 | EMERSON7 | 115 | 5.4485 | 5.4481 | 0.0004
GEN-2019-070 | 02 NEBRASKA | 640181 | GENOA 7 | 115 | 4.8706 | 4.8698 | 0.0008
GEN-2019-070 | 02 NEBRASKA | 640200 | GR ISLD4 | 230 | 16.413 | 16.4112 | 0.0018
GEN-2019-070 | 02 NEBRASKA | 640213 | HARTGTN8 | 69 | 3.4988 | 3.4986 | 0.0002
GEN-2019-070 | 02 NEBRASKA | 640271 | MCCOOL 3 | 345 | 10.8752 | 10.8743 | 0.0009
GEN-2019-070 | 02 NEBRASKA | 640278 | SHELDON7 | 115 | 42.1871 | 42.1833 | 0.0038
GEN-2019-070 | 02 NEBRASKA | 640294 | NELIGH 8 | 69 | 5.8977 | 5.8967 | 0.001
GEN-2019-070 | 02 NEBRASKA | 640316 | PAWNEEL7 | 115 | 11.1764 | 11.1757 | 0.0007
GEN-2019-070 | 02 NEBRASKA | 640336 | SCHUYLR7 | 115 | 5.8 | 5.7991 | 0.0009
GEN-2019-070 | 02 NEBRASKA | 640345 | SILVRCK7 | 115 | 4.5561 | 4.5556 | 0.0005
GEN-2019-070 | 02 NEBRASKA | 640377 | TEKAMAH5 | 161 | 8.8894 | 8.889 | 0.0004
GEN-2019-070 | 02 NEBRASKA | 640388 | TWIN CH8 | 69 | 7.7842 | 7.7836 | 0.0006
GEN-2019-070 | 02 NEBRASKA | 640402 | WAHOO 7 | 115 | 4.7578 | 4.7575 | 0.0003
GEN-2019-070 | 02 NEBRASKA | 640424 | S.SIOUXCITY7 | 115 | 7.3706 | 7.3698 | 0.0008
GEN-2019-070 | 02 NEBRASKA | 640444 | PETERSBRG.N7 | 115 | 5.4317 | 5.4308 | 0.0009
GEN-2019-070 | 02 NEBRASKA | 640525 | TOBIAS 3 | 345 | 11.6744 | 11.6735 | 0.0009
GEN-2019-070 | 02 NEBRASKA | 640590 | MONOLITH 3 | 345 | 21.9978 | 21.9935 | 0.0043
GEN-2019-070 | 02 NEBRASKA | 645454 | S3454 3 | 345 | 27.4247 | 27.4226 | 0.0021
GEN-2019-070 | 02 NEBRASKA | 645459 | S3459 3 | 345 | 24.0005 | 23.9992 | 0.0013
GEN-2019-070 | 02 NEBRASKA | 646251 | S1251 5 | 161 | 30.7514 | 30.75 | 0.0014
GEN-2019-070 | 02 NEBRASKA | 648506 | PR BRZ 4 | 230 | 3.5115 | 3.5111 | 0.0004
GEN-2019-070 | 02 NEBRASKA | 650189 | 103&ROKEBY3 | 345 | 19.9772 | 19.9739 | 0.0033
GEN-2019-070 | 02 NEBRASKA | 650210 | NW70FAIRFD7 | 115 | 20.3803 | 20.3785 | 0.0018
GEN-2019-070 | 02 NEBRASKA | 650216 | SW27&F 7 | 115 | 21.0693 | 21.0676 | 0.0017
GEN-2019-070 | 02 NEBRASKA | 650285 | WAGENER 7 | 115 | 30.6415 | 30.6386 | 0.0029
GEN-2019-070 | 02 NEBRASKA | 650290 | ROKEBY 7 | 115 | 24.4224 | 24.4205 | 0.0019
GEN-2019-070 | 02 NEBRASKA | 652509 | FTRANDL4 | 230 | 12.1336 | 12.133 | 0.0006
GEN-2019-070 | 02 NEBRASKA | 652511 | GAVINS 7 | 115 | 8.4307 | 8.4301 | 0.0006
GEN-2019-070 | 02 NEBRASKA | 652565 | SIOUXCY4 | 230 | 20.341 | 20.3374 | 0.0036
GEN-2019-070 | 02 NEBRASKA | 659900 | EAGLE___-NI4 | 230 | 7.3012 | 7.3009 | 0.0003
GEN-2019-070 | 02 NEBRASKA | 762070 | GEN-2017-105 | 161 | 8.3472 | 8.3469 | 0.0003
GEN-2019-070 | 02 NEBRASKA | 762603 | GEN-2018-025 | 345 | 20.4121 | 20.4107 | 0.0014
GEN-2019-073 | 02 NEBRASKA | 763982 | G19-069-TAP | 345 | 11.2849 | 11.0888 | 0.1961
GEN-2019-073 | 02 NEBRASKA | 640226 | HOSKINS3 | 345 | 13.0113 | 12.8746 | 0.1367
GEN-2019-073 | 02 NEBRASKA | 640342 | SHELCRK3 | 345 | 10.533 | 10.4514 | 0.0816
GEN-2019-073 | 02 NEBRASKA | 763142 | GEN-2018-083 | 345 | 2.1648 | 2.1601 | 0.0047
GEN-2019-073 | 02 NEBRASKA | 763978 | GEN-2019-069 | 345 | 11.2497 | 11.0536 | 0.1961
GEN-2019-073 | 02 NEBRASKA | 635200 | RAUN 3 | 345 | 27.0138 | 26.9891 | 0.0247
GEN-2019-073 | 02 NEBRASKA | 640125 | COLMB.E3 | 345 | 10.209 | 10.1516 | 0.0574
GEN-2019-073 | 02 NEBRASKA | 640227 | HOSKINS4 | 230 | 10.0896 | 10.0521 | 0.0375
GEN-2019-073 | 02 NEBRASKA | 640228 | HOSKINS7 | 115 | 18.0994 | 18.039 | 0.0604
GEN-2019-073 | 02 NEBRASKA | 640343 | SHELCRK4 | 230 | 10.8729 | 10.8407 | 0.0322
GEN-2019-073 | 02 NEBRASKA | 640520 | ANTELOPE 3 | 345 | 6.9888 | 6.9604 | 0.0284
GEN-2019-073 | 02 NEBRASKA | 640588 | TURTLE.CRK 3 | 345 | 11.1479 | 11.0534 | 0.0945
GEN-2019-073 | 02 NEBRASKA | 87487 | J748POI | 345 | 15.0615 | 15.0579 | 0.0036
GEN-2019-073 | 02 NEBRASKA | 635201 | RAUN 5 | 161 | 27.0927 | 27.0828 | 0.0099
GEN-2019-073 | 02 NEBRASKA | 635252 | J412 POI 3 | 345 | 9.6628 | 9.6614 | 0.0014
GEN-2019-073 | 02 NEBRASKA | 635398 | REMSEN 3 | 345 | 14.4843 | 14.4808 | 0.0035
GEN-2019-073 | 02 NEBRASKA | 640080 | BELDEN 7 | 115 | 5.9733 | 5.9709 | 0.0024
GEN-2019-073 | 02 NEBRASKA | 640127 | COLMB.E7 | 115 | 22.1185 | 22.0677 | 0.0508
GEN-2019-073 | 02 NEBRASKA | 640133 | COLMBUS4 | 230 | 11.4877 | 11.4582 | 0.0295
GEN-2019-073 | 02 NEBRASKA | 640296 | NORFK.N7 | 115 | 13.1793 | 13.1484 | 0.0309
GEN-2019-073 | 02 NEBRASKA | 640298 | NORFOLK7 | 115 | 12.385 | 12.3579 | 0.0271
GEN-2019-073 | 02 NEBRASKA | 640363 | STNTN.N7 | 115 | 6.977 | 6.9697 | 0.0073
GEN-2019-073 | 02 NEBRASKA | 640521 | ANTELOPE 7 | 115 | 14.1104 | 14.084 | 0.0264
GEN-2019-073 | 02 NEBRASKA | 640560 | WAKEFIELD 4 | 230 | 7.9675 | 7.9603 | 0.0072
GEN-2019-073 | 02 NEBRASKA | 640589 | SHOLES.W 3 | 345 | 9.0182 | 8.9583 | 0.0599
GEN-2019-073 | 02 NEBRASKA | 640598 | HAYSTACK.WD3 | 345 | 8.6554 | 8.6021 | 0.0533
GEN-2019-073 | 02 NEBRASKA | 643271 | PLUMBCR.W 3 | 345 | 10.8968 | 10.8064 | 0.0904
GEN-2019-073 | 02 NEBRASKA | 650114 | NW68HOLDRG3 | 345 | 16.8066 | 16.792 | 0.0146
GEN-2019-073 | 02 NEBRASKA | 652564 | SIOUXCY3 | 345 | 15.3816 | 15.3753 | 0.0063
GEN-2019-073 | 02 NEBRASKA | 762779 | G18-043-TAP | 345 | 15.621 | 15.6183 | 0.0027
GEN-2019-073 | 02 NEBRASKA | 763032 | GEN-2018-068 | 345 | 5.9447 | 5.9251 | 0.0196
GEN-2019-073 | 02 NEBRASKA | 763439 | GEN-2018-131 | 345 | 6.9826 | 6.9543 | 0.0283
GEN-2019-073 | 02 NEBRASKA | 45906 | J1590 SUB | 345 | 14.2602 | 14.2567 | 0.0035
GEN-2019-073 | 02 NEBRASKA | 87486 | J748GENTIE | 345 | 13.2728 | 13.27 | 0.0028
GEN-2019-073 | 02 NEBRASKA | 635202 | NEAL S 5 | 161 | 22.3496 | 22.343 | 0.0066
GEN-2019-073 | 02 NEBRASKA | 635203 | NEAL N 5 | 161 | 25.6073 | 25.5984 | 0.0089
GEN-2019-073 | 02 NEBRASKA | 635206 | IDA CO 3 | 345 | 9.3103 | 9.3092 | 0.0011
GEN-2019-073 | 02 NEBRASKA | 635220 | INTCHG 5 | 161 | 14.526 | 14.5232 | 0.0028
GEN-2019-073 | 02 NEBRASKA | 635230 | LIBERTY5 | 161 | 24.9266 | 24.9182 | 0.0084
GEN-2019-073 | 02 NEBRASKA | 635399 | CHEROKEE 3 | 345 | 15.9186 | 15.9148 | 0.0038
GEN-2019-073 | 02 NEBRASKA | 640072 | BATTLCR7 | 115 | 7.3087 | 7.2999 | 0.0088
GEN-2019-073 | 02 NEBRASKA | 640081 | BELDEN 8 | 69 | 3.6996 | 3.699 | 0.0006
GEN-2019-073 | 02 NEBRASKA | 640115 | CO.LINE7 | 115 | 7.2295 | 7.2218 | 0.0077
GEN-2019-073 | 02 NEBRASKA | 640119 | COL.COG7 | 115 | 19.5195 | 19.4824 | 0.0371
GEN-2019-073 | 02 NEBRASKA | 640126 | E.COL. 4 | 230 | 10.0667 | 10.0443 | 0.0224
GEN-2019-073 | 02 NEBRASKA | 640131 | COLMB.W4 | 230 | 9.8308 | 9.8112 | 0.0196
GEN-2019-073 | 02 NEBRASKA | 640134 | KELLY 7 | 115 | 17.6974 | 17.668 | 0.0294
GEN-2019-073 | 02 NEBRASKA | 640136 | COLMBUS7 | 115 | 19.1401 | 19.106 | 0.0341
GEN-2019-073 | 02 NEBRASKA | 640149 | CREITON7 | 115 | 4.7116 | 4.71 | 0.0016
GEN-2019-073 | 02 NEBRASKA | 640157 | DAVIDCY7 | 115 | 5.6545 | 5.6525 | 0.002
GEN-2019-073 | 02 NEBRASKA | 640212 | HARTGTN7 | 115 | 5.1832 | 5.1819 | 0.0013
GEN-2019-073 | 02 NEBRASKA | 640263 | MADISON7 | 115 | 6.1678 | 6.1623 | 0.0055
GEN-2019-073 | 02 NEBRASKA | 640277 | MOORE 3 | 345 | 22.4804 | 22.47 | 0.0104
GEN-2019-073 | 02 NEBRASKA | 640293 | NELIGH 7 | 115 | 9.9449 | 9.9339 | 0.011
GEN-2019-073 | 02 NEBRASKA | 640357 | STANTON7 | 115 | 5.115 | 5.1118 | 0.0032
GEN-2019-073 | 02 NEBRASKA | 640386 | TWIN CH4 | 230 | 8.9225 | 8.9175 | 0.005
GEN-2019-073 | 02 NEBRASKA | 640387 | TWIN CH7 | 115 | 10.7822 | 10.7782 | 0.004
GEN-2019-073 | 02 NEBRASKA | 640522 | ANTELOPE 8 | 69 | 5.119 | 5.1169 | 0.0021
GEN-2019-073 | 02 NEBRASKA | 640540 | MEADOWGROVE4 | 230 | 5.0998 | 5.0973 | 0.0025
GEN-2019-073 | 02 NEBRASKA | 640561 | RTLSNAKE.W 4 | 230 | 7.1132 | 7.108 | 0.0052
GEN-2019-073 | 02 NEBRASKA | 643254 | UPSTREAM.W 7 | 115 | 13.3751 | 13.3516 | 0.0235
GEN-2019-073 | 02 NEBRASKA | 645451 | S3451 3 | 345 | 21.3318 | 21.3284 | 0.0034
GEN-2019-073 | 02 NEBRASKA | 650185 | WAGENER 3 | 345 | 20.0853 | 20.0765 | 0.0088
GEN-2019-073 | 02 NEBRASKA | 650214 | NW68HOLDRG7 | 115 | 24.3952 | 24.389 | 0.0062
GEN-2019-073 | 02 NEBRASKA | 652552 | SIOUXCY2 | 230 | 20.341 | 20.3329 | 0.0081
GEN-2019-073 | 02 NEBRASKA | 652864 | SIOUXCY-LNX3 | 345 | 15.1969 | 15.1908 | 0.0061
GEN-2019-073 | 02 NEBRASKA | 760788 | GEN-2017-201 | 345 | 8.2239 | 8.1747 | 0.0492
GEN-2019-073 | 02 NEBRASKA | 762069 | G17-105TAP | 161 | 8.3472 | 8.3464 | 0.0008
GEN-2019-073 | 02 NEBRASKA | 762780 | GEN-2018-043 | 345 | 12.7205 | 12.7188 | 0.0017
GEN-2019-073 | 02 NEBRASKA | 763450 | GEN-2018-132 | 345 | 6.6695 | 6.6436 | 0.0259
GEN-2019-073 | 02 NEBRASKA | 601006 | SPLT RK3 | 345 | 14.9416 | 14.9407 | 0.0009
GEN-2019-073 | 02 NEBRASKA | 635204 | NEAL N 8 | 69 | 9.7689 | 9.7684 | 0.0005
GEN-2019-073 | 02 NEBRASKA | 635219 | GARD AVE 3 | 345 | 8.9677 | 8.9668 | 0.0009
GEN-2019-073 | 02 NEBRASKA | 635221 | KELLOGG5 | 161 | 17.1226 | 17.1189 | 0.0037
GEN-2019-073 | 02 NEBRASKA | 635229 | AIRPORT 5 | 161 | 16.9835 | 16.9797 | 0.0038
GEN-2019-073 | 02 NEBRASKA | 635235 | SALIX 5 | 161 | 14.6126 | 14.6099 | 0.0027
GEN-2019-073 | 02 NEBRASKA | 635300 | MONONA 5 | 161 | 5.4609 | 5.4607 | 0.0002
GEN-2019-073 | 02 NEBRASKA | 635400 | HIGHLND 3 | 345 | 14.5121 | 14.5103 | 0.0018
GEN-2019-073 | 02 NEBRASKA | 637009 | GLACIAL EDGE | 345 | 15.6443 | 15.6406 | 0.0037
GEN-2019-073 | 02 NEBRASKA | 640073 | BATTLCR8 | 69 | 3.8906 | 3.8891 | 0.0015
GEN-2019-073 | 02 NEBRASKA | 640078 | BEEMER 7 | 115 | 4.396 | 4.3947 | 0.0013
GEN-2019-073 | 02 NEBRASKA | 640084 | BLMFLD 7 | 115 | 5.1275 | 5.1266 | 0.0009
GEN-2019-073 | 02 NEBRASKA | 640113 | CLRWATR7 | 115 | 5.1516 | 5.1493 | 0.0023
GEN-2019-073 | 02 NEBRASKA | 640122 | COL.DRY7 | 115 | 16.4842 | 16.4576 | 0.0266
GEN-2019-073 | 02 NEBRASKA | 640124 | COL.SE 7 | 115 | 16.6202 | 16.5944 | 0.0258
GEN-2019-073 | 02 NEBRASKA | 640150 | CREITON8 | 69 | 4.3586 | 4.3578 | 0.0008
GEN-2019-073 | 02 NEBRASKA | 640151 | CRESTON7 | 115 | 5.9927 | 5.988 | 0.0047
GEN-2019-073 | 02 NEBRASKA | 640163 | EMERSON7 | 115 | 5.4485 | 5.4475 | 0.001
GEN-2019-073 | 02 NEBRASKA | 640181 | GENOA 7 | 115 | 4.8706 | 4.8688 | 0.0018
GEN-2019-073 | 02 NEBRASKA | 640200 | GR ISLD4 | 230 | 16.413 | 16.4088 | 0.0042
GEN-2019-073 | 02 NEBRASKA | 640213 | HARTGTN8 | 69 | 3.4988 | 3.4984 | 0.0004
GEN-2019-073 | 02 NEBRASKA | 640271 | MCCOOL 3 | 345 | 10.8752 | 10.8732 | 0.002
GEN-2019-073 | 02 NEBRASKA | 640278 | SHELDON7 | 115 | 42.1871 | 42.1784 | 0.0087
GEN-2019-073 | 02 NEBRASKA | 640294 | NELIGH 8 | 69 | 5.8977 | 5.8954 | 0.0023
GEN-2019-073 | 02 NEBRASKA | 640316 | PAWNEEL7 | 115 | 11.1764 | 11.1748 | 0.0016
GEN-2019-073 | 02 NEBRASKA | 640336 | SCHUYLR7 | 115 | 5.8 | 5.7978 | 0.0022
GEN-2019-073 | 02 NEBRASKA | 640345 | SILVRCK7 | 115 | 4.5561 | 4.555 | 0.0011
GEN-2019-073 | 02 NEBRASKA | 640377 | TEKAMAH5 | 161 | 8.8894 | 8.8884 | 0.001
GEN-2019-073 | 02 NEBRASKA | 640388 | TWIN CH8 | 69 | 7.7842 | 7.7829 | 0.0013
GEN-2019-073 | 02 NEBRASKA | 640402 | WAHOO 7 | 115 | 4.7578 | 4.7572 | 0.0006
GEN-2019-073 | 02 NEBRASKA | 640424 | S.SIOUXCITY7 | 115 | 7.3706 | 7.3687 | 0.0019
GEN-2019-073 | 02 NEBRASKA | 640444 | PETERSBRG.N7 | 115 | 5.4317 | 5.4297 | 0.002
GEN-2019-073 | 02 NEBRASKA | 640525 | TOBIAS 3 | 345 | 11.6744 | 11.6724 | 0.002
GEN-2019-073 | 02 NEBRASKA | 640590 | MONOLITH 3 | 345 | 21.9978 | 21.988 | 0.0098
GEN-2019-073 | 02 NEBRASKA | 645454 | S3454 3 | 345 | 27.4247 | 27.4199 | 0.0048
GEN-2019-073 | 02 NEBRASKA | 645459 | S3459 3 | 345 | 24.0005 | 23.9976 | 0.0029
GEN-2019-073 | 02 NEBRASKA | 646251 | S1251 5 | 161 | 30.7514 | 30.7481 | 0.0033
GEN-2019-073 | 02 NEBRASKA | 648506 | PR BRZ 4 | 230 | 3.5115 | 3.5106 | 0.0009
GEN-2019-073 | 02 NEBRASKA | 650189 | 103&ROKEBY3 | 345 | 19.9772 | 19.9697 | 0.0075
GEN-2019-073 | 02 NEBRASKA | 650210 | NW70FAIRFD7 | 115 | 20.3803 | 20.3761 | 0.0042
GEN-2019-073 | 02 NEBRASKA | 650216 | SW27&F 7 | 115 | 21.0693 | 21.0654 | 0.0039
GEN-2019-073 | 02 NEBRASKA | 650285 | WAGENER 7 | 115 | 30.6415 | 30.6348 | 0.0067
GEN-2019-073 | 02 NEBRASKA | 650290 | ROKEBY 7 | 115 | 24.4224 | 24.4181 | 0.0043
GEN-2019-073 | 02 NEBRASKA | 652509 | FTRANDL4 | 230 | 12.1336 | 12.1322 | 0.0014
GEN-2019-073 | 02 NEBRASKA | 652511 | GAVINS 7 | 115 | 8.4307 | 8.4293 | 0.0014
GEN-2019-073 | 02 NEBRASKA | 652565 | SIOUXCY4 | 230 | 20.341 | 20.3329 | 0.0081
GEN-2019-073 | 02 NEBRASKA | 659900 | EAGLE___-NI4 | 230 | 7.3012 | 7.3006 | 0.0006
GEN-2019-073 | 02 NEBRASKA | 762070 | GEN-2017-105 | 161 | 8.3472 | 8.3464 | 0.0008
GEN-2019-073 | 02 NEBRASKA | 762603 | GEN-2018-025 | 345 | 20.4121 | 20.4089 | 0.0032
GEN-2018-063 | 03 CENTRAL | 762992 | G18-063-TAP | 69 | 7.6098 | 7.0438 | 0.566
GEN-2018-063 | 03 CENTRAL | 541271 | SEDN 2 | 69 | 7.6575 | 7.101 | 0.5565
GEN-2018-063 | 03 CENTRAL | 541273 | KELHYS 2 | 69 | 7.1973 | 6.7366 | 0.4607
GEN-2018-063 | 03 CENTRAL | 762988 | GEN-2018-063 | 69 | 7.5168 | 6.9502 | 0.5666
GEN-2018-063 | 03 CENTRAL | 541209 | SEDALIA5 | 161 | 9.488 | 9.3239 | 0.1641
GEN-2018-063 | 03 CENTRAL | 541272 | SEDS 2 | 69 | 6.4972 | 6.3168 | 0.1804
GEN-2018-063 | 03 CENTRAL | 541275 | SEDPLT 2 | 69 | 6.7045 | 6.4312 | 0.2733
GEN-2018-063 | 03 CENTRAL | 541535 | LAMONTETP | 69 | 5.019 | 4.8629 | 0.1561
GEN-2018-063 | 03 CENTRAL | 300082 | 5GEORGE | 161 | 8.0678 | 7.9636 | 0.1042
GEN-2018-063 | 03 CENTRAL | 300117 | 5SEDALA | 161 | 8.7226 | 8.6047 | 0.1179
GEN-2018-063 | 03 CENTRAL | 541146 | SEDLIAW_CAP5 | 161 | 8.9714 | 8.8246 | 0.1468
GEN-2018-063 | 03 CENTRAL | 541241 | SEDEAST5 | 161 | 7.4272 | 7.3539 | 0.0733
GEN-2018-063 | 03 CENTRAL | 541274 | PITTCRN2 | 69 | 6.4634 | 6.2621 | 0.2013
GEN-2018-063 | 03 CENTRAL | 541276 | COLECMP2 | 69 | 2.9832 | 2.9547 | 0.0285
GEN-2018-063 | 03 CENTRAL | 541337 | WAFBE_SW5 | 161 | 6.4778 | 6.4238 | 0.054
GEN-2018-063 | 03 CENTRAL | 541534 | KNOSTERTP | 69 | 4.8432 | 4.7642 | 0.079
GEN-2018-063 | 03 CENTRAL | 541536 | LAMONTE | 69 | 4.8612 | 4.7145 | 0.1467
GEN-2018-063 | 03 CENTRAL | 300531 | 2GEORGE | 69 | 7.7248 | 7.6955 | 0.0293
GEN-2018-063 | 03 CENTRAL | 300541 | 2SEDALI | 69 | 9.8713 | 9.8296 | 0.0417
GEN-2018-063 | 03 CENTRAL | 301567 | 5NORTONTP | 161 | 5.9707 | 5.9479 | 0.0228
GEN-2018-063 | 03 CENTRAL | 345411 | 5OVERTON 2 | 161 | 20.312 | 20.2904 | 0.0216
GEN-2018-063 | 03 CENTRAL | 541217 | WINDSR 5 | 161 | 7.4775 | 7.4402 | 0.0373
GEN-2018-063 | 03 CENTRAL | 541270 | KNOSTER2 | 69 | 4.7888 | 4.7116 | 0.0772
GEN-2018-063 | 03 CENTRAL | 541281 | WARSAWTP | 69 | 2.9776 | 2.9676 | 0.01
GEN-2018-063 | 03 CENTRAL | 541335 | WAFBW_SW5 | 161 | 6.4505 | 6.3977 | 0.0528
GEN-2018-063 | 03 CENTRAL | 541338 | WAFBE5 | 161 | 5.8893 | 5.8444 | 0.0449
GEN-2018-063 | 03 CENTRAL | 541395 | NUCOR5 | 161 | 6.9616 | 6.8972 | 0.0644
GEN-2018-063 | 03 CENTRAL | 541524 | MONSERTP | 69 | 5.6743 | 5.6129 | 0.0614
GEN-2018-063 | 03 CENTRAL | 99911 | GI91POI | 69 | 2.8091 | 2.8075 | 0.0016
GEN-2018-063 | 03 CENTRAL | 300071 | 5CLINTN | 161 | 13.6834 | 13.6494 | 0.034
GEN-2018-063 | 03 CENTRAL | 300105 | 5NORTON | 161 | 6.4294 | 6.4089 | 0.0205
GEN-2018-063 | 03 CENTRAL | 300529 | 2GEOGT1 | 69 | 7.0756 | 7.0513 | 0.0243
GEN-2018-063 | 03 CENTRAL | 300530 | 2GEOGT2 | 69 | 7.6378 | 7.6096 | 0.0282
GEN-2018-063 | 03 CENTRAL | 300534 | 2LINCLN | 69 | 4.7353 | 4.7302 | 0.0051
GEN-2018-063 | 03 CENTRAL | 300545 | 2SYLVAN | 69 | 4.7109 | 4.7033 | 0.0076
GEN-2018-063 | 03 CENTRAL | 344233 | 5CALIF UE 1 | 161 | 10.3061 | 10.3014 | 0.0047
GEN-2018-063 | 03 CENTRAL | 345071 | 5MCBAIN T | 161 | 13.8678 | 13.8628 | 0.005
GEN-2018-063 | 03 CENTRAL | 345409 | 5OVERTON | 161 | 20.312 | 20.2904 | 0.0216
GEN-2018-063 | 03 CENTRAL | 346117 | 2OVERTON | 69 | 3.5113 | 3.511 | 0.0003
GEN-2018-063 | 03 CENTRAL | 541228 | WBURGE 5 | 161 | 6.3699 | 6.3271 | 0.0428
GEN-2018-063 | 03 CENTRAL | 541269 | WBURGE 2 | 69 | 6.7522 | 6.6934 | 0.0588
GEN-2018-063 | 03 CENTRAL | 541277 | WARSAW 2 | 69 | 3.2689 | 3.2603 | 0.0086
GEN-2018-063 | 03 CENTRAL | 541336 | WAFBW5 | 161 | 5.8632 | 5.8193 | 0.0439
GEN-2018-093 | 03 CENTRAL | 533040 | EVANS N4 | 138 | 32.3573 | 32.3573 | 0
GEN-2018-093 | 03 CENTRAL | 532796 | WICHITA7 | 345 | 23.7708 | 23.7708 | 0
GEN-2018-093 | 03 CENTRAL | 533041 | EVANS S4 | 138 | 32.2762 | 32.2762 | 0
GEN-2018-093 | 03 CENTRAL | 533054 | MAIZE 4 | 138 | 20.7931 | 20.7931 | 0
GEN-2018-093 | 03 CENTRAL | 533065 | SG12COL4 | 138 | 19.3466 | 19.3466 | 0
GEN-2018-093 | 03 CENTRAL | 589060 | GEN-2017-068 | 138 | 29.2988 | 29.2988 | 0
GEN-2018-093 | 03 CENTRAL | 760620 | GEN-2017-179 | 138 | 7.0944 | 7.0944 | 0
GEN-2018-093 | 03 CENTRAL | 760641 | GEN-2017-226 | 138 | 32.1766 | 32.1766 | 0
GEN-2018-093 | 03 CENTRAL | 762922 | GEN-2018-057 | 138 | 17.2503 | 17.2503 | 0
GEN-2018-093 | 03 CENTRAL | 532771 | RENO 7 | 345 | 11.0976 | 11.0976 | 0
GEN-2018-093 | 03 CENTRAL | 532782 | BUFFALO7 | 345 | 20.7555 | 20.7555 | 0
GEN-2018-093 | 03 CENTRAL | 532791 | BENTON 7 | 345 | 19.0077 | 19.0077 | 0
GEN-2018-093 | 03 CENTRAL | 532798 | VIOLA 7 | 345 | 14.0837 | 14.0837 | 0
GEN-2018-093 | 03 CENTRAL | 533015 | BENTLEY4 | 138 | 10.662 | 10.662 | 0
GEN-2018-093 | 03 CENTRAL | 533035 | CHISHLM4 | 138 | 21.2473 | 21.2473 | 0
GEN-2018-093 | 03 CENTRAL | 533053 | LAKERDG4 | 138 | 17.1004 | 17.1004 | 0
GEN-2018-093 | 03 CENTRAL | 533074 | 45TH ST4 | 138 | 23.6427 | 23.6427 | 0
GEN-2018-093 | 03 CENTRAL | 562476 | G14-001-TAP | 345 | 10.3737 | 10.3737 | 0
GEN-2018-093 | 03 CENTRAL | 532768 | EMPEC 7 | 345 | 16.1367 | 16.1367 | 0
GEN-2018-093 | 03 CENTRAL | 532783 | KINGMAN7 | 345 | 7.0277 | 7.0277 | 0
GEN-2018-093 | 03 CENTRAL | 532794 | ROSEHIL7 | 345 | 18.8487 | 18.8487 | 0
GEN-2018-093 | 03 CENTRAL | 532797 | WOLFCRK7 | 345 | 20.9355 | 20.9355 | 0
GEN-2018-093 | 03 CENTRAL | 532986 | BENTON 4 | 138 | 27.7644 | 27.7644 | 0
GEN-2018-093 | 03 CENTRAL | 533011 | HALSTD 4 | 138 | 8.2176 | 8.2176 | 0
GEN-2018-093 | 03 CENTRAL | 533016 | WWUPLNT4 | 138 | 8.0701 | 8.0701 | 0
GEN-2018-093 | 03 CENTRAL | 533038 | COWSKIN4 | 138 | 17.2987 | 17.2987 | 0
GEN-2018-093 | 03 CENTRAL | 533049 | HOOVERN4 | 138 | 17.0029 | 17.0029 | 0
GEN-2018-093 | 03 CENTRAL | 533052 | PARKCTY4 | 138 | 20.0506 | 20.0506 | 0
GEN-2018-093 | 03 CENTRAL | 533064 | 17TH 4 | 138 | 17.4541 | 17.4541 | 0
GEN-2018-093 | 03 CENTRAL | 533075 | VIOLA 4 | 138 | 24.178 | 24.178 | 0
GEN-2018-093 | 03 CENTRAL | 533416 | RENO 3 | 115 | 22.1556 | 22.1556 | 0
GEN-2018-093 | 03 CENTRAL | 533786 | CHISHLM2 | 69 | 19.6762 | 19.6762 | 0
GEN-2018-093 | 03 CENTRAL | 539801 | THISTLE7 | 345 | 16.6662 | 16.6662 | 0
GEN-2018-093 | 03 CENTRAL | 583850 | GEN-2014-001 | 345 | 6.9804 | 6.9804 | 0
GEN-2018-093 | 03 CENTRAL | 587500 | GEN-2016-073 | 345 | 15.2224 | 15.2224 | 0
GEN-2018-093 | 03 CENTRAL | 587884 | G16-111-TAP | 345 | 9.7651 | 9.7651 | 0
GEN-2018-093 | 03 CENTRAL | 588364 | G16-153-TAP | 345 | 7.5063 | 7.5063 | 0
GEN-2018-093 | 03 CENTRAL | 760284 | GEN-2017-220 | 345 | 20.642 | 20.642 | 0
GEN-2018-093 | 03 CENTRAL | 763421 | G18-128-TAP | 345 | 12.3337 | 12.3337 | 0
GEN-2018-093 | 03 CENTRAL | 300739 | 7BLACKBERRY | 345 | 15.3686 | 15.3686 | 0
GEN-2018-093 | 03 CENTRAL | 515543 | RENFROW7 | 345 | 12.8614 | 12.8614 | 0
GEN-2018-093 | 03 CENTRAL | 515852 | DGRASSE7 | 345 | 15.3179 | 15.3179 | 0
GEN-2018-093 | 03 CENTRAL | 532769 | LANG 7 | 345 | 15.9573 | 15.9573 | 0
GEN-2018-093 | 03 CENTRAL | 532770 | MORRIS 7 | 345 | 12.3047 | 12.3047 | 0
GEN-2018-093 | 03 CENTRAL | 532773 | SUMMIT 7 | 345 | 10.8577 | 10.8577 | 0
GEN-2018-093 | 03 CENTRAL | 532774 | SWISVAL7 | 345 | 17.4752 | 17.4752 | 0
GEN-2018-093 | 03 CENTRAL | 532776 | READWF 7 | 345 | 13.4721 | 13.4721 | 0
GEN-2018-093 | 03 CENTRAL | 532784 | NINN1WF7 | 345 | 5.8368 | 5.8368 | 0
GEN-2018-093 | 03 CENTRAL | 532792 | FR2EAST7 | 345 | 6.7853 | 6.7853 | 0
GEN-2018-093 | 03 CENTRAL | 532799 | WAVERLY7 | 345 | 17.6458 | 17.6458 | 0
GEN-2018-093 | 03 CENTRAL | 532800 | LATHAMS7 | 345 | 10.1116 | 10.1116 | 0
GEN-2018-093 | 03 CENTRAL | 532984 | SUMNER 4 | 138 | 12.1641 | 12.1641 | 0
GEN-2018-093 | 03 CENTRAL | 532988 | BELAIRE4 | 138 | 18.7122 | 18.7122 | 0
GEN-2018-093 | 03 CENTRAL | 532990 | MIDIAN 4 | 138 | 10.9264 | 10.9264 | 0
GEN-2018-093 | 03 CENTRAL | 533013 | MOUND 4 | 138 | 6.8271 | 6.8271 | 0
GEN-2018-093 | 03 CENTRAL | 533024 | 29TH 4 | 138 | 19.3465 | 19.3465 | 0
GEN-2018-093 | 03 CENTRAL | 533034 | CENTENN4 | 138 | 14.5959 | 14.5959 | 0
GEN-2018-093 | 03 CENTRAL | 533036 | CLEARWT4 | 138 | 14.0798 | 14.0798 | 0
GEN-2018-093 | 03 CENTRAL | 533043 | FOWLER 4 | 138 | 15.9921 | 15.9921 | 0
GEN-2018-093 | 03 CENTRAL | 533047 | GILL 4 | 138 | 21.798 | 21.798 | 0
GEN-2018-093 | 03 CENTRAL | 533050 | HOOVERS4 | 138 | 16.999 | 16.999 | 0
GEN-2018-093 | 03 CENTRAL | 533062 | ROSEHIL4 | 138 | 30.9062 | 30.9062 | 0
GEN-2018-093 | 03 CENTRAL | 533413 | CIRCLE 3 | 115 | 18.3479 | 18.3479 | 0
GEN-2018-093 | 03 CENTRAL | 533415 | DAVIS 3 | 115 | 8.0324 | 8.0324 | 0
GEN-2018-093 | 03 CENTRAL | 533429 | MOUNDRG3 | 115 | 8.416 | 8.416 | 0
GEN-2018-093 | 03 CENTRAL | 533438 | WMCPHER3 | 115 | 10.8946 | 10.8946 | 0
GEN-2018-093 | 03 CENTRAL | 533653 | WOLFCRK2 | 69 | 5.9769 | 5.9769 | 0
GEN-2018-093 | 03 CENTRAL | 533736 | HALSTED2 | 69 | 7.2362 | 7.2362 | 0
GEN-2018-093 | 03 CENTRAL | 533788 | COWSKIN2 | 69 | 15.7975 | 15.7975 | 0
GEN-2018-093 | 03 CENTRAL | 533799 | GRANT 2 | 69 | 12.2572 | 12.2572 | 0
GEN-2018-093 | 03 CENTRAL | 533805 | HOOVERN2 | 69 | 30.3162 | 30.3162 | 0
GEN-2018-093 | 03 CENTRAL | 533840 | 17TH 2 | 69 | 26.6358 | 26.6358 | 0
GEN-2018-093 | 03 CENTRAL | 533859 | RIPLEYE2 | 69 | 22.1933 | 22.1933 | 0
GEN-2018-093 | 03 CENTRAL | 539008 | MILAN_GOAB | 138 | 11.6885 | 11.6885 | 0
GEN-2018-093 | 03 CENTRAL | 539009 | CONWAY | 138 | 11.216 | 11.216 | 0
GEN-2018-093 | 03 CENTRAL | 539800 | CLARKCOUNTY7 | 345 | 12.7785 | 12.7785 | 0
GEN-2018-093 | 03 CENTRAL | 539804 | THISTLE4 | 138 | 17.5567 | 17.5567 | 0
GEN-2018-093 | 03 CENTRAL | 542965 | W.GRDNR7 | 345 | 31.7637 | 31.7637 | 0
GEN-2018-093 | 03 CENTRAL | 560053 | G15-052T | 345 | 13.3131 | 13.3131 | 0
GEN-2018-093 | 03 CENTRAL | 587880 | GEN-2016-111 | 345 | 6.4948 | 6.4948 | 0
GEN-2018-093 | 03 CENTRAL | 588360 | GEN-2016-153 | 345 | 7.1567 | 7.1567 | 0
GEN-2018-093 | 03 CENTRAL | 588630 | GEN-2017-018 | 345 | 16.6662 | 16.6662 | 0
GEN-2018-093 | 03 CENTRAL | 589240 | GEN-2017-086 | 345 | 6.2694 | 6.2694 | 0
GEN-2018-093 | 03 CENTRAL | 762834 | GEN-2018-049 | 345 | 6.9567 | 6.9567 | 0
GEN-2018-093 | 03 CENTRAL | 763417 | GEN-2018-128 | 345 | 11.1457 | 11.1457 | 0
GEN-2018-093 | 03 CENTRAL | 300740 | 7SPORTSMAN | 345 | 23.7932 | 23.7932 | 0
GEN-2018-093 | 03 CENTRAL | 300949 | 7JASPER | 345 | 12.5964 | 12.5964 | 0
GEN-2018-093 | 03 CENTRAL | 515375 | WWRDEHV7 | 345 | 22.3641 | 22.3641 | 0
GEN-2018-093 | 03 CENTRAL | 515476 | HUNTERS7 | 345 | 13.1988 | 13.1988 | 0
GEN-2018-093 | 03 CENTRAL | 515544 | RENFROW4 | 138 | 14.5957 | 14.5957 | 0
GEN-2018-093 | 03 CENTRAL | 515621 | OPENSKY7 | 345 | 13.269 | 13.269 | 0
GEN-2018-093 | 03 CENTRAL | 515646 | GRNTWD 7 | 345 | 11.2623 | 11.2623 | 0
GEN-2018-093 | 03 CENTRAL | 515853 | DGRASSE4 | 138 | 17.0745 | 17.0745 | 0
GEN-2018-093 | 03 CENTRAL | 531469 | SPERVIL7 | 345 | 13.6098 | 13.6098 | 0
GEN-2018-093 | 03 CENTRAL | 532766 | JEC N 7 | 345 | 21.3295 | 21.3295 | 0
GEN-2018-093 | 03 CENTRAL | 532767 | GEARY 7 | 345 | 9.8704 | 9.8704 | 0
GEN-2018-093 | 03 CENTRAL | 532780 | CANEYRV7 | 345 | 9.4765 | 9.4765 | 0
GEN-2018-093 | 03 CENTRAL | 532785 | PRATTWF7 | 345 | 4.8525 | 4.8525 | 0
GEN-2018-093 | 03 CENTRAL | 532793 | NEOSHO 7 | 345 | 17.5726 | 17.5726 | 0
GEN-2018-093 | 03 CENTRAL | 532795 | FR2WEST7 | 345 | 5.4247 | 5.4247 | 0
GEN-2018-093 | 03 CENTRAL | 532801 | ELKRVR17 | 345 | 8.9569 | 8.9569 | 0
GEN-2018-093 | 03 CENTRAL | 532802 | WAVERTX7 | 345 | 14.4336 | 14.4336 | 0
GEN-2018-093 | 03 CENTRAL | 532856 | SWISVAL6 | 230 | 21.669 | 21.669 | 0
GEN-2018-093 | 03 CENTRAL | 532863 | MORRIS 6 | 230 | 13.4941 | 13.4941 | 0
GEN-2018-093 | 03 CENTRAL | 532871 | CIRCLE 6 | 230 | 8.4637 | 8.4637 | 0
GEN-2018-093 | 03 CENTRAL | 532873 | SUMMIT 6 | 230 | 12.899 | 12.899 | 0
GEN-2018-093 | 03 CENTRAL | 532982 | OXFORD 4 | 138 | 10.7611 | 10.7611 | 0
GEN-2018-093 | 03 CENTRAL | 532987 | BUTLER 4 | 138 | 10.8593 | 10.8593 | 0
GEN-2018-093 | 03 CENTRAL | 532991 | WEAVER 4 | 138 | 21.9573 | 21.9573 | 0
GEN-2018-093 | 03 CENTRAL | 532992 | TIMBJCT4 | 138 | 6.4586 | 6.4586 | 0
GEN-2018-093 | 03 CENTRAL | 532994 | TCBURNS4 | 138 | 3.9642 | 3.9642 | 0
GEN-2018-093 | 03 CENTRAL | 533033 | CANAL 4 | 138 | 16.2295 | 16.2295 | 0
GEN-2018-093 | 03 CENTRAL | 533037 | COMOTAR4 | 138 | 18.4286 | 18.4286 | 0
GEN-2018-093 | 03 CENTRAL | 533039 | ELPASO 4 | 138 | 24.7628 | 24.7628 | 0
GEN-2018-093 | 03 CENTRAL | 533045 | GILL W 4 | 138 | 21.8043 | 21.8043 | 0
GEN-2018-093 | 03 CENTRAL | 533046 | GILL S 4 | 138 | 21.8015 | 21.8015 | 0
GEN-2018-093 | 03 CENTRAL | 533051 | INTERST4 | 138 | 15.6034 | 15.6034 | 0
GEN-2018-093 | 03 CENTRAL | 533060 | NOEASTE4 | 138 | 20.2853 | 20.2853 | 0
GEN-2018-093 | 03 CENTRAL | 533063 | SC10BEL4 | 138 | 11.9885 | 11.9885 | 0
GEN-2018-093 | 03 CENTRAL | 533068 | STEARMN4 | 138 | 19.3341 | 19.3341 | 0
GEN-2018-093 | 03 CENTRAL | 533073 | WACO N 4 | 138 | 18.8805 | 18.8805 | 0
GEN-2018-093 | 03 CENTRAL | 533304 | LANG 3 | 115 | 14.9641 | 14.9641 | 0
GEN-2018-093 | 03 CENTRAL | 533380 | SPRGCRK3 | 115 | 3.7906 | 3.7906 | 0
GEN-2018-093 | 03 CENTRAL | 533394 | CORONAD3 | 115 | 6.9686 | 6.9686 | 0
GEN-2018-093 | 03 CENTRAL | 533412 | ARKVALJ3 | 115 | 9.6861 | 9.6861 | 0
GEN-2018-093 | 03 CENTRAL | 533414 | CITIES 3 | 115 | 7.852 | 7.852 | 0
GEN-2018-093 | 03 CENTRAL | 533419 | HEC 3 | 115 | 17.1573 | 17.1573 | 0
GEN-2018-093 | 03 CENTRAL | 533421 | HEC GT 3 | 115 | 17.8389 | 17.8389 | 0
GEN-2018-093 | 03 CENTRAL | 533426 | MANVILE3 | 115 | 8.3015 | 8.3015 | 0
GEN-2018-093 | 03 CENTRAL | 533428 | MCPHER 3 | 115 | 10.5159 | 10.5159 | 0
GEN-2018-093 | 03 CENTRAL | 533430 | MNDRGCT3 | 115 | 6.4875 | 6.4875 | 0
GEN-2018-093 | 03 CENTRAL | 533439 | WHEATLD3 | 115 | 6.7596 | 6.7596 | 0
GEN-2018-093 | 03 CENTRAL | 533506 | DAVIS 2 | 69 | 7.1642 | 7.1642 | 0
GEN-2018-093 | 03 CENTRAL | 533597 | MIDIANW2 | 69 | 14.0106 | 14.0106 | 0
GEN-2018-093 | 03 CENTRAL | 533626 | BURLJCT2 | 69 | 4.935 | 4.935 | 0
GEN-2018-093 | 03 CENTRAL | 533629 | CC2SHAR2 | 69 | 4.6157 | 4.6157 | 0
GEN-2018-093 | 03 CENTRAL | 533732 | BURRTON2 | 69 | 2.8616 | 2.8616 | 0
GEN-2018-093 | 03 CENTRAL | 533742 | MOUND 2 | 69 | 7.005 | 7.005 | 0
GEN-2018-093 | 03 CENTRAL | 533744 | MUDCRKJ2 | 69 | 5.9011 | 5.9011 | 0
GEN-2018-093 | 03 CENTRAL | 533800 | GRANT J2 | 69 | 9.6057 | 9.6057 | 0
GEN-2018-093 | 03 CENTRAL | 533806 | HOOVERS2 | 69 | 30.3398 | 30.3398 | 0
GEN-2018-093 | 03 CENTRAL | 533814 | MASCOT 2 | 69 | 19.4577 | 19.4577 | 0
GEN-2018-093 | 03 CENTRAL | 533818 | MEAD N 2 | 69 | 25.1118 | 25.1118 | 0
GEN-2018-093 | 03 CENTRAL | 533820 | MOSSMAN2 | 69 | 17.6038 | 17.6038 | 0
GEN-2018-093 | 03 CENTRAL | 533831 | RENEW 2 | 69 | 17.1966 | 17.1966 | 0
GEN-2018-093 | 03 CENTRAL | 533835 | 17TH TP2 | 69 | 24.4573 | 24.4573 | 0
GEN-2018-093 | 03 CENTRAL | 533849 | VISTAPK2 | 69 | 16.7447 | 16.7447 | 0
GEN-2018-093 | 03 CENTRAL | 533854 | WESTLNK2 | 69 | 14.8803 | 14.8803 | 0
GEN-2018-093 | 03 CENTRAL | 533855 | WATER1 2 | 69 | 23.2756 | 23.2756 | 0
GEN-2018-093 | 03 CENTRAL | 533860 | RIPLEYM2 | 69 | 22.1966 | 22.1966 | 0
GEN-2018-093 | 03 CENTRAL | 533861 | BU5FURL2 | 69 | 6.9643 | 6.9643 | 0
GEN-2018-093 | 03 CENTRAL | 533874 | SG9STMK2 | 69 | 15.7676 | 15.7676 | 0
GEN-2018-093 | 03 CENTRAL | 533879 | GODDTAP2 | 69 | 7.9736 | 7.9736 | 0
GEN-2018-093 | 03 CENTRAL | 539003 | CLDWELL4 | 138 | 5.565 | 5.565 | 0
GEN-2018-093 | 03 CENTRAL | 539638 | FLATRDG4 | 138 | 15.5636 | 15.5636 | 0
GEN-2018-093 | 03 CENTRAL | 539675 | MILANTP4 | 138 | 9.9006 | 9.9006 | 0
GEN-2018-093 | 03 CENTRAL | 539676 | MILAN 4 | 138 | 10.3753 | 10.3753 | 0
GEN-2018-093 | 03 CENTRAL | 539813 | TRANSFORMER | 345 | 10.6791 | 10.6791 | 0
GEN-2018-093 | 03 CENTRAL | 539840 | GEN-2011-008 | 345 | 10.5555 | 10.5555 | 0
GEN-2018-093 | 03 CENTRAL | 542966 | WGARDNR5 | 161 | 29.2108 | 29.2108 | 0
GEN-2018-093 | 03 CENTRAL | 542968 | STILWEL7 | 345 | 25.8957 | 25.8957 | 0
GEN-2018-093 | 03 CENTRAL | 542977 | CRAIG 7 | 345 | 26.3941 | 26.3941 | 0
GEN-2018-093 | 03 CENTRAL | 542981 | LACYGNE7 | 345 | 26.1692 | 26.1692 | 0
GEN-2018-093 | 03 CENTRAL | 560080 | G16-046-TAP | 345 | 11.3684 | 11.3684 | 0
GEN-2018-093 | 03 CENTRAL | 584900 | GEN-2015-052 | 345 | 13.2613 | 13.2613 | 0
GEN-2018-093 | 03 CENTRAL | 588300 | GEN-2016-157 | 345 | 5.0515 | 5.0515 | 0
GEN-2018-093 | 03 CENTRAL | 588494 | G17-004-TAP | 345 | 9.3029 | 9.3029 | 0
GEN-2018-093 | 03 CENTRAL | 760809 | GEN-2017-203 | 345 | 9.1645 | 9.1645 | 0
GEN-2018-093 | 03 CENTRAL | 761838 | GEN-2017-121 | 138 | 9.138 | 9.138 | 0
GEN-2018-093 | 03 CENTRAL | 761901 | GEN-2017-125 | 345 | 5.5096 | 5.5096 | 0
GEN-2018-093 | 03 CENTRAL | 761943 | GEN-2017-191 | 345 | 17.4283 | 17.4283 | 0
GEN-2018-093 | 03 CENTRAL | 762279 | GEN-2017-195 | 345 | 31.6624 | 31.6624 | 0
GEN-2018-093 | 03 CENTRAL | 763890 | GEN-2019-058 | 345 | 12.52 | 12.52 | 0
GEN-2018-108 | 03 CENTRAL | 539801 | THISTLE7 | 345 | 16.6662 | 16.6662 | 0
GEN-2018-108 | 03 CENTRAL | 515852 | DGRASSE7 | 345 | 15.3179 | 15.3179 | 0
GEN-2018-108 | 03 CENTRAL | 532782 | BUFFALO7 | 345 | 20.7555 | 20.7555 | 0
GEN-2018-108 | 03 CENTRAL | 539800 | CLARKCOUNTY7 | 345 | 12.7785 | 12.7785 | 0
GEN-2018-108 | 03 CENTRAL | 539804 | THISTLE4 | 138 | 17.5567 | 17.5567 | 0
GEN-2018-108 | 03 CENTRAL | 588630 | GEN-2017-018 | 345 | 16.6662 | 16.6662 | 0
GEN-2018-108 | 03 CENTRAL | 762834 | GEN-2018-049 | 345 | 6.9567 | 6.9567 | 0
GEN-2018-108 | 03 CENTRAL | 515375 | WWRDEHV7 | 345 | 22.3641 | 22.3641 | 0
GEN-2018-108 | 03 CENTRAL | 515853 | DGRASSE4 | 138 | 17.0745 | 17.0745 | 0
GEN-2018-108 | 03 CENTRAL | 531469 | SPERVIL7 | 345 | 13.6098 | 13.6098 | 0
GEN-2018-108 | 03 CENTRAL | 532783 | KINGMAN7 | 345 | 7.0277 | 7.0277 | 0
GEN-2018-108 | 03 CENTRAL | 532796 | WICHITA7 | 345 | 23.7708 | 23.7708 | 0
GEN-2018-108 | 03 CENTRAL | 539638 | FLATRDG4 | 138 | 15.5636 | 15.5636 | 0
GEN-2018-108 | 03 CENTRAL | 539813 | TRANSFORMER | 345 | 10.6791 | 10.6791 | 0
GEN-2018-108 | 03 CENTRAL | 539840 | GEN-2011-008 | 345 | 10.5555 | 10.5555 | 0
GEN-2018-108 | 03 CENTRAL | 560080 | G16-046-TAP | 345 | 11.3684 | 11.3684 | 0
GEN-2018-108 | 03 CENTRAL | 587500 | GEN-2016-073 | 345 | 15.2224 | 15.2224 | 0
GEN-2018-108 | 03 CENTRAL | 760284 | GEN-2017-220 | 345 | 20.642 | 20.642 | 0
GEN-2018-108 | 03 CENTRAL | 763890 | GEN-2019-058 | 345 | 12.52 | 12.52 | 0
GEN-2018-108 | 03 CENTRAL | 514795 | KNOBHIL4 | 138 | 10.2855 | 10.2855 | 0
GEN-2018-108 | 03 CENTRAL | 515376 | WWRDEHV4 | 138 | 24.8769 | 24.8769 | 0
GEN-2018-108 | 03 CENTRAL | 515407 | TATONGA7 | 345 | 17.5658 | 17.5658 | 0
GEN-2018-108 | 03 CENTRAL | 515554 | BVRCNTY7 | 345 | 15.3093 | 15.3093 | 0
GEN-2018-108 | 03 CENTRAL | 515599 | G07621119-20 | 345 | 13.4849 | 13.4849 | 0
GEN-2018-108 | 03 CENTRAL | 515961 | GUTHRIE7 | 345 | 12.8816 | 12.8816 | 0
GEN-2018-108 | 03 CENTRAL | 516106 | BOBCAT 7 | 345 | 15.796 | 15.796 | 0
GEN-2018-108 | 03 CENTRAL | 520436 | ROSEVLY4 | 138 | 12.3574 | 12.3574 | 0
GEN-2018-108 | 03 CENTRAL | 520999 | MOORLND4 | 138 | 20.0616 | 20.0616 | 0
GEN-2018-108 | 03 CENTRAL | 530583 | POSTROCK7 | 345 | 7.7231 | 7.7231 | 0
GEN-2018-108 | 03 CENTRAL | 531501 | BUCKNER7 | 345 | 9.2456 | 9.2456 | 0
GEN-2018-108 | 03 CENTRAL | 532771 | RENO 7 | 345 | 11.0976 | 11.0976 | 0
GEN-2018-108 | 03 CENTRAL | 532784 | NINN1WF7 | 345 | 5.8368 | 5.8368 | 0
GEN-2018-108 | 03 CENTRAL | 532791 | BENTON 7 | 345 | 19.0077 | 19.0077 | 0
GEN-2018-108 | 03 CENTRAL | 532798 | VIOLA 7 | 345 | 14.0837 | 14.0837 | 0
GEN-2018-108 | 03 CENTRAL | 533040 | EVANS N4 | 138 | 32.3573 | 32.3573 | 0
GEN-2018-108 | 03 CENTRAL | 539631 | FLATRWD4 | 138 | 10.3815 | 10.3815 | 0
GEN-2018-108 | 03 CENTRAL | 539668 | HARPER 4 | 138 | 7.2122 | 7.2122 | 0
GEN-2018-108 | 03 CENTRAL | 539674 | BARBER 4 | 138 | 8.2322 | 8.2322 | 0
GEN-2018-108 | 03 CENTRAL | 539695 | SPEARVL6 | 230 | 12.772 | 12.772 | 0
GEN-2018-108 | 03 CENTRAL | 539759 | SPRVL 3 | 115 | 12.8273 | 12.8273 | 0
GEN-2018-108 | 03 CENTRAL | 539803 | IRONWOOD7 | 345 | 13.1638 | 13.1638 | 0
GEN-2018-108 | 03 CENTRAL | 539841 | G-2011-008-1 | 345 | 10.5555 | 10.5555 | 0
GEN-2018-108 | 03 CENTRAL | 539855 | G-2011-008-2 | 345 | 8.8342 | 8.8342 | 0
GEN-2018-108 | 03 CENTRAL | 539857 | G-2011-008-3 | 345 | 8.2708 | 8.2708 | 0
GEN-2018-108 | 03 CENTRAL | 562476 | G14-001-TAP | 345 | 10.3737 | 10.3737 | 0
GEN-2018-108 | 03 CENTRAL | 585300 | GEN-2015-095 | 138 | 16.8692 | 16.8692 | 0
GEN-2018-108 | 03 CENTRAL | 587310 | GEN-2016-046 | 345 | 9.9533 | 9.9533 | 0
GEN-2018-108 | 03 CENTRAL | 755000 | WWDBORDT | 345 | 12.2648 | 12.2648 | 0
GEN-2018-108 | 03 CENTRAL | 763527 | GEN-2019-012 | 345 | 19.3711 | 19.3711 | 0
GEN-2018-108 | 03 CENTRAL | 763769 | GEN-2019-045 | 138 | 17.0745 | 17.0745 | 0
GEN-2018-108 | 03 CENTRAL | 511553 | CHISHOLM7 | 345 | 12.3397 | 12.3397 | 0
GEN-2018-108 | 03 CENTRAL | 514785 | WOODWRD4 | 138 | 13.1123 | 13.1123 | 0
GEN-2018-108 | 03 CENTRAL | 514788 | GLASMTN4 | 138 | 5.1117 | 5.1117 | 0
GEN-2018-108 | 03 CENTRAL | 514794 | KNOBHIL2 | 69 | 8.8727 | 8.8727 | 0
GEN-2018-108 | 03 CENTRAL | 514796 | IODINE-4 | 138 | 7.3201 | 7.3201 | 0
GEN-2018-108 | 03 CENTRAL | 515394 | KEENAN 4 | 138 | 8.9414 | 8.9414 | 0
GEN-2018-108 | 03 CENTRAL | 515398 | OUSPRT 4 | 138 | 9.528 | 9.528 | 0
GEN-2018-108 | 03 CENTRAL | 515425 | WWDPST 4 | 138 | 17.7977 | 17.7977 | 0
GEN-2018-108 | 03 CENTRAL | 515448 | CRSRDSW7 | 345 | 12.1468 | 12.1468 | 0
GEN-2018-108 | 03 CENTRAL | 515458 | BORDER 7 | 345 | 8.2517 | 8.2517 | 0
GEN-2018-108 | 03 CENTRAL | 515497 | MATHWSN7 | 345 | 32.7952 | 32.7952 | 0
GEN-2018-108 | 03 CENTRAL | 515582 | SLNGWND7 | 345 | 8.4766 | 8.4766 | 0
GEN-2018-108 | 03 CENTRAL | 515585 | MAMTHPW7 | 345 | 13.5669 | 13.5669 | 0
GEN-2018-108 | 03 CENTRAL | 515590 | PALDR2W7 | 345 | 12.8669 | 12.8669 | 0
GEN-2018-108 | 03 CENTRAL | 515618 | BALKOW 7 | 345 | 12.5807 | 12.5807 | 0
GEN-2018-108 | 03 CENTRAL | 515677 | BADGER 7 | 345 | 13.7821 | 13.7821 | 0
GEN-2018-108 | 03 CENTRAL | 515785 | WINDFRM4 | 138 | 19.5945 | 19.5945 | 0
GEN-2018-108 | 03 CENTRAL | 515825 | GRTWSRN7 | 345 | 9.0702 | 9.0702 | 0
GEN-2018-108 | 03 CENTRAL | 515951 | PERSIMN7 | 345 | 11.0796 | 11.0796 | 0
GEN-2018-108 | 03 CENTRAL | 516146 | 25MILE 7 | 345 | 11.1221 | 11.1221 | 0
GEN-2018-108 | 03 CENTRAL | 520425 | PIC4 | 138 | 7.9856 | 7.9856 | 0
GEN-2018-108 | 03 CENTRAL | 520430 | NOELSW 4 | 138 | 10.3556 | 10.3556 | 0
GEN-2018-108 | 03 CENTRAL | 520462 | ASPEN 4 | 138 | 19.3561 | 19.3561 | 0
GEN-2018-108 | 03 CENTRAL | 520553 | SEILING4 | 138 | 6.6101 | 6.6101 | 0
GEN-2018-108 | 03 CENTRAL | 520601 | AVARD 4 | 138 | 6.857 | 6.857 | 0
GEN-2018-108 | 03 CENTRAL | 520957 | IODINE 4 | 138 | 7.673 | 7.673 | 0
GEN-2018-108 | 03 CENTRAL | 520995 | MOORLND2 | 69 | 8.5299 | 8.5299 | 0
GEN-2018-108 | 03 CENTRAL | 523097 | HITCHLAND 7 | 345 | 14.9713 | 14.9713 | 0
GEN-2018-108 | 03 CENTRAL | 530584 | POSTROCK6 | 230 | 10.7096 | 10.7096 | 0
GEN-2018-108 | 03 CENTRAL | 531449 | HOLCOMB7 | 345 | 9.9438 | 9.9438 | 0
GEN-2018-108 | 03 CENTRAL | 531502 | CIMRRN 7 | 345 | 7.3025 | 7.3025 | 0
GEN-2018-108 | 03 CENTRAL | 531504 | CIMWD2 7 | 345 | 7.4234 | 7.4234 | 0
GEN-2018-108 | 03 CENTRAL | 532768 | EMPEC 7 | 345 | 16.1367 | 16.1367 | 0
GEN-2018-108 | 03 CENTRAL | 532785 | PRATTWF7 | 345 | 4.8525 | 4.8525 | 0
GEN-2018-108 | 03 CENTRAL | 532794 | ROSEHIL7 | 345 | 18.8487 | 18.8487 | 0
GEN-2018-108 | 03 CENTRAL | 532797 | WOLFCRK7 | 345 | 20.9355 | 20.9355 | 0
GEN-2018-108 | 03 CENTRAL | 532986 | BENTON 4 | 138 | 27.7644 | 27.7644 | 0
GEN-2018-108 | 03 CENTRAL | 533041 | EVANS S4 | 138 | 32.2762 | 32.2762 | 0
GEN-2018-108 | 03 CENTRAL | 533054 | MAIZE 4 | 138 | 20.7931 | 20.7931 | 0
GEN-2018-108 | 03 CENTRAL | 533065 | SG12COL4 | 138 | 19.3466 | 19.3466 | 0
GEN-2018-108 | 03 CENTRAL | 533075 | VIOLA 4 | 138 | 24.178 | 24.178 | 0
GEN-2018-108 | 03 CENTRAL | 533416 | RENO 3 | 115 | 22.1556 | 22.1556 | 0
GEN-2018-108 | 03 CENTRAL | 539000 | RAGO 4 | 138 | 3.9467 | 3.9467 | 0
GEN-2018-108 | 03 CENTRAL | 539001 | ANTHONY4 | 138 | 5.012 | 5.012 | 0
GEN-2018-108 | 03 CENTRAL | 539117 | SPRVILL-EHVB | 230 | 12.4582 | 12.4582 | 0
GEN-2018-108 | 03 CENTRAL | 539675 | MILANTP4 | 138 | 9.9006 | 9.9006 | 0
GEN-2018-108 | 03 CENTRAL | 539694 | SPEARVL3 | 115 | 9.9365 | 9.9365 | 0
GEN-2018-108 | 03 CENTRAL | 539760 | BARBER 3 | 115 | 8.1332 | 8.1332 | 0
GEN-2018-108 | 03 CENTRAL | 539771 | NFTDODG3 | 115 | 9.7556 | 9.7556 | 0
GEN-2018-108 | 03 CENTRAL | 539815 | IRONWOOD WF7 | 345 | 11.8843 | 11.8843 | 0
GEN-2018-108 | 03 CENTRAL | 560082 | G16-050-TAP | 345 | 6.9512 | 6.9512 | 0
GEN-2018-108 | 03 CENTRAL | 579480 | GEN-2008-124 | 345 | 12.711 | 12.711 | 0
GEN-2018-108 | 03 CENTRAL | 583850 | GEN-2014-001 | 345 | 6.9804 | 6.9804 | 0
GEN-2018-108 | 03 CENTRAL | 585410 | GREAT_WESTRN | 345 | 9.7415 | 9.7415 | 0
GEN-2018-108 | 03 CENTRAL | 585430 | PRSIMN_CRK1 | 345 | 11.7445 | 11.7445 | 0
GEN-2018-108 | 03 CENTRAL | 587140 | GEN-2016-020 | 138 | 7.4213 | 7.4213 | 0
GEN-2018-108 | 03 CENTRAL | 587311 | G16-046XFMR1 | 115 | 14.7707 | 14.7707 | 0
GEN-2018-108 | 03 CENTRAL | 587884 | G16-111-TAP | 345 | 9.7651 | 9.7651 | 0
GEN-2018-108 | 03 CENTRAL | 588364 | G16-153-TAP | 345 | 7.5063 | 7.5063 | 0
GEN-2018-108 | 03 CENTRAL | 588560 | GEN-2017-011 | 345 | 12.6206 | 12.6206 | 0
GEN-2018-108 | 03 CENTRAL | 589060 | GEN-2017-068 | 138 | 29.2988 | 29.2988 | 0
GEN-2018-108 | 03 CENTRAL | 760620 | GEN-2017-179 | 138 | 7.0944 | 7.0944 | 0
GEN-2018-108 | 03 CENTRAL | 760641 | GEN-2017-226 | 138 | 32.1766 | 32.1766 | 0
GEN-2018-108 | 03 CENTRAL | 762922 | GEN-2018-057 | 138 | 17.2503 | 17.2503 | 0
GEN-2018-108 | 03 CENTRAL | 763421 | G18-128-TAP | 345 | 12.3337 | 12.3337 | 0
GEN-2018-108 | 03 CENTRAL | 763670 | GEN-2019-030 | 345 | 10.4948 | 10.4948 | 0
GEN-2018-108 | 03 CENTRAL | 763850 | G19-055-TAP | 230 | 7.2471 | 7.2471 | 0
GEN-2018-108 | 03 CENTRAL | 300739 | 7BLACKBERRY | 345 | 15.3686 | 15.3686 | 0
GEN-2018-108 | 03 CENTRAL | 511557 | CHISHOLM6 | 230 | 12.1566 | 12.1566 | 0
GEN-2018-108 | 03 CENTRAL | 514778 | CLEOCOR4 | 138 | 6.333 | 6.333 | 0
GEN-2018-108 | 03 CENTRAL | 514782 | WODWRD 2 | 69 | 10.8998 | 10.8998 | 0
GEN-2018-108 | 03 CENTRAL | 514792 | ALVAOGE2 | 69 | 7.5035 | 7.5035 | 0
GEN-2018-108 | 03 CENTRAL | 514880 | NORTWST7 | 345 | 32.9086 | 32.9086 | 0
GEN-2018-108 | 03 CENTRAL | 514901 | CIMARON7 | 345 | 34.2931 | 34.2931 | 0
GEN-2018-108 | 03 CENTRAL | 515363 | CENT 4 | 138 | 3.0872 | 3.0872 | 0
GEN-2018-108 | 03 CENTRAL | 515533 | REDCLFT4 | 138 | 6.6178 | 6.6178 | 0
GEN-2018-108 | 03 CENTRAL | 515543 | RENFROW7 | 345 | 12.8614 | 12.8614 | 0
GEN-2018-108 | 03 CENTRAL | 515560 | CZYCRVT2 | 69 | 3.2399 | 3.2399 | 0
GEN-2018-108 | 03 CENTRAL | 515634 | PALDR1W7 | 345 | 10.943 | 10.943 | 0
GEN-2018-108 | 03 CENTRAL | 515686 | BLUWND 7 | 345 | 12.3633 | 12.3633 | 0
GEN-2018-108 | 03 CENTRAL | 515786 | FPLWIND4 | 138 | 6.1883 | 6.1883 | 0
GEN-2018-108 | 03 CENTRAL | 515875 | REDNGTN7 | 345 | 16.7149 | 16.7149 | 0
GEN-2018-108 | 03 CENTRAL | 516159 | 25MILZ 7 | 345 | 11.1104 | 11.1104 | 0
GEN-2018-108 | 03 CENTRAL | 520437 | SALTPLN4 | 138 | 6.3315 | 6.3315 | 0
GEN-2018-108 | 03 CENTRAL | 520500 | BEARCAT4 | 138 | 14.2641 | 14.2641 | 0
GEN-2018-108 | 03 CENTRAL | 520848 | CDRDLTP4 | 138 | 5.714 | 5.714 | 0
GEN-2018-108 | 03 CENTRAL | 520920 | FTSUPLY4 | 138 | 5.225 | 5.225 | 0
GEN-2018-108 | 03 CENTRAL | 521065 | TALOGA 4 | 138 | 7.1703 | 7.1703 | 0
GEN-2018-108 | 03 CENTRAL | 521197 | CRTSJCT2 | 69 | 8.1375 | 8.1375 | 0
GEN-2018-108 | 03 CENTRAL | 523095 | HITCHLAND 6 | 230 | 14.5761 | 14.5761 | 0
GEN-2018-108 | 03 CENTRAL | 523101 | NOBLE_WND 7 | 345 | 14.9103 | 14.9103 | 0
GEN-2018-108 | 03 CENTRAL | 523112 | NOVUS1 7 | 345 | 14.6716 | 14.6716 | 0
GEN-2018-108 | 03 CENTRAL | 523823 | CARPENTER 7 | 345 | 6.5781 | 6.5781 | 0
GEN-2018-108 | 03 CENTRAL | 523853 | FINNEY 7 | 345 | 9.8362 | 9.8362 | 0
GEN-2018-108 | 03 CENTRAL | 523961 | POTTER_CO 7 | 345 | 11.6631 | 11.6631 | 0
GEN-2018-108 | 03 CENTRAL | 530558 | KNOLL N 6 | 230 | 10.6179 | 10.6179 | 0
GEN-2018-108 | 03 CENTRAL | 530582 | S HAYS6 | 230 | 8.805 | 8.805 | 0
GEN-2018-108 | 03 CENTRAL | 530702 | BUCKEYE_230 | 230 | 7.8435 | 7.8435 | 0
GEN-2018-108 | 03 CENTRAL | 530720 | KNOLL S 6 | 230 | 10.6179 | 10.6179 | 0
GEN-2018-108 | 03 CENTRAL | 531448 | HOLCOMB3 | 115 | 21.2532 | 21.2532 | 0
GEN-2018-108 | 03 CENTRAL | 531465 | SETAB 7 | 345 | 6.866 | 6.866 | 0
GEN-2018-108 | 03 CENTRAL | 532769 | LANG 7 | 345 | 15.9573 | 15.9573 | 0
GEN-2018-108 | 03 CENTRAL | 532770 | MORRIS 7 | 345 | 12.3047 | 12.3047 | 0
GEN-2018-108 | 03 CENTRAL | 532773 | SUMMIT 7 | 345 | 10.8577 | 10.8577 | 0
GEN-2018-108 | 03 CENTRAL | 532774 | SWISVAL7 | 345 | 17.4752 | 17.4752 | 0
GEN-2018-108 | 03 CENTRAL | 532776 | READWF 7 | 345 | 13.4721 | 13.4721 | 0
GEN-2018-108 | 03 CENTRAL | 532792 | FR2EAST7 | 345 | 6.7853 | 6.7853 | 0
GEN-2018-108 | 03 CENTRAL | 532799 | WAVERLY7 | 345 | 17.6458 | 17.6458 | 0
GEN-2018-108 | 03 CENTRAL | 532800 | LATHAMS7 | 345 | 10.1116 | 10.1116 | 0
GEN-2018-108 | 03 CENTRAL | 532984 | SUMNER 4 | 138 | 12.1641 | 12.1641 | 0
GEN-2018-108 | 03 CENTRAL | 532988 | BELAIRE4 | 138 | 18.7122 | 18.7122 | 0
GEN-2018-108 | 03 CENTRAL | 532990 | MIDIAN 4 | 138 | 10.9264 | 10.9264 | 0
GEN-2018-108 | 03 CENTRAL | 533015 | BENTLEY4 | 138 | 10.662 | 10.662 | 0
GEN-2018-108 | 03 CENTRAL | 533024 | 29TH 4 | 138 | 19.3465 | 19.3465 | 0
GEN-2018-108 | 03 CENTRAL | 533035 | CHISHLM4 | 138 | 21.2473 | 21.2473 | 0
GEN-2018-108 | 03 CENTRAL | 533036 | CLEARWT4 | 138 | 14.0798 | 14.0798 | 0
GEN-2018-108 | 03 CENTRAL | 533047 | GILL 4 | 138 | 21.798 | 21.798 | 0
GEN-2018-108 | 03 CENTRAL | 533052 | PARKCTY4 | 138 | 20.0506 | 20.0506 | 0
GEN-2018-108 | 03 CENTRAL | 533053 | LAKERDG4 | 138 | 17.1004 | 17.1004 | 0
GEN-2018-108 | 03 CENTRAL | 533062 | ROSEHIL4 | 138 | 30.9062 | 30.9062 | 0
GEN-2018-108 | 03 CENTRAL | 533074 | 45TH ST4 | 138 | 23.6427 | 23.6427 | 0
GEN-2018-108 | 03 CENTRAL | 533413 | CIRCLE 3 | 115 | 18.3479 | 18.3479 | 0
GEN-2018-108 | 03 CENTRAL | 533415 | DAVIS 3 | 115 | 8.0324 | 8.0324 | 0
GEN-2018-108 | 03 CENTRAL | 533429 | MOUNDRG3 | 115 | 8.416 | 8.416 | 0
GEN-2018-108 | 03 CENTRAL | 533438 | WMCPHER3 | 115 | 10.8946 | 10.8946 | 0
GEN-2018-108 | 03 CENTRAL | 533653 | WOLFCRK2 | 69 | 5.9769 | 5.9769 | 0
GEN-2018-108 | 03 CENTRAL | 539002 | BLF-CRK4 | 138 | 4.6886 | 4.6886 | 0
GEN-2018-108 | 03 CENTRAL | 539008 | MILAN_GOAB | 138 | 11.6885 | 11.6885 | 0
GEN-2018-108 | 03 CENTRAL | 539009 | CONWAY | 138 | 11.216 | 11.216 | 0
GEN-2018-108 | 03 CENTRAL | 539649 | SAWYER 3 | 115 | 4.5902 | 4.5902 | 0
GEN-2018-108 | 03 CENTRAL | 539671 | FTDODGE3 | 115 | 9.6942 | 9.6942 | 0
GEN-2018-108 | 03 CENTRAL | 539673 | MED-LDG3 | 115 | 7.9553 | 7.9553 | 0
GEN-2018-108 | 03 CENTRAL | 539679 | GRTBEND6 | 230 | 8.7899 | 8.7899 | 0
GEN-2018-108 | 03 CENTRAL | 539688 | S-DODGE3 | 115 | 6.7777 | 6.7777 | 0
GEN-2018-108 | 03 CENTRAL | 539758 | FORD 3 | 115 | 5.204 | 5.204 | 0
GEN-2018-108 | 03 CENTRAL | 542965 | W.GRDNR7 | 345 | 31.7637 | 31.7637 | 0
GEN-2018-108 | 03 CENTRAL | 560022 | CRAWFISH_DR | 345 | 13.842 | 13.842 | 0
GEN-2018-108 | 03 CENTRAL | 560035 | GRAPEVINE | 345 | 6.4589 | 6.4589 | 0
GEN-2018-108 | 03 CENTRAL | 560053 | G15-052T | 345 | 13.3131 | 13.3131 | 0
GEN-2018-108 | 03 CENTRAL | 560078 | G16-037-TAP | 345 | 10.1427 | 10.1427 | 0
GEN-2018-108 | 03 CENTRAL | 576397 | G10014G11022 | 345 | 10.3812 | 10.3812 | 0
GEN-2018-108 | 03 CENTRAL | 585190 | GEN-2015-082 | 345 | 7.0512 | 7.0512 | 0
GEN-2018-108 | 03 CENTRAL | 585420 | COWBOY_RIDGE | 345 | 7.5551 | 7.5551 | 0
GEN-2018-108 | 03 CENTRAL | 585440 | PRSIMN_CRK2 | 345 | 10.7138 | 10.7138 | 0
GEN-2018-108 | 03 CENTRAL | 587350 | GEN-2016-050 | 345 | 5.8546 | 5.8546 | 0
GEN-2018-108 | 03 CENTRAL | 587880 | GEN-2016-111 | 345 | 6.4948 | 6.4948 | 0
GEN-2018-108 | 03 CENTRAL | 588360 | GEN-2016-153 | 345 | 7.1567 | 7.1567 | 0
GEN-2018-108 | 03 CENTRAL | 589240 | GEN-2017-086 | 345 | 6.2694 | 6.2694 | 0
GEN-2018-108 | 03 CENTRAL | 640065 | AXTELL 3 | 345 | 9.208 | 9.208 | 0
GEN-2018-108 | 03 CENTRAL | 763417 | GEN-2018-128 | 345 | 11.1457 | 11.1457 | 0
GEN-2018-108 | 03 CENTRAL | 763758 | GEN-2019-044 | 115 | 6.4739 | 6.4739 | 0
GEN-2018-108 | 03 CENTRAL | 763846 | G19-053/055 | 230 | 7.1612 | 7.1612 | 0
GEN-2018-108 | 03 CENTRAL | 900001 | TRAVERSE3 | 345 | 6.9271 | 6.9271 | 0
GEN-2018-116 | 03 CENTRAL | 539661 | 24-FREY3 | 115 | 8.1561 | 7.3743 | 0.7818
GEN-2018-116 | 03 CENTRAL | 539681 | N-GBEND3 | 115 | 9.1049 | 8.5007 | 0.6042
GEN-2018-116 | 03 CENTRAL | 539689 | 2ND-KS 3 | 115 | 7.9906 | 7.3239 | 0.6667
GEN-2018-116 | 03 CENTRAL | 763329 | GEN-2018-116 | 115 | 8.1395 | 7.3574 | 0.7821
GEN-2018-116 | 03 CENTRAL | 539666 | GBENDTP3 | 115 | 8.7185 | 8.1726 | 0.5459
GEN-2018-116 | 03 CENTRAL | 539678 | GRTBEND3 | 115 | 12.2449 | 11.5614 | 0.6835
GEN-2018-116 | 03 CENTRAL | 530601 | HEIZER 3 | 115 | 12.1453 | 11.5035 | 0.6418
GEN-2018-116 | 03 CENTRAL | 539642 | ELLSWTP3 | 115 | 3.9126 | 3.8858 | 0.0268
GEN-2018-116 | 03 CENTRAL | 539679 | GRTBEND6 | 230 | 8.7899 | 8.5441 | 0.2458
GEN-2018-116 | 03 CENTRAL | 539684 | OTISSUB3 | 115 | 2.9219 | 2.8811 | 0.0408
GEN-2018-116 | 03 CENTRAL | 539692 | SEWARD 3 | 115 | 5.8179 | 5.67 | 0.1479
GEN-2018-116 | 03 CENTRAL | 530563 | HEIZER 2 | 69 | 8.7188 | 8.5253 | 0.1935
GEN-2018-116 | 03 CENTRAL | 530582 | S HAYS6 | 230 | 8.805 | 8.728 | 0.077
GEN-2018-116 | 03 CENTRAL | 530602 | LAXTAP 3 | 115 | 4.087 | 4.0422 | 0.0448
GEN-2018-116 | 03 CENTRAL | 530609 | HZRNGPL3 | 115 | 7.7647 | 7.4971 | 0.2676
GEN-2018-116 | 03 CENTRAL | 530679 | SEWRDMW3 | 115 | 5.1213 | 5.007 | 0.1143
GEN-2018-116 | 03 CENTRAL | 530680 | HEIZER 6 | 230 | 8.7324 | 8.4883 | 0.2441
GEN-2018-116 | 03 CENTRAL | 539643 | ROLLHLS3 | 115 | 3.5855 | 3.5654 | 0.0201
GEN-2018-116 | 03 CENTRAL | 539696 | ST-JOHN3 | 115 | 5.2881 | 5.2366 | 0.0515
GEN-2018-116 | 03 CENTRAL | 539701 | RUSSELL3 | 115 | 3.4282 | 3.4096 | 0.0186
GEN-2018-116 | 03 CENTRAL | 763850 | G19-055-TAP | 230 | 7.2471 | 7.2003 | 0.0468
GEN-2018-116 | 03 CENTRAL | 763862 | G19-054-TAP | 230 | 6.9761 | 6.8617 | 0.1144
GEN-2018-116 | 03 CENTRAL | 530553 | S HAYS 3 | 115 | 8.4163 | 8.3901 | 0.0262
GEN-2018-116 | 03 CENTRAL | 530565 | SEWARD 2 | 69 | 5.3611 | 5.289 | 0.0721
GEN-2018-116 | 03 CENTRAL | 530568 | GB NTH 2 | 69 | 6.7283 | 6.6123 | 0.116
GEN-2018-116 | 03 CENTRAL | 530584 | POSTROCK6 | 230 | 10.7096 | 10.6503 | 0.0593
GEN-2018-116 | 03 CENTRAL | 530586 | ALBERT 2 | 69 | 3.6217 | 3.5929 | 0.0288
GEN-2018-116 | 03 CENTRAL | 530587 | WSPRTTP2 | 69 | 5.93 | 5.8397 | 0.0903
GEN-2018-116 | 03 CENTRAL | 530603 | LACROS 3 | 115 | 3.54 | 3.5064 | 0.0336
GEN-2018-116 | 03 CENTRAL | 530608 | NEKOMA 3 | 115 | 3.9676 | 3.9321 | 0.0355
GEN-2018-116 | 03 CENTRAL | 530610 | SHAYS_230 | 230 | 3.4161 | 3.4069 | 0.0092
GEN-2018-116 | 03 CENTRAL | 530624 | ST JOHN3 | 115 | 5.2881 | 5.2366 | 0.0515
GEN-2018-116 | 03 CENTRAL | 532871 | CIRCLE 6 | 230 | 8.4637 | 8.4296 | 0.0341
GEN-2018-116 | 03 CENTRAL | 539010 | SADLHRN3 | 115 | 4.5492 | 4.5212 | 0.028
GEN-2018-116 | 03 CENTRAL | 539660 | EHALLTP3 | 115 | 3.2328 | 3.2225 | 0.0103
GEN-2018-116 | 03 CENTRAL | 539695 | SPEARVL6 | 230 | 12.772 | 12.736 | 0.036
GEN-2018-116 | 03 CENTRAL | 539698 | WALDO 3 | 115 | 2.7316 | 2.7231 | 0.0085
GEN-2018-116 | 03 CENTRAL | 763846 | G19-053/055 | 230 | 7.1612 | 7.1156 | 0.0456
GEN-2018-116 | 03 CENTRAL | 763857 | G19-054/068 | 230 | 6.8962 | 6.7847 | 0.1115
GEN-2018-121 | 03 CENTRAL | 541231 | NRAYMORETP 5 | 161 | 6.158 | 6.158 | 0
GEN-2018-121 | 03 CENTRAL | 541245 | KCSOUTH5 | 161 | 13.7401 | 13.7401 | 0
GEN-2018-121 | 03 CENTRAL | 541317 | NRAYMORE | 161 | 9.0788 | 9.0788 | 0
GEN-2018-121 | 03 CENTRAL | 760116 | GEN-2018-054 | 161 | 6.094 | 6.094 | 0
GEN-2018-121 | 03 CENTRAL | 541224 | LNGVW 5 | 161 | 22.3206 | 22.3206 | 0
GEN-2018-121 | 03 CENTRAL | 542998 | LVISTA 5 | 161 | 23.5912 | 23.5912 | 0
GEN-2018-121 | 03 CENTRAL | 541220 | FROSTRD5 | 161 | 13.2386 | 13.2386 | 0
GEN-2018-121 | 03 CENTRAL | 541222 | WSTELEC5 | 161 | 16.4613 | 16.4613 | 0
GEN-2018-121 | 03 CENTRAL | 541223 | GRDVWE 5 | 161 | 20.0882 | 20.0882 | 0
GEN-2018-121 | 03 CENTRAL | 541249 | HOOKRD 5 | 161 | 22.2127 | 22.2127 | 0
GEN-2018-121 | 03 CENTRAL | 541282 | LNGVW 2 | 69 | 10.181 | 10.181 | 0
GEN-2018-121 | 03 CENTRAL | 543008 | BUNKRDG5 | 161 | 23.6152 | 23.6152 | 0
GEN-2018-121 | 03 CENTRAL | 543009 | WINJT N5 | 161 | 23.1601 | 23.1601 | 0
GEN-2018-121 | 03 CENTRAL | 541139 | FROSTRD_CAP5 | 161 | 12.2529 | 12.2529 | 0
GEN-2018-121 | 03 CENTRAL | 541149 | WSTELEC_CAP5 | 161 | 14.9642 | 14.9642 | 0
GEN-2018-121 | 03 CENTRAL | 541210 | MARTCTY5 | 161 | 28.8519 | 28.8519 | 0
GEN-2018-121 | 03 CENTRAL | 541219 | RAYTOWN5 | 161 | 12.7552 | 12.7552 | 0
GEN-2018-121 | 03 CENTRAL | 541243 | LKWINBG5 | 161 | 24.2373 | 24.2373 | 0
GEN-2018-121 | 03 CENTRAL | 541246 | STROTHR5 | 161 | 14.1721 | 14.1721 | 0
GEN-2018-121 | 03 CENTRAL | 541283 | BRMALL 2 | 69 | 14.7445 | 14.7445 | 0
GEN-2018-121 | 03 CENTRAL | 541284 | GRDVWTP2 | 69 | 9.0532 | 9.0532 | 0
GEN-2018-121 | 03 CENTRAL | 542993 | STHTOWN5 | 161 | 36.2598 | 36.2598 | 0
GEN-2018-121 | 03 CENTRAL | 542997 | LEEDS 5 | 161 | 34.0994 | 34.0994 | 0
GEN-2018-121 | 03 CENTRAL | 543006 | SWOPE N5 | 161 | 21.2278 | 21.2278 | 0
GEN-2018-121 | 03 CENTRAL | 541206 | PRALEE 5 | 161 | 20.1233 | 20.1233 | 0
GEN-2018-121 | 03 CENTRAL | 541225 | PHILL 5 | 161 | 32.5433 | 32.5433 | 0
GEN-2018-121 | 03 CENTRAL | 541238 | LKWOOD 5 | 161 | 13.0117 | 13.0117 | 0
GEN-2018-121 | 03 CENTRAL | 541285 | GRDWCTY2 | 69 | 8.6759 | 8.6759 | 0
GEN-2018-121 | 03 CENTRAL | 541287 | MARTCTY2 | 69 | 7.0186 | 7.0186 | 0
GEN-2018-121 | 03 CENTRAL | 541322 | RGAFBTP2 | 69 | 8.733 | 8.733 | 0
GEN-2018-121 | 03 CENTRAL | 541382 | HONEYWL5 | 161 | 22.7694 | 22.7694 | 0
GEN-2018-121 | 03 CENTRAL | 542950 | STHTOWN_CAP5 | 161 | 29.7118 | 29.7117 | 0.0001
GEN-2018-121 | 03 CENTRAL | 542973 | HAWTHS5 | 161 | 55.8133 | 55.8133 | 0
GEN-2018-121 | 03 CENTRAL | 542992 | BENDIX 5 | 161 | 29.3048 | 29.3048 | 0
GEN-2018-121 | 03 CENTRAL | 542994 | HICKMAN5 | 161 | 19.2564 | 19.2564 | 0
GEN-2018-121 | 03 CENTRAL | 542996 | MIDTOWN5 | 161 | 34.4111 | 34.4111 | 0
GEN-2018-121 | 03 CENTRAL | 543001 | FOREST 5 | 161 | 30.8393 | 30.8393 | 0
GEN-2018-121 | 03 CENTRAL | 543002 | MARTCIT5 | 161 | 26.7804 | 26.7804 | 0
GEN-2018-121 | 03 CENTRAL | 543010 | WINJT S5 | 161 | 22.7863 | 22.7863 | 0
GEN-2018-121 | 03 CENTRAL | 548821 | SUB N | 69 | 17.1713 | 17.1713 | 0
GEN-2018-128 | 03 CENTRAL | 763417 | GEN-2018-128 | 345 | 11.1457 | 10.8073 | 0.3384
GEN-2018-128 | 03 CENTRAL | 763421 | G18-128-TAP | 345 | 12.3337 | 11.9963 | 0.3374
GEN-2018-128 | 03 CENTRAL | 515543 | RENFROW7 | 345 | 12.8614 | 12.6294 | 0.232
GEN-2018-128 | 03 CENTRAL | 532798 | VIOLA 7 | 345 | 14.0837 | 13.9091 | 0.1746
GEN-2018-128 | 03 CENTRAL | 515476 | HUNTERS7 | 345 | 13.1988 | 13.0881 | 0.1107
GEN-2018-128 | 03 CENTRAL | 515544 | RENFROW4 | 138 | 14.5957 | 14.5237 | 0.072
GEN-2018-128 | 03 CENTRAL | 515646 | GRNTWD 7 | 345 | 11.2623 | 11.0864 | 0.1759
GEN-2018-128 | 03 CENTRAL | 532796 | WICHITA7 | 345 | 23.7708 | 23.7029 | 0.0679
GEN-2018-128 | 03 CENTRAL | 533075 | VIOLA 4 | 138 | 24.178 | 24.0444 | 0.1336
GEN-2018-128 | 03 CENTRAL | 588364 | G16-153-TAP | 345 | 7.5063 | 7.4667 | 0.0396
GEN-2018-128 | 03 CENTRAL | 760809 | GEN-2017-203 | 345 | 9.1645 | 9.0497 | 0.1148
GEN-2018-128 | 03 CENTRAL | 514715 | WOODRNG7 | 345 | 18.7369 | 18.6713 | 0.0656
GEN-2018-128 | 03 CENTRAL | 515477 | CHSHLMV7 | 345 | 13.1796 | 13.0692 | 0.1104
GEN-2018-128 | 03 CENTRAL | 515546 | GRANTCO4 | 138 | 6.4868 | 6.4743 | 0.0125
GEN-2018-128 | 03 CENTRAL | 515569 | MDFRDTP4 | 138 | 11.6733 | 11.6331 | 0.0402
GEN-2018-128 | 03 CENTRAL | 520409 | WFEC_RNFRO4 | 138 | 10.6919 | 10.6571 | 0.0348
GEN-2018-128 | 03 CENTRAL | 532771 | RENO 7 | 345 | 11.0976 | 11.0912 | 0.0064
GEN-2018-128 | 03 CENTRAL | 532782 | BUFFALO7 | 345 | 20.7555 | 20.7122 | 0.0433
GEN-2018-128 | 03 CENTRAL | 532791 | BENTON 7 | 345 | 19.0077 | 18.9821 | 0.0256
GEN-2018-128 | 03 CENTRAL | 532792 | FR2EAST7 | 345 | 6.7853 | 6.7542 | 0.0311
GEN-2018-128 | 03 CENTRAL | 532984 | SUMNER 4 | 138 | 12.1641 | 12.1558 | 0.0083
GEN-2018-128 | 03 CENTRAL | 533036 | CLEARWT4 | 138 | 14.0798 | 14.0563 | 0.0235
GEN-2018-128 | 03 CENTRAL | 533040 | EVANS N4 | 138 | 32.3573 | 32.3117 | 0.0456
GEN-2018-128 | 03 CENTRAL | 533047 | GILL 4 | 138 | 21.798 | 21.7591 | 0.0389
GEN-2018-128 | 03 CENTRAL | 539008 | MILAN_GOAB | 138 | 11.6885 | 11.6588 | 0.0297
GEN-2018-128 | 03 CENTRAL | 539009 | CONWAY | 138 | 11.216 | 11.1908 | 0.0252
GEN-2018-128 | 03 CENTRAL | 562476 | G14-001-TAP | 345 | 10.3737 | 10.3675 | 0.0062
GEN-2018-128 | 03 CENTRAL | 588360 | GEN-2016-153 | 345 | 7.1567 | 7.1208 | 0.0359
GEN-2018-128 | 03 CENTRAL | 589240 | GEN-2017-086 | 345 | 6.2694 | 6.2421 | 0.0273
GEN-2018-128 | 03 CENTRAL | 514714 | WOODRNG4 | 138 | 19.2315 | 19.2199 | 0.0116
GEN-2018-128 | 03 CENTRAL | 515426 | RDRUNNR4 | 138 | 8.7458 | 8.7346 | 0.0112
GEN-2018-128 | 03 CENTRAL | 515547 | GRANTCO2 | 69 | 7.47 | 7.4637 | 0.0063
GEN-2018-128 | 03 CENTRAL | 515875 | REDNGTN7 | 345 | 16.7149 | 16.6918 | 0.0231
GEN-2018-128 | 03 CENTRAL | 515990 | SKELTON7 | 345 | 4.5043 | 4.5009 | 0.0034
GEN-2018-128 | 03 CENTRAL | 516010 | PINTAIL7 | 345 | 16.6869 | 16.6629 | 0.024
GEN-2018-128 | 03 CENTRAL | 520434 | WAKTASW4 | 138 | 6.2858 | 6.2789 | 0.0069
GEN-2018-128 | 03 CENTRAL | 522397 | MEDFORD4 | 138 | 7.5711 | 7.5541 | 0.017
GEN-2018-128 | 03 CENTRAL | 532768 | EMPEC 7 | 345 | 16.1367 | 16.1345 | 0.0022
GEN-2018-128 | 03 CENTRAL | 532783 | KINGMAN7 | 345 | 7.0277 | 7.0241 | 0.0036
GEN-2018-128 | 03 CENTRAL | 532794 | ROSEHIL7 | 345 | 18.8487 | 18.8309 | 0.0178
GEN-2018-128 | 03 CENTRAL | 532795 | FR2WEST7 | 345 | 5.4247 | 5.4059 | 0.0188
GEN-2018-128 | 03 CENTRAL | 532797 | WOLFCRK7 | 345 | 20.9355 | 20.9326 | 0.0029
GEN-2018-128 | 03 CENTRAL | 532982 | OXFORD 4 | 138 | 10.7611 | 10.7549 | 0.0062
GEN-2018-128 | 03 CENTRAL | 532986 | BENTON 4 | 138 | 27.7644 | 27.7398 | 0.0246
GEN-2018-128 | 03 CENTRAL | 532992 | TIMBJCT4 | 138 | 6.4586 | 6.4565 | 0.0021
GEN-2018-128 | 03 CENTRAL | 533041 | EVANS S4 | 138 | 32.2762 | 32.2307 | 0.0455
GEN-2018-128 | 03 CENTRAL | 533045 | GILL W 4 | 138 | 21.8043 | 21.7655 | 0.0388
GEN-2018-128 | 03 CENTRAL | 533046 | GILL S 4 | 138 | 21.8015 | 21.7627 | 0.0388
GEN-2018-128 | 03 CENTRAL | 533054 | MAIZE 4 | 138 | 20.7931 | 20.775 | 0.0181
GEN-2018-128 | 03 CENTRAL | 533063 | SC10BEL4 | 138 | 11.9885 | 11.9806 | 0.0079
GEN-2018-128 | 03 CENTRAL | 533065 | SG12COL4 | 138 | 19.3466 | 19.3309 | 0.0157
GEN-2018-128 | 03 CENTRAL | 533416 | RENO 3 | 115 | 22.1556 | 22.149 | 0.0066
GEN-2018-128 | 03 CENTRAL | 539003 | CLDWELL4 | 138 | 5.565 | 5.5593 | 0.0057
GEN-2018-128 | 03 CENTRAL | 539675 | MILANTP4 | 138 | 9.9006 | 9.8819 | 0.0187
GEN-2018-128 | 03 CENTRAL | 539676 | MILAN 4 | 138 | 10.3753 | 10.3519 | 0.0234
GEN-2018-128 | 03 CENTRAL | 539801 | THISTLE7 | 345 | 16.6662 | 16.6543 | 0.0119
GEN-2018-128 | 03 CENTRAL | 583850 | GEN-2014-001 | 345 | 6.9804 | 6.9777 | 0.0027
GEN-2018-128 | 03 CENTRAL | 587500 | GEN-2016-073 | 345 | 15.2224 | 15.1995 | 0.0229
GEN-2018-128 | 03 CENTRAL | 587884 | G16-111-TAP | 345 | 9.7651 | 9.7618 | 0.0033
GEN-2018-128 | 03 CENTRAL | 589060 | GEN-2017-068 | 138 | 29.2988 | 29.2614 | 0.0374
GEN-2018-128 | 03 CENTRAL | 760284 | GEN-2017-220 | 345 | 20.642 | 20.5992 | 0.0428
GEN-2018-128 | 03 CENTRAL | 760620 | GEN-2017-179 | 138 | 7.0944 | 7.0927 | 0.0017
GEN-2018-128 | 03 CENTRAL | 760641 | GEN-2017-226 | 138 | 32.1766 | 32.1315 | 0.0451
GEN-2018-128 | 03 CENTRAL | 761838 | GEN-2017-121 | 138 | 9.138 | 9.1335 | 0.0045
GEN-2018-128 | 03 CENTRAL | 762321 | GEN-2017-164 | 345 | 11.1781 | 11.1556 | 0.0225
GEN-2018-128 | 03 CENTRAL | 762922 | GEN-2018-057 | 138 | 17.2503 | 17.238 | 0.0123
GEN-2019-001 | 03 CENTRAL | 532782 | BUFFALO7 | 345 | 20.7555 | 20.7294 | 0.0261
GEN-2019-001 | 03 CENTRAL | 532783 | KINGMAN7 | 345 | 7.0277 | 6.9921 | 0.0356
GEN-2019-001 | 03 CENTRAL | 532796 | WICHITA7 | 345 | 23.7708 | 23.7498 | 0.021
GEN-2019-001 | 03 CENTRAL | 539801 | THISTLE7 | 345 | 16.6662 | 16.6616 | 0.0046
GEN-2019-001 | 03 CENTRAL | 587500 | GEN-2016-073 | 345 | 15.2224 | 15.2086 | 0.0138
GEN-2019-001 | 03 CENTRAL | 760284 | GEN-2017-220 | 345 | 20.642 | 20.6163 | 0.0257
GEN-2019-001 | 03 CENTRAL | 515852 | DGRASSE7 | 345 | 15.3179 | 15.3165 | 0.0014
GEN-2019-001 | 03 CENTRAL | 532771 | RENO 7 | 345 | 11.0976 | 11.0957 | 0.0019
GEN-2019-001 | 03 CENTRAL | 532784 | NINN1WF7 | 345 | 5.8368 | 5.7988 | 0.038
GEN-2019-001 | 03 CENTRAL | 532791 | BENTON 7 | 345 | 19.0077 | 19.0018 | 0.0059
GEN-2019-001 | 03 CENTRAL | 532798 | VIOLA 7 | 345 | 14.0837 | 14.0809 | 0.0028
GEN-2019-001 | 03 CENTRAL | 533040 | EVANS N4 | 138 | 32.3573 | 32.3481 | 0.0092
GEN-2019-001 | 03 CENTRAL | 539800 | CLARKCOUNTY7 | 345 | 12.7785 | 12.7777 | 0.0008
GEN-2019-001 | 03 CENTRAL | 539804 | THISTLE4 | 138 | 17.5567 | 17.5549 | 0.0018
GEN-2019-001 | 03 CENTRAL | 562476 | G14-001-TAP | 345 | 10.3737 | 10.3718 | 0.0019
GEN-2019-001 | 03 CENTRAL | 588630 | GEN-2017-018 | 345 | 16.6662 | 16.6616 | 0.0046
GEN-2019-001 | 03 CENTRAL | 762834 | GEN-2018-049 | 345 | 6.9567 | 6.9559 | 0.0008
GEN-2019-001 | 03 CENTRAL | 515375 | WWRDEHV7 | 345 | 22.3641 | 22.3635 | 0.0006
GEN-2019-001 | 03 CENTRAL | 515853 | DGRASSE4 | 138 | 17.0745 | 17.0741 | 0.0004
GEN-2019-001 | 03 CENTRAL | 531469 | SPERVIL7 | 345 | 13.6098 | 13.6093 | 0.0005
GEN-2019-001 | 03 CENTRAL | 532768 | EMPEC 7 | 345 | 16.1367 | 16.136 | 0.0007
GEN-2019-001 | 03 CENTRAL | 532785 | PRATTWF7 | 345 | 4.8525 | 4.8129 | 0.0396
GEN-2019-001 | 03 CENTRAL | 532794 | ROSEHIL7 | 345 | 18.8487 | 18.8454 | 0.0033
GEN-2019-001 | 03 CENTRAL | 532797 | WOLFCRK7 | 345 | 20.9355 | 20.9349 | 0.0006
GEN-2019-001 | 03 CENTRAL | 532986 | BENTON 4 | 138 | 27.7644 | 27.7597 | 0.0047
GEN-2019-001 | 03 CENTRAL | 533041 | EVANS S4 | 138 | 32.2762 | 32.267 | 0.0092
GEN-2019-001 | 03 CENTRAL | 533054 | MAIZE 4 | 138 | 20.7931 | 20.7896 | 0.0035
GEN-2019-001 | 03 CENTRAL | 533065 | SG12COL4 | 138 | 19.3466 | 19.3434 | 0.0032
GEN-2019-001 | 03 CENTRAL | 533075 | VIOLA 4 | 138 | 24.178 | 24.1748 | 0.0032
GEN-2019-001 | 03 CENTRAL | 533416 | RENO 3 | 115 | 22.1556 | 22.1537 | 0.0019
GEN-2019-001 | 03 CENTRAL | 539638 | FLATRDG4 | 138 | 15.5636 | 15.5623 | 0.0013
GEN-2019-001 | 03 CENTRAL | 539813 | TRANSFORMER | 345 | 10.6791 | 10.6786 | 0.0005
GEN-2019-001 | 03 CENTRAL | 539840 | GEN-2011-008 | 345 | 10.5555 | 10.555 | 0.0005
GEN-2019-001 | 03 CENTRAL | 560080 | G16-046-TAP | 345 | 11.3684 | 11.3679 | 0.0005
GEN-2019-001 | 03 CENTRAL | 583850 | GEN-2014-001 | 345 | 6.9804 | 6.9796 | 0.0008
GEN-2019-001 | 03 CENTRAL | 587884 | G16-111-TAP | 345 | 9.7651 | 9.7641 | 0.001
GEN-2019-001 | 03 CENTRAL | 588364 | G16-153-TAP | 345 | 7.5063 | 7.5057 | 0.0006
GEN-2019-001 | 03 CENTRAL | 589060 | GEN-2017-068 | 138 | 29.2988 | 29.2912 | 0.0076
GEN-2019-001 | 03 CENTRAL | 760620 | GEN-2017-179 | 138 | 7.0944 | 7.0941 | 0.0003
GEN-2019-001 | 03 CENTRAL | 760641 | GEN-2017-226 | 138 | 32.1766 | 32.1675 | 0.0091
GEN-2019-001 | 03 CENTRAL | 762922 | GEN-2018-057 | 138 | 17.2503 | 17.2478 | 0.0025
GEN-2019-001 | 03 CENTRAL | 763421 | G18-128-TAP | 345 | 12.3337 | 12.3325 | 0.0012
GEN-2019-001 | 03 CENTRAL | 763890 | GEN-2019-058 | 345 | 12.52 | 12.5193 | 0.0007
GEN-2019-001 | 03 CENTRAL | 300739 | 7BLACKBERRY | 345 | 15.3686 | 15.3685 | 0.0001
GEN-2019-001 | 03 CENTRAL | 514795 | KNOBHIL4 | 138 | 10.2855 | 10.2854 | 0.0001
GEN-2019-001 | 03 CENTRAL | 515376 | WWRDEHV4 | 138 | 24.8769 | 24.8766 | 0.0003
GEN-2019-001 | 03 CENTRAL | 515407 | TATONGA7 | 345 | 17.5658 | 17.5656 | 0.0002
GEN-2019-001 | 03 CENTRAL | 515543 | RENFROW7 | 345 | 12.8614 | 12.8606 | 0.0008
GEN-2019-001 | 03 CENTRAL | 515554 | BVRCNTY7 | 345 | 15.3093 | 15.3092 | 0.0001
GEN-2019-001 | 03 CENTRAL | 515599 | G07621119-20 | 345 | 13.4849 | 13.4847 | 0.0002
GEN-2019-001 | 03 CENTRAL | 515961 | GUTHRIE7 | 345 | 12.8816 | 12.8814 | 0.0002
GEN-2019-001 | 03 CENTRAL | 516106 | BOBCAT 7 | 345 | 15.796 | 15.7958 | 0.0002
GEN-2019-001 | 03 CENTRAL | 520436 | ROSEVLY4 | 138 | 12.3574 | 12.3572 | 0.0002
GEN-2019-001 | 03 CENTRAL | 520999 | MOORLND4 | 138 | 20.0616 | 20.0616 | 0
GEN-2019-001 | 03 CENTRAL | 530583 | POSTROCK7 | 345 | 7.7231 | 7.723 | 0.0001
GEN-2019-001 | 03 CENTRAL | 531501 | BUCKNER7 | 345 | 9.2456 | 9.2455 | 0.0001
GEN-2019-001 | 03 CENTRAL | 532769 | LANG 7 | 345 | 15.9573 | 15.9567 | 0.0006
GEN-2019-001 | 03 CENTRAL | 532770 | MORRIS 7 | 345 | 12.3047 | 12.3044 | 0.0003
GEN-2019-001 | 03 CENTRAL | 532773 | SUMMIT 7 | 345 | 10.8577 | 10.8572 | 0.0005
GEN-2019-001 | 03 CENTRAL | 532774 | SWISVAL7 | 345 | 17.4752 | 17.475 | 0.0002
GEN-2019-001 | 03 CENTRAL | 532776 | READWF 7 | 345 | 13.4721 | 13.4717 | 0.0004
GEN-2019-001 | 03 CENTRAL | 532792 | FR2EAST7 | 345 | 6.7853 | 6.7848 | 0.0005
GEN-2019-001 | 03 CENTRAL | 532799 | WAVERLY7 | 345 | 17.6458 | 17.6454 | 0.0004
GEN-2019-001 | 03 CENTRAL | 532800 | LATHAMS7 | 345 | 10.1116 | 10.111 | 0.0006
GEN-2019-001 | 03 CENTRAL | 532984 | SUMNER 4 | 138 | 12.1641 | 12.1637 | 0.0004
GEN-2019-001 | 03 CENTRAL | 532988 | BELAIRE4 | 138 | 18.7122 | 18.7101 | 0.0021
GEN-2019-001 | 03 CENTRAL | 532990 | MIDIAN 4 | 138 | 10.9264 | 10.9259 | 0.0005
GEN-2019-001 | 03 CENTRAL | 533015 | BENTLEY4 | 138 | 10.662 | 10.6611 | 0.0009
GEN-2019-001 | 03 CENTRAL | 533024 | 29TH 4 | 138 | 19.3465 | 19.3443 | 0.0022
GEN-2019-001 | 03 CENTRAL | 533035 | CHISHLM4 | 138 | 21.2473 | 21.2443 | 0.003
GEN-2019-001 | 03 CENTRAL | 533036 | CLEARWT4 | 138 | 14.0798 | 14.0786 | 0.0012
GEN-2019-001 | 03 CENTRAL | 533047 | GILL 4 | 138 | 21.798 | 21.7951 | 0.0029
GEN-2019-001 | 03 CENTRAL | 533052 | PARKCTY4 | 138 | 20.0506 | 20.048 | 0.0026
GEN-2019-001 | 03 CENTRAL | 533053 | LAKERDG4 | 138 | 17.1004 | 17.0982 | 0.0022
GEN-2019-001 | 03 CENTRAL | 533062 | ROSEHIL4 | 138 | 30.9062 | 30.9022 | 0.004
GEN-2019-001 | 03 CENTRAL | 533074 | 45TH ST4 | 138 | 23.6427 | 23.6379 | 0.0048
GEN-2019-001 | 03 CENTRAL | 533413 | CIRCLE 3 | 115 | 18.3479 | 18.3468 | 0.0011
GEN-2019-001 | 03 CENTRAL | 533415 | DAVIS 3 | 115 | 8.0324 | 8.0322 | 0.0002
GEN-2019-001 | 03 CENTRAL | 533429 | MOUNDRG3 | 115 | 8.416 | 8.4157 | 0.0003
GEN-2019-001 | 03 CENTRAL | 533438 | WMCPHER3 | 115 | 10.8946 | 10.8944 | 0.0002
GEN-2019-001 | 03 CENTRAL | 533653 | WOLFCRK2 | 69 | 5.9769 | 5.9769 | 0
GEN-2019-001 | 03 CENTRAL | 539008 | MILAN_GOAB | 138 | 11.6885 | 11.6877 | 0.0008
GEN-2019-001 | 03 CENTRAL | 539009 | CONWAY | 138 | 11.216 | 11.2153 | 0.0007
GEN-2019-001 | 03 CENTRAL | 539631 | FLATRWD4 | 138 | 10.3815 | 10.3809 | 0.0006
GEN-2019-001 | 03 CENTRAL | 539668 | HARPER 4 | 138 | 7.2122 | 7.2119 | 0.0003
GEN-2019-001 | 03 CENTRAL | 539674 | BARBER 4 | 138 | 8.2322 | 8.2318 | 0.0004
GEN-2019-001 | 03 CENTRAL | 539695 | SPEARVL6 | 230 | 12.772 | 12.7717 | 0.0003
GEN-2019-001 | 03 CENTRAL | 539759 | SPRVL 3 | 115 | 12.8273 | 12.8271 | 0.0002
GEN-2019-001 | 03 CENTRAL | 539803 | IRONWOOD7 | 345 | 13.1638 | 13.1633 | 0.0005
GEN-2019-001 | 03 CENTRAL | 539841 | G-2011-008-1 | 345 | 10.5555 | 10.555 | 0.0005
GEN-2019-001 | 03 CENTRAL | 539855 | G-2011-008-2 | 345 | 8.8342 | 8.8339 | 0.0003
GEN-2019-001 | 03 CENTRAL | 539857 | G-2011-008-3 | 345 | 8.2708 | 8.2705 | 0.0003
GEN-2019-001 | 03 CENTRAL | 542965 | W.GRDNR7 | 345 | 31.7637 | 31.7635 | 0.0002
GEN-2019-001 | 03 CENTRAL | 560053 | G15-052T | 345 | 13.3131 | 13.3123 | 0.0008
GEN-2019-001 | 03 CENTRAL | 585300 | GEN-2015-095 | 138 | 16.8692 | 16.8688 | 0.0004
GEN-2019-001 | 03 CENTRAL | 587310 | GEN-2016-046 | 345 | 9.9533 | 9.953 | 0.0003
GEN-2019-001 | 03 CENTRAL | 587880 | GEN-2016-111 | 345 | 6.4948 | 6.4944 | 0.0004
GEN-2019-001 | 03 CENTRAL | 588360 | GEN-2016-153 | 345 | 7.1567 | 7.1561 | 0.0006
GEN-2019-001 | 03 CENTRAL | 589240 | GEN-2017-086 | 345 | 6.2694 | 6.269 | 0.0004
GEN-2019-001 | 03 CENTRAL | 755000 | WWDBORDT | 345 | 12.2648 | 12.2647 | 0.0001
GEN-2019-001 | 03 CENTRAL | 763417 | GEN-2018-128 | 345 | 11.1457 | 11.1448 | 0.0009
GEN-2019-001 | 03 CENTRAL | 763527 | GEN-2019-012 | 345 | 19.3711 | 19.3706 | 0.0005
GEN-2019-001 | 03 CENTRAL | 763769 | GEN-2019-045 | 138 | 17.0745 | 17.0741 | 0.0004
GEN-2019-001 | 03 CENTRAL | 300740 | 7SPORTSMAN | 345 | 23.7932 | 23.7932 | 0
GEN-2019-001 | 03 CENTRAL | 300949 | 7JASPER | 345 | 12.5964 | 12.5963 | 0.0001
GEN-2019-001 | 03 CENTRAL | 511553 | CHISHOLM7 | 345 | 12.3397 | 12.3396 | 0.0001
GEN-2019-001 | 03 CENTRAL | 514785 | WOODWRD4 | 138 | 13.1123 | 13.1122 | 0.0001
GEN-2019-001 | 03 CENTRAL | 514788 | GLASMTN4 | 138 | 5.1117 | 5.1117 | 0
GEN-2019-001 | 03 CENTRAL | 514794 | KNOBHIL2 | 69 | 8.8727 | 8.8726 | 0.0001
GEN-2019-001 | 03 CENTRAL | 514796 | IODINE-4 | 138 | 7.3201 | 7.3201 | 0
GEN-2019-001 | 03 CENTRAL | 515394 | KEENAN 4 | 138 | 8.9414 | 8.9413 | 0.0001
GEN-2019-001 | 03 CENTRAL | 515398 | OUSPRT 4 | 138 | 9.528 | 9.5279 | 0.0001
GEN-2019-001 | 03 CENTRAL | 515425 | WWDPST 4 | 138 | 17.7977 | 17.7976 | 0.0001
GEN-2019-001 | 03 CENTRAL | 515448 | CRSRDSW7 | 345 | 12.1468 | 12.1467 | 0.0001
GEN-2019-001 | 03 CENTRAL | 515458 | BORDER 7 | 345 | 8.2517 | 8.2517 | 0
GEN-2019-001 | 03 CENTRAL | 515476 | HUNTERS7 | 345 | 13.1988 | 13.1984 | 0.0004
GEN-2019-001 | 03 CENTRAL | 515497 | MATHWSN7 | 345 | 32.7952 | 32.795 | 0.0002
GEN-2019-001 | 03 CENTRAL | 515544 | RENFROW4 | 138 | 14.5957 | 14.5954 | 0.0003
GEN-2019-001 | 03 CENTRAL | 515582 | SLNGWND7 | 345 | 8.4766 | 8.4765 | 0.0001
GEN-2019-001 | 03 CENTRAL | 515585 | MAMTHPW7 | 345 | 13.5669 | 13.5668 | 0.0001
GEN-2019-001 | 03 CENTRAL | 515590 | PALDR2W7 | 345 | 12.8669 | 12.8668 | 0.0001
GEN-2019-001 | 03 CENTRAL | 515618 | BALKOW 7 | 345 | 12.5807 | 12.5806 | 0.0001
GEN-2019-001 | 03 CENTRAL | 515621 | OPENSKY7 | 345 | 13.269 | 13.2687 | 0.0003
GEN-2019-001 | 03 CENTRAL | 515646 | GRNTWD 7 | 345 | 11.2623 | 11.2616 | 0.0007
GEN-2019-001 | 03 CENTRAL | 515677 | BADGER 7 | 345 | 13.7821 | 13.782 | 0.0001
GEN-2019-001 | 03 CENTRAL | 515785 | WINDFRM4 | 138 | 19.5945 | 19.5944 | 0.0001
GEN-2019-001 | 03 CENTRAL | 515825 | GRTWSRN7 | 345 | 9.0702 | 9.0701 | 0.0001
GEN-2019-001 | 03 CENTRAL | 515951 | PERSIMN7 | 345 | 11.0796 | 11.0795 | 0.0001
GEN-2019-001 | 03 CENTRAL | 516146 | 25MILE 7 | 345 | 11.1221 | 11.122 | 0.0001
GEN-2019-001 | 03 CENTRAL | 520425 | PIC4 | 138 | 7.9856 | 7.9856 | 0
GEN-2019-001 | 03 CENTRAL | 520430 | NOELSW 4 | 138 | 10.3556 | 10.3555 | 0.0001
GEN-2019-001 | 03 CENTRAL | 520462 | ASPEN 4 | 138 | 19.3561 | 19.356 | 0.0001
GEN-2019-001 | 03 CENTRAL | 520553 | SEILING4 | 138 | 6.6101 | 6.6101 | 0
GEN-2019-001 | 03 CENTRAL | 520601 | AVARD 4 | 138 | 6.857 | 6.857 | 0
GEN-2019-001 | 03 CENTRAL | 520957 | IODINE 4 | 138 | 7.673 | 7.673 | 0
GEN-2019-001 | 03 CENTRAL | 520995 | MOORLND2 | 69 | 8.5299 | 8.5299 | 0
GEN-2019-001 | 03 CENTRAL | 523097 | HITCHLAND 7 | 345 | 14.9713 | 14.9712 | 0.0001
GEN-2019-001 | 03 CENTRAL | 530584 | POSTROCK6 | 230 | 10.7096 | 10.7095 | 0.0001
GEN-2019-001 | 03 CENTRAL | 531449 | HOLCOMB7 | 345 | 9.9438 | 9.9437 | 0.0001
GEN-2019-001 | 03 CENTRAL | 531502 | CIMRRN 7 | 345 | 7.3025 | 7.3024 | 0.0001
GEN-2019-001 | 03 CENTRAL | 531504 | CIMWD2 7 | 345 | 7.4234 | 7.4233 | 0.0001
GEN-2019-001 | 03 CENTRAL | 532766 | JEC N 7 | 345 | 21.3295 | 21.3292 | 0.0003
GEN-2019-001 | 03 CENTRAL | 532767 | GEARY 7 | 345 | 9.8704 | 9.8702 | 0.0002
GEN-2019-001 | 03 CENTRAL | 532780 | CANEYRV7 | 345 | 9.4765 | 9.476 | 0.0005
GEN-2019-001 | 03 CENTRAL | 532793 | NEOSHO 7 | 345 | 17.5726 | 17.5724 | 0.0002
GEN-2019-001 | 03 CENTRAL | 532795 | FR2WEST7 | 345 | 5.4247 | 5.4244 | 0.0003
GEN-2019-001 | 03 CENTRAL | 532801 | ELKRVR17 | 345 | 8.9569 | 8.9564 | 0.0005
GEN-2019-001 | 03 CENTRAL | 532802 | WAVERTX7 | 345 | 14.4336 | 14.4334 | 0.0002
GEN-2019-001 | 03 CENTRAL | 532856 | SWISVAL6 | 230 | 21.669 | 21.6688 | 0.0002
GEN-2019-001 | 03 CENTRAL | 532863 | MORRIS 6 | 230 | 13.4941 | 13.4939 | 0.0002
GEN-2019-001 | 03 CENTRAL | 532871 | CIRCLE 6 | 230 | 8.4637 | 8.4634 | 0.0003
GEN-2019-001 | 03 CENTRAL | 532873 | SUMMIT 6 | 230 | 12.899 | 12.8986 | 0.0004
GEN-2019-001 | 03 CENTRAL | 532982 | OXFORD 4 | 138 | 10.7611 | 10.7608 | 0.0003
GEN-2019-001 | 03 CENTRAL | 532987 | BUTLER 4 | 138 | 10.8593 | 10.8588 | 0.0005
GEN-2019-001 | 03 CENTRAL | 532991 | WEAVER 4 | 138 | 21.9573 | 21.955 | 0.0023
GEN-2019-001 | 03 CENTRAL | 532992 | TIMBJCT4 | 138 | 6.4586 | 6.4585 | 0.0001
GEN-2019-001 | 03 CENTRAL | 532994 | TCBURNS4 | 138 | 3.9642 | 3.9642 | 0
GEN-2019-001 | 03 CENTRAL | 533011 | HALSTD 4 | 138 | 8.2176 | 8.2171 | 0.0005
GEN-2019-001 | 03 CENTRAL | 533013 | MOUND 4 | 138 | 6.8271 | 6.8268 | 0.0003
GEN-2019-001 | 03 CENTRAL | 533016 | WWUPLNT4 | 138 | 8.0701 | 8.0696 | 0.0005
GEN-2019-001 | 03 CENTRAL | 533037 | COMOTAR4 | 138 | 18.4286 | 18.4267 | 0.0019
GEN-2019-001 | 03 CENTRAL | 533038 | COWSKIN4 | 138 | 17.2987 | 17.2963 | 0.0024
GEN-2019-001 | 03 CENTRAL | 533039 | ELPASO 4 | 138 | 24.7628 | 24.7599 | 0.0029
GEN-2019-001 | 03 CENTRAL | 533045 | GILL W 4 | 138 | 21.8043 | 21.8014 | 0.0029
GEN-2019-001 | 03 CENTRAL | 533046 | GILL S 4 | 138 | 21.8015 | 21.7986 | 0.0029
GEN-2019-001 | 03 CENTRAL | 533049 | HOOVERN4 | 138 | 17.0029 | 17.0008 | 0.0021
GEN-2019-001 | 03 CENTRAL | 533060 | NOEASTE4 | 138 | 20.2853 | 20.283 | 0.0023
GEN-2019-001 | 03 CENTRAL | 533063 | SC10BEL4 | 138 | 11.9885 | 11.9881 | 0.0004
GEN-2019-001 | 03 CENTRAL | 533064 | 17TH 4 | 138 | 17.4541 | 17.4522 | 0.0019
GEN-2019-001 | 03 CENTRAL | 533068 | STEARMN4 | 138 | 19.3341 | 19.3322 | 0.0019
GEN-2019-001 | 03 CENTRAL | 533304 | LANG 3 | 115 | 14.9641 | 14.9639 | 0.0002
GEN-2019-001 | 03 CENTRAL | 533380 | SPRGCRK3 | 115 | 3.7906 | 3.7906 | 0
GEN-2019-001 | 03 CENTRAL | 533394 | CORONAD3 | 115 | 6.9686 | 6.9685 | 0.0001
GEN-2019-001 | 03 CENTRAL | 533412 | ARKVALJ3 | 115 | 9.6861 | 9.6858 | 0.0003
GEN-2019-001 | 03 CENTRAL | 533414 | CITIES 3 | 115 | 7.852 | 7.8517 | 0.0003
GEN-2019-001 | 03 CENTRAL | 533419 | HEC 3 | 115 | 17.1573 | 17.1564 | 0.0009
GEN-2019-001 | 03 CENTRAL | 533421 | HEC GT 3 | 115 | 17.8389 | 17.8379 | 0.001
GEN-2019-001 | 03 CENTRAL | 533426 | MANVILE3 | 115 | 8.3015 | 8.3014 | 0.0001
GEN-2019-001 | 03 CENTRAL | 533428 | MCPHER 3 | 115 | 10.5159 | 10.5156 | 0.0003
GEN-2019-001 | 03 CENTRAL | 533430 | MNDRGCT3 | 115 | 6.4875 | 6.4874 | 0.0001
GEN-2019-001 | 03 CENTRAL | 533439 | WHEATLD3 | 115 | 6.7596 | 6.7595 | 0.0001
GEN-2019-001 | 03 CENTRAL | 533506 | DAVIS 2 | 69 | 7.1642 | 7.1641 | 0.0001
GEN-2019-001 | 03 CENTRAL | 533597 | MIDIANW2 | 69 | 14.0106 | 14.0102 | 0.0004
GEN-2019-001 | 03 CENTRAL | 533626 | BURLJCT2 | 69 | 4.935 | 4.935 | 0
GEN-2019-001 | 03 CENTRAL | 533629 | CC2SHAR2 | 69 | 4.6157 | 4.6157 | 0
GEN-2019-001 | 03 CENTRAL | 533786 | CHISHLM2 | 69 | 19.6762 | 19.6749 | 0.0013
GEN-2019-001 | 03 CENTRAL | 539000 | RAGO 4 | 138 | 3.9467 | 3.9466 | 0.0001
GEN-2019-001 | 03 CENTRAL | 539001 | ANTHONY4 | 138 | 5.012 | 5.0119 | 0.0001
GEN-2019-001 | 03 CENTRAL | 539003 | CLDWELL4 | 138 | 5.565 | 5.5648 | 0.0002
GEN-2019-001 | 03 CENTRAL | 539117 | SPRVILL-EHVB | 230 | 12.4582 | 12.458 | 0.0002
GEN-2019-001 | 03 CENTRAL | 539675 | MILANTP4 | 138 | 9.9006 | 9.9001 | 0.0005
GEN-2019-001 | 03 CENTRAL | 539676 | MILAN 4 | 138 | 10.3753 | 10.3747 | 0.0006
GEN-2019-001 | 03 CENTRAL | 539694 | SPEARVL3 | 115 | 9.9365 | 9.9364 | 0.0001
GEN-2019-001 | 03 CENTRAL | 539760 | BARBER 3 | 115 | 8.1332 | 8.133 | 0.0002
GEN-2019-001 | 03 CENTRAL | 539771 | NFTDODG3 | 115 | 9.7556 | 9.7556 | 0
GEN-2019-001 | 03 CENTRAL | 539815 | IRONWOOD WF7 | 345 | 11.8843 | 11.8839 | 0.0004
GEN-2019-001 | 03 CENTRAL | 542966 | WGARDNR5 | 161 | 29.2108 | 29.2107 | 0.0001
GEN-2019-001 | 03 CENTRAL | 542968 | STILWEL7 | 345 | 25.8957 | 25.8955 | 0.0002
GEN-2019-001 | 03 CENTRAL | 542977 | CRAIG 7 | 345 | 26.3941 | 26.394 | 0.0001
GEN-2019-001 | 03 CENTRAL | 542981 | LACYGNE7 | 345 | 26.1692 | 26.169 | 0.0002
GEN-2019-001 | 03 CENTRAL | 560082 | G16-050-TAP | 345 | 6.9512 | 6.9512 | 0
GEN-2019-001 | 03 CENTRAL | 579480 | GEN-2008-124 | 345 | 12.711 | 12.7106 | 0.0004
GEN-2019-001 | 03 CENTRAL | 584900 | GEN-2015-052 | 345 | 13.2613 | 13.2605 | 0.0008
GEN-2019-001 | 03 CENTRAL | 585410 | GREAT_WESTRN | 345 | 9.7415 | 9.7414 | 0.0001
GEN-2019-001 | 03 CENTRAL | 585430 | PRSIMN_CRK1 | 345 | 11.7445 | 11.7444 | 0.0001
GEN-2019-001 | 03 CENTRAL | 587140 | GEN-2016-020 | 138 | 7.4213 | 7.4213 | 0
GEN-2019-001 | 03 CENTRAL | 587311 | G16-046XFMR1 | 115 | 14.7707 | 14.7705 | 0.0002
GEN-2019-001 | 03 CENTRAL | 588300 | GEN-2016-157 | 345 | 5.0515 | 5.0515 | 0
GEN-2019-001 | 03 CENTRAL | 588494 | G17-004-TAP | 345 | 9.3029 | 9.3025 | 0.0004
GEN-2019-001 | 03 CENTRAL | 588560 | GEN-2017-011 | 345 | 12.6206 | 12.6204 | 0.0002
GEN-2019-001 | 03 CENTRAL | 760809 | GEN-2017-203 | 345 | 9.1645 | 9.1641 | 0.0004
GEN-2019-001 | 03 CENTRAL | 761838 | GEN-2017-121 | 138 | 9.138 | 9.1377 | 0.0003
GEN-2019-001 | 03 CENTRAL | 761901 | GEN-2017-125 | 345 | 5.5096 | 5.5096 | 0
GEN-2019-001 | 03 CENTRAL | 761943 | GEN-2017-191 | 345 | 17.4283 | 17.428 | 0.0003
GEN-2019-001 | 03 CENTRAL | 762279 | GEN-2017-195 | 345 | 31.6624 | 31.6621 | 0.0003
GEN-2019-001 | 03 CENTRAL | 763670 | GEN-2019-030 | 345 | 10.4948 | 10.4946 | 0.0002
GEN-2019-001 | 03 CENTRAL | 763850 | G19-055-TAP | 230 | 7.2471 | 7.247 | 0.0001
GEN-2019-014 | 03 CENTRAL | 531448 | HOLCOMB3 | 115 | 21.2532 | 20.6187 | 0.6345
GEN-2019-014 | 03 CENTRAL | 531379 | JONES3 | 115 | 10.6043 | 10.4715 | 0.1328
GEN-2019-014 | 03 CENTRAL | 531393 | PLYMELL3 | 115 | 7.6981 | 7.6421 | 0.056
GEN-2019-014 | 03 CENTRAL | 531420 | FLETCHR3 | 115 | 6.7619 | 6.7197 | 0.0422
GEN-2019-014 | 03 CENTRAL | 531445 | GRDNCTY3 | 115 | 12.5516 | 12.4053 | 0.1463
GEN-2019-014 | 03 CENTRAL | 531449 | HOLCOMB7 | 345 | 9.9438 | 9.8703 | 0.0735
GEN-2019-014 | 03 CENTRAL | 763549 | GEN-2019-014 | 115 | 10.049 | 9.3932 | 0.6558
GEN-2019-014 | 03 CENTRAL | 523853 | FINNEY 7 | 345 | 9.8362 | 9.765 | 0.0712
GEN-2019-014 | 03 CENTRAL | 531392 | PIONTAP3 | 115 | 6.6929 | 6.6715 | 0.0214
GEN-2019-014 | 03 CENTRAL | 531400 | PK_GOAB3 | 115 | 4.8673 | 4.8535 | 0.0138
GEN-2019-014 | 03 CENTRAL | 531408 | PIERCVL3 | 115 | 3.8708 | 3.8567 | 0.0141
GEN-2019-014 | 03 CENTRAL | 531423 | GARDNCY2 | 69 | 3.5783 | 3.5711 | 0.0072
GEN-2019-014 | 03 CENTRAL | 531426 | JAMESON3 | 115 | 10.0589 | 9.946 | 0.1129
GEN-2019-014 | 03 CENTRAL | 531440 | WILLIAM3 | 115 | 3.76 | 3.7505 | 0.0095
GEN-2019-014 | 03 CENTRAL | 531465 | SETAB 7 | 345 | 6.866 | 6.8397 | 0.0263
GEN-2019-014 | 03 CENTRAL | 531476 | SWNDTAP3 | 115 | 7.2115 | 7.1647 | 0.0468
GEN-2019-014 | 03 CENTRAL | 531480 | KSAVWTP3 | 115 | 12.1905 | 12.0528 | 0.1377
GEN-2019-014 | 03 CENTRAL | 531501 | BUCKNER7 | 345 | 9.2456 | 9.2183 | 0.0273
GEN-2019-014 | 03 CENTRAL | 523118 | BUFF_DUNES 7 | 345 | 6.0272 | 6.002 | 0.0252
GEN-2019-014 | 03 CENTRAL | 523823 | CARPENTER 7 | 345 | 6.5781 | 6.5675 | 0.0106
GEN-2019-014 | 03 CENTRAL | 531203 | PNTPR-GOAB3 | 115 | 6.1301 | 6.1159 | 0.0142
GEN-2019-014 | 03 CENTRAL | 531213 | SANTAFE3 | 115 | 2.6965 | 2.6896 | 0.0069
GEN-2019-014 | 03 CENTRAL | 531375 | PUCKET 3 | 115 | 4.8537 | 4.84 | 0.0137
GEN-2019-014 | 03 CENTRAL | 531391 | PIONEER3 | 115 | 5.8805 | 5.8666 | 0.0139
GEN-2019-014 | 03 CENTRAL | 531398 | SUBLETE3 | 115 | 5.9712 | 5.9542 | 0.017
GEN-2019-014 | 03 CENTRAL | 531419 | DOBSON 3 | 115 | 11.3075 | 11.1913 | 0.1162
GEN-2019-014 | 03 CENTRAL | 531425 | LOWETAP3 | 115 | 9.9333 | 9.8303 | 0.103
GEN-2019-014 | 03 CENTRAL | 531437 | SYRACUS3 | 115 | 3.6031 | 3.5962 | 0.0069
GEN-2019-014 | 03 CENTRAL | 531442 | SAT-TAP3 | 115 | 5.0432 | 5.0349 | 0.0083
GEN-2019-014 | 03 CENTRAL | 531451 | MINGO 7 | 345 | 6.0094 | 6.0005 | 0.0089
GEN-2019-014 | 03 CENTRAL | 531464 | SETAB 3 | 115 | 10.1837 | 10.1576 | 0.0261
GEN-2019-014 | 03 CENTRAL | 531469 | SPERVIL7 | 345 | 13.6098 | 13.5947 | 0.0151
GEN-2019-014 | 03 CENTRAL | 531477 | S. WIND3 | 115 | 6.639 | 6.5993 | 0.0397
GEN-2019-014 | 03 CENTRAL | 531478 | IRSKDOL3 | 115 | 6.3396 | 6.3049 | 0.0347
GEN-2019-014 | 03 CENTRAL | 531502 | CIMRRN 7 | 345 | 7.3025 | 7.2854 | 0.0171
GEN-2019-014 | 03 CENTRAL | 531504 | CIMWD2 7 | 345 | 7.4234 | 7.4061 | 0.0173
GEN-2019-014 | 03 CENTRAL | 762662 | G18-030-TAP | 345 | 5.8775 | 5.8532 | 0.0243
GEN-2019-014 | 03 CENTRAL | 523097 | HITCHLAND 7 | 345 | 14.9713 | 14.9665 | 0.0048
GEN-2019-014 | 03 CENTRAL | 530583 | POSTROCK7 | 345 | 7.7231 | 7.7213 | 0.0018
GEN-2019-014 | 03 CENTRAL | 531204 | PLSNTPR3 | 115 | 4.5457 | 4.5379 | 0.0078
GEN-2019-014 | 03 CENTRAL | 531210 | BLUEJAY3 | 115 | 2.113 | 2.1087 | 0.0043
GEN-2019-014 | 03 CENTRAL | 531211 | CHRLSTN3 | 115 | 2.0519 | 2.0479 | 0.004
GEN-2019-014 | 03 CENTRAL | 531374 | HASKELL3 | 115 | 4.9979 | 4.9901 | 0.0078
GEN-2019-014 | 03 CENTRAL | 531378 | HICKOCK3 | 115 | 5.4204 | 5.4105 | 0.0099
GEN-2019-014 | 03 CENTRAL | 531390 | PIONEER2 | 69 | 3.8959 | 3.8922 | 0.0037
GEN-2019-014 | 03 CENTRAL | 531396 | SATATAP3 | 115 | 6.1451 | 6.1317 | 0.0134
GEN-2019-014 | 03 CENTRAL | 531407 | INGALLS3 | 115 | 2.695 | 2.6882 | 0.0068
GEN-2019-014 | 03 CENTRAL | 531429 | MINGO 3 | 115 | 12.2091 | 12.1976 | 0.0115
GEN-2019-014 | 03 CENTRAL | 531430 | MORRIS-3 | 115 | 7.3118 | 7.2668 | 0.045
GEN-2019-014 | 03 CENTRAL | 531433 | SCOTCTY3 | 115 | 8.6896 | 8.6682 | 0.0214
GEN-2019-014 | 03 CENTRAL | 531435 | LOWESUB3 | 115 | 8.7887 | 8.7083 | 0.0804
GEN-2019-014 | 03 CENTRAL | 531439 | TRIBUNE3 | 115 | 3.4428 | 3.439 | 0.0038
GEN-2019-014 | 03 CENTRAL | 531473 | BEARCRK3 | 115 | 2.8132 | 2.8095 | 0.0037
GEN-2019-014 | 03 CENTRAL | 531483 | GRANTTP3 | 115 | 4.8236 | 4.8165 | 0.0071
GEN-2019-014 | 03 CENTRAL | 531485 | CNTRLPL3 | 115 | 5.892 | 5.8836 | 0.0084
GEN-2019-014 | 03 CENTRAL | 531490 | ULYSPLT3 | 115 | 3.9265 | 3.9201 | 0.0064
GEN-2019-014 | 03 CENTRAL | 531493 | GANO 3 | 115 | 6.6299 | 6.602 | 0.0279
GEN-2019-014 | 03 CENTRAL | 531512 | HARBNGR7 | 345 | 6.5579 | 6.5474 | 0.0105
GEN-2019-014 | 03 CENTRAL | 531632 | GEN-2015-065 | 345 | 5.3136 | 5.3068 | 0.0068
GEN-2019-014 | 03 CENTRAL | 539691 | SATMKEC3 | 115 | 5.0332 | 5.025 | 0.0082
GEN-2019-014 | 03 CENTRAL | 539695 | SPEARVL6 | 230 | 12.772 | 12.7651 | 0.0069
GEN-2019-014 | 03 CENTRAL | 539759 | SPRVL 3 | 115 | 12.8273 | 12.8231 | 0.0042
GEN-2019-014 | 03 CENTRAL | 539800 | CLARKCOUNTY7 | 345 | 12.7785 | 12.771 | 0.0075
GEN-2019-014 | 03 CENTRAL | 539803 | IRONWOOD7 | 345 | 13.1638 | 13.1504 | 0.0134
GEN-2019-014 | 03 CENTRAL | 599950 | LAMAR7 | 345 | 4.0728 | 4.0612 | 0.0116
GEN-2019-014 | 03 CENTRAL | 640325 | REDWILO3 | 345 | 6.1522 | 6.1496 | 0.0026
GEN-2019-014 | 03 CENTRAL | 762658 | GEN-2018-030 | 345 | 5.2186 | 5.1997 | 0.0189
GEN-2019-014 | 03 CENTRAL | 515554 | BVRCNTY7 | 345 | 15.3093 | 15.3063 | 0.003
GEN-2019-014 | 03 CENTRAL | 523095 | HITCHLAND 6 | 230 | 14.5761 | 14.5735 | 0.0026
GEN-2019-014 | 03 CENTRAL | 523101 | NOBLE_WND 7 | 345 | 14.9103 | 14.9055 | 0.0048
GEN-2019-014 | 03 CENTRAL | 523112 | NOVUS1 7 | 345 | 14.6716 | 14.6669 | 0.0047
GEN-2019-014 | 03 CENTRAL | 523961 | POTTER_CO 7 | 345 | 11.6631 | 11.6628 | 0.0003
GEN-2019-014 | 03 CENTRAL | 530555 | COLBY 3 | 115 | 5.8396 | 5.8373 | 0.0023
GEN-2019-014 | 03 CENTRAL | 530559 | PH RUN 3 | 115 | 4.4815 | 4.4801 | 0.0014
GEN-2019-014 | 03 CENTRAL | 530584 | POSTROCK6 | 230 | 10.7096 | 10.7078 | 0.0018
GEN-2019-014 | 03 CENTRAL | 531200 | RUBART 3 | 115 | 6.5142 | 6.5017 | 0.0125
GEN-2019-014 | 03 CENTRAL | 531212 | TWNSPRG3 | 115 | 1.5951 | 1.5927 | 0.0024
GEN-2019-014 | 03 CENTRAL | 531351 | BREWSTR3 | 115 | 3.0791 | 3.0782 | 0.0009
GEN-2019-014 | 03 CENTRAL | 531362 | MANNGT 3 | 115 | 4.9648 | 4.9589 | 0.0059
GEN-2019-014 | 03 CENTRAL | 531377 | HICKOCK2 | 69 | 2.7531 | 2.7516 | 0.0015
GEN-2019-014 | 03 CENTRAL | 531397 | SATANTA3 | 115 | 3.9494 | 3.9439 | 0.0055
GEN-2019-014 | 03 CENTRAL | 531401 | ULU E 2 | 69 | 3.6521 | 3.6488 | 0.0033
GEN-2019-014 | 03 CENTRAL | 531402 | ULU NW 2 | 69 | 3.0755 | 3.0732 | 0.0023
GEN-2019-014 | 03 CENTRAL | 531424 | JOHNCR 3 | 115 | 2.813 | 2.8095 | 0.0035
GEN-2019-014 | 03 CENTRAL | 531428 | LEOTI 3 | 115 | 4.2083 | 4.2037 | 0.0046
GEN-2019-014 | 03 CENTRAL | 531432 | PILE 3 | 115 | 6.3493 | 6.3302 | 0.0191
GEN-2019-014 | 03 CENTRAL | 531438 | TRIB SW3 | 115 | 3.5142 | 3.5103 | 0.0039
GEN-2019-014 | 03 CENTRAL | 531467 | SEWARD-3 | 115 | 4.9344 | 4.9284 | 0.006
GEN-2019-014 | 03 CENTRAL | 531472 | AMOCO 3 | 115 | 4.8321 | 4.8242 | 0.0079
GEN-2019-014 | 03 CENTRAL | 531481 | HUGOTON3 | 115 | 5.6343 | 5.6286 | 0.0057
GEN-2019-014 | 03 CENTRAL | 531484 | GRANT 3 | 115 | 4.5424 | 4.5361 | 0.0063
GEN-2019-014 | 03 CENTRAL | 531491 | BIG BOW 3 | 115 | 3.1036 | 3.0994 | 0.0042
GEN-2019-014 | 03 CENTRAL | 531510 | HARBNGR3 | 115 | 10.6191 | 10.6068 | 0.0123
GEN-2019-014 | 03 CENTRAL | 531623 | EASTFORK3 | 115 | 9.6776 | 9.6705 | 0.0071
GEN-2019-014 | 03 CENTRAL | 539117 | SPRVILL-EHVB | 230 | 12.4582 | 12.4517 | 0.0065
GEN-2019-014 | 03 CENTRAL | 539694 | SPEARVL3 | 115 | 9.9365 | 9.9344 | 0.0021
GEN-2019-014 | 03 CENTRAL | 539771 | NFTDODG3 | 115 | 9.7556 | 9.7537 | 0.0019
GEN-2019-014 | 03 CENTRAL | 539801 | THISTLE7 | 345 | 16.6662 | 16.6636 | 0.0026
GEN-2019-014 | 03 CENTRAL | 539813 | TRANSFORMER | 345 | 10.6791 | 10.674 | 0.0051
GEN-2019-014 | 03 CENTRAL | 539815 | IRONWOOD WF7 | 345 | 11.8843 | 11.8735 | 0.0108
GEN-2019-014 | 03 CENTRAL | 539840 | GEN-2011-008 | 345 | 10.5555 | 10.5506 | 0.0049
GEN-2019-014 | 03 CENTRAL | 560080 | G16-046-TAP | 345 | 11.3684 | 11.3613 | 0.0071
GEN-2019-014 | 03 CENTRAL | 560082 | G16-050-TAP | 345 | 6.9512 | 6.9508 | 0.0004
GEN-2019-014 | 03 CENTRAL | 576397 | G10014G11022 | 345 | 10.3812 | 10.3791 | 0.0021
GEN-2019-014 | 03 CENTRAL | 579480 | GEN-2008-124 | 345 | 12.711 | 12.6985 | 0.0125
GEN-2019-014 | 03 CENTRAL | 640183 | GENTLMN3 | 345 | 15.5779 | 15.5766 | 0.0013
GEN-2019-014 | 03 CENTRAL | 640326 | REDWILO7 | 115 | 10.8676 | 10.8659 | 0.0017
GEN-2019-014 | 03 CENTRAL | 763670 | GEN-2019-030 | 345 | 10.4948 | 10.4865 | 0.0083
GEN-2019-014 | 03 CENTRAL | 763850 | G19-055-TAP | 230 | 7.2471 | 7.2457 | 0.0014
GEN-2019-014 | 03 CENTRAL | 763890 | GEN-2019-058 | 345 | 12.52 | 12.5129 | 0.0071
GEN-2019-016 | 03 CENTRAL | 547478 | DAD368 5 | 161 | 18.2088 | 17.4042 | 0.8046
GEN-2019-016 | 03 CENTRAL | 300101 | 5MORGAN | 161 | 19.3195 | 18.5438 | 0.7757
GEN-2019-016 | 03 CENTRAL | 547493 | BOL431 5 | 161 | 5.8877 | 5.8121 | 0.0756
GEN-2019-016 | 03 CENTRAL | 547499 | CPK446 5 | 161 | 8.3865 | 8.3275 | 0.059
GEN-2019-016 | 03 CENTRAL | 547585 | DAD368 2 | 69 | 9.4491 | 9.3874 | 0.0617
GEN-2019-016 | 03 CENTRAL | 763560 | GEN-2019-016 | 161 | 17.8983 | 17.0931 | 0.8052
GEN-2019-016 | 03 CENTRAL | 300782 | 2MORGAN | 69 | 6.7965 | 6.779 | 0.0175
GEN-2019-016 | 03 CENTRAL | 301622 | 5MORGANXF2 | 161 | 19.3191 | 18.5452 | 0.7739
GEN-2019-016 | 03 CENTRAL | 505498 | STOCKTN5 | 161 | 9.6537 | 9.5799 | 0.0738
GEN-2019-016 | 03 CENTRAL | 547436 | CUPTAP 2 | 69 | 5.8229 | 5.8016 | 0.0213
GEN-2019-016 | 03 CENTRAL | 547464 | BOL 73 5 | 161 | 4.7095 | 4.6644 | 0.0451
GEN-2019-016 | 03 CENTRAL | 547468 | AUR124 5 | 161 | 10.2987 | 10.2639 | 0.0348
GEN-2019-016 | 03 CENTRAL | 547536 | ASH121 2 | 69 | 6.9144 | 6.8975 | 0.0169
GEN-2019-016 | 03 CENTRAL | 547545 | FRP217 2 | 69 | 4.3359 | 4.3235 | 0.0124
GEN-2019-016 | 03 CENTRAL | 547618 | CPK446 2 | 69 | 10.0189 | 9.9923 | 0.0266
GEN-2019-016 | 03 CENTRAL | 549969 | BROOKLINE 5 | 161 | 27.5423 | 27.3698 | 0.1725
GEN-2019-016 | 03 CENTRAL | 300045 | 7MORGAN | 345 | 14.5406 | 14.3571 | 0.1835
GEN-2019-016 | 03 CENTRAL | 300118 | 5STKAEC | 161 | 8.9446 | 8.8869 | 0.0577
GEN-2019-016 | 03 CENTRAL | 300658 | 2BILLNG | 69 | 8.0361 | 8.0233 | 0.0128
GEN-2019-016 | 03 CENTRAL | 300668 | 2DADEVL | 69 | 5.5893 | 5.5789 | 0.0104
GEN-2019-016 | 03 CENTRAL | 300677 | 2MTVRN | 69 | 8.6777 | 8.6584 | 0.0193
GEN-2019-016 | 03 CENTRAL | 300774 | 2EUDORA | 69 | 5.8902 | 5.8792 | 0.011
GEN-2019-016 | 03 CENTRAL | 300816 | 5COLLINS | 161 | 6.4861 | 6.4661 | 0.02
GEN-2019-016 | 03 CENTRAL | 505492 | SPRGFLD5 | 161 | 26.4401 | 26.2987 | 0.1414
GEN-2019-016 | 03 CENTRAL | 547437 | CUPSUB 2 | 69 | 4.7527 | 4.7386 | 0.0141
GEN-2019-016 | 03 CENTRAL | 547480 | MON383 5 | 161 | 11.5525 | 11.5315 | 0.021
GEN-2019-016 | 03 CENTRAL | 547528 | BOL 73 2 | 69 | 7.6543 | 7.6169 | 0.0374
GEN-2019-016 | 03 CENTRAL | 547537 | AUR124 2 | 69 | 12.0093 | 11.9894 | 0.0199
GEN-2019-016 | 03 CENTRAL | 547552 | LAW260 2 | 69 | 5.4425 | 5.4343 | 0.0082
GEN-2019-016 | 03 CENTRAL | 547612 | BOL602 2 | 69 | 4.6483 | 4.6342 | 0.0141
GEN-2019-016 | 03 CENTRAL | 547613 | GRN614 2 | 69 | 4.0781 | 4.0727 | 0.0054
GEN-2019-016 | 03 CENTRAL | 547726 | WIL482 | 69 | 6.8876 | 6.8753 | 0.0123
GEN-2019-016 | 03 CENTRAL | 549954 | JTEC 5 | 161 | 26.0288 | 25.8981 | 0.1307
GEN-2019-016 | 03 CENTRAL | 549955 | JUNCTION 5 | 161 | 20.2174 | 20.1279 | 0.0895
GEN-2019-016 | 03 CENTRAL | 549984 | BROOKLINE 7 | 345 | 11.7653 | 11.6884 | 0.0769
GEN-2019-016 | 03 CENTRAL | 763696 | G19-035-TAP | 161 | 7.5161 | 7.5037 | 0.0124
GEN-2019-016 | 03 CENTRAL | 300042 | 7HUBEN | 345 | 10.2894 | 10.2559 | 0.0335
GEN-2019-016 | 03 CENTRAL | 300108 | 5OSCEOLTP | 161 | 6.4005 | 6.3888 | 0.0117
GEN-2019-016 | 03 CENTRAL | 300348 | 5BTLFD | 161 | 21.1186 | 21.0327 | 0.0859
GEN-2019-016 | 03 CENTRAL | 300672 | 2GRNFLD | 69 | 5.8363 | 5.8285 | 0.0078
GEN-2019-016 | 03 CENTRAL | 300678 | 5NIXA-1 | 161 | 18.6376 | 18.5695 | 0.0681
GEN-2019-016 | 03 CENTRAL | 300684 | 2MIDWYTP | 69 | 8.5 | 8.4816 | 0.0184
GEN-2019-016 | 03 CENTRAL | 300788 | 2SLAGLE | 69 | 5.9499 | 5.943 | 0.0069
GEN-2019-016 | 03 CENTRAL | 300793 | 5HYDERHL | 161 | 8.2826 | 8.2391 | 0.0435
GEN-2019-016 | 03 CENTRAL | 300800 | 2BONA | 69 | 3.3325 | 3.3288 | 0.0037
GEN-2019-016 | 03 CENTRAL | 300949 | 7JASPER | 345 | 12.5964 | 12.5546 | 0.0418
GEN-2019-016 | 03 CENTRAL | 505494 | SPRGFLD2 | 69 | 15.4692 | 15.447 | 0.0222
GEN-2019-016 | 03 CENTRAL | 505496 | NIXA 5 | 161 | 12.1794 | 12.1537 | 0.0257
GEN-2019-016 | 03 CENTRAL | 506935 | FLINTCR7 | 345 | 15.1826 | 15.1745 | 0.0081
GEN-2019-016 | 03 CENTRAL | 547425 | HER209 2 | 69 | 1.331 | 1.3299 | 0.0011
GEN-2019-016 | 03 CENTRAL | 547440 | EXP450T2 | 69 | 5.4736 | 5.4607 | 0.0129
GEN-2019-016 | 03 CENTRAL | 547472 | TIP292 5 | 161 | 17.5176 | 17.5086 | 0.009
GEN-2019-016 | 03 CENTRAL | 547473 | RDS295 5 | 161 | 7.691 | 7.6824 | 0.0086
GEN-2019-016 | 03 CENTRAL | 547479 | LAR382 5 | 161 | 14.1883 | 14.1744 | 0.0139
GEN-2019-016 | 03 CENTRAL | 547540 | MON152 2 | 69 | 10.4737 | 10.4649 | 0.0088
GEN-2019-016 | 03 CENTRAL | 547546 | BIL221 2 | 69 | 9.6155 | 9.6 | 0.0155
GEN-2019-016 | 03 CENTRAL | 547549 | ARC250 2 | 69 | 3.8871 | 3.8821 | 0.005
GEN-2019-016 | 03 CENTRAL | 547573 | HTC338 2 | 69 | 6.2994 | 6.2901 | 0.0093
GEN-2019-016 | 03 CENTRAL | 547575 | BUF342 2 | 69 | 3.4172 | 3.4123 | 0.0049
GEN-2019-016 | 03 CENTRAL | 547578 | AUR355 2 | 69 | 9.1248 | 9.1126 | 0.0122
GEN-2019-016 | 03 CENTRAL | 547584 | BOL367 2 | 69 | 4.9809 | 4.9649 | 0.016
GEN-2019-016 | 03 CENTRAL | 547591 | MON383 2 | 69 | 12.0813 | 12.0704 | 0.0109
GEN-2019-016 | 03 CENTRAL | 547598 | LKW400 2 | 69 | 3.5349 | 3.5316 | 0.0033
GEN-2019-016 | 03 CENTRAL | 547605 | STK418 2 | 69 | 7.2693 | 7.2524 | 0.0169
GEN-2019-016 | 03 CENTRAL | 547611 | MAR437 2 | 69 | 5.7371 | 5.7324 | 0.0047
GEN-2019-016 | 03 CENTRAL | 547691 | WIL369 2 | 69 | 5.9752 | 5.966 | 0.0092
GEN-2019-016 | 03 CENTRAL | 547727 | WIL479 | 69 | 7.2783 | 7.2655 | 0.0128
GEN-2019-016 | 03 CENTRAL | 549956 | NICHOLS 5 | 161 | 18.4132 | 18.3385 | 0.0747
GEN-2019-016 | 03 CENTRAL | 549959 | BATTLEFIELD5 | 161 | 25.8009 | 25.6661 | 0.1348
GEN-2019-016 | 03 CENTRAL | 549960 | SW DISP PLT5 | 161 | 24.7793 | 24.6598 | 0.1195
GEN-2019-016 | 03 CENTRAL | 549961 | JAMES RIVER5 | 161 | 15.1885 | 15.1527 | 0.0358
GEN-2019-016 | 03 CENTRAL | 549970 | CLAY 5 | 161 | 18.0381 | 17.9833 | 0.0548
GEN-2019-016 | 03 CENTRAL | 549971 | PIC WEST 5 | 161 | 16.6072 | 16.5485 | 0.0587
GEN-2019-016 | 03 CENTRAL | 709500 | GI-95_POI | 345 | 8.3433 | 8.2853 | 0.058
GEN-2019-016 | 03 CENTRAL | 763692 | GEN-2019-035 | 161 | 7.4994 | 7.487 | 0.0124
GEN-2019-016 | 03 CENTRAL | 999920 | GI85-MSU1 | 345 | 14.2911 | 14.1144 | 0.1767
GEN-2019-016 | 03 CENTRAL | 300051 | 7FRANKSRCTP | 345 | 15.4906 | 15.478 | 0.0126
GEN-2019-016 | 03 CENTRAL | 300070 | 5CLARK | 161 | 7.8253 | 7.8094 | 0.0159
GEN-2019-016 | 03 CENTRAL | 300088 | 5HUBEN | 161 | 15.3156 | 15.2891 | 0.0265
GEN-2019-016 | 03 CENTRAL | 300089 | 5JAMESV | 161 | 15.4618 | 15.4173 | 0.0445
GEN-2019-016 | 03 CENTRAL | 300657 | 2ASHGRV | 69 | 3.8626 | 3.8606 | 0.002
GEN-2019-016 | 03 CENTRAL | 300665 | 2CLEVER | 69 | 4.4911 | 4.4883 | 0.0028
GEN-2019-016 | 03 CENTRAL | 300669 | 2ELWOOD | 69 | 5.1756 | 5.1727 | 0.0029
GEN-2019-016 | 03 CENTRAL | 300676 | 2LOCKWD | 69 | 3.9001 | 3.8972 | 0.0029
GEN-2019-016 | 03 CENTRAL | 300680 | 2VERONA | 69 | 6.2812 | 6.2785 | 0.0027
GEN-2019-016 | 03 CENTRAL | 300683 | 2MIDWY | 69 | 4.5589 | 4.5536 | 0.0053
GEN-2019-016 | 03 CENTRAL | 300739 | 7BLACKBERRY | 345 | 15.3686 | 15.3395 | 0.0291
GEN-2019-016 | 03 CENTRAL | 300770 | 2BUFFLO | 69 | 5.6613 | 5.6576 | 0.0037
GEN-2019-016 | 03 CENTRAL | 300785 | 2PLEAST | 69 | 4.2071 | 4.2043 | 0.0028
GEN-2019-016 | 03 CENTRAL | 300797 | 2ARCOLA | 69 | 4.7256 | 4.7208 | 0.0048
GEN-2019-016 | 03 CENTRAL | 300798 | 2HYDERHL | 69 | 8.1798 | 8.1659 | 0.0139
GEN-2019-016 | 03 CENTRAL | 300950 | 5JASPER | 161 | 12.5569 | 12.534 | 0.0229
GEN-2019-016 | 03 CENTRAL | 301040 | 5OSCEOL | 161 | 6.385 | 6.3734 | 0.0116
GEN-2019-016 | 03 CENTRAL | 301161 | 5LOGAN | 161 | 13.122 | 13.0949 | 0.0271
GEN-2019-016 | 03 CENTRAL | 301395 | 2ROUNDGRVETP | 69 | 4.2737 | 4.2704 | 0.0033
GEN-2019-016 | 03 CENTRAL | 301477 | 5OSCEOKCTP | 161 | 6.3993 | 6.3876 | 0.0117
GEN-2019-016 | 03 CENTRAL | 301521 | 5REEDSP | 161 | 8.2374 | 8.2287 | 0.0087
GEN-2019-016 | 03 CENTRAL | 505472 | TABLE R5 | 161 | 14.4249 | 14.4087 | 0.0162
GEN-2019-016 | 03 CENTRAL | 505486 | NEO SPA5 | 161 | 15.2822 | 15.2756 | 0.0066
GEN-2019-016 | 03 CENTRAL | 505488 | CARTHAG5 | 161 | 16.0469 | 16.0364 | 0.0105
GEN-2019-016 | 03 CENTRAL | 505501 | NIXA 2 | 69 | 11.9199 | 11.909 | 0.0109
GEN-2019-016 | 03 CENTRAL | 506934 | FLINTCR5 | 161 | 33.2983 | 33.2871 | 0.0112
GEN-2019-016 | 03 CENTRAL | 506979 | SHIPERD7 | 345 | 10.1603 | 10.1568 | 0.0035
GEN-2019-016 | 03 CENTRAL | 512750 | TONECE7 | 345 | 14.9626 | 14.9553 | 0.0073
GEN-2019-016 | 03 CENTRAL | 547400 | MON376J2 | 69 | 3.932 | 3.9309 | 0.0011
GEN-2019-016 | 03 CENTRAL | 547405 | MON352J2 | 69 | 7.549 | 7.5448 | 0.0042
GEN-2019-016 | 03 CENTRAL | 547432 | BUF243J2 | 69 | 3.2163 | 3.2127 | 0.0036
GEN-2019-016 | 03 CENTRAL | 547434 | BUF409 2 | 69 | 2.5623 | 2.5595 | 0.0028
GEN-2019-016 | 03 CENTRAL | 547441 | EXP4502 | 69 | 4.4111 | 4.4028 | 0.0083
GEN-2019-016 | 03 CENTRAL | 547449 | PRC460 2 | 69 | 5.4851 | 5.4835 | 0.0016
GEN-2019-016 | 03 CENTRAL | 547483 | JOP389 5 | 161 | 20.3233 | 20.3148 | 0.0085
GEN-2019-016 | 03 CENTRAL | 547500 | RNM393 5 | 161 | 14.2217 | 14.2162 | 0.0055
GEN-2019-016 | 03 CENTRAL | 547529 | SED 80 2 | 69 | 15.9425 | 15.8994 | 0.0431
GEN-2019-016 | 03 CENTRAL | 547550 | GLD251 2 | 69 | 3.625 | 3.6228 | 0.0022
GEN-2019-016 | 03 CENTRAL | 547553 | ALB262 2 | 69 | 8.3509 | 8.3363 | 0.0146
GEN-2019-016 | 03 CENTRAL | 547567 | BRT323 2 | 69 | 5.6653 | 5.6543 | 0.011
GEN-2019-016 | 03 CENTRAL | 547580 | REP359 2 | 69 | 12.6424 | 12.6192 | 0.0232
GEN-2019-016 | 03 CENTRAL | 547606 | MTV420 2 | 69 | 6.7933 | 6.7848 | 0.0085
GEN-2019-016 | 03 CENTRAL | 547616 | STK324J2 | 69 | 5.8547 | 5.8436 | 0.0111
GEN-2019-016 | 03 CENTRAL | 549903 | JRPS 69B-2 2 | 69 | 18.6697 | 18.6412 | 0.0285
GEN-2019-016 | 03 CENTRAL | 549904 | JAMES RIVER2 | 69 | 15.3833 | 15.3652 | 0.0181
GEN-2019-016 | 03 CENTRAL | 549911 | GOLDEN 2 | 69 | 19.6784 | 19.6402 | 0.0382
GEN-2019-016 | 03 CENTRAL | 549925 | NICHOLS 2 | 69 | 23.1146 | 23.0439 | 0.0707
GEN-2019-016 | 03 CENTRAL | 549957 | WEST BELT 5 | 161 | 18.1482 | 18.0766 | 0.0716
GEN-2019-016 | 03 CENTRAL | 549958 | MAIN STREET5 | 161 | 18.3661 | 18.2937 | 0.0724
GEN-2019-016 | 03 CENTRAL | 549962 | MILL 5 | 161 | 15.3637 | 15.3244 | 0.0393
GEN-2019-016 | 03 CENTRAL | 549963 | MENTOR 5 | 161 | 14.4101 | 14.3761 | 0.034
GEN-2019-016 | 03 CENTRAL | 549966 | SUMMIT 5 | 161 | 12.8309 | 12.7996 | 0.0313
GEN-2019-016 | 03 CENTRAL | 549979 | BATTLEFIELD2 | 69 | 19.9561 | 19.9173 | 0.0388
GEN-2019-016 | 03 CENTRAL | 588980 | GEN-2017-060 | 161 | 5.838 | 5.8359 | 0.0021
GEN-2019-016 | 03 CENTRAL | 709501 | GI-95_HV | 345 | 8.3433 | 8.2853 | 0.058
GEN-2019-016 | 03 CENTRAL | 999940 | GI85-MSU3 | 345 | 13.2591 | 13.1076 | 0.1515
GEN-2019-018 | 03 CENTRAL | 530711 | SAXMAN 3 | 115 | 4.4373 | 4.079 | 0.3583
GEN-2019-018 | 03 CENTRAL | 530620 | LYONS 3 | 115 | 5.4243 | 5.0717 | 0.3526
GEN-2019-018 | 03 CENTRAL | 530623 | RICE 3 | 115 | 6.4817 | 6.2734 | 0.2083
GEN-2019-018 | 03 CENTRAL | 533439 | WHEATLD3 | 115 | 6.7596 | 6.608 | 0.1516
GEN-2019-018 | 03 CENTRAL | 530681 | BUSHTON3 | 115 | 4.9177 | 4.8118 | 0.1059
GEN-2019-018 | 03 CENTRAL | 530686 | RICE 6 | 230 | 4.1143 | 4.0405 | 0.0738
GEN-2019-018 | 03 CENTRAL | 530718 | BUSHTONW 3 | 115 | 4.1338 | 4.0479 | 0.0859
GEN-2019-018 | 03 CENTRAL | 533438 | WMCPHER3 | 115 | 10.8946 | 10.7522 | 0.1424
GEN-2019-018 | 03 CENTRAL | 530688 | BUFLOCRK6 | 230 | 2.7508 | 2.7232 | 0.0276
GEN-2019-018 | 03 CENTRAL | 532871 | CIRCLE 6 | 230 | 8.4637 | 8.385 | 0.0787
GEN-2019-018 | 03 CENTRAL | 533394 | CORONAD3 | 115 | 6.9686 | 6.9402 | 0.0284
GEN-2019-018 | 03 CENTRAL | 533416 | RENO 3 | 115 | 22.1556 | 22.0555 | 0.1001
GEN-2019-018 | 03 CENTRAL | 533426 | MANVILE3 | 115 | 8.3015 | 8.2314 | 0.0701
GEN-2019-018 | 03 CENTRAL | 533428 | MCPHER 3 | 115 | 10.5159 | 10.3905 | 0.1254
GEN-2019-018 | 03 CENTRAL | 539662 | ELLSWTH3 | 115 | 3.4499 | 3.415 | 0.0349
GEN-2019-018 | 03 CENTRAL | 532771 | RENO 7 | 345 | 11.0976 | 11.0706 | 0.027
GEN-2019-018 | 03 CENTRAL | 532872 | EMCPHER6 | 230 | 7.7208 | 7.6593 | 0.0615
GEN-2019-018 | 03 CENTRAL | 533374 | MENTOR 3 | 115 | 12.3397 | 12.3098 | 0.0299
GEN-2019-018 | 03 CENTRAL | 533413 | CIRCLE 3 | 115 | 18.3479 | 18.2539 | 0.094
GEN-2019-018 | 03 CENTRAL | 533415 | DAVIS 3 | 115 | 8.0324 | 8.0172 | 0.0152
GEN-2019-018 | 03 CENTRAL | 533417 | EMCPHER3 | 115 | 11.1793 | 11.0705 | 0.1088
GEN-2019-018 | 03 CENTRAL | 533427 | REFINRY3 | 115 | 10.3372 | 10.2265 | 0.1107
GEN-2019-018 | 03 CENTRAL | 533429 | MOUNDRG3 | 115 | 8.416 | 8.4102 | 0.0058
GEN-2019-018 | 03 CENTRAL | 539660 | EHALLTP3 | 115 | 3.2328 | 3.2099 | 0.0229
GEN-2019-018 | 03 CENTRAL | 763862 | G19-054-TAP | 230 | 6.9761 | 6.9625 | 0.0136
GEN-2019-030 | 03 CENTRAL | 539803 | IRONWOOD7 | 345 | 13.1638 | 12.6493 | 0.5145
GEN-2019-030 | 03 CENTRAL | 531469 | SPERVIL7 | 345 | 13.6098 | 13.1198 | 0.49
GEN-2019-030 | 03 CENTRAL | 539815 | IRONWOOD WF7 | 345 | 11.8843 | 11.4664 | 0.4179
GEN-2019-030 | 03 CENTRAL | 560080 | G16-046-TAP | 345 | 11.3684 | 11.1081 | 0.2603
GEN-2019-030 | 03 CENTRAL | 579480 | GEN-2008-124 | 345 | 12.711 | 12.2317 | 0.4793
GEN-2019-030 | 03 CENTRAL | 763670 | GEN-2019-030 | 345 | 10.4948 | 9.9752 | 0.5196
GEN-2019-030 | 03 CENTRAL | 530583 | POSTROCK7 | 345 | 7.7231 | 7.6782 | 0.0449
GEN-2019-030 | 03 CENTRAL | 531501 | BUCKNER7 | 345 | 9.2456 | 9.1295 | 0.1161
GEN-2019-030 | 03 CENTRAL | 539695 | SPEARVL6 | 230 | 12.772 | 12.5589 | 0.2131
GEN-2019-030 | 03 CENTRAL | 539759 | SPRVL 3 | 115 | 12.8273 | 12.7045 | 0.1228
GEN-2019-030 | 03 CENTRAL | 539800 | CLARKCOUNTY7 | 345 | 12.7785 | 12.52 | 0.2585
GEN-2019-030 | 03 CENTRAL | 587310 | GEN-2016-046 | 345 | 9.9533 | 9.7565 | 0.1968
GEN-2019-030 | 03 CENTRAL | 530584 | POSTROCK6 | 230 | 10.7096 | 10.6684 | 0.0412
GEN-2019-030 | 03 CENTRAL | 531449 | HOLCOMB7 | 345 | 9.9438 | 9.8917 | 0.0521
GEN-2019-030 | 03 CENTRAL | 531502 | CIMRRN 7 | 345 | 7.3025 | 7.2298 | 0.0727
GEN-2019-030 | 03 CENTRAL | 531504 | CIMWD2 7 | 345 | 7.4234 | 7.3497 | 0.0737
GEN-2019-030 | 03 CENTRAL | 539117 | SPRVILL-EHVB | 230 | 12.4582 | 12.2564 | 0.2018
GEN-2019-030 | 03 CENTRAL | 539694 | SPEARVL3 | 115 | 9.9365 | 9.8811 | 0.0554
GEN-2019-030 | 03 CENTRAL | 539771 | NFTDODG3 | 115 | 9.7556 | 9.7172 | 0.0384
GEN-2019-030 | 03 CENTRAL | 539801 | THISTLE7 | 345 | 16.6662 | 16.5941 | 0.0721
GEN-2019-030 | 03 CENTRAL | 539813 | TRANSFORMER | 345 | 10.6791 | 10.4998 | 0.1793
GEN-2019-030 | 03 CENTRAL | 539840 | GEN-2011-008 | 345 | 10.5555 | 10.3855 | 0.17
GEN-2019-030 | 03 CENTRAL | 560082 | G16-050-TAP | 345 | 6.9512 | 6.9444 | 0.0068
GEN-2019-030 | 03 CENTRAL | 587311 | G16-046XFMR1 | 115 | 14.7707 | 14.6469 | 0.1238
GEN-2019-030 | 03 CENTRAL | 763850 | G19-055-TAP | 230 | 7.2471 | 7.2075 | 0.0396
GEN-2019-030 | 03 CENTRAL | 763890 | GEN-2019-058 | 345 | 12.52 | 12.2721 | 0.2479
GEN-2019-030 | 03 CENTRAL | 515852 | DGRASSE7 | 345 | 15.3179 | 15.2953 | 0.0226
GEN-2019-030 | 03 CENTRAL | 523853 | FINNEY 7 | 345 | 9.8362 | 9.7858 | 0.0504
GEN-2019-030 | 03 CENTRAL | 530558 | KNOLL N 6 | 230 | 10.6179 | 10.5776 | 0.0403
GEN-2019-030 | 03 CENTRAL | 530582 | S HAYS6 | 230 | 8.805 | 8.7801 | 0.0249
GEN-2019-030 | 03 CENTRAL | 530702 | BUCKEYE_230 | 230 | 7.8435 | 7.8224 | 0.0211
GEN-2019-030 | 03 CENTRAL | 530720 | KNOLL S 6 | 230 | 10.6179 | 10.5776 | 0.0403
GEN-2019-030 | 03 CENTRAL | 531448 | HOLCOMB3 | 115 | 21.2532 | 21.2246 | 0.0286
GEN-2019-030 | 03 CENTRAL | 531465 | SETAB 7 | 345 | 6.866 | 6.85 | 0.016
GEN-2019-030 | 03 CENTRAL | 532782 | BUFFALO7 | 345 | 20.7555 | 20.7322 | 0.0233
GEN-2019-030 | 03 CENTRAL | 539671 | FTDODGE3 | 115 | 9.6942 | 9.6564 | 0.0378
GEN-2019-030 | 03 CENTRAL | 539679 | GRTBEND6 | 230 | 8.7899 | 8.7671 | 0.0228
GEN-2019-030 | 03 CENTRAL | 539688 | S-DODGE3 | 115 | 6.7777 | 6.7601 | 0.0176
GEN-2019-030 | 03 CENTRAL | 539758 | FORD 3 | 115 | 5.204 | 5.1957 | 0.0083
GEN-2019-030 | 03 CENTRAL | 539804 | THISTLE4 | 138 | 17.5567 | 17.5288 | 0.0279
GEN-2019-030 | 03 CENTRAL | 539841 | G-2011-008-1 | 345 | 10.5555 | 10.3855 | 0.17
GEN-2019-030 | 03 CENTRAL | 539855 | G-2011-008-2 | 345 | 8.8342 | 8.7163 | 0.1179
GEN-2019-030 | 03 CENTRAL | 539857 | G-2011-008-3 | 345 | 8.2708 | 8.1684 | 0.1024
GEN-2019-030 | 03 CENTRAL | 587350 | GEN-2016-050 | 345 | 5.8546 | 5.8499 | 0.0047
GEN-2019-030 | 03 CENTRAL | 588630 | GEN-2017-018 | 345 | 16.6662 | 16.5941 | 0.0721
GEN-2019-030 | 03 CENTRAL | 640065 | AXTELL 3 | 345 | 9.208 | 9.2032 | 0.0048
GEN-2019-030 | 03 CENTRAL | 762834 | GEN-2018-049 | 345 | 6.9567 | 6.9446 | 0.0121
GEN-2019-030 | 03 CENTRAL | 763758 | GEN-2019-044 | 115 | 6.4739 | 6.4581 | 0.0158
GEN-2019-030 | 03 CENTRAL | 763846 | G19-053/055 | 230 | 7.1612 | 7.1226 | 0.0386
GEN-2019-030 | 03 CENTRAL | 515375 | WWRDEHV7 | 345 | 22.3641 | 22.3512 | 0.0129
GEN-2019-030 | 03 CENTRAL | 515853 | DGRASSE4 | 138 | 17.0745 | 17.0689 | 0.0056
GEN-2019-030 | 03 CENTRAL | 523118 | BUFF_DUNES 7 | 345 | 6.0272 | 6.0094 | 0.0178
GEN-2019-030 | 03 CENTRAL | 523823 | CARPENTER 7 | 345 | 6.5781 | 6.5712 | 0.0069
GEN-2019-030 | 03 CENTRAL | 530553 | S HAYS 3 | 115 | 8.4163 | 8.4055 | 0.0108
GEN-2019-030 | 03 CENTRAL | 530561 | KNOLL 3 | 115 | 10.3394 | 10.3241 | 0.0153
GEN-2019-030 | 03 CENTRAL | 530592 | SMOKYHL6 | 230 | 6.0395 | 6.0364 | 0.0031
GEN-2019-030 | 03 CENTRAL | 530610 | SHAYS_230 | 230 | 3.4161 | 3.4131 | 0.003
GEN-2019-030 | 03 CENTRAL | 530680 | HEIZER 6 | 230 | 8.7324 | 8.7099 | 0.0225
GEN-2019-030 | 03 CENTRAL | 531379 | JONES3 | 115 | 10.6043 | 10.5977 | 0.0066
GEN-2019-030 | 03 CENTRAL | 531393 | PLYMELL3 | 115 | 7.6981 | 7.695 | 0.0031
GEN-2019-030 | 03 CENTRAL | 531420 | FLETCHR3 | 115 | 6.7619 | 6.7593 | 0.0026
GEN-2019-030 | 03 CENTRAL | 531445 | GRDNCTY3 | 115 | 12.5516 | 12.5439 | 0.0077
GEN-2019-030 | 03 CENTRAL | 531451 | MINGO 7 | 345 | 6.0094 | 6.0034 | 0.006
GEN-2019-030 | 03 CENTRAL | 531464 | SETAB 3 | 115 | 10.1837 | 10.1742 | 0.0095
GEN-2019-030 | 03 CENTRAL | 532783 | KINGMAN7 | 345 | 7.0277 | 7.0257 | 0.002
GEN-2019-030 | 03 CENTRAL | 532796 | WICHITA7 | 345 | 23.7708 | 23.7496 | 0.0212
GEN-2019-030 | 03 CENTRAL | 539638 | FLATRDG4 | 138 | 15.5636 | 15.5426 | 0.021
GEN-2019-030 | 03 CENTRAL | 539645 | DCBEEF3 | 115 | 6.943 | 6.9236 | 0.0194
GEN-2019-030 | 03 CENTRAL | 539678 | GRTBEND3 | 115 | 12.2449 | 12.2275 | 0.0174
GEN-2019-030 | 03 CENTRAL | 539699 | W-DODGE3 | 115 | 4.3105 | 4.3041 | 0.0064
GEN-2019-030 | 03 CENTRAL | 539763 | SSTARTP3 | 115 | 4.0742 | 4.0711 | 0.0031
GEN-2019-030 | 03 CENTRAL | 539783 | CRKCK 3 | 115 | 4.65 | 4.6458 | 0.0042
GEN-2019-030 | 03 CENTRAL | 587500 | GEN-2016-073 | 345 | 15.2224 | 15.2101 | 0.0123
GEN-2019-030 | 03 CENTRAL | 640066 | AXTELL 7 | 115 | 14.0353 | 14.0331 | 0.0022
GEN-2019-030 | 03 CENTRAL | 640312 | PAULINE3 | 345 | 7.8813 | 7.88 | 0.0013
GEN-2019-030 | 03 CENTRAL | 640374 | SWEET W3 | 345 | 10.1673 | 10.1652 | 0.0021
GEN-2019-030 | 03 CENTRAL | 760284 | GEN-2017-220 | 345 | 20.642 | 20.619 | 0.023
GEN-2019-030 | 03 CENTRAL | 762662 | G18-030-TAP | 345 | 5.8775 | 5.8604 | 0.0171
GEN-2019-030 | 03 CENTRAL | 763549 | GEN-2019-014 | 115 | 10.049 | 10.0431 | 0.0059
GEN-2019-030 | 03 CENTRAL | 763862 | G19-054-TAP | 230 | 6.9761 | 6.9653 | 0.0108
GEN-2019-035 | 03 CENTRAL | 763696 | G19-035-TAP | 161 | 7.5161 | 7.197 | 0.3191
GEN-2019-035 | 03 CENTRAL | 547468 | AUR124 5 | 161 | 10.2987 | 10.1186 | 0.1801
GEN-2019-035 | 03 CENTRAL | 547473 | RDS295 5 | 161 | 7.691 | 7.541 | 0.15
GEN-2019-035 | 03 CENTRAL | 763692 | GEN-2019-035 | 161 | 7.4994 | 7.1802 | 0.3192
GEN-2019-035 | 03 CENTRAL | 301521 | 5REEDSP | 161 | 8.2374 | 8.1077 | 0.1297
GEN-2019-035 | 03 CENTRAL | 547480 | MON383 5 | 161 | 11.5525 | 11.4676 | 0.0849
GEN-2019-035 | 03 CENTRAL | 547499 | CPK446 5 | 161 | 8.3865 | 8.3304 | 0.0561
GEN-2019-035 | 03 CENTRAL | 547537 | AUR124 2 | 69 | 12.0093 | 11.9444 | 0.0649
GEN-2019-035 | 03 CENTRAL | 300725 | 2REEDSP | 69 | 9.9093 | 9.8708 | 0.0385
GEN-2019-035 | 03 CENTRAL | 547472 | TIP292 5 | 161 | 17.5176 | 17.4954 | 0.0222
GEN-2019-035 | 03 CENTRAL | 547478 | DAD368 5 | 161 | 18.2088 | 18.1793 | 0.0295
GEN-2019-035 | 03 CENTRAL | 547479 | LAR382 5 | 161 | 14.1883 | 14.156 | 0.0323
GEN-2019-035 | 03 CENTRAL | 547488 | BRN412 5 | 161 | 9.7523 | 9.6625 | 0.0898
GEN-2019-035 | 03 CENTRAL | 547540 | MON152 2 | 69 | 10.4737 | 10.4427 | 0.031
GEN-2019-035 | 03 CENTRAL | 547578 | AUR355 2 | 69 | 9.1248 | 9.0904 | 0.0344
GEN-2019-035 | 03 CENTRAL | 547591 | MON383 2 | 69 | 12.0813 | 12.0428 | 0.0385
GEN-2019-035 | 03 CENTRAL | 547611 | MAR437 2 | 69 | 5.7371 | 5.7268 | 0.0103
GEN-2019-035 | 03 CENTRAL | 547618 | CPK446 2 | 69 | 10.0189 | 9.9938 | 0.0251
GEN-2019-035 | 03 CENTRAL | 300101 | 5MORGAN | 161 | 19.3195 | 19.2897 | 0.0298
GEN-2019-035 | 03 CENTRAL | 300658 | 2BILLNG | 69 | 8.0361 | 8.0239 | 0.0122
GEN-2019-035 | 03 CENTRAL | 300677 | 2MTVRN | 69 | 8.6777 | 8.6593 | 0.0184
GEN-2019-035 | 03 CENTRAL | 300680 | 2VERONA | 69 | 6.2812 | 6.273 | 0.0082
GEN-2019-035 | 03 CENTRAL | 300720 | 2GRTNA | 69 | 5.4096 | 5.3999 | 0.0097
GEN-2019-035 | 03 CENTRAL | 300722 | 2LAKE-K | 69 | 9.984 | 9.9537 | 0.0303
GEN-2019-035 | 03 CENTRAL | 505486 | NEO SPA5 | 161 | 15.2822 | 15.2676 | 0.0146
GEN-2019-035 | 03 CENTRAL | 505488 | CARTHAG5 | 161 | 16.0469 | 16.0276 | 0.0193
GEN-2019-035 | 03 CENTRAL | 505492 | SPRGFLD5 | 161 | 26.4401 | 26.3969 | 0.0432
GEN-2019-035 | 03 CENTRAL | 547400 | MON376J2 | 69 | 3.932 | 3.9279 | 0.0041
GEN-2019-035 | 03 CENTRAL | 547405 | MON352J2 | 69 | 7.549 | 7.5338 | 0.0152
GEN-2019-035 | 03 CENTRAL | 547449 | PRC460 2 | 69 | 5.4851 | 5.4792 | 0.0059
GEN-2019-035 | 03 CENTRAL | 547475 | BRN331 5 | 161 | 9.4475 | 9.3674 | 0.0801
GEN-2019-035 | 03 CENTRAL | 547483 | JOP389 5 | 161 | 20.3233 | 20.3048 | 0.0185
GEN-2019-035 | 03 CENTRAL | 547493 | BOL431 5 | 161 | 5.8877 | 5.8845 | 0.0032
GEN-2019-035 | 03 CENTRAL | 547495 | GRT433 5 | 161 | 9.6805 | 9.6069 | 0.0736
GEN-2019-035 | 03 CENTRAL | 547500 | RNM393 5 | 161 | 14.2217 | 14.2087 | 0.013
GEN-2019-035 | 03 CENTRAL | 547546 | BIL221 2 | 69 | 9.6155 | 9.6008 | 0.0147
GEN-2019-035 | 03 CENTRAL | 547585 | DAD368 2 | 69 | 9.4491 | 9.445 | 0.0041
GEN-2019-035 | 03 CENTRAL | 547606 | MTV420 2 | 69 | 6.7933 | 6.7805 | 0.0128
GEN-2019-035 | 03 CENTRAL | 588980 | GEN-2017-060 | 161 | 5.838 | 5.8331 | 0.0049
GEN-2019-035 | 03 CENTRAL | 763560 | GEN-2019-016 | 161 | 17.8983 | 17.87 | 0.0283
GEN-2019-035 | 03 CENTRAL | 300662 | 2CAPEFR | 69 | 5.3543 | 5.3467 | 0.0076
GEN-2019-035 | 03 CENTRAL | 300665 | 2CLEVER | 69 | 4.4911 | 4.4878 | 0.0033
GEN-2019-035 | 03 CENTRAL | 300667 | 2CRANE | 69 | 3.1862 | 3.1844 | 0.0018
GEN-2019-035 | 03 CENTRAL | 300678 | 5NIXA-1 | 161 | 18.6376 | 18.6131 | 0.0245
GEN-2019-035 | 03 CENTRAL | 300679 | 2PRDYTP | 69 | 4.9271 | 4.9229 | 0.0042
GEN-2019-035 | 03 CENTRAL | 300684 | 2MIDWYTP | 69 | 8.5 | 8.4825 | 0.0175
GEN-2019-035 | 03 CENTRAL | 300713 | 2BEARCK | 69 | 4.8223 | 4.8155 | 0.0068
GEN-2019-035 | 03 CENTRAL | 300714 | 2BLUWTP | 69 | 7.6153 | 7.5977 | 0.0176
GEN-2019-035 | 03 CENTRAL | 300730 | 2SILDOL | 69 | 8.9344 | 8.9143 | 0.0201
GEN-2019-035 | 03 CENTRAL | 300733 | 2STONBR | 69 | 7.124 | 7.1085 | 0.0155
GEN-2019-035 | 03 CENTRAL | 300734 | 2STULTS | 69 | 5.938 | 5.9305 | 0.0075
GEN-2019-035 | 03 CENTRAL | 300782 | 2MORGAN | 69 | 6.7965 | 6.7951 | 0.0014
GEN-2019-035 | 03 CENTRAL | 301622 | 5MORGANXF2 | 161 | 19.3191 | 19.2893 | 0.0298
GEN-2019-035 | 03 CENTRAL | 505485 | WASHBURN5 | 161 | 7.9704 | 7.9656 | 0.0048
GEN-2019-035 | 03 CENTRAL | 505490 | CARTHG 2 | 69 | 13.4194 | 13.413 | 0.0064
GEN-2019-035 | 03 CENTRAL | 505494 | SPRGFLD2 | 69 | 15.4692 | 15.4629 | 0.0063
GEN-2019-035 | 03 CENTRAL | 505496 | NIXA 5 | 161 | 12.1794 | 12.1651 | 0.0143
GEN-2019-035 | 03 CENTRAL | 505498 | STOCKTN5 | 161 | 9.6537 | 9.6504 | 0.0033
GEN-2019-035 | 03 CENTRAL | 547401 | MON376 2 | 69 | 6.3801 | 6.3692 | 0.0109
GEN-2019-035 | 03 CENTRAL | 547402 | MON416J2 | 69 | 3.4627 | 3.4595 | 0.0032
GEN-2019-035 | 03 CENTRAL | 547406 | MON352 2 | 69 | 7.2516 | 7.2376 | 0.014
GEN-2019-035 | 03 CENTRAL | 547407 | MON311J2 | 69 | 6.4611 | 6.4499 | 0.0112
GEN-2019-035 | 03 CENTRAL | 547436 | CUPTAP 2 | 69 | 5.8229 | 5.8215 | 0.0014
GEN-2019-035 | 03 CENTRAL | 547462 | SVRCK469 5 | 161 | 14.2703 | 14.2598 | 0.0105
GEN-2019-035 | 03 CENTRAL | 547464 | BOL 73 5 | 161 | 4.7095 | 4.7075 | 0.002
GEN-2019-035 | 03 CENTRAL | 547466 | ATL109 5 | 161 | 15.9307 | 15.9182 | 0.0125
GEN-2019-035 | 03 CENTRAL | 547471 | NEO184 5 | 161 | 14.0651 | 14.0534 | 0.0117
GEN-2019-035 | 03 CENTRAL | 547474 | OZD312 5 | 161 | 9.3888 | 9.334 | 0.0548
GEN-2019-035 | 03 CENTRAL | 547485 | CAR395 5 | 161 | 11.9275 | 11.918 | 0.0095
GEN-2019-035 | 03 CENTRAL | 547489 | BRN413 5 | 161 | 10.2361 | 10.169 | 0.0671
GEN-2019-035 | 03 CENTRAL | 547498 | STL439 5 | 161 | 24.8049 | 24.7862 | 0.0187
GEN-2019-035 | 03 CENTRAL | 547536 | ASH121 2 | 69 | 6.9144 | 6.9107 | 0.0037
GEN-2019-035 | 03 CENTRAL | 547544 | WEN205 2 | 69 | 4.3361 | 4.3334 | 0.0027
GEN-2019-035 | 03 CENTRAL | 547545 | FRP217 2 | 69 | 4.3359 | 4.3351 | 0.0008
GEN-2019-035 | 03 CENTRAL | 547577 | MTV351 2 | 69 | 6.8632 | 6.8508 | 0.0124
GEN-2019-035 | 03 CENTRAL | 547580 | REP359 2 | 69 | 12.6424 | 12.6299 | 0.0125
GEN-2019-035 | 03 CENTRAL | 547592 | JOP389 2 | 69 | 15.0356 | 15.0312 | 0.0044
GEN-2019-035 | 03 CENTRAL | 547593 | JOP391 5 | 161 | 13.3544 | 13.3436 | 0.0108
GEN-2019-035 | 03 CENTRAL | 547595 | RNM393 2 | 69 | 18.9765 | 18.9669 | 0.0096
GEN-2019-035 | 03 CENTRAL | 549959 | BATTLEFIELD5 | 161 | 25.8009 | 25.7602 | 0.0407
GEN-2019-035 | 03 CENTRAL | 549969 | BROOKLINE 5 | 161 | 27.5423 | 27.5007 | 0.0416
GEN-2019-035 | 03 CENTRAL | 549970 | CLAY 5 | 161 | 18.0381 | 18.0216 | 0.0165
GEN-2019-035 | 03 CENTRAL | 760893 | GEN-2017-148 | 161 | 4.6217 | 4.621 | 0.0007
GEN-2019-044 | 03 CENTRAL | 539771 | NFTDODG3 | 115 | 9.7556 | 9.1843 | 0.5713
GEN-2019-044 | 03 CENTRAL | 539671 | FTDODGE3 | 115 | 9.6942 | 9.1311 | 0.5631
GEN-2019-044 | 03 CENTRAL | 539688 | S-DODGE3 | 115 | 6.7777 | 6.5092 | 0.2685
GEN-2019-044 | 03 CENTRAL | 539694 | SPEARVL3 | 115 | 9.9365 | 9.7862 | 0.1503
GEN-2019-044 | 03 CENTRAL | 539758 | FORD 3 | 115 | 5.204 | 5.0858 | 0.1182
GEN-2019-044 | 03 CENTRAL | 539759 | SPRVL 3 | 115 | 12.8273 | 12.6702 | 0.1571
GEN-2019-044 | 03 CENTRAL | 763758 | GEN-2019-044 | 115 | 6.4739 | 5.8865 | 0.5874
GEN-2019-044 | 03 CENTRAL | 531469 | SPERVIL7 | 345 | 13.6098 | 13.521 | 0.0888
GEN-2019-044 | 03 CENTRAL | 539645 | DCBEEF3 | 115 | 6.943 | 6.6481 | 0.2949
GEN-2019-044 | 03 CENTRAL | 539695 | SPEARVL6 | 230 | 12.772 | 12.6846 | 0.0874
GEN-2019-044 | 03 CENTRAL | 539699 | W-DODGE3 | 115 | 4.3105 | 4.2111 | 0.0994
GEN-2019-044 | 03 CENTRAL | 539763 | SSTARTP3 | 115 | 4.0742 | 4.0379 | 0.0363
GEN-2019-044 | 03 CENTRAL | 539783 | CRKCK 3 | 115 | 4.65 | 4.5945 | 0.0555
GEN-2019-044 | 03 CENTRAL | 530583 | POSTROCK7 | 345 | 7.7231 | 7.7141 | 0.009
GEN-2019-044 | 03 CENTRAL | 531501 | BUCKNER7 | 345 | 9.2456 | 9.2233 | 0.0223
GEN-2019-044 | 03 CENTRAL | 539117 | SPRVILL-EHVB | 230 | 12.4582 | 12.3755 | 0.0827
GEN-2019-044 | 03 CENTRAL | 539628 | NW-DGTP3 | 115 | 3.4945 | 3.4289 | 0.0656
GEN-2019-044 | 03 CENTRAL | 539659 | CUDAHY 3 | 115 | 4.1422 | 4.1116 | 0.0306
GEN-2019-044 | 03 CENTRAL | 539664 | GRNBURG3 | 115 | 3.807 | 3.7828 | 0.0242
GEN-2019-044 | 03 CENTRAL | 539740 | EDODGE 3 | 115 | 6.3259 | 6.0802 | 0.2457
GEN-2019-044 | 03 CENTRAL | 539761 | SSTARW 3 | 115 | 3.4178 | 3.3939 | 0.0239
GEN-2019-044 | 03 CENTRAL | 539778 | GYCOTAP3 | 115 | 2.4458 | 2.4219 | 0.0239
GEN-2019-044 | 03 CENTRAL | 539784 | ENSNGW 3 | 115 | 3.423 | 3.3968 | 0.0262
GEN-2019-044 | 03 CENTRAL | 539800 | CLARKCOUNTY7 | 345 | 12.7785 | 12.7341 | 0.0444
GEN-2019-044 | 03 CENTRAL | 539803 | IRONWOOD7 | 345 | 13.1638 | 13.0847 | 0.0791
GEN-2019-044 | 03 CENTRAL | 763850 | G19-055-TAP | 230 | 7.2471 | 7.2318 | 0.0153
GEN-2019-044 | 03 CENTRAL | 530584 | POSTROCK6 | 230 | 10.7096 | 10.7007 | 0.0089
GEN-2019-044 | 03 CENTRAL | 531449 | HOLCOMB7 | 345 | 9.9438 | 9.9321 | 0.0117
GEN-2019-044 | 03 CENTRAL | 531502 | CIMRRN 7 | 345 | 7.3025 | 7.2886 | 0.0139
GEN-2019-044 | 03 CENTRAL | 531504 | CIMWD2 7 | 345 | 7.4234 | 7.4093 | 0.0141
GEN-2019-044 | 03 CENTRAL | 539641 | NW-DODG3 | 115 | 3.5807 | 3.5007 | 0.08
GEN-2019-044 | 03 CENTRAL | 539646 | KISMET 3 | 115 | 5.2182 | 5.2058 | 0.0124
GEN-2019-044 | 03 CENTRAL | 539667 | HAGGARD3 | 115 | 2.4458 | 2.4219 | 0.0239
GEN-2019-044 | 03 CENTRAL | 539679 | GRTBEND6 | 230 | 8.7899 | 8.7825 | 0.0074
GEN-2019-044 | 03 CENTRAL | 539680 | N-DODGE3 | 115 | 4.6268 | 4.4941 | 0.1327
GEN-2019-044 | 03 CENTRAL | 539697 | SUNCITY3 | 115 | 4.0347 | 4.0251 | 0.0096
GEN-2019-044 | 03 CENTRAL | 539779 | GRAY CO3 | 115 | 2.4458 | 2.4219 | 0.0239
GEN-2019-044 | 03 CENTRAL | 539801 | THISTLE7 | 345 | 16.6662 | 16.6489 | 0.0173
GEN-2019-044 | 03 CENTRAL | 539813 | TRANSFORMER | 345 | 10.6791 | 10.6484 | 0.0307
GEN-2019-044 | 03 CENTRAL | 539815 | IRONWOOD WF7 | 345 | 11.8843 | 11.8203 | 0.064
GEN-2019-044 | 03 CENTRAL | 539840 | GEN-2011-008 | 345 | 10.5555 | 10.5264 | 0.0291
GEN-2019-044 | 03 CENTRAL | 539944 | LOCHS | 115 | 3.2221 | 3.1661 | 0.056
GEN-2019-044 | 03 CENTRAL | 560080 | G16-046-TAP | 345 | 11.3684 | 11.3261 | 0.0423
GEN-2019-044 | 03 CENTRAL | 560082 | G16-050-TAP | 345 | 6.9512 | 6.9498 | 0.0014
GEN-2019-044 | 03 CENTRAL | 579480 | GEN-2008-124 | 345 | 12.711 | 12.6374 | 0.0736
GEN-2019-044 | 03 CENTRAL | 763670 | GEN-2019-030 | 345 | 10.4948 | 10.4455 | 0.0493
GEN-2019-044 | 03 CENTRAL | 763846 | G19-053/055 | 230 | 7.1612 | 7.1463 | 0.0149
GEN-2019-044 | 03 CENTRAL | 763890 | GEN-2019-058 | 345 | 12.52 | 12.4774 | 0.0426
GEN-2019-044 | 03 CENTRAL | 515852 | DGRASSE7 | 345 | 15.3179 | 15.3122 | 0.0057
GEN-2019-044 | 03 CENTRAL | 523853 | FINNEY 7 | 345 | 9.8362 | 9.8248 | 0.0114
GEN-2019-044 | 03 CENTRAL | 530558 | KNOLL N 6 | 230 | 10.6179 | 10.6091 | 0.0088
GEN-2019-044 | 03 CENTRAL | 530582 | S HAYS6 | 230 | 8.805 | 8.799 | 0.006
GEN-2019-044 | 03 CENTRAL | 530680 | HEIZER 6 | 230 | 8.7324 | 8.7252 | 0.0072
GEN-2019-044 | 03 CENTRAL | 530702 | BUCKEYE_230 | 230 | 7.8435 | 7.8389 | 0.0046
GEN-2019-044 | 03 CENTRAL | 530720 | KNOLL S 6 | 230 | 10.6179 | 10.6091 | 0.0088
GEN-2019-044 | 03 CENTRAL | 531448 | HOLCOMB3 | 115 | 21.2532 | 21.2447 | 0.0085
GEN-2019-044 | 03 CENTRAL | 531465 | SETAB 7 | 345 | 6.866 | 6.8624 | 0.0036
GEN-2019-044 | 03 CENTRAL | 532782 | BUFFALO7 | 345 | 20.7555 | 20.7496 | 0.0059
GEN-2019-044 | 03 CENTRAL | 539652 | CMRIVTP3 | 115 | 5.8522 | 5.8407 | 0.0115
GEN-2019-044 | 03 CENTRAL | 539673 | MED-LDG3 | 115 | 7.9553 | 7.9472 | 0.0081
GEN-2019-044 | 03 CENTRAL | 539678 | GRTBEND3 | 115 | 12.2449 | 12.239 | 0.0059
GEN-2019-044 | 03 CENTRAL | 539804 | THISTLE4 | 138 | 17.5567 | 17.5447 | 0.012
GEN-2019-044 | 03 CENTRAL | 539841 | G-2011-008-1 | 345 | 10.5555 | 10.5264 | 0.0291
GEN-2019-044 | 03 CENTRAL | 539855 | G-2011-008-2 | 345 | 8.8342 | 8.8141 | 0.0201
GEN-2019-044 | 03 CENTRAL | 539857 | G-2011-008-3 | 345 | 8.2708 | 8.2533 | 0.0175
GEN-2019-044 | 03 CENTRAL | 587310 | GEN-2016-046 | 345 | 9.9533 | 9.9214 | 0.0319
GEN-2019-044 | 03 CENTRAL | 587350 | GEN-2016-050 | 345 | 5.8546 | 5.8537 | 0.0009
GEN-2019-044 | 03 CENTRAL | 588630 | GEN-2017-018 | 345 | 16.6662 | 16.6489 | 0.0173
GEN-2019-044 | 03 CENTRAL | 640065 | AXTELL 3 | 345 | 9.208 | 9.2071 | 0.0009
GEN-2019-044 | 03 CENTRAL | 762834 | GEN-2018-049 | 345 | 6.9567 | 6.9538 | 0.0029
GEN-2019-044 | 03 CENTRAL | 763862 | G19-054-TAP | 230 | 6.9761 | 6.9726 | 0.0035
GEN-2019-048 | 03 CENTRAL | 543091 | DUNCNRD2 | 69 | 6.3611 | 6.3611 | 0
GEN-2019-048 | 03 CENTRAL | 541235 | DUNCAN 5 | 161 | 19.6761 | 19.6761 | 0
GEN-2019-048 | 03 CENTRAL | 543093 | LAKCTYK2 | 69 | 7.4716 | 7.4716 | 0
GEN-2019-048 | 03 CENTRAL | 763802 | GEN-2019-048 | 69 | 6.2255 | 6.2255 | 0
GEN-2019-048 | 03 CENTRAL | 541205 | BLSPE 5 | 161 | 20.9255 | 20.9255 | 0
GEN-2019-048 | 03 CENTRAL | 541250 | SIBLEYPL | 161 | 32.6166 | 32.6166 | 0
GEN-2019-048 | 03 CENTRAL | 543088 | BLUSPRG2 | 69 | 8.0006 | 8.0006 | 0
GEN-2019-048 | 03 CENTRAL | 541202 | SIBLEY 5 | 161 | 32.3338 | 32.3338 | 0
GEN-2019-048 | 03 CENTRAL | 541211 | BLSPS 5 | 161 | 19.4568 | 19.4568 | 0
GEN-2019-048 | 03 CENTRAL | 541215 | HLLMRK 5 | 161 | 13.7604 | 13.7604 | 0
GEN-2019-048 | 03 CENTRAL | 541226 | GRAINVL5 | 161 | 13.6858 | 13.6858 | 0
GEN-2019-048 | 03 CENTRAL | 541237 | BLSPW 5 | 161 | 15.1362 | 15.1362 | 0
GEN-2019-048 | 03 CENTRAL | 541244 | ORRICK 5 | 161 | 14.3914 | 14.3914 | 0
GEN-2019-048 | 03 CENTRAL | 541263 | SIBLEY 2 | 69 | 11.5464 | 11.5464 | 0
GEN-2019-048 | 03 CENTRAL | 543092 | LAKCTY 2 | 69 | 8.878 | 8.878 | 0
GEN-2019-048 | 03 CENTRAL | 548808 | ECKLES-161 | 161 | 26.4468 | 26.4468 | 0
GEN-2019-048 | 03 CENTRAL | 300320 | 5LEVASY | 161 | 10.2976 | 10.2976 | 0
GEN-2019-048 | 03 CENTRAL | 301563 | 5MOCITYB1 | 161 | 19.3387 | 19.3387 | 0
GEN-2019-048 | 03 CENTRAL | 541201 | SIBLEY 7 | 345 | 21.6871 | 21.6871 | 0
GEN-2019-048 | 03 CENTRAL | 541206 | PRALEE 5 | 161 | 20.1233 | 20.1233 | 0
GEN-2019-048 | 03 CENTRAL | 541227 | OAKGRV 5 | 161 | 12.017 | 12.017 | 0
GEN-2019-048 | 03 CENTRAL | 541236 | RICHMND5 | 161 | 7.8781 | 7.8781 | 0
GEN-2019-048 | 03 CENTRAL | 541238 | LKWOOD 5 | 161 | 13.0117 | 13.0117 | 0
GEN-2019-048 | 03 CENTRAL | 541247 | LBRTYWT5 | 161 | 15.459 | 15.459 | 0
GEN-2019-048 | 03 CENTRAL | 541262 | LIBERTY2 | 69 | 9.6481 | 9.6481 | 0
GEN-2019-048 | 03 CENTRAL | 543004 | BLUMILS5 | 161 | 17.0306 | 17.0306 | 0
GEN-2019-048 | 03 CENTRAL | 543087 | LAKCTYJ2 | 69 | 10.2205 | 10.2205 | 0
GEN-2019-048 | 03 CENTRAL | 300091 | 5LATHRP | 161 | 7.7756 | 7.7756 | 0
GEN-2019-048 | 03 CENTRAL | 300098 | 5MOCITYB2 | 161 | 19.3106 | 19.3106 | 0
GEN-2019-048 | 03 CENTRAL | 300110 | 5PITTSV | 161 | 8.525 | 8.525 | 0
GEN-2019-048 | 03 CENTRAL | 300304 | 2MOCITY | 69 | 9.1697 | 9.1697 | 0
GEN-2019-048 | 03 CENTRAL | 345408 | 7OVERTON | 345 | 12.3922 | 12.3922 | 0
GEN-2019-048 | 03 CENTRAL | 541200 | PHILL 7 | 345 | 18.399 | 18.399 | 0
GEN-2019-048 | 03 CENTRAL | 541203 | NASHUA 5 | 161 | 33.0731 | 33.0731 | 0
GEN-2019-048 | 03 CENTRAL | 541219 | RAYTOWN5 | 161 | 12.7552 | 12.7552 | 0
GEN-2019-048 | 03 CENTRAL | 541229 | ODESSA 5 | 161 | 9.5887 | 9.5887 | 0
GEN-2019-048 | 03 CENTRAL | 541232 | LEX161 5 | 161 | 7.5801 | 7.5801 | 0
GEN-2019-048 | 03 CENTRAL | 541233 | LEESUM 5 | 161 | 19.756 | 19.756 | 0
GEN-2019-048 | 03 CENTRAL | 541246 | STROTHR5 | 161 | 14.1721 | 14.1721 | 0
GEN-2019-048 | 03 CENTRAL | 541261 | STALEY 2 | 69 | 5.6086 | 5.6086 | 0
GEN-2019-048 | 03 CENTRAL | 541414 | SIB REA1 | 345 | 19.2051 | 19.2051 | 0
GEN-2019-048 | 03 CENTRAL | 541500 | KETCHEM7 | 345 | 8.9464 | 8.9464 | 0
GEN-2019-048 | 03 CENTRAL | 542972 | HAWTH 7 | 345 | 22.5877 | 22.5877 | 0
GEN-2019-048 | 03 CENTRAL | 543114 | PLUMRRD2 | 69 | 12.1385 | 12.1385 | 0
GEN-2019-048 | 03 CENTRAL | 543116 | BLUEMLS2 | 69 | 7.3328 | 7.3328 | 0
GEN-2019-048 | 03 CENTRAL | 548806 | BLUVLY | 69 | 22.65 | 22.65 | 0
GEN-2019-048 | 03 CENTRAL | 548807 | BLUVLY-161 | 161 | 17.7458 | 17.7458 | 0
GEN-2019-051 | 03 CENTRAL | 539661 | 24-FREY3 | 115 | 8.1561 | 7.9045 | 0.2516
GEN-2019-051 | 03 CENTRAL | 539681 | N-GBEND3 | 115 | 9.1049 | 8.9146 | 0.1903
GEN-2019-051 | 03 CENTRAL | 539689 | 2ND-KS 3 | 115 | 7.9906 | 7.778 | 0.2126
GEN-2019-051 | 03 CENTRAL | 763329 | GEN-2018-116 | 115 | 8.1395 | 7.8878 | 0.2517
GEN-2019-051 | 03 CENTRAL | 539666 | GBENDTP3 | 115 | 8.7185 | 8.547 | 0.1715
GEN-2019-051 | 03 CENTRAL | 539678 | GRTBEND3 | 115 | 12.2449 | 12.0313 | 0.2136
GEN-2019-051 | 03 CENTRAL | 530601 | HEIZER 3 | 115 | 12.1453 | 11.9451 | 0.2002
GEN-2019-051 | 03 CENTRAL | 539642 | ELLSWTP3 | 115 | 3.9126 | 3.9045 | 0.0081
GEN-2019-051 | 03 CENTRAL | 539679 | GRTBEND6 | 230 | 8.7899 | 8.7146 | 0.0753
GEN-2019-051 | 03 CENTRAL | 539684 | OTISSUB3 | 115 | 2.9219 | 2.9095 | 0.0124
GEN-2019-051 | 03 CENTRAL | 539692 | SEWARD 3 | 115 | 5.8179 | 5.7727 | 0.0452
GEN-2019-051 | 03 CENTRAL | 530563 | HEIZER 2 | 69 | 8.7188 | 8.6597 | 0.0591
GEN-2019-051 | 03 CENTRAL | 530582 | S HAYS6 | 230 | 8.805 | 8.7817 | 0.0233
GEN-2019-051 | 03 CENTRAL | 530602 | LAXTAP 3 | 115 | 4.087 | 4.0734 | 0.0136
GEN-2019-051 | 03 CENTRAL | 530609 | HZRNGPL3 | 115 | 7.7647 | 7.6824 | 0.0823
GEN-2019-051 | 03 CENTRAL | 530679 | SEWRDMW3 | 115 | 5.1213 | 5.0864 | 0.0349
GEN-2019-051 | 03 CENTRAL | 530680 | HEIZER 6 | 230 | 8.7324 | 8.6576 | 0.0748
GEN-2019-051 | 03 CENTRAL | 539643 | ROLLHLS3 | 115 | 3.5855 | 3.5794 | 0.0061
GEN-2019-051 | 03 CENTRAL | 539696 | ST-JOHN3 | 115 | 5.2881 | 5.2725 | 0.0156
GEN-2019-051 | 03 CENTRAL | 539701 | RUSSELL3 | 115 | 3.4282 | 3.4226 | 0.0056
GEN-2019-051 | 03 CENTRAL | 763850 | G19-055-TAP | 230 | 7.2471 | 7.233 | 0.0141
GEN-2019-051 | 03 CENTRAL | 763862 | G19-054-TAP | 230 | 6.9761 | 6.9413 | 0.0348
GEN-2019-051 | 03 CENTRAL | 530553 | S HAYS 3 | 115 | 8.4163 | 8.4084 | 0.0079
GEN-2019-051 | 03 CENTRAL | 530565 | SEWARD 2 | 69 | 5.3611 | 5.3393 | 0.0218
GEN-2019-051 | 03 CENTRAL | 530568 | GB NTH 2 | 69 | 6.7283 | 6.693 | 0.0353
GEN-2019-051 | 03 CENTRAL | 530584 | POSTROCK6 | 230 | 10.7096 | 10.6917 | 0.0179
GEN-2019-051 | 03 CENTRAL | 530586 | ALBERT 2 | 69 | 3.6217 | 3.613 | 0.0087
GEN-2019-051 | 03 CENTRAL | 530587 | WSPRTTP2 | 69 | 5.93 | 5.9026 | 0.0274
GEN-2019-051 | 03 CENTRAL | 530603 | LACROS 3 | 115 | 3.54 | 3.5299 | 0.0101
GEN-2019-051 | 03 CENTRAL | 530608 | NEKOMA 3 | 115 | 3.9676 | 3.9568 | 0.0108
GEN-2019-051 | 03 CENTRAL | 530610 | SHAYS_230 | 230 | 3.4161 | 3.4133 | 0.0028
GEN-2019-051 | 03 CENTRAL | 530624 | ST JOHN3 | 115 | 5.2881 | 5.2725 | 0.0156
GEN-2019-051 | 03 CENTRAL | 532871 | CIRCLE 6 | 230 | 8.4637 | 8.4534 | 0.0103
GEN-2019-051 | 03 CENTRAL | 539010 | SADLHRN3 | 115 | 4.5492 | 4.5408 | 0.0084
GEN-2019-051 | 03 CENTRAL | 539660 | EHALLTP3 | 115 | 3.2328 | 3.2297 | 0.0031
GEN-2019-051 | 03 CENTRAL | 539695 | SPEARVL6 | 230 | 12.772 | 12.7612 | 0.0108
GEN-2019-051 | 03 CENTRAL | 539698 | WALDO 3 | 115 | 2.7316 | 2.729 | 0.0026
GEN-2019-051 | 03 CENTRAL | 763846 | G19-053/055 | 230 | 7.1612 | 7.1474 | 0.0138
GEN-2019-051 | 03 CENTRAL | 763857 | G19-054/068 | 230 | 6.8962 | 6.8623 | 0.0339
GEN-2019-053 | 03 CENTRAL | 763850 | G19-055-TAP | 230 | 7.2471 | 7.0528 | 0.1943
GEN-2019-053 | 03 CENTRAL | 539679 | GRTBEND6 | 230 | 8.7899 | 8.737 | 0.0529
GEN-2019-053 | 03 CENTRAL | 539695 | SPEARVL6 | 230 | 12.772 | 12.6709 | 0.1011
GEN-2019-053 | 03 CENTRAL | 763846 | G19-053/055 | 230 | 7.1612 | 6.9664 | 0.1948
GEN-2019-053 | 03 CENTRAL | 530582 | S HAYS6 | 230 | 8.805 | 8.7844 | 0.0206
GEN-2019-053 | 03 CENTRAL | 530680 | HEIZER 6 | 230 | 8.7324 | 8.6803 | 0.0521
GEN-2019-053 | 03 CENTRAL | 531469 | SPERVIL7 | 345 | 13.6098 | 13.5547 | 0.0551
GEN-2019-053 | 03 CENTRAL | 539117 | SPRVILL-EHVB | 230 | 12.4582 | 12.3625 | 0.0957
GEN-2019-053 | 03 CENTRAL | 539678 | GRTBEND3 | 115 | 12.2449 | 12.2084 | 0.0365
GEN-2019-053 | 03 CENTRAL | 539694 | SPEARVL3 | 115 | 9.9365 | 9.9147 | 0.0218
GEN-2019-053 | 03 CENTRAL | 763862 | G19-054-TAP | 230 | 6.9761 | 6.9521 | 0.024
GEN-2019-053 | 03 CENTRAL | 530553 | S HAYS 3 | 115 | 8.4163 | 8.4089 | 0.0074
GEN-2019-053 | 03 CENTRAL | 530583 | POSTROCK7 | 345 | 7.7231 | 7.7104 | 0.0127
GEN-2019-053 | 03 CENTRAL | 530584 | POSTROCK6 | 230 | 10.7096 | 10.69 | 0.0196
GEN-2019-053 | 03 CENTRAL | 530601 | HEIZER 3 | 115 | 12.1453 | 12.109 | 0.0363
GEN-2019-053 | 03 CENTRAL | 530610 | SHAYS_230 | 230 | 3.4161 | 3.4137 | 0.0024
GEN-2019-053 | 03 CENTRAL | 531501 | BUCKNER7 | 345 | 9.2456 | 9.2323 | 0.0133
GEN-2019-053 | 03 CENTRAL | 532871 | CIRCLE 6 | 230 | 8.4637 | 8.4578 | 0.0059
GEN-2019-053 | 03 CENTRAL | 539642 | ELLSWTP3 | 115 | 3.9126 | 3.9109 | 0.0017
GEN-2019-053 | 03 CENTRAL | 539666 | GBENDTP3 | 115 | 8.7185 | 8.7026 | 0.0159
GEN-2019-053 | 03 CENTRAL | 539681 | N-GBEND3 | 115 | 9.1049 | 9.086 | 0.0189
GEN-2019-053 | 03 CENTRAL | 539684 | OTISSUB3 | 115 | 2.9219 | 2.9198 | 0.0021
GEN-2019-053 | 03 CENTRAL | 539759 | SPRVL 3 | 115 | 12.8273 | 12.8111 | 0.0162
GEN-2019-053 | 03 CENTRAL | 539771 | NFTDODG3 | 115 | 9.7556 | 9.7465 | 0.0091
GEN-2019-053 | 03 CENTRAL | 539800 | CLARKCOUNTY7 | 345 | 12.7785 | 12.7515 | 0.027
GEN-2019-053 | 03 CENTRAL | 539803 | IRONWOOD7 | 345 | 13.1638 | 13.1148 | 0.049
GEN-2019-053 | 03 CENTRAL | 763857 | G19-054/068 | 230 | 6.8962 | 6.8729 | 0.0233
GEN-2019-053 | 03 CENTRAL | 530558 | KNOLL N 6 | 230 | 10.6179 | 10.5986 | 0.0193
GEN-2019-053 | 03 CENTRAL | 530563 | HEIZER 2 | 69 | 8.7188 | 8.7087 | 0.0101
GEN-2019-053 | 03 CENTRAL | 530602 | LAXTAP 3 | 115 | 4.087 | 4.0844 | 0.0026
GEN-2019-053 | 03 CENTRAL | 530609 | HZRNGPL3 | 115 | 7.7647 | 7.7499 | 0.0148
GEN-2019-053 | 03 CENTRAL | 530686 | RICE 6 | 230 | 4.1143 | 4.1131 | 0.0012
GEN-2019-053 | 03 CENTRAL | 530695 | CHETOLAH3 | 115 | 8.3599 | 8.3531 | 0.0068
GEN-2019-053 | 03 CENTRAL | 530702 | BUCKEYE_230 | 230 | 7.8435 | 7.8334 | 0.0101
GEN-2019-053 | 03 CENTRAL | 530714 | ANGUS 3 | 115 | 5.1891 | 5.1863 | 0.0028
GEN-2019-053 | 03 CENTRAL | 530720 | KNOLL S 6 | 230 | 10.6179 | 10.5986 | 0.0193
GEN-2019-053 | 03 CENTRAL | 530725 | PFEIFER 3 | 115 | 3.4004 | 3.3992 | 0.0012
GEN-2019-053 | 03 CENTRAL | 531449 | HOLCOMB7 | 345 | 9.9438 | 9.9373 | 0.0065
GEN-2019-053 | 03 CENTRAL | 531502 | CIMRRN 7 | 345 | 7.3025 | 7.2942 | 0.0083
GEN-2019-053 | 03 CENTRAL | 531504 | CIMWD2 7 | 345 | 7.4234 | 7.415 | 0.0084
GEN-2019-053 | 03 CENTRAL | 532872 | EMCPHER6 | 230 | 7.7208 | 7.718 | 0.0028
GEN-2019-053 | 03 CENTRAL | 533413 | CIRCLE 3 | 115 | 18.3479 | 18.3407 | 0.0072
GEN-2019-053 | 03 CENTRAL | 539643 | ROLLHLS3 | 115 | 3.5855 | 3.5842 | 0.0013
GEN-2019-053 | 03 CENTRAL | 539661 | 24-FREY3 | 115 | 8.1561 | 8.1424 | 0.0137
GEN-2019-053 | 03 CENTRAL | 539671 | FTDODGE3 | 115 | 9.6942 | 9.6852 | 0.009
GEN-2019-053 | 03 CENTRAL | 539688 | S-DODGE3 | 115 | 6.7777 | 6.7735 | 0.0042
GEN-2019-053 | 03 CENTRAL | 539689 | 2ND-KS 3 | 115 | 7.9906 | 7.9774 | 0.0132
GEN-2019-053 | 03 CENTRAL | 539692 | SEWARD 3 | 115 | 5.8179 | 5.8129 | 0.005
GEN-2019-053 | 03 CENTRAL | 539701 | RUSSELL3 | 115 | 3.4282 | 3.427 | 0.0012
GEN-2019-053 | 03 CENTRAL | 539758 | FORD 3 | 115 | 5.204 | 5.202 | 0.002
GEN-2019-053 | 03 CENTRAL | 539801 | THISTLE7 | 345 | 16.6662 | 16.6571 | 0.0091
GEN-2019-053 | 03 CENTRAL | 539813 | TRANSFORMER | 345 | 10.6791 | 10.6605 | 0.0186
GEN-2019-053 | 03 CENTRAL | 539815 | IRONWOOD WF7 | 345 | 11.8843 | 11.8447 | 0.0396
GEN-2019-053 | 03 CENTRAL | 539840 | GEN-2011-008 | 345 | 10.5555 | 10.5378 | 0.0177
GEN-2019-053 | 03 CENTRAL | 560080 | G16-046-TAP | 345 | 11.3684 | 11.3425 | 0.0259
GEN-2019-053 | 03 CENTRAL | 560082 | G16-050-TAP | 345 | 6.9512 | 6.9493 | 0.0019
GEN-2019-053 | 03 CENTRAL | 579480 | GEN-2008-124 | 345 | 12.711 | 12.6655 | 0.0455
GEN-2019-053 | 03 CENTRAL | 763670 | GEN-2019-030 | 345 | 10.4948 | 10.4643 | 0.0305
GEN-2019-053 | 03 CENTRAL | 763758 | GEN-2019-044 | 115 | 6.4739 | 6.4701 | 0.0038
GEN-2019-053 | 03 CENTRAL | 763890 | GEN-2019-058 | 345 | 12.52 | 12.4942 | 0.0258
GEN-2019-053 | 03 CENTRAL | 515852 | DGRASSE7 | 345 | 15.3179 | 15.315 | 0.0029
GEN-2019-053 | 03 CENTRAL | 523853 | FINNEY 7 | 345 | 9.8362 | 9.8299 | 0.0063
GEN-2019-053 | 03 CENTRAL | 530552 | GORHAM 3 | 115 | 3.0814 | 3.0804 | 0.001
GEN-2019-053 | 03 CENTRAL | 530561 | KNOLL 3 | 115 | 10.3394 | 10.3308 | 0.0086
GEN-2019-053 | 03 CENTRAL | 530568 | GB NTH 2 | 69 | 6.7283 | 6.7224 | 0.0059
GEN-2019-053 | 03 CENTRAL | 530586 | ALBERT 2 | 69 | 3.6217 | 3.6202 | 0.0015
GEN-2019-053 | 03 CENTRAL | 530587 | WSPRTTP2 | 69 | 5.93 | 5.9255 | 0.0045
GEN-2019-053 | 03 CENTRAL | 530592 | SMOKYHL6 | 230 | 6.0395 | 6.0378 | 0.0017
GEN-2019-053 | 03 CENTRAL | 530603 | LACROS 3 | 115 | 3.54 | 3.5381 | 0.0019
GEN-2019-053 | 03 CENTRAL | 530608 | NEKOMA 3 | 115 | 3.9676 | 3.9655 | 0.0021
GEN-2019-053 | 03 CENTRAL | 530623 | RICE 3 | 115 | 6.4817 | 6.4802 | 0.0015
GEN-2019-053 | 03 CENTRAL | 530679 | SEWRDMW3 | 115 | 5.1213 | 5.1174 | 0.0039
GEN-2019-053 | 03 CENTRAL | 530688 | BUFLOCRK6 | 230 | 2.7508 | 2.7504 | 0.0004
GEN-2019-053 | 03 CENTRAL | 530693 | VINETAP3 | 115 | 8.4097 | 8.4029 | 0.0068
GEN-2019-053 | 03 CENTRAL | 530722 | VINEDE_S | 115 | 7.7328 | 7.727 | 0.0058
GEN-2019-053 | 03 CENTRAL | 531448 | HOLCOMB3 | 115 | 21.2532 | 21.2494 | 0.0038
GEN-2019-053 | 03 CENTRAL | 531465 | SETAB 7 | 345 | 6.866 | 6.8638 | 0.0022
GEN-2019-053 | 03 CENTRAL | 532782 | BUFFALO7 | 345 | 20.7555 | 20.7511 | 0.0044
GEN-2019-053 | 03 CENTRAL | 532873 | SUMMIT 6 | 230 | 12.899 | 12.8958 | 0.0032
GEN-2019-053 | 03 CENTRAL | 533412 | ARKVALJ3 | 115 | 9.6861 | 9.6838 | 0.0023
GEN-2019-053 | 03 CENTRAL | 533416 | RENO 3 | 115 | 22.1556 | 22.1485 | 0.0071
GEN-2019-053 | 03 CENTRAL | 533417 | EMCPHER3 | 115 | 11.1793 | 11.1766 | 0.0027
GEN-2019-053 | 03 CENTRAL | 533419 | HEC 3 | 115 | 17.1573 | 17.1511 | 0.0062
GEN-2019-053 | 03 CENTRAL | 533421 | HEC GT 3 | 115 | 17.8389 | 17.8321 | 0.0068
GEN-2019-053 | 03 CENTRAL | 539645 | DCBEEF3 | 115 | 6.943 | 6.9384 | 0.0046
GEN-2019-053 | 03 CENTRAL | 539660 | EHALLTP3 | 115 | 3.2328 | 3.232 | 0.0008
GEN-2019-053 | 03 CENTRAL | 539696 | ST-JOHN3 | 115 | 5.2881 | 5.286 | 0.0021
GEN-2019-053 | 03 CENTRAL | 539698 | WALDO 3 | 115 | 2.7316 | 2.731 | 0.0006
GEN-2019-053 | 03 CENTRAL | 539699 | W-DODGE3 | 115 | 4.3105 | 4.309 | 0.0015
GEN-2019-053 | 03 CENTRAL | 539763 | SSTARTP3 | 115 | 4.0742 | 4.0735 | 0.0007
GEN-2019-053 | 03 CENTRAL | 539783 | CRKCK 3 | 115 | 4.65 | 4.649 | 0.001
GEN-2019-053 | 03 CENTRAL | 539804 | THISTLE4 | 138 | 17.5567 | 17.5524 | 0.0043
GEN-2019-053 | 03 CENTRAL | 539841 | G-2011-008-1 | 345 | 10.5555 | 10.5378 | 0.0177
GEN-2019-053 | 03 CENTRAL | 539855 | G-2011-008-2 | 345 | 8.8342 | 8.822 | 0.0122
GEN-2019-053 | 03 CENTRAL | 539857 | G-2011-008-3 | 345 | 8.2708 | 8.2602 | 0.0106
GEN-2019-053 | 03 CENTRAL | 587310 | GEN-2016-046 | 345 | 9.9533 | 9.9338 | 0.0195
GEN-2019-053 | 03 CENTRAL | 587350 | GEN-2016-050 | 345 | 5.8546 | 5.8533 | 0.0013
GEN-2019-053 | 03 CENTRAL | 588630 | GEN-2017-018 | 345 | 16.6662 | 16.6571 | 0.0091
GEN-2019-053 | 03 CENTRAL | 640065 | AXTELL 3 | 345 | 9.208 | 9.2067 | 0.0013
GEN-2019-053 | 03 CENTRAL | 762834 | GEN-2018-049 | 345 | 6.9567 | 6.9552 | 0.0015
GEN-2019-053 | 03 CENTRAL | 763329 | GEN-2018-116 | 115 | 8.1395 | 8.1259 | 0.0136
GEN-2019-054 | 03 CENTRAL | 763862 | G19-054-TAP | 230 | 6.9761 | 6.5811 | 0.395
GEN-2019-054 | 03 CENTRAL | 532871 | CIRCLE 6 | 230 | 8.4637 | 8.3867 | 0.077
GEN-2019-054 | 03 CENTRAL | 539679 | GRTBEND6 | 230 | 8.7899 | 8.5016 | 0.2883
GEN-2019-054 | 03 CENTRAL | 763857 | G19-054/068 | 230 | 6.8962 | 6.5006 | 0.3956
GEN-2019-054 | 03 CENTRAL | 530582 | S HAYS6 | 230 | 8.805 | 8.7155 | 0.0895
GEN-2019-054 | 03 CENTRAL | 530680 | HEIZER 6 | 230 | 8.7324 | 8.4482 | 0.2842
GEN-2019-054 | 03 CENTRAL | 530686 | RICE 6 | 230 | 4.1143 | 4.1005 | 0.0138
GEN-2019-054 | 03 CENTRAL | 532872 | EMCPHER6 | 230 | 7.7208 | 7.6883 | 0.0325
GEN-2019-054 | 03 CENTRAL | 533413 | CIRCLE 3 | 115 | 18.3479 | 18.2684 | 0.0795
GEN-2019-054 | 03 CENTRAL | 539678 | GRTBEND3 | 115 | 12.2449 | 12.0435 | 0.2014
GEN-2019-054 | 03 CENTRAL | 763850 | G19-055-TAP | 230 | 7.2471 | 7.1931 | 0.054
GEN-2019-054 | 03 CENTRAL | 530553 | S HAYS 3 | 115 | 8.4163 | 8.3864 | 0.0299
GEN-2019-054 | 03 CENTRAL | 530584 | POSTROCK6 | 230 | 10.7096 | 10.6412 | 0.0684
GEN-2019-054 | 03 CENTRAL | 530601 | HEIZER 3 | 115 | 12.1453 | 11.9457 | 0.1996
GEN-2019-054 | 03 CENTRAL | 530610 | SHAYS_230 | 230 | 3.4161 | 3.4054 | 0.0107
GEN-2019-054 | 03 CENTRAL | 530623 | RICE 3 | 115 | 6.4817 | 6.4654 | 0.0163
GEN-2019-054 | 03 CENTRAL | 530688 | BUFLOCRK6 | 230 | 2.7508 | 2.7457 | 0.0051
GEN-2019-054 | 03 CENTRAL | 532873 | SUMMIT 6 | 230 | 12.899 | 12.8725 | 0.0265
GEN-2019-054 | 03 CENTRAL | 533412 | ARKVALJ3 | 115 | 9.6861 | 9.6627 | 0.0234
GEN-2019-054 | 03 CENTRAL | 533416 | RENO 3 | 115 | 22.1556 | 22.084 | 0.0716
GEN-2019-054 | 03 CENTRAL | 533417 | EMCPHER3 | 115 | 11.1793 | 11.1492 | 0.0301
GEN-2019-054 | 03 CENTRAL | 533419 | HEC 3 | 115 | 17.1573 | 17.0881 | 0.0692
GEN-2019-054 | 03 CENTRAL | 533421 | HEC GT 3 | 115 | 17.8389 | 17.7637 | 0.0752
GEN-2019-054 | 03 CENTRAL | 539642 | ELLSWTP3 | 115 | 3.9126 | 3.9019 | 0.0107
GEN-2019-054 | 03 CENTRAL | 539666 | GBENDTP3 | 115 | 8.7185 | 8.6306 | 0.0879
GEN-2019-054 | 03 CENTRAL | 539681 | N-GBEND3 | 115 | 9.1049 | 9.0002 | 0.1047
GEN-2019-054 | 03 CENTRAL | 539684 | OTISSUB3 | 115 | 2.9219 | 2.9101 | 0.0118
GEN-2019-054 | 03 CENTRAL | 539695 | SPEARVL6 | 230 | 12.772 | 12.7324 | 0.0396
GEN-2019-054 | 03 CENTRAL | 763846 | G19-053/055 | 230 | 7.1612 | 7.1086 | 0.0526
GEN-2019-054 | 03 CENTRAL | 530558 | KNOLL N 6 | 230 | 10.6179 | 10.5507 | 0.0672
GEN-2019-054 | 03 CENTRAL | 530563 | HEIZER 2 | 69 | 8.7188 | 8.6633 | 0.0555
GEN-2019-054 | 03 CENTRAL | 530583 | POSTROCK7 | 345 | 7.7231 | 7.6919 | 0.0312
GEN-2019-054 | 03 CENTRAL | 530592 | SMOKYHL6 | 230 | 6.0395 | 6.031 | 0.0085
GEN-2019-054 | 03 CENTRAL | 530602 | LAXTAP 3 | 115 | 4.087 | 4.0733 | 0.0137
GEN-2019-054 | 03 CENTRAL | 530609 | HZRNGPL3 | 115 | 7.7647 | 7.6825 | 0.0822
GEN-2019-054 | 03 CENTRAL | 530618 | HUNTSVL3 | 115 | 4.0068 | 4.0017 | 0.0051
GEN-2019-054 | 03 CENTRAL | 530620 | LYONS 3 | 115 | 5.4243 | 5.4152 | 0.0091
GEN-2019-054 | 03 CENTRAL | 530681 | BUSHTON3 | 115 | 4.9177 | 4.9076 | 0.0101
GEN-2019-054 | 03 CENTRAL | 530695 | CHETOLAH3 | 115 | 8.3599 | 8.3327 | 0.0272
GEN-2019-054 | 03 CENTRAL | 530702 | BUCKEYE_230 | 230 | 7.8435 | 7.8083 | 0.0352
GEN-2019-054 | 03 CENTRAL | 530714 | ANGUS 3 | 115 | 5.1891 | 5.1777 | 0.0114
GEN-2019-054 | 03 CENTRAL | 530718 | BUSHTONW 3 | 115 | 4.1338 | 4.1272 | 0.0066
GEN-2019-054 | 03 CENTRAL | 530720 | KNOLL S 6 | 230 | 10.6179 | 10.5507 | 0.0672
GEN-2019-054 | 03 CENTRAL | 530725 | PFEIFER 3 | 115 | 3.4004 | 3.3955 | 0.0049
GEN-2019-054 | 03 CENTRAL | 531469 | SPERVIL7 | 345 | 13.6098 | 13.5761 | 0.0337
GEN-2019-054 | 03 CENTRAL | 532771 | RENO 7 | 345 | 11.0976 | 11.0775 | 0.0201
GEN-2019-054 | 03 CENTRAL | 532773 | SUMMIT 7 | 345 | 10.8577 | 10.8429 | 0.0148
GEN-2019-054 | 03 CENTRAL | 532874 | UNIONRG6 | 230 | 7.9143 | 7.9102 | 0.0041
GEN-2019-054 | 03 CENTRAL | 533381 | SUMMIT 3 | 115 | 17.2114 | 17.1881 | 0.0233
GEN-2019-054 | 03 CENTRAL | 533411 | ARKVAL 3 | 115 | 9.5019 | 9.4794 | 0.0225
GEN-2019-054 | 03 CENTRAL | 533415 | DAVIS 3 | 115 | 8.0324 | 8.0207 | 0.0117
GEN-2019-054 | 03 CENTRAL | 533426 | MANVILE3 | 115 | 8.3015 | 8.2856 | 0.0159
GEN-2019-054 | 03 CENTRAL | 533427 | REFINRY3 | 115 | 10.3372 | 10.3128 | 0.0244
GEN-2019-054 | 03 CENTRAL | 533429 | MOUNDRG3 | 115 | 8.416 | 8.4117 | 0.0043
GEN-2019-054 | 03 CENTRAL | 533438 | WMCPHER3 | 115 | 10.8946 | 10.8688 | 0.0258
GEN-2019-054 | 03 CENTRAL | 533440 | 43LORAN | 115 | 12.2903 | 12.256 | 0.0343
GEN-2019-054 | 03 CENTRAL | 533513 | HEC 2 | 69 | 7.8588 | 7.8501 | 0.0087
GEN-2019-054 | 03 CENTRAL | 539117 | SPRVILL-EHVB | 230 | 12.4582 | 12.4208 | 0.0374
GEN-2019-054 | 03 CENTRAL | 539643 | ROLLHLS3 | 115 | 3.5855 | 3.5769 | 0.0086
GEN-2019-054 | 03 CENTRAL | 539661 | 24-FREY3 | 115 | 8.1561 | 8.08 | 0.0761
GEN-2019-054 | 03 CENTRAL | 539689 | 2ND-KS 3 | 115 | 7.9906 | 7.9172 | 0.0734
GEN-2019-054 | 03 CENTRAL | 539692 | SEWARD 3 | 115 | 5.8179 | 5.7905 | 0.0274
GEN-2019-054 | 03 CENTRAL | 539694 | SPEARVL3 | 115 | 9.9365 | 9.9274 | 0.0091
GEN-2019-054 | 03 CENTRAL | 539701 | RUSSELL3 | 115 | 3.4282 | 3.4207 | 0.0075
GEN-2019-054 | 03 CENTRAL | 530552 | GORHAM 3 | 115 | 3.0814 | 3.0774 | 0.004
GEN-2019-054 | 03 CENTRAL | 530561 | KNOLL 3 | 115 | 10.3394 | 10.3066 | 0.0328
GEN-2019-054 | 03 CENTRAL | 530568 | GB NTH 2 | 69 | 6.7283 | 6.6958 | 0.0325
GEN-2019-054 | 03 CENTRAL | 530586 | ALBERT 2 | 69 | 3.6217 | 3.6134 | 0.0083
GEN-2019-054 | 03 CENTRAL | 530587 | WSPRTTP2 | 69 | 5.93 | 5.9047 | 0.0253
GEN-2019-054 | 03 CENTRAL | 530593 | SMKYP1 6 | 230 | 5.3037 | 5.2974 | 0.0063
GEN-2019-054 | 03 CENTRAL | 530599 | SMKYP2 6 | 230 | 5.5659 | 5.5588 | 0.0071
GEN-2019-054 | 03 CENTRAL | 530603 | LACROS 3 | 115 | 3.54 | 3.5298 | 0.0102
GEN-2019-054 | 03 CENTRAL | 530608 | NEKOMA 3 | 115 | 3.9676 | 3.9568 | 0.0108
GEN-2019-054 | 03 CENTRAL | 530624 | ST JOHN3 | 115 | 5.2881 | 5.2764 | 0.0117
GEN-2019-054 | 03 CENTRAL | 530679 | SEWRDMW3 | 115 | 5.1213 | 5.0997 | 0.0216
GEN-2019-054 | 03 CENTRAL | 530693 | VINETAP3 | 115 | 8.4097 | 8.3828 | 0.0269
GEN-2019-054 | 03 CENTRAL | 530711 | SAXMAN 3 | 115 | 4.4373 | 4.4314 | 0.0059
GEN-2019-054 | 03 CENTRAL | 530722 | VINEDE_S | 115 | 7.7328 | 7.7096 | 0.0232
GEN-2019-054 | 03 CENTRAL | 531501 | BUCKNER7 | 345 | 9.2456 | 9.2367 | 0.0089
GEN-2019-054 | 03 CENTRAL | 532767 | GEARY 7 | 345 | 9.8704 | 9.8657 | 0.0047
GEN-2019-054 | 03 CENTRAL | 532796 | WICHITA7 | 345 | 23.7708 | 23.7549 | 0.0159
GEN-2019-054 | 03 CENTRAL | 532863 | MORRIS 6 | 230 | 13.4941 | 13.4912 | 0.0029
GEN-2019-054 | 03 CENTRAL | 532875 | DVISTA 6 | 230 | 4.6669 | 4.6657 | 0.0012
GEN-2019-054 | 03 CENTRAL | 533013 | MOUND 4 | 138 | 6.8271 | 6.825 | 0.0021
GEN-2019-054 | 03 CENTRAL | 533359 | UNIONRG3 | 115 | 3.6979 | 3.6975 | 0.0004
GEN-2019-054 | 03 CENTRAL | 533371 | NORTHVW3 | 115 | 12.0774 | 12.0675 | 0.0099
GEN-2019-054 | 03 CENTRAL | 533374 | MENTOR 3 | 115 | 12.3397 | 12.3268 | 0.0129
GEN-2019-054 | 03 CENTRAL | 533379 | SO GATE3 | 115 | 10.1975 | 10.1889 | 0.0086
GEN-2019-054 | 03 CENTRAL | 533380 | SPRGCRK3 | 115 | 3.7906 | 3.7901 | 0.0005
GEN-2019-054 | 03 CENTRAL | 533394 | CORONAD3 | 115 | 6.9686 | 6.9617 | 0.0069
GEN-2019-054 | 03 CENTRAL | 533414 | CITIES 3 | 115 | 7.852 | 7.8395 | 0.0125
GEN-2019-054 | 03 CENTRAL | 533428 | MCPHER 3 | 115 | 10.5159 | 10.4913 | 0.0246
GEN-2019-054 | 03 CENTRAL | 533430 | MNDRGCT3 | 115 | 6.4875 | 6.485 | 0.0025
GEN-2019-054 | 03 CENTRAL | 533439 | WHEATLD3 | 115 | 6.7596 | 6.7484 | 0.0112
GEN-2019-054 | 03 CENTRAL | 533455 | TWR 33 3 | 115 | 10.1735 | 10.1508 | 0.0227
GEN-2019-054 | 03 CENTRAL | 533506 | DAVIS 2 | 69 | 7.1642 | 7.1583 | 0.0059
GEN-2019-054 | 03 CENTRAL | 533514 | HEC GT 2 | 69 | 7.6507 | 7.6424 | 0.0083
GEN-2019-054 | 03 CENTRAL | 533521 | 17HALST2 | 69 | 6.2205 | 6.215 | 0.0055
GEN-2019-054 | 03 CENTRAL | 539660 | EHALLTP3 | 115 | 3.2328 | 3.227 | 0.0058
GEN-2019-054 | 03 CENTRAL | 539662 | ELLSWTH3 | 115 | 3.4499 | 3.4439 | 0.006
GEN-2019-054 | 03 CENTRAL | 539696 | ST-JOHN3 | 115 | 5.2881 | 5.2764 | 0.0117
GEN-2019-054 | 03 CENTRAL | 539698 | WALDO 3 | 115 | 2.7316 | 2.728 | 0.0036
GEN-2019-054 | 03 CENTRAL | 539759 | SPRVL 3 | 115 | 12.8273 | 12.8178 | 0.0095
GEN-2019-054 | 03 CENTRAL | 539771 | NFTDODG3 | 115 | 9.7556 | 9.7509 | 0.0047
GEN-2019-054 | 03 CENTRAL | 539800 | CLARKCOUNTY7 | 345 | 12.7785 | 12.7604 | 0.0181
GEN-2019-054 | 03 CENTRAL | 539803 | IRONWOOD7 | 345 | 13.1638 | 13.1337 | 0.0301
GEN-2019-054 | 03 CENTRAL | 560082 | G16-050-TAP | 345 | 6.9512 | 6.9466 | 0.0046
GEN-2019-054 | 03 CENTRAL | 587884 | G16-111-TAP | 345 | 9.7651 | 9.7515 | 0.0136
GEN-2019-054 | 03 CENTRAL | 588494 | G17-004-TAP | 345 | 9.3029 | 9.2927 | 0.0102
GEN-2019-054 | 03 CENTRAL | 763329 | GEN-2018-116 | 115 | 8.1395 | 8.0638 | 0.0757
GEN-2019-055 | 03 CENTRAL | 763850 | G19-055-TAP | 230 | 7.2471 | 6.8579 | 0.3892
GEN-2019-055 | 03 CENTRAL | 539679 | GRTBEND6 | 230 | 8.7899 | 8.6817 | 0.1082
GEN-2019-055 | 03 CENTRAL | 539695 | SPEARVL6 | 230 | 12.772 | 12.5656 | 0.2064
GEN-2019-055 | 03 CENTRAL | 763846 | G19-053/055 | 230 | 7.1612 | 6.7713 | 0.3899
GEN-2019-055 | 03 CENTRAL | 530582 | S HAYS6 | 230 | 8.805 | 8.7626 | 0.0424
GEN-2019-055 | 03 CENTRAL | 530680 | HEIZER 6 | 230 | 8.7324 | 8.6258 | 0.1066
GEN-2019-055 | 03 CENTRAL | 531469 | SPERVIL7 | 345 | 13.6098 | 13.4969 | 0.1129
GEN-2019-055 | 03 CENTRAL | 539117 | SPRVILL-EHVB | 230 | 12.4582 | 12.2628 | 0.1954
GEN-2019-055 | 03 CENTRAL | 539678 | GRTBEND3 | 115 | 12.2449 | 12.1699 | 0.075
GEN-2019-055 | 03 CENTRAL | 539694 | SPEARVL3 | 115 | 9.9365 | 9.8918 | 0.0447
GEN-2019-055 | 03 CENTRAL | 763862 | G19-054-TAP | 230 | 6.9761 | 6.9269 | 0.0492
GEN-2019-055 | 03 CENTRAL | 530553 | S HAYS 3 | 115 | 8.4163 | 8.4012 | 0.0151
GEN-2019-055 | 03 CENTRAL | 530583 | POSTROCK7 | 345 | 7.7231 | 7.697 | 0.0261
GEN-2019-055 | 03 CENTRAL | 530584 | POSTROCK6 | 230 | 10.7096 | 10.6692 | 0.0404
GEN-2019-055 | 03 CENTRAL | 530601 | HEIZER 3 | 115 | 12.1453 | 12.0708 | 0.0745
GEN-2019-055 | 03 CENTRAL | 530610 | SHAYS_230 | 230 | 3.4161 | 3.411 | 0.0051
GEN-2019-055 | 03 CENTRAL | 531501 | BUCKNER7 | 345 | 9.2456 | 9.2183 | 0.0273
GEN-2019-055 | 03 CENTRAL | 532871 | CIRCLE 6 | 230 | 8.4637 | 8.4516 | 0.0121
GEN-2019-055 | 03 CENTRAL | 539642 | ELLSWTP3 | 115 | 3.9126 | 3.9091 | 0.0035
GEN-2019-055 | 03 CENTRAL | 539666 | GBENDTP3 | 115 | 8.7185 | 8.6859 | 0.0326
GEN-2019-055 | 03 CENTRAL | 539681 | N-GBEND3 | 115 | 9.1049 | 9.0661 | 0.0388
GEN-2019-055 | 03 CENTRAL | 539684 | OTISSUB3 | 115 | 2.9219 | 2.9176 | 0.0043
GEN-2019-055 | 03 CENTRAL | 539759 | SPRVL 3 | 115 | 12.8273 | 12.794 | 0.0333
GEN-2019-055 | 03 CENTRAL | 539771 | NFTDODG3 | 115 | 9.7556 | 9.7368 | 0.0188
GEN-2019-055 | 03 CENTRAL | 539800 | CLARKCOUNTY7 | 345 | 12.7785 | 12.7231 | 0.0554
GEN-2019-055 | 03 CENTRAL | 539803 | IRONWOOD7 | 345 | 13.1638 | 13.0634 | 0.1004
GEN-2019-055 | 03 CENTRAL | 763857 | G19-054/068 | 230 | 6.8962 | 6.8483 | 0.0479
GEN-2019-055 | 03 CENTRAL | 530558 | KNOLL N 6 | 230 | 10.6179 | 10.5783 | 0.0396
GEN-2019-055 | 03 CENTRAL | 530563 | HEIZER 2 | 69 | 8.7188 | 8.6981 | 0.0207
GEN-2019-055 | 03 CENTRAL | 530602 | LAXTAP 3 | 115 | 4.087 | 4.0816 | 0.0054
GEN-2019-055 | 03 CENTRAL | 530609 | HZRNGPL3 | 115 | 7.7647 | 7.7342 | 0.0305
GEN-2019-055 | 03 CENTRAL | 530686 | RICE 6 | 230 | 4.1143 | 4.1119 | 0.0024
GEN-2019-055 | 03 CENTRAL | 530695 | CHETOLAH3 | 115 | 8.3599 | 8.3459 | 0.014
GEN-2019-055 | 03 CENTRAL | 530702 | BUCKEYE_230 | 230 | 7.8435 | 7.8228 | 0.0207
GEN-2019-055 | 03 CENTRAL | 530714 | ANGUS 3 | 115 | 5.1891 | 5.1834 | 0.0057
GEN-2019-055 | 03 CENTRAL | 530720 | KNOLL S 6 | 230 | 10.6179 | 10.5783 | 0.0396
GEN-2019-055 | 03 CENTRAL | 530725 | PFEIFER 3 | 115 | 3.4004 | 3.3979 | 0.0025
GEN-2019-055 | 03 CENTRAL | 531449 | HOLCOMB7 | 345 | 9.9438 | 9.9305 | 0.0133
GEN-2019-055 | 03 CENTRAL | 531502 | CIMRRN 7 | 345 | 7.3025 | 7.2854 | 0.0171
GEN-2019-055 | 03 CENTRAL | 531504 | CIMWD2 7 | 345 | 7.4234 | 7.4061 | 0.0173
GEN-2019-055 | 03 CENTRAL | 532872 | EMCPHER6 | 230 | 7.7208 | 7.7151 | 0.0057
GEN-2019-055 | 03 CENTRAL | 533413 | CIRCLE 3 | 115 | 18.3479 | 18.3331 | 0.0148
GEN-2019-055 | 03 CENTRAL | 539643 | ROLLHLS3 | 115 | 3.5855 | 3.5828 | 0.0027
GEN-2019-055 | 03 CENTRAL | 539661 | 24-FREY3 | 115 | 8.1561 | 8.1279 | 0.0282
GEN-2019-055 | 03 CENTRAL | 539671 | FTDODGE3 | 115 | 9.6942 | 9.6757 | 0.0185
GEN-2019-055 | 03 CENTRAL | 539688 | S-DODGE3 | 115 | 6.7777 | 6.7691 | 0.0086
GEN-2019-055 | 03 CENTRAL | 539689 | 2ND-KS 3 | 115 | 7.9906 | 7.9634 | 0.0272
GEN-2019-055 | 03 CENTRAL | 539692 | SEWARD 3 | 115 | 5.8179 | 5.8077 | 0.0102
GEN-2019-055 | 03 CENTRAL | 539701 | RUSSELL3 | 115 | 3.4282 | 3.4258 | 0.0024
GEN-2019-055 | 03 CENTRAL | 539758 | FORD 3 | 115 | 5.204 | 5.1999 | 0.0041
GEN-2019-055 | 03 CENTRAL | 539801 | THISTLE7 | 345 | 16.6662 | 16.6475 | 0.0187
GEN-2019-055 | 03 CENTRAL | 539813 | TRANSFORMER | 345 | 10.6791 | 10.6408 | 0.0383
GEN-2019-055 | 03 CENTRAL | 539815 | IRONWOOD WF7 | 345 | 11.8843 | 11.803 | 0.0813
GEN-2019-055 | 03 CENTRAL | 539840 | GEN-2011-008 | 345 | 10.5555 | 10.5192 | 0.0363
GEN-2019-055 | 03 CENTRAL | 560080 | G16-046-TAP | 345 | 11.3684 | 11.3152 | 0.0532
GEN-2019-055 | 03 CENTRAL | 560082 | G16-050-TAP | 345 | 6.9512 | 6.9473 | 0.0039
GEN-2019-055 | 03 CENTRAL | 579480 | GEN-2008-124 | 345 | 12.711 | 12.6175 | 0.0935
GEN-2019-055 | 03 CENTRAL | 763670 | GEN-2019-030 | 345 | 10.4948 | 10.4322 | 0.0626
GEN-2019-055 | 03 CENTRAL | 763758 | GEN-2019-044 | 115 | 6.4739 | 6.4661 | 0.0078
GEN-2019-055 | 03 CENTRAL | 763890 | GEN-2019-058 | 345 | 12.52 | 12.4669 | 0.0531
GEN-2019-055 | 03 CENTRAL | 515852 | DGRASSE7 | 345 | 15.3179 | 15.312 | 0.0059
GEN-2019-055 | 03 CENTRAL | 523853 | FINNEY 7 | 345 | 9.8362 | 9.8233 | 0.0129
GEN-2019-055 | 03 CENTRAL | 530552 | GORHAM 3 | 115 | 3.0814 | 3.0794 | 0.002
GEN-2019-055 | 03 CENTRAL | 530561 | KNOLL 3 | 115 | 10.3394 | 10.3216 | 0.0178
GEN-2019-055 | 03 CENTRAL | 530568 | GB NTH 2 | 69 | 6.7283 | 6.7162 | 0.0121
GEN-2019-055 | 03 CENTRAL | 530586 | ALBERT 2 | 69 | 3.6217 | 3.6186 | 0.0031
GEN-2019-055 | 03 CENTRAL | 530587 | WSPRTTP2 | 69 | 5.93 | 5.9207 | 0.0093
GEN-2019-055 | 03 CENTRAL | 530592 | SMOKYHL6 | 230 | 6.0395 | 6.036 | 0.0035
GEN-2019-055 | 03 CENTRAL | 530603 | LACROS 3 | 115 | 3.54 | 3.536 | 0.004
GEN-2019-055 | 03 CENTRAL | 530608 | NEKOMA 3 | 115 | 3.9676 | 3.9633 | 0.0043
GEN-2019-055 | 03 CENTRAL | 530623 | RICE 3 | 115 | 6.4817 | 6.4785 | 0.0032
GEN-2019-055 | 03 CENTRAL | 530679 | SEWRDMW3 | 115 | 5.1213 | 5.1133 | 0.008
GEN-2019-055 | 03 CENTRAL | 530688 | BUFLOCRK6 | 230 | 2.7508 | 2.7499 | 0.0009
GEN-2019-055 | 03 CENTRAL | 530693 | VINETAP3 | 115 | 8.4097 | 8.3958 | 0.0139
GEN-2019-055 | 03 CENTRAL | 530722 | VINEDE_S | 115 | 7.7328 | 7.7209 | 0.0119
GEN-2019-055 | 03 CENTRAL | 531448 | HOLCOMB3 | 115 | 21.2532 | 21.2454 | 0.0078
GEN-2019-055 | 03 CENTRAL | 531465 | SETAB 7 | 345 | 6.866 | 6.8613 | 0.0047
GEN-2019-055 | 03 CENTRAL | 532782 | BUFFALO7 | 345 | 20.7555 | 20.7465 | 0.009
GEN-2019-055 | 03 CENTRAL | 532873 | SUMMIT 6 | 230 | 12.899 | 12.8925 | 0.0065
GEN-2019-055 | 03 CENTRAL | 533412 | ARKVALJ3 | 115 | 9.6861 | 9.6814 | 0.0047
GEN-2019-055 | 03 CENTRAL | 533416 | RENO 3 | 115 | 22.1556 | 22.1411 | 0.0145
GEN-2019-055 | 03 CENTRAL | 533417 | EMCPHER3 | 115 | 11.1793 | 11.1738 | 0.0055
GEN-2019-055 | 03 CENTRAL | 533419 | HEC 3 | 115 | 17.1573 | 17.1444 | 0.0129
GEN-2019-055 | 03 CENTRAL | 533421 | HEC GT 3 | 115 | 17.8389 | 17.8249 | 0.014
GEN-2019-055 | 03 CENTRAL | 539645 | DCBEEF3 | 115 | 6.943 | 6.9335 | 0.0095
GEN-2019-055 | 03 CENTRAL | 539660 | EHALLTP3 | 115 | 3.2328 | 3.2312 | 0.0016
GEN-2019-055 | 03 CENTRAL | 539696 | ST-JOHN3 | 115 | 5.2881 | 5.2837 | 0.0044
GEN-2019-055 | 03 CENTRAL | 539698 | WALDO 3 | 115 | 2.7316 | 2.7304 | 0.0012
GEN-2019-055 | 03 CENTRAL | 539699 | W-DODGE3 | 115 | 4.3105 | 4.3074 | 0.0031
GEN-2019-055 | 03 CENTRAL | 539763 | SSTARTP3 | 115 | 4.0742 | 4.0727 | 0.0015
GEN-2019-055 | 03 CENTRAL | 539783 | CRKCK 3 | 115 | 4.65 | 4.648 | 0.002
GEN-2019-055 | 03 CENTRAL | 539804 | THISTLE4 | 138 | 17.5567 | 17.5479 | 0.0088
GEN-2019-055 | 03 CENTRAL | 539841 | G-2011-008-1 | 345 | 10.5555 | 10.5192 | 0.0363
GEN-2019-055 | 03 CENTRAL | 539855 | G-2011-008-2 | 345 | 8.8342 | 8.8091 | 0.0251
GEN-2019-055 | 03 CENTRAL | 539857 | G-2011-008-3 | 345 | 8.2708 | 8.249 | 0.0218
GEN-2019-055 | 03 CENTRAL | 587310 | GEN-2016-046 | 345 | 9.9533 | 9.9132 | 0.0401
GEN-2019-055 | 03 CENTRAL | 587350 | GEN-2016-050 | 345 | 5.8546 | 5.8519 | 0.0027
GEN-2019-055 | 03 CENTRAL | 588630 | GEN-2017-018 | 345 | 16.6662 | 16.6475 | 0.0187
GEN-2019-055 | 03 CENTRAL | 640065 | AXTELL 3 | 345 | 9.208 | 9.2053 | 0.0027
GEN-2019-055 | 03 CENTRAL | 762834 | GEN-2018-049 | 345 | 6.9567 | 6.9536 | 0.0031
GEN-2019-055 | 03 CENTRAL | 763329 | GEN-2018-116 | 115 | 8.1395 | 8.1115 | 0.028
GEN-2019-058 | 03 CENTRAL | 539800 | CLARKCOUNTY7 | 345 | 12.7785 | 12.5256 | 0.2529
GEN-2019-058 | 03 CENTRAL | 531469 | SPERVIL7 | 345 | 13.6098 | 13.472 | 0.1378
GEN-2019-058 | 03 CENTRAL | 539801 | THISTLE7 | 345 | 16.6662 | 16.6 | 0.0662
GEN-2019-058 | 03 CENTRAL | 539813 | TRANSFORMER | 345 | 10.6791 | 10.5037 | 0.1754
GEN-2019-058 | 03 CENTRAL | 539840 | GEN-2011-008 | 345 | 10.5555 | 10.3892 | 0.1663
GEN-2019-058 | 03 CENTRAL | 560080 | G16-046-TAP | 345 | 11.3684 | 11.2145 | 0.1539
GEN-2019-058 | 03 CENTRAL | 763890 | GEN-2019-058 | 345 | 12.52 | 12.267 | 0.253
GEN-2019-058 | 03 CENTRAL | 515852 | DGRASSE7 | 345 | 15.3179 | 15.298 | 0.0199
GEN-2019-058 | 03 CENTRAL | 530583 | POSTROCK7 | 345 | 7.7231 | 7.7105 | 0.0126
GEN-2019-058 | 03 CENTRAL | 531501 | BUCKNER7 | 345 | 9.2456 | 9.2132 | 0.0324
GEN-2019-058 | 03 CENTRAL | 532782 | BUFFALO7 | 345 | 20.7555 | 20.7357 | 0.0198
GEN-2019-058 | 03 CENTRAL | 539695 | SPEARVL6 | 230 | 12.772 | 12.7125 | 0.0595
GEN-2019-058 | 03 CENTRAL | 539759 | SPRVL 3 | 115 | 12.8273 | 12.7931 | 0.0342
GEN-2019-058 | 03 CENTRAL | 539803 | IRONWOOD7 | 345 | 13.1638 | 13.0303 | 0.1335
GEN-2019-058 | 03 CENTRAL | 539804 | THISTLE4 | 138 | 17.5567 | 17.5327 | 0.024
GEN-2019-058 | 03 CENTRAL | 539841 | G-2011-008-1 | 345 | 10.5555 | 10.3892 | 0.1663
GEN-2019-058 | 03 CENTRAL | 539855 | G-2011-008-2 | 345 | 8.8342 | 8.7189 | 0.1153
GEN-2019-058 | 03 CENTRAL | 539857 | G-2011-008-3 | 345 | 8.2708 | 8.1706 | 0.1002
GEN-2019-058 | 03 CENTRAL | 587310 | GEN-2016-046 | 345 | 9.9533 | 9.8371 | 0.1162
GEN-2019-058 | 03 CENTRAL | 588630 | GEN-2017-018 | 345 | 16.6662 | 16.6 | 0.0662
GEN-2019-058 | 03 CENTRAL | 762834 | GEN-2018-049 | 345 | 6.9567 | 6.9456 | 0.0111
GEN-2019-058 | 03 CENTRAL | 515375 | WWRDEHV7 | 345 | 22.3641 | 22.3541 | 0.01
GEN-2019-058 | 03 CENTRAL | 515853 | DGRASSE4 | 138 | 17.0745 | 17.0696 | 0.0049
GEN-2019-058 | 03 CENTRAL | 530584 | POSTROCK6 | 230 | 10.7096 | 10.6979 | 0.0117
GEN-2019-058 | 03 CENTRAL | 531449 | HOLCOMB7 | 345 | 9.9438 | 9.9291 | 0.0147
GEN-2019-058 | 03 CENTRAL | 531502 | CIMRRN 7 | 345 | 7.3025 | 7.2823 | 0.0202
GEN-2019-058 | 03 CENTRAL | 531504 | CIMWD2 7 | 345 | 7.4234 | 7.4029 | 0.0205
GEN-2019-058 | 03 CENTRAL | 532783 | KINGMAN7 | 345 | 7.0277 | 7.026 | 0.0017
GEN-2019-058 | 03 CENTRAL | 532796 | WICHITA7 | 345 | 23.7708 | 23.7535 | 0.0173
GEN-2019-058 | 03 CENTRAL | 539117 | SPRVILL-EHVB | 230 | 12.4582 | 12.4019 | 0.0563
GEN-2019-058 | 03 CENTRAL | 539638 | FLATRDG4 | 138 | 15.5636 | 15.546 | 0.0176
GEN-2019-058 | 03 CENTRAL | 539694 | SPEARVL3 | 115 | 9.9365 | 9.921 | 0.0155
GEN-2019-058 | 03 CENTRAL | 539771 | NFTDODG3 | 115 | 9.7556 | 9.7446 | 0.011
GEN-2019-058 | 03 CENTRAL | 539815 | IRONWOOD WF7 | 345 | 11.8843 | 11.7762 | 0.1081
GEN-2019-058 | 03 CENTRAL | 560082 | G16-050-TAP | 345 | 6.9512 | 6.9493 | 0.0019
GEN-2019-058 | 03 CENTRAL | 579480 | GEN-2008-124 | 345 | 12.711 | 12.5868 | 0.1242
GEN-2019-058 | 03 CENTRAL | 587311 | G16-046XFMR1 | 115 | 14.7707 | 14.6979 | 0.0728
GEN-2019-058 | 03 CENTRAL | 587500 | GEN-2016-073 | 345 | 15.2224 | 15.212 | 0.0104
GEN-2019-058 | 03 CENTRAL | 760284 | GEN-2017-220 | 345 | 20.642 | 20.6225 | 0.0195
GEN-2019-058 | 03 CENTRAL | 763670 | GEN-2019-030 | 345 | 10.4948 | 10.4116 | 0.0832
GEN-2019-058 | 03 CENTRAL | 763850 | G19-055-TAP | 230 | 7.2471 | 7.236 | 0.0111
GEN-2019-058 | 03 CENTRAL | 514795 | KNOBHIL4 | 138 | 10.2855 | 10.284 | 0.0015
GEN-2019-058 | 03 CENTRAL | 515376 | WWRDEHV4 | 138 | 24.8769 | 24.8732 | 0.0037
GEN-2019-058 | 03 CENTRAL | 515407 | TATONGA7 | 345 | 17.5658 | 17.5634 | 0.0024
GEN-2019-058 | 03 CENTRAL | 515554 | BVRCNTY7 | 345 | 15.3093 | 15.3062 | 0.0031
GEN-2019-058 | 03 CENTRAL | 515599 | G07621119-20 | 345 | 13.4849 | 13.4814 | 0.0035
GEN-2019-058 | 03 CENTRAL | 515961 | GUTHRIE7 | 345 | 12.8816 | 12.8782 | 0.0034
GEN-2019-058 | 03 CENTRAL | 516106 | BOBCAT 7 | 345 | 15.796 | 15.7918 | 0.0042
GEN-2019-058 | 03 CENTRAL | 520436 | ROSEVLY4 | 138 | 12.3574 | 12.3549 | 0.0025
GEN-2019-058 | 03 CENTRAL | 520999 | MOORLND4 | 138 | 20.0616 | 20.061 | 0.0006
GEN-2019-058 | 03 CENTRAL | 523853 | FINNEY 7 | 345 | 9.8362 | 9.8219 | 0.0143
GEN-2019-058 | 03 CENTRAL | 530558 | KNOLL N 6 | 230 | 10.6179 | 10.6064 | 0.0115
GEN-2019-058 | 03 CENTRAL | 530582 | S HAYS6 | 230 | 8.805 | 8.7978 | 0.0072
GEN-2019-058 | 03 CENTRAL | 530702 | BUCKEYE_230 | 230 | 7.8435 | 7.8375 | 0.006
GEN-2019-058 | 03 CENTRAL | 530720 | KNOLL S 6 | 230 | 10.6179 | 10.6064 | 0.0115
GEN-2019-058 | 03 CENTRAL | 531448 | HOLCOMB3 | 115 | 21.2532 | 21.2451 | 0.0081
GEN-2019-058 | 03 CENTRAL | 531465 | SETAB 7 | 345 | 6.866 | 6.8615 | 0.0045
GEN-2019-058 | 03 CENTRAL | 532771 | RENO 7 | 345 | 11.0976 | 11.0949 | 0.0027
GEN-2019-058 | 03 CENTRAL | 532784 | NINN1WF7 | 345 | 5.8368 | 5.8358 | 0.001
GEN-2019-058 | 03 CENTRAL | 532791 | BENTON 7 | 345 | 19.0077 | 19.0026 | 0.0051
GEN-2019-058 | 03 CENTRAL | 532798 | VIOLA 7 | 345 | 14.0837 | 14.0806 | 0.0031
GEN-2019-058 | 03 CENTRAL | 533040 | EVANS N4 | 138 | 32.3573 | 32.349 | 0.0083
GEN-2019-058 | 03 CENTRAL | 539631 | FLATRWD4 | 138 | 10.3815 | 10.3739 | 0.0076
GEN-2019-058 | 03 CENTRAL | 539668 | HARPER 4 | 138 | 7.2122 | 7.2106 | 0.0016
GEN-2019-058 | 03 CENTRAL | 539671 | FTDODGE3 | 115 | 9.6942 | 9.6834 | 0.0108
GEN-2019-058 | 03 CENTRAL | 539674 | BARBER 4 | 138 | 8.2322 | 8.2275 | 0.0047
GEN-2019-058 | 03 CENTRAL | 539679 | GRTBEND6 | 230 | 8.7899 | 8.7831 | 0.0068
GEN-2019-058 | 03 CENTRAL | 539688 | S-DODGE3 | 115 | 6.7777 | 6.7727 | 0.005
GEN-2019-058 | 03 CENTRAL | 539758 | FORD 3 | 115 | 5.204 | 5.2015 | 0.0025
GEN-2019-058 | 03 CENTRAL | 562476 | G14-001-TAP | 345 | 10.3737 | 10.372 | 0.0017
GEN-2019-058 | 03 CENTRAL | 585300 | GEN-2015-095 | 138 | 16.8692 | 16.8644 | 0.0048
GEN-2019-058 | 03 CENTRAL | 587350 | GEN-2016-050 | 345 | 5.8546 | 5.8533 | 0.0013
GEN-2019-058 | 03 CENTRAL | 640065 | AXTELL 3 | 345 | 9.208 | 9.2067 | 0.0013
GEN-2019-058 | 03 CENTRAL | 755000 | WWDBORDT | 345 | 12.2648 | 12.2642 | 0.0006
GEN-2019-058 | 03 CENTRAL | 763527 | GEN-2019-012 | 345 | 19.3711 | 19.3636 | 0.0075
GEN-2019-058 | 03 CENTRAL | 763758 | GEN-2019-044 | 115 | 6.4739 | 6.4693 | 0.0046
GEN-2019-058 | 03 CENTRAL | 763769 | GEN-2019-045 | 138 | 17.0745 | 17.0696 | 0.0049
GEN-2019-058 | 03 CENTRAL | 763846 | G19-053/055 | 230 | 7.1612 | 7.1503 | 0.0109
GEN-2019-058 | 03 CENTRAL | 511553 | CHISHOLM7 | 345 | 12.3397 | 12.3392 | 0.0005
GEN-2019-058 | 03 CENTRAL | 514785 | WOODWRD4 | 138 | 13.1123 | 13.1117 | 0.0006
GEN-2019-058 | 03 CENTRAL | 514788 | GLASMTN4 | 138 | 5.1117 | 5.1116 | 0.0001
GEN-2019-058 | 03 CENTRAL | 514794 | KNOBHIL2 | 69 | 8.8727 | 8.8723 | 0.0004
GEN-2019-058 | 03 CENTRAL | 514796 | IODINE-4 | 138 | 7.3201 | 7.3199 | 0.0002
GEN-2019-058 | 03 CENTRAL | 515394 | KEENAN 4 | 138 | 8.9414 | 8.9409 | 0.0005
GEN-2019-058 | 03 CENTRAL | 515398 | OUSPRT 4 | 138 | 9.528 | 9.5275 | 0.0005
GEN-2019-058 | 03 CENTRAL | 515425 | WWDPST 4 | 138 | 17.7977 | 17.7961 | 0.0016
GEN-2019-058 | 03 CENTRAL | 515448 | CRSRDSW7 | 345 | 12.1468 | 12.1456 | 0.0012
GEN-2019-058 | 03 CENTRAL | 515458 | BORDER 7 | 345 | 8.2517 | 8.2515 | 0.0002
GEN-2019-058 | 03 CENTRAL | 515497 | MATHWSN7 | 345 | 32.7952 | 32.7937 | 0.0015
GEN-2019-058 | 03 CENTRAL | 515582 | SLNGWND7 | 345 | 8.4766 | 8.4761 | 0.0005
GEN-2019-058 | 03 CENTRAL | 515585 | MAMTHPW7 | 345 | 13.5669 | 13.5655 | 0.0014
GEN-2019-058 | 03 CENTRAL | 515590 | PALDR2W7 | 345 | 12.8669 | 12.8647 | 0.0022
GEN-2019-058 | 03 CENTRAL | 515618 | BALKOW 7 | 345 | 12.5807 | 12.5786 | 0.0021
GEN-2019-058 | 03 CENTRAL | 515677 | BADGER 7 | 345 | 13.7821 | 13.7795 | 0.0026
GEN-2019-058 | 03 CENTRAL | 515785 | WINDFRM4 | 138 | 19.5945 | 19.5939 | 0.0006
GEN-2019-058 | 03 CENTRAL | 515825 | GRTWSRN7 | 345 | 9.0702 | 9.0686 | 0.0016
GEN-2019-058 | 03 CENTRAL | 515951 | PERSIMN7 | 345 | 11.0796 | 11.0771 | 0.0025
GEN-2019-058 | 03 CENTRAL | 516146 | 25MILE 7 | 345 | 11.1221 | 11.1202 | 0.0019
GEN-2019-058 | 03 CENTRAL | 520425 | PIC4 | 138 | 7.9856 | 7.9856 | 0
GEN-2019-058 | 03 CENTRAL | 520430 | NOELSW 4 | 138 | 10.3556 | 10.3541 | 0.0015
GEN-2019-058 | 03 CENTRAL | 520462 | ASPEN 4 | 138 | 19.3561 | 19.3555 | 0.0006
GEN-2019-058 | 03 CENTRAL | 520553 | SEILING4 | 138 | 6.6101 | 6.61 | 0.0001
GEN-2019-058 | 03 CENTRAL | 520601 | AVARD 4 | 138 | 6.857 | 6.8563 | 0.0007
GEN-2019-058 | 03 CENTRAL | 520957 | IODINE 4 | 138 | 7.673 | 7.6729 | 0.0001
GEN-2019-058 | 03 CENTRAL | 520995 | MOORLND2 | 69 | 8.5299 | 8.5299 | 0
GEN-2019-058 | 03 CENTRAL | 523097 | HITCHLAND 7 | 345 | 14.9713 | 14.9685 | 0.0028
GEN-2019-058 | 03 CENTRAL | 523118 | BUFF_DUNES 7 | 345 | 6.0272 | 6.0221 | 0.0051
GEN-2019-058 | 03 CENTRAL | 523823 | CARPENTER 7 | 345 | 6.5781 | 6.5759 | 0.0022
GEN-2019-058 | 03 CENTRAL | 530553 | S HAYS 3 | 115 | 8.4163 | 8.4132 | 0.0031
GEN-2019-058 | 03 CENTRAL | 530561 | KNOLL 3 | 115 | 10.3394 | 10.335 | 0.0044
GEN-2019-058 | 03 CENTRAL | 530592 | SMOKYHL6 | 230 | 6.0395 | 6.0385 | 0.001
GEN-2019-058 | 03 CENTRAL | 530610 | SHAYS_230 | 230 | 3.4161 | 3.4153 | 0.0008
GEN-2019-058 | 03 CENTRAL | 530680 | HEIZER 6 | 230 | 8.7324 | 8.7257 | 0.0067
GEN-2019-058 | 03 CENTRAL | 531379 | JONES3 | 115 | 10.6043 | 10.6024 | 0.0019
GEN-2019-058 | 03 CENTRAL | 531393 | PLYMELL3 | 115 | 7.6981 | 7.6972 | 0.0009
GEN-2019-058 | 03 CENTRAL | 531420 | FLETCHR3 | 115 | 6.7619 | 6.7611 | 0.0008
GEN-2019-058 | 03 CENTRAL | 531445 | GRDNCTY3 | 115 | 12.5516 | 12.5494 | 0.0022
GEN-2019-058 | 03 CENTRAL | 531451 | MINGO 7 | 345 | 6.0094 | 6.0077 | 0.0017
GEN-2019-058 | 03 CENTRAL | 531464 | SETAB 3 | 115 | 10.1837 | 10.181 | 0.0027
GEN-2019-058 | 03 CENTRAL | 532768 | EMPEC 7 | 345 | 16.1367 | 16.136 | 0.0007
GEN-2019-058 | 03 CENTRAL | 532785 | PRATTWF7 | 345 | 4.8525 | 4.8518 | 0.0007
GEN-2019-058 | 03 CENTRAL | 532794 | ROSEHIL7 | 345 | 18.8487 | 18.8458 | 0.0029
GEN-2019-058 | 03 CENTRAL | 532797 | WOLFCRK7 | 345 | 20.9355 | 20.9349 | 0.0006
GEN-2019-058 | 03 CENTRAL | 532986 | BENTON 4 | 138 | 27.7644 | 27.7602 | 0.0042
GEN-2019-058 | 03 CENTRAL | 533041 | EVANS S4 | 138 | 32.2762 | 32.2679 | 0.0083
GEN-2019-058 | 03 CENTRAL | 533054 | MAIZE 4 | 138 | 20.7931 | 20.79 | 0.0031
GEN-2019-058 | 03 CENTRAL | 533065 | SG12COL4 | 138 | 19.3466 | 19.3437 | 0.0029
GEN-2019-058 | 03 CENTRAL | 533075 | VIOLA 4 | 138 | 24.178 | 24.1736 | 0.0044
GEN-2019-058 | 03 CENTRAL | 533416 | RENO 3 | 115 | 22.1556 | 22.1514 | 0.0042
GEN-2019-058 | 03 CENTRAL | 539000 | RAGO 4 | 138 | 3.9467 | 3.9462 | 0.0005
GEN-2019-058 | 03 CENTRAL | 539001 | ANTHONY4 | 138 | 5.012 | 5.0114 | 0.0006
GEN-2019-058 | 03 CENTRAL | 539645 | DCBEEF3 | 115 | 6.943 | 6.9374 | 0.0056
GEN-2019-058 | 03 CENTRAL | 539675 | MILANTP4 | 138 | 9.9006 | 9.8995 | 0.0011
GEN-2019-058 | 03 CENTRAL | 539678 | GRTBEND3 | 115 | 12.2449 | 12.2396 | 0.0053
GEN-2019-058 | 03 CENTRAL | 539699 | W-DODGE3 | 115 | 4.3105 | 4.3087 | 0.0018
GEN-2019-058 | 03 CENTRAL | 539760 | BARBER 3 | 115 | 8.1332 | 8.1296 | 0.0036
GEN-2019-058 | 03 CENTRAL | 539763 | SSTARTP3 | 115 | 4.0742 | 4.0731 | 0.0011
GEN-2019-058 | 03 CENTRAL | 539783 | CRKCK 3 | 115 | 4.65 | 4.6488 | 0.0012
GEN-2019-058 | 03 CENTRAL | 583850 | GEN-2014-001 | 345 | 6.9804 | 6.9797 | 0.0007
GEN-2019-058 | 03 CENTRAL | 585410 | GREAT_WESTRN | 345 | 9.7415 | 9.7398 | 0.0017
GEN-2019-058 | 03 CENTRAL | 585430 | PRSIMN_CRK1 | 345 | 11.7445 | 11.7419 | 0.0026
GEN-2019-058 | 03 CENTRAL | 587140 | GEN-2016-020 | 138 | 7.4213 | 7.4212 | 0.0001
GEN-2019-058 | 03 CENTRAL | 587884 | G16-111-TAP | 345 | 9.7651 | 9.7635 | 0.0016
GEN-2019-058 | 03 CENTRAL | 588364 | G16-153-TAP | 345 | 7.5063 | 7.5056 | 0.0007
GEN-2019-058 | 03 CENTRAL | 588560 | GEN-2017-011 | 345 | 12.6206 | 12.6179 | 0.0027
GEN-2019-058 | 03 CENTRAL | 589060 | GEN-2017-068 | 138 | 29.2988 | 29.292 | 0.0068
GEN-2019-058 | 03 CENTRAL | 640066 | AXTELL 7 | 115 | 14.0353 | 14.0347 | 0.0006
GEN-2019-058 | 03 CENTRAL | 640312 | PAULINE3 | 345 | 7.8813 | 7.8809 | 0.0004
GEN-2019-058 | 03 CENTRAL | 640374 | SWEET W3 | 345 | 10.1673 | 10.1667 | 0.0006
GEN-2019-058 | 03 CENTRAL | 760620 | GEN-2017-179 | 138 | 7.0944 | 7.0941 | 0.0003
GEN-2019-058 | 03 CENTRAL | 760641 | GEN-2017-226 | 138 | 32.1766 | 32.1684 | 0.0082
GEN-2019-058 | 03 CENTRAL | 762662 | G18-030-TAP | 345 | 5.8775 | 5.8727 | 0.0048
GEN-2019-058 | 03 CENTRAL | 762922 | GEN-2018-057 | 138 | 17.2503 | 17.2481 | 0.0022
GEN-2019-058 | 03 CENTRAL | 763421 | G18-128-TAP | 345 | 12.3337 | 12.3322 | 0.0015
GEN-2019-058 | 03 CENTRAL | 763549 | GEN-2019-014 | 115 | 10.049 | 10.0473 | 0.0017
GEN-2019-058 | 03 CENTRAL | 763862 | G19-054-TAP | 230 | 6.9761 | 6.9728 | 0.0033
GEN-2019-062 | 03 CENTRAL | 533032 | BU11PON4 | 138 | 14.9483 | 14.9483 | 0
GEN-2019-062 | 03 CENTRAL | 532991 | WEAVER 4 | 138 | 21.9573 | 21.9573 | 0
GEN-2019-062 | 03 CENTRAL | 763917 | G19-062-TAP | 138 | 14.883 | 14.883 | 0
GEN-2019-062 | 03 CENTRAL | 532993 | TALLGRS4 | 138 | 10.3196 | 10.3196 | 0
GEN-2019-062 | 03 CENTRAL | 533026 | ANDOVER4 | 138 | 17.6801 | 17.6801 | 0
GEN-2019-062 | 03 CENTRAL | 533059 | ELPASOE4 | 138 | 24.7207 | 24.7207 | 0
GEN-2019-062 | 03 CENTRAL | 533062 | ROSEHIL4 | 138 | 30.9062 | 30.9062 | 0
GEN-2019-062 | 03 CENTRAL | 533067 | SPRNGDL4 | 138 | 14.3347 | 14.3347 | 0
GEN-2019-062 | 03 CENTRAL | 533604 | WEAVER 2 | 69 | 11.8181 | 11.8181 | 0
GEN-2019-062 | 03 CENTRAL | 763912 | GEN-2019-062 | 138 | 14.2808 | 14.2808 | 0
GEN-2019-062 | 03 CENTRAL | 532794 | ROSEHIL7 | 345 | 18.8487 | 18.8487 | 0
GEN-2019-062 | 03 CENTRAL | 532989 | BUTLERS4 | 138 | 10.852 | 10.852 | 0
GEN-2019-062 | 03 CENTRAL | 533028 | BEECHTP4 | 138 | 13.3444 | 13.3444 | 0
GEN-2019-062 | 03 CENTRAL | 533039 | ELPASO 4 | 138 | 24.7628 | 24.7628 | 0
GEN-2019-062 | 03 CENTRAL | 533042 | FARBER 4 | 138 | 16.6063 | 16.6063 | 0
GEN-2019-062 | 03 CENTRAL | 533058 | 47TH ST4 | 138 | 17.1186 | 17.1186 | 0
GEN-2019-062 | 03 CENTRAL | 533060 | NOEASTE4 | 138 | 20.2853 | 20.2853 | 0
GEN-2019-062 | 03 CENTRAL | 533068 | STEARMN4 | 138 | 19.3341 | 19.3341 | 0
GEN-2019-062 | 03 CENTRAL | 533585 | BU10BEN2 | 69 | 10.6109 | 10.6109 | 0
GEN-2019-062 | 03 CENTRAL | 533793 | ELPASO 2 | 69 | 11.6637 | 11.6637 | 0
GEN-2019-062 | 03 CENTRAL | 533837 | RH JCT 2 | 69 | 6.6982 | 6.6982 | 0
GEN-2019-062 | 03 CENTRAL | 532791 | BENTON 7 | 345 | 19.0077 | 19.0077 | 0
GEN-2019-062 | 03 CENTRAL | 532797 | WOLFCRK7 | 345 | 20.9355 | 20.9355 | 0
GEN-2019-062 | 03 CENTRAL | 532800 | LATHAMS7 | 345 | 10.1116 | 10.1116 | 0
GEN-2019-062 | 03 CENTRAL | 532987 | BUTLER 4 | 138 | 10.8593 | 10.8593 | 0
GEN-2019-062 | 03 CENTRAL | 533024 | 29TH 4 | 138 | 19.3465 | 19.3465 | 0
GEN-2019-062 | 03 CENTRAL | 533027 | BEECH 4 | 138 | 11.5808 | 11.5808 | 0
GEN-2019-062 | 03 CENTRAL | 533029 | 59TH ST4 | 138 | 17.1774 | 17.1774 | 0
GEN-2019-062 | 03 CENTRAL | 533030 | BOEINGE4 | 138 | 16.7286 | 16.7286 | 0
GEN-2019-062 | 03 CENTRAL | 533048 | HARRY 4 | 138 | 13.4342 | 13.4342 | 0
GEN-2019-062 | 03 CENTRAL | 533061 | NOEASTW4 | 138 | 20.2556 | 20.2556 | 0
GEN-2019-062 | 03 CENTRAL | 533063 | SC10BEL4 | 138 | 11.9885 | 11.9885 | 0
GEN-2019-062 | 03 CENTRAL | 533066 | 64TH 4 | 138 | 14.3559 | 14.3559 | 0
GEN-2019-062 | 03 CENTRAL | 533550 | RICHLAN2 | 69 | 6.0288 | 6.0288 | 0
GEN-2019-062 | 03 CENTRAL | 533598 | MOBIL 2 | 69 | 7.5885 | 7.5885 | 0
GEN-2019-062 | 03 CENTRAL | 533609 | BUTLERS2 | 69 | 13.6364 | 13.6364 | 0
GEN-2019-062 | 03 CENTRAL | 533821 | MULVANE2 | 69 | 5.3282 | 5.3282 | 0
GEN-2019-062 | 03 CENTRAL | 533823 | NOEASTE2 | 69 | 25.1791 | 25.1791 | 0
GEN-2019-062 | 03 CENTRAL | 533824 | OAKLAWN2 | 69 | 15.2802 | 15.2802 | 0
GEN-2019-062 | 03 CENTRAL | 533836 | ROSEHIL2 | 69 | 5.4599 | 5.4599 | 0
GEN-2019-062 | 03 CENTRAL | 560053 | G15-052T | 345 | 13.3131 | 13.3131 | 0
GEN-2019-062 | 03 CENTRAL | 300739 | 7BLACKBERRY | 345 | 15.3686 | 15.3686 | 0
GEN-2019-062 | 03 CENTRAL | 515621 | OPENSKY7 | 345 | 13.269 | 13.269 | 0
GEN-2019-062 | 03 CENTRAL | 532780 | CANEYRV7 | 345 | 9.4765 | 9.4765 | 0
GEN-2019-062 | 03 CENTRAL | 532796 | WICHITA7 | 345 | 23.7708 | 23.7708 | 0
GEN-2019-062 | 03 CENTRAL | 532799 | WAVERLY7 | 345 | 17.6458 | 17.6458 | 0
GEN-2019-062 | 03 CENTRAL | 532801 | ELKRVR17 | 345 | 8.9569 | 8.9569 | 0
GEN-2019-062 | 03 CENTRAL | 532984 | SUMNER 4 | 138 | 12.1641 | 12.1641 | 0
GEN-2019-062 | 03 CENTRAL | 532986 | BENTON 4 | 138 | 27.7644 | 27.7644 | 0
GEN-2019-062 | 03 CENTRAL | 532990 | MIDIAN 4 | 138 | 10.9264 | 10.9264 | 0
GEN-2019-062 | 03 CENTRAL | 532996 | TIOGA 4 | 138 | 5.4402 | 5.4402 | 0
GEN-2019-062 | 03 CENTRAL | 532997 | OTTRCRK4 | 138 | 5.477 | 5.477 | 0
GEN-2019-062 | 03 CENTRAL | 533037 | COMOTAR4 | 138 | 18.4286 | 18.4286 | 0
GEN-2019-062 | 03 CENTRAL | 533046 | GILL S 4 | 138 | 21.8015 | 21.8015 | 0
GEN-2019-062 | 03 CENTRAL | 533055 | BOEINGW4 | 138 | 16.7124 | 16.7124 | 0
GEN-2019-062 | 03 CENTRAL | 533559 | UDALL 2 | 69 | 7.4822 | 7.4822 | 0
GEN-2019-062 | 03 CENTRAL | 533582 | AUGUSTA2 | 69 | 7.3295 | 7.3295 | 0
GEN-2019-062 | 03 CENTRAL | 533583 | BUTLERN2 | 69 | 13.6435 | 13.6435 | 0
GEN-2019-062 | 03 CENTRAL | 533593 | FRNTR N2 | 69 | 11.8341 | 11.8341 | 0
GEN-2019-062 | 03 CENTRAL | 533653 | WOLFCRK2 | 69 | 5.9769 | 5.9769 | 0
GEN-2019-062 | 03 CENTRAL | 533808 | HYDRJN2 | 69 | 15.5487 | 15.5487 | 0
GEN-2019-062 | 03 CENTRAL | 533817 | MINNEHA2 | 69 | 15.9942 | 15.9942 | 0
GEN-2019-062 | 03 CENTRAL | 533822 | NOEASTW2 | 69 | 25.1911 | 25.1911 | 0
GEN-2019-062 | 03 CENTRAL | 533826 | OLIVER 2 | 69 | 13.856 | 13.856 | 0
GEN-2019-062 | 03 CENTRAL | 533842 | 64TH 2 | 69 | 14.6428 | 14.6428 | 0
GEN-2019-062 | 03 CENTRAL | 542965 | W.GRDNR7 | 345 | 31.7637 | 31.7637 | 0
GEN-2019-062 | 03 CENTRAL | 584900 | GEN-2015-052 | 345 | 13.2613 | 13.2613 | 0
GEN-2019-063 | 03 CENTRAL | 539800 | CLARKCOUNTY7 | 345 | 12.7785 | 12.6765 | 0.102
GEN-2019-063 | 03 CENTRAL | 531469 | SPERVIL7 | 345 | 13.6098 | 13.5546 | 0.0552
GEN-2019-063 | 03 CENTRAL | 539801 | THISTLE7 | 345 | 16.6662 | 16.6398 | 0.0264
GEN-2019-063 | 03 CENTRAL | 539813 | TRANSFORMER | 345 | 10.6791 | 10.6085 | 0.0706
GEN-2019-063 | 03 CENTRAL | 539840 | GEN-2011-008 | 345 | 10.5555 | 10.4886 | 0.0669
GEN-2019-063 | 03 CENTRAL | 560080 | G16-046-TAP | 345 | 11.3684 | 11.3066 | 0.0618
GEN-2019-063 | 03 CENTRAL | 763890 | GEN-2019-058 | 345 | 12.52 | 12.418 | 0.102
GEN-2019-063 | 03 CENTRAL | 515852 | DGRASSE7 | 345 | 15.3179 | 15.31 | 0.0079
GEN-2019-063 | 03 CENTRAL | 530583 | POSTROCK7 | 345 | 7.7231 | 7.718 | 0.0051
GEN-2019-063 | 03 CENTRAL | 531501 | BUCKNER7 | 345 | 9.2456 | 9.2327 | 0.0129
GEN-2019-063 | 03 CENTRAL | 532782 | BUFFALO7 | 345 | 20.7555 | 20.7476 | 0.0079
GEN-2019-063 | 03 CENTRAL | 539695 | SPEARVL6 | 230 | 12.772 | 12.7482 | 0.0238
GEN-2019-063 | 03 CENTRAL | 539759 | SPRVL 3 | 115 | 12.8273 | 12.8136 | 0.0137
GEN-2019-063 | 03 CENTRAL | 539803 | IRONWOOD7 | 345 | 13.1638 | 13.1103 | 0.0535
GEN-2019-063 | 03 CENTRAL | 539804 | THISTLE4 | 138 | 17.5567 | 17.5471 | 0.0096
GEN-2019-063 | 03 CENTRAL | 539841 | G-2011-008-1 | 345 | 10.5555 | 10.4886 | 0.0669
GEN-2019-063 | 03 CENTRAL | 539855 | G-2011-008-2 | 345 | 8.8342 | 8.7879 | 0.0463
GEN-2019-063 | 03 CENTRAL | 539857 | G-2011-008-3 | 345 | 8.2708 | 8.2306 | 0.0402
GEN-2019-063 | 03 CENTRAL | 587310 | GEN-2016-046 | 345 | 9.9533 | 9.9067 | 0.0466
GEN-2019-063 | 03 CENTRAL | 588630 | GEN-2017-018 | 345 | 16.6662 | 16.6398 | 0.0264
GEN-2019-063 | 03 CENTRAL | 762834 | GEN-2018-049 | 345 | 6.9567 | 6.9523 | 0.0044
GEN-2019-063 | 03 CENTRAL | 515375 | WWRDEHV7 | 345 | 22.3641 | 22.3601 | 0.004
GEN-2019-063 | 03 CENTRAL | 515853 | DGRASSE4 | 138 | 17.0745 | 17.0726 | 0.0019
GEN-2019-063 | 03 CENTRAL | 530584 | POSTROCK6 | 230 | 10.7096 | 10.7049 | 0.0047
GEN-2019-063 | 03 CENTRAL | 531449 | HOLCOMB7 | 345 | 9.9438 | 9.9379 | 0.0059
GEN-2019-063 | 03 CENTRAL | 531502 | CIMRRN 7 | 345 | 7.3025 | 7.2944 | 0.0081
GEN-2019-063 | 03 CENTRAL | 531504 | CIMWD2 7 | 345 | 7.4234 | 7.4152 | 0.0082
GEN-2019-063 | 03 CENTRAL | 532783 | KINGMAN7 | 345 | 7.0277 | 7.027 | 0.0007
GEN-2019-063 | 03 CENTRAL | 532796 | WICHITA7 | 345 | 23.7708 | 23.7639 | 0.0069
GEN-2019-063 | 03 CENTRAL | 539117 | SPRVILL-EHVB | 230 | 12.4582 | 12.4357 | 0.0225
GEN-2019-063 | 03 CENTRAL | 539638 | FLATRDG4 | 138 | 15.5636 | 15.5566 | 0.007
GEN-2019-063 | 03 CENTRAL | 539694 | SPEARVL3 | 115 | 9.9365 | 9.9303 | 0.0062
GEN-2019-063 | 03 CENTRAL | 539771 | NFTDODG3 | 115 | 9.7556 | 9.7512 | 0.0044
GEN-2019-063 | 03 CENTRAL | 539815 | IRONWOOD WF7 | 345 | 11.8843 | 11.841 | 0.0433
GEN-2019-063 | 03 CENTRAL | 560082 | G16-050-TAP | 345 | 6.9512 | 6.9504 | 0.0008
GEN-2019-063 | 03 CENTRAL | 579480 | GEN-2008-124 | 345 | 12.711 | 12.6612 | 0.0498
GEN-2019-063 | 03 CENTRAL | 587311 | G16-046XFMR1 | 115 | 14.7707 | 14.7416 | 0.0291
GEN-2019-063 | 03 CENTRAL | 587500 | GEN-2016-073 | 345 | 15.2224 | 15.2183 | 0.0041
GEN-2019-063 | 03 CENTRAL | 760284 | GEN-2017-220 | 345 | 20.642 | 20.6342 | 0.0078
GEN-2019-063 | 03 CENTRAL | 763670 | GEN-2019-030 | 345 | 10.4948 | 10.4615 | 0.0333
GEN-2019-063 | 03 CENTRAL | 763850 | G19-055-TAP | 230 | 7.2471 | 7.2427 | 0.0044
GEN-2019-063 | 03 CENTRAL | 514795 | KNOBHIL4 | 138 | 10.2855 | 10.2849 | 0.0006
GEN-2019-063 | 03 CENTRAL | 515376 | WWRDEHV4 | 138 | 24.8769 | 24.8754 | 0.0015
GEN-2019-063 | 03 CENTRAL | 515407 | TATONGA7 | 345 | 17.5658 | 17.5648 | 0.001
GEN-2019-063 | 03 CENTRAL | 515554 | BVRCNTY7 | 345 | 15.3093 | 15.3081 | 0.0012
GEN-2019-063 | 03 CENTRAL | 515599 | G07621119-20 | 345 | 13.4849 | 13.4835 | 0.0014
GEN-2019-063 | 03 CENTRAL | 515961 | GUTHRIE7 | 345 | 12.8816 | 12.8802 | 0.0014
GEN-2019-063 | 03 CENTRAL | 516106 | BOBCAT 7 | 345 | 15.796 | 15.7944 | 0.0016
GEN-2019-063 | 03 CENTRAL | 520436 | ROSEVLY4 | 138 | 12.3574 | 12.3564 | 0.001
GEN-2019-063 | 03 CENTRAL | 520999 | MOORLND4 | 138 | 20.0616 | 20.0614 | 0.0002
GEN-2019-063 | 03 CENTRAL | 523853 | FINNEY 7 | 345 | 9.8362 | 9.8305 | 0.0057
GEN-2019-063 | 03 CENTRAL | 530558 | KNOLL N 6 | 230 | 10.6179 | 10.6133 | 0.0046
GEN-2019-063 | 03 CENTRAL | 530582 | S HAYS6 | 230 | 8.805 | 8.8022 | 0.0028
GEN-2019-063 | 03 CENTRAL | 530702 | BUCKEYE_230 | 230 | 7.8435 | 7.8411 | 0.0024
GEN-2019-063 | 03 CENTRAL | 530720 | KNOLL S 6 | 230 | 10.6179 | 10.6133 | 0.0046
GEN-2019-063 | 03 CENTRAL | 531448 | HOLCOMB3 | 115 | 21.2532 | 21.25 | 0.0032
GEN-2019-063 | 03 CENTRAL | 531465 | SETAB 7 | 345 | 6.866 | 6.8642 | 0.0018
GEN-2019-063 | 03 CENTRAL | 532771 | RENO 7 | 345 | 11.0976 | 11.0965 | 0.0011
GEN-2019-063 | 03 CENTRAL | 532784 | NINN1WF7 | 345 | 5.8368 | 5.8364 | 0.0004
GEN-2019-063 | 03 CENTRAL | 532791 | BENTON 7 | 345 | 19.0077 | 19.0057 | 0.002
GEN-2019-063 | 03 CENTRAL | 532798 | VIOLA 7 | 345 | 14.0837 | 14.0824 | 0.0013
GEN-2019-063 | 03 CENTRAL | 533040 | EVANS N4 | 138 | 32.3573 | 32.354 | 0.0033
GEN-2019-063 | 03 CENTRAL | 539631 | FLATRWD4 | 138 | 10.3815 | 10.3784 | 0.0031
GEN-2019-063 | 03 CENTRAL | 539668 | HARPER 4 | 138 | 7.2122 | 7.2116 | 0.0006
GEN-2019-063 | 03 CENTRAL | 539671 | FTDODGE3 | 115 | 9.6942 | 9.6899 | 0.0043
GEN-2019-063 | 03 CENTRAL | 539674 | BARBER 4 | 138 | 8.2322 | 8.2303 | 0.0019
GEN-2019-063 | 03 CENTRAL | 539679 | GRTBEND6 | 230 | 8.7899 | 8.7872 | 0.0027
GEN-2019-063 | 03 CENTRAL | 539688 | S-DODGE3 | 115 | 6.7777 | 6.7757 | 0.002
GEN-2019-063 | 03 CENTRAL | 539758 | FORD 3 | 115 | 5.204 | 5.203 | 0.001
GEN-2019-063 | 03 CENTRAL | 562476 | G14-001-TAP | 345 | 10.3737 | 10.373 | 0.0007
GEN-2019-063 | 03 CENTRAL | 585300 | GEN-2015-095 | 138 | 16.8692 | 16.8673 | 0.0019
GEN-2019-063 | 03 CENTRAL | 587350 | GEN-2016-050 | 345 | 5.8546 | 5.8541 | 0.0005
GEN-2019-063 | 03 CENTRAL | 640065 | AXTELL 3 | 345 | 9.208 | 9.2075 | 0.0005
GEN-2019-063 | 03 CENTRAL | 755000 | WWDBORDT | 345 | 12.2648 | 12.2645 | 0.0003
GEN-2019-063 | 03 CENTRAL | 763527 | GEN-2019-012 | 345 | 19.3711 | 19.3681 | 0.003
GEN-2019-063 | 03 CENTRAL | 763758 | GEN-2019-044 | 115 | 6.4739 | 6.4721 | 0.0018
GEN-2019-063 | 03 CENTRAL | 763769 | GEN-2019-045 | 138 | 17.0745 | 17.0726 | 0.0019
GEN-2019-063 | 03 CENTRAL | 763846 | G19-053/055 | 230 | 7.1612 | 7.1568 | 0.0044
GEN-2019-063 | 03 CENTRAL | 511553 | CHISHOLM7 | 345 | 12.3397 | 12.3395 | 0.0002
GEN-2019-063 | 03 CENTRAL | 514785 | WOODWRD4 | 138 | 13.1123 | 13.112 | 0.0003
GEN-2019-063 | 03 CENTRAL | 514788 | GLASMTN4 | 138 | 5.1117 | 5.1116 | 0.0001
GEN-2019-063 | 03 CENTRAL | 514794 | KNOBHIL2 | 69 | 8.8727 | 8.8725 | 0.0002
GEN-2019-063 | 03 CENTRAL | 514796 | IODINE-4 | 138 | 7.3201 | 7.32 | 0.0001
GEN-2019-063 | 03 CENTRAL | 515394 | KEENAN 4 | 138 | 8.9414 | 8.9412 | 0.0002
GEN-2019-063 | 03 CENTRAL | 515398 | OUSPRT 4 | 138 | 9.528 | 9.5278 | 0.0002
GEN-2019-063 | 03 CENTRAL | 515425 | WWDPST 4 | 138 | 17.7977 | 17.7971 | 0.0006
GEN-2019-063 | 03 CENTRAL | 515448 | CRSRDSW7 | 345 | 12.1468 | 12.1463 | 0.0005
GEN-2019-063 | 03 CENTRAL | 515458 | BORDER 7 | 345 | 8.2517 | 8.2516 | 0.0001
GEN-2019-063 | 03 CENTRAL | 515497 | MATHWSN7 | 345 | 32.7952 | 32.7946 | 0.0006
GEN-2019-063 | 03 CENTRAL | 515582 | SLNGWND7 | 345 | 8.4766 | 8.4764 | 0.0002
GEN-2019-063 | 03 CENTRAL | 515585 | MAMTHPW7 | 345 | 13.5669 | 13.5664 | 0.0005
GEN-2019-063 | 03 CENTRAL | 515590 | PALDR2W7 | 345 | 12.8669 | 12.8661 | 0.0008
GEN-2019-063 | 03 CENTRAL | 515618 | BALKOW 7 | 345 | 12.5807 | 12.5799 | 0.0008
GEN-2019-063 | 03 CENTRAL | 515677 | BADGER 7 | 345 | 13.7821 | 13.7811 | 0.001
GEN-2019-063 | 03 CENTRAL | 515785 | WINDFRM4 | 138 | 19.5945 | 19.5942 | 0.0003
GEN-2019-063 | 03 CENTRAL | 515825 | GRTWSRN7 | 345 | 9.0702 | 9.0695 | 0.0007
GEN-2019-063 | 03 CENTRAL | 515951 | PERSIMN7 | 345 | 11.0796 | 11.0786 | 0.001
GEN-2019-063 | 03 CENTRAL | 516146 | 25MILE 7 | 345 | 11.1221 | 11.1213 | 0.0008
GEN-2019-063 | 03 CENTRAL | 520425 | PIC4 | 138 | 7.9856 | 7.9856 | 0
GEN-2019-063 | 03 CENTRAL | 520430 | NOELSW 4 | 138 | 10.3556 | 10.355 | 0.0006
GEN-2019-063 | 03 CENTRAL | 520462 | ASPEN 4 | 138 | 19.3561 | 19.3558 | 0.0003
GEN-2019-063 | 03 CENTRAL | 520553 | SEILING4 | 138 | 6.6101 | 6.6101 | 0
GEN-2019-063 | 03 CENTRAL | 520601 | AVARD 4 | 138 | 6.857 | 6.8567 | 0.0003
GEN-2019-063 | 03 CENTRAL | 520957 | IODINE 4 | 138 | 7.673 | 7.673 | 0
GEN-2019-063 | 03 CENTRAL | 520995 | MOORLND2 | 69 | 8.5299 | 8.5299 | 0
GEN-2019-063 | 03 CENTRAL | 523097 | HITCHLAND 7 | 345 | 14.9713 | 14.9702 | 0.0011
GEN-2019-063 | 03 CENTRAL | 523118 | BUFF_DUNES 7 | 345 | 6.0272 | 6.0252 | 0.002
GEN-2019-063 | 03 CENTRAL | 523823 | CARPENTER 7 | 345 | 6.5781 | 6.5772 | 0.0009
GEN-2019-063 | 03 CENTRAL | 530553 | S HAYS 3 | 115 | 8.4163 | 8.415 | 0.0013
GEN-2019-063 | 03 CENTRAL | 530561 | KNOLL 3 | 115 | 10.3394 | 10.3377 | 0.0017
GEN-2019-063 | 03 CENTRAL | 530592 | SMOKYHL6 | 230 | 6.0395 | 6.0391 | 0.0004
GEN-2019-063 | 03 CENTRAL | 530610 | SHAYS_230 | 230 | 3.4161 | 3.4158 | 0.0003
GEN-2019-063 | 03 CENTRAL | 530680 | HEIZER 6 | 230 | 8.7324 | 8.7298 | 0.0026
GEN-2019-063 | 03 CENTRAL | 531379 | JONES3 | 115 | 10.6043 | 10.6035 | 0.0008
GEN-2019-063 | 03 CENTRAL | 531393 | PLYMELL3 | 115 | 7.6981 | 7.6978 | 0.0003
GEN-2019-063 | 03 CENTRAL | 531420 | FLETCHR3 | 115 | 6.7619 | 6.7616 | 0.0003
GEN-2019-063 | 03 CENTRAL | 531445 | GRDNCTY3 | 115 | 12.5516 | 12.5508 | 0.0008
GEN-2019-063 | 03 CENTRAL | 531451 | MINGO 7 | 345 | 6.0094 | 6.0087 | 0.0007
GEN-2019-063 | 03 CENTRAL | 531464 | SETAB 3 | 115 | 10.1837 | 10.1826 | 0.0011
GEN-2019-063 | 03 CENTRAL | 532768 | EMPEC 7 | 345 | 16.1367 | 16.1364 | 0.0003
GEN-2019-063 | 03 CENTRAL | 532785 | PRATTWF7 | 345 | 4.8525 | 4.8522 | 0.0003
GEN-2019-063 | 03 CENTRAL | 532794 | ROSEHIL7 | 345 | 18.8487 | 18.8475 | 0.0012
GEN-2019-063 | 03 CENTRAL | 532797 | WOLFCRK7 | 345 | 20.9355 | 20.9352 | 0.0003
GEN-2019-063 | 03 CENTRAL | 532986 | BENTON 4 | 138 | 27.7644 | 27.7628 | 0.0016
GEN-2019-063 | 03 CENTRAL | 533041 | EVANS S4 | 138 | 32.2762 | 32.2729 | 0.0033
GEN-2019-063 | 03 CENTRAL | 533054 | MAIZE 4 | 138 | 20.7931 | 20.7918 | 0.0013
GEN-2019-063 | 03 CENTRAL | 533065 | SG12COL4 | 138 | 19.3466 | 19.3454 | 0.0012
GEN-2019-063 | 03 CENTRAL | 533075 | VIOLA 4 | 138 | 24.178 | 24.1763 | 0.0017
GEN-2019-063 | 03 CENTRAL | 533416 | RENO 3 | 115 | 22.1556 | 22.1539 | 0.0017
GEN-2019-063 | 03 CENTRAL | 539000 | RAGO 4 | 138 | 3.9467 | 3.9465 | 0.0002
GEN-2019-063 | 03 CENTRAL | 539001 | ANTHONY4 | 138 | 5.012 | 5.0118 | 0.0002
GEN-2019-063 | 03 CENTRAL | 539645 | DCBEEF3 | 115 | 6.943 | 6.9408 | 0.0022
GEN-2019-063 | 03 CENTRAL | 539675 | MILANTP4 | 138 | 9.9006 | 9.9002 | 0.0004
GEN-2019-063 | 03 CENTRAL | 539678 | GRTBEND3 | 115 | 12.2449 | 12.2428 | 0.0021
GEN-2019-063 | 03 CENTRAL | 539699 | W-DODGE3 | 115 | 4.3105 | 4.3098 | 0.0007
GEN-2019-063 | 03 CENTRAL | 539760 | BARBER 3 | 115 | 8.1332 | 8.1318 | 0.0014
GEN-2019-063 | 03 CENTRAL | 539763 | SSTARTP3 | 115 | 4.0742 | 4.0738 | 0.0004
GEN-2019-063 | 03 CENTRAL | 539783 | CRKCK 3 | 115 | 4.65 | 4.6495 | 0.0005
GEN-2019-063 | 03 CENTRAL | 583850 | GEN-2014-001 | 345 | 6.9804 | 6.9801 | 0.0003
GEN-2019-063 | 03 CENTRAL | 585410 | GREAT_WESTRN | 345 | 9.7415 | 9.7408 | 0.0007
GEN-2019-063 | 03 CENTRAL | 585430 | PRSIMN_CRK1 | 345 | 11.7445 | 11.7435 | 0.001
GEN-2019-063 | 03 CENTRAL | 587140 | GEN-2016-020 | 138 | 7.4213 | 7.4212 | 0.0001
GEN-2019-063 | 03 CENTRAL | 587884 | G16-111-TAP | 345 | 9.7651 | 9.7645 | 0.0006
GEN-2019-063 | 03 CENTRAL | 588364 | G16-153-TAP | 345 | 7.5063 | 7.5061 | 0.0002
GEN-2019-063 | 03 CENTRAL | 588560 | GEN-2017-011 | 345 | 12.6206 | 12.6195 | 0.0011
GEN-2019-063 | 03 CENTRAL | 589060 | GEN-2017-068 | 138 | 29.2988 | 29.2961 | 0.0027
GEN-2019-063 | 03 CENTRAL | 640066 | AXTELL 7 | 115 | 14.0353 | 14.035 | 0.0003
GEN-2019-063 | 03 CENTRAL | 640312 | PAULINE3 | 345 | 7.8813 | 7.8812 | 0.0001
GEN-2019-063 | 03 CENTRAL | 640374 | SWEET W3 | 345 | 10.1673 | 10.167 | 0.0003
GEN-2019-063 | 03 CENTRAL | 760620 | GEN-2017-179 | 138 | 7.0944 | 7.0943 | 0.0001
GEN-2019-063 | 03 CENTRAL | 760641 | GEN-2017-226 | 138 | 32.1766 | 32.1734 | 0.0032
GEN-2019-063 | 03 CENTRAL | 762662 | G18-030-TAP | 345 | 5.8775 | 5.8756 | 0.0019
GEN-2019-063 | 03 CENTRAL | 762922 | GEN-2018-057 | 138 | 17.2503 | 17.2494 | 0.0009
GEN-2019-063 | 03 CENTRAL | 763421 | G18-128-TAP | 345 | 12.3337 | 12.3331 | 0.0006
GEN-2019-063 | 03 CENTRAL | 763549 | GEN-2019-014 | 115 | 10.049 | 10.0483 | 0.0007
GEN-2019-063 | 03 CENTRAL | 763862 | G19-054-TAP | 230 | 6.9761 | 6.9748 | 0.0013
GEN-2019-068 | 03 CENTRAL | 763862 | G19-054-TAP | 230 | 6.9761 | 6.8175 | 0.1586
GEN-2019-068 | 03 CENTRAL | 532871 | CIRCLE 6 | 230 | 8.4637 | 8.4337 | 0.03
GEN-2019-068 | 03 CENTRAL | 539679 | GRTBEND6 | 230 | 8.7899 | 8.6758 | 0.1141
GEN-2019-068 | 03 CENTRAL | 763857 | G19-054/068 | 230 | 6.8962 | 6.7373 | 0.1589
GEN-2019-068 | 03 CENTRAL | 530582 | S HAYS6 | 230 | 8.805 | 8.7701 | 0.0349
GEN-2019-068 | 03 CENTRAL | 530680 | HEIZER 6 | 230 | 8.7324 | 8.62 | 0.1124
GEN-2019-068 | 03 CENTRAL | 530686 | RICE 6 | 230 | 4.1143 | 4.1089 | 0.0054
GEN-2019-068 | 03 CENTRAL | 532872 | EMCPHER6 | 230 | 7.7208 | 7.7082 | 0.0126
GEN-2019-068 | 03 CENTRAL | 533413 | CIRCLE 3 | 115 | 18.3479 | 18.317 | 0.0309
GEN-2019-068 | 03 CENTRAL | 539678 | GRTBEND3 | 115 | 12.2449 | 12.1661 | 0.0788
GEN-2019-068 | 03 CENTRAL | 763850 | G19-055-TAP | 230 | 7.2471 | 7.2261 | 0.021
GEN-2019-068 | 03 CENTRAL | 530553 | S HAYS 3 | 115 | 8.4163 | 8.4047 | 0.0116
GEN-2019-068 | 03 CENTRAL | 530584 | POSTROCK6 | 230 | 10.7096 | 10.683 | 0.0266
GEN-2019-068 | 03 CENTRAL | 530601 | HEIZER 3 | 115 | 12.1453 | 12.0671 | 0.0782
GEN-2019-068 | 03 CENTRAL | 530610 | SHAYS_230 | 230 | 3.4161 | 3.4119 | 0.0042
GEN-2019-068 | 03 CENTRAL | 530623 | RICE 3 | 115 | 6.4817 | 6.4754 | 0.0063
GEN-2019-068 | 03 CENTRAL | 530688 | BUFLOCRK6 | 230 | 2.7508 | 2.7488 | 0.002
GEN-2019-068 | 03 CENTRAL | 532873 | SUMMIT 6 | 230 | 12.899 | 12.8887 | 0.0103
GEN-2019-068 | 03 CENTRAL | 533412 | ARKVALJ3 | 115 | 9.6861 | 9.677 | 0.0091
GEN-2019-068 | 03 CENTRAL | 533416 | RENO 3 | 115 | 22.1556 | 22.1278 | 0.0278
GEN-2019-068 | 03 CENTRAL | 533417 | EMCPHER3 | 115 | 11.1793 | 11.1676 | 0.0117
GEN-2019-068 | 03 CENTRAL | 533419 | HEC 3 | 115 | 17.1573 | 17.1304 | 0.0269
GEN-2019-068 | 03 CENTRAL | 533421 | HEC GT 3 | 115 | 17.8389 | 17.8097 | 0.0292
GEN-2019-068 | 03 CENTRAL | 539642 | ELLSWTP3 | 115 | 3.9126 | 3.9084 | 0.0042
GEN-2019-068 | 03 CENTRAL | 539666 | GBENDTP3 | 115 | 8.7185 | 8.6842 | 0.0343
GEN-2019-068 | 03 CENTRAL | 539681 | N-GBEND3 | 115 | 9.1049 | 9.064 | 0.0409
GEN-2019-068 | 03 CENTRAL | 539684 | OTISSUB3 | 115 | 2.9219 | 2.9173 | 0.0046
GEN-2019-068 | 03 CENTRAL | 539695 | SPEARVL6 | 230 | 12.772 | 12.7566 | 0.0154
GEN-2019-068 | 03 CENTRAL | 763846 | G19-053/055 | 230 | 7.1612 | 7.1407 | 0.0205
GEN-2019-068 | 03 CENTRAL | 530558 | KNOLL N 6 | 230 | 10.6179 | 10.5917 | 0.0262
GEN-2019-068 | 03 CENTRAL | 530563 | HEIZER 2 | 69 | 8.7188 | 8.6972 | 0.0216
GEN-2019-068 | 03 CENTRAL | 530583 | POSTROCK7 | 345 | 7.7231 | 7.711 | 0.0121
GEN-2019-068 | 03 CENTRAL | 530592 | SMOKYHL6 | 230 | 6.0395 | 6.0362 | 0.0033
GEN-2019-068 | 03 CENTRAL | 530602 | LAXTAP 3 | 115 | 4.087 | 4.0817 | 0.0053
GEN-2019-068 | 03 CENTRAL | 530609 | HZRNGPL3 | 115 | 7.7647 | 7.7327 | 0.032
GEN-2019-068 | 03 CENTRAL | 530618 | HUNTSVL3 | 115 | 4.0068 | 4.0048 | 0.002
GEN-2019-068 | 03 CENTRAL | 530620 | LYONS 3 | 115 | 5.4243 | 5.4208 | 0.0035
GEN-2019-068 | 03 CENTRAL | 530681 | BUSHTON3 | 115 | 4.9177 | 4.9138 | 0.0039
GEN-2019-068 | 03 CENTRAL | 530695 | CHETOLAH3 | 115 | 8.3599 | 8.3493 | 0.0106
GEN-2019-068 | 03 CENTRAL | 530702 | BUCKEYE_230 | 230 | 7.8435 | 7.8298 | 0.0137
GEN-2019-068 | 03 CENTRAL | 530714 | ANGUS 3 | 115 | 5.1891 | 5.1847 | 0.0044
GEN-2019-068 | 03 CENTRAL | 530718 | BUSHTONW 3 | 115 | 4.1338 | 4.1312 | 0.0026
GEN-2019-068 | 03 CENTRAL | 530720 | KNOLL S 6 | 230 | 10.6179 | 10.5917 | 0.0262
GEN-2019-068 | 03 CENTRAL | 530725 | PFEIFER 3 | 115 | 3.4004 | 3.3985 | 0.0019
GEN-2019-068 | 03 CENTRAL | 531469 | SPERVIL7 | 345 | 13.6098 | 13.5967 | 0.0131
GEN-2019-068 | 03 CENTRAL | 532771 | RENO 7 | 345 | 11.0976 | 11.0898 | 0.0078
GEN-2019-068 | 03 CENTRAL | 532773 | SUMMIT 7 | 345 | 10.8577 | 10.852 | 0.0057
GEN-2019-068 | 03 CENTRAL | 532874 | UNIONRG6 | 230 | 7.9143 | 7.9127 | 0.0016
GEN-2019-068 | 03 CENTRAL | 533381 | SUMMIT 3 | 115 | 17.2114 | 17.2023 | 0.0091
GEN-2019-068 | 03 CENTRAL | 533411 | ARKVAL 3 | 115 | 9.5019 | 9.4932 | 0.0087
GEN-2019-068 | 03 CENTRAL | 533415 | DAVIS 3 | 115 | 8.0324 | 8.0279 | 0.0045
GEN-2019-068 | 03 CENTRAL | 533426 | MANVILE3 | 115 | 8.3015 | 8.2953 | 0.0062
GEN-2019-068 | 03 CENTRAL | 533427 | REFINRY3 | 115 | 10.3372 | 10.3277 | 0.0095
GEN-2019-068 | 03 CENTRAL | 533429 | MOUNDRG3 | 115 | 8.416 | 8.4143 | 0.0017
GEN-2019-068 | 03 CENTRAL | 533438 | WMCPHER3 | 115 | 10.8946 | 10.8846 | 0.01
GEN-2019-068 | 03 CENTRAL | 533440 | 43LORAN | 115 | 12.2903 | 12.277 | 0.0133
GEN-2019-068 | 03 CENTRAL | 533513 | HEC 2 | 69 | 7.8588 | 7.8554 | 0.0034
GEN-2019-068 | 03 CENTRAL | 539117 | SPRVILL-EHVB | 230 | 12.4582 | 12.4436 | 0.0146
GEN-2019-068 | 03 CENTRAL | 539643 | ROLLHLS3 | 115 | 3.5855 | 3.5821 | 0.0034
GEN-2019-068 | 03 CENTRAL | 539661 | 24-FREY3 | 115 | 8.1561 | 8.1264 | 0.0297
GEN-2019-068 | 03 CENTRAL | 539689 | 2ND-KS 3 | 115 | 7.9906 | 7.962 | 0.0286
GEN-2019-068 | 03 CENTRAL | 539692 | SEWARD 3 | 115 | 5.8179 | 5.8072 | 0.0107
GEN-2019-068 | 03 CENTRAL | 539694 | SPEARVL3 | 115 | 9.9365 | 9.9329 | 0.0036
GEN-2019-068 | 03 CENTRAL | 539701 | RUSSELL3 | 115 | 3.4282 | 3.4253 | 0.0029
GEN-2019-068 | 03 CENTRAL | 530552 | GORHAM 3 | 115 | 3.0814 | 3.0798 | 0.0016
GEN-2019-068 | 03 CENTRAL | 530561 | KNOLL 3 | 115 | 10.3394 | 10.3267 | 0.0127
GEN-2019-068 | 03 CENTRAL | 530568 | GB NTH 2 | 69 | 6.7283 | 6.7156 | 0.0127
GEN-2019-068 | 03 CENTRAL | 530586 | ALBERT 2 | 69 | 3.6217 | 3.6185 | 0.0032
GEN-2019-068 | 03 CENTRAL | 530587 | WSPRTTP2 | 69 | 5.93 | 5.9202 | 0.0098
GEN-2019-068 | 03 CENTRAL | 530593 | SMKYP1 6 | 230 | 5.3037 | 5.3012 | 0.0025
GEN-2019-068 | 03 CENTRAL | 530599 | SMKYP2 6 | 230 | 5.5659 | 5.5632 | 0.0027
GEN-2019-068 | 03 CENTRAL | 530603 | LACROS 3 | 115 | 3.54 | 3.5361 | 0.0039
GEN-2019-068 | 03 CENTRAL | 530608 | NEKOMA 3 | 115 | 3.9676 | 3.9634 | 0.0042
GEN-2019-068 | 03 CENTRAL | 530624 | ST JOHN3 | 115 | 5.2881 | 5.2835 | 0.0046
GEN-2019-068 | 03 CENTRAL | 530679 | SEWRDMW3 | 115 | 5.1213 | 5.1129 | 0.0084
GEN-2019-068 | 03 CENTRAL | 530693 | VINETAP3 | 115 | 8.4097 | 8.3992 | 0.0105
GEN-2019-068 | 03 CENTRAL | 530711 | SAXMAN 3 | 115 | 4.4373 | 4.435 | 0.0023
GEN-2019-068 | 03 CENTRAL | 530722 | VINEDE_S | 115 | 7.7328 | 7.7238 | 0.009
GEN-2019-068 | 03 CENTRAL | 531501 | BUCKNER7 | 345 | 9.2456 | 9.2421 | 0.0035
GEN-2019-068 | 03 CENTRAL | 532767 | GEARY 7 | 345 | 9.8704 | 9.8685 | 0.0019
GEN-2019-068 | 03 CENTRAL | 532796 | WICHITA7 | 345 | 23.7708 | 23.7646 | 0.0062
GEN-2019-068 | 03 CENTRAL | 532863 | MORRIS 6 | 230 | 13.4941 | 13.493 | 0.0011
GEN-2019-068 | 03 CENTRAL | 532875 | DVISTA 6 | 230 | 4.6669 | 4.6664 | 0.0005
GEN-2019-068 | 03 CENTRAL | 533013 | MOUND 4 | 138 | 6.8271 | 6.8263 | 0.0008
GEN-2019-068 | 03 CENTRAL | 533359 | UNIONRG3 | 115 | 3.6979 | 3.6978 | 0.0001
GEN-2019-068 | 03 CENTRAL | 533371 | NORTHVW3 | 115 | 12.0774 | 12.0736 | 0.0038
GEN-2019-068 | 03 CENTRAL | 533374 | MENTOR 3 | 115 | 12.3397 | 12.3347 | 0.005
GEN-2019-068 | 03 CENTRAL | 533379 | SO GATE3 | 115 | 10.1975 | 10.1942 | 0.0033
GEN-2019-068 | 03 CENTRAL | 533380 | SPRGCRK3 | 115 | 3.7906 | 3.7904 | 0.0002
GEN-2019-068 | 03 CENTRAL | 533394 | CORONAD3 | 115 | 6.9686 | 6.9659 | 0.0027
GEN-2019-068 | 03 CENTRAL | 533414 | CITIES 3 | 115 | 7.852 | 7.8471 | 0.0049
GEN-2019-068 | 03 CENTRAL | 533428 | MCPHER 3 | 115 | 10.5159 | 10.5063 | 0.0096
GEN-2019-068 | 03 CENTRAL | 533430 | MNDRGCT3 | 115 | 6.4875 | 6.4866 | 0.0009
GEN-2019-068 | 03 CENTRAL | 533439 | WHEATLD3 | 115 | 6.7596 | 6.7552 | 0.0044
GEN-2019-068 | 03 CENTRAL | 533455 | TWR 33 3 | 115 | 10.1735 | 10.1647 | 0.0088
GEN-2019-068 | 03 CENTRAL | 533506 | DAVIS 2 | 69 | 7.1642 | 7.1619 | 0.0023
GEN-2019-068 | 03 CENTRAL | 533514 | HEC GT 2 | 69 | 7.6507 | 7.6475 | 0.0032
GEN-2019-068 | 03 CENTRAL | 533521 | 17HALST2 | 69 | 6.2205 | 6.2183 | 0.0022
GEN-2019-068 | 03 CENTRAL | 539660 | EHALLTP3 | 115 | 3.2328 | 3.2306 | 0.0022
GEN-2019-068 | 03 CENTRAL | 539662 | ELLSWTH3 | 115 | 3.4499 | 3.4476 | 0.0023
GEN-2019-068 | 03 CENTRAL | 539696 | ST-JOHN3 | 115 | 5.2881 | 5.2835 | 0.0046
GEN-2019-068 | 03 CENTRAL | 539698 | WALDO 3 | 115 | 2.7316 | 2.7302 | 0.0014
GEN-2019-068 | 03 CENTRAL | 539759 | SPRVL 3 | 115 | 12.8273 | 12.8236 | 0.0037
GEN-2019-068 | 03 CENTRAL | 539771 | NFTDODG3 | 115 | 9.7556 | 9.7538 | 0.0018
GEN-2019-068 | 03 CENTRAL | 539800 | CLARKCOUNTY7 | 345 | 12.7785 | 12.7715 | 0.007
GEN-2019-068 | 03 CENTRAL | 539803 | IRONWOOD7 | 345 | 13.1638 | 13.1521 | 0.0117
GEN-2019-068 | 03 CENTRAL | 560082 | G16-050-TAP | 345 | 6.9512 | 6.9494 | 0.0018
GEN-2019-068 | 03 CENTRAL | 587884 | G16-111-TAP | 345 | 9.7651 | 9.7598 | 0.0053
GEN-2019-068 | 03 CENTRAL | 588494 | G17-004-TAP | 345 | 9.3029 | 9.299 | 0.0039
GEN-2019-068 | 03 CENTRAL | 763329 | GEN-2018-116 | 115 | 8.1395 | 8.11 | 0.0295
GEN-2018-064 | 04 SOUTHEAST | 512728 | ARKLIN2 | 69 | 4.0838 | 3.6562 | 0.4276
GEN-2018-064 | 04 SOUTHEAST | 512747 | SSNEWN2 | 69 | 3.3299 | 3.0408 | 0.2891
GEN-2018-064 | 04 SOUTHEAST | 512756 | TONECESTR2 | 69 | 4.2197 | 3.7648 | 0.4549
GEN-2018-064 | 04 SOUTHEAST | 512746 | SSNORT2 | 69 | 3.0469 | 2.8034 | 0.2435
GEN-2018-064 | 04 SOUTHEAST | 512753 | TONNEC2 | 69 | 5.4668 | 4.7262 | 0.7406
GEN-2018-064 | 04 SOUTHEAST | 512745 | SSLINC2 | 69 | 2.9837 | 2.7499 | 0.2338
GEN-2018-064 | 04 SOUTHEAST | 512751 | TONECE5 | 161 | 15.1632 | 14.884 | 0.2792
GEN-2018-064 | 04 SOUTHEAST | 762999 | GEN-2018-064 | 69 | 4.2827 | 3.5007 | 0.782
GEN-2018-064 | 04 SOUTHEAST | 512643 | SILMCTY5 | 161 | 19.7192 | 19.5474 | 0.1718
GEN-2018-064 | 04 SOUTHEAST | 512744 | SSMOSS2 | 69 | 10.1372 | 10.1177 | 0.0195
GEN-2018-064 | 04 SOUTHEAST | 512750 | TONECE7 | 345 | 14.9626 | 14.8882 | 0.0744
GEN-2018-064 | 04 SOUTHEAST | 506935 | FLINTCR7 | 345 | 15.1826 | 15.1109 | 0.0717
GEN-2018-064 | 04 SOUTHEAST | 506948 | SILOAM 5 | 161 | 21.7868 | 21.6369 | 0.1499
GEN-2018-064 | 04 SOUTHEAST | 512642 | SILSPWW5 | 161 | 14.6147 | 14.5379 | 0.0768
GEN-2018-064 | 04 SOUTHEAST | 512650 | GRDA1 7 | 345 | 26.1397 | 26.1146 | 0.0251
GEN-2018-064 | 04 SOUTHEAST | 512737 | SSSWTP2 | 69 | 12.3008 | 12.2721 | 0.0287
GEN-2018-064 | 04 SOUTHEAST | 512820 | SILMCTY2 | 69 | 13.1922 | 13.1592 | 0.033
GEN-2018-071 | 04 SOUTHEAST | 515576 | RANCHRD7 | 345 | 15.0658 | 14.7357 | 0.3301
GEN-2018-071 | 04 SOUTHEAST | 514803 | SOONER 7 | 345 | 28.2956 | 28.1718 | 0.1238
GEN-2018-071 | 04 SOUTHEAST | 515621 | OPENSKY7 | 345 | 13.269 | 13.0886 | 0.1804
GEN-2018-071 | 04 SOUTHEAST | 515688 | FRNTWND7 | 345 | 11.6855 | 11.4885 | 0.197
GEN-2018-071 | 04 SOUTHEAST | 529200 | OMCDLEC7 | 345 | 15.0386 | 14.7098 | 0.3288
GEN-2018-071 | 04 SOUTHEAST | 763069 | G18-071_TAP | 345 | 14.6502 | 14.3181 | 0.3321
GEN-2018-071 | 04 SOUTHEAST | 509755 | WEKIWA-7 | 345 | 22.3506 | 22.3416 | 0.009
GEN-2018-071 | 04 SOUTHEAST | 514802 | SOONER 4 | 138 | 30.9526 | 30.9381 | 0.0145
GEN-2018-071 | 04 SOUTHEAST | 514825 | KAYWIND7 | 345 | 13.2303 | 13.0509 | 0.1794
GEN-2018-071 | 04 SOUTHEAST | 515894 | THUNDER7 | 345 | 10.9745 | 10.9569 | 0.0176
GEN-2018-071 | 04 SOUTHEAST | 516010 | PINTAIL7 | 345 | 16.6869 | 16.6676 | 0.0193
GEN-2018-071 | 04 SOUTHEAST | 516066 | FRNT2WD7 | 345 | 11.6793 | 11.4741 | 0.2052
GEN-2018-071 | 04 SOUTHEAST | 560053 | G15-052T | 345 | 13.3131 | 13.241 | 0.0721
GEN-2018-071 | 04 SOUTHEAST | 560056 | G15-066T | 345 | 19.1787 | 19.135 | 0.0437
GEN-2018-071 | 04 SOUTHEAST | 587804 | G16-119-TAP | 345 | 15.2197 | 15.204 | 0.0157
GEN-2018-071 | 04 SOUTHEAST | 763065 | GEN-2018-071 | 345 | 14.5917 | 14.2594 | 0.3323
GEN-2018-071 | 04 SOUTHEAST | 509757 | WEKIWA-4 | 138 | 33.2483 | 33.2434 | 0.0049
GEN-2018-071 | 04 SOUTHEAST | 509852 | T.NO.--7 | 345 | 24.108 | 24.0992 | 0.0088
GEN-2018-071 | 04 SOUTHEAST | 509870 | SAPLPRD7 | 345 | 22.7944 | 22.7904 | 0.004
GEN-2018-071 | 04 SOUTHEAST | 512694 | CLEVLND7 | 345 | 15.2233 | 15.2111 | 0.0122
GEN-2018-071 | 04 SOUTHEAST | 514704 | MILLERT4 | 138 | 20.2191 | 20.2133 | 0.0058
GEN-2018-071 | 04 SOUTHEAST | 514707 | PERRY 4 | 138 | 10.9156 | 10.9143 | 0.0013
GEN-2018-071 | 04 SOUTHEAST | 514715 | WOODRNG7 | 345 | 18.7369 | 18.7259 | 0.011
GEN-2018-071 | 04 SOUTHEAST | 514798 | SNRPMPT4 | 138 | 20.2791 | 20.2734 | 0.0057
GEN-2018-071 | 04 SOUTHEAST | 514881 | SPRNGCK7 | 345 | 23.3445 | 23.3378 | 0.0067
GEN-2018-071 | 04 SOUTHEAST | 515447 | MORISNT4 | 138 | 13.9231 | 13.9214 | 0.0017
GEN-2018-071 | 04 SOUTHEAST | 516019 | KINGWD 7 | 345 | 16.6292 | 16.61 | 0.0192
GEN-2018-071 | 04 SOUTHEAST | 532794 | ROSEHIL7 | 345 | 18.8487 | 18.8127 | 0.036
GEN-2018-071 | 04 SOUTHEAST | 584900 | GEN-2015-052 | 345 | 13.2613 | 13.1898 | 0.0715
GEN-2018-071 | 04 SOUTHEAST | 585040 | GEN-2015-066 | 345 | 18.9906 | 18.9477 | 0.0429
GEN-2018-071 | 04 SOUTHEAST | 587950 | GEN-2016-119 | 345 | 9.0139 | 9.0089 | 0.005
GEN-2018-071 | 04 SOUTHEAST | 505610 | KEYSTON4 | 138 | 22.9145 | 22.9121 | 0.0024
GEN-2018-071 | 04 SOUTHEAST | 509782 | R.S.S.-7 | 345 | 32.1585 | 32.1549 | 0.0036
GEN-2018-071 | 04 SOUTHEAST | 509812 | SHEFFD-4 | 138 | 26.0329 | 26.0311 | 0.0018
GEN-2018-071 | 04 SOUTHEAST | 509823 | WED-TAP4 | 138 | 19.21 | 19.2089 | 0.0011
GEN-2018-071 | 04 SOUTHEAST | 509851 | P&P WTP4 | 138 | 15.2242 | 15.2233 | 0.0009
GEN-2018-071 | 04 SOUTHEAST | 509871 | SAPLPRD4 | 138 | 33.1488 | 33.1467 | 0.0021
GEN-2018-071 | 04 SOUTHEAST | 509895 | T.NO.2-4 | 138 | 35.3698 | 35.3656 | 0.0042
GEN-2018-071 | 04 SOUTHEAST | 510406 | N.E.S.-7 | 345 | 18.8437 | 18.8413 | 0.0024
GEN-2018-071 | 04 SOUTHEAST | 512726 | SILVCTYGR4 | 138 | 16.4043 | 16.4031 | 0.0012
GEN-2018-071 | 04 SOUTHEAST | 512729 | CLEVLND 4 | 138 | 18.6308 | 18.6276 | 0.0032
GEN-2018-071 | 04 SOUTHEAST | 513596 | IGLOOV 7 | 345 | 19.8028 | 19.8018 | 0.001
GEN-2018-071 | 04 SOUTHEAST | 514706 | COWCRK 4 | 138 | 11.1839 | 11.1825 | 0.0014
GEN-2018-071 | 04 SOUTHEAST | 514714 | WOODRNG4 | 138 | 19.2315 | 19.2289 | 0.0026
GEN-2018-071 | 04 SOUTHEAST | 514743 | OSAGE 4 | 138 | 17.2792 | 17.2768 | 0.0024
GEN-2018-071 | 04 SOUTHEAST | 514799 | SNRPMP 4 | 138 | 11.2198 | 11.2181 | 0.0017
GEN-2018-071 | 04 SOUTHEAST | 514880 | NORTWST7 | 345 | 32.9086 | 32.901 | 0.0076
GEN-2018-071 | 04 SOUTHEAST | 515006 | MORRISN4 | 138 | 13.8958 | 13.894 | 0.0018
GEN-2018-071 | 04 SOUTHEAST | 515011 | STILWTR4 | 138 | 14.4064 | 14.4054 | 0.001
GEN-2018-071 | 04 SOUTHEAST | 515412 | DMNCRKT4 | 138 | 13.827 | 13.8248 | 0.0022
GEN-2018-071 | 04 SOUTHEAST | 515476 | HUNTERS7 | 345 | 13.1988 | 13.1946 | 0.0042
GEN-2018-071 | 04 SOUTHEAST | 515875 | REDNGTN7 | 345 | 16.7149 | 16.7101 | 0.0048
GEN-2018-071 | 04 SOUTHEAST | 515978 | OTOETAP4 | 138 | 16.1943 | 16.1906 | 0.0037
GEN-2018-071 | 04 SOUTHEAST | 515990 | SKELTON7 | 345 | 4.5043 | 4.5037 | 0.0006
GEN-2018-071 | 04 SOUTHEAST | 532791 | BENTON 7 | 345 | 19.0077 | 18.9894 | 0.0183
GEN-2018-071 | 04 SOUTHEAST | 532797 | WOLFCRK7 | 345 | 20.9355 | 20.9319 | 0.0036
GEN-2018-071 | 04 SOUTHEAST | 532800 | LATHAMS7 | 345 | 10.1116 | 10.1054 | 0.0062
GEN-2018-071 | 04 SOUTHEAST | 533062 | ROSEHIL4 | 138 | 30.9062 | 30.8778 | 0.0284
GEN-2018-071 | 04 SOUTHEAST | 560389 | GEN-2010-055 | 138 | 33.2483 | 33.2434 | 0.0049
GEN-2018-071 | 04 SOUTHEAST | 587955 | GEN2016-119B | 345 | 7.7605 | 7.7569 | 0.0036
GEN-2018-071 | 04 SOUTHEAST | 762321 | GEN-2017-164 | 345 | 11.1781 | 11.1743 | 0.0038
GEN-2018-071 | 04 SOUTHEAST | 300131 | 4FISHERTP | 138 | 15.1447 | 15.1437 | 0.001
GEN-2018-071 | 04 SOUTHEAST | 300138 | 4CLEVLND | 138 | 18.6311 | 18.6279 | 0.0032
GEN-2018-071 | 04 SOUTHEAST | 300140 | 4SILVCTY | 138 | 16.5824 | 16.5811 | 0.0013
GEN-2018-071 | 04 SOUTHEAST | 300739 | 7BLACKBERRY | 345 | 15.3686 | 15.3677 | 0.0009
GEN-2018-071 | 04 SOUTHEAST | 301011 | 4REDRCK | 138 | 15.8313 | 15.8278 | 0.0035
GEN-2018-071 | 04 SOUTHEAST | 505609 | KEYSTON5 | 161 | 7.1239 | 7.1237 | 0.0002
GEN-2018-071 | 04 SOUTHEAST | 509759 | JENKS--4 | 138 | 25.4411 | 25.4402 | 0.0009
GEN-2018-071 | 04 SOUTHEAST | 509773 | RSS T1 4 | 138 | 51.5303 | 51.5273 | 0.003
GEN-2018-071 | 04 SOUTHEAST | 509805 | PP----W4 | 138 | 8.3418 | 8.3415 | 0.0003
GEN-2018-071 | 04 SOUTHEAST | 509807 | ONETA--7 | 345 | 29.2478 | 29.2458 | 0.002
GEN-2018-071 | 04 SOUTHEAST | 509815 | S.S.---4 | 138 | 28.8458 | 28.8437 | 0.0021
GEN-2018-071 | 04 SOUTHEAST | 509817 | T.NO.--4 | 138 | 35.4016 | 35.3976 | 0.004
GEN-2018-071 | 04 SOUTHEAST | 509834 | COGENT 7 | 345 | 29.7975 | 29.7945 | 0.003
GEN-2018-071 | 04 SOUTHEAST | 509848 | OAKSWTP4 | 138 | 24.9315 | 24.9306 | 0.0009
GEN-2018-071 | 04 SOUTHEAST | 509865 | CARSONT4 | 138 | 11.9445 | 11.9441 | 0.0004
GEN-2018-071 | 04 SOUTHEAST | 509875 | RSS T2 4 | 138 | 52.4475 | 52.4445 | 0.003
GEN-2018-071 | 04 SOUTHEAST | 509888 | 72ELWOD4 | 138 | 23.3708 | 23.3699 | 0.0009
GEN-2018-071 | 04 SOUTHEAST | 509896 | DENV_WTAP4 | 138 | 28.11 | 28.108 | 0.002
GEN-2018-071 | 04 SOUTHEAST | 510376 | WEBBTAP4 | 138 | 7.6084 | 7.6081 | 0.0003
GEN-2018-071 | 04 SOUTHEAST | 510380 | DELWARE7 | 345 | 11.7555 | 11.7546 | 0.0009
GEN-2018-071 | 04 SOUTHEAST | 512865 | GREC TAP5 | 345 | 24.9713 | 24.9703 | 0.001
GEN-2018-071 | 04 SOUTHEAST | 513593 | IGLOOV1 5 | 161 | 16.7122 | 16.7119 | 0.0003
GEN-2018-071 | 04 SOUTHEAST | 513595 | IGLOOV2 5 | 161 | 16.7122 | 16.7119 | 0.0003
GEN-2018-071 | 04 SOUTHEAST | 514705 | COWCRK 2 | 69 | 4.0401 | 4.04 | 0.0001
GEN-2018-071 | 04 SOUTHEAST | 514708 | OTTER 4 | 138 | 8.6952 | 8.6946 | 0.0006
GEN-2018-071 | 04 SOUTHEAST | 514709 | FRMNTAP4 | 138 | 17.9839 | 17.9818 | 0.0021
GEN-2018-071 | 04 SOUTHEAST | 514711 | WAUKOTP4 | 138 | 15.7289 | 15.7274 | 0.0015
GEN-2018-071 | 04 SOUTHEAST | 514713 | WRVALLY4 | 138 | 8.4747 | 8.474 | 0.0007
GEN-2018-071 | 04 SOUTHEAST | 514733 | MARSHL 4 | 138 | 7.9487 | 7.9484 | 0.0003
GEN-2018-071 | 04 SOUTHEAST | 514737 | OTOE 4 | 138 | 16.1494 | 16.1457 | 0.0037
GEN-2018-071 | 04 SOUTHEAST | 514742 | OSGE 2 | 69 | 19.0954 | 19.0946 | 0.0008
GEN-2018-071 | 04 SOUTHEAST | 514758 | STDBEAR4 | 138 | 14.3651 | 14.3634 | 0.0017
GEN-2018-071 | 04 SOUTHEAST | 514761 | WHEAGLE4 | 138 | 16.3199 | 16.3177 | 0.0022
GEN-2018-071 | 04 SOUTHEAST | 514770 | MARLNDT4 | 138 | 11.1905 | 11.1895 | 0.001
GEN-2018-071 | 04 SOUTHEAST | 514879 | NORTWST4 | 138 | 44.7892 | 44.7853 | 0.0039
GEN-2018-071 | 04 SOUTHEAST | 514901 | CIMARON7 | 345 | 34.2931 | 34.2878 | 0.0053
GEN-2018-071 | 04 SOUTHEAST | 514908 | ARCADIA7 | 345 | 28.6269 | 28.625 | 0.0019
GEN-2018-071 | 04 SOUTHEAST | 514909 | REDBUD 7 | 345 | 27.6026 | 27.601 | 0.0016
GEN-2018-071 | 04 SOUTHEAST | 515009 | MCELROY4 | 138 | 14.1486 | 14.1477 | 0.0009
GEN-2018-071 | 04 SOUTHEAST | 515235 | PECANCK7 | 345 | 22.1253 | 22.1247 | 0.0006
GEN-2018-071 | 04 SOUTHEAST | 515400 | DMANCRK4 | 138 | 8.087 | 8.0863 | 0.0007
GEN-2018-071 | 04 SOUTHEAST | 515477 | CHSHLMV7 | 345 | 13.1796 | 13.1754 | 0.0042
GEN-2018-071 | 04 SOUTHEAST | 515497 | MATHWSN7 | 345 | 32.7952 | 32.7886 | 0.0066
GEN-2018-071 | 04 SOUTHEAST | 515543 | RENFROW7 | 345 | 12.8614 | 12.8583 | 0.0031
GEN-2018-071 | 04 SOUTHEAST | 515574 | SPGVLLY4 | 138 | 10.8391 | 10.8387 | 0.0004
GEN-2018-071 | 04 SOUTHEAST | 515877 | REDDIRT7 | 345 | 16.7106 | 16.7058 | 0.0048
GEN-2018-071 | 04 SOUTHEAST | 532780 | CANEYRV7 | 345 | 9.4765 | 9.4718 | 0.0047
GEN-2018-071 | 04 SOUTHEAST | 532796 | WICHITA7 | 345 | 23.7708 | 23.7599 | 0.0109
GEN-2018-071 | 04 SOUTHEAST | 532799 | WAVERLY7 | 345 | 17.6458 | 17.6435 | 0.0023
GEN-2018-071 | 04 SOUTHEAST | 532801 | ELKRVR17 | 345 | 8.9569 | 8.9521 | 0.0048
GEN-2018-071 | 04 SOUTHEAST | 532986 | BENTON 4 | 138 | 27.7644 | 27.75 | 0.0144
GEN-2018-071 | 04 SOUTHEAST | 532991 | WEAVER 4 | 138 | 21.9573 | 21.9463 | 0.011
GEN-2018-071 | 04 SOUTHEAST | 533039 | ELPASO 4 | 138 | 24.7628 | 24.7501 | 0.0127
GEN-2018-071 | 04 SOUTHEAST | 533068 | STEARMN4 | 138 | 19.3341 | 19.3258 | 0.0083
GEN-2018-071 | 04 SOUTHEAST | 533653 | WOLFCRK2 | 69 | 5.9769 | 5.9769 | 0
GEN-2018-071 | 04 SOUTHEAST | 542965 | W.GRDNR7 | 345 | 31.7637 | 31.7628 | 0.0009
GEN-2018-071 | 04 SOUTHEAST | 588039 | G16133G16146 | 345 | 32.1585 | 32.1549 | 0.0036
GEN-2018-071 | 04 SOUTHEAST | 588190 | GEN-2016-128 | 345 | 4.3057 | 4.3052 | 0.0005
GEN-2018-071 | 04 SOUTHEAST | 762342 | GEN-2017-178 | 345 | 7.8339 | 7.832 | 0.0019
GEN-2018-071 | 04 SOUTHEAST | 762636 | GEN-2018-028 | 138 | 35.3537 | 35.3496 | 0.0041
GEN-2018-072 | 04 SOUTHEAST | 515576 | RANCHRD7 | 345 | 15.0658 | 14.7632 | 0.3026
GEN-2018-072 | 04 SOUTHEAST | 514803 | SOONER 7 | 345 | 28.2956 | 28.1823 | 0.1133
GEN-2018-072 | 04 SOUTHEAST | 515621 | OPENSKY7 | 345 | 13.269 | 13.1037 | 0.1653
GEN-2018-072 | 04 SOUTHEAST | 515688 | FRNTWND7 | 345 | 11.6855 | 11.505 | 0.1805
GEN-2018-072 | 04 SOUTHEAST | 529200 | OMCDLEC7 | 345 | 15.0386 | 14.7372 | 0.3014
GEN-2018-072 | 04 SOUTHEAST | 763069 | G18-071_TAP | 345 | 14.6502 | 14.3458 | 0.3044
GEN-2018-072 | 04 SOUTHEAST | 509755 | WEKIWA-7 | 345 | 22.3506 | 22.3424 | 0.0082
GEN-2018-072 | 04 SOUTHEAST | 514802 | SOONER 4 | 138 | 30.9526 | 30.9394 | 0.0132
GEN-2018-072 | 04 SOUTHEAST | 514825 | KAYWIND7 | 345 | 13.2303 | 13.066 | 0.1643
GEN-2018-072 | 04 SOUTHEAST | 515894 | THUNDER7 | 345 | 10.9745 | 10.9584 | 0.0161
GEN-2018-072 | 04 SOUTHEAST | 516010 | PINTAIL7 | 345 | 16.6869 | 16.6692 | 0.0177
GEN-2018-072 | 04 SOUTHEAST | 516066 | FRNT2WD7 | 345 | 11.6793 | 11.4913 | 0.188
GEN-2018-072 | 04 SOUTHEAST | 560053 | G15-052T | 345 | 13.3131 | 13.2471 | 0.066
GEN-2018-072 | 04 SOUTHEAST | 560056 | G15-066T | 345 | 19.1787 | 19.1387 | 0.04
GEN-2018-072 | 04 SOUTHEAST | 587804 | G16-119-TAP | 345 | 15.2197 | 15.2054 | 0.0143
GEN-2018-072 | 04 SOUTHEAST | 763065 | GEN-2018-071 | 345 | 14.5917 | 14.2871 | 0.3046
GEN-2018-072 | 04 SOUTHEAST | 509757 | WEKIWA-4 | 138 | 33.2483 | 33.2438 | 0.0045
GEN-2018-072 | 04 SOUTHEAST | 509852 | T.NO.--7 | 345 | 24.108 | 24.0999 | 0.0081
GEN-2018-072 | 04 SOUTHEAST | 509870 | SAPLPRD7 | 345 | 22.7944 | 22.7907 | 0.0037
GEN-2018-072 | 04 SOUTHEAST | 512694 | CLEVLND7 | 345 | 15.2233 | 15.2122 | 0.0111
GEN-2018-072 | 04 SOUTHEAST | 514704 | MILLERT4 | 138 | 20.2191 | 20.2138 | 0.0053
GEN-2018-072 | 04 SOUTHEAST | 514707 | PERRY 4 | 138 | 10.9156 | 10.9144 | 0.0012
GEN-2018-072 | 04 SOUTHEAST | 514715 | WOODRNG7 | 345 | 18.7369 | 18.7268 | 0.0101
GEN-2018-072 | 04 SOUTHEAST | 514798 | SNRPMPT4 | 138 | 20.2791 | 20.2739 | 0.0052
GEN-2018-072 | 04 SOUTHEAST | 514881 | SPRNGCK7 | 345 | 23.3445 | 23.3384 | 0.0061
GEN-2018-072 | 04 SOUTHEAST | 515447 | MORISNT4 | 138 | 13.9231 | 13.9215 | 0.0016
GEN-2018-072 | 04 SOUTHEAST | 516019 | KINGWD 7 | 345 | 16.6292 | 16.6116 | 0.0176
GEN-2018-072 | 04 SOUTHEAST | 532794 | ROSEHIL7 | 345 | 18.8487 | 18.8158 | 0.0329
GEN-2018-072 | 04 SOUTHEAST | 584900 | GEN-2015-052 | 345 | 13.2613 | 13.1959 | 0.0654
GEN-2018-072 | 04 SOUTHEAST | 585040 | GEN-2015-066 | 345 | 18.9906 | 18.9514 | 0.0392
GEN-2018-072 | 04 SOUTHEAST | 587950 | GEN-2016-119 | 345 | 9.0139 | 9.0093 | 0.0046
GEN-2018-072 | 04 SOUTHEAST | 505610 | KEYSTON4 | 138 | 22.9145 | 22.9123 | 0.0022
GEN-2018-072 | 04 SOUTHEAST | 509782 | R.S.S.-7 | 345 | 32.1585 | 32.1552 | 0.0033
GEN-2018-072 | 04 SOUTHEAST | 509812 | SHEFFD-4 | 138 | 26.0329 | 26.0312 | 0.0017
GEN-2018-072 | 04 SOUTHEAST | 509823 | WED-TAP4 | 138 | 19.21 | 19.209 | 0.001
GEN-2018-072 | 04 SOUTHEAST | 509851 | P&P WTP4 | 138 | 15.2242 | 15.2234 | 0.0008
GEN-2018-072 | 04 SOUTHEAST | 509871 | SAPLPRD4 | 138 | 33.1488 | 33.1468 | 0.002
GEN-2018-072 | 04 SOUTHEAST | 509895 | T.NO.2-4 | 138 | 35.3698 | 35.366 | 0.0038
GEN-2018-072 | 04 SOUTHEAST | 510406 | N.E.S.-7 | 345 | 18.8437 | 18.8415 | 0.0022
GEN-2018-072 | 04 SOUTHEAST | 512726 | SILVCTYGR4 | 138 | 16.4043 | 16.4032 | 0.0011
GEN-2018-072 | 04 SOUTHEAST | 512729 | CLEVLND 4 | 138 | 18.6308 | 18.6279 | 0.0029
GEN-2018-072 | 04 SOUTHEAST | 513596 | IGLOOV 7 | 345 | 19.8028 | 19.8019 | 0.0009
GEN-2018-072 | 04 SOUTHEAST | 514706 | COWCRK 4 | 138 | 11.1839 | 11.1827 | 0.0012
GEN-2018-072 | 04 SOUTHEAST | 514714 | WOODRNG4 | 138 | 19.2315 | 19.2291 | 0.0024
GEN-2018-072 | 04 SOUTHEAST | 514743 | OSAGE 4 | 138 | 17.2792 | 17.277 | 0.0022
GEN-2018-072 | 04 SOUTHEAST | 514799 | SNRPMP 4 | 138 | 11.2198 | 11.2182 | 0.0016
GEN-2018-072 | 04 SOUTHEAST | 514880 | NORTWST7 | 345 | 32.9086 | 32.9016 | 0.007
GEN-2018-072 | 04 SOUTHEAST | 515006 | MORRISN4 | 138 | 13.8958 | 13.8942 | 0.0016
GEN-2018-072 | 04 SOUTHEAST | 515011 | STILWTR4 | 138 | 14.4064 | 14.4054 | 0.001
GEN-2018-072 | 04 SOUTHEAST | 515412 | DMNCRKT4 | 138 | 13.827 | 13.825 | 0.002
GEN-2018-072 | 04 SOUTHEAST | 515476 | HUNTERS7 | 345 | 13.1988 | 13.195 | 0.0038
GEN-2018-072 | 04 SOUTHEAST | 515875 | REDNGTN7 | 345 | 16.7149 | 16.7105 | 0.0044
GEN-2018-072 | 04 SOUTHEAST | 515978 | OTOETAP4 | 138 | 16.1943 | 16.1909 | 0.0034
GEN-2018-072 | 04 SOUTHEAST | 515990 | SKELTON7 | 345 | 4.5043 | 4.5037 | 0.0006
GEN-2018-072 | 04 SOUTHEAST | 532791 | BENTON 7 | 345 | 19.0077 | 18.9909 | 0.0168
GEN-2018-072 | 04 SOUTHEAST | 532797 | WOLFCRK7 | 345 | 20.9355 | 20.9322 | 0.0033
GEN-2018-072 | 04 SOUTHEAST | 532800 | LATHAMS7 | 345 | 10.1116 | 10.1059 | 0.0057
GEN-2018-072 | 04 SOUTHEAST | 533062 | ROSEHIL4 | 138 | 30.9062 | 30.8802 | 0.026
GEN-2018-072 | 04 SOUTHEAST | 560389 | GEN-2010-055 | 138 | 33.2483 | 33.2438 | 0.0045
GEN-2018-072 | 04 SOUTHEAST | 587955 | GEN2016-119B | 345 | 7.7605 | 7.7572 | 0.0033
GEN-2018-072 | 04 SOUTHEAST | 762321 | GEN-2017-164 | 345 | 11.1781 | 11.1747 | 0.0034
GEN-2018-072 | 04 SOUTHEAST | 300131 | 4FISHERTP | 138 | 15.1447 | 15.1438 | 0.0009
GEN-2018-072 | 04 SOUTHEAST | 300138 | 4CLEVLND | 138 | 18.6311 | 18.6281 | 0.003
GEN-2018-072 | 04 SOUTHEAST | 300140 | 4SILVCTY | 138 | 16.5824 | 16.5812 | 0.0012
GEN-2018-072 | 04 SOUTHEAST | 300739 | 7BLACKBERRY | 345 | 15.3686 | 15.3678 | 0.0008
GEN-2018-072 | 04 SOUTHEAST | 301011 | 4REDRCK | 138 | 15.8313 | 15.8281 | 0.0032
GEN-2018-072 | 04 SOUTHEAST | 505609 | KEYSTON5 | 161 | 7.1239 | 7.1237 | 0.0002
GEN-2018-072 | 04 SOUTHEAST | 509759 | JENKS--4 | 138 | 25.4411 | 25.4403 | 0.0008
GEN-2018-072 | 04 SOUTHEAST | 509773 | RSS T1 4 | 138 | 51.5303 | 51.5276 | 0.0027
GEN-2018-072 | 04 SOUTHEAST | 509805 | PP----W4 | 138 | 8.3418 | 8.3415 | 0.0003
GEN-2018-072 | 04 SOUTHEAST | 509807 | ONETA--7 | 345 | 29.2478 | 29.2459 | 0.0019
GEN-2018-072 | 04 SOUTHEAST | 509815 | S.S.---4 | 138 | 28.8458 | 28.8439 | 0.0019
GEN-2018-072 | 04 SOUTHEAST | 509817 | T.NO.--4 | 138 | 35.4016 | 35.3979 | 0.0037
GEN-2018-072 | 04 SOUTHEAST | 509834 | COGENT 7 | 345 | 29.7975 | 29.7947 | 0.0028
GEN-2018-072 | 04 SOUTHEAST | 509848 | OAKSWTP4 | 138 | 24.9315 | 24.9307 | 0.0008
GEN-2018-072 | 04 SOUTHEAST | 509865 | CARSONT4 | 138 | 11.9445 | 11.9441 | 0.0004
GEN-2018-072 | 04 SOUTHEAST | 509875 | RSS T2 4 | 138 | 52.4475 | 52.4447 | 0.0028
GEN-2018-072 | 04 SOUTHEAST | 509888 | 72ELWOD4 | 138 | 23.3708 | 23.37 | 0.0008
GEN-2018-072 | 04 SOUTHEAST | 509896 | DENV_WTAP4 | 138 | 28.11 | 28.1082 | 0.0018
GEN-2018-072 | 04 SOUTHEAST | 510376 | WEBBTAP4 | 138 | 7.6084 | 7.6081 | 0.0003
GEN-2018-072 | 04 SOUTHEAST | 510380 | DELWARE7 | 345 | 11.7555 | 11.7547 | 0.0008
GEN-2018-072 | 04 SOUTHEAST | 512865 | GREC TAP5 | 345 | 24.9713 | 24.9704 | 0.0009
GEN-2018-072 | 04 SOUTHEAST | 513593 | IGLOOV1 5 | 161 | 16.7122 | 16.7119 | 0.0003
GEN-2018-072 | 04 SOUTHEAST | 513595 | IGLOOV2 5 | 161 | 16.7122 | 16.7119 | 0.0003
GEN-2018-072 | 04 SOUTHEAST | 514705 | COWCRK 2 | 69 | 4.0401 | 4.04 | 0.0001
GEN-2018-072 | 04 SOUTHEAST | 514708 | OTTER 4 | 138 | 8.6952 | 8.6946 | 0.0006
GEN-2018-072 | 04 SOUTHEAST | 514709 | FRMNTAP4 | 138 | 17.9839 | 17.9819 | 0.002
GEN-2018-072 | 04 SOUTHEAST | 514711 | WAUKOTP4 | 138 | 15.7289 | 15.7275 | 0.0014
GEN-2018-072 | 04 SOUTHEAST | 514713 | WRVALLY4 | 138 | 8.4747 | 8.4741 | 0.0006
GEN-2018-072 | 04 SOUTHEAST | 514733 | MARSHL 4 | 138 | 7.9487 | 7.9484 | 0.0003
GEN-2018-072 | 04 SOUTHEAST | 514737 | OTOE 4 | 138 | 16.1494 | 16.1461 | 0.0033
GEN-2018-072 | 04 SOUTHEAST | 514742 | OSGE 2 | 69 | 19.0954 | 19.0947 | 0.0007
GEN-2018-072 | 04 SOUTHEAST | 514758 | STDBEAR4 | 138 | 14.3651 | 14.3635 | 0.0016
GEN-2018-072 | 04 SOUTHEAST | 514761 | WHEAGLE4 | 138 | 16.3199 | 16.3179 | 0.002
GEN-2018-072 | 04 SOUTHEAST | 514770 | MARLNDT4 | 138 | 11.1905 | 11.1896 | 0.0009
GEN-2018-072 | 04 SOUTHEAST | 514879 | NORTWST4 | 138 | 44.7892 | 44.7856 | 0.0036
GEN-2018-072 | 04 SOUTHEAST | 514901 | CIMARON7 | 345 | 34.2931 | 34.2882 | 0.0049
GEN-2018-072 | 04 SOUTHEAST | 514908 | ARCADIA7 | 345 | 28.6269 | 28.6252 | 0.0017
GEN-2018-072 | 04 SOUTHEAST | 514909 | REDBUD 7 | 345 | 27.6026 | 27.6012 | 0.0014
GEN-2018-072 | 04 SOUTHEAST | 515009 | MCELROY4 | 138 | 14.1486 | 14.1478 | 0.0008
GEN-2018-072 | 04 SOUTHEAST | 515235 | PECANCK7 | 345 | 22.1253 | 22.1247 | 0.0006
GEN-2018-072 | 04 SOUTHEAST | 515400 | DMANCRK4 | 138 | 8.087 | 8.0863 | 0.0007
GEN-2018-072 | 04 SOUTHEAST | 515477 | CHSHLMV7 | 345 | 13.1796 | 13.1758 | 0.0038
GEN-2018-072 | 04 SOUTHEAST | 515497 | MATHWSN7 | 345 | 32.7952 | 32.7891 | 0.0061
GEN-2018-072 | 04 SOUTHEAST | 515543 | RENFROW7 | 345 | 12.8614 | 12.8586 | 0.0028
GEN-2018-072 | 04 SOUTHEAST | 515574 | SPGVLLY4 | 138 | 10.8391 | 10.8387 | 0.0004
GEN-2018-072 | 04 SOUTHEAST | 515877 | REDDIRT7 | 345 | 16.7106 | 16.7062 | 0.0044
GEN-2018-072 | 04 SOUTHEAST | 532780 | CANEYRV7 | 345 | 9.4765 | 9.4722 | 0.0043
GEN-2018-072 | 04 SOUTHEAST | 532796 | WICHITA7 | 345 | 23.7708 | 23.7609 | 0.0099
GEN-2018-072 | 04 SOUTHEAST | 532799 | WAVERLY7 | 345 | 17.6458 | 17.6437 | 0.0021
GEN-2018-072 | 04 SOUTHEAST | 532801 | ELKRVR17 | 345 | 8.9569 | 8.9525 | 0.0044
GEN-2018-072 | 04 SOUTHEAST | 532986 | BENTON 4 | 138 | 27.7644 | 27.7513 | 0.0131
GEN-2018-072 | 04 SOUTHEAST | 532991 | WEAVER 4 | 138 | 21.9573 | 21.9473 | 0.01
GEN-2018-072 | 04 SOUTHEAST | 533039 | ELPASO 4 | 138 | 24.7628 | 24.7511 | 0.0117
GEN-2018-072 | 04 SOUTHEAST | 533068 | STEARMN4 | 138 | 19.3341 | 19.3265 | 0.0076
GEN-2018-072 | 04 SOUTHEAST | 533653 | WOLFCRK2 | 69 | 5.9769 | 5.9769 | 0
GEN-2018-072 | 04 SOUTHEAST | 542965 | W.GRDNR7 | 345 | 31.7637 | 31.7629 | 0.0008
GEN-2018-072 | 04 SOUTHEAST | 588039 | G16133G16146 | 345 | 32.1585 | 32.1552 | 0.0033
GEN-2018-072 | 04 SOUTHEAST | 588190 | GEN-2016-128 | 345 | 4.3057 | 4.3052 | 0.0005
GEN-2018-072 | 04 SOUTHEAST | 762342 | GEN-2017-178 | 345 | 7.8339 | 7.8322 | 0.0017
GEN-2018-072 | 04 SOUTHEAST | 762636 | GEN-2018-028 | 138 | 35.3537 | 35.35 | 0.0037
GEN-2018-079 | 04 SOUTHEAST | 763113 | G18-079-TAP | 138 | 9.6699 | 8.9689 | 0.701
GEN-2018-079 | 04 SOUTHEAST | 510379 | DELWARE4 | 138 | 11.509 | 10.9682 | 0.5408
GEN-2018-079 | 04 SOUTHEAST | 512734 | FARML 4 | 138 | 8.2465 | 8.0446 | 0.2019
GEN-2018-079 | 04 SOUTHEAST | 763109 | GEN-2018-079 | 138 | 7.025 | 6.3007 | 0.7243
GEN-2018-079 | 04 SOUTHEAST | 510378 | SCOFCTY4 | 138 | 8.5616 | 8.4391 | 0.1225
GEN-2018-079 | 04 SOUTHEAST | 510380 | DELWARE7 | 345 | 11.7555 | 11.6011 | 0.1544
GEN-2018-079 | 04 SOUTHEAST | 512735 | COFCTY2 | 69 | 8.7043 | 8.6275 | 0.0768
GEN-2018-079 | 04 SOUTHEAST | 510406 | N.E.S.-7 | 345 | 18.8437 | 18.7687 | 0.075
GEN-2018-079 | 04 SOUTHEAST | 510420 | SCOFFEYV4 | 138 | 8.1802 | 8.0683 | 0.1119
GEN-2018-079 | 04 SOUTHEAST | 510422 | COFFEYT4 | 138 | 9.8626 | 9.768 | 0.0946
GEN-2018-079 | 04 SOUTHEAST | 532793 | NEOSHO 7 | 345 | 17.5726 | 17.5179 | 0.0547
GEN-2018-079 | 04 SOUTHEAST | 300739 | 7BLACKBERRY | 345 | 15.3686 | 15.3554 | 0.0132
GEN-2018-079 | 04 SOUTHEAST | 509807 | ONETA--7 | 345 | 29.2478 | 29.2297 | 0.0181
GEN-2018-079 | 04 SOUTHEAST | 509852 | T.NO.--7 | 345 | 24.108 | 24.0795 | 0.0285
GEN-2018-079 | 04 SOUTHEAST | 510386 | NBVILLE4 | 138 | 9.2701 | 9.2355 | 0.0346
GEN-2018-079 | 04 SOUTHEAST | 532777 | G17-009-TAP | 345 | 11.4737 | 11.4567 | 0.017
GEN-2018-079 | 04 SOUTHEAST | 532937 | NEOSHO 5 | 161 | 22.653 | 22.613 | 0.04
GEN-2018-079 | 04 SOUTHEAST | 533002 | DEARING4 | 138 | 9.2314 | 9.166 | 0.0654
GEN-2018-079 | 04 SOUTHEAST | 533021 | NEOSHO 4 | 138 | 24.2444 | 24.1964 | 0.048
GEN-2018-079 | 04 SOUTHEAST | 760921 | G17-209-TAP | 345 | 18.8437 | 18.8394 | 0.0043
GEN-2018-079 | 04 SOUTHEAST | 762680 | GEN-2018-032 | 345 | 11.5309 | 11.5074 | 0.0235
GEN-2018-079 | 04 SOUTHEAST | 300740 | 7SPORTSMAN | 345 | 23.7932 | 23.7881 | 0.0051
GEN-2018-079 | 04 SOUTHEAST | 300949 | 7JASPER | 345 | 12.5964 | 12.5904 | 0.006
GEN-2018-079 | 04 SOUTHEAST | 509745 | CLARKSV7 | 345 | 20.6199 | 20.6159 | 0.004
GEN-2018-079 | 04 SOUTHEAST | 509755 | WEKIWA-7 | 345 | 22.3506 | 22.3402 | 0.0104
GEN-2018-079 | 04 SOUTHEAST | 509782 | R.S.S.-7 | 345 | 32.1585 | 32.1487 | 0.0098
GEN-2018-079 | 04 SOUTHEAST | 509806 | ONETA--4 | 138 | 49.9736 | 49.9548 | 0.0188
GEN-2018-079 | 04 SOUTHEAST | 509836 | OEC 7 | 345 | 28.9576 | 28.94 | 0.0176
GEN-2018-079 | 04 SOUTHEAST | 509895 | T.NO.2-4 | 138 | 35.3698 | 35.3497 | 0.0201
GEN-2018-079 | 04 SOUTHEAST | 510391 | BV-SE--4 | 138 | 11.9597 | 11.936 | 0.0237
GEN-2018-079 | 04 SOUTHEAST | 512694 | CLEVLND7 | 345 | 15.2233 | 15.2184 | 0.0049
GEN-2018-079 | 04 SOUTHEAST | 513596 | IGLOOV 7 | 345 | 19.8028 | 19.7982 | 0.0046
GEN-2018-079 | 04 SOUTHEAST | 532778 | GEN-2017-009 | 345 | 10.6042 | 10.5897 | 0.0145
GEN-2018-079 | 04 SOUTHEAST | 532780 | CANEYRV7 | 345 | 9.4765 | 9.4731 | 0.0034
GEN-2018-079 | 04 SOUTHEAST | 532797 | WOLFCRK7 | 345 | 20.9355 | 20.9328 | 0.0027
GEN-2018-079 | 04 SOUTHEAST | 532935 | MARMTNW5 | 161 | 7.7966 | 7.7954 | 0.0012
GEN-2018-079 | 04 SOUTHEAST | 533003 | LIBERTY4 | 138 | 7.2835 | 7.2544 | 0.0291
GEN-2018-079 | 04 SOUTHEAST | 533004 | MONTGOM4 | 138 | 6.9412 | 6.9162 | 0.025
GEN-2018-079 | 04 SOUTHEAST | 533020 | NEOSHOS4 | 138 | 24.2032 | 24.1553 | 0.0479
GEN-2018-079 | 04 SOUTHEAST | 533022 | NEOSHON4 | 138 | 24.1308 | 24.0832 | 0.0476
GEN-2018-079 | 04 SOUTHEAST | 533688 | DEARING2 | 69 | 7.9047 | 7.8832 | 0.0215
GEN-2018-079 | 04 SOUTHEAST | 533778 | NEOSHOS2 | 69 | 22.8797 | 22.8602 | 0.0195
GEN-2018-079 | 04 SOUTHEAST | 542981 | LACYGNE7 | 345 | 26.1692 | 26.1648 | 0.0044
GEN-2018-079 | 04 SOUTHEAST | 547469 | RIV4525 | 161 | 23.8483 | 23.8439 | 0.0044
GEN-2018-079 | 04 SOUTHEAST | 760914 | GEN-2017-209 | 345 | 18.3644 | 18.3603 | 0.0041
GEN-2018-082 | 04 SOUTHEAST | 510907 | PITTSB-7 | 345 | 16.4511 | 16.0732 | 0.3779
GEN-2018-082 | 04 SOUTHEAST | 510911 | VALIANT7 | 345 | 16.6284 | 16.5386 | 0.0898
GEN-2018-082 | 04 SOUTHEAST | 510925 | KIOWA 7 | 345 | 16.1028 | 15.7405 | 0.3623
GEN-2018-082 | 04 SOUTHEAST | 514809 | JOHNCO 7 | 345 | 10.9329 | 10.8901 | 0.0428
GEN-2018-082 | 04 SOUTHEAST | 515045 | SEMINOL7 | 345 | 30.8428 | 30.7531 | 0.0897
GEN-2018-082 | 04 SOUTHEAST | 515422 | C-RIVER7 | 345 | 11.6454 | 11.5669 | 0.0785
GEN-2018-082 | 04 SOUTHEAST | 763131 | GEN-2018-082 | 345 | 10.1533 | 9.7696 | 0.3837
GEN-2018-082 | 04 SOUTHEAST | 507455 | TURK 7 | 345 | 11.6362 | 11.6237 | 0.0125
GEN-2018-082 | 04 SOUTHEAST | 508072 | NWTXARK7 | 345 | 16.4948 | 16.4727 | 0.0221
GEN-2018-082 | 04 SOUTHEAST | 508298 | LYDIA 7 | 345 | 13.4983 | 13.4788 | 0.0195
GEN-2018-082 | 04 SOUTHEAST | 510918 | VALIANT4 | 138 | 15.7903 | 15.7659 | 0.0244
GEN-2018-082 | 04 SOUTHEAST | 510946 | C-RIVER4 | 138 | 13.6517 | 13.6182 | 0.0335
GEN-2018-082 | 04 SOUTHEAST | 514808 | JOHNCO 4 | 138 | 15.4874 | 15.4646 | 0.0228
GEN-2018-082 | 04 SOUTHEAST | 514908 | ARCADIA7 | 345 | 28.6269 | 28.621 | 0.0059
GEN-2018-082 | 04 SOUTHEAST | 514934 | DRAPER 7 | 345 | 26.1641 | 26.1398 | 0.0243
GEN-2018-082 | 04 SOUTHEAST | 515044 | SEMINOL4 | 138 | 40.4325 | 40.3948 | 0.0377
GEN-2018-082 | 04 SOUTHEAST | 515136 | SUNNYSD7 | 345 | 12.0848 | 12.0593 | 0.0255
GEN-2018-082 | 04 SOUTHEAST | 516006 | DMNDSPG7 | 345 | 7.4023 | 7.3838 | 0.0185
GEN-2018-082 | 04 SOUTHEAST | 521157 | HUGO 7 | 345 | 12.5857 | 12.5448 | 0.0409
GEN-2018-082 | 04 SOUTHEAST | 588839 | FIREWHL-TAP | 345 | 20.1846 | 20.1376 | 0.047
GEN-2018-082 | 04 SOUTHEAST | 760830 | GEN-2017-149 | 345 | 4.1868 | 4.1822 | 0.0046
GEN-2018-082 | 04 SOUTHEAST | 507454 | TURK 4 | 138 | 27.2509 | 27.2361 | 0.0148
GEN-2018-082 | 04 SOUTHEAST | 508071 | NWTXARK4 | 138 | 28.0292 | 28.0076 | 0.0216
GEN-2018-082 | 04 SOUTHEAST | 508359 | WELSH 7 | 345 | 21.3102 | 21.2976 | 0.0126
GEN-2018-082 | 04 SOUTHEAST | 508841 | WILKES 7 | 345 | 17.8224 | 17.816 | 0.0064
GEN-2018-082 | 04 SOUTHEAST | 510866 | V-WEYCO4 | 138 | 9.8522 | 9.8427 | 0.0095
GEN-2018-082 | 04 SOUTHEAST | 510886 | IDABEL-4 | 138 | 6.8774 | 6.8743 | 0.0031
GEN-2018-082 | 04 SOUTHEAST | 510901 | HUGO---4 | 138 | 3.5315 | 3.5303 | 0.0012
GEN-2018-082 | 04 SOUTHEAST | 510910 | VALIANT2 | 69 | 7.4325 | 7.4298 | 0.0027
GEN-2018-082 | 04 SOUTHEAST | 510951 | TALAWANDA 4 | 138 | 9.756 | 9.7456 | 0.0104
GEN-2018-082 | 04 SOUTHEAST | 511568 | TERRYRD7 | 345 | 11.0146 | 11.0081 | 0.0065
GEN-2018-082 | 04 SOUTHEAST | 514880 | NORTWST7 | 345 | 32.9086 | 32.9022 | 0.0064
GEN-2018-082 | 04 SOUTHEAST | 514907 | ARCADIA4 | 138 | 47.2233 | 47.2174 | 0.0059
GEN-2018-082 | 04 SOUTHEAST | 514909 | REDBUD 7 | 345 | 27.6026 | 27.5977 | 0.0049
GEN-2018-082 | 04 SOUTHEAST | 514933 | DRAPER 4 | 138 | 42.9122 | 42.8935 | 0.0187
GEN-2018-082 | 04 SOUTHEAST | 515055 | MAUD 4 | 138 | 20.1325 | 20.1258 | 0.0067
GEN-2018-082 | 04 SOUTHEAST | 515100 | PAOLI- 4 | 138 | 10.3088 | 10.3063 | 0.0025
GEN-2018-082 | 04 SOUTHEAST | 515120 | RUSSET-4 | 138 | 11.3858 | 11.3759 | 0.0099
GEN-2018-082 | 04 SOUTHEAST | 515122 | SXMLCKT4 | 138 | 11.135 | 11.1255 | 0.0095
GEN-2018-082 | 04 SOUTHEAST | 515135 | SUNNYSD4 | 138 | 19.117 | 19.0951 | 0.0219
GEN-2018-082 | 04 SOUTHEAST | 515150 | CANEYCK4 | 138 | 9.1286 | 9.1226 | 0.006
GEN-2018-082 | 04 SOUTHEAST | 515224 | MUSKOGE7 | 345 | 28.6414 | 28.626 | 0.0154
GEN-2018-082 | 04 SOUTHEAST | 515531 | VANOSTP4 | 138 | 13.3128 | 13.3074 | 0.0054
GEN-2018-082 | 04 SOUTHEAST | 515977 | LKKONWA4 | 138 | 39.5128 | 39.4768 | 0.036
GEN-2018-082 | 04 SOUTHEAST | 520560 | HUGOITC4 | 138 | 22.7437 | 22.7095 | 0.0342
GEN-2018-082 | 04 SOUTHEAST | 520948 | HUGO PP4 | 138 | 22.938 | 22.9048 | 0.0332
GEN-2018-082 | 04 SOUTHEAST | 555234 | NSUB345 | 345 | 27.0301 | 27.0124 | 0.0177
GEN-2018-082 | 04 SOUTHEAST | 560088 | G16-063-TAP | 345 | 8.1603 | 8.1489 | 0.0114
GEN-2018-082 | 04 SOUTHEAST | 588838 | G17-092-SWYD | 345 | 20.1846 | 20.1376 | 0.047
GEN-2018-082 | 04 SOUTHEAST | 760032 | GEN-2017-132 | 345 | 6.7839 | 6.7837 | 0.0002
GEN-2018-082 | 04 SOUTHEAST | 760851 | GEN-2017-154 | 345 | 3.8126 | 3.8089 | 0.0037
GEN-2018-082 | 04 SOUTHEAST | 761859 | GEN-2017-166 | 345 | 7.2286 | 7.2205 | 0.0081
GEN-2018-082 | 04 SOUTHEAST | 763164 | GEN-2018-087 | 345 | 12.9226 | 12.9048 | 0.0178
GEN-2018-082 | 04 SOUTHEAST | 5917 | SPPMAINBUS | 345 | 21.3102 | 21.2976 | 0.0126
GEN-2018-082 | 04 SOUTHEAST | 507428 | OKAY 4 | 138 | 10.226 | 10.2238 | 0.0022
GEN-2018-082 | 04 SOUTHEAST | 507431 | PATTERS4 | 138 | 13.5516 | 13.5471 | 0.0045
GEN-2018-082 | 04 SOUTHEAST | 507456 | TURK 3 | 115 | 17.0546 | 17.0509 | 0.0037
GEN-2018-082 | 04 SOUTHEAST | 508049 | NASH 4 | 138 | 21.038 | 21.0264 | 0.0116
GEN-2018-082 | 04 SOUTHEAST | 508070 | NWT-BNT4 | 138 | 26.7366 | 26.7171 | 0.0195
GEN-2018-082 | 04 SOUTHEAST | 508080 | SUGARHL4 | 138 | 12.5445 | 12.5406 | 0.0039
GEN-2018-082 | 04 SOUTHEAST | 508105 | MANDEVILTP4 | 138 | 9.5942 | 9.5922 | 0.002
GEN-2018-082 | 04 SOUTHEAST | 508809 | LONGWD 7 | 345 | 16.2105 | 16.2086 | 0.0019
GEN-2018-082 | 04 SOUTHEAST | 508832 | DIANA 7 | 345 | 18.9825 | 18.9772 | 0.0053
GEN-2018-082 | 04 SOUTHEAST | 508840 | WILKES 4 | 138 | 30.4579 | 30.4534 | 0.0045
GEN-2018-082 | 04 SOUTHEAST | 509745 | CLARKSV7 | 345 | 20.6199 | 20.6169 | 0.003
GEN-2018-082 | 04 SOUTHEAST | 509782 | R.S.S.-7 | 345 | 32.1585 | 32.1554 | 0.0031
GEN-2018-082 | 04 SOUTHEAST | 510870 | WCITYTP2 | 69 | 6.4522 | 6.4501 | 0.0021
GEN-2018-082 | 04 SOUTHEAST | 510876 | KIPUMPT2 | 69 | 4.9097 | 4.9085 | 0.0012
GEN-2018-082 | 04 SOUTHEAST | 510888 | B.BOWTP4 | 138 | 7.2031 | 7.2005 | 0.0026
GEN-2018-082 | 04 SOUTHEAST | 510893 | HUGO---2 | 69 | 5.1212 | 5.12 | 0.0012
GEN-2018-082 | 04 SOUTHEAST | 510908 | MCALEST4 | 138 | 9.838 | 9.8302 | 0.0078
GEN-2018-082 | 04 SOUTHEAST | 510909 | MCALESTIND 4 | 138 | 5.6342 | 5.6308 | 0.0034
GEN-2018-082 | 04 SOUTHEAST | 510948 | EARLSBORO 4 | 138 | 8.3628 | 8.3617 | 0.0011
GEN-2018-082 | 04 SOUTHEAST | 511508 | BLANCHD4 | 138 | 6.4796 | 6.4793 | 0.0003
GEN-2018-082 | 04 SOUTHEAST | 511571 | RUSHSPR7 | 345 | 7.0502 | 7.0479 | 0.0023
GEN-2018-082 | 04 SOUTHEAST | 514801 | MINCO 7 | 345 | 23.2915 | 23.2858 | 0.0057
GEN-2018-082 | 04 SOUTHEAST | 514827 | CTNWOOD4 | 138 | 18.3527 | 18.3522 | 0.0005
GEN-2018-082 | 04 SOUTHEAST | 514879 | NORTWST4 | 138 | 44.7892 | 44.7843 | 0.0049
GEN-2018-082 | 04 SOUTHEAST | 514881 | SPRNGCK7 | 345 | 23.3445 | 23.342 | 0.0025
GEN-2018-082 | 04 SOUTHEAST | 514901 | CIMARON7 | 345 | 34.2931 | 34.2837 | 0.0094
GEN-2018-082 | 04 SOUTHEAST | 514906 | JNSKAMO4 | 138 | 21.601 | 21.5998 | 0.0012
GEN-2018-082 | 04 SOUTHEAST | 514929 | PLVALLY4 | 138 | 45.9536 | 45.9401 | 0.0135
GEN-2018-082 | 04 SOUTHEAST | 514946 | MIDWEST4 | 138 | 34.4184 | 34.4087 | 0.0097
GEN-2018-082 | 04 SOUTHEAST | 514949 | SOONRTP4 | 138 | 22.8076 | 22.8034 | 0.0042
GEN-2018-082 | 04 SOUTHEAST | 514961 | GM 4 | 138 | 19.964 | 19.9612 | 0.0028
GEN-2018-082 | 04 SOUTHEAST | 515003 | BARNES 4 | 138 | 16.1837 | 16.1818 | 0.0019
GEN-2018-082 | 04 SOUTHEAST | 515054 | MAUD 2 | 69 | 10.7919 | 10.791 | 0.0009
GEN-2018-082 | 04 SOUTHEAST | 515075 | FRSTHIL4 | 138 | 13.8926 | 13.8907 | 0.0019
GEN-2018-082 | 04 SOUTHEAST | 515097 | WLNUTCK4 | 138 | 9.4627 | 9.4615 | 0.0012
GEN-2018-082 | 04 SOUTHEAST | 515099 | PALIOGE2 | 69 | 8.6053 | 8.6044 | 0.0009
GEN-2018-082 | 04 SOUTHEAST | 515114 | CHIGLEY4 | 138 | 8.0908 | 8.0887 | 0.0021
GEN-2018-082 | 04 SOUTHEAST | 515117 | ARBUCKL4 | 138 | 15.679 | 15.669 | 0.01
GEN-2018-082 | 04 SOUTHEAST | 515121 | MILLCKT4 | 138 | 10.9803 | 10.9713 | 0.009
GEN-2018-082 | 04 SOUTHEAST | 515124 | MAYSVIL4 | 138 | 6.1217 | 6.1207 | 0.001
GEN-2018-082 | 04 SOUTHEAST | 515137 | UNIROY 4 | 138 | 12.7256 | 12.7164 | 0.0092
GEN-2018-082 | 04 SOUTHEAST | 515144 | LONEGRV4 | 138 | 13.5118 | 13.5011 | 0.0107
GEN-2018-082 | 04 SOUTHEAST | 515147 | GLASSES4 | 138 | 8.3469 | 8.3418 | 0.0051
GEN-2018-082 | 04 SOUTHEAST | 515149 | MADINDT4 | 138 | 8.3445 | 8.3394 | 0.0051
GEN-2018-082 | 04 SOUTHEAST | 515151 | LTLCITY4 | 138 | 7.2419 | 7.2384 | 0.0035
GEN-2018-082 | 04 SOUTHEAST | 515164 | ROCKYPT4 | 138 | 11.8709 | 11.8627 | 0.0082
GEN-2018-082 | 04 SOUTHEAST | 515174 | VANOSS 4 | 138 | 13.1868 | 13.1815 | 0.0053
GEN-2018-082 | 04 SOUTHEAST | 515178 | PARKLN 4 | 138 | 16.2511 | 16.2435 | 0.0076
GEN-2018-082 | 04 SOUTHEAST | 515235 | PECANCK7 | 345 | 22.1253 | 22.119 | 0.0063
GEN-2018-082 | 04 SOUTHEAST | 515302 | FTSMITH7 | 345 | 10.063 | 10.0627 | 0.0003
GEN-2018-082 | 04 SOUTHEAST | 515461 | RNDBARN4 | 138 | 44.4777 | 44.4724 | 0.0053
GEN-2018-082 | 04 SOUTHEAST | 515465 | LGARBER4 | 138 | 21.6212 | 21.6199 | 0.0013
GEN-2018-082 | 04 SOUTHEAST | 515497 | MATHWSN7 | 345 | 32.7952 | 32.789 | 0.0062
GEN-2018-082 | 04 SOUTHEAST | 515561 | CARTRCO4 | 138 | 8.1628 | 8.1601 | 0.0027
GEN-2018-082 | 04 SOUTHEAST | 515932 | STIRLNG4 | 138 | 9.955 | 9.9489 | 0.0061
GEN-2018-082 | 04 SOUTHEAST | 520411 | SAWYER4 | 138 | 10.5586 | 10.5519 | 0.0067
GEN-2018-082 | 04 SOUTHEAST | 520918 | FROGVIL4 | 138 | 10.6779 | 10.6707 | 0.0072
GEN-2018-082 | 04 SOUTHEAST | 521044 | RUSSETT4 | 138 | 11.3142 | 11.3045 | 0.0097
GEN-2018-082 | 04 SOUTHEAST | 521067 | TEXOMAJ4 | 138 | 9.0392 | 9.0334 | 0.0058
GEN-2018-082 | 04 SOUTHEAST | 521079 | VALLANT4 | 138 | 8.6292 | 8.6249 | 0.0043
GEN-2018-082 | 04 SOUTHEAST | 521122 | HOWE 4 | 138 | 11.0288 | 11.0194 | 0.0094
GEN-2018-082 | 04 SOUTHEAST | 587430 | GEN-2016-063 | 345 | 8.0519 | 8.0409 | 0.011
GEN-2018-082 | 04 SOUTHEAST | 588670 | GEN-2017-023 | 138 | 18.8779 | 18.8555 | 0.0224
GEN-2018-082 | 04 SOUTHEAST | 588810 | GEN-2017-040 | 345 | 19.683 | 19.6383 | 0.0447
GEN-2018-082 | 04 SOUTHEAST | 589130 | GEN-2017-075 | 345 | 8.1486 | 8.1373 | 0.0113
GEN-2018-082 | 04 SOUTHEAST | 589300 | GEN-2017-092 | 345 | 16.0922 | 16.0626 | 0.0296
GEN-2018-082 | 04 SOUTHEAST | 760938 | G17-171-TAP | 345 | 12.0416 | 12.0366 | 0.005
GEN-2018-082 | 04 SOUTHEAST | 761334 | GEN-2017-155 | 345 | 12.2948 | 12.2921 | 0.0027
GEN-2018-082 | 04 SOUTHEAST | 761880 | GEN-2017-167 | 345 | 5.364 | 5.3594 | 0.0046
GEN-2018-082 | 04 SOUTHEAST | 762592 | GEN-2018-024 | 345 | 19.5226 | 19.4787 | 0.0439
GEN-2018-082 | 04 SOUTHEAST | 5919 | WELSHDC1 | 345 | 21.3102 | 21.2976 | 0.0126
GEN-2018-082 | 04 SOUTHEAST | 5921 | SPP-CAP1 | 345 | 21.3102 | 21.2976 | 0.0126
GEN-2018-082 | 04 SOUTHEAST | 5922 | SPP-CAP2 | 345 | 21.3102 | 21.2976 | 0.0126
GEN-2018-082 | 04 SOUTHEAST | 5923 | SPP-CAP3 | 345 | 21.3102 | 21.2976 | 0.0126
GEN-2018-082 | 04 SOUTHEAST | 5924 | SPP-REAC1 | 345 | 21.3102 | 21.2976 | 0.0126
GEN-2018-082 | 04 SOUTHEAST | 300136 | 4MEMORALT | 138 | 21.4309 | 21.4297 | 0.0012
GEN-2018-082 | 04 SOUTHEAST | 337376 | 7SAREPTA% | 345 | 9.8524 | 9.8521 | 0.0003
GEN-2018-082 | 04 SOUTHEAST | 504029 | SFOREMAN 4 | 138 | 8.6908 | 8.6892 | 0.0016
GEN-2018-082 | 04 SOUTHEAST | 504122 | MCNAB 3 | 115 | 13.7239 | 13.7219 | 0.002
GEN-2018-082 | 04 SOUTHEAST | 504123 | LOCKSBRG 4 | 138 | 5.9074 | 5.9065 | 0.0009
GEN-2018-082 | 04 SOUTHEAST | 504124 | ASHDWN_W 4 | 138 | 10.093 | 10.0903 | 0.0027
GEN-2018-082 | 04 SOUTHEAST | 504363 | NE-TEXARK2 | 69 | 5.3477 | 5.3474 | 0.0003
GEN-2018-082 | 04 SOUTHEAST | 505602 | S BROWN4 | 138 | 8.3533 | 8.3487 | 0.0046
GEN-2018-082 | 04 SOUTHEAST | 506945 | CHAMSPR7 | 345 | 10.0754 | 10.0752 | 0.0002
GEN-2018-082 | 04 SOUTHEAST | 507402 | ASHDWNR4 | 138 | 10.3735 | 10.371 | 0.0025
GEN-2018-082 | 04 SOUTHEAST | 507427 | OKAY 2 | 69 | 7.4399 | 7.4393 | 0.0006
GEN-2018-082 | 04 SOUTHEAST | 507429 | PATTERS2 | 69 | 14.3228 | 14.3203 | 0.0025
GEN-2018-082 | 04 SOUTHEAST | 507434 | SNASHVL4 | 138 | 3.7064 | 3.7062 | 0.0002
GEN-2018-082 | 04 SOUTHEAST | 507760 | SW SHV 7 | 345 | 16.0426 | 16.0411 | 0.0015
GEN-2018-082 | 04 SOUTHEAST | 508054 | BANN 4 | 138 | 22.0554 | 22.0427 | 0.0127
GEN-2018-082 | 04 SOUTHEAST | 508064 | MUNZCTY4 | 138 | 7.2417 | 7.2411 | 0.0006
GEN-2018-082 | 04 SOUTHEAST | 508078 | SETEXAR4 | 138 | 11.0707 | 11.0678 | 0.0029
GEN-2018-082 | 04 SOUTHEAST | 508079 | SUGARHL2 | 69 | 17.828 | 17.8242 | 0.0038
GEN-2018-082 | 04 SOUTHEAST | 508090 | WATLANT4 | 138 | 7.3631 | 7.3624 | 0.0007
GEN-2018-082 | 04 SOUTHEAST | 508091 | ALUMAX 4 | 138 | 18.4423 | 18.4334 | 0.0089
GEN-2018-082 | 04 SOUTHEAST | 508297 | LSSOUTH4 | 138 | 17.1869 | 17.1855 | 0.0014
GEN-2018-082 | 04 SOUTHEAST | 508355 | WELSHRE4 | 138 | 7.3371 | 7.3368 | 0.0003
GEN-2018-082 | 04 SOUTHEAST | 508563 | PIRKEY 7 | 345 | 16.8996 | 16.898 | 0.0016
GEN-2018-082 | 04 SOUTHEAST | 508808 | LONGWD 4 | 138 | 24.8141 | 24.8128 | 0.0013
GEN-2018-082 | 04 SOUTHEAST | 508831 | DIANA 4 | 138 | 29.429 | 29.4247 | 0.0043
GEN-2018-082 | 04 SOUTHEAST | 508835 | JEFFRSN4 | 138 | 13.4042 | 13.4036 | 0.0006
GEN-2018-082 | 04 SOUTHEAST | 509773 | RSS T1 4 | 138 | 51.5303 | 51.5278 | 0.0025
GEN-2018-082 | 04 SOUTHEAST | 509807 | ONETA--7 | 345 | 29.2478 | 29.2455 | 0.0023
GEN-2018-082 | 04 SOUTHEAST | 509834 | COGENT 7 | 345 | 29.7975 | 29.7949 | 0.0026
GEN-2018-082 | 04 SOUTHEAST | 509870 | SAPLPRD7 | 345 | 22.7944 | 22.7932 | 0.0012
GEN-2018-082 | 04 SOUTHEAST | 509875 | RSS T2 4 | 138 | 52.4475 | 52.4449 | 0.0026
GEN-2018-082 | 04 SOUTHEAST | 510864 | B.BOW 4 | 138 | 6.1863 | 6.1843 | 0.002
GEN-2018-082 | 04 SOUTHEAST | 510868 | GA PAC 2 | 69 | 2.4963 | 2.496 | 0.0003
GEN-2018-082 | 04 SOUTHEAST | 510869 | W CITY 2 | 69 | 3.8784 | 3.8777 | 0.0007
GEN-2018-082 | 04 SOUTHEAST | 510875 | KI PMPN2 | 69 | 3.4684 | 3.4679 | 0.0005
GEN-2018-082 | 04 SOUTHEAST | 510877 | FIXCT4 | 138 | 7.9437 | 7.9428 | 0.0009
GEN-2018-082 | 04 SOUTHEAST | 510890 | CRAIGJT4 | 138 | 8.6935 | 8.6902 | 0.0033
GEN-2018-082 | 04 SOUTHEAST | 510894 | VALYTIM2 | 69 | 2.7048 | 2.7046 | 0.0002
GEN-2018-082 | 04 SOUTHEAST | 510897 | LONEOAK4 | 138 | 8.6778 | 8.6732 | 0.0046
GEN-2018-082 | 04 SOUTHEAST | 510899 | MCALEST2 | 69 | 4.8026 | 4.8017 | 0.0009
GEN-2018-082 | 04 SOUTHEAST | 510906 | SMCALTP4 | 138 | 8.4614 | 8.4559 | 0.0055
GEN-2018-082 | 04 SOUTHEAST | 510917 | FTOWSON2 | 69 | 3.8066 | 3.806 | 0.0006
GEN-2018-082 | 04 SOUTHEAST | 510920 | SAWYER 2 | 69 | 3.9035 | 3.9028 | 0.0007
GEN-2018-082 | 04 SOUTHEAST | 510921 | DUSTIN-4 | 138 | 8.7351 | 8.7333 | 0.0018
GEN-2018-082 | 04 SOUTHEAST | 511449 | CORNVIL4 | 138 | 15.8854 | 15.8844 | 0.001
GEN-2018-082 | 04 SOUTHEAST | 511468 | L.E.S.-7 | 345 | 14.8644 | 14.8602 | 0.0042
GEN-2018-082 | 04 SOUTHEAST | 514510 | BURGETT4 | 138 | 23.0882 | 23.0868 | 0.0014
GEN-2018-082 | 04 SOUTHEAST | 514733 | MARSHL 4 | 138 | 7.9487 | 7.9486 | 0.0001
GEN-2018-082 | 04 SOUTHEAST | 514828 | KETCHTP4 | 138 | 26.9478 | 26.946 | 0.0018
GEN-2018-082 | 04 SOUTHEAST | 514829 | PINE ST4 | 138 | 12.4063 | 12.4061 | 0.0002
GEN-2018-082 | 04 SOUTHEAST | 514842 | CHTWOOD4 | 138 | 21.1353 | 21.1341 | 0.0012
GEN-2018-082 | 04 SOUTHEAST | 514854 | BRADEN 4 | 138 | 31.8391 | 31.8366 | 0.0025
GEN-2018-082 | 04 SOUTHEAST | 514864 | PIEDMNT4 | 138 | 22.6006 | 22.5993 | 0.0013
GEN-2018-082 | 04 SOUTHEAST | 514873 | LNEOAK 4 | 138 | 27.2272 | 27.2254 | 0.0018
GEN-2018-082 | 04 SOUTHEAST | 514898 | CIMARON4 | 138 | 45.5365 | 45.5305 | 0.006
GEN-2018-082 | 04 SOUTHEAST | 514902 | MCCLAIN4 | 138 | 37.8236 | 37.8177 | 0.0059
GEN-2018-082 | 04 SOUTHEAST | 514930 | OAKTRET4 | 138 | 21.4074 | 21.4037 | 0.0037
GEN-2018-082 | 04 SOUTHEAST | 514941 | HSL 4 | 138 | 42.6129 | 42.6078 | 0.0051
GEN-2018-082 | 04 SOUTHEAST | 514948 | CEDARLN4 | 138 | 23.7441 | 23.7395 | 0.0046
GEN-2018-082 | 04 SOUTHEAST | 514953 | HOLLYWD4 | 138 | 36.8243 | 36.8149 | 0.0094
GEN-2018-082 | 04 SOUTHEAST | 514957 | CHERYCK4 | 138 | 22.6144 | 22.6108 | 0.0036
GEN-2018-082 | 04 SOUTHEAST | 514992 | TURNER 4 | 138 | 31.61 | 31.6042 | 0.0058
GEN-2018-082 | 04 SOUTHEAST | 514993 | SE15TH 4 | 138 | 15.3595 | 15.358 | 0.0015
GEN-2018-082 | 04 SOUTHEAST | 514994 | TINKER54 | 138 | 14.0119 | 14.0105 | 0.0014
GEN-2018-082 | 04 SOUTHEAST | 515004 | ROSEDAL2 | 69 | 4.5541 | 4.5539 | 0.0002
GEN-2018-082 | 04 SOUTHEAST | 515053 | PEARSNT2 | 69 | 4.3081 | 4.308 | 0.0001
GEN-2018-082 | 04 SOUTHEAST | 515073 | ERLSBOR2 | 69 | 8.2858 | 8.2853 | 0.0005
GEN-2018-082 | 04 SOUTHEAST | 515074 | FRSTHIL2 | 69 | 11.1367 | 11.1361 | 0.0006
GEN-2018-082 | 04 SOUTHEAST | 515101 | PAULSVL2 | 69 | 5.8116 | 5.8112 | 0.0004
GEN-2018-082 | 04 SOUTHEAST | 515113 | CHIGLEY2 | 69 | 6.8886 | 6.8879 | 0.0007
GEN-2018-082 | 04 SOUTHEAST | 515116 | ARBUCKL2 | 69 | 6.127 | 6.1263 | 0.0007
GEN-2018-082 | 04 SOUTHEAST | 515123 | OAKLAW-4 | 138 | 12.6872 | 12.6809 | 0.0063
GEN-2018-082 | 04 SOUTHEAST | 515129 | RATLIFF4 | 138 | 6.3691 | 6.3676 | 0.0015
GEN-2018-082 | 04 SOUTHEAST | 515130 | POOLVIL4 | 138 | 7.992 | 7.9894 | 0.0026
GEN-2018-082 | 04 SOUTHEAST | 515133 | BLUERIV4 | 138 | 10.4663 | 10.4626 | 0.0037
GEN-2018-082 | 04 SOUTHEAST | 515152 | BROWNTP4 | 138 | 8.2037 | 8.1993 | 0.0044
GEN-2018-082 | 04 SOUTHEAST | 515158 | MADLIND4 | 138 | 7.7624 | 7.758 | 0.0044
GEN-2018-082 | 04 SOUTHEAST | 515160 | MRIETA 2 | 138 | 7.4115 | 7.4086 | 0.0029
GEN-2018-082 | 04 SOUTHEAST | 515163 | ROCKYPT2 | 69 | 7.899 | 7.8973 | 0.0017
GEN-2018-082 | 04 SOUTHEAST | 515172 | SPRNDAL4 | 138 | 11.8523 | 11.8441 | 0.0082
GEN-2018-082 | 04 SOUTHEAST | 515173 | BERWYN 4 | 138 | 8.26 | 8.2566 | 0.0034
GEN-2018-082 | 04 SOUTHEAST | 515177 | PARKLN 2 | 69 | 14.1914 | 14.1885 | 0.0029
GEN-2018-082 | 04 SOUTHEAST | 515196 | MILLCRK4 | 138 | 9.0224 | 9.0163 | 0.0061
GEN-2018-082 | 04 SOUTHEAST | 515234 | PECANCK5 | 161 | 21.1902 | 21.1883 | 0.0019
GEN-2018-082 | 04 SOUTHEAST | 515286 | STRLGTP4 | 138 | 13.8215 | 13.8198 | 0.0017
GEN-2018-082 | 04 SOUTHEAST | 515301 | FTSMTHW5 | 161 | 22.9216 | 22.9211 | 0.0005
GEN-2018-082 | 04 SOUTHEAST | 515305 | FTSMITH8 | 500 | 8.4183 | 8.4181 | 0.0002
GEN-2018-082 | 04 SOUTHEAST | 515318 | SOTHADA4 | 138 | 11.2886 | 11.2848 | 0.0038
GEN-2018-082 | 04 SOUTHEAST | 515372 | ARDWEST4 | 138 | 12.549 | 12.5401 | 0.0089
GEN-2018-082 | 04 SOUTHEAST | 515373 | LBRTYLK4 | 138 | 14.2037 | 14.2033 | 0.0004
GEN-2018-082 | 04 SOUTHEAST | 515377 | CRESENT4 | 138 | 10.6382 | 10.6381 | 0.0001
GEN-2018-082 | 04 SOUTHEAST | 515407 | TATONGA7 | 345 | 17.5658 | 17.5651 | 0.0007
GEN-2018-082 | 04 SOUTHEAST | 515415 | CHEEKTP4 | 138 | 12.1643 | 12.1558 | 0.0085
GEN-2018-082 | 04 SOUTHEAST | 515444 | MCNOWND7 | 345 | 23.197 | 23.1914 | 0.0056
GEN-2018-082 | 04 SOUTHEAST | 515457 | AIRDEPT4 | 138 | 20.3553 | 20.3526 | 0.0027
GEN-2018-082 | 04 SOUTHEAST | 515475 | PURCELL4 | 138 | 10.1093 | 10.108 | 0.0013
GEN-2018-082 | 04 SOUTHEAST | 515496 | KNAWATP2 | 69 | 4.3857 | 4.3855 | 0.0002
GEN-2018-082 | 04 SOUTHEAST | 515503 | LTRIVRT2 | 69 | 4.6768 | 4.6766 | 0.0002
GEN-2018-082 | 04 SOUTHEAST | 515549 | MNCWND37 | 345 | 14.1504 | 14.1484 | 0.002
GEN-2018-082 | 04 SOUTHEAST | 515559 | SULPHR 4 | 138 | 14.2338 | 14.2254 | 0.0084
GEN-2018-082 | 04 SOUTHEAST | 515563 | ORIGINW4 | 138 | 4.2056 | 4.205 | 0.0006
GEN-2018-082 | 04 SOUTHEAST | 515570 | MAYSVLT4 | 138 | 5.7467 | 5.7458 | 0.0009
GEN-2018-082 | 04 SOUTHEAST | 515610 | FSHRTAP7 | 345 | 16.0539 | 16.052 | 0.0019
GEN-2018-082 | 04 SOUTHEAST | 515800 | GRACMNT7 | 345 | 20.5087 | 20.5049 | 0.0038
GEN-2018-082 | 04 SOUTHEAST | 515873 | DRPSPRG4 | 138 | 10.9734 | 10.9662 | 0.0072
GEN-2018-082 | 04 SOUTHEAST | 515875 | REDNGTN7 | 345 | 16.7149 | 16.714 | 0.0009
GEN-2018-082 | 04 SOUTHEAST | 520419 | GARVIN4 | 138 | 5.9763 | 5.9745 | 0.0018
GEN-2018-082 | 04 SOUTHEAST | 520465 | REAGAN 4 | 138 | 4.2063 | 4.205 | 0.0013
GEN-2018-082 | 04 SOUTHEAST | 520467 | ENOSJCT4 | 138 | 7.6277 | 7.6236 | 0.0041
GEN-2018-082 | 04 SOUTHEAST | 520917 | FRNKLNS4 | 138 | 29.592 | 29.5851 | 0.0069
GEN-2018-082 | 04 SOUTHEAST | 520972 | LEBANTP4 | 138 | 6.8876 | 6.8845 | 0.0031
GEN-2018-082 | 04 SOUTHEAST | 521036 | RATTAN 4 | 138 | 6.8302 | 6.8275 | 0.0027
GEN-2018-082 | 04 SOUTHEAST | 521098 | WSBNKTP4 | 138 | 6.5692 | 6.5664 | 0.0028
GEN-2018-082 | 04 SOUTHEAST | 563259 | GEN-2015-092 | 345 | 6.8087 | 6.8066 | 0.0021
GEN-2018-082 | 04 SOUTHEAST | 587804 | G16-119-TAP | 345 | 15.2197 | 15.2192 | 0.0005
GEN-2018-082 | 04 SOUTHEAST | 588039 | G16133G16146 | 345 | 32.1585 | 32.1554 | 0.0031
GEN-2018-082 | 04 SOUTHEAST | 588180 | GEN-2016-126 | 138 | 12.9698 | 12.9631 | 0.0067
GEN-2018-082 | 04 SOUTHEAST | 588710 | GEN-2017-027 | 138 | 8.1238 | 8.1212 | 0.0026
GEN-2018-082 | 04 SOUTHEAST | 760389 | GEN-2017-140 | 345 | 1.8416 | 1.8416 | 0
GEN-2018-082 | 04 SOUTHEAST | 760939 | GEN-2017-171 | 345 | 11.9683 | 11.9635 | 0.0048
GEN-2018-082 | 04 SOUTHEAST | 761250 | GEN-2017-233 | 345 | 22.5233 | 22.518 | 0.0053
GEN-2018-082 | 04 SOUTHEAST | 762431 | G18-003-TAP | 138 | 11.1524 | 11.1504 | 0.002
GEN-2018-082 | 04 SOUTHEAST | 762823 | GEN-2018-048 | 345 | 16.4959 | 16.4925 | 0.0034
GEN-2018-082 | 04 SOUTHEAST | 762845 | GEN-2018-050 | 345 | 12.4023 | 12.4013 | 0.001
GEN-2018-082 | 04 SOUTHEAST | 762900 | GEN-2018-055 | 345 | 4.8244 | 4.8234 | 0.001
GEN-2018-082 | 04 SOUTHEAST | 900001 | TRAVERSE3 | 345 | 6.9271 | 6.9269 | 0.0002
GEN-2018-082 | 04 SOUTHEAST | 914902 | G17-152_TAP | 138 | 37.5659 | 37.56 | 0.0059
GEN-2018-087 | 04 SOUTHEAST | 508298 | LYDIA 7 | 345 | 13.4983 | 13.4983 | 0
GEN-2018-087 | 04 SOUTHEAST | 508072 | NWTXARK7 | 345 | 16.4948 | 16.4948 | 0
GEN-2018-087 | 04 SOUTHEAST | 508359 | WELSH 7 | 345 | 21.3102 | 21.3102 | 0
GEN-2018-087 | 04 SOUTHEAST | 510911 | VALIANT7 | 345 | 16.6284 | 16.6284 | 0
GEN-2018-087 | 04 SOUTHEAST | 763164 | GEN-2018-087 | 345 | 12.9226 | 12.9226 | 0
GEN-2018-087 | 04 SOUTHEAST | 5917 | SPPMAINBUS | 345 | 21.3102 | 21.3102 | 0
GEN-2018-087 | 04 SOUTHEAST | 507455 | TURK 7 | 345 | 11.6362 | 11.6362 | 0
GEN-2018-087 | 04 SOUTHEAST | 508071 | NWTXARK4 | 138 | 28.0292 | 28.0292 | 0
GEN-2018-087 | 04 SOUTHEAST | 508832 | DIANA 7 | 345 | 18.9825 | 18.9825 | 0
GEN-2018-087 | 04 SOUTHEAST | 508841 | WILKES 7 | 345 | 17.8224 | 17.8224 | 0
GEN-2018-087 | 04 SOUTHEAST | 510907 | PITTSB-7 | 345 | 16.4511 | 16.4511 | 0
GEN-2018-087 | 04 SOUTHEAST | 510918 | VALIANT4 | 138 | 15.7903 | 15.7903 | 0
GEN-2018-087 | 04 SOUTHEAST | 521157 | HUGO 7 | 345 | 12.5857 | 12.5857 | 0
GEN-2018-087 | 04 SOUTHEAST | 5919 | WELSHDC1 | 345 | 21.3102 | 21.3102 | 0
GEN-2018-087 | 04 SOUTHEAST | 5921 | SPP-CAP1 | 345 | 21.3102 | 21.3102 | 0
GEN-2018-087 | 04 SOUTHEAST | 5922 | SPP-CAP2 | 345 | 21.3102 | 21.3102 | 0
GEN-2018-087 | 04 SOUTHEAST | 5923 | SPP-CAP3 | 345 | 21.3102 | 21.3102 | 0
GEN-2018-087 | 04 SOUTHEAST | 5924 | SPP-REAC1 | 345 | 21.3102 | 21.3102 | 0
GEN-2018-087 | 04 SOUTHEAST | 507431 | PATTERS4 | 138 | 13.5516 | 13.5516 | 0
GEN-2018-087 | 04 SOUTHEAST | 507454 | TURK 4 | 138 | 27.2509 | 27.2509 | 0
GEN-2018-087 | 04 SOUTHEAST | 507760 | SW SHV 7 | 345 | 16.0426 | 16.0426 | 0
GEN-2018-087 | 04 SOUTHEAST | 508049 | NASH 4 | 138 | 21.038 | 21.038 | 0
GEN-2018-087 | 04 SOUTHEAST | 508070 | NWT-BNT4 | 138 | 26.7366 | 26.7366 | 0
GEN-2018-087 | 04 SOUTHEAST | 508080 | SUGARHL4 | 138 | 12.5445 | 12.5445 | 0
GEN-2018-087 | 04 SOUTHEAST | 508563 | PIRKEY 7 | 345 | 16.8996 | 16.8996 | 0
GEN-2018-087 | 04 SOUTHEAST | 508809 | LONGWD 7 | 345 | 16.2105 | 16.2105 | 0
GEN-2018-087 | 04 SOUTHEAST | 508831 | DIANA 4 | 138 | 29.429 | 29.429 | 0
GEN-2018-087 | 04 SOUTHEAST | 508840 | WILKES 4 | 138 | 30.4579 | 30.4579 | 0
GEN-2018-087 | 04 SOUTHEAST | 510866 | V-WEYCO4 | 138 | 9.8522 | 9.8522 | 0
GEN-2018-087 | 04 SOUTHEAST | 510886 | IDABEL-4 | 138 | 6.8774 | 6.8774 | 0
GEN-2018-087 | 04 SOUTHEAST | 510901 | HUGO---4 | 138 | 3.5315 | 3.5315 | 0
GEN-2018-087 | 04 SOUTHEAST | 510910 | VALIANT2 | 69 | 7.4325 | 7.4325 | 0
GEN-2018-087 | 04 SOUTHEAST | 510925 | KIOWA 7 | 345 | 16.1028 | 16.1028 | 0
GEN-2018-087 | 04 SOUTHEAST | 514809 | JOHNCO 7 | 345 | 10.9329 | 10.9329 | 0
GEN-2018-087 | 04 SOUTHEAST | 515045 | SEMINOL7 | 345 | 30.8428 | 30.8428 | 0
GEN-2018-087 | 04 SOUTHEAST | 515422 | C-RIVER7 | 345 | 11.6454 | 11.6454 | 0
GEN-2018-087 | 04 SOUTHEAST | 520560 | HUGOITC4 | 138 | 22.7437 | 22.7437 | 0
GEN-2018-087 | 04 SOUTHEAST | 520948 | HUGO PP4 | 138 | 22.938 | 22.938 | 0
GEN-2018-087 | 04 SOUTHEAST | 560088 | G16-063-TAP | 345 | 8.1603 | 8.1603 | 0
GEN-2018-087 | 04 SOUTHEAST | 763131 | GEN-2018-082 | 345 | 10.1533 | 10.1533 | 0
GEN-2018-087 | 04 SOUTHEAST | 337376 | 7SAREPTA% | 345 | 9.8524 | 9.8524 | 0
GEN-2018-087 | 04 SOUTHEAST | 500250 | DOLHILL7 | 345 | 12.3341 | 12.3341 | 0
GEN-2018-087 | 04 SOUTHEAST | 504029 | SFOREMAN 4 | 138 | 8.6908 | 8.6908 | 0
GEN-2018-087 | 04 SOUTHEAST | 504123 | LOCKSBRG 4 | 138 | 5.9074 | 5.9074 | 0
GEN-2018-087 | 04 SOUTHEAST | 504124 | ASHDWN_W 4 | 138 | 10.093 | 10.093 | 0
GEN-2018-087 | 04 SOUTHEAST | 507402 | ASHDWNR4 | 138 | 10.3735 | 10.3735 | 0
GEN-2018-087 | 04 SOUTHEAST | 507428 | OKAY 4 | 138 | 10.226 | 10.226 | 0
GEN-2018-087 | 04 SOUTHEAST | 507429 | PATTERS2 | 69 | 14.3228 | 14.3228 | 0
GEN-2018-087 | 04 SOUTHEAST | 507434 | SNASHVL4 | 138 | 3.7064 | 3.7064 | 0
GEN-2018-087 | 04 SOUTHEAST | 507456 | TURK 3 | 115 | 17.0546 | 17.0546 | 0
GEN-2018-087 | 04 SOUTHEAST | 507759 | SW SHV 4 | 138 | 30.6446 | 30.6446 | 0
GEN-2018-087 | 04 SOUTHEAST | 508054 | BANN 4 | 138 | 22.0554 | 22.0554 | 0
GEN-2018-087 | 04 SOUTHEAST | 508064 | MUNZCTY4 | 138 | 7.2417 | 7.2417 | 0
GEN-2018-087 | 04 SOUTHEAST | 508079 | SUGARHL2 | 69 | 17.828 | 17.828 | 0
GEN-2018-087 | 04 SOUTHEAST | 508090 | WATLANT4 | 138 | 7.3631 | 7.3631 | 0
GEN-2018-087 | 04 SOUTHEAST | 508091 | ALUMAX 4 | 138 | 18.4423 | 18.4423 | 0
GEN-2018-087 | 04 SOUTHEAST | 508105 | MANDEVILTP4 | 138 | 9.5942 | 9.5942 | 0
GEN-2018-087 | 04 SOUTHEAST | 508297 | LSSOUTH4 | 138 | 17.1869 | 17.1869 | 0
GEN-2018-087 | 04 SOUTHEAST | 508351 | PERDUE 4 | 138 | 10.5571 | 10.5571 | 0
GEN-2018-087 | 04 SOUTHEAST | 508355 | WELSHRE4 | 138 | 7.3371 | 7.3371 | 0
GEN-2018-087 | 04 SOUTHEAST | 508562 | PIRKEY 4 | 138 | 41.7547 | 41.7547 | 0
GEN-2018-087 | 04 SOUTHEAST | 508571 | SPRHILL4 | 138 | 8.2944 | 8.2944 | 0
GEN-2018-087 | 04 SOUTHEAST | 508572 | LEBROCK7 | 345 | 15.7793 | 15.7793 | 0
GEN-2018-087 | 04 SOUTHEAST | 508808 | LONGWD 4 | 138 | 24.8141 | 24.8141 | 0
GEN-2018-087 | 04 SOUTHEAST | 508835 | JEFFRSN4 | 138 | 13.4042 | 13.4042 | 0
GEN-2018-087 | 04 SOUTHEAST | 508837 | NGPLTAP4 | 138 | 13.3857 | 13.3857 | 0
GEN-2018-087 | 04 SOUTHEAST | 509639 | DIANASW4 | 138 | 12.0216 | 12.0216 | 0
GEN-2018-087 | 04 SOUTHEAST | 510870 | WCITYTP2 | 69 | 6.4522 | 6.4522 | 0
GEN-2018-087 | 04 SOUTHEAST | 510876 | KIPUMPT2 | 69 | 4.9097 | 4.9097 | 0
GEN-2018-087 | 04 SOUTHEAST | 510888 | B.BOWTP4 | 138 | 7.2031 | 7.2031 | 0
GEN-2018-087 | 04 SOUTHEAST | 510893 | HUGO---2 | 69 | 5.1212 | 5.1212 | 0
GEN-2018-087 | 04 SOUTHEAST | 510946 | C-RIVER4 | 138 | 13.6517 | 13.6517 | 0
GEN-2018-087 | 04 SOUTHEAST | 514808 | JOHNCO 4 | 138 | 15.4874 | 15.4874 | 0
GEN-2018-087 | 04 SOUTHEAST | 514908 | ARCADIA7 | 345 | 28.6269 | 28.6269 | 0
GEN-2018-087 | 04 SOUTHEAST | 514934 | DRAPER 7 | 345 | 26.1641 | 26.1641 | 0
GEN-2018-087 | 04 SOUTHEAST | 515044 | SEMINOL4 | 138 | 40.4325 | 40.4325 | 0
GEN-2018-087 | 04 SOUTHEAST | 515136 | SUNNYSD7 | 345 | 12.0848 | 12.0848 | 0
GEN-2018-087 | 04 SOUTHEAST | 516006 | DMNDSPG7 | 345 | 7.4023 | 7.4023 | 0
GEN-2018-087 | 04 SOUTHEAST | 520411 | SAWYER4 | 138 | 10.5586 | 10.5586 | 0
GEN-2018-087 | 04 SOUTHEAST | 520918 | FROGVIL4 | 138 | 10.6779 | 10.6779 | 0
GEN-2018-087 | 04 SOUTHEAST | 521079 | VALLANT4 | 138 | 8.6292 | 8.6292 | 0
GEN-2018-087 | 04 SOUTHEAST | 587430 | GEN-2016-063 | 345 | 8.0519 | 8.0519 | 0
GEN-2018-087 | 04 SOUTHEAST | 588670 | GEN-2017-023 | 138 | 18.8779 | 18.8779 | 0
GEN-2018-087 | 04 SOUTHEAST | 588839 | FIREWHL-TAP | 345 | 20.1846 | 20.1846 | 0
GEN-2018-087 | 04 SOUTHEAST | 589130 | GEN-2017-075 | 345 | 8.1486 | 8.1486 | 0
GEN-2018-087 | 04 SOUTHEAST | 760830 | GEN-2017-149 | 345 | 4.1868 | 4.1868 | 0
GEN-2018-087 | 04 SOUTHEAST | 762431 | G18-003-TAP | 138 | 11.1524 | 11.1524 | 0
GEN-2018-087 | 04 SOUTHEAST | 762845 | GEN-2018-050 | 345 | 12.4023 | 12.4023 | 0
GEN-2018-087 | 04 SOUTHEAST | 337363 | 3SAREPTA! | 115 | 19.6304 | 19.6304 | 0
GEN-2018-087 | 04 SOUTHEAST | 337562 | 7EL DORADO | 345 | 13.7374 | 13.7374 | 0
GEN-2018-087 | 04 SOUTHEAST | 337672 | 4MURFBORO | 138 | 2.8751 | 2.8751 | 0
GEN-2018-087 | 04 SOUTHEAST | 500260 | DOLHILL6 | 230 | 14.9977 | 14.9977 | 0
GEN-2018-087 | 04 SOUTHEAST | 504030 | SFORE_1 2 | 69 | 2.8399 | 2.8399 | 0
GEN-2018-087 | 04 SOUTHEAST | 504122 | MCNAB 3 | 115 | 13.7239 | 13.7239 | 0
GEN-2018-087 | 04 SOUTHEAST | 504363 | NE-TEXARK2 | 69 | 5.3477 | 5.3477 | 0
GEN-2018-087 | 04 SOUTHEAST | 507421 | FOREMAN2 | 69 | 3.6654 | 3.6654 | 0
GEN-2018-087 | 04 SOUTHEAST | 507427 | OKAY 2 | 69 | 7.4399 | 7.4399 | 0
GEN-2018-087 | 04 SOUTHEAST | 507463 | BARITERDTP 4 | 138 | 3.6005 | 3.6005 | 0
GEN-2018-087 | 04 SOUTHEAST | 507732 | GENMOTR4 | 138 | 17.6233 | 17.6233 | 0
GEN-2018-087 | 04 SOUTHEAST | 507748 | POWELL 4 | 138 | 19.2003 | 19.2003 | 0
GEN-2018-087 | 04 SOUTHEAST | 507755 | S SHV 4 | 138 | 22.7776 | 22.7776 | 0
GEN-2018-087 | 04 SOUTHEAST | 507757 | SPRIDGE4 | 138 | 11.1659 | 11.1659 | 0
GEN-2018-087 | 04 SOUTHEAST | 507774 | NORAM 4 | 138 | 17.1024 | 17.1024 | 0
GEN-2018-087 | 04 SOUTHEAST | 507793 | LEASIDE 4 | 138 | 22.1591 | 22.1591 | 0
GEN-2018-087 | 04 SOUTHEAST | 508051 | ASHDOWN2 | 69 | 11.9233 | 11.9233 | 0
GEN-2018-087 | 04 SOUTHEAST | 508053 | BANN 2 | 69 | 20.5916 | 20.5916 | 0
GEN-2018-087 | 04 SOUTHEAST | 508056 | BRYANML4 | 138 | 7.1404 | 7.1404 | 0
GEN-2018-087 | 04 SOUTHEAST | 508065 | NEKOOSA2 | 69 | 6.2847 | 6.2847 | 0
GEN-2018-087 | 04 SOUTHEAST | 508069 | NNBOSTN4 | 138 | 11.2391 | 11.2391 | 0
GEN-2018-087 | 04 SOUTHEAST | 508075 | REDSPRG4 | 138 | 14.5368 | 14.5368 | 0
GEN-2018-087 | 04 SOUTHEAST | 508078 | SETEXAR4 | 138 | 11.0707 | 11.0707 | 0
GEN-2018-087 | 04 SOUTHEAST | 508081 | SUGHLET2 | 69 | 17.006 | 17.006 | 0
GEN-2018-087 | 04 SOUTHEAST | 508082 | SUGHLWT2 | 69 | 16.9581 | 16.9581 | 0
GEN-2018-087 | 04 SOUTHEAST | 508089 | WATLANT2 | 69 | 8.2175 | 8.2175 | 0
GEN-2018-087 | 04 SOUTHEAST | 508106 | CASSTP4 | 138 | 7.3459 | 7.3459 | 0
GEN-2018-087 | 04 SOUTHEAST | 508296 | LSSOUTH2 | 69 | 10.079 | 10.079 | 0
GEN-2018-087 | 04 SOUTHEAST | 508313 | PITTSB_4 | 138 | 8.748 | 8.748 | 0
GEN-2018-087 | 04 SOUTHEAST | 508337 | CHAPELH4 | 138 | 7.3226 | 7.3226 | 0
GEN-2018-087 | 04 SOUTHEAST | 508350 | PERDUE 2 | 69 | 13.2936 | 13.2936 | 0
GEN-2018-087 | 04 SOUTHEAST | 508369 | EXXONM 4 | 138 | 6.5643 | 6.5643 | 0
GEN-2018-087 | 04 SOUTHEAST | 508552 | LLAMOND4 | 138 | 6.9872 | 6.9872 | 0
GEN-2018-087 | 04 SOUTHEAST | 508557 | MARSHL-4 | 138 | 16.5294 | 16.5294 | 0
GEN-2018-087 | 04 SOUTHEAST | 508560 | NEWGLAD4 | 138 | 9.4659 | 9.4659 | 0
GEN-2018-087 | 04 SOUTHEAST | 508564 | PLILER 4 | 138 | 12.1571 | 12.1571 | 0
GEN-2018-087 | 04 SOUTHEAST | 508566 | SABMINT4 | 138 | 33.977 | 33.977 | 0
GEN-2018-087 | 04 SOUTHEAST | 508567 | SCOTTSV4 | 138 | 12.0614 | 12.0614 | 0
GEN-2018-087 | 04 SOUTHEAST | 508585 | TENRUSK7 | 345 | 7.7847 | 7.7847 | 0
GEN-2018-087 | 04 SOUTHEAST | 508595 | HALLSVLS4 | 138 | 18.487 | 18.487 | 0
GEN-2018-087 | 04 SOUTHEAST | 508806 | LIEBERM4 | 138 | 16.6692 | 16.6692 | 0
GEN-2018-087 | 04 SOUTHEAST | 508816 | OAKPH 4 | 138 | 19.3555 | 19.3555 | 0
GEN-2018-087 | 04 SOUTHEAST | 508827 | NGPL 4 | 138 | 10.0941 | 10.0941 | 0
GEN-2018-087 | 04 SOUTHEAST | 508833 | IPCJEFF4 | 138 | 12.136 | 12.136 | 0
GEN-2018-087 | 04 SOUTHEAST | 509092 | EASTON 4 | 138 | 24.3732 | 24.3732 | 0
GEN-2018-087 | 04 SOUTHEAST | 509603 | BIGSAND4 | 138 | 7.0909 | 7.0909 | 0
GEN-2018-087 | 04 SOUTHEAST | 509607 | DIAN 4 | 138 | 11.5427 | 11.5427 | 0
GEN-2018-087 | 04 SOUTHEAST | 509624 | LAKEPIN4 | 138 | 7.3647 | 7.3647 | 0
GEN-2018-087 | 04 SOUTHEAST | 509628 | NOONDAY4 | 138 | 5.7974 | 5.7974 | 0
GEN-2018-087 | 04 SOUTHEAST | 509666 | DUGLASV4 | 138 | 5.0334 | 5.0334 | 0
GEN-2018-087 | 04 SOUTHEAST | 510864 | B.BOW 4 | 138 | 6.1863 | 6.1863 | 0
GEN-2018-087 | 04 SOUTHEAST | 510868 | GA PAC 2 | 69 | 2.4963 | 2.4963 | 0
GEN-2018-087 | 04 SOUTHEAST | 510869 | W CITY 2 | 69 | 3.8784 | 3.8784 | 0
GEN-2018-087 | 04 SOUTHEAST | 510875 | KI PMPN2 | 69 | 3.4684 | 3.4684 | 0
GEN-2018-087 | 04 SOUTHEAST | 510890 | CRAIGJT4 | 138 | 8.6935 | 8.6935 | 0
GEN-2018-087 | 04 SOUTHEAST | 510894 | VALYTIM2 | 69 | 2.7048 | 2.7048 | 0
GEN-2018-087 | 04 SOUTHEAST | 510917 | FTOWSON2 | 69 | 3.8066 | 3.8066 | 0
GEN-2018-087 | 04 SOUTHEAST | 510920 | SAWYER 2 | 69 | 3.9035 | 3.9035 | 0
GEN-2018-087 | 04 SOUTHEAST | 510951 | TALAWANDA 4 | 138 | 9.756 | 9.756 | 0
GEN-2018-087 | 04 SOUTHEAST | 511568 | TERRYRD7 | 345 | 11.0146 | 11.0146 | 0
GEN-2018-087 | 04 SOUTHEAST | 514880 | NORTWST7 | 345 | 32.9086 | 32.9086 | 0
GEN-2018-087 | 04 SOUTHEAST | 514907 | ARCADIA4 | 138 | 47.2233 | 47.2233 | 0
GEN-2018-087 | 04 SOUTHEAST | 514909 | REDBUD 7 | 345 | 27.6026 | 27.6026 | 0
GEN-2018-087 | 04 SOUTHEAST | 514933 | DRAPER 4 | 138 | 42.9122 | 42.9122 | 0
GEN-2018-087 | 04 SOUTHEAST | 515055 | MAUD 4 | 138 | 20.1325 | 20.1325 | 0
GEN-2018-087 | 04 SOUTHEAST | 515100 | PAOLI- 4 | 138 | 10.3088 | 10.3088 | 0
GEN-2018-087 | 04 SOUTHEAST | 515120 | RUSSET-4 | 138 | 11.3858 | 11.3858 | 0
GEN-2018-087 | 04 SOUTHEAST | 515122 | SXMLCKT4 | 138 | 11.135 | 11.135 | 0
GEN-2018-087 | 04 SOUTHEAST | 515135 | SUNNYSD4 | 138 | 19.117 | 19.117 | 0
GEN-2018-087 | 04 SOUTHEAST | 515150 | CANEYCK4 | 138 | 9.1286 | 9.1286 | 0
GEN-2018-087 | 04 SOUTHEAST | 515224 | MUSKOGE7 | 345 | 28.6414 | 28.6414 | 0
GEN-2018-087 | 04 SOUTHEAST | 515531 | VANOSTP4 | 138 | 13.3128 | 13.3128 | 0
GEN-2018-087 | 04 SOUTHEAST | 515977 | LKKONWA4 | 138 | 39.5128 | 39.5128 | 0
GEN-2018-087 | 04 SOUTHEAST | 520419 | GARVIN4 | 138 | 5.9763 | 5.9763 | 0
GEN-2018-087 | 04 SOUTHEAST | 521036 | RATTAN 4 | 138 | 6.8302 | 6.8302 | 0
GEN-2018-087 | 04 SOUTHEAST | 521098 | WSBNKTP4 | 138 | 6.5692 | 6.5692 | 0
GEN-2018-087 | 04 SOUTHEAST | 555234 | NSUB345 | 345 | 27.0301 | 27.0301 | 0
GEN-2018-087 | 04 SOUTHEAST | 588838 | G17-092-SWYD | 345 | 20.1846 | 20.1846 | 0
GEN-2018-087 | 04 SOUTHEAST | 760032 | GEN-2017-132 | 345 | 6.7839 | 6.7839 | 0
GEN-2018-087 | 04 SOUTHEAST | 760851 | GEN-2017-154 | 345 | 3.8126 | 3.8126 | 0
GEN-2018-087 | 04 SOUTHEAST | 761859 | GEN-2017-166 | 345 | 7.2286 | 7.2286 | 0
GEN-2018-087 | 04 SOUTHEAST | 762427 | GEN-2018-003 | 138 | 11.1524 | 11.1524 | 0
GEN-2018-088 | 04 SOUTHEAST | 508298 | LYDIA 7 | 345 | 13.4983 | 13.4983 | 0
GEN-2018-088 | 04 SOUTHEAST | 508072 | NWTXARK7 | 345 | 16.4948 | 16.4948 | 0
GEN-2018-088 | 04 SOUTHEAST | 508359 | WELSH 7 | 345 | 21.3102 | 21.3102 | 0
GEN-2018-088 | 04 SOUTHEAST | 510911 | VALIANT7 | 345 | 16.6284 | 16.6284 | 0
GEN-2018-088 | 04 SOUTHEAST | 763164 | GEN-2018-087 | 345 | 12.9226 | 12.9226 | 0
GEN-2018-088 | 04 SOUTHEAST | 5917 | SPPMAINBUS | 345 | 21.3102 | 21.3102 | 0
GEN-2018-088 | 04 SOUTHEAST | 507455 | TURK 7 | 345 | 11.6362 | 11.6362 | 0
GEN-2018-088 | 04 SOUTHEAST | 508071 | NWTXARK4 | 138 | 28.0292 | 28.0292 | 0
GEN-2018-088 | 04 SOUTHEAST | 508832 | DIANA 7 | 345 | 18.9825 | 18.9825 | 0
GEN-2018-088 | 04 SOUTHEAST | 508841 | WILKES 7 | 345 | 17.8224 | 17.8224 | 0
GEN-2018-088 | 04 SOUTHEAST | 510907 | PITTSB-7 | 345 | 16.4511 | 16.4511 | 0
GEN-2018-088 | 04 SOUTHEAST | 510918 | VALIANT4 | 138 | 15.7903 | 15.7903 | 0
GEN-2018-088 | 04 SOUTHEAST | 521157 | HUGO 7 | 345 | 12.5857 | 12.5857 | 0
GEN-2018-088 | 04 SOUTHEAST | 5919 | WELSHDC1 | 345 | 21.3102 | 21.3102 | 0
GEN-2018-088 | 04 SOUTHEAST | 5921 | SPP-CAP1 | 345 | 21.3102 | 21.3102 | 0
GEN-2018-088 | 04 SOUTHEAST | 5922 | SPP-CAP2 | 345 | 21.3102 | 21.3102 | 0
GEN-2018-088 | 04 SOUTHEAST | 5923 | SPP-CAP3 | 345 | 21.3102 | 21.3102 | 0
GEN-2018-088 | 04 SOUTHEAST | 5924 | SPP-REAC1 | 345 | 21.3102 | 21.3102 | 0
GEN-2018-088 | 04 SOUTHEAST | 507431 | PATTERS4 | 138 | 13.5516 | 13.5516 | 0
GEN-2018-088 | 04 SOUTHEAST | 507454 | TURK 4 | 138 | 27.2509 | 27.2509 | 0
GEN-2018-088 | 04 SOUTHEAST | 507760 | SW SHV 7 | 345 | 16.0426 | 16.0426 | 0
GEN-2018-088 | 04 SOUTHEAST | 508049 | NASH 4 | 138 | 21.038 | 21.038 | 0
GEN-2018-088 | 04 SOUTHEAST | 508070 | NWT-BNT4 | 138 | 26.7366 | 26.7366 | 0
GEN-2018-088 | 04 SOUTHEAST | 508080 | SUGARHL4 | 138 | 12.5445 | 12.5445 | 0
GEN-2018-088 | 04 SOUTHEAST | 508563 | PIRKEY 7 | 345 | 16.8996 | 16.8996 | 0
GEN-2018-088 | 04 SOUTHEAST | 508809 | LONGWD 7 | 345 | 16.2105 | 16.2105 | 0
GEN-2018-088 | 04 SOUTHEAST | 508831 | DIANA 4 | 138 | 29.429 | 29.429 | 0
GEN-2018-088 | 04 SOUTHEAST | 508840 | WILKES 4 | 138 | 30.4579 | 30.4579 | 0
GEN-2018-088 | 04 SOUTHEAST | 510866 | V-WEYCO4 | 138 | 9.8522 | 9.8522 | 0
GEN-2018-088 | 04 SOUTHEAST | 510886 | IDABEL-4 | 138 | 6.8774 | 6.8774 | 0
GEN-2018-088 | 04 SOUTHEAST | 510901 | HUGO---4 | 138 | 3.5315 | 3.5315 | 0
GEN-2018-088 | 04 SOUTHEAST | 510910 | VALIANT2 | 69 | 7.4325 | 7.4325 | 0
GEN-2018-088 | 04 SOUTHEAST | 510925 | KIOWA 7 | 345 | 16.1028 | 16.1028 | 0
GEN-2018-088 | 04 SOUTHEAST | 514809 | JOHNCO 7 | 345 | 10.9329 | 10.9329 | 0
GEN-2018-088 | 04 SOUTHEAST | 515045 | SEMINOL7 | 345 | 30.8428 | 30.8428 | 0
GEN-2018-088 | 04 SOUTHEAST | 515422 | C-RIVER7 | 345 | 11.6454 | 11.6454 | 0
GEN-2018-088 | 04 SOUTHEAST | 520560 | HUGOITC4 | 138 | 22.7437 | 22.7437 | 0
GEN-2018-088 | 04 SOUTHEAST | 520948 | HUGO PP4 | 138 | 22.938 | 22.938 | 0
GEN-2018-088 | 04 SOUTHEAST | 560088 | G16-063-TAP | 345 | 8.1603 | 8.1603 | 0
GEN-2018-088 | 04 SOUTHEAST | 763131 | GEN-2018-082 | 345 | 10.1533 | 10.1533 | 0
GEN-2018-088 | 04 SOUTHEAST | 337376 | 7SAREPTA% | 345 | 9.8524 | 9.8524 | 0
GEN-2018-088 | 04 SOUTHEAST | 500250 | DOLHILL7 | 345 | 12.3341 | 12.3341 | 0
GEN-2018-088 | 04 SOUTHEAST | 504029 | SFOREMAN 4 | 138 | 8.6908 | 8.6908 | 0
GEN-2018-088 | 04 SOUTHEAST | 504123 | LOCKSBRG 4 | 138 | 5.9074 | 5.9074 | 0
GEN-2018-088 | 04 SOUTHEAST | 504124 | ASHDWN_W 4 | 138 | 10.093 | 10.093 | 0
GEN-2018-088 | 04 SOUTHEAST | 507402 | ASHDWNR4 | 138 | 10.3735 | 10.3735 | 0
GEN-2018-088 | 04 SOUTHEAST | 507428 | OKAY 4 | 138 | 10.226 | 10.226 | 0
GEN-2018-088 | 04 SOUTHEAST | 507429 | PATTERS2 | 69 | 14.3228 | 14.3228 | 0
GEN-2018-088 | 04 SOUTHEAST | 507434 | SNASHVL4 | 138 | 3.7064 | 3.7064 | 0
GEN-2018-088 | 04 SOUTHEAST | 507456 | TURK 3 | 115 | 17.0546 | 17.0546 | 0
GEN-2018-088 | 04 SOUTHEAST | 507759 | SW SHV 4 | 138 | 30.6446 | 30.6446 | 0
GEN-2018-088 | 04 SOUTHEAST | 508054 | BANN 4 | 138 | 22.0554 | 22.0554 | 0
GEN-2018-088 | 04 SOUTHEAST | 508064 | MUNZCTY4 | 138 | 7.2417 | 7.2417 | 0
GEN-2018-088 | 04 SOUTHEAST | 508079 | SUGARHL2 | 69 | 17.828 | 17.828 | 0
GEN-2018-088 | 04 SOUTHEAST | 508090 | WATLANT4 | 138 | 7.3631 | 7.3631 | 0
GEN-2018-088 | 04 SOUTHEAST | 508091 | ALUMAX 4 | 138 | 18.4423 | 18.4423 | 0
GEN-2018-088 | 04 SOUTHEAST | 508105 | MANDEVILTP4 | 138 | 9.5942 | 9.5942 | 0
GEN-2018-088 | 04 SOUTHEAST | 508297 | LSSOUTH4 | 138 | 17.1869 | 17.1869 | 0
GEN-2018-088 | 04 SOUTHEAST | 508351 | PERDUE 4 | 138 | 10.5571 | 10.5571 | 0
GEN-2018-088 | 04 SOUTHEAST | 508355 | WELSHRE4 | 138 | 7.3371 | 7.3371 | 0
GEN-2018-088 | 04 SOUTHEAST | 508562 | PIRKEY 4 | 138 | 41.7547 | 41.7547 | 0
GEN-2018-088 | 04 SOUTHEAST | 508571 | SPRHILL4 | 138 | 8.2944 | 8.2944 | 0
GEN-2018-088 | 04 SOUTHEAST | 508572 | LEBROCK7 | 345 | 15.7793 | 15.7793 | 0
GEN-2018-088 | 04 SOUTHEAST | 508808 | LONGWD 4 | 138 | 24.8141 | 24.8141 | 0
GEN-2018-088 | 04 SOUTHEAST | 508835 | JEFFRSN4 | 138 | 13.4042 | 13.4042 | 0
GEN-2018-088 | 04 SOUTHEAST | 508837 | NGPLTAP4 | 138 | 13.3857 | 13.3857 | 0
GEN-2018-088 | 04 SOUTHEAST | 509639 | DIANASW4 | 138 | 12.0216 | 12.0216 | 0
GEN-2018-088 | 04 SOUTHEAST | 510870 | WCITYTP2 | 69 | 6.4522 | 6.4522 | 0
GEN-2018-088 | 04 SOUTHEAST | 510876 | KIPUMPT2 | 69 | 4.9097 | 4.9097 | 0
GEN-2018-088 | 04 SOUTHEAST | 510888 | B.BOWTP4 | 138 | 7.2031 | 7.2031 | 0
GEN-2018-088 | 04 SOUTHEAST | 510893 | HUGO---2 | 69 | 5.1212 | 5.1212 | 0
GEN-2018-088 | 04 SOUTHEAST | 510946 | C-RIVER4 | 138 | 13.6517 | 13.6517 | 0
GEN-2018-088 | 04 SOUTHEAST | 514808 | JOHNCO 4 | 138 | 15.4874 | 15.4874 | 0
GEN-2018-088 | 04 SOUTHEAST | 514908 | ARCADIA7 | 345 | 28.6269 | 28.6269 | 0
GEN-2018-088 | 04 SOUTHEAST | 514934 | DRAPER 7 | 345 | 26.1641 | 26.1641 | 0
GEN-2018-088 | 04 SOUTHEAST | 515044 | SEMINOL4 | 138 | 40.4325 | 40.4325 | 0
GEN-2018-088 | 04 SOUTHEAST | 515136 | SUNNYSD7 | 345 | 12.0848 | 12.0848 | 0
GEN-2018-088 | 04 SOUTHEAST | 516006 | DMNDSPG7 | 345 | 7.4023 | 7.4023 | 0
GEN-2018-088 | 04 SOUTHEAST | 520411 | SAWYER4 | 138 | 10.5586 | 10.5586 | 0
GEN-2018-088 | 04 SOUTHEAST | 520918 | FROGVIL4 | 138 | 10.6779 | 10.6779 | 0
GEN-2018-088 | 04 SOUTHEAST | 521079 | VALLANT4 | 138 | 8.6292 | 8.6292 | 0
GEN-2018-088 | 04 SOUTHEAST | 587430 | GEN-2016-063 | 345 | 8.0519 | 8.0519 | 0
GEN-2018-088 | 04 SOUTHEAST | 588670 | GEN-2017-023 | 138 | 18.8779 | 18.8779 | 0
GEN-2018-088 | 04 SOUTHEAST | 588839 | FIREWHL-TAP | 345 | 20.1846 | 20.1846 | 0
GEN-2018-088 | 04 SOUTHEAST | 589130 | GEN-2017-075 | 345 | 8.1486 | 8.1486 | 0
GEN-2018-088 | 04 SOUTHEAST | 760830 | GEN-2017-149 | 345 | 4.1868 | 4.1868 | 0
GEN-2018-088 | 04 SOUTHEAST | 762431 | G18-003-TAP | 138 | 11.1524 | 11.1524 | 0
GEN-2018-088 | 04 SOUTHEAST | 762845 | GEN-2018-050 | 345 | 12.4023 | 12.4023 | 0
GEN-2018-088 | 04 SOUTHEAST | 337363 | 3SAREPTA! | 115 | 19.6304 | 19.6304 | 0
GEN-2018-088 | 04 SOUTHEAST | 337562 | 7EL DORADO | 345 | 13.7374 | 13.7374 | 0
GEN-2018-088 | 04 SOUTHEAST | 337672 | 4MURFBORO | 138 | 2.8751 | 2.8751 | 0
GEN-2018-088 | 04 SOUTHEAST | 500260 | DOLHILL6 | 230 | 14.9977 | 14.9977 | 0
GEN-2018-088 | 04 SOUTHEAST | 504030 | SFORE_1 2 | 69 | 2.8399 | 2.8399 | 0
GEN-2018-088 | 04 SOUTHEAST | 504122 | MCNAB 3 | 115 | 13.7239 | 13.7239 | 0
GEN-2018-088 | 04 SOUTHEAST | 504363 | NE-TEXARK2 | 69 | 5.3477 | 5.3477 | 0
GEN-2018-088 | 04 SOUTHEAST | 507421 | FOREMAN2 | 69 | 3.6654 | 3.6654 | 0
GEN-2018-088 | 04 SOUTHEAST | 507427 | OKAY 2 | 69 | 7.4399 | 7.4399 | 0
GEN-2018-088 | 04 SOUTHEAST | 507463 | BARITERDTP 4 | 138 | 3.6005 | 3.6005 | 0
GEN-2018-088 | 04 SOUTHEAST | 507732 | GENMOTR4 | 138 | 17.6233 | 17.6233 | 0
GEN-2018-088 | 04 SOUTHEAST | 507748 | POWELL 4 | 138 | 19.2003 | 19.2003 | 0
GEN-2018-088 | 04 SOUTHEAST | 507755 | S SHV 4 | 138 | 22.7776 | 22.7776 | 0
GEN-2018-088 | 04 SOUTHEAST | 507757 | SPRIDGE4 | 138 | 11.1659 | 11.1659 | 0
GEN-2018-088 | 04 SOUTHEAST | 507774 | NORAM 4 | 138 | 17.1024 | 17.1024 | 0
GEN-2018-088 | 04 SOUTHEAST | 507793 | LEASIDE 4 | 138 | 22.1591 | 22.1591 | 0
GEN-2018-088 | 04 SOUTHEAST | 508051 | ASHDOWN2 | 69 | 11.9233 | 11.9233 | 0
GEN-2018-088 | 04 SOUTHEAST | 508053 | BANN 2 | 69 | 20.5916 | 20.5916 | 0
GEN-2018-088 | 04 SOUTHEAST | 508056 | BRYANML4 | 138 | 7.1404 | 7.1404 | 0
GEN-2018-088 | 04 SOUTHEAST | 508065 | NEKOOSA2 | 69 | 6.2847 | 6.2847 | 0
GEN-2018-088 | 04 SOUTHEAST | 508069 | NNBOSTN4 | 138 | 11.2391 | 11.2391 | 0
GEN-2018-088 | 04 SOUTHEAST | 508075 | REDSPRG4 | 138 | 14.5368 | 14.5368 | 0
GEN-2018-088 | 04 SOUTHEAST | 508078 | SETEXAR4 | 138 | 11.0707 | 11.0707 | 0
GEN-2018-088 | 04 SOUTHEAST | 508081 | SUGHLET2 | 69 | 17.006 | 17.006 | 0
GEN-2018-088 | 04 SOUTHEAST | 508082 | SUGHLWT2 | 69 | 16.9581 | 16.9581 | 0
GEN-2018-088 | 04 SOUTHEAST | 508089 | WATLANT2 | 69 | 8.2175 | 8.2175 | 0
GEN-2018-088 | 04 SOUTHEAST | 508106 | CASSTP4 | 138 | 7.3459 | 7.3459 | 0
GEN-2018-088 | 04 SOUTHEAST | 508296 | LSSOUTH2 | 69 | 10.079 | 10.079 | 0
GEN-2018-088 | 04 SOUTHEAST | 508313 | PITTSB_4 | 138 | 8.748 | 8.748 | 0
GEN-2018-088 | 04 SOUTHEAST | 508337 | CHAPELH4 | 138 | 7.3226 | 7.3226 | 0
GEN-2018-088 | 04 SOUTHEAST | 508350 | PERDUE 2 | 69 | 13.2936 | 13.2936 | 0
GEN-2018-088 | 04 SOUTHEAST | 508369 | EXXONM 4 | 138 | 6.5643 | 6.5643 | 0
GEN-2018-088 | 04 SOUTHEAST | 508552 | LLAMOND4 | 138 | 6.9872 | 6.9872 | 0
GEN-2018-088 | 04 SOUTHEAST | 508557 | MARSHL-4 | 138 | 16.5294 | 16.5294 | 0
GEN-2018-088 | 04 SOUTHEAST | 508560 | NEWGLAD4 | 138 | 9.4659 | 9.4659 | 0
GEN-2018-088 | 04 SOUTHEAST | 508564 | PLILER 4 | 138 | 12.1571 | 12.1571 | 0
GEN-2018-088 | 04 SOUTHEAST | 508566 | SABMINT4 | 138 | 33.977 | 33.977 | 0
GEN-2018-088 | 04 SOUTHEAST | 508567 | SCOTTSV4 | 138 | 12.0614 | 12.0614 | 0
GEN-2018-088 | 04 SOUTHEAST | 508585 | TENRUSK7 | 345 | 7.7847 | 7.7847 | 0
GEN-2018-088 | 04 SOUTHEAST | 508595 | HALLSVLS4 | 138 | 18.487 | 18.487 | 0
GEN-2018-088 | 04 SOUTHEAST | 508806 | LIEBERM4 | 138 | 16.6692 | 16.6692 | 0
GEN-2018-088 | 04 SOUTHEAST | 508816 | OAKPH 4 | 138 | 19.3555 | 19.3555 | 0
GEN-2018-088 | 04 SOUTHEAST | 508827 | NGPL 4 | 138 | 10.0941 | 10.0941 | 0
GEN-2018-088 | 04 SOUTHEAST | 508833 | IPCJEFF4 | 138 | 12.136 | 12.136 | 0
GEN-2018-088 | 04 SOUTHEAST | 509092 | EASTON 4 | 138 | 24.3732 | 24.3732 | 0
GEN-2018-088 | 04 SOUTHEAST | 509603 | BIGSAND4 | 138 | 7.0909 | 7.0909 | 0
GEN-2018-088 | 04 SOUTHEAST | 509607 | DIAN 4 | 138 | 11.5427 | 11.5427 | 0
GEN-2018-088 | 04 SOUTHEAST | 509624 | LAKEPIN4 | 138 | 7.3647 | 7.3647 | 0
GEN-2018-088 | 04 SOUTHEAST | 509628 | NOONDAY4 | 138 | 5.7974 | 5.7974 | 0
GEN-2018-088 | 04 SOUTHEAST | 509666 | DUGLASV4 | 138 | 5.0334 | 5.0334 | 0
GEN-2018-088 | 04 SOUTHEAST | 510864 | B.BOW 4 | 138 | 6.1863 | 6.1863 | 0
GEN-2018-088 | 04 SOUTHEAST | 510868 | GA PAC 2 | 69 | 2.4963 | 2.4963 | 0
GEN-2018-088 | 04 SOUTHEAST | 510869 | W CITY 2 | 69 | 3.8784 | 3.8784 | 0
GEN-2018-088 | 04 SOUTHEAST | 510875 | KI PMPN2 | 69 | 3.4684 | 3.4684 | 0
GEN-2018-088 | 04 SOUTHEAST | 510890 | CRAIGJT4 | 138 | 8.6935 | 8.6935 | 0
GEN-2018-088 | 04 SOUTHEAST | 510894 | VALYTIM2 | 69 | 2.7048 | 2.7048 | 0
GEN-2018-088 | 04 SOUTHEAST | 510917 | FTOWSON2 | 69 | 3.8066 | 3.8066 | 0
GEN-2018-088 | 04 SOUTHEAST | 510920 | SAWYER 2 | 69 | 3.9035 | 3.9035 | 0
GEN-2018-088 | 04 SOUTHEAST | 510951 | TALAWANDA 4 | 138 | 9.756 | 9.756 | 0
GEN-2018-088 | 04 SOUTHEAST | 511568 | TERRYRD7 | 345 | 11.0146 | 11.0146 | 0
GEN-2018-088 | 04 SOUTHEAST | 514880 | NORTWST7 | 345 | 32.9086 | 32.9086 | 0
GEN-2018-088 | 04 SOUTHEAST | 514907 | ARCADIA4 | 138 | 47.2233 | 47.2233 | 0
GEN-2018-088 | 04 SOUTHEAST | 514909 | REDBUD 7 | 345 | 27.6026 | 27.6026 | 0
GEN-2018-088 | 04 SOUTHEAST | 514933 | DRAPER 4 | 138 | 42.9122 | 42.9122 | 0
GEN-2018-088 | 04 SOUTHEAST | 515055 | MAUD 4 | 138 | 20.1325 | 20.1325 | 0
GEN-2018-088 | 04 SOUTHEAST | 515100 | PAOLI- 4 | 138 | 10.3088 | 10.3088 | 0
GEN-2018-088 | 04 SOUTHEAST | 515120 | RUSSET-4 | 138 | 11.3858 | 11.3858 | 0
GEN-2018-088 | 04 SOUTHEAST | 515122 | SXMLCKT4 | 138 | 11.135 | 11.135 | 0
GEN-2018-088 | 04 SOUTHEAST | 515135 | SUNNYSD4 | 138 | 19.117 | 19.117 | 0
GEN-2018-088 | 04 SOUTHEAST | 515150 | CANEYCK4 | 138 | 9.1286 | 9.1286 | 0
GEN-2018-088 | 04 SOUTHEAST | 515224 | MUSKOGE7 | 345 | 28.6414 | 28.6414 | 0
GEN-2018-088 | 04 SOUTHEAST | 515531 | VANOSTP4 | 138 | 13.3128 | 13.3128 | 0
GEN-2018-088 | 04 SOUTHEAST | 515977 | LKKONWA4 | 138 | 39.5128 | 39.5128 | 0
GEN-2018-088 | 04 SOUTHEAST | 520419 | GARVIN4 | 138 | 5.9763 | 5.9763 | 0
GEN-2018-088 | 04 SOUTHEAST | 521036 | RATTAN 4 | 138 | 6.8302 | 6.8302 | 0
GEN-2018-088 | 04 SOUTHEAST | 521098 | WSBNKTP4 | 138 | 6.5692 | 6.5692 | 0
GEN-2018-088 | 04 SOUTHEAST | 555234 | NSUB345 | 345 | 27.0301 | 27.0301 | 0
GEN-2018-088 | 04 SOUTHEAST | 588838 | G17-092-SWYD | 345 | 20.1846 | 20.1846 | 0
GEN-2018-088 | 04 SOUTHEAST | 760032 | GEN-2017-132 | 345 | 6.7839 | 6.7839 | 0
GEN-2018-088 | 04 SOUTHEAST | 760851 | GEN-2017-154 | 345 | 3.8126 | 3.8126 | 0
GEN-2018-088 | 04 SOUTHEAST | 761859 | GEN-2017-166 | 345 | 7.2286 | 7.2286 | 0
GEN-2018-088 | 04 SOUTHEAST | 762427 | GEN-2018-003 | 138 | 11.1524 | 11.1524 | 0
GEN-2018-106 | 04 SOUTHEAST | 508809 | LONGWD 7 | 345 | 16.2105 | 15.8796 | 0.3309
GEN-2018-106 | 04 SOUTHEAST | 337376 | 7SAREPTA% | 345 | 9.8524 | 9.8045 | 0.0479
GEN-2018-106 | 04 SOUTHEAST | 507760 | SW SHV 7 | 345 | 16.0426 | 15.8849 | 0.1577
GEN-2018-106 | 04 SOUTHEAST | 508808 | LONGWD 4 | 138 | 24.8141 | 24.6649 | 0.1492
GEN-2018-106 | 04 SOUTHEAST | 508841 | WILKES 7 | 345 | 17.8224 | 17.7377 | 0.0847
GEN-2018-106 | 04 SOUTHEAST | 762845 | GEN-2018-050 | 345 | 12.4023 | 12.0795 | 0.3228
GEN-2018-106 | 04 SOUTHEAST | 337363 | 3SAREPTA! | 115 | 19.6304 | 19.5791 | 0.0513
GEN-2018-106 | 04 SOUTHEAST | 337562 | 7EL DORADO | 345 | 13.7374 | 13.725 | 0.0124
GEN-2018-106 | 04 SOUTHEAST | 500250 | DOLHILL7 | 345 | 12.3341 | 12.3092 | 0.0249
GEN-2018-106 | 04 SOUTHEAST | 507759 | SW SHV 4 | 138 | 30.6446 | 30.4594 | 0.1852
GEN-2018-106 | 04 SOUTHEAST | 507774 | NORAM 4 | 138 | 17.1024 | 17.0419 | 0.0605
GEN-2018-106 | 04 SOUTHEAST | 508072 | NWTXARK7 | 345 | 16.4948 | 16.4742 | 0.0206
GEN-2018-106 | 04 SOUTHEAST | 508359 | WELSH 7 | 345 | 21.3102 | 21.2633 | 0.0469
GEN-2018-106 | 04 SOUTHEAST | 508567 | SCOTTSV4 | 138 | 12.0614 | 12.0453 | 0.0161
GEN-2018-106 | 04 SOUTHEAST | 508806 | LIEBERM4 | 138 | 16.6692 | 16.6203 | 0.0489
GEN-2018-106 | 04 SOUTHEAST | 508816 | OAKPH 4 | 138 | 19.3555 | 19.2667 | 0.0888
GEN-2018-106 | 04 SOUTHEAST | 508832 | DIANA 7 | 345 | 18.9825 | 18.939 | 0.0435
GEN-2018-106 | 04 SOUTHEAST | 508840 | WILKES 4 | 138 | 30.4579 | 30.4134 | 0.0445
GEN-2018-106 | 04 SOUTHEAST | 5917 | SPPMAINBUS | 345 | 21.3102 | 21.2633 | 0.0469
GEN-2018-106 | 04 SOUTHEAST | 337361 | 3MINDEN_LA! | 115 | 6.6253 | 6.6229 | 0.0024
GEN-2018-106 | 04 SOUTHEAST | 337364 | 3CULLEN | 115 | 8.315 | 8.3058 | 0.0092
GEN-2018-106 | 04 SOUTHEAST | 337365 | 3SPRINGHILL | 115 | 9.5458 | 9.5362 | 0.0096
GEN-2018-106 | 04 SOUTHEAST | 337366 | 3HAYNESVILLE | 115 | 5.7711 | 5.7689 | 0.0022
GEN-2018-106 | 04 SOUTHEAST | 337561 | 8EL DORADO% | 500 | 27.4804 | 27.4706 | 0.0098
GEN-2018-106 | 04 SOUTHEAST | 500260 | DOLHILL6 | 230 | 14.9977 | 14.9801 | 0.0176
GEN-2018-106 | 04 SOUTHEAST | 507455 | TURK 7 | 345 | 11.6362 | 11.6298 | 0.0064
GEN-2018-106 | 04 SOUTHEAST | 507711 | ARSHILL4 | 138 | 24.6725 | 24.5954 | 0.0771
GEN-2018-106 | 04 SOUTHEAST | 507727 | FLOURNY4 | 138 | 16.4304 | 16.3749 | 0.0555
GEN-2018-106 | 04 SOUTHEAST | 507732 | GENMOTR4 | 138 | 17.6233 | 17.5601 | 0.0632
GEN-2018-106 | 04 SOUTHEAST | 507748 | POWELL 4 | 138 | 19.2003 | 19.1391 | 0.0612
GEN-2018-106 | 04 SOUTHEAST | 507749 | RAINES 4 | 138 | 16.2405 | 16.1965 | 0.044
GEN-2018-106 | 04 SOUTHEAST | 507755 | S SHV 4 | 138 | 22.7776 | 22.6954 | 0.0822
GEN-2018-106 | 04 SOUTHEAST | 507757 | SPRIDGE4 | 138 | 11.1659 | 11.1468 | 0.0191
GEN-2018-106 | 04 SOUTHEAST | 507793 | LEASIDE 4 | 138 | 22.1591 | 22.0717 | 0.0874
GEN-2018-106 | 04 SOUTHEAST | 508064 | MUNZCTY4 | 138 | 7.2417 | 7.2399 | 0.0018
GEN-2018-106 | 04 SOUTHEAST | 508071 | NWTXARK4 | 138 | 28.0292 | 28.0082 | 0.021
GEN-2018-106 | 04 SOUTHEAST | 508090 | WATLANT4 | 138 | 7.3631 | 7.3611 | 0.002
GEN-2018-106 | 04 SOUTHEAST | 508297 | LSSOUTH4 | 138 | 17.1869 | 17.1737 | 0.0132
GEN-2018-106 | 04 SOUTHEAST | 508298 | LYDIA 7 | 345 | 13.4983 | 13.486 | 0.0123
GEN-2018-106 | 04 SOUTHEAST | 508355 | WELSHRE4 | 138 | 7.3371 | 7.3347 | 0.0024
GEN-2018-106 | 04 SOUTHEAST | 508563 | PIRKEY 7 | 345 | 16.8996 | 16.8813 | 0.0183
GEN-2018-106 | 04 SOUTHEAST | 508569 | SEMRSHL4 | 138 | 13.3695 | 13.3563 | 0.0132
GEN-2018-106 | 04 SOUTHEAST | 508805 | LIEBERM2 | 69 | 8.9405 | 8.9352 | 0.0053
GEN-2018-106 | 04 SOUTHEAST | 508831 | DIANA 4 | 138 | 29.429 | 29.3914 | 0.0376
GEN-2018-106 | 04 SOUTHEAST | 508833 | IPCJEFF4 | 138 | 12.136 | 12.1268 | 0.0092
GEN-2018-106 | 04 SOUTHEAST | 508835 | JEFFRSN4 | 138 | 13.4042 | 13.3936 | 0.0106
GEN-2018-106 | 04 SOUTHEAST | 510911 | VALIANT7 | 345 | 16.6284 | 16.621 | 0.0074
GEN-2018-106 | 04 SOUTHEAST | 588404 | G16-167-TAP | 138 | 9.7797 | 9.7642 | 0.0155
GEN-2018-106 | 04 SOUTHEAST | 5919 | WELSHDC1 | 345 | 21.3102 | 21.2633 | 0.0469
GEN-2018-106 | 04 SOUTHEAST | 5921 | SPP-CAP1 | 345 | 21.3102 | 21.2633 | 0.0469
GEN-2018-106 | 04 SOUTHEAST | 5922 | SPP-CAP2 | 345 | 21.3102 | 21.2633 | 0.0469
GEN-2018-106 | 04 SOUTHEAST | 5923 | SPP-CAP3 | 345 | 21.3102 | 21.2633 | 0.0469
GEN-2018-106 | 04 SOUTHEAST | 5924 | SPP-REAC1 | 345 | 21.3102 | 21.2633 | 0.0469
GEN-2018-106 | 04 SOUTHEAST | 303302 | 3MINDEN_LG | 115 | 5.4661 | 5.4648 | 0.0013
GEN-2018-106 | 04 SOUTHEAST | 337360 | 3ADA_LA | 115 | 5.4117 | 5.4105 | 0.0012
GEN-2018-106 | 04 SOUTHEAST | 337362 | 3LA_ORD_PLNT | 115 | 4.3257 | 4.3246 | 0.0011
GEN-2018-106 | 04 SOUTHEAST | 337368 | 8MT_OLIVE% | 500 | 11.806 | 11.8038 | 0.0022
GEN-2018-106 | 04 SOUTHEAST | 337420 | 8STERLING% | 500 | 20.0611 | 20.0599 | 0.0012
GEN-2018-106 | 04 SOUTHEAST | 337500 | 3TAYLOR | 115 | 6.9558 | 6.952 | 0.0038
GEN-2018-106 | 04 SOUTHEAST | 337515 | 8MCNEIL% | 500 | 14.1196 | 14.1172 | 0.0024
GEN-2018-106 | 04 SOUTHEAST | 337526 | 3EMERSON! | 115 | 5.7427 | 5.7414 | 0.0013
GEN-2018-106 | 04 SOUTHEAST | 337539 | 3EL DORADO! | 115 | 27.8269 | 27.8246 | 0.0023
GEN-2018-106 | 04 SOUTHEAST | 337643 | 8SHERIDAN% | 500 | 27.4372 | 27.4359 | 0.0013
GEN-2018-106 | 04 SOUTHEAST | 338440 | 8PANDA% | 500 | 27.4138 | 27.404 | 0.0098
GEN-2018-106 | 04 SOUTHEAST | 500140 | CARROLL6 | 230 | 13.3091 | 13.3001 | 0.009
GEN-2018-106 | 04 SOUTHEAST | 500255 | REDBAYOU_6 | 230 | 10.4498 | 10.442 | 0.0078
GEN-2018-106 | 04 SOUTHEAST | 507431 | PATTERS4 | 138 | 13.5516 | 13.5483 | 0.0033
GEN-2018-106 | 04 SOUTHEAST | 507454 | TURK 4 | 138 | 27.2509 | 27.2416 | 0.0093
GEN-2018-106 | 04 SOUTHEAST | 507710 | ARSHILL2 | 69 | 28.1703 | 28.1176 | 0.0527
GEN-2018-106 | 04 SOUTHEAST | 507726 | FLOURNY2 | 69 | 14.3327 | 14.3146 | 0.0181
GEN-2018-106 | 04 SOUTHEAST | 507731 | FTHUMBG4 | 138 | 18.9983 | 18.9493 | 0.049
GEN-2018-106 | 04 SOUTHEAST | 507735 | HARTSIS4 | 138 | 16.0533 | 16.0155 | 0.0378
GEN-2018-106 | 04 SOUTHEAST | 507738 | LINWOOD4 | 138 | 22.0594 | 21.984 | 0.0754
GEN-2018-106 | 04 SOUTHEAST | 507742 | MCWILLI4 | 138 | 20.8896 | 20.8269 | 0.0627
GEN-2018-106 | 04 SOUTHEAST | 507754 | S SHV 2 | 69 | 18.7861 | 18.7594 | 0.0267
GEN-2018-106 | 04 SOUTHEAST | 507765 | WALLAKE4 | 138 | 10.4407 | 10.4255 | 0.0152
GEN-2018-106 | 04 SOUTHEAST | 507767 | WESTELC4 | 138 | 20.4074 | 20.3351 | 0.0723
GEN-2018-106 | 04 SOUTHEAST | 507771 | CEDARGR4 | 138 | 21.9363 | 21.8616 | 0.0747
GEN-2018-106 | 04 SOUTHEAST | 507788 | MINDEN-3 | 115 | 5.3452 | 5.3437 | 0.0015
GEN-2018-106 | 04 SOUTHEAST | 507789 | STLGENS4 | 138 | 24.2835 | 24.2111 | 0.0724
GEN-2018-106 | 04 SOUTHEAST | 507794 | LEASIDE 2 | 69 | 12.8497 | 12.8349 | 0.0148
GEN-2018-106 | 04 SOUTHEAST | 508049 | NASH 4 | 138 | 21.038 | 21.0263 | 0.0117
GEN-2018-106 | 04 SOUTHEAST | 508056 | BRYANML4 | 138 | 7.1404 | 7.1387 | 0.0017
GEN-2018-106 | 04 SOUTHEAST | 508070 | NWT-BNT4 | 138 | 26.7366 | 26.7176 | 0.019
GEN-2018-106 | 04 SOUTHEAST | 508080 | SUGARHL4 | 138 | 12.5445 | 12.541 | 0.0035
GEN-2018-106 | 04 SOUTHEAST | 508089 | WATLANT2 | 69 | 8.2175 | 8.2162 | 0.0013
GEN-2018-106 | 04 SOUTHEAST | 508106 | CASSTP4 | 138 | 7.3459 | 7.3439 | 0.002
GEN-2018-106 | 04 SOUTHEAST | 508296 | LSSOUTH2 | 69 | 10.079 | 10.0768 | 0.0022
GEN-2018-106 | 04 SOUTHEAST | 508313 | PITTSB_4 | 138 | 8.748 | 8.7447 | 0.0033
GEN-2018-106 | 04 SOUTHEAST | 508337 | CHAPELH4 | 138 | 7.3226 | 7.3203 | 0.0023
GEN-2018-106 | 04 SOUTHEAST | 508351 | PERDUE 4 | 138 | 10.5571 | 10.5535 | 0.0036
GEN-2018-106 | 04 SOUTHEAST | 508557 | MARSHL-4 | 138 | 16.5294 | 16.5198 | 0.0096
GEN-2018-106 | 04 SOUTHEAST | 508562 | PIRKEY 4 | 138 | 41.7547 | 41.7115 | 0.0432
GEN-2018-106 | 04 SOUTHEAST | 508566 | SABMINT4 | 138 | 33.977 | 33.9452 | 0.0318
GEN-2018-106 | 04 SOUTHEAST | 508571 | SPRHILL4 | 138 | 8.2944 | 8.2917 | 0.0027
GEN-2018-106 | 04 SOUTHEAST | 508572 | LEBROCK7 | 345 | 15.7793 | 15.7646 | 0.0147
GEN-2018-106 | 04 SOUTHEAST | 508801 | BLANCH-2 | 69 | 6.6775 | 6.6745 | 0.003
GEN-2018-106 | 04 SOUTHEAST | 508811 | NBENTON4 | 138 | 9.0965 | 9.0835 | 0.013
GEN-2018-106 | 04 SOUTHEAST | 508812 | OILCITY2 | 69 | 7.1997 | 7.1967 | 0.003
GEN-2018-106 | 04 SOUTHEAST | 508837 | NGPLTAP4 | 138 | 13.3857 | 13.3792 | 0.0065
GEN-2018-106 | 04 SOUTHEAST | 509052 | STONWAL4 | 138 | 10.3107 | 10.2945 | 0.0162
GEN-2018-106 | 04 SOUTHEAST | 509103 | WLNTSPRINGS4 | 138 | 8.9479 | 8.9416 | 0.0063
GEN-2018-106 | 04 SOUTHEAST | 509624 | LAKEPIN4 | 138 | 7.3647 | 7.3615 | 0.0032
GEN-2018-106 | 04 SOUTHEAST | 509639 | DIANASW4 | 138 | 12.0216 | 12.0153 | 0.0063
GEN-2018-106 | 04 SOUTHEAST | 509666 | DUGLASV4 | 138 | 5.0334 | 5.0325 | 0.0009
GEN-2018-106 | 04 SOUTHEAST | 510907 | PITTSB-7 | 345 | 16.4511 | 16.4494 | 0.0017
GEN-2018-106 | 04 SOUTHEAST | 510918 | VALIANT4 | 138 | 15.7903 | 15.7882 | 0.0021
GEN-2018-106 | 04 SOUTHEAST | 521157 | HUGO 7 | 345 | 12.5857 | 12.5827 | 0.003
GEN-2018-106 | 04 SOUTHEAST | 588400 | GEN-2016-167 | 138 | 9.682 | 9.6667 | 0.0153
GEN-2018-106 | 04 SOUTHEAST | 763164 | GEN-2018-087 | 345 | 12.9226 | 12.9114 | 0.0112
GEN-2018-106 | 04 SOUTHEAST | 337351 | 3SAILES! | 115 | 5.9526 | 5.9515 | 0.0011
GEN-2018-106 | 04 SOUTHEAST | 337367 | 3ARCADIA | 115 | 5.3346 | 5.334 | 0.0006
GEN-2018-106 | 04 SOUTHEAST | 337369 | 6MT_OLIVE% | 230 | 13.5001 | 13.4985 | 0.0016
GEN-2018-106 | 04 SOUTHEAST | 337413 | 8STERLING2% | 500 | 20.0611 | 20.0599 | 0.0012
GEN-2018-106 | 04 SOUTHEAST | 337415 | 3STERLING% | 115 | 35.201 | 35.2002 | 0.0008
GEN-2018-106 | 04 SOUTHEAST | 337427 | 8PERRYVILLE% | 500 | 19.7364 | 19.7353 | 0.0011
GEN-2018-106 | 04 SOUTHEAST | 337514 | 3MACEDONA | 115 | 6.2658 | 6.2636 | 0.0022
GEN-2018-106 | 04 SOUTHEAST | 337516 | 3MCNEIL! | 115 | 24.0098 | 24.006 | 0.0038
GEN-2018-106 | 04 SOUTHEAST | 337524 | 3KERLIN+ | 115 | 7.0156 | 7.0145 | 0.0011
GEN-2018-106 | 04 SOUTHEAST | 337537 | 3SMACKOVER+ | 115 | 9.0279 | 9.0277 | 0.0002
GEN-2018-106 | 04 SOUTHEAST | 337540 | 3ELD DONAN | 115 | 14.4576 | 14.457 | 0.0006
GEN-2018-106 | 04 SOUTHEAST | 337553 | 3ELDORADO.E! | 115 | 13.173 | 13.1725 | 0.0005
GEN-2018-106 | 04 SOUTHEAST | 337560 | 3ELD QUINN | 115 | 27.0987 | 27.0965 | 0.0022
GEN-2018-106 | 04 SOUTHEAST | 337651 | 8WHT BLUFF% | 500 | 27.2573 | 27.2567 | 0.0006
GEN-2018-106 | 04 SOUTHEAST | 337754 | 8ETTA% | 500 | 18.5741 | 18.5732 | 0.0009
GEN-2018-106 | 04 SOUTHEAST | 337763 | 8MAGNETCOVE% | 500 | 22.1193 | 22.1183 | 0.001
GEN-2018-106 | 04 SOUTHEAST | 337808 | 8MABELVALE% | 500 | 27.0398 | 27.039 | 0.0008
GEN-2018-106 | 04 SOUTHEAST | 500150 | CARROLL4 | 138 | 12.8489 | 12.8434 | 0.0055
GEN-2018-106 | 04 SOUTHEAST | 500430 | IPAPER 4 | 138 | 5.3587 | 5.3556 | 0.0031
GEN-2018-106 | 04 SOUTHEAST | 500465 | 6LAYFLD | 230 | 15.4897 | 15.4853 | 0.0044
GEN-2018-106 | 04 SOUTHEAST | 500525 | MANCOMP 6 | 230 | 8.5297 | 8.525 | 0.0047
GEN-2018-106 | 04 SOUTHEAST | 504029 | SFOREMAN 4 | 138 | 8.6908 | 8.6892 | 0.0016
GEN-2018-106 | 04 SOUTHEAST | 504123 | LOCKSBRG 4 | 138 | 5.9074 | 5.9068 | 0.0006
GEN-2018-106 | 04 SOUTHEAST | 504124 | ASHDWN_W 4 | 138 | 10.093 | 10.0913 | 0.0017
GEN-2018-106 | 04 SOUTHEAST | 507402 | ASHDWNR4 | 138 | 10.3735 | 10.3717 | 0.0018
GEN-2018-106 | 04 SOUTHEAST | 507428 | OKAY 4 | 138 | 10.226 | 10.2246 | 0.0014
GEN-2018-106 | 04 SOUTHEAST | 507429 | PATTERS2 | 69 | 14.3228 | 14.321 | 0.0018
GEN-2018-106 | 04 SOUTHEAST | 507434 | SNASHVL4 | 138 | 3.7064 | 3.7063 | 0.0001
GEN-2018-106 | 04 SOUTHEAST | 507456 | TURK 3 | 115 | 17.0546 | 17.052 | 0.0026
GEN-2018-106 | 04 SOUTHEAST | 507717 | BROOKS 2 | 69 | 20.4349 | 20.4069 | 0.028
GEN-2018-106 | 04 SOUTHEAST | 507728 | FORBNGT2 | 69 | 17.9212 | 17.897 | 0.0242
GEN-2018-106 | 04 SOUTHEAST | 507730 | FTHUMBG2 | 69 | 18.2563 | 18.2335 | 0.0228
GEN-2018-106 | 04 SOUTHEAST | 507745 | NMARKET2 | 69 | 15.8633 | 15.8465 | 0.0168
GEN-2018-106 | 04 SOUTHEAST | 507746 | PIERMNT4 | 138 | 16.08 | 16.0429 | 0.0371
GEN-2018-106 | 04 SOUTHEAST | 507747 | PINESRD2 | 69 | 10.6214 | 10.6124 | 0.009
GEN-2018-106 | 04 SOUTHEAST | 507756 | SHEDRD 2 | 69 | 17.1751 | 17.1556 | 0.0195
GEN-2018-106 | 04 SOUTHEAST | 507758 | SUMMERG2 | 69 | 11.1344 | 11.1234 | 0.011
GEN-2018-106 | 04 SOUTHEAST | 507762 | T70THST2 | 69 | 12.6206 | 12.6088 | 0.0118
GEN-2018-106 | 04 SOUTHEAST | 507763 | TRICHEL4 | 138 | 15.9483 | 15.9135 | 0.0348
GEN-2018-106 | 04 SOUTHEAST | 507764 | WALLAKE2 | 69 | 9.0009 | 8.9951 | 0.0058
GEN-2018-106 | 04 SOUTHEAST | 507766 | WATERWK2 | 69 | 16.6222 | 16.6027 | 0.0195
GEN-2018-106 | 04 SOUTHEAST | 507770 | WOOLWTP2 | 69 | 11.7678 | 11.7556 | 0.0122
GEN-2018-106 | 04 SOUTHEAST | 507782 | PROBSON4 | 138 | 8.4001 | 8.3902 | 0.0099
GEN-2018-106 | 04 SOUTHEAST | 508050 | ANDRSNC4 | 138 | 7.6966 | 7.695 | 0.0016
GEN-2018-106 | 04 SOUTHEAST | 508052 | ATLANTA2 | 69 | 5.4327 | 5.4321 | 0.0006
GEN-2018-106 | 04 SOUTHEAST | 508054 | BANN 4 | 138 | 22.0554 | 22.0425 | 0.0129
GEN-2018-106 | 04 SOUTHEAST | 508059 | IPC T 4 | 138 | 8.1543 | 8.1522 | 0.0021
GEN-2018-106 | 04 SOUTHEAST | 508062 | LINDEN 2 | 69 | 5.8281 | 5.8274 | 0.0007
GEN-2018-106 | 04 SOUTHEAST | 508079 | SUGARHL2 | 69 | 17.828 | 17.8243 | 0.0037
GEN-2018-106 | 04 SOUTHEAST | 508091 | ALUMAX 4 | 138 | 18.4423 | 18.4333 | 0.009
GEN-2018-106 | 04 SOUTHEAST | 508105 | MANDEVILTP4 | 138 | 9.5942 | 9.5926 | 0.0016
GEN-2018-106 | 04 SOUTHEAST | 508286 | CAMPCOR4 | 138 | 7.9712 | 7.9685 | 0.0027
GEN-2018-106 | 04 SOUTHEAST | 508295 | LSREC 2 | 69 | 7.6703 | 7.6691 | 0.0012
GEN-2018-106 | 04 SOUTHEAST | 508310 | PETTY 4 | 138 | 7.7522 | 7.7496 | 0.0026
GEN-2018-106 | 04 SOUTHEAST | 508312 | PITTSB_2 | 69 | 8.8457 | 8.8441 | 0.0016
GEN-2018-106 | 04 SOUTHEAST | 508320 | LONSTAR2 | 69 | 8.3309 | 8.3294 | 0.0015
GEN-2018-106 | 04 SOUTHEAST | 508350 | PERDUE 2 | 69 | 13.2936 | 13.2908 | 0.0028
GEN-2018-106 | 04 SOUTHEAST | 508368 | SCROGNSSW4 | 138 | 5.7565 | 5.7551 | 0.0014
GEN-2018-106 | 04 SOUTHEAST | 508369 | EXXONM 4 | 138 | 6.5643 | 6.5629 | 0.0014
GEN-2018-106 | 04 SOUTHEAST | 508552 | LLAMOND4 | 138 | 6.9872 | 6.9855 | 0.0017
GEN-2018-106 | 04 SOUTHEAST | 508560 | NEWGLAD4 | 138 | 9.4659 | 9.4632 | 0.0027
GEN-2018-106 | 04 SOUTHEAST | 508564 | PLILER 4 | 138 | 12.1571 | 12.1524 | 0.0047
GEN-2018-106 | 04 SOUTHEAST | 508576 | MARAUTO2 | 69 | 17.8767 | 17.8704 | 0.0063
GEN-2018-106 | 04 SOUTHEAST | 508577 | SABINEM4 | 138 | 22.3348 | 22.3212 | 0.0136
GEN-2018-106 | 04 SOUTHEAST | 508585 | TENRUSK7 | 345 | 7.7847 | 7.782 | 0.0027
GEN-2018-106 | 04 SOUTHEAST | 508595 | HALLSVLS4 | 138 | 18.487 | 18.4789 | 0.0081
GEN-2018-106 | 04 SOUTHEAST | 508802 | BLANCHR2 | 69 | 7.5532 | 7.5494 | 0.0038
GEN-2018-106 | 04 SOUTHEAST | 508807 | LINTNRD4 | 138 | 8.7869 | 8.7748 | 0.0121
GEN-2018-106 | 04 SOUTHEAST | 508810 | NBENTON2 | 69 | 4.2944 | 4.2932 | 0.0012
GEN-2018-106 | 04 SOUTHEAST | 508815 | SUPEROR2 | 69 | 6.6978 | 6.6957 | 0.0021
GEN-2018-106 | 04 SOUTHEAST | 508827 | NGPL 4 | 138 | 10.0941 | 10.0905 | 0.0036
GEN-2018-106 | 04 SOUTHEAST | 508839 | WASKOM 2 | 69 | 4.4505 | 4.4491 | 0.0014
GEN-2018-106 | 04 SOUTHEAST | 509050 | KEATCHI4 | 138 | 7.8757 | 7.8675 | 0.0082
GEN-2018-106 | 04 SOUTHEAST | 509083 | ROKHILL4 | 138 | 11.3038 | 11.2964 | 0.0074
GEN-2018-106 | 04 SOUTHEAST | 509092 | EASTON 4 | 138 | 24.3732 | 24.3608 | 0.0124
GEN-2018-106 | 04 SOUTHEAST | 509366 | LAYFLD8 | 500 | 10.2325 | 10.2308 | 0.0017
GEN-2018-106 | 04 SOUTHEAST | 509603 | BIGSAND4 | 138 | 7.0909 | 7.0893 | 0.0016
GEN-2018-106 | 04 SOUTHEAST | 509607 | DIAN 4 | 138 | 11.5427 | 11.5369 | 0.0058
GEN-2018-106 | 04 SOUTHEAST | 509623 | LAKEPIN2 | 69 | 7.2941 | 7.2926 | 0.0015
GEN-2018-106 | 04 SOUTHEAST | 509628 | NOONDAY4 | 138 | 5.7974 | 5.7959 | 0.0015
GEN-2018-106 | 04 SOUTHEAST | 509645 | DUGLASV2 | 69 | 6.3636 | 6.3629 | 0.0007
GEN-2018-106 | 04 SOUTHEAST | 509664 | CHAPLHL4 | 138 | 7.088 | 7.0858 | 0.0022
GEN-2018-106 | 04 SOUTHEAST | 509668 | ROACH 2 | 69 | 6.262 | 6.2613 | 0.0007
GEN-2018-106 | 04 SOUTHEAST | 510866 | V-WEYCO4 | 138 | 9.8522 | 9.8514 | 0.0008
GEN-2018-106 | 04 SOUTHEAST | 510886 | IDABEL-4 | 138 | 6.8774 | 6.8771 | 0.0003
GEN-2018-106 | 04 SOUTHEAST | 510901 | HUGO---4 | 138 | 3.5315 | 3.5314 | 0.0001
GEN-2018-106 | 04 SOUTHEAST | 510910 | VALIANT2 | 69 | 7.4325 | 7.4322 | 0.0003
GEN-2018-106 | 04 SOUTHEAST | 510925 | KIOWA 7 | 345 | 16.1028 | 16.1012 | 0.0016
GEN-2018-106 | 04 SOUTHEAST | 514809 | JOHNCO 7 | 345 | 10.9329 | 10.9326 | 0.0003
GEN-2018-106 | 04 SOUTHEAST | 515045 | SEMINOL7 | 345 | 30.8428 | 30.8423 | 0.0005
GEN-2018-106 | 04 SOUTHEAST | 515422 | C-RIVER7 | 345 | 11.6454 | 11.645 | 0.0004
GEN-2018-106 | 04 SOUTHEAST | 520560 | HUGOITC4 | 138 | 22.7437 | 22.7412 | 0.0025
GEN-2018-106 | 04 SOUTHEAST | 520948 | HUGO PP4 | 138 | 22.938 | 22.9355 | 0.0025
GEN-2018-106 | 04 SOUTHEAST | 560088 | G16-063-TAP | 345 | 8.1603 | 8.1599 | 0.0004
GEN-2018-106 | 04 SOUTHEAST | 762431 | G18-003-TAP | 138 | 11.1524 | 11.1498 | 0.0026
GEN-2018-106 | 04 SOUTHEAST | 763131 | GEN-2018-082 | 345 | 10.1533 | 10.1527 | 0.0006
GEN-2018-115 | 04 SOUTHEAST | 511468 | L.E.S.-7 | 345 | 14.8644 | 14.2738 | 0.5906
GEN-2018-115 | 04 SOUTHEAST | 511456 | O.K.U.-7 | 345 | 6.3254 | 6.2796 | 0.0458
GEN-2018-115 | 04 SOUTHEAST | 511467 | L.E.S.-4 | 138 | 25.3857 | 24.997 | 0.3887
GEN-2018-115 | 04 SOUTHEAST | 587744 | G16-091-TAP | 345 | 16.3944 | 16.1793 | 0.2151
GEN-2018-115 | 04 SOUTHEAST | 760938 | G17-171-TAP | 345 | 12.0416 | 11.7686 | 0.273
GEN-2018-115 | 04 SOUTHEAST | 763318 | GEN-2018-115 | 345 | 14.5675 | 13.9764 | 0.5911
GEN-2018-115 | 04 SOUTHEAST | 511423 | FLE TAP4 | 138 | 8.7336 | 8.7131 | 0.0205
GEN-2018-115 | 04 SOUTHEAST | 511437 | COMANC-4 | 138 | 18.3773 | 18.2024 | 0.1749
GEN-2018-115 | 04 SOUTHEAST | 511439 | LWSTAP 4 | 138 | 11.6423 | 11.5703 | 0.072
GEN-2018-115 | 04 SOUTHEAST | 511466 | L.E.S.-2 | 69 | 16.4224 | 16.3587 | 0.0637
GEN-2018-115 | 04 SOUTHEAST | 511474 | SHERID4 | 138 | 12.4494 | 12.3628 | 0.0866
GEN-2018-115 | 04 SOUTHEAST | 511486 | ELGINJT4 | 138 | 10.0413 | 10.0094 | 0.0319
GEN-2018-115 | 04 SOUTHEAST | 511494 | COMMTAP4 | 138 | 22.0417 | 21.7606 | 0.2811
GEN-2018-115 | 04 SOUTHEAST | 511565 | OKLAUN HVDC7 | 345 | 6.3037 | 6.2582 | 0.0455
GEN-2018-115 | 04 SOUTHEAST | 511568 | TERRYRD7 | 345 | 11.0146 | 10.8586 | 0.156
GEN-2018-115 | 04 SOUTHEAST | 515800 | GRACMNT7 | 345 | 20.5087 | 20.3377 | 0.171
GEN-2018-115 | 04 SOUTHEAST | 587740 | GEN-2016-091 | 345 | 11.1551 | 11.0581 | 0.097
GEN-2018-115 | 04 SOUTHEAST | 587770 | GEN-2016-095 | 345 | 11.4525 | 11.3489 | 0.1036
GEN-2018-115 | 04 SOUTHEAST | 588760 | GEN-2017-033 | 345 | 4.4427 | 4.4213 | 0.0214
GEN-2018-115 | 04 SOUTHEAST | 760939 | GEN-2017-171 | 345 | 11.9683 | 11.6988 | 0.2695
GEN-2018-115 | 04 SOUTHEAST | 763215 | G18-092-TAP | 345 | 6.0024 | 5.9796 | 0.0228
GEN-2018-115 | 04 SOUTHEAST | 511422 | FLETCHR4 | 138 | 7.9769 | 7.9597 | 0.0172
GEN-2018-115 | 04 SOUTHEAST | 511431 | LWS S4 | 138 | 11.1592 | 11.093 | 0.0662
GEN-2018-115 | 04 SOUTHEAST | 511436 | COMANC-2 | 69 | 9.2141 | 9.2013 | 0.0128
GEN-2018-115 | 04 SOUTHEAST | 511469 | LGORE-N2 | 69 | 7.9734 | 7.9593 | 0.0141
GEN-2018-115 | 04 SOUTHEAST | 511470 | LGORE-S2 | 69 | 6.9103 | 6.8989 | 0.0114
GEN-2018-115 | 04 SOUTHEAST | 511487 | ELGINJT2 | 69 | 8.5044 | 8.4933 | 0.0111
GEN-2018-115 | 04 SOUTHEAST | 511488 | 112GORE4 | 138 | 12.8136 | 12.7301 | 0.0835
GEN-2018-115 | 04 SOUTHEAST | 511512 | RPPAPER4 | 138 | 12.0656 | 11.99 | 0.0756
GEN-2018-115 | 04 SOUTHEAST | 511537 | ARTVLTP4 | 138 | 11.828 | 11.752 | 0.076
GEN-2018-115 | 04 SOUTHEAST | 511563 | ELSWORTH 4 | 138 | 9.9666 | 9.936 | 0.0306
GEN-2018-115 | 04 SOUTHEAST | 511571 | RUSHSPR7 | 345 | 7.0502 | 6.9965 | 0.0537
GEN-2018-115 | 04 SOUTHEAST | 514801 | MINCO 7 | 345 | 23.2915 | 23.2302 | 0.0613
GEN-2018-115 | 04 SOUTHEAST | 515136 | SUNNYSD7 | 345 | 12.0848 | 12.0389 | 0.0459
GEN-2018-115 | 04 SOUTHEAST | 515802 | GRACMNT4 | 138 | 37.8367 | 37.7067 | 0.13
GEN-2018-115 | 04 SOUTHEAST | 529304 | OMDUNCN4 | 138 | 6.6263 | 6.612 | 0.0143
GEN-2018-115 | 04 SOUTHEAST | 560078 | G16-037-TAP | 345 | 10.1427 | 10.1259 | 0.0168
GEN-2018-115 | 04 SOUTHEAST | 563269 | GEN-2015-093 | 345 | 10.8212 | 10.7753 | 0.0459
GEN-2018-115 | 04 SOUTHEAST | 587794 | G16-097-TAP | 138 | 11.1766 | 11.1576 | 0.019
GEN-2018-115 | 04 SOUTHEAST | 762467 | G18-015-TAP | 345 | 5.8242 | 5.8096 | 0.0146
GEN-2018-115 | 04 SOUTHEAST | 763208 | GEN-2018-092 | 345 | 5.809 | 5.7879 | 0.0211
GEN-2018-115 | 04 SOUTHEAST | 511428 | LG-YEAR4 | 138 | 12.0102 | 11.9368 | 0.0734
GEN-2018-115 | 04 SOUTHEAST | 511451 | CYRIL--2 | 69 | 4.6452 | 4.6426 | 0.0026
GEN-2018-115 | 04 SOUTHEAST | 511453 | DUNCAN-4 | 138 | 6.3818 | 6.3705 | 0.0113
GEN-2018-115 | 04 SOUTHEAST | 511461 | FT.SILL2 | 69 | 5.924 | 5.9168 | 0.0072
GEN-2018-115 | 04 SOUTHEAST | 511471 | LWS-NTP4 | 138 | 11.7704 | 11.6962 | 0.0742
GEN-2018-115 | 04 SOUTHEAST | 511473 | PO.HILL2 | 69 | 5.8111 | 5.8053 | 0.0058
GEN-2018-115 | 04 SOUTHEAST | 511477 | S.W.S.-4 | 138 | 34.1031 | 34.0148 | 0.0883
GEN-2018-115 | 04 SOUTHEAST | 511503 | LAW WC2 | 69 | 4.5189 | 4.5141 | 0.0048
GEN-2018-115 | 04 SOUTHEAST | 511509 | 53CACHE4 | 138 | 11.8079 | 11.7323 | 0.0756
GEN-2018-115 | 04 SOUTHEAST | 511510 | LAIRGST4 | 138 | 12.4019 | 12.3245 | 0.0774
GEN-2018-115 | 04 SOUTHEAST | 511524 | L-DISTP2 | 69 | 8.5366 | 8.5258 | 0.0108
GEN-2018-115 | 04 SOUTHEAST | 511538 | ARTVILL4 | 138 | 8.5293 | 8.4897 | 0.0396
GEN-2018-115 | 04 SOUTHEAST | 511553 | CHISHOLM7 | 345 | 12.3397 | 12.3311 | 0.0086
GEN-2018-115 | 04 SOUTHEAST | 514809 | JOHNCO 7 | 345 | 10.9329 | 10.9151 | 0.0178
GEN-2018-115 | 04 SOUTHEAST | 514901 | CIMARON7 | 345 | 34.2931 | 34.2594 | 0.0337
GEN-2018-115 | 04 SOUTHEAST | 515135 | SUNNYSD4 | 138 | 19.117 | 19.0839 | 0.0331
GEN-2018-115 | 04 SOUTHEAST | 515444 | MCNOWND7 | 345 | 23.197 | 23.1363 | 0.0607
GEN-2018-115 | 04 SOUTHEAST | 515549 | MNCWND37 | 345 | 14.1504 | 14.1289 | 0.0215
GEN-2018-115 | 04 SOUTHEAST | 520814 | ANADARK4 | 138 | 37.3056 | 37.2189 | 0.0867
GEN-2018-115 | 04 SOUTHEAST | 521089 | WASHITA4 | 138 | 30.8551 | 30.7814 | 0.0737
GEN-2018-115 | 04 SOUTHEAST | 555234 | NSUB345 | 345 | 27.0301 | 27.0056 | 0.0245
GEN-2018-115 | 04 SOUTHEAST | 560088 | G16-063-TAP | 345 | 8.1603 | 8.1513 | 0.009
GEN-2018-115 | 04 SOUTHEAST | 563259 | GEN-2015-092 | 345 | 6.8087 | 6.7589 | 0.0498
GEN-2018-115 | 04 SOUTHEAST | 587230 | GEN-2016-037 | 345 | 9.6646 | 9.6494 | 0.0152
GEN-2018-115 | 04 SOUTHEAST | 587790 | GEN-2016-097 | 138 | 9.0227 | 9.0105 | 0.0122
GEN-2018-115 | 04 SOUTHEAST | 761250 | GEN-2017-233 | 345 | 22.5233 | 22.4661 | 0.0572
GEN-2018-115 | 04 SOUTHEAST | 761859 | GEN-2017-166 | 345 | 7.2286 | 7.2137 | 0.0149
GEN-2018-115 | 04 SOUTHEAST | 762216 | G17-151TAP | 345 | 8.5119 | 8.5066 | 0.0053
GEN-2018-115 | 04 SOUTHEAST | 762460 | GEN-2018-015 | 345 | 5.812 | 5.7974 | 0.0146
GEN-2018-115 | 04 SOUTHEAST | 762900 | GEN-2018-055 | 345 | 4.8244 | 4.8009 | 0.0235
GEN-2018-115 | 04 SOUTHEAST | 510907 | PITTSB-7 | 345 | 16.4511 | 16.4428 | 0.0083
GEN-2018-115 | 04 SOUTHEAST | 511421 | VERDEN 4 | 138 | 9.8107 | 9.8039 | 0.0068
GEN-2018-115 | 04 SOUTHEAST | 511429 | L AIRGS4 | 138 | 11.5924 | 11.5247 | 0.0677
GEN-2018-115 | 04 SOUTHEAST | 511430 | LWS N4 | 138 | 10.4875 | 10.4284 | 0.0591
GEN-2018-115 | 04 SOUTHEAST | 511445 | CARNEG-4 | 138 | 7.8125 | 7.8082 | 0.0043
GEN-2018-115 | 04 SOUTHEAST | 511450 | CORNVIL2 | 69 | 6.4936 | 6.4916 | 0.002
GEN-2018-115 | 04 SOUTHEAST | 511452 | DUNCAN-2 | 69 | 6.8743 | 6.8696 | 0.0047
GEN-2018-115 | 04 SOUTHEAST | 511476 | S.W.S.-2 | 69 | 4.2207 | 4.22 | 0.0007
GEN-2018-115 | 04 SOUTHEAST | 511483 | NORGE--4 | 138 | 11.1843 | 11.1759 | 0.0084
GEN-2018-115 | 04 SOUTHEAST | 511500 | CACHE4 | 138 | 8.3497 | 8.3211 | 0.0286
GEN-2018-115 | 04 SOUTHEAST | 511525 | LDISPOS2 | 69 | 4.9073 | 4.9038 | 0.0035
GEN-2018-115 | 04 SOUTHEAST | 511526 | L-RLITP2 | 69 | 7.2226 | 7.2152 | 0.0074
GEN-2018-115 | 04 SOUTHEAST | 511552 | DUNCHERTP4 | 138 | 6.1657 | 6.1555 | 0.0102
GEN-2018-115 | 04 SOUTHEAST | 511557 | CHISHOLM6 | 230 | 12.1566 | 12.1521 | 0.0045
GEN-2018-115 | 04 SOUTHEAST | 514808 | JOHNCO 4 | 138 | 15.4874 | 15.4756 | 0.0118
GEN-2018-115 | 04 SOUTHEAST | 514880 | NORTWST7 | 345 | 32.9086 | 32.8918 | 0.0168
GEN-2018-115 | 04 SOUTHEAST | 514898 | CIMARON4 | 138 | 45.5365 | 45.5161 | 0.0204
GEN-2018-115 | 04 SOUTHEAST | 514929 | PLVALLY4 | 138 | 45.9536 | 45.9339 | 0.0197
GEN-2018-115 | 04 SOUTHEAST | 514934 | DRAPER 7 | 345 | 26.1641 | 26.1455 | 0.0186
GEN-2018-115 | 04 SOUTHEAST | 515137 | UNIROY 4 | 138 | 12.7256 | 12.7136 | 0.012
GEN-2018-115 | 04 SOUTHEAST | 515144 | LONEGRV4 | 138 | 13.5118 | 13.4956 | 0.0162
GEN-2018-115 | 04 SOUTHEAST | 515164 | ROCKYPT4 | 138 | 11.8709 | 11.8608 | 0.0101
GEN-2018-115 | 04 SOUTHEAST | 515497 | MATHWSN7 | 345 | 32.7952 | 32.7748 | 0.0204
GEN-2018-115 | 04 SOUTHEAST | 515561 | CARTRCO4 | 138 | 8.1628 | 8.159 | 0.0038
GEN-2018-115 | 04 SOUTHEAST | 515610 | FSHRTAP7 | 345 | 16.0539 | 16.047 | 0.0069
GEN-2018-115 | 04 SOUTHEAST | 515939 | MNCWND47 | 345 | 9.8862 | 9.8762 | 0.01
GEN-2018-115 | 04 SOUTHEAST | 516006 | DMNDSPG7 | 345 | 7.4023 | 7.3946 | 0.0077
GEN-2018-115 | 04 SOUTHEAST | 520422 | SEQUOYAHJ4 | 138 | 26.2586 | 26.2157 | 0.0429
GEN-2018-115 | 04 SOUTHEAST | 520508 | CLVLDSW4 | 138 | 12.6695 | 12.6633 | 0.0062
GEN-2018-115 | 04 SOUTHEAST | 520810 | ANADARK2 | 69 | 14.4688 | 14.4621 | 0.0067
GEN-2018-115 | 04 SOUTHEAST | 520923 | GEORGIA4 | 138 | 18.7095 | 18.6873 | 0.0222
GEN-2018-115 | 04 SOUTHEAST | 521017 | ONEY 4 | 138 | 11.0996 | 11.0909 | 0.0087
GEN-2018-115 | 04 SOUTHEAST | 521031 | POCASET4 | 138 | 8.1012 | 8.0985 | 0.0027
GEN-2018-115 | 04 SOUTHEAST | 521088 | WASHITA2 | 69 | 9.083 | 9.0804 | 0.0026
GEN-2018-115 | 04 SOUTHEAST | 521103 | SLKHILLS 4 | 138 | 6.45 | 6.4481 | 0.0019
GEN-2018-115 | 04 SOUTHEAST | 521129 | CHERRYRD 4 | 138 | 5.6562 | 5.6534 | 0.0028
GEN-2018-115 | 04 SOUTHEAST | 521157 | HUGO 7 | 345 | 12.5857 | 12.5812 | 0.0045
GEN-2018-115 | 04 SOUTHEAST | 560022 | CRAWFISH_DR | 345 | 13.842 | 13.8373 | 0.0047
GEN-2018-115 | 04 SOUTHEAST | 560035 | GRAPEVINE | 345 | 6.4589 | 6.4579 | 0.001
GEN-2018-115 | 04 SOUTHEAST | 587430 | GEN-2016-063 | 345 | 8.0519 | 8.0432 | 0.0087
GEN-2018-115 | 04 SOUTHEAST | 589130 | GEN-2017-075 | 345 | 8.1486 | 8.1397 | 0.0089
GEN-2018-115 | 04 SOUTHEAST | 755000 | WWDBORDT | 345 | 12.2648 | 12.2564 | 0.0084
GEN-2018-115 | 04 SOUTHEAST | 760830 | GEN-2017-149 | 345 | 4.1868 | 4.1849 | 0.0019
GEN-2018-115 | 04 SOUTHEAST | 761229 | GEN-2017-150 | 345 | 22.4791 | 22.4222 | 0.0569
GEN-2018-115 | 04 SOUTHEAST | 761880 | GEN-2017-167 | 345 | 5.364 | 5.3557 | 0.0083
GEN-2018-115 | 04 SOUTHEAST | 762217 | GEN-2017-151 | 345 | 6.1754 | 6.1727 | 0.0027
GEN-2019-002 | 04 SOUTHEAST | 512648 | MAID 5 | 161 | 44.1007 | 43.6942 | 0.4065
GEN-2019-002 | 04 SOUTHEAST | 300069 | 5CHOTEAU1 | 161 | 40.9364 | 40.8444 | 0.092
GEN-2019-002 | 04 SOUTHEAST | 512626 | MAID 2 | 69 | 14.1535 | 14.1382 | 0.0153
GEN-2019-002 | 04 SOUTHEAST | 512629 | DRYGULCH5 | 161 | 15.4387 | 15.4003 | 0.0384
GEN-2019-002 | 04 SOUTHEAST | 512635 | KERR GR5 | 161 | 28.7757 | 28.6479 | 0.1278
GEN-2019-002 | 04 SOUTHEAST | 512638 | CATSAGR5 | 161 | 23.636 | 23.6114 | 0.0246
GEN-2019-002 | 04 SOUTHEAST | 512656 | GRDA1 5 | 161 | 43.6027 | 43.2019 | 0.4008
GEN-2019-002 | 04 SOUTHEAST | 512760 | GERALDGAY5 | 161 | 28.832 | 28.4706 | 0.3614
GEN-2019-002 | 04 SOUTHEAST | 513050 | LOCSTGVKM 5 | 161 | 13.5464 | 13.5188 | 0.0276
GEN-2019-002 | 04 SOUTHEAST | 300993 | 5ELMCRK | 161 | 13.0117 | 13.0044 | 0.0073
GEN-2019-002 | 04 SOUTHEAST | 301344 | 5CDRCRST | 161 | 10.6424 | 10.6295 | 0.0129
GEN-2019-002 | 04 SOUTHEAST | 301348 | 5CHOTEAU2 | 161 | 40.9364 | 40.8444 | 0.092
GEN-2019-002 | 04 SOUTHEAST | 509790 | CATOOSA4 | 138 | 35.596 | 35.5707 | 0.0253
GEN-2019-002 | 04 SOUTHEAST | 512637 | 412SUB 5 | 161 | 11.6499 | 11.6376 | 0.0123
GEN-2019-002 | 04 SOUTHEAST | 512650 | GRDA1 7 | 345 | 26.1397 | 26.0613 | 0.0784
GEN-2019-002 | 04 SOUTHEAST | 512651 | CLARMR 5 | 161 | 12.6416 | 12.6314 | 0.0102
GEN-2019-002 | 04 SOUTHEAST | 512654 | PENSA 5 | 161 | 12.8683 | 12.8513 | 0.017
GEN-2019-002 | 04 SOUTHEAST | 512681 | AMERCAST S2 | 69 | 12.9267 | 12.9145 | 0.0122
GEN-2019-002 | 04 SOUTHEAST | 512698 | REDDEN 2 | 69 | 10.4021 | 10.3938 | 0.0083
GEN-2019-002 | 04 SOUTHEAST | 512700 | WAGNOR 5 | 161 | 9.5186 | 9.5106 | 0.008
GEN-2019-002 | 04 SOUTHEAST | 512727 | GRDA1 2 | 69 | 12.0119 | 12.0011 | 0.0108
GEN-2019-002 | 04 SOUTHEAST | 512742 | WMAIN ST5 | 161 | 27.8967 | 27.5093 | 0.3874
GEN-2019-002 | 04 SOUTHEAST | 512757 | NWMAID5 | 161 | 27.6771 | 27.2373 | 0.4398
GEN-2019-002 | 04 SOUTHEAST | 512770 | KERR BRK1 5 | 161 | 28.7757 | 28.6479 | 0.1278
GEN-2019-002 | 04 SOUTHEAST | 512771 | KERR BRK4 5 | 161 | 28.7757 | 28.6479 | 0.1278
GEN-2019-002 | 04 SOUTHEAST | 512805 | SALNCRK5 | 161 | 18.362 | 18.3153 | 0.0467
GEN-2019-002 | 04 SOUTHEAST | 589110 | GEN-2017-073 | 161 | 14.3476 | 14.3146 | 0.033
GEN-2019-002 | 04 SOUTHEAST | 300740 | 7SPORTSMAN | 345 | 23.7932 | 23.7307 | 0.0625
GEN-2019-002 | 04 SOUTHEAST | 300741 | 5SPORTSMAN | 161 | 39.373 | 39.2891 | 0.0839
GEN-2019-002 | 04 SOUTHEAST | 300997 | 5KETONVL | 161 | 10.5277 | 10.522 | 0.0057
GEN-2019-002 | 04 SOUTHEAST | 301345 | 2CDRCRST | 69 | 8.0335 | 8.0309 | 0.0026
GEN-2019-002 | 04 SOUTHEAST | 509722 | SPNKY CK4 | 138 | 30.0381 | 30.0206 | 0.0175
GEN-2019-002 | 04 SOUTHEAST | 509752 | INOLATP4 | 138 | 9.3389 | 9.3366 | 0.0023
GEN-2019-002 | 04 SOUTHEAST | 509771 | LLAN ET4 | 138 | 24.1902 | 24.1814 | 0.0088
GEN-2019-002 | 04 SOUTHEAST | 509799 | CATOOSA2 | 69 | 10.4844 | 10.4833 | 0.0011
GEN-2019-002 | 04 SOUTHEAST | 509804 | LLANETP4 | 138 | 27.0465 | 27.0341 | 0.0124
GEN-2019-002 | 04 SOUTHEAST | 509835 | TERNITP4 | 138 | 15.8024 | 15.7984 | 0.004
GEN-2019-002 | 04 SOUTHEAST | 509841 | PCATSAT4 | 138 | 17.6843 | 17.679 | 0.0053
GEN-2019-002 | 04 SOUTHEAST | 509887 | OWAS88_4 | 138 | 16.698 | 16.6946 | 0.0034
GEN-2019-002 | 04 SOUTHEAST | 512625 | MAIDTP2 | 69 | 11.5947 | 11.5851 | 0.0096
GEN-2019-002 | 04 SOUTHEAST | 512627 | COLINS 5 | 161 | 11.8761 | 11.8701 | 0.006
GEN-2019-002 | 04 SOUTHEAST | 512628 | PENSA 2 | 69 | 13.1471 | 13.1423 | 0.0048
GEN-2019-002 | 04 SOUTHEAST | 512634 | KERR GR3 | 115 | 17.4328 | 17.4047 | 0.0281
GEN-2019-002 | 04 SOUTHEAST | 512640 | OKAYGR 5 | 161 | 9.7966 | 9.7911 | 0.0055
GEN-2019-002 | 04 SOUTHEAST | 512655 | TAHLQH 5 | 161 | 10.203 | 10.1976 | 0.0054
GEN-2019-002 | 04 SOUTHEAST | 512661 | CPPTAP 2 | 69 | 12.5809 | 12.5697 | 0.0112
GEN-2019-002 | 04 SOUTHEAST | 512669 | KETCHUM5 | 161 | 10.4025 | 10.3928 | 0.0097
GEN-2019-002 | 04 SOUTHEAST | 512679 | CLARMR 2 | 69 | 12.4028 | 12.3986 | 0.0042
GEN-2019-002 | 04 SOUTHEAST | 512683 | AMERCAST N2 | 69 | 8.1805 | 8.1754 | 0.0051
GEN-2019-002 | 04 SOUTHEAST | 512685 | CASTING TAP2 | 69 | 9.109 | 9.1026 | 0.0064
GEN-2019-002 | 04 SOUTHEAST | 512686 | SALINA 5 | 161 | 17.7259 | 17.683 | 0.0429
GEN-2019-002 | 04 SOUTHEAST | 512697 | WAGNOR 2 | 69 | 6.971 | 6.9696 | 0.0014
GEN-2019-002 | 04 SOUTHEAST | 512707 | CLARMR 4 | 138 | 13.1982 | 13.1934 | 0.0048
GEN-2019-002 | 04 SOUTHEAST | 512714 | KANSATP5 | 161 | 11.5087 | 11.5015 | 0.0072
GEN-2019-002 | 04 SOUTHEAST | 512750 | TONECE7 | 345 | 14.9626 | 14.953 | 0.0096
GEN-2019-002 | 04 SOUTHEAST | 512865 | GREC TAP5 | 345 | 24.9713 | 24.9034 | 0.0679
GEN-2019-002 | 04 SOUTHEAST | 588990 | GEN-2017-061 | 161 | 22.34 | 22.0925 | 0.2475
GEN-2019-002 | 04 SOUTHEAST | 763472 | GEN-2019-002 | 161 | 26.4056 | 25.9657 | 0.4399
GEN-2019-002 | 04 SOUTHEAST | 300739 | 7BLACKBERRY | 345 | 15.3686 | 15.3662 | 0.0024
GEN-2019-002 | 04 SOUTHEAST | 300960 | 2LOWERY | 69 | 4.7097 | 4.7089 | 0.0008
GEN-2019-002 | 04 SOUTHEAST | 300962 | 2PEGGS | 69 | 6.0889 | 6.0875 | 0.0014
GEN-2019-002 | 04 SOUTHEAST | 300972 | 2WAGNERW | 69 | 4.4944 | 4.4938 | 0.0006
GEN-2019-002 | 04 SOUTHEAST | 301307 | 5PARK | 161 | 9.0708 | 9.0665 | 0.0043
GEN-2019-002 | 04 SOUTHEAST | 301451 | 2GRAY TP | 69 | 7.4599 | 7.4585 | 0.0014
GEN-2019-002 | 04 SOUTHEAST | 505560 | FT GIB 5 | 161 | 10.4701 | 10.4657 | 0.0044
GEN-2019-002 | 04 SOUTHEAST | 506935 | FLINTCR7 | 345 | 15.1826 | 15.1737 | 0.0089
GEN-2019-002 | 04 SOUTHEAST | 509723 | TER-NIT4 | 138 | 13.052 | 13.0493 | 0.0027
GEN-2019-002 | 04 SOUTHEAST | 509728 | LLANE-E4 | 138 | 19.6964 | 19.6905 | 0.0059
GEN-2019-002 | 04 SOUTHEAST | 509736 | INOLA 4 | 138 | 7.9472 | 7.9456 | 0.0016
GEN-2019-002 | 04 SOUTHEAST | 509770 | LLAN WT4 | 138 | 24.2192 | 24.2093 | 0.0099
GEN-2019-002 | 04 SOUTHEAST | 509786 | BA.N-ST4 | 138 | 23.7819 | 23.778 | 0.0039
GEN-2019-002 | 04 SOUTHEAST | 509794 | BCIRCLE2 | 69 | 9.174 | 9.1732 | 0.0008
GEN-2019-002 | 04 SOUTHEAST | 509839 | CDC-ET 4 | 138 | 18.7951 | 18.7914 | 0.0037
GEN-2019-002 | 04 SOUTHEAST | 509843 | OWASO2_4 | 138 | 13.9063 | 13.9036 | 0.0027
GEN-2019-002 | 04 SOUTHEAST | 509854 | VERDIGS4 | 138 | 13.5838 | 13.5813 | 0.0025
GEN-2019-002 | 04 SOUTHEAST | 509886 | E41ST_W4 | 138 | 21.4099 | 21.4053 | 0.0046
GEN-2019-002 | 04 SOUTHEAST | 509892 | 141PINE4 | 138 | 20.2247 | 20.2178 | 0.0069
GEN-2019-002 | 04 SOUTHEAST | 509899 | BIRDCREE-4 | 138 | 17.1232 | 17.1182 | 0.005
GEN-2019-002 | 04 SOUTHEAST | 510423 | L GROVE3 | 115 | 16.3622 | 16.3379 | 0.0243
GEN-2019-002 | 04 SOUTHEAST | 510437 | ROCKPT-4 | 138 | 8.2642 | 8.2623 | 0.0019
GEN-2019-002 | 04 SOUTHEAST | 512624 | CENTLFT2 | 69 | 11.1113 | 11.1079 | 0.0034
GEN-2019-002 | 04 SOUTHEAST | 512632 | AFTON 5 | 161 | 8.2035 | 8.2002 | 0.0033
GEN-2019-002 | 04 SOUTHEAST | 512642 | SILSPWW5 | 161 | 14.6147 | 14.6082 | 0.0065
GEN-2019-002 | 04 SOUTHEAST | 512646 | OKAYGR 2 | 69 | 11.7997 | 11.7964 | 0.0033
GEN-2019-002 | 04 SOUTHEAST | 512647 | TAHLQH 2 | 69 | 11.5543 | 11.5513 | 0.003
GEN-2019-002 | 04 SOUTHEAST | 512671 | HUNT 2 | 69 | 13.0395 | 13.0286 | 0.0109
GEN-2019-002 | 04 SOUTHEAST | 512690 | WAGNRTP2 | 69 | 7.0854 | 7.084 | 0.0014
GEN-2019-002 | 04 SOUTHEAST | 512692 | CLEORTP2 | 69 | 7.3304 | 7.3293 | 0.0011
GEN-2019-002 | 04 SOUTHEAST | 512695 | ADARNEO2 | 69 | 4.7473 | 4.7467 | 0.0006
GEN-2019-002 | 04 SOUTHEAST | 512699 | PRYORCHEM2 | 69 | 12.4543 | 12.4436 | 0.0107
GEN-2019-002 | 04 SOUTHEAST | 512705 | COLLINS4 | 138 | 8.3928 | 8.3908 | 0.002
GEN-2019-002 | 04 SOUTHEAST | 512716 | KANSAS 5 | 161 | 10.9317 | 10.9251 | 0.0066
GEN-2019-002 | 04 SOUTHEAST | 512751 | TONECE5 | 161 | 15.1632 | 15.1585 | 0.0047
GEN-2019-002 | 04 SOUTHEAST | 512759 | WAGCTY22 | 69 | 5.624 | 5.6231 | 0.0009
GEN-2019-002 | 04 SOUTHEAST | 512870 | COLNSGR2 | 69 | 9.8758 | 9.8745 | 0.0013
GEN-2019-002 | 04 SOUTHEAST | 513008 | CLARMTP 2 | 69 | 10.2462 | 10.2433 | 0.0029
GEN-2019-002 | 04 SOUTHEAST | 513014 | CLARCTY4 2 | 69 | 5.8208 | 5.8199 | 0.0009
GEN-2019-002 | 04 SOUTHEAST | 513044 | BRIGSKM 5 | 161 | 8.3071 | 8.3036 | 0.0035
GEN-2019-002 | 04 SOUTHEAST | 513124 | OOLOGAHKM 4 | 138 | 20.2302 | 20.2252 | 0.005
GEN-2019-002 | 04 SOUTHEAST | 513129 | SEQUOYAKM 2 | 69 | 6.7921 | 6.7909 | 0.0012
GEN-2019-002 | 04 SOUTHEAST | 513596 | IGLOOV 7 | 345 | 19.8028 | 19.765 | 0.0378
GEN-2019-002 | 04 SOUTHEAST | 515527 | HWY59TP5 | 161 | 15.6539 | 15.6531 | 0.0008
GEN-2019-002 | 04 SOUTHEAST | 515956 | 7CLANS 5 | 161 | 9.7494 | 9.7448 | 0.0046
GEN-2019-002 | 04 SOUTHEAST | 300146 | 4SKIAETP | 138 | 6.9025 | 6.9015 | 0.001
GEN-2019-002 | 04 SOUTHEAST | 300767 | 5BRIGGS | 161 | 7.2194 | 7.2167 | 0.0027
GEN-2019-002 | 04 SOUTHEAST | 300949 | 7JASPER | 345 | 12.5964 | 12.5951 | 0.0013
GEN-2019-002 | 04 SOUTHEAST | 300955 | 2COWETA | 69 | 2.4215 | 2.4214 | 0.0001
GEN-2019-002 | 04 SOUTHEAST | 300968 | 2SLEEPYH | 69 | 4.7973 | 4.7966 | 0.0007
GEN-2019-002 | 04 SOUTHEAST | 300973 | 2WHITETP | 69 | 6.4362 | 6.435 | 0.0012
GEN-2019-002 | 04 SOUTHEAST | 300975 | 2HULBERT | 69 | 6.3656 | 6.3645 | 0.0011
GEN-2019-002 | 04 SOUTHEAST | 300992 | 2COLINS | 69 | 9.8756 | 9.8744 | 0.0012
GEN-2019-002 | 04 SOUTHEAST | 300998 | 2OWASSO | 69 | 6.6248 | 6.6243 | 0.0005
GEN-2019-002 | 04 SOUTHEAST | 301006 | 2VERA | 69 | 6.1079 | 6.1075 | 0.0004
GEN-2019-002 | 04 SOUTHEAST | 301452 | 2GRAY | 69 | 6.103 | 6.1021 | 0.0009
GEN-2019-002 | 04 SOUTHEAST | 301453 | 2ZENA TP | 69 | 5.7059 | 5.7052 | 0.0007
GEN-2019-002 | 04 SOUTHEAST | 301460 | 2CLEORA | 69 | 3.8188 | 3.8185 | 0.0003
GEN-2019-002 | 04 SOUTHEAST | 301472 | 2PARK | 69 | 8.8632 | 8.8615 | 0.0017
GEN-2019-002 | 04 SOUTHEAST | 504191 | HWY59 5 | 161 | 15.4586 | 15.4579 | 0.0007
GEN-2019-002 | 04 SOUTHEAST | 505558 | MUSKTAP5 | 161 | 14.0217 | 14.0173 | 0.0044
GEN-2019-002 | 04 SOUTHEAST | 506934 | FLINTCR5 | 161 | 33.2983 | 33.2842 | 0.0141
GEN-2019-002 | 04 SOUTHEAST | 506979 | SHIPERD7 | 345 | 10.1603 | 10.1565 | 0.0038
GEN-2019-002 | 04 SOUTHEAST | 509714 | CIP 4 | 138 | 13.4775 | 13.4756 | 0.0019
GEN-2019-002 | 04 SOUTHEAST | 509720 | LLANE-W4 | 138 | 19.6106 | 19.6041 | 0.0065
GEN-2019-002 | 04 SOUTHEAST | 509721 | BA.NO-S4 | 138 | 12.1529 | 12.1519 | 0.001
GEN-2019-002 | 04 SOUTHEAST | 509725 | PCATOSA4 | 138 | 11.2904 | 11.2882 | 0.0022
GEN-2019-002 | 04 SOUTHEAST | 509779 | MAYO--N4 | 138 | 23.2794 | 23.2756 | 0.0038
GEN-2019-002 | 04 SOUTHEAST | 509787 | DAWSN-N4 | 138 | 17.5355 | 17.5309 | 0.0046
GEN-2019-002 | 04 SOUTHEAST | 509791 | DAWSON-2 | 69 | 10.0381 | 10.0371 | 0.001
GEN-2019-002 | 04 SOUTHEAST | 509803 | DAWSONT4 | 138 | 12.0609 | 12.0584 | 0.0025
GEN-2019-002 | 04 SOUTHEAST | 509806 | ONETA--4 | 138 | 49.9736 | 49.966 | 0.0076
GEN-2019-002 | 04 SOUTHEAST | 509817 | T.NO.--4 | 138 | 35.4016 | 35.3918 | 0.0098
GEN-2019-002 | 04 SOUTHEAST | 509852 | T.NO.--7 | 345 | 24.108 | 24.0994 | 0.0086
GEN-2019-002 | 04 SOUTHEAST | 509864 | CLARTOK4 | 138 | 13.5787 | 13.5763 | 0.0024
GEN-2019-002 | 04 SOUTHEAST | 510373 | CHOUTEA4 | 138 | 6.9231 | 6.9213 | 0.0018
GEN-2019-002 | 04 SOUTHEAST | 510396 | N.E.S.-4 | 138 | 34.7002 | 34.6913 | 0.0089
GEN-2019-002 | 04 SOUTHEAST | 510399 | LSTAR--3 | 115 | 10.7106 | 10.7019 | 0.0087
GEN-2019-002 | 04 SOUTHEAST | 510416 | HUNTAP-2 | 69 | 8.8102 | 8.8059 | 0.0043
GEN-2019-002 | 04 SOUTHEAST | 512631 | MIAMI 5 | 161 | 9.2537 | 9.2517 | 0.002
GEN-2019-002 | 04 SOUTHEAST | 512633 | AFTON 2 | 69 | 10.1803 | 10.1787 | 0.0016
GEN-2019-002 | 04 SOUTHEAST | 512639 | PRY0RC22 | 69 | 9.715 | 9.7096 | 0.0054
GEN-2019-002 | 04 SOUTHEAST | 512643 | SILMCTY5 | 161 | 19.7192 | 19.7109 | 0.0083
GEN-2019-002 | 04 SOUTHEAST | 512687 | AIRPROD2 | 69 | 12.4747 | 12.4642 | 0.0105
GEN-2019-002 | 04 SOUTHEAST | 512696 | PARKER 2 | 69 | 4.4214 | 4.4209 | 0.0005
GEN-2019-002 | 04 SOUTHEAST | 512703 | PARKMEDTP | 69 | 5.6844 | 5.6841 | 0.0003
GEN-2019-002 | 04 SOUTHEAST | 512704 | STIWEL5 | 161 | 4.7476 | 4.7465 | 0.0011
GEN-2019-002 | 04 SOUTHEAST | 512715 | KANSAS 2 | 69 | 6.282 | 6.2812 | 0.0008
GEN-2019-002 | 04 SOUTHEAST | 512725 | CHELSGR2 | 69 | 4.4668 | 4.4662 | 0.0006
GEN-2019-002 | 04 SOUTHEAST | 512753 | TONNEC2 | 69 | 5.4668 | 5.4666 | 0.0002
GEN-2019-002 | 04 SOUTHEAST | 512801 | WAGCTY12 | 69 | 5.2733 | 5.2725 | 0.0008
GEN-2019-002 | 04 SOUTHEAST | 512804 | RDFRNTP2 | 69 | 9.0109 | 9.0091 | 0.0018
GEN-2019-002 | 04 SOUTHEAST | 512812 | ARMIN 2 | 69 | 10.7174 | 10.71 | 0.0074
GEN-2019-002 | 04 SOUTHEAST | 512822 | TAH22CT2 | 69 | 10.2153 | 10.2129 | 0.0024
GEN-2019-002 | 04 SOUTHEAST | 512828 | UNARCO 2 | 69 | 7.1042 | 7.1028 | 0.0014
GEN-2019-002 | 04 SOUTHEAST | 513010 | CLARCTY1 2 | 69 | 5.1786 | 5.1778 | 0.0008
GEN-2019-002 | 04 SOUTHEAST | 513012 | CLARCTY2 2 | 69 | 8.7422 | 8.7401 | 0.0021
GEN-2019-002 | 04 SOUTHEAST | 513041 | TITANKM 2 | 69 | 6.2024 | 6.2017 | 0.0007
GEN-2019-002 | 04 SOUTHEAST | 513053 | FTGIBKM 2 | 69 | 7.8897 | 7.8882 | 0.0015
GEN-2019-002 | 04 SOUTHEAST | 513065 | SWAGONERKM 2 | 69 | 7.5269 | 7.5254 | 0.0015
GEN-2019-002 | 04 SOUTHEAST | 513074 | MUSKSWKM 2 | 69 | 5.985 | 5.9846 | 0.0004
GEN-2019-002 | 04 SOUTHEAST | 513593 | IGLOOV1 5 | 161 | 16.7122 | 16.6996 | 0.0126
GEN-2019-002 | 04 SOUTHEAST | 513595 | IGLOOV2 5 | 161 | 16.7122 | 16.6996 | 0.0126
GEN-2019-002 | 04 SOUTHEAST | 515339 | VBI 5 | 161 | 18.3371 | 18.3362 | 0.0009
GEN-2019-002 | 04 SOUTHEAST | 516027 | KETOWAH5 | 161 | 12.5146 | 12.5112 | 0.0034
GEN-2019-002 | 04 SOUTHEAST | 532793 | NEOSHO 7 | 345 | 17.5726 | 17.5711 | 0.0015
GEN-2019-002 | 04 SOUTHEAST | 532797 | WOLFCRK7 | 345 | 20.9355 | 20.9352 | 0.0003
GEN-2019-002 | 04 SOUTHEAST | 549984 | BROOKLINE 7 | 345 | 11.7653 | 11.7645 | 0.0008
GEN-2019-012 | 04 SOUTHEAST | 515375 | WWRDEHV7 | 345 | 22.3641 | 22.006 | 0.3581
GEN-2019-012 | 04 SOUTHEAST | 515376 | WWRDEHV4 | 138 | 24.8769 | 24.7529 | 0.124
GEN-2019-012 | 04 SOUTHEAST | 515407 | TATONGA7 | 345 | 17.5658 | 17.4833 | 0.0825
GEN-2019-012 | 04 SOUTHEAST | 515554 | BVRCNTY7 | 345 | 15.3093 | 15.2434 | 0.0659
GEN-2019-012 | 04 SOUTHEAST | 515599 | G07621119-20 | 345 | 13.4849 | 13.3615 | 0.1234
GEN-2019-012 | 04 SOUTHEAST | 515852 | DGRASSE7 | 345 | 15.3179 | 15.2462 | 0.0717
GEN-2019-012 | 04 SOUTHEAST | 515961 | GUTHRIE7 | 345 | 12.8816 | 12.7619 | 0.1197
GEN-2019-012 | 04 SOUTHEAST | 516106 | BOBCAT 7 | 345 | 15.796 | 15.661 | 0.135
GEN-2019-012 | 04 SOUTHEAST | 755000 | WWDBORDT | 345 | 12.2648 | 12.2481 | 0.0167
GEN-2019-012 | 04 SOUTHEAST | 763527 | GEN-2019-012 | 345 | 19.3711 | 19.0123 | 0.3588
GEN-2019-012 | 04 SOUTHEAST | 511553 | CHISHOLM7 | 345 | 12.3397 | 12.3233 | 0.0164
GEN-2019-012 | 04 SOUTHEAST | 514785 | WOODWRD4 | 138 | 13.1123 | 13.0955 | 0.0168
GEN-2019-012 | 04 SOUTHEAST | 514796 | IODINE-4 | 138 | 7.3201 | 7.3134 | 0.0067
GEN-2019-012 | 04 SOUTHEAST | 515394 | KEENAN 4 | 138 | 8.9414 | 8.9271 | 0.0143
GEN-2019-012 | 04 SOUTHEAST | 515398 | OUSPRT 4 | 138 | 9.528 | 9.5109 | 0.0171
GEN-2019-012 | 04 SOUTHEAST | 515425 | WWDPST 4 | 138 | 17.7977 | 17.7446 | 0.0531
GEN-2019-012 | 04 SOUTHEAST | 515448 | CRSRDSW7 | 345 | 12.1468 | 12.1083 | 0.0385
GEN-2019-012 | 04 SOUTHEAST | 515458 | BORDER 7 | 345 | 8.2517 | 8.2452 | 0.0065
GEN-2019-012 | 04 SOUTHEAST | 515497 | MATHWSN7 | 345 | 32.7952 | 32.7615 | 0.0337
GEN-2019-012 | 04 SOUTHEAST | 515582 | SLNGWND7 | 345 | 8.4766 | 8.4586 | 0.018
GEN-2019-012 | 04 SOUTHEAST | 515585 | MAMTHPW7 | 345 | 13.5669 | 13.5183 | 0.0486
GEN-2019-012 | 04 SOUTHEAST | 515590 | PALDR2W7 | 345 | 12.8669 | 12.8209 | 0.046
GEN-2019-012 | 04 SOUTHEAST | 515618 | BALKOW 7 | 345 | 12.5807 | 12.5368 | 0.0439
GEN-2019-012 | 04 SOUTHEAST | 515677 | BADGER 7 | 345 | 13.7821 | 13.7177 | 0.0644
GEN-2019-012 | 04 SOUTHEAST | 515825 | GRTWSRN7 | 345 | 9.0702 | 9.0107 | 0.0595
GEN-2019-012 | 04 SOUTHEAST | 515853 | DGRASSE4 | 138 | 17.0745 | 17.0553 | 0.0192
GEN-2019-012 | 04 SOUTHEAST | 515951 | PERSIMN7 | 345 | 11.0796 | 10.9909 | 0.0887
GEN-2019-012 | 04 SOUTHEAST | 516146 | 25MILE 7 | 345 | 11.1221 | 11.0602 | 0.0619
GEN-2019-012 | 04 SOUTHEAST | 523097 | HITCHLAND 7 | 345 | 14.9713 | 14.9342 | 0.0371
GEN-2019-012 | 04 SOUTHEAST | 539801 | THISTLE7 | 345 | 16.6662 | 16.6408 | 0.0254
GEN-2019-012 | 04 SOUTHEAST | 585410 | GREAT_WESTRN | 345 | 9.7415 | 9.6795 | 0.062
GEN-2019-012 | 04 SOUTHEAST | 585430 | PRSIMN_CRK1 | 345 | 11.7445 | 11.6514 | 0.0931
GEN-2019-012 | 04 SOUTHEAST | 588560 | GEN-2017-011 | 345 | 12.6206 | 12.5342 | 0.0864
GEN-2019-012 | 04 SOUTHEAST | 511557 | CHISHOLM6 | 230 | 12.1566 | 12.1494 | 0.0072
GEN-2019-012 | 04 SOUTHEAST | 514782 | WODWRD 2 | 69 | 10.8998 | 10.8956 | 0.0042
GEN-2019-012 | 04 SOUTHEAST | 514795 | KNOBHIL4 | 138 | 10.2855 | 10.2798 | 0.0057
GEN-2019-012 | 04 SOUTHEAST | 514880 | NORTWST7 | 345 | 32.9086 | 32.8911 | 0.0175
GEN-2019-012 | 04 SOUTHEAST | 514901 | CIMARON7 | 345 | 34.2931 | 34.2704 | 0.0227
GEN-2019-012 | 04 SOUTHEAST | 515363 | CENT 4 | 138 | 3.0872 | 3.0865 | 0.0007
GEN-2019-012 | 04 SOUTHEAST | 515533 | REDCLFT4 | 138 | 6.6178 | 6.6135 | 0.0043
GEN-2019-012 | 04 SOUTHEAST | 515634 | PALDR1W7 | 345 | 10.943 | 10.9102 | 0.0328
GEN-2019-012 | 04 SOUTHEAST | 515686 | BLUWND 7 | 345 | 12.3633 | 12.3117 | 0.0516
GEN-2019-012 | 04 SOUTHEAST | 515785 | WINDFRM4 | 138 | 19.5945 | 19.5844 | 0.0101
GEN-2019-012 | 04 SOUTHEAST | 515875 | REDNGTN7 | 345 | 16.7149 | 16.7097 | 0.0052
GEN-2019-012 | 04 SOUTHEAST | 516159 | 25MILZ 7 | 345 | 11.1104 | 11.0487 | 0.0617
GEN-2019-012 | 04 SOUTHEAST | 520436 | ROSEVLY4 | 138 | 12.3574 | 12.3478 | 0.0096
GEN-2019-012 | 04 SOUTHEAST | 520999 | MOORLND4 | 138 | 20.0616 | 20.0513 | 0.0103
GEN-2019-012 | 04 SOUTHEAST | 523095 | HITCHLAND 6 | 230 | 14.5761 | 14.5583 | 0.0178
GEN-2019-012 | 04 SOUTHEAST | 523101 | NOBLE_WND 7 | 345 | 14.9103 | 14.8735 | 0.0368
GEN-2019-012 | 04 SOUTHEAST | 523112 | NOVUS1 7 | 345 | 14.6716 | 14.636 | 0.0356
GEN-2019-012 | 04 SOUTHEAST | 523823 | CARPENTER 7 | 345 | 6.5781 | 6.5749 | 0.0032
GEN-2019-012 | 04 SOUTHEAST | 523961 | POTTER_CO 7 | 345 | 11.6631 | 11.6586 | 0.0045
GEN-2019-012 | 04 SOUTHEAST | 532782 | BUFFALO7 | 345 | 20.7555 | 20.7476 | 0.0079
GEN-2019-012 | 04 SOUTHEAST | 539800 | CLARKCOUNTY7 | 345 | 12.7785 | 12.7738 | 0.0047
GEN-2019-012 | 04 SOUTHEAST | 539804 | THISTLE4 | 138 | 17.5567 | 17.5479 | 0.0088
GEN-2019-012 | 04 SOUTHEAST | 560022 | CRAWFISH_DR | 345 | 13.842 | 13.8415 | 0.0005
GEN-2019-012 | 04 SOUTHEAST | 560035 | GRAPEVINE | 345 | 6.4589 | 6.4562 | 0.0027
GEN-2019-012 | 04 SOUTHEAST | 560078 | G16-037-TAP | 345 | 10.1427 | 10.1378 | 0.0049
GEN-2019-012 | 04 SOUTHEAST | 576397 | G10014G11022 | 345 | 10.3812 | 10.3648 | 0.0164
GEN-2019-012 | 04 SOUTHEAST | 585190 | GEN-2015-082 | 345 | 7.0512 | 7.0352 | 0.016
GEN-2019-012 | 04 SOUTHEAST | 585300 | GEN-2015-095 | 138 | 16.8692 | 16.8505 | 0.0187
GEN-2019-012 | 04 SOUTHEAST | 585420 | COWBOY_RIDGE | 345 | 7.5551 | 7.5194 | 0.0357
GEN-2019-012 | 04 SOUTHEAST | 585440 | PRSIMN_CRK2 | 345 | 10.7138 | 10.6367 | 0.0771
GEN-2019-012 | 04 SOUTHEAST | 588630 | GEN-2017-018 | 345 | 16.6662 | 16.6408 | 0.0254
GEN-2019-012 | 04 SOUTHEAST | 762834 | GEN-2018-049 | 345 | 6.9567 | 6.9524 | 0.0043
GEN-2019-012 | 04 SOUTHEAST | 763769 | GEN-2019-045 | 138 | 17.0745 | 17.0553 | 0.0192
GEN-2019-012 | 04 SOUTHEAST | 900001 | TRAVERSE3 | 345 | 6.9271 | 6.9261 | 0.001
GEN-2019-012 | 04 SOUTHEAST | 511490 | ELKCITY6 | 230 | 7.3607 | 7.3588 | 0.0019
GEN-2019-012 | 04 SOUTHEAST | 511541 | SWEETWT6 | 230 | 8.8366 | 8.8337 | 0.0029
GEN-2019-012 | 04 SOUTHEAST | 514715 | WOODRNG7 | 345 | 18.7369 | 18.7333 | 0.0036
GEN-2019-012 | 04 SOUTHEAST | 514776 | NEWGRTP2 | 69 | 5.4519 | 5.4509 | 0.001
GEN-2019-012 | 04 SOUTHEAST | 514781 | CEDARAV2 | 69 | 5.6927 | 5.6916 | 0.0011
GEN-2019-012 | 04 SOUTHEAST | 514787 | DEWEY 4 | 138 | 7.3672 | 7.3644 | 0.0028
GEN-2019-012 | 04 SOUTHEAST | 514788 | GLASMTN4 | 138 | 5.1117 | 5.1112 | 0.0005
GEN-2019-012 | 04 SOUTHEAST | 514794 | KNOBHIL2 | 69 | 8.8727 | 8.8711 | 0.0016
GEN-2019-012 | 04 SOUTHEAST | 514801 | MINCO 7 | 345 | 23.2915 | 23.2848 | 0.0067
GEN-2019-012 | 04 SOUTHEAST | 514879 | NORTWST4 | 138 | 44.7892 | 44.7798 | 0.0094
GEN-2019-012 | 04 SOUTHEAST | 514881 | SPRNGCK7 | 345 | 23.3445 | 23.3376 | 0.0069
GEN-2019-012 | 04 SOUTHEAST | 514898 | CIMARON4 | 138 | 45.5365 | 45.5266 | 0.0099
GEN-2019-012 | 04 SOUTHEAST | 514908 | ARCADIA7 | 345 | 28.6269 | 28.6235 | 0.0034
GEN-2019-012 | 04 SOUTHEAST | 515610 | FSHRTAP7 | 345 | 16.0539 | 16.0493 | 0.0046
GEN-2019-012 | 04 SOUTHEAST | 515786 | FPLWIND4 | 138 | 6.1883 | 6.1873 | 0.001
GEN-2019-012 | 04 SOUTHEAST | 515800 | GRACMNT7 | 345 | 20.5087 | 20.5037 | 0.005
GEN-2019-012 | 04 SOUTHEAST | 515863 | REDCLF 4 | 138 | 6.6037 | 6.5994 | 0.0043
GEN-2019-012 | 04 SOUTHEAST | 515877 | REDDIRT7 | 345 | 16.7106 | 16.7054 | 0.0052
GEN-2019-012 | 04 SOUTHEAST | 520425 | PIC4 | 138 | 7.9856 | 7.9843 | 0.0013
GEN-2019-012 | 04 SOUTHEAST | 520430 | NOELSW 4 | 138 | 10.3556 | 10.3498 | 0.0058
GEN-2019-012 | 04 SOUTHEAST | 520462 | ASPEN 4 | 138 | 19.3561 | 19.3465 | 0.0096
GEN-2019-012 | 04 SOUTHEAST | 520553 | SEILING4 | 138 | 6.6101 | 6.6082 | 0.0019
GEN-2019-012 | 04 SOUTHEAST | 520601 | AVARD 4 | 138 | 6.857 | 6.8541 | 0.0029
GEN-2019-012 | 04 SOUTHEAST | 520957 | IODINE 4 | 138 | 7.673 | 7.6716 | 0.0014
GEN-2019-012 | 04 SOUTHEAST | 520995 | MOORLND2 | 69 | 8.5299 | 8.5286 | 0.0013
GEN-2019-012 | 04 SOUTHEAST | 521096 | WOODWRD2 | 69 | 9.8637 | 9.861 | 0.0027
GEN-2019-012 | 04 SOUTHEAST | 523093 | HITCHLAND 3 | 115 | 17.3358 | 17.3274 | 0.0084
GEN-2019-012 | 04 SOUTHEAST | 523103 | NOBLE_WND 3 | 115 | 10.6199 | 10.6148 | 0.0051
GEN-2019-012 | 04 SOUTHEAST | 523111 | NOVUS1 3 | 115 | 7.8432 | 7.8407 | 0.0025
GEN-2019-012 | 04 SOUTHEAST | 523155 | OCHILTREE 6 | 230 | 4.265 | 4.2637 | 0.0013
GEN-2019-012 | 04 SOUTHEAST | 523215 | GEN-2011-022 | 345 | 10.3812 | 10.3648 | 0.0164
GEN-2019-012 | 04 SOUTHEAST | 523309 | MOORE_CNTY 6 | 230 | 6.6813 | 6.6801 | 0.0012
GEN-2019-012 | 04 SOUTHEAST | 523853 | FINNEY 7 | 345 | 9.8362 | 9.8346 | 0.0016
GEN-2019-012 | 04 SOUTHEAST | 523959 | POTTER_CO 6 | 230 | 22.4376 | 22.4335 | 0.0041
GEN-2019-012 | 04 SOUTHEAST | 524296 | SPNSPUR_WND7 | 345 | 5.3278 | 5.327 | 0.0008
GEN-2019-012 | 04 SOUTHEAST | 525549 | TOLK 7 | 345 | 15.0276 | 15.0271 | 0.0005
GEN-2019-012 | 04 SOUTHEAST | 525832 | TUCO_INT 7 | 345 | 14.0745 | 14.074 | 0.0005
GEN-2019-012 | 04 SOUTHEAST | 531469 | SPERVIL7 | 345 | 13.6098 | 13.6066 | 0.0032
GEN-2019-012 | 04 SOUTHEAST | 531512 | HARBNGR7 | 345 | 6.5579 | 6.5548 | 0.0031
GEN-2019-012 | 04 SOUTHEAST | 532783 | KINGMAN7 | 345 | 7.0277 | 7.027 | 0.0007
GEN-2019-012 | 04 SOUTHEAST | 532796 | WICHITA7 | 345 | 23.7708 | 23.7637 | 0.0071
GEN-2019-012 | 04 SOUTHEAST | 539638 | FLATRDG4 | 138 | 15.5636 | 15.5573 | 0.0063
GEN-2019-012 | 04 SOUTHEAST | 539813 | TRANSFORMER | 345 | 10.6791 | 10.6759 | 0.0032
GEN-2019-012 | 04 SOUTHEAST | 539840 | GEN-2011-008 | 345 | 10.5555 | 10.5524 | 0.0031
GEN-2019-012 | 04 SOUTHEAST | 555234 | NSUB345 | 345 | 27.0301 | 27.0241 | 0.006
GEN-2019-012 | 04 SOUTHEAST | 560080 | G16-046-TAP | 345 | 11.3684 | 11.3654 | 0.003
GEN-2019-012 | 04 SOUTHEAST | 560577 | G06-44 | 115 | 7.5797 | 7.5773 | 0.0024
GEN-2019-012 | 04 SOUTHEAST | 576395 | GEN-2010-014 | 345 | 10.3812 | 10.3648 | 0.0164
GEN-2019-012 | 04 SOUTHEAST | 587140 | GEN-2016-020 | 138 | 7.4213 | 7.42 | 0.0013
GEN-2019-012 | 04 SOUTHEAST | 587230 | GEN-2016-037 | 345 | 9.6646 | 9.6601 | 0.0045
GEN-2019-012 | 04 SOUTHEAST | 587500 | GEN-2016-073 | 345 | 15.2224 | 15.2182 | 0.0042
GEN-2019-012 | 04 SOUTHEAST | 760284 | GEN-2017-220 | 345 | 20.642 | 20.6342 | 0.0078
GEN-2019-012 | 04 SOUTHEAST | 762216 | G17-151TAP | 345 | 8.5119 | 8.5117 | 0.0002
GEN-2019-012 | 04 SOUTHEAST | 763087 | GEN-2018-073 | 345 | 11.9423 | 11.9419 | 0.0004
GEN-2019-012 | 04 SOUTHEAST | 763890 | GEN-2019-058 | 345 | 12.52 | 12.5156 | 0.0044
GEN-2019-012 | 04 SOUTHEAST | 900004 | TRW2-TRW3 | 345 | 6.2021 | 6.2014 | 0.0007
GEN-2019-012 | 04 SOUTHEAST | 511425 | TUTCONT4 | 138 | 10.052 | 10.0517 | 0.0003
GEN-2019-012 | 04 SOUTHEAST | 511458 | ELKCTY-4 | 138 | 11.2004 | 11.1985 | 0.0019
GEN-2019-012 | 04 SOUTHEAST | 511542 | BUFFCK6 | 230 | 6.4162 | 6.4148 | 0.0014
GEN-2019-012 | 04 SOUTHEAST | 511544 | DEMPSEY6 | 230 | 5.2718 | 5.2709 | 0.0009
GEN-2019-012 | 04 SOUTHEAST | 511547 | ROARK6 | 230 | 4.785 | 4.7842 | 0.0008
GEN-2019-012 | 04 SOUTHEAST | 514714 | WOODRNG4 | 138 | 19.2315 | 19.2302 | 0.0013
GEN-2019-012 | 04 SOUTHEAST | 514773 | NEWMAN 2 | 69 | 1.546 | 1.5459 | 0.0001
GEN-2019-012 | 04 SOUTHEAST | 514775 | TANGRTP2 | 69 | 4.7749 | 4.7741 | 0.0008
GEN-2019-012 | 04 SOUTHEAST | 514778 | CLEOCOR4 | 138 | 6.333 | 6.3326 | 0.0004
GEN-2019-012 | 04 SOUTHEAST | 514779 | WDNITRO2 | 69 | 4.7628 | 4.762 | 0.0008
GEN-2019-012 | 04 SOUTHEAST | 514792 | ALVAOGE2 | 69 | 7.5035 | 7.5024 | 0.0011
GEN-2019-012 | 04 SOUTHEAST | 514819 | EL-RENO4 | 138 | 16.7698 | 16.7683 | 0.0015
GEN-2019-012 | 04 SOUTHEAST | 514820 | JENSENT4 | 138 | 18.1844 | 18.1826 | 0.0018
GEN-2019-012 | 04 SOUTHEAST | 514828 | KETCHTP4 | 138 | 26.9478 | 26.9456 | 0.0022
GEN-2019-012 | 04 SOUTHEAST | 514854 | BRADEN 4 | 138 | 31.8391 | 31.8348 | 0.0043
GEN-2019-012 | 04 SOUTHEAST | 514863 | HAYMAKR4 | 138 | 26.8465 | 26.8435 | 0.003
GEN-2019-012 | 04 SOUTHEAST | 514864 | PIEDMNT4 | 138 | 22.6006 | 22.5984 | 0.0022
GEN-2019-012 | 04 SOUTHEAST | 514873 | LNEOAK 4 | 138 | 27.2272 | 27.2241 | 0.0031
GEN-2019-012 | 04 SOUTHEAST | 514894 | CZECHAL4 | 138 | 28.8657 | 28.863 | 0.0027
GEN-2019-012 | 04 SOUTHEAST | 514895 | SARA 4 | 138 | 19.7537 | 19.7524 | 0.0013
GEN-2019-012 | 04 SOUTHEAST | 514907 | ARCADIA4 | 138 | 47.2233 | 47.2195 | 0.0038
GEN-2019-012 | 04 SOUTHEAST | 514909 | REDBUD 7 | 345 | 27.6026 | 27.5999 | 0.0027
GEN-2019-012 | 04 SOUTHEAST | 514929 | PLVALLY4 | 138 | 45.9536 | 45.9488 | 0.0048
GEN-2019-012 | 04 SOUTHEAST | 514934 | DRAPER 7 | 345 | 26.1641 | 26.16 | 0.0041
GEN-2019-012 | 04 SOUTHEAST | 515045 | SEMINOL7 | 345 | 30.8428 | 30.8407 | 0.0021
GEN-2019-012 | 04 SOUTHEAST | 515390 | TLGAWND4 | 138 | 3.592 | 3.5915 | 0.0005
GEN-2019-012 | 04 SOUTHEAST | 515444 | MCNOWND7 | 345 | 23.197 | 23.1905 | 0.0065
GEN-2019-012 | 04 SOUTHEAST | 515476 | HUNTERS7 | 345 | 13.1988 | 13.1972 | 0.0016
GEN-2019-012 | 04 SOUTHEAST | 515549 | MNCWND37 | 345 | 14.1504 | 14.1481 | 0.0023
GEN-2019-012 | 04 SOUTHEAST | 515560 | CZYCRVT2 | 69 | 3.2399 | 3.2398 | 0.0001
GEN-2019-012 | 04 SOUTHEAST | 515600 | KNGFSHR7 | 345 | 10.5637 | 10.5618 | 0.0019
GEN-2019-012 | 04 SOUTHEAST | 515605 | CANADN7 | 345 | 11.5734 | 11.5711 | 0.0023
GEN-2019-012 | 04 SOUTHEAST | 515802 | GRACMNT4 | 138 | 37.8367 | 37.833 | 0.0037
GEN-2019-012 | 04 SOUTHEAST | 515964 | CANTNLK4 | 138 | 4.7319 | 4.7311 | 0.0008
GEN-2019-012 | 04 SOUTHEAST | 515990 | SKELTON7 | 345 | 4.5043 | 4.5041 | 0.0002
GEN-2019-012 | 04 SOUTHEAST | 516010 | PINTAIL7 | 345 | 16.6869 | 16.6854 | 0.0015
GEN-2019-012 | 04 SOUTHEAST | 520437 | SALTPLN4 | 138 | 6.3315 | 6.33 | 0.0015
GEN-2019-012 | 04 SOUTHEAST | 520500 | BEARCAT4 | 138 | 14.2641 | 14.259 | 0.0051
GEN-2019-012 | 04 SOUTHEAST | 520848 | CDRDLTP4 | 138 | 5.714 | 5.7134 | 0.0006
GEN-2019-012 | 04 SOUTHEAST | 520920 | FTSUPLY4 | 138 | 5.225 | 5.2243 | 0.0007
GEN-2019-012 | 04 SOUTHEAST | 521065 | TALOGA 4 | 138 | 7.1703 | 7.1678 | 0.0025
GEN-2019-012 | 04 SOUTHEAST | 521082 | VICI 2 | 69 | 3.8314 | 3.8311 | 0.0003
GEN-2019-012 | 04 SOUTHEAST | 521196 | FARGOJCT2 | 69 | 7.5366 | 7.5352 | 0.0014
GEN-2019-012 | 04 SOUTHEAST | 521197 | CRTSJCT2 | 69 | 8.1375 | 8.1362 | 0.0013
GEN-2019-012 | 04 SOUTHEAST | 523090 | TEXAS_CNTY 3 | 115 | 8.8999 | 8.8982 | 0.0017
GEN-2019-012 | 04 SOUTHEAST | 523118 | BUFF_DUNES 7 | 345 | 6.0272 | 6.0266 | 0.0006
GEN-2019-012 | 04 SOUTHEAST | 523131 | GRPLNS-HV2-3 | 115 | 9.8132 | 9.809 | 0.0042
GEN-2019-012 | 04 SOUTHEAST | 523154 | OCHILTREE 3 | 115 | 6.3386 | 6.3376 | 0.001
GEN-2019-012 | 04 SOUTHEAST | 523160 | FRISCO_WND 3 | 115 | 6.5277 | 6.5268 | 0.0009
GEN-2019-012 | 04 SOUTHEAST | 523174 | GOODWELLWND3 | 115 | 6.653 | 6.6522 | 0.0008
GEN-2019-012 | 04 SOUTHEAST | 523195 | HANSFORD 3 | 115 | 9.5075 | 9.5055 | 0.002
GEN-2019-012 | 04 SOUTHEAST | 523308 | MOORE_E 3 | 115 | 10.3425 | 10.3415 | 0.001
GEN-2019-012 | 04 SOUTHEAST | 523323 | MCDWL_CREEK6 | 230 | 8.9802 | 8.9791 | 0.0011
GEN-2019-012 | 04 SOUTHEAST | 523779 | STLN-DEMARC6 | 230 | 8.0635 | 8.0613 | 0.0022
GEN-2019-012 | 04 SOUTHEAST | 523869 | CHAN+TASCOS6 | 230 | 4.2464 | 4.2462 | 0.0002
GEN-2019-012 | 04 SOUTHEAST | 523979 | HARRNG_EST 6 | 230 | 26.9856 | 26.9822 | 0.0034
GEN-2019-012 | 04 SOUTHEAST | 524010 | ROLLHILLS 6 | 230 | 20.2306 | 20.2282 | 0.0024
GEN-2019-012 | 04 SOUTHEAST | 524267 | BUSHLAND 6 | 230 | 10.1739 | 10.1734 | 0.0005
GEN-2019-012 | 04 SOUTHEAST | 524299 | SPNSPUR_COL7 | 345 | 5.3278 | 5.327 | 0.0008
GEN-2019-012 | 04 SOUTHEAST | 525461 | NEWHART 6 | 230 | 10.9971 | 10.9969 | 0.0002
GEN-2019-012 | 04 SOUTHEAST | 525531 | TOLK 6 | 230 | 31.4946 | 31.4938 | 0.0008
GEN-2019-012 | 04 SOUTHEAST | 525830 | TUCO_INT 6 | 230 | 21.9895 | 21.989 | 0.0005
GEN-2019-012 | 04 SOUTHEAST | 525850 | ELK_CT1 | 345 | 13.9398 | 13.9392 | 0.0006
GEN-2019-012 | 04 SOUTHEAST | 526936 | YOAKUM_345 | 345 | 9.9314 | 9.9314 | 0
GEN-2019-012 | 04 SOUTHEAST | 527656 | CROSSROADS 7 | 345 | 11.539 | 11.5389 | 0.0001
GEN-2019-012 | 04 SOUTHEAST | 530583 | POSTROCK7 | 345 | 7.7231 | 7.7227 | 0.0004
GEN-2019-012 | 04 SOUTHEAST | 531449 | HOLCOMB7 | 345 | 9.9438 | 9.9422 | 0.0016
GEN-2019-012 | 04 SOUTHEAST | 531501 | BUCKNER7 | 345 | 9.2456 | 9.2442 | 0.0014
GEN-2019-012 | 04 SOUTHEAST | 531510 | HARBNGR3 | 115 | 10.6191 | 10.617 | 0.0021
GEN-2019-012 | 04 SOUTHEAST | 532771 | RENO 7 | 345 | 11.0976 | 11.0968 | 0.0008
GEN-2019-012 | 04 SOUTHEAST | 532784 | NINN1WF7 | 345 | 5.8368 | 5.8364 | 0.0004
GEN-2019-012 | 04 SOUTHEAST | 532791 | BENTON 7 | 345 | 19.0077 | 19.0055 | 0.0022
GEN-2019-012 | 04 SOUTHEAST | 532798 | VIOLA 7 | 345 | 14.0837 | 14.0818 | 0.0019
GEN-2019-012 | 04 SOUTHEAST | 533040 | EVANS N4 | 138 | 32.3573 | 32.3538 | 0.0035
GEN-2019-012 | 04 SOUTHEAST | 539631 | FLATRWD4 | 138 | 10.3815 | 10.3787 | 0.0028
GEN-2019-012 | 04 SOUTHEAST | 539668 | HARPER 4 | 138 | 7.2122 | 7.2116 | 0.0006
GEN-2019-012 | 04 SOUTHEAST | 539674 | BARBER 4 | 138 | 8.2322 | 8.2307 | 0.0015
GEN-2019-012 | 04 SOUTHEAST | 539695 | SPEARVL6 | 230 | 12.772 | 12.7705 | 0.0015
GEN-2019-012 | 04 SOUTHEAST | 539759 | SPRVL 3 | 115 | 12.8273 | 12.8264 | 0.0009
GEN-2019-012 | 04 SOUTHEAST | 539803 | IRONWOOD7 | 345 | 13.1638 | 13.1607 | 0.0031
GEN-2019-012 | 04 SOUTHEAST | 539841 | G-2011-008-1 | 345 | 10.5555 | 10.5524 | 0.0031
GEN-2019-012 | 04 SOUTHEAST | 539855 | G-2011-008-2 | 345 | 8.8342 | 8.8321 | 0.0021
GEN-2019-012 | 04 SOUTHEAST | 539857 | G-2011-008-3 | 345 | 8.2708 | 8.269 | 0.0018
GEN-2019-012 | 04 SOUTHEAST | 562476 | G14-001-TAP | 345 | 10.3737 | 10.373 | 0.0007
GEN-2019-012 | 04 SOUTHEAST | 563269 | GEN-2015-093 | 345 | 10.8212 | 10.8199 | 0.0013
GEN-2019-012 | 04 SOUTHEAST | 587310 | GEN-2016-046 | 345 | 9.9533 | 9.9511 | 0.0022
GEN-2019-012 | 04 SOUTHEAST | 587744 | G16-091-TAP | 345 | 16.3944 | 16.392 | 0.0024
GEN-2019-012 | 04 SOUTHEAST | 587804 | G16-119-TAP | 345 | 15.2197 | 15.2184 | 0.0013
GEN-2019-012 | 04 SOUTHEAST | 760032 | GEN-2017-132 | 345 | 6.7839 | 6.7838 | 0.0001
GEN-2019-012 | 04 SOUTHEAST | 761250 | GEN-2017-233 | 345 | 22.5233 | 22.5171 | 0.0062
GEN-2019-012 | 04 SOUTHEAST | 762217 | GEN-2017-151 | 345 | 6.1754 | 6.1753 | 0.0001
GEN-2019-012 | 04 SOUTHEAST | 762321 | GEN-2017-164 | 345 | 11.1781 | 11.1769 | 0.0012
GEN-2019-012 | 04 SOUTHEAST | 762467 | G18-015-TAP | 345 | 5.8242 | 5.8242 | 0
GEN-2019-012 | 04 SOUTHEAST | 762662 | G18-030-TAP | 345 | 5.8775 | 5.877 | 0.0005
GEN-2019-012 | 04 SOUTHEAST | 900002 | TRAVERSE-2 | 345 | 5.5654 | 5.5649 | 0.0005
GEN-2019-013 | 04 SOUTHEAST | 511544 | DEMPSEY6 | 230 | 5.2718 | 5.0806 | 0.1912
GEN-2019-013 | 04 SOUTHEAST | 511541 | SWEETWT6 | 230 | 8.8366 | 8.6581 | 0.1785
GEN-2019-013 | 04 SOUTHEAST | 763538 | GEN-2019-013 | 230 | 3.6769 | 3.4826 | 0.1943
GEN-2019-013 | 04 SOUTHEAST | 511542 | BUFFCK6 | 230 | 6.4162 | 6.3241 | 0.0921
GEN-2019-013 | 04 SOUTHEAST | 511547 | ROARK6 | 230 | 4.785 | 4.7355 | 0.0495
GEN-2019-013 | 04 SOUTHEAST | 511557 | CHISHOLM6 | 230 | 12.1566 | 12.0307 | 0.1259
GEN-2019-013 | 04 SOUTHEAST | 523779 | STLN-DEMARC6 | 230 | 8.0635 | 7.9255 | 0.138
GEN-2019-013 | 04 SOUTHEAST | 511490 | ELKCITY6 | 230 | 7.3607 | 7.3322 | 0.0285
GEN-2019-013 | 04 SOUTHEAST | 511553 | CHISHOLM7 | 345 | 12.3397 | 12.2861 | 0.0536
GEN-2019-013 | 04 SOUTHEAST | 523777 | WHEELER 6 | 230 | 6.7683 | 6.6907 | 0.0776
GEN-2019-013 | 04 SOUTHEAST | 511458 | ELKCTY-4 | 138 | 11.2004 | 11.1778 | 0.0226
GEN-2019-013 | 04 SOUTHEAST | 523771 | GRAPEVINE 6 | 230 | 5.9762 | 5.9542 | 0.022
GEN-2019-013 | 04 SOUTHEAST | 523776 | WHEELER 3 | 115 | 6.8177 | 6.7835 | 0.0342
GEN-2019-013 | 04 SOUTHEAST | 560035 | GRAPEVINE | 345 | 6.4589 | 6.453 | 0.0059
GEN-2019-013 | 04 SOUTHEAST | 560078 | G16-037-TAP | 345 | 10.1427 | 10.129 | 0.0137
GEN-2019-013 | 04 SOUTHEAST | 755000 | WWDBORDT | 345 | 12.2648 | 12.213 | 0.0518
GEN-2019-013 | 04 SOUTHEAST | 511446 | CL-AFTP4 | 138 | 6.4006 | 6.396 | 0.0046
GEN-2019-013 | 04 SOUTHEAST | 511459 | ELKCTY-2 | 69 | 6.9555 | 6.9519 | 0.0036
GEN-2019-013 | 04 SOUTHEAST | 511485 | CLINTJC4 | 138 | 6.162 | 6.1597 | 0.0023
GEN-2019-013 | 04 SOUTHEAST | 511511 | FALCNRD4 | 138 | 7.8063 | 7.7956 | 0.0107
GEN-2019-013 | 04 SOUTHEAST | 515375 | WWRDEHV7 | 345 | 22.3641 | 22.3551 | 0.009
GEN-2019-013 | 04 SOUTHEAST | 515458 | BORDER 7 | 345 | 8.2517 | 8.2316 | 0.0201
GEN-2019-013 | 04 SOUTHEAST | 515800 | GRACMNT7 | 345 | 20.5087 | 20.5018 | 0.0069
GEN-2019-013 | 04 SOUTHEAST | 521116 | REDHLSW4 | 138 | 6.966 | 6.9601 | 0.0059
GEN-2019-013 | 04 SOUTHEAST | 523770 | GRAPEVINE 3 | 115 | 7.9787 | 7.963 | 0.0157
GEN-2019-013 | 04 SOUTHEAST | 523772 | COBRN_CREEK3 | 115 | 3.6267 | 3.617 | 0.0097
GEN-2019-013 | 04 SOUTHEAST | 523797 | HOWARD 3 | 115 | 5.1847 | 5.1674 | 0.0173
GEN-2019-013 | 04 SOUTHEAST | 523961 | POTTER_CO 7 | 345 | 11.6631 | 11.6585 | 0.0046
GEN-2019-013 | 04 SOUTHEAST | 524044 | NICHOLS 6 | 230 | 26.1237 | 26.111 | 0.0127
GEN-2019-013 | 04 SOUTHEAST | 587230 | GEN-2016-037 | 345 | 9.6646 | 9.6522 | 0.0124
GEN-2019-045 | 04 SOUTHEAST | 515853 | DGRASSE4 | 138 | 17.0745 | 16.2978 | 0.7767
GEN-2019-045 | 04 SOUTHEAST | 514795 | KNOBHIL4 | 138 | 10.2855 | 10.0627 | 0.2228
GEN-2019-045 | 04 SOUTHEAST | 515852 | DGRASSE7 | 345 | 15.3179 | 15.1627 | 0.1552
GEN-2019-045 | 04 SOUTHEAST | 520436 | ROSEVLY4 | 138 | 12.3574 | 11.9717 | 0.3857
GEN-2019-045 | 04 SOUTHEAST | 520999 | MOORLND4 | 138 | 20.0616 | 20.0283 | 0.0333
GEN-2019-045 | 04 SOUTHEAST | 585300 | GEN-2015-095 | 138 | 16.8692 | 16.1131 | 0.7561
GEN-2019-045 | 04 SOUTHEAST | 763769 | GEN-2019-045 | 138 | 17.0745 | 16.2978 | 0.7767
GEN-2019-045 | 04 SOUTHEAST | 514788 | GLASMTN4 | 138 | 5.1117 | 5.1099 | 0.0018
GEN-2019-045 | 04 SOUTHEAST | 514794 | KNOBHIL2 | 69 | 8.8727 | 8.8171 | 0.0556
GEN-2019-045 | 04 SOUTHEAST | 515375 | WWRDEHV7 | 345 | 22.3641 | 22.2906 | 0.0735
GEN-2019-045 | 04 SOUTHEAST | 515785 | WINDFRM4 | 138 | 19.5945 | 19.5629 | 0.0316
GEN-2019-045 | 04 SOUTHEAST | 520425 | PIC4 | 138 | 7.9856 | 7.9813 | 0.0043
GEN-2019-045 | 04 SOUTHEAST | 520430 | NOELSW 4 | 138 | 10.3556 | 10.131 | 0.2246
GEN-2019-045 | 04 SOUTHEAST | 520462 | ASPEN 4 | 138 | 19.3561 | 19.3252 | 0.0309
GEN-2019-045 | 04 SOUTHEAST | 520553 | SEILING4 | 138 | 6.6101 | 6.6079 | 0.0022
GEN-2019-045 | 04 SOUTHEAST | 520601 | AVARD 4 | 138 | 6.857 | 6.7371 | 0.1199
GEN-2019-045 | 04 SOUTHEAST | 520957 | IODINE 4 | 138 | 7.673 | 7.6683 | 0.0047
GEN-2019-045 | 04 SOUTHEAST | 520995 | MOORLND2 | 69 | 8.5299 | 8.5271 | 0.0028
GEN-2019-045 | 04 SOUTHEAST | 539801 | THISTLE7 | 345 | 16.6662 | 16.6117 | 0.0545
GEN-2019-045 | 04 SOUTHEAST | 587140 | GEN-2016-020 | 138 | 7.4213 | 7.4172 | 0.0041
GEN-2019-045 | 04 SOUTHEAST | 514778 | CLEOCOR4 | 138 | 6.333 | 6.3305 | 0.0025
GEN-2019-045 | 04 SOUTHEAST | 514785 | WOODWRD4 | 138 | 13.1123 | 13.1016 | 0.0107
GEN-2019-045 | 04 SOUTHEAST | 514792 | ALVAOGE2 | 69 | 7.5035 | 7.469 | 0.0345
GEN-2019-045 | 04 SOUTHEAST | 515376 | WWRDEHV4 | 138 | 24.8769 | 24.8426 | 0.0343
GEN-2019-045 | 04 SOUTHEAST | 515407 | TATONGA7 | 345 | 17.5658 | 17.5478 | 0.018
GEN-2019-045 | 04 SOUTHEAST | 515554 | BVRCNTY7 | 345 | 15.3093 | 15.2954 | 0.0139
GEN-2019-045 | 04 SOUTHEAST | 515560 | CZYCRVT2 | 69 | 3.2399 | 3.2365 | 0.0034
GEN-2019-045 | 04 SOUTHEAST | 515599 | G07621119-20 | 345 | 13.4849 | 13.4596 | 0.0253
GEN-2019-045 | 04 SOUTHEAST | 515786 | FPLWIND4 | 138 | 6.1883 | 6.1854 | 0.0029
GEN-2019-045 | 04 SOUTHEAST | 515961 | GUTHRIE7 | 345 | 12.8816 | 12.8571 | 0.0245
GEN-2019-045 | 04 SOUTHEAST | 516106 | BOBCAT 7 | 345 | 15.796 | 15.7683 | 0.0277
GEN-2019-045 | 04 SOUTHEAST | 520437 | SALTPLN4 | 138 | 6.3315 | 6.2772 | 0.0543
GEN-2019-045 | 04 SOUTHEAST | 520500 | BEARCAT4 | 138 | 14.2641 | 14.2481 | 0.016
GEN-2019-045 | 04 SOUTHEAST | 520848 | CDRDLTP4 | 138 | 5.714 | 5.7122 | 0.0018
GEN-2019-045 | 04 SOUTHEAST | 520920 | FTSUPLY4 | 138 | 5.225 | 5.2229 | 0.0021
GEN-2019-045 | 04 SOUTHEAST | 521065 | TALOGA 4 | 138 | 7.1703 | 7.168 | 0.0023
GEN-2019-045 | 04 SOUTHEAST | 521197 | CRTSJCT2 | 69 | 8.1375 | 8.135 | 0.0025
GEN-2019-045 | 04 SOUTHEAST | 532782 | BUFFALO7 | 345 | 20.7555 | 20.7379 | 0.0176
GEN-2019-045 | 04 SOUTHEAST | 539800 | CLARKCOUNTY7 | 345 | 12.7785 | 12.7698 | 0.0087
GEN-2019-045 | 04 SOUTHEAST | 539804 | THISTLE4 | 138 | 17.5567 | 17.5379 | 0.0188
GEN-2019-045 | 04 SOUTHEAST | 588630 | GEN-2017-018 | 345 | 16.6662 | 16.6117 | 0.0545
GEN-2019-045 | 04 SOUTHEAST | 755000 | WWDBORDT | 345 | 12.2648 | 12.2609 | 0.0039
GEN-2019-045 | 04 SOUTHEAST | 762834 | GEN-2018-049 | 345 | 6.9567 | 6.9476 | 0.0091
GEN-2019-045 | 04 SOUTHEAST | 763527 | GEN-2019-012 | 345 | 19.3711 | 19.3161 | 0.055
GEN-2019-045 | 04 SOUTHEAST | 511553 | CHISHOLM7 | 345 | 12.3397 | 12.3359 | 0.0038
GEN-2019-045 | 04 SOUTHEAST | 514716 | SALINE 2 | 69 | 3.1478 | 3.1455 | 0.0023
GEN-2019-045 | 04 SOUTHEAST | 514777 | CLEOCOR2 | 69 | 8.1689 | 8.1645 | 0.0044
GEN-2019-045 | 04 SOUTHEAST | 514782 | WODWRD 2 | 69 | 10.8998 | 10.8959 | 0.0039
GEN-2019-045 | 04 SOUTHEAST | 514787 | DEWEY 4 | 138 | 7.3672 | 7.3651 | 0.0021
GEN-2019-045 | 04 SOUTHEAST | 514796 | IODINE-4 | 138 | 7.3201 | 7.3175 | 0.0026
GEN-2019-045 | 04 SOUTHEAST | 515363 | CENT 4 | 138 | 3.0872 | 3.0868 | 0.0004
GEN-2019-045 | 04 SOUTHEAST | 515394 | KEENAN 4 | 138 | 8.9414 | 8.9374 | 0.004
GEN-2019-045 | 04 SOUTHEAST | 515398 | OUSPRT 4 | 138 | 9.528 | 9.5233 | 0.0047
GEN-2019-045 | 04 SOUTHEAST | 515425 | WWDPST 4 | 138 | 17.7977 | 17.7795 | 0.0182
GEN-2019-045 | 04 SOUTHEAST | 515448 | CRSRDSW7 | 345 | 12.1468 | 12.1384 | 0.0084
GEN-2019-045 | 04 SOUTHEAST | 515458 | BORDER 7 | 345 | 8.2517 | 8.2502 | 0.0015
GEN-2019-045 | 04 SOUTHEAST | 515497 | MATHWSN7 | 345 | 32.7952 | 32.7845 | 0.0107
GEN-2019-045 | 04 SOUTHEAST | 515562 | CLEOPLT4 | 138 | 6.3301 | 6.3276 | 0.0025
GEN-2019-045 | 04 SOUTHEAST | 515582 | SLNGWND7 | 345 | 8.4766 | 8.4727 | 0.0039
GEN-2019-045 | 04 SOUTHEAST | 515585 | MAMTHPW7 | 345 | 13.5669 | 13.5563 | 0.0106
GEN-2019-045 | 04 SOUTHEAST | 515590 | PALDR2W7 | 345 | 12.8669 | 12.8573 | 0.0096
GEN-2019-045 | 04 SOUTHEAST | 515618 | BALKOW 7 | 345 | 12.5807 | 12.5715 | 0.0092
GEN-2019-045 | 04 SOUTHEAST | 515677 | BADGER 7 | 345 | 13.7821 | 13.7687 | 0.0134
GEN-2019-045 | 04 SOUTHEAST | 515803 | ALINETP2 | 69 | 3.4991 | 3.4975 | 0.0016
GEN-2019-045 | 04 SOUTHEAST | 515825 | GRTWSRN7 | 345 | 9.0702 | 9.0581 | 0.0121
GEN-2019-045 | 04 SOUTHEAST | 515951 | PERSIMN7 | 345 | 11.0796 | 11.0615 | 0.0181
GEN-2019-045 | 04 SOUTHEAST | 516025 | SUNDANC4 | 138 | 4.4828 | 4.4817 | 0.0011
GEN-2019-045 | 04 SOUTHEAST | 516146 | 25MILE 7 | 345 | 11.1221 | 11.1094 | 0.0127
GEN-2019-045 | 04 SOUTHEAST | 520431 | CHRKCTY4 | 138 | 6.1533 | 6.1058 | 0.0475
GEN-2019-045 | 04 SOUTHEAST | 520480 | CURTIS 2 | 69 | 3.9232 | 3.9227 | 0.0005
GEN-2019-045 | 04 SOUTHEAST | 520507 | CEDRDAL4 | 138 | 4.5919 | 4.5907 | 0.0012
GEN-2019-045 | 04 SOUTHEAST | 520806 | ALVA 2 | 69 | 6.5668 | 6.5426 | 0.0242
GEN-2019-045 | 04 SOUTHEAST | 520919 | FTSUPLY2 | 69 | 7.4598 | 7.4573 | 0.0025
GEN-2019-045 | 04 SOUTHEAST | 520922 | SLEEPBR4 | 138 | 4.0952 | 4.0941 | 0.0011
GEN-2019-045 | 04 SOUTHEAST | 521016 | OKEENE 4 | 138 | 7.0692 | 7.0682 | 0.001
GEN-2019-045 | 04 SOUTHEAST | 521064 | TALOGA 2 | 69 | 8.125 | 8.1236 | 0.0014
GEN-2019-045 | 04 SOUTHEAST | 521096 | WOODWRD2 | 69 | 9.8637 | 9.8603 | 0.0034
GEN-2019-045 | 04 SOUTHEAST | 521128 | NINMLTP4 | 138 | 4.7158 | 4.715 | 0.0008
GEN-2019-045 | 04 SOUTHEAST | 523097 | HITCHLAND 7 | 345 | 14.9713 | 14.9632 | 0.0081
GEN-2019-045 | 04 SOUTHEAST | 531469 | SPERVIL7 | 345 | 13.6098 | 13.6045 | 0.0053
GEN-2019-045 | 04 SOUTHEAST | 532783 | KINGMAN7 | 345 | 7.0277 | 7.0262 | 0.0015
GEN-2019-045 | 04 SOUTHEAST | 532796 | WICHITA7 | 345 | 23.7708 | 23.7548 | 0.016
GEN-2019-045 | 04 SOUTHEAST | 539638 | FLATRDG4 | 138 | 15.5636 | 15.55 | 0.0136
GEN-2019-045 | 04 SOUTHEAST | 539813 | TRANSFORMER | 345 | 10.6791 | 10.6731 | 0.006
GEN-2019-045 | 04 SOUTHEAST | 539840 | GEN-2011-008 | 345 | 10.5555 | 10.5498 | 0.0057
GEN-2019-045 | 04 SOUTHEAST | 560080 | G16-046-TAP | 345 | 11.3684 | 11.363 | 0.0054
GEN-2019-045 | 04 SOUTHEAST | 585410 | GREAT_WESTRN | 345 | 9.7415 | 9.7289 | 0.0126
GEN-2019-045 | 04 SOUTHEAST | 585430 | PRSIMN_CRK1 | 345 | 11.7445 | 11.7255 | 0.019
GEN-2019-045 | 04 SOUTHEAST | 587500 | GEN-2016-073 | 345 | 15.2224 | 15.2131 | 0.0093
GEN-2019-045 | 04 SOUTHEAST | 588560 | GEN-2017-011 | 345 | 12.6206 | 12.6029 | 0.0177
GEN-2019-045 | 04 SOUTHEAST | 760284 | GEN-2017-220 | 345 | 20.642 | 20.6246 | 0.0174
GEN-2019-045 | 04 SOUTHEAST | 763890 | GEN-2019-058 | 345 | 12.52 | 12.5117 | 0.0083
GEN-2019-045 | 04 SOUTHEAST | 511557 | CHISHOLM6 | 230 | 12.1566 | 12.1547 | 0.0019
GEN-2019-045 | 04 SOUTHEAST | 514776 | NEWGRTP2 | 69 | 5.4519 | 5.451 | 0.0009
GEN-2019-045 | 04 SOUTHEAST | 514781 | CEDARAV2 | 69 | 5.6927 | 5.6917 | 0.001
GEN-2019-045 | 04 SOUTHEAST | 514789 | MENOTAP4 | 138 | 7.0374 | 7.0356 | 0.0018
GEN-2019-045 | 04 SOUTHEAST | 514793 | ALINE 2 | 69 | 3.4943 | 3.4928 | 0.0015
GEN-2019-045 | 04 SOUTHEAST | 514880 | NORTWST7 | 345 | 32.9086 | 32.9026 | 0.006
GEN-2019-045 | 04 SOUTHEAST | 514901 | CIMARON7 | 345 | 34.2931 | 34.2856 | 0.0075
GEN-2019-045 | 04 SOUTHEAST | 515371 | HELENAT2 | 69 | 3.1659 | 3.1638 | 0.0021
GEN-2019-045 | 04 SOUTHEAST | 515390 | TLGAWND4 | 138 | 3.592 | 3.5916 | 0.0004
GEN-2019-045 | 04 SOUTHEAST | 515533 | REDCLFT4 | 138 | 6.6178 | 6.6158 | 0.002
GEN-2019-045 | 04 SOUTHEAST | 515553 | CLEO PL4 | 138 | 5.3253 | 5.3235 | 0.0018
GEN-2019-045 | 04 SOUTHEAST | 515634 | PALDR1W7 | 345 | 10.943 | 10.9361 | 0.0069
GEN-2019-045 | 04 SOUTHEAST | 515686 | BLUWND 7 | 345 | 12.3633 | 12.3525 | 0.0108
GEN-2019-045 | 04 SOUTHEAST | 515804 | CLEOTP 2 | 69 | 7.1427 | 7.1391 | 0.0036
GEN-2019-045 | 04 SOUTHEAST | 515875 | REDNGTN7 | 345 | 16.7149 | 16.7117 | 0.0032
GEN-2019-045 | 04 SOUTHEAST | 515964 | CANTNLK4 | 138 | 4.7319 | 4.7313 | 0.0006
GEN-2019-045 | 04 SOUTHEAST | 516159 | 25MILZ 7 | 345 | 11.1104 | 11.0978 | 0.0126
GEN-2019-045 | 04 SOUTHEAST | 520407 | WINCHTP2 | 69 | 3.9925 | 3.9847 | 0.0078
GEN-2019-045 | 04 SOUTHEAST | 520421 | STOCKHOLM2 | 69 | 3.9642 | 3.9632 | 0.001
GEN-2019-045 | 04 SOUTHEAST | 520454 | STALOGA2 | 69 | 4.4194 | 4.419 | 0.0004
GEN-2019-045 | 04 SOUTHEAST | 520456 | FTSPLY 2 | 69 | 6.4106 | 6.4089 | 0.0017
GEN-2019-045 | 04 SOUTHEAST | 520492 | NINMILE4 | 138 | 3.6632 | 3.6628 | 0.0004
GEN-2019-045 | 04 SOUTHEAST | 520536 | WATNGSW4 | 138 | 6.9746 | 6.9741 | 0.0005
GEN-2019-045 | 04 SOUTHEAST | 520825 | BEAVERJ2 | 69 | 2.1423 | 2.1421 | 0.0002
GEN-2019-045 | 04 SOUTHEAST | 520843 | CANTON-2 | 69 | 4.7017 | 4.7012 | 0.0005
GEN-2019-045 | 04 SOUTHEAST | 520851 | CHEROKS2 | 69 | 5.2217 | 5.211 | 0.0107
GEN-2019-045 | 04 SOUTHEAST | 520855 | CLEOSW 2 | 69 | 7.6016 | 7.5974 | 0.0042
GEN-2019-045 | 04 SOUTHEAST | 520882 | DOVERSW4 | 138 | 10.9376 | 10.9367 | 0.0009
GEN-2019-045 | 04 SOUTHEAST | 521001 | MORWODS4 | 138 | 5.1171 | 5.1166 | 0.0005
GEN-2019-045 | 04 SOUTHEAST | 521015 | OKEENE 2 | 69 | 6.3884 | 6.3876 | 0.0008
GEN-2019-045 | 04 SOUTHEAST | 521082 | VICI 2 | 69 | 3.8314 | 3.8311 | 0.0003
GEN-2019-045 | 04 SOUTHEAST | 521196 | FARGOJCT2 | 69 | 7.5366 | 7.5346 | 0.002
GEN-2019-045 | 04 SOUTHEAST | 521200 | DRIFTWD4 | 138 | 5.9181 | 5.8852 | 0.0329
GEN-2019-045 | 04 SOUTHEAST | 523095 | HITCHLAND 6 | 230 | 14.5761 | 14.5722 | 0.0039
GEN-2019-045 | 04 SOUTHEAST | 523101 | NOBLE_WND 7 | 345 | 14.9103 | 14.9023 | 0.008
GEN-2019-045 | 04 SOUTHEAST | 523112 | NOVUS1 7 | 345 | 14.6716 | 14.6638 | 0.0078
GEN-2019-045 | 04 SOUTHEAST | 523823 | CARPENTER 7 | 345 | 6.5781 | 6.5772 | 0.0009
GEN-2019-045 | 04 SOUTHEAST | 523961 | POTTER_CO 7 | 345 | 11.6631 | 11.6621 | 0.001
GEN-2019-045 | 04 SOUTHEAST | 530583 | POSTROCK7 | 345 | 7.7231 | 7.7225 | 0.0006
GEN-2019-045 | 04 SOUTHEAST | 531501 | BUCKNER7 | 345 | 9.2456 | 9.244 | 0.0016
GEN-2019-045 | 04 SOUTHEAST | 532771 | RENO 7 | 345 | 11.0976 | 11.0959 | 0.0017
GEN-2019-045 | 04 SOUTHEAST | 532784 | NINN1WF7 | 345 | 5.8368 | 5.8359 | 0.0009
GEN-2019-045 | 04 SOUTHEAST | 532791 | BENTON 7 | 345 | 19.0077 | 19.0027 | 0.005
GEN-2019-045 | 04 SOUTHEAST | 532798 | VIOLA 7 | 345 | 14.0837 | 14.0785 | 0.0052
GEN-2019-045 | 04 SOUTHEAST | 533040 | EVANS N4 | 138 | 32.3573 | 32.3493 | 0.008
GEN-2019-045 | 04 SOUTHEAST | 539631 | FLATRWD4 | 138 | 10.3815 | 10.3756 | 0.0059
GEN-2019-045 | 04 SOUTHEAST | 539668 | HARPER 4 | 138 | 7.2122 | 7.2107 | 0.0015
GEN-2019-045 | 04 SOUTHEAST | 539674 | BARBER 4 | 138 | 8.2322 | 8.2291 | 0.0031
GEN-2019-045 | 04 SOUTHEAST | 539695 | SPEARVL6 | 230 | 12.772 | 12.7696 | 0.0024
GEN-2019-045 | 04 SOUTHEAST | 539759 | SPRVL 3 | 115 | 12.8273 | 12.8258 | 0.0015
GEN-2019-045 | 04 SOUTHEAST | 539803 | IRONWOOD7 | 345 | 13.1638 | 13.1587 | 0.0051
GEN-2019-045 | 04 SOUTHEAST | 539841 | G-2011-008-1 | 345 | 10.5555 | 10.5498 | 0.0057
GEN-2019-045 | 04 SOUTHEAST | 539855 | G-2011-008-2 | 345 | 8.8342 | 8.8303 | 0.0039
GEN-2019-045 | 04 SOUTHEAST | 539857 | G-2011-008-3 | 345 | 8.2708 | 8.2674 | 0.0034
GEN-2019-045 | 04 SOUTHEAST | 560022 | CRAWFISH_DR | 345 | 13.842 | 13.8419 | 0.0001
GEN-2019-045 | 04 SOUTHEAST | 560035 | GRAPEVINE | 345 | 6.4589 | 6.4583 | 0.0006
GEN-2019-045 | 04 SOUTHEAST | 560078 | G16-037-TAP | 345 | 10.1427 | 10.1415 | 0.0012
GEN-2019-045 | 04 SOUTHEAST | 562476 | G14-001-TAP | 345 | 10.3737 | 10.3722 | 0.0015
GEN-2019-045 | 04 SOUTHEAST | 576397 | G10014G11022 | 345 | 10.3812 | 10.3777 | 0.0035
GEN-2019-045 | 04 SOUTHEAST | 585190 | GEN-2015-082 | 345 | 7.0512 | 7.0479 | 0.0033
GEN-2019-045 | 04 SOUTHEAST | 585420 | COWBOY_RIDGE | 345 | 7.5551 | 7.5478 | 0.0073
GEN-2019-045 | 04 SOUTHEAST | 585440 | PRSIMN_CRK2 | 345 | 10.7138 | 10.6981 | 0.0157
GEN-2019-045 | 04 SOUTHEAST | 587310 | GEN-2016-046 | 345 | 9.9533 | 9.9492 | 0.0041
GEN-2019-045 | 04 SOUTHEAST | 900001 | TRAVERSE3 | 345 | 6.9271 | 6.9268 | 0.0003
GEN-2019-065 | 04 SOUTHEAST | 514901 | CIMARON7 | 345 | 34.2931 | 34.2931 | 0
GEN-2019-065 | 04 SOUTHEAST | 514801 | MINCO 7 | 345 | 23.2915 | 23.2915 | 0
GEN-2019-065 | 04 SOUTHEAST | 514880 | NORTWST7 | 345 | 32.9086 | 32.9085 | 0.0001
GEN-2019-065 | 04 SOUTHEAST | 514898 | CIMARON4 | 138 | 45.5365 | 45.5365 | 0
GEN-2019-065 | 04 SOUTHEAST | 515497 | MATHWSN7 | 345 | 32.7952 | 32.7952 | 0
GEN-2019-065 | 04 SOUTHEAST | 515610 | FSHRTAP7 | 345 | 16.0539 | 16.0539 | 0
GEN-2019-065 | 04 SOUTHEAST | 555234 | NSUB345 | 345 | 27.0301 | 27.03 | 0.0001
GEN-2019-065 | 04 SOUTHEAST | 511425 | TUTCONT4 | 138 | 10.052 | 10.052 | 0
GEN-2019-065 | 04 SOUTHEAST | 514819 | EL-RENO4 | 138 | 16.7698 | 16.7698 | 0
GEN-2019-065 | 04 SOUTHEAST | 514820 | JENSENT4 | 138 | 18.1844 | 18.1844 | 0
GEN-2019-065 | 04 SOUTHEAST | 514863 | HAYMAKR4 | 138 | 26.8465 | 26.8464 | 0.0001
GEN-2019-065 | 04 SOUTHEAST | 514879 | NORTWST4 | 138 | 44.7892 | 44.7892 | 0
GEN-2019-065 | 04 SOUTHEAST | 514881 | SPRNGCK7 | 345 | 23.3445 | 23.3445 | 0
GEN-2019-065 | 04 SOUTHEAST | 514894 | CZECHAL4 | 138 | 28.8657 | 28.8657 | 0
GEN-2019-065 | 04 SOUTHEAST | 514895 | SARA 4 | 138 | 19.7537 | 19.7537 | 0
GEN-2019-065 | 04 SOUTHEAST | 514908 | ARCADIA7 | 345 | 28.6269 | 28.6269 | 0
GEN-2019-065 | 04 SOUTHEAST | 514929 | PLVALLY4 | 138 | 45.9536 | 45.9536 | 0
GEN-2019-065 | 04 SOUTHEAST | 514934 | DRAPER 7 | 345 | 26.1641 | 26.1641 | 0
GEN-2019-065 | 04 SOUTHEAST | 515407 | TATONGA7 | 345 | 17.5658 | 17.5658 | 0
GEN-2019-065 | 04 SOUTHEAST | 515444 | MCNOWND7 | 345 | 23.197 | 23.197 | 0
GEN-2019-065 | 04 SOUTHEAST | 515549 | MNCWND37 | 345 | 14.1504 | 14.1504 | 0
GEN-2019-065 | 04 SOUTHEAST | 515600 | KNGFSHR7 | 345 | 10.5637 | 10.5637 | 0
GEN-2019-065 | 04 SOUTHEAST | 515605 | CANADN7 | 345 | 11.5734 | 11.5734 | 0
GEN-2019-065 | 04 SOUTHEAST | 515800 | GRACMNT7 | 345 | 20.5087 | 20.5087 | 0
GEN-2019-065 | 04 SOUTHEAST | 515875 | REDNGTN7 | 345 | 16.7149 | 16.7149 | 0
GEN-2019-065 | 04 SOUTHEAST | 761250 | GEN-2017-233 | 345 | 22.5233 | 22.5233 | 0
GEN-2019-065 | 04 SOUTHEAST | 900001 | TRAVERSE3 | 345 | 6.9271 | 6.927 | 0.0001
GEN-2019-065 | 04 SOUTHEAST | 511501 | TUTTLE4 | 138 | 9.8736 | 9.8736 | 0
GEN-2019-065 | 04 SOUTHEAST | 511576 | CEMRD_TP4 | 138 | 6.6874 | 6.6874 | 0
GEN-2019-065 | 04 SOUTHEAST | 514715 | WOODRNG7 | 345 | 18.7369 | 18.7369 | 0
GEN-2019-065 | 04 SOUTHEAST | 514818 | ELRENO 2 | 69 | 7.3817 | 7.3817 | 0
GEN-2019-065 | 04 SOUTHEAST | 514821 | JENSEN 4 | 138 | 15.3506 | 15.3506 | 0
GEN-2019-065 | 04 SOUTHEAST | 514828 | KETCHTP4 | 138 | 26.9478 | 26.9477 | 0.0001
GEN-2019-065 | 04 SOUTHEAST | 514853 | DVISION4 | 138 | 36.7295 | 36.7295 | 0
GEN-2019-065 | 04 SOUTHEAST | 514854 | BRADEN 4 | 138 | 31.8391 | 31.8391 | 0
GEN-2019-065 | 04 SOUTHEAST | 514864 | PIEDMNT4 | 138 | 22.6006 | 22.6006 | 0
GEN-2019-065 | 04 SOUTHEAST | 514873 | LNEOAK 4 | 138 | 27.2272 | 27.2272 | 0
GEN-2019-065 | 04 SOUTHEAST | 514893 | XEROX 4 | 138 | 30.2152 | 30.2152 | 0
GEN-2019-065 | 04 SOUTHEAST | 514902 | MCCLAIN4 | 138 | 37.8236 | 37.8236 | 0
GEN-2019-065 | 04 SOUTHEAST | 514907 | ARCADIA4 | 138 | 47.2233 | 47.2233 | 0
GEN-2019-065 | 04 SOUTHEAST | 514909 | REDBUD 7 | 345 | 27.6026 | 27.6026 | 0
GEN-2019-065 | 04 SOUTHEAST | 514933 | DRAPER 4 | 138 | 42.9122 | 42.9121 | 0.0001
GEN-2019-065 | 04 SOUTHEAST | 514953 | HOLLYWD4 | 138 | 36.8243 | 36.8243 | 0
GEN-2019-065 | 04 SOUTHEAST | 514957 | CHERYCK4 | 138 | 22.6144 | 22.6144 | 0
GEN-2019-065 | 04 SOUTHEAST | 514992 | TURNER 4 | 138 | 31.61 | 31.61 | 0
GEN-2019-065 | 04 SOUTHEAST | 515045 | SEMINOL7 | 345 | 30.8428 | 30.8426 | 0.0002
GEN-2019-065 | 04 SOUTHEAST | 515375 | WWRDEHV7 | 345 | 22.3641 | 22.3641 | 0
GEN-2019-065 | 04 SOUTHEAST | 515448 | CRSRDSW7 | 345 | 12.1468 | 12.1468 | 0
GEN-2019-065 | 04 SOUTHEAST | 515582 | SLNGWND7 | 345 | 8.4766 | 8.4766 | 0
GEN-2019-065 | 04 SOUTHEAST | 515585 | MAMTHPW7 | 345 | 13.5669 | 13.5669 | 0
GEN-2019-065 | 04 SOUTHEAST | 515802 | GRACMNT4 | 138 | 37.8367 | 37.8367 | 0
GEN-2019-065 | 04 SOUTHEAST | 515877 | REDDIRT7 | 345 | 16.7106 | 16.7106 | 0
GEN-2019-065 | 04 SOUTHEAST | 515939 | MNCWND47 | 345 | 9.8862 | 9.8862 | 0
GEN-2019-065 | 04 SOUTHEAST | 515962 | OMEGA 4 | 138 | 5.713 | 5.713 | 0
GEN-2019-065 | 04 SOUTHEAST | 560078 | G16-037-TAP | 345 | 10.1427 | 10.1427 | 0
GEN-2019-065 | 04 SOUTHEAST | 563269 | GEN-2015-093 | 345 | 10.8212 | 10.8212 | 0
GEN-2019-065 | 04 SOUTHEAST | 587744 | G16-091-TAP | 345 | 16.3944 | 16.3944 | 0
GEN-2019-065 | 04 SOUTHEAST | 587804 | G16-119-TAP | 345 | 15.2197 | 15.2197 | 0
GEN-2019-065 | 04 SOUTHEAST | 760032 | GEN-2017-132 | 345 | 6.7839 | 6.7839 | 0
GEN-2019-065 | 04 SOUTHEAST | 761229 | GEN-2017-150 | 345 | 22.4791 | 22.4791 | 0
GEN-2019-065 | 04 SOUTHEAST | 900004 | TRW2-TRW3 | 345 | 6.2021 | 6.2021 | 0
GEN-2019-065 | 04 SOUTHEAST | 914902 | G17-152_TAP | 138 | 37.5659 | 37.5659 | 0
GEN-2019-065 | 04 SOUTHEAST | 509782 | R.S.S.-7 | 345 | 32.1585 | 32.1585 | 0
GEN-2019-065 | 04 SOUTHEAST | 510907 | PITTSB-7 | 345 | 16.4511 | 16.4504 | 0.0007
GEN-2019-065 | 04 SOUTHEAST | 511424 | T-CONCO4 | 138 | 6.6491 | 6.6491 | 0
GEN-2019-065 | 04 SOUTHEAST | 511468 | L.E.S.-7 | 345 | 14.8644 | 14.8644 | 0
GEN-2019-065 | 04 SOUTHEAST | 511540 | CAN_GAS4 | 138 | 8.9671 | 8.9671 | 0
GEN-2019-065 | 04 SOUTHEAST | 511553 | CHISHOLM7 | 345 | 12.3397 | 12.3397 | 0
GEN-2019-065 | 04 SOUTHEAST | 511575 | LEONARD4 | 138 | 9.6759 | 9.6759 | 0
GEN-2019-065 | 04 SOUTHEAST | 514714 | WOODRNG4 | 138 | 19.2315 | 19.2315 | 0
GEN-2019-065 | 04 SOUTHEAST | 514803 | SOONER 7 | 345 | 28.2956 | 28.2956 | 0
GEN-2019-065 | 04 SOUTHEAST | 514817 | SVCELRN2 | 69 | 6.4236 | 6.4236 | 0
GEN-2019-065 | 04 SOUTHEAST | 514823 | ROMNOSE4 | 138 | 5.9069 | 5.9069 | 0
GEN-2019-065 | 04 SOUTHEAST | 514827 | CTNWOOD4 | 138 | 18.3527 | 18.3527 | 0
GEN-2019-065 | 04 SOUTHEAST | 514834 | KETCH 4 | 138 | 27.4311 | 27.4311 | 0
GEN-2019-065 | 04 SOUTHEAST | 514849 | LAKESID4 | 138 | 24.7987 | 24.7987 | 0
GEN-2019-065 | 04 SOUTHEAST | 514851 | QUAILCK4 | 138 | 29.772 | 29.772 | 0
GEN-2019-065 | 04 SOUTHEAST | 514852 | SLVRLAK4 | 138 | 33.222 | 33.222 | 0
GEN-2019-065 | 04 SOUTHEAST | 514861 | MUSTANG4 | 138 | 39.268 | 39.268 | 0
GEN-2019-065 | 04 SOUTHEAST | 514862 | RICHRDS4 | 138 | 21.9673 | 21.9673 | 0
GEN-2019-065 | 04 SOUTHEAST | 514876 | SW134TP4 | 138 | 31.1811 | 31.1811 | 0
GEN-2019-065 | 04 SOUTHEAST | 514896 | MORGAN 4 | 138 | 33.5988 | 33.5988 | 0
GEN-2019-065 | 04 SOUTHEAST | 514906 | JNSKAMO4 | 138 | 21.601 | 21.601 | 0
GEN-2019-065 | 04 SOUTHEAST | 514928 | SOGATE 4 | 138 | 29.1387 | 29.1387 | 0
GEN-2019-065 | 04 SOUTHEAST | 514946 | MIDWEST4 | 138 | 34.4184 | 34.4184 | 0
GEN-2019-065 | 04 SOUTHEAST | 514949 | SOONRTP4 | 138 | 22.8076 | 22.8076 | 0
GEN-2019-065 | 04 SOUTHEAST | 514952 | STUBMAN4 | 138 | 25.0448 | 25.0448 | 0
GEN-2019-065 | 04 SOUTHEAST | 514954 | INDNHIL4 | 138 | 28.8671 | 28.8671 | 0
GEN-2019-065 | 04 SOUTHEAST | 514958 | BOYD 4 | 138 | 20.8043 | 20.8043 | 0
GEN-2019-065 | 04 SOUTHEAST | 514961 | GM 4 | 138 | 19.964 | 19.964 | 0
GEN-2019-065 | 04 SOUTHEAST | 515003 | BARNES 4 | 138 | 16.1837 | 16.1837 | 0
GEN-2019-065 | 04 SOUTHEAST | 515044 | SEMINOL4 | 138 | 40.4325 | 40.4324 | 0.0001
GEN-2019-065 | 04 SOUTHEAST | 515376 | WWRDEHV4 | 138 | 24.8769 | 24.8769 | 0
GEN-2019-065 | 04 SOUTHEAST | 515461 | RNDBARN4 | 138 | 44.4777 | 44.4777 | 0
GEN-2019-065 | 04 SOUTHEAST | 515465 | LGARBER4 | 138 | 21.6212 | 21.6212 | 0
GEN-2019-065 | 04 SOUTHEAST | 515466 | MITCHSB4 | 138 | 21.7532 | 21.7532 | 0
GEN-2019-065 | 04 SOUTHEAST | 515476 | HUNTERS7 | 345 | 13.1988 | 13.1988 | 0
GEN-2019-065 | 04 SOUTHEAST | 515506 | OKRCHET2 | 69 | 3.6454 | 3.6454 | 0
GEN-2019-065 | 04 SOUTHEAST | 515554 | BVRCNTY7 | 345 | 15.3093 | 15.3093 | 0
GEN-2019-065 | 04 SOUTHEAST | 515599 | G07621119-20 | 345 | 13.4849 | 13.4849 | 0
GEN-2019-065 | 04 SOUTHEAST | 515852 | DGRASSE7 | 345 | 15.3179 | 15.3179 | 0
GEN-2019-065 | 04 SOUTHEAST | 515864 | CMTRYRD4 | 138 | 6.4981 | 6.4981 | 0
GEN-2019-065 | 04 SOUTHEAST | 515961 | GUTHRIE7 | 345 | 12.8816 | 12.8816 | 0
GEN-2019-065 | 04 SOUTHEAST | 515980 | MNCWND57 | 345 | 7.1657 | 7.1657 | 0
GEN-2019-065 | 04 SOUTHEAST | 515990 | SKELTON7 | 345 | 4.5043 | 4.5043 | 0
GEN-2019-065 | 04 SOUTHEAST | 516010 | PINTAIL7 | 345 | 16.6869 | 16.6869 | 0
GEN-2019-065 | 04 SOUTHEAST | 516106 | BOBCAT 7 | 345 | 15.796 | 15.796 | 0
GEN-2019-065 | 04 SOUTHEAST | 520814 | ANADARK4 | 138 | 37.3056 | 37.3056 | 0
GEN-2019-065 | 04 SOUTHEAST | 520893 | EL RENO4 | 138 | 14.2059 | 14.2059 | 0
GEN-2019-065 | 04 SOUTHEAST | 521089 | WASHITA4 | 138 | 30.8551 | 30.855 | 0.0001
GEN-2019-065 | 04 SOUTHEAST | 587230 | GEN-2016-037 | 345 | 9.6646 | 9.6646 | 0
GEN-2019-065 | 04 SOUTHEAST | 587740 | GEN-2016-091 | 345 | 11.1551 | 11.155 | 0.0001
GEN-2019-065 | 04 SOUTHEAST | 587770 | GEN-2016-095 | 345 | 11.4525 | 11.4525 | 0
GEN-2019-065 | 04 SOUTHEAST | 587950 | GEN-2016-119 | 345 | 9.0139 | 9.0139 | 0
GEN-2019-065 | 04 SOUTHEAST | 588839 | FIREWHL-TAP | 345 | 20.1846 | 20.1845 | 0.0001
GEN-2019-065 | 04 SOUTHEAST | 755000 | WWDBORDT | 345 | 12.2648 | 12.2648 | 0
GEN-2019-065 | 04 SOUTHEAST | 761125 | GEN-2017-152 | 138 | 6.4396 | 6.4396 | 0
GEN-2019-065 | 04 SOUTHEAST | 762321 | GEN-2017-164 | 345 | 11.1781 | 11.1781 | 0
GEN-2019-065 | 04 SOUTHEAST | 763527 | GEN-2019-012 | 345 | 19.3711 | 19.3711 | 0
GEN-2019-065 | 04 SOUTHEAST | 900002 | TRAVERSE-2 | 345 | 5.5654 | 5.5654 | 0
GEN-2019-065 | 04 SOUTHEAST | 300136 | 4MEMORALT | 138 | 21.4309 | 21.4309 | 0
GEN-2019-065 | 04 SOUTHEAST | 509755 | WEKIWA-7 | 345 | 22.3506 | 22.3506 | 0
GEN-2019-065 | 04 SOUTHEAST | 509773 | RSS T1 4 | 138 | 51.5303 | 51.5303 | 0
GEN-2019-065 | 04 SOUTHEAST | 509807 | ONETA--7 | 345 | 29.2478 | 29.2478 | 0
GEN-2019-065 | 04 SOUTHEAST | 509834 | COGENT 7 | 345 | 29.7975 | 29.7975 | 0
GEN-2019-065 | 04 SOUTHEAST | 509870 | SAPLPRD7 | 345 | 22.7944 | 22.7944 | 0
GEN-2019-065 | 04 SOUTHEAST | 509875 | RSS T2 4 | 138 | 52.4475 | 52.4475 | 0
GEN-2019-065 | 04 SOUTHEAST | 510911 | VALIANT7 | 345 | 16.6284 | 16.6254 | 0.003
GEN-2019-065 | 04 SOUTHEAST | 510925 | KIOWA 7 | 345 | 16.1028 | 16.1022 | 0.0006
GEN-2019-065 | 04 SOUTHEAST | 511449 | CORNVIL4 | 138 | 15.8854 | 15.8854 | 0
GEN-2019-065 | 04 SOUTHEAST | 511456 | O.K.U.-7 | 345 | 6.3254 | 6.3254 | 0
GEN-2019-065 | 04 SOUTHEAST | 511467 | L.E.S.-4 | 138 | 25.3857 | 25.3857 | 0
GEN-2019-065 | 04 SOUTHEAST | 511477 | S.W.S.-4 | 138 | 34.1031 | 34.1031 | 0
GEN-2019-065 | 04 SOUTHEAST | 511548 | REDROCKRD4 | 138 | 8.7368 | 8.7368 | 0
GEN-2019-065 | 04 SOUTHEAST | 511557 | CHISHOLM6 | 230 | 12.1566 | 12.1566 | 0
GEN-2019-065 | 04 SOUTHEAST | 511573 | REDBDPLN4 | 138 | 4.0454 | 4.0454 | 0
GEN-2019-065 | 04 SOUTHEAST | 514510 | BURGETT4 | 138 | 23.0882 | 23.0882 | 0
GEN-2019-065 | 04 SOUTHEAST | 514708 | OTTER 4 | 138 | 8.6952 | 8.6952 | 0
GEN-2019-065 | 04 SOUTHEAST | 514709 | FRMNTAP4 | 138 | 17.9839 | 17.9839 | 0
GEN-2019-065 | 04 SOUTHEAST | 514711 | WAUKOTP4 | 138 | 15.7289 | 15.7289 | 0
GEN-2019-065 | 04 SOUTHEAST | 514733 | MARSHL 4 | 138 | 7.9487 | 7.9487 | 0
GEN-2019-065 | 04 SOUTHEAST | 514785 | WOODWRD4 | 138 | 13.1123 | 13.1123 | 0
GEN-2019-065 | 04 SOUTHEAST | 514796 | IODINE-4 | 138 | 7.3201 | 7.3201 | 0
GEN-2019-065 | 04 SOUTHEAST | 514802 | SOONER 4 | 138 | 30.9526 | 30.9526 | 0
GEN-2019-065 | 04 SOUTHEAST | 514809 | JOHNCO 7 | 345 | 10.9329 | 10.9328 | 0.0001
GEN-2019-065 | 04 SOUTHEAST | 514811 | OKARCHE2 | 69 | 3.6396 | 3.6396 | 0
GEN-2019-065 | 04 SOUTHEAST | 514816 | YUKON 2 | 69 | 7.3067 | 7.3067 | 0
GEN-2019-065 | 04 SOUTHEAST | 514822 | SOUTHRD4 | 138 | 4.5674 | 4.5674 | 0
GEN-2019-065 | 04 SOUTHEAST | 514829 | PINE ST4 | 138 | 12.4063 | 12.4063 | 0
GEN-2019-065 | 04 SOUTHEAST | 514833 | DANFRTH4 | 138 | 26.5387 | 26.5387 | 0
GEN-2019-065 | 04 SOUTHEAST | 514842 | CHTWOOD4 | 138 | 21.1353 | 21.1353 | 0
GEN-2019-065 | 04 SOUTHEAST | 514848 | HEFNER 4 | 138 | 24.8822 | 24.8822 | 0
GEN-2019-065 | 04 SOUTHEAST | 514850 | SKYLINE4 | 138 | 32.6292 | 32.6292 | 0
GEN-2019-065 | 04 SOUTHEAST | 514860 | MSTANG 2 | 69 | 21.8758 | 21.8758 | 0
GEN-2019-065 | 04 SOUTHEAST | 514865 | COUNCIL4 | 138 | 29.7097 | 29.7097 | 0
GEN-2019-065 | 04 SOUTHEAST | 514887 | WESTMOR4 | 138 | 29.4809 | 29.4808 | 0.0001
GEN-2019-065 | 04 SOUTHEAST | 514892 | DAYTON 4 | 138 | 26.1471 | 26.1471 | 0
GEN-2019-065 | 04 SOUTHEAST | 514904 | WESTHSE4 | 138 | 19.2641 | 19.2641 | 0
GEN-2019-065 | 04 SOUTHEAST | 514920 | SW 5TH 4 | 138 | 30.2903 | 30.2903 | 0
GEN-2019-065 | 04 SOUTHEAST | 514930 | OAKTRET4 | 138 | 21.4074 | 21.4074 | 0
GEN-2019-065 | 04 SOUTHEAST | 514932 | MLENIUM4 | 138 | 20.5712 | 20.5712 | 0
GEN-2019-065 | 04 SOUTHEAST | 514941 | HSL 4 | 138 | 42.6129 | 42.6129 | 0
GEN-2019-065 | 04 SOUTHEAST | 514948 | CEDARLN4 | 138 | 23.7441 | 23.7441 | 0
GEN-2019-065 | 04 SOUTHEAST | 514993 | SE15TH 4 | 138 | 15.3595 | 15.3595 | 0
GEN-2019-065 | 04 SOUTHEAST | 514994 | TINKER54 | 138 | 14.0119 | 14.0118 | 0.0001
GEN-2019-065 | 04 SOUTHEAST | 515055 | MAUD 4 | 138 | 20.1325 | 20.1324 | 0.0001
GEN-2019-065 | 04 SOUTHEAST | 515100 | PAOLI- 4 | 138 | 10.3088 | 10.3088 | 0
GEN-2019-065 | 04 SOUTHEAST | 515224 | MUSKOGE7 | 345 | 28.6414 | 28.6414 | 0
GEN-2019-065 | 04 SOUTHEAST | 515235 | PECANCK7 | 345 | 22.1253 | 22.1253 | 0
GEN-2019-065 | 04 SOUTHEAST | 515373 | LBRTYLK4 | 138 | 14.2037 | 14.2037 | 0
GEN-2019-065 | 04 SOUTHEAST | 515377 | CRESENT4 | 138 | 10.6382 | 10.6382 | 0
GEN-2019-065 | 04 SOUTHEAST | 515380 | INDIANH4 | 138 | 28.6703 | 28.6703 | 0
GEN-2019-065 | 04 SOUTHEAST | 515394 | KEENAN 4 | 138 | 8.9414 | 8.9414 | 0
GEN-2019-065 | 04 SOUTHEAST | 515398 | OUSPRT 4 | 138 | 9.528 | 9.528 | 0
GEN-2019-065 | 04 SOUTHEAST | 515422 | C-RIVER7 | 345 | 11.6454 | 11.6453 | 0.0001
GEN-2019-065 | 04 SOUTHEAST | 515425 | WWDPST 4 | 138 | 17.7977 | 17.7977 | 0
GEN-2019-065 | 04 SOUTHEAST | 515457 | AIRDEPT4 | 138 | 20.3553 | 20.3553 | 0
GEN-2019-065 | 04 SOUTHEAST | 515458 | BORDER 7 | 345 | 8.2517 | 8.2517 | 0
GEN-2019-065 | 04 SOUTHEAST | 515467 | WHITESB4 | 138 | 15.6824 | 15.6824 | 0
GEN-2019-065 | 04 SOUTHEAST | 515468 | FAIRFLD4 | 138 | 23.3916 | 23.3916 | 0
GEN-2019-065 | 04 SOUTHEAST | 515472 | TLBEART4 | 138 | 8.9137 | 8.9137 | 0
GEN-2019-065 | 04 SOUTHEAST | 515477 | CHSHLMV7 | 345 | 13.1796 | 13.1796 | 0
GEN-2019-065 | 04 SOUTHEAST | 515531 | VANOSTP4 | 138 | 13.3128 | 13.3128 | 0
GEN-2019-065 | 04 SOUTHEAST | 515543 | RENFROW7 | 345 | 12.8614 | 12.8614 | 0
GEN-2019-065 | 04 SOUTHEAST | 515576 | RANCHRD7 | 345 | 15.0658 | 15.0658 | 0
GEN-2019-065 | 04 SOUTHEAST | 515590 | PALDR2W7 | 345 | 12.8669 | 12.8669 | 0
GEN-2019-065 | 04 SOUTHEAST | 515618 | BALKOW 7 | 345 | 12.5807 | 12.5807 | 0
GEN-2019-065 | 04 SOUTHEAST | 515625 | KNGINDT2 | 69 | 3.4615 | 3.4615 | 0
GEN-2019-065 | 04 SOUTHEAST | 515677 | BADGER 7 | 345 | 13.7821 | 13.7821 | 0
GEN-2019-065 | 04 SOUTHEAST | 515825 | GRTWSRN7 | 345 | 9.0702 | 9.0702 | 0
GEN-2019-065 | 04 SOUTHEAST | 515853 | DGRASSE4 | 138 | 17.0745 | 17.0745 | 0
GEN-2019-065 | 04 SOUTHEAST | 515894 | THUNDER7 | 345 | 10.9745 | 10.9745 | 0
GEN-2019-065 | 04 SOUTHEAST | 515931 | GEARYTP4 | 138 | 5.4324 | 5.4324 | 0
GEN-2019-065 | 04 SOUTHEAST | 515933 | MLCLMRD4 | 138 | 8.7599 | 8.7599 | 0
GEN-2019-065 | 04 SOUTHEAST | 515951 | PERSIMN7 | 345 | 11.0796 | 11.0796 | 0
GEN-2019-065 | 04 SOUTHEAST | 515977 | LKKONWA4 | 138 | 39.5128 | 39.5127 | 0.0001
GEN-2019-065 | 04 SOUTHEAST | 516019 | KINGWD 7 | 345 | 16.6292 | 16.6292 | 0
GEN-2019-065 | 04 SOUTHEAST | 516146 | 25MILE 7 | 345 | 11.1221 | 11.1221 | 0
GEN-2019-065 | 04 SOUTHEAST | 520412 | MUSTANG4 | 138 | 7.0211 | 7.0211 | 0
GEN-2019-065 | 04 SOUTHEAST | 520422 | SEQUOYAHJ4 | 138 | 26.2586 | 26.2586 | 0
GEN-2019-065 | 04 SOUTHEAST | 520508 | CLVLDSW4 | 138 | 12.6695 | 12.6695 | 0
GEN-2019-065 | 04 SOUTHEAST | 520810 | ANADARK2 | 69 | 14.4688 | 14.4688 | 0
GEN-2019-065 | 04 SOUTHEAST | 520899 | SCOTTSW4 | 138 | 11.6838 | 11.6838 | 0
GEN-2019-065 | 04 SOUTHEAST | 520917 | FRNKLNS4 | 138 | 29.592 | 29.592 | 0
GEN-2019-065 | 04 SOUTHEAST | 520923 | GEORGIA4 | 138 | 18.7095 | 18.7095 | 0
GEN-2019-065 | 04 SOUTHEAST | 521017 | ONEY 4 | 138 | 11.0996 | 11.0996 | 0
GEN-2019-065 | 04 SOUTHEAST | 521031 | POCASET4 | 138 | 8.1012 | 8.1012 | 0
GEN-2019-065 | 04 SOUTHEAST | 521088 | WASHITA2 | 69 | 9.083 | 9.083 | 0
GEN-2019-065 | 04 SOUTHEAST | 521103 | SLKHILLS 4 | 138 | 6.45 | 6.45 | 0
GEN-2019-065 | 04 SOUTHEAST | 521129 | CHERRYRD 4 | 138 | 5.6562 | 5.6562 | 0
GEN-2019-065 | 04 SOUTHEAST | 523097 | HITCHLAND 7 | 345 | 14.9713 | 14.9713 | 0
GEN-2019-065 | 04 SOUTHEAST | 539801 | THISTLE7 | 345 | 16.6662 | 16.6662 | 0
GEN-2019-065 | 04 SOUTHEAST | 560035 | GRAPEVINE | 345 | 6.4589 | 6.4589 | 0
GEN-2019-065 | 04 SOUTHEAST | 560056 | G15-066T | 345 | 19.1787 | 19.1787 | 0
GEN-2019-065 | 04 SOUTHEAST | 585410 | GREAT_WESTRN | 345 | 9.7415 | 9.7415 | 0
GEN-2019-065 | 04 SOUTHEAST | 585430 | PRSIMN_CRK1 | 345 | 11.7445 | 11.7445 | 0
GEN-2019-065 | 04 SOUTHEAST | 587955 | GEN2016-119B | 345 | 7.7605 | 7.7605 | 0
GEN-2019-065 | 04 SOUTHEAST | 588039 | G16133G16146 | 345 | 32.1585 | 32.1585 | 0
GEN-2019-065 | 04 SOUTHEAST | 588190 | GEN-2016-128 | 345 | 4.3057 | 4.3057 | 0
GEN-2019-065 | 04 SOUTHEAST | 588560 | GEN-2017-011 | 345 | 12.6206 | 12.6206 | 0
GEN-2019-065 | 04 SOUTHEAST | 588720 | GEN-2017-117 | 138 | 14.2059 | 14.2059 | 0
GEN-2019-065 | 04 SOUTHEAST | 588838 | G17-092-SWYD | 345 | 20.1846 | 20.1845 | 0.0001
GEN-2019-065 | 04 SOUTHEAST | 760938 | G17-171-TAP | 345 | 12.0416 | 12.0415 | 0.0001
GEN-2019-065 | 04 SOUTHEAST | 762342 | GEN-2017-178 | 345 | 7.8339 | 7.8339 | 0
GEN-2019-065 | 04 SOUTHEAST | 762614 | GEN-2018-026 | 138 | 36.7532 | 36.7532 | 0
GEN-2019-065 | 04 SOUTHEAST | 763131 | GEN-2018-082 | 345 | 10.1533 | 10.1531 | 0.0002
GEN-2019-065 | 04 SOUTHEAST | 763318 | GEN-2018-115 | 345 | 14.5675 | 14.5675 | 0
GEN-2019-065 | 04 SOUTHEAST | 900003 | TRAVERSE1 | 345 | 5.1578 | 5.1578 | 0
GEN-2006-026_GEN-2019-004 | 05 SOUTHWEST | 527891 | HOBBS_INT 3 | 115 | 33.0667 | 24.115 | 8.9517
GEN-2006-026_GEN-2019-004 | 05 SOUTHWEST | 527864 | CUNNINHAM 3 | 115 | 28.6112 | 22.7845 | 5.8267
GEN-2006-026_GEN-2019-004 | 05 SOUTHWEST | 527894 | HOBBS_INT 6 | 230 | 19.4767 | 15.8476 | 3.6291
GEN-2006-026_GEN-2019-004 | 05 SOUTHWEST | 528333 | LE-WEST_SUB3 | 115 | 8.9508 | 8.5536 | 0.3972
GEN-2006-026_GEN-2019-004 | 05 SOUTHWEST | 528355 | MADDOX 3 | 115 | 27.5212 | 22.2001 | 5.3211
GEN-2006-026_GEN-2019-004 | 05 SOUTHWEST | 528433 | BENSING 3 | 115 | 8.0843 | 7.661 | 0.4233
GEN-2006-026_GEN-2019-004 | 05 SOUTHWEST | 528434 | MILLEN_TPW 3 | 115 | 11.851 | 10.7541 | 1.0969
GEN-2006-026_GEN-2019-004 | 05 SOUTHWEST | 527028 | INK_BASIN 6 | 230 | 11.2413 | 10.7427 | 0.4986
GEN-2006-026_GEN-2019-004 | 05 SOUTHWEST | 527363 | HIGG 3 | 115 | 10.3839 | 10.0111 | 0.3728
GEN-2006-026_GEN-2019-004 | 05 SOUTHWEST | 527867 | CUNNIGHM_S 6 | 230 | 17.5364 | 15.0062 | 2.5302
GEN-2006-026_GEN-2019-004 | 05 SOUTHWEST | 527896 | HOBBS_INT 7 | 345 | 12.0143 | 11.1016 | 0.9127
GEN-2006-026_GEN-2019-004 | 05 SOUTHWEST | 528334 | LE-NRTH_INT3 | 115 | 8.8908 | 8.5051 | 0.3857
GEN-2006-026_GEN-2019-004 | 05 SOUTHWEST | 528348 | BUCKEYE_TP 3 | 115 | 8.2953 | 7.7524 | 0.5429
GEN-2006-026_GEN-2019-004 | 05 SOUTHWEST | 528353 | MADDOXG23 3 | 115 | 27.5212 | 22.2001 | 5.3211
GEN-2006-026_GEN-2019-004 | 05 SOUTHWEST | 528392 | PEARLE 3 | 115 | 6.3678 | 6.0928 | 0.275
GEN-2006-026_GEN-2019-004 | 05 SOUTHWEST | 528394 | QUAHADA 3 | 115 | 8.071 | 7.7423 | 0.3287
GEN-2006-026_GEN-2019-004 | 05 SOUTHWEST | 528435 | MILLEN 3 | 115 | 11.851 | 10.7541 | 1.0969
GEN-2006-026_GEN-2019-004 | 05 SOUTHWEST | 528436 | MILLEN_TPE 3 | 115 | 11.851 | 10.7541 | 1.0969
GEN-2006-026_GEN-2019-004 | 05 SOUTHWEST | 528491 | MONUMENT 3 | 115 | 15.8502 | 14.049 | 1.8012
GEN-2006-026_GEN-2019-004 | 05 SOUTHWEST | 528568 | MONUMNT_TP 3 | 115 | 10.3926 | 9.6183 | 0.7743
GEN-2006-026_GEN-2019-004 | 05 SOUTHWEST | 528604 | ANDREWS 6 | 230 | 6.0764 | 5.6946 | 0.3818
GEN-2006-026_GEN-2019-004 | 05 SOUTHWEST | 762442 | G18-004-TAP | 115 | 23.6999 | 19.6972 | 4.0027
GEN-2006-026_GEN-2019-004 | 05 SOUTHWEST | 526935 | YOAKUM 6 | 230 | 19.6825 | 19.0742 | 0.6083
GEN-2006-026_GEN-2019-004 | 05 SOUTHWEST | 526936 | YOAKUM_345 | 345 | 9.9314 | 9.6208 | 0.3106
GEN-2006-026_GEN-2019-004 | 05 SOUTHWEST | 527027 | INK_BASIN 3 | 115 | 13.258 | 12.9085 | 0.3495
GEN-2006-026_GEN-2019-004 | 05 SOUTHWEST | 527284 | RUSSELL 3 | 115 | 9.2203 | 8.9254 | 0.2949
GEN-2006-026_GEN-2019-004 | 05 SOUTHWEST | 527286 | HIGGEAST 3 | 115 | 10.2075 | 9.8704 | 0.3371
GEN-2006-026_GEN-2019-004 | 05 SOUTHWEST | 527362 | JOHNSON_DRW3 | 115 | 10.8926 | 10.4235 | 0.4691
GEN-2006-026_GEN-2019-004 | 05 SOUTHWEST | 527656 | CROSSROADS 7 | 345 | 11.539 | 11.21 | 0.329
GEN-2006-026_GEN-2019-004 | 05 SOUTHWEST | 527865 | CUNNIGHM_N 6 | 230 | 17.5364 | 15.0062 | 2.5302
GEN-2006-026_GEN-2019-004 | 05 SOUTHWEST | 527965 | KIOWA 7 | 345 | 8.82 | 8.2965 | 0.5235
GEN-2006-026_GEN-2019-004 | 05 SOUTHWEST | 528027 | RDRUNNER 7 | 345 | 8.6815 | 8.1731 | 0.5084
GEN-2006-026_GEN-2019-004 | 05 SOUTHWEST | 528317 | ENRON_TP 3 | 115 | 6.7901 | 6.5443 | 0.2458
GEN-2006-026_GEN-2019-004 | 05 SOUTHWEST | 528325 | LE-WAITS 3 | 115 | 8.9967 | 8.7752 | 0.2215
GEN-2006-026_GEN-2019-004 | 05 SOUTHWEST | 528385 | BUCKEYE 3 | 115 | 7.4564 | 7.0153 | 0.4411
GEN-2006-026_GEN-2019-004 | 05 SOUTHWEST | 528396 | XTO_BIGEDDY3 | 115 | 8.8101 | 8.4997 | 0.3104
GEN-2006-026_GEN-2019-004 | 05 SOUTHWEST | 528399 | LEA_NATIONL3 | 115 | 6.8298 | 6.5816 | 0.2482
GEN-2006-026_GEN-2019-004 | 05 SOUTHWEST | 528422 | DCP_ZIA TP 3 | 115 | 6.9962 | 6.7485 | 0.2477
GEN-2006-026_GEN-2019-004 | 05 SOUTHWEST | 528442 | NE_HOBBS 3 | 115 | 12.104 | 11.0226 | 1.0814
GEN-2006-026_GEN-2019-004 | 05 SOUTHWEST | 528463 | SANGER_SW 3 | 115 | 16.2427 | 14.3314 | 1.9113
GEN-2006-026_GEN-2019-004 | 05 SOUTHWEST | 528498 | W_HOBBS 3 | 115 | 11.83 | 10.8891 | 0.9409
GEN-2006-026_GEN-2019-004 | 05 SOUTHWEST | 528581 | BYRD_TP 3 | 115 | 8.0775 | 7.6397 | 0.4378
GEN-2006-026_GEN-2019-004 | 05 SOUTHWEST | 528602 | ANDREWS 3 | 115 | 9.8058 | 9.3236 | 0.4822
GEN-2006-026_GEN-2019-004 | 05 SOUTHWEST | 528618 | LE-LOVINTON2 | 69 | 6.8279 | 6.6873 | 0.1406
GEN-2006-026_GEN-2019-004 | 05 SOUTHWEST | 528627 | LE-TXACO_TP3 | 115 | 7.1688 | 6.7652 | 0.4036
GEN-2006-026_GEN-2019-004 | 05 SOUTHWEST | 762438 | GEN-2018-004 | 115 | 23.3418 | 19.451 | 3.8908
GEN-2006-026_GEN-2019-004 | 05 SOUTHWEST | 525549 | TOLK 7 | 345 | 15.0276 | 14.9094 | 0.1182
GEN-2006-026_GEN-2019-004 | 05 SOUTHWEST | 525586 | NEEDMORE 6 | 230 | 11.0214 | 10.9831 | 0.0383
GEN-2006-026_GEN-2019-004 | 05 SOUTHWEST | 525832 | TUCO_INT 7 | 345 | 14.0745 | 14.0243 | 0.0502
GEN-2006-026_GEN-2019-004 | 05 SOUTHWEST | 526460 | AMOCO_SS 6 | 230 | 10.1771 | 10.1218 | 0.0553
GEN-2006-026_GEN-2019-004 | 05 SOUTHWEST | 526934 | YOAKUM 3 | 115 | 19.2326 | 18.9623 | 0.2703
GEN-2006-026_GEN-2019-004 | 05 SOUTHWEST | 527009 | BRU_SUB 6 | 230 | 15.6513 | 15.3142 | 0.3371
GEN-2006-026_GEN-2019-004 | 05 SOUTHWEST | 527030 | ALRDCRTZ_TP3 | 115 | 12.2915 | 12.0361 | 0.2554
GEN-2006-026_GEN-2019-004 | 05 SOUTHWEST | 527130 | DENVER_N 3 | 115 | 22.5277 | 22.0124 | 0.5153
GEN-2006-026_GEN-2019-004 | 05 SOUTHWEST | 527149 | MUSTANG 6 | 230 | 17.9238 | 17.5632 | 0.3606
GEN-2006-026_GEN-2019-004 | 05 SOUTHWEST | 527325 | OXY_WSEM_TP3 | 115 | 9.309 | 9.1294 | 0.1796
GEN-2006-026_GEN-2019-004 | 05 SOUTHWEST | 527360 | MAPCO 3 | 115 | 10.6414 | 10.1936 | 0.4478
GEN-2006-026_GEN-2019-004 | 05 SOUTHWEST | 527610 | SAGA_SCOL 7 | 345 | 10.2321 | 9.9868 | 0.2453
GEN-2006-026_GEN-2019-004 | 05 SOUTHWEST | 527655 | RSVLT_CC_E 7 | 345 | 10.0154 | 9.7762 | 0.2392
GEN-2006-026_GEN-2019-004 | 05 SOUTHWEST | 527799 | EDDY_NORTH 6 | 230 | 9.402 | 8.9974 | 0.4046
GEN-2006-026_GEN-2019-004 | 05 SOUTHWEST | 527802 | EDDY_CNTY 7 | 345 | 7.3273 | 7.0035 | 0.3238
GEN-2006-026_GEN-2019-004 | 05 SOUTHWEST | 527930 | PCA 3 | 115 | 11.9796 | 11.514 | 0.4656
GEN-2006-026_GEN-2019-004 | 05 SOUTHWEST | 527963 | POTASH_JCT 6 | 230 | 7.464 | 7.1077 | 0.3563
GEN-2006-026_GEN-2019-004 | 05 SOUTHWEST | 527966 | KIOWA 3 | 115 | 17.1508 | 16.3264 | 0.8244
GEN-2006-026_GEN-2019-004 | 05 SOUTHWEST | 528015 | PHANTOM 7 | 345 | 5.675 | 5.4493 | 0.2257
GEN-2006-026_GEN-2019-004 | 05 SOUTHWEST | 528025 | RDRUNNER 3 | 115 | 13.7957 | 13.3106 | 0.4851
GEN-2006-026_GEN-2019-004 | 05 SOUTHWEST | 528185 | N_LOVING 7 | 345 | 6.5496 | 6.2537 | 0.2959
GEN-2006-026_GEN-2019-004 | 05 SOUTHWEST | 528318 | ENRON 3 | 115 | 5.9058 | 5.7191 | 0.1867
GEN-2006-026_GEN-2019-004 | 05 SOUTHWEST | 528341 | LE-SANANDRS3 | 115 | 6.4474 | 6.1229 | 0.3245
GEN-2006-026_GEN-2019-004 | 05 SOUTHWEST | 528404 | SUMMIT_3 | 115 | 5.6643 | 5.4928 | 0.1715
GEN-2006-026_GEN-2019-004 | 05 SOUTHWEST | 528413 | TAYLOR 3 | 115 | 14.7335 | 13.3016 | 1.4319
GEN-2006-026_GEN-2019-004 | 05 SOUTHWEST | 528420 | ZIA 3 | 115 | 6.5376 | 6.3211 | 0.2165
GEN-2006-026_GEN-2019-004 | 05 SOUTHWEST | 528423 | DCP_ZIA 3 | 115 | 6.6343 | 6.4109 | 0.2234
GEN-2006-026_GEN-2019-004 | 05 SOUTHWEST | 528484 | SW_4J44 3 | 115 | 11.263 | 10.4077 | 0.8553
GEN-2006-026_GEN-2019-004 | 05 SOUTHWEST | 528533 | DRINKARD_TP3 | 115 | 7.5628 | 7.2359 | 0.3269
GEN-2006-026_GEN-2019-004 | 05 SOUTHWEST | 528554 | COOPER_RNCH3 | 115 | 6.7042 | 6.4314 | 0.2728
GEN-2006-026_GEN-2019-004 | 05 SOUTHWEST | 528575 | OXYPERMIAN 3 | 115 | 15.5727 | 13.8207 | 1.752
GEN-2006-026_GEN-2019-004 | 05 SOUTHWEST | 528582 | BYRD 3 | 115 | 7.4531 | 7.0791 | 0.374
GEN-2006-026_GEN-2019-004 | 05 SOUTHWEST | 528603 | NA_ENRICH 3 | 115 | 9.7292 | 9.2586 | 0.4706
GEN-2006-026_GEN-2019-004 | 05 SOUTHWEST | 528617 | LE-WAITS 2 | 69 | 3.5458 | 3.5248 | 0.021
GEN-2006-026_GEN-2019-004 | 05 SOUTHWEST | 528638 | LE-SAUNDRTP2 | 69 | 3.4902 | 3.4532 | 0.037
GEN-2006-026_GEN-2019-004 | 05 SOUTHWEST | 528675 | LE-FAMARISS2 | 69 | 3.2709 | 3.239 | 0.0319
GEN-2006-026_GEN-2019-004 | 05 SOUTHWEST | 528677 | LE-DSYSRPOI2 | 69 | 5.4319 | 5.34 | 0.0919
GEN-2006-026_GEN-2019-004 | 05 SOUTHWEST | 528679 | LE-TATMGOAB2 | 69 | 3.8696 | 3.8286 | 0.041
GEN-2006-026_GEN-2019-004 | 05 SOUTHWEST | 528699 | LE-GRAY 2 | 69 | 3.2971 | 3.2648 | 0.0323
GEN-2006-026_GEN-2019-004 | 05 SOUTHWEST | 528775 | LE-ERF 3 | 115 | 10.8926 | 10.4235 | 0.4691
GEN-2006-026_GEN-2019-004 | 05 SOUTHWEST | 528792 | LE-TEXACO 3 | 115 | 6.4853 | 6.1534 | 0.3319
GEN-2006-026_GEN-2019-004 | 05 SOUTHWEST | 588460 | A16-008SUB | 115 | 13.258 | 12.9085 | 0.3495
GEN-2006-026_GEN-2019-004 | 05 SOUTHWEST | 763516 | GEN-2019-011 | 345 | 9.2852 | 9.0131 | 0.2721
GEN-2006-026_GEN-2019-004 | 05 SOUTHWEST | 523961 | POTTER_CO 7 | 345 | 11.6631 | 11.6556 | 0.0075
GEN-2006-026_GEN-2019-004 | 05 SOUTHWEST | 525531 | TOLK 6 | 230 | 31.4946 | 31.2945 | 0.2001
GEN-2006-026_GEN-2019-004 | 05 SOUTHWEST | 525585 | BLUECLDPOI 6 | 230 | 11.0214 | 10.9831 | 0.0383
GEN-2006-026_GEN-2019-004 | 05 SOUTHWEST | 525830 | TUCO_INT 6 | 230 | 21.9895 | 21.9214 | 0.0681
GEN-2006-026_GEN-2019-004 | 05 SOUTHWEST | 525850 | ELK_CT1 | 345 | 13.9398 | 13.8906 | 0.0492
GEN-2006-026_GEN-2019-004 | 05 SOUTHWEST | 526435 | SUNDOWN 6 | 230 | 11.7438 | 11.6845 | 0.0593
GEN-2006-026_GEN-2019-004 | 05 SOUTHWEST | 526736 | TERRY_CNTY 3 | 115 | 10.6679 | 10.6212 | 0.0467
GEN-2006-026_GEN-2019-004 | 05 SOUTHWEST | 526784 | AMOCOWASSON6 | 230 | 15.6353 | 15.3405 | 0.2948
GEN-2006-026_GEN-2019-004 | 05 SOUTHWEST | 526792 | PRENTICE 3 | 115 | 6.0286 | 6.0092 | 0.0194
GEN-2006-026_GEN-2019-004 | 05 SOUTHWEST | 526928 | PLAINS_INT 3 | 115 | 10.0196 | 9.9539 | 0.0657
GEN-2006-026_GEN-2019-004 | 05 SOUTHWEST | 527010 | OXYBRU 6 | 230 | 15.5052 | 15.1742 | 0.331
GEN-2006-026_GEN-2019-004 | 05 SOUTHWEST | 527011 | XTO_MAHONEY6 | 230 | 15.3578 | 15.0479 | 0.3099
GEN-2006-026_GEN-2019-004 | 05 SOUTHWEST | 527024 | ALLRED_SUB 3 | 115 | 10.7765 | 10.5801 | 0.1964
GEN-2006-026_GEN-2019-004 | 05 SOUTHWEST | 527033 | XTO_CORNEL+3 | 115 | 12.4096 | 12.1676 | 0.242
GEN-2006-026_GEN-2019-004 | 05 SOUTHWEST | 527041 | ARCO_TP 3 | 115 | 13.6807 | 13.5237 | 0.157
GEN-2006-026_GEN-2019-004 | 05 SOUTHWEST | 527080 | EL_PASO 3 | 115 | 16.4487 | 16.2051 | 0.2436
GEN-2006-026_GEN-2019-004 | 05 SOUTHWEST | 527125 | DENVER_CTY 2 | 69 | 8.7911 | 8.7425 | 0.0486
GEN-2006-026_GEN-2019-004 | 05 SOUTHWEST | 527136 | DENVER_S 3 | 115 | 22.5277 | 22.0124 | 0.5153
GEN-2006-026_GEN-2019-004 | 05 SOUTHWEST | 527146 | MUSTANG 3 | 115 | 24.0628 | 23.5858 | 0.477
GEN-2006-026_GEN-2019-004 | 05 SOUTHWEST | 527151 | GS-MUSTANG 6 | 230 | 17.9238 | 17.5632 | 0.3606
GEN-2006-026_GEN-2019-004 | 05 SOUTHWEST | 527194 | LG-PLSHILL 3 | 115 | 7.9741 | 7.9326 | 0.0415
GEN-2006-026_GEN-2019-004 | 05 SOUTHWEST | 527276 | SEMINOLE 6 | 230 | 8.197 | 8.0839 | 0.1131
GEN-2006-026_GEN-2019-004 | 05 SOUTHWEST | 527300 | AM_FRAC 3 | 115 | 9.6861 | 9.3151 | 0.371
GEN-2006-026_GEN-2019-004 | 05 SOUTHWEST | 527322 | GAINES 3 | 115 | 9.4721 | 9.2944 | 0.1777
GEN-2006-026_GEN-2019-004 | 05 SOUTHWEST | 527323 | OXY_WSTSEM 3 | 115 | 6.9013 | 6.8023 | 0.099
GEN-2006-026_GEN-2019-004 | 05 SOUTHWEST | 527483 | CHAVES_CNTY6 | 230 | 4.4929 | 4.4454 | 0.0475
GEN-2006-026_GEN-2019-004 | 05 SOUTHWEST | 527599 | SAGA_SDCOL 7 | 345 | 10.2321 | 9.9868 | 0.2453
GEN-2006-026_GEN-2019-004 | 05 SOUTHWEST | 527654 | RSVLT_CC_W 7 | 345 | 8.7265 | 8.5505 | 0.176
GEN-2006-026_GEN-2019-004 | 05 SOUTHWEST | 527793 | EDDY_STH 3 | 115 | 11.9559 | 11.622 | 0.3339
GEN-2006-026_GEN-2019-004 | 05 SOUTHWEST | 527798 | EDDY_NTH 3 | 115 | 11.9559 | 11.622 | 0.3339
GEN-2006-026_GEN-2019-004 | 05 SOUTHWEST | 527929 | PCA 2 | 69 | 7.8902 | 7.7731 | 0.1171
GEN-2006-026_GEN-2019-004 | 05 SOUTHWEST | 527948 | CV-LUSK_TP 3 | 115 | 4.2849 | 4.2237 | 0.0612
GEN-2006-026_GEN-2019-004 | 05 SOUTHWEST | 527962 | POTASH_JCT 3 | 115 | 17.1771 | 16.3424 | 0.8347
GEN-2006-026_GEN-2019-004 | 05 SOUTHWEST | 528013 | PHANTOM 3 | 115 | 13.0934 | 12.681 | 0.4124
GEN-2006-026_GEN-2019-004 | 05 SOUTHWEST | 528018 | RED_BLUFF 3 | 115 | 10.2086 | 9.9403 | 0.2683
GEN-2006-026_GEN-2019-004 | 05 SOUTHWEST | 528024 | RR_SVC_HV 3 | 115 | 13.7957 | 13.3106 | 0.4851
GEN-2006-026_GEN-2019-004 | 05 SOUTHWEST | 528040 | BATTLE_AXE 3 | 115 | 3.2123 | 3.1855 | 0.0268
GEN-2006-026_GEN-2019-004 | 05 SOUTHWEST | 528095 | 7-RIVERS 6 | 230 | 6.3874 | 6.1735 | 0.2139
GEN-2006-026_GEN-2019-004 | 05 SOUTHWEST | 528160 | CARLSBAD 3 | 115 | 11.3979 | 11.043 | 0.3549
GEN-2006-026_GEN-2019-004 | 05 SOUTHWEST | 528179 | PECOS 6 | 230 | 6.6719 | 6.4121 | 0.2598
GEN-2006-026_GEN-2019-004 | 05 SOUTHWEST | 528182 | NORTH_LOVNG3 | 115 | 12.4183 | 12.0552 | 0.3631
GEN-2006-026_GEN-2019-004 | 05 SOUTHWEST | 528223 | CHINA_DRAW 7 | 345 | 5.8229 | 5.5865 | 0.2364
GEN-2006-026_GEN-2019-004 | 05 SOUTHWEST | 528230 | AGAVE_RHILL3 | 115 | 12.3643 | 11.9734 | 0.3909
GEN-2006-026_GEN-2019-004 | 05 SOUTHWEST | 528231 | AGAVE_RHIL23 | 115 | 11.6311 | 11.2847 | 0.3464
GEN-2006-026_GEN-2019-004 | 05 SOUTHWEST | 528239 | CUSTERMTN 3 | 115 | 7.7101 | 7.5153 | 0.1948
GEN-2006-026_GEN-2019-004 | 05 SOUTHWEST | 528406 | MALJMAR1&2 3 | 115 | 3.2168 | 3.1642 | 0.0526
GEN-2006-026_GEN-2019-004 | 05 SOUTHWEST | 528449 | W_BENDER 3 | 115 | 15.0354 | 13.4083 | 1.6271
GEN-2006-026_GEN-2019-004 | 05 SOUTHWEST | 528470 | E_SANGER 3 | 115 | 12.824 | 11.7274 | 1.0966
GEN-2006-026_GEN-2019-004 | 05 SOUTHWEST | 528480 | OXY_S_HOBBS3 | 115 | 10.6512 | 9.8842 | 0.767
GEN-2006-026_GEN-2019-004 | 05 SOUTHWEST | 528512 | EUNICE 3 | 115 | 5.8934 | 5.6933 | 0.2001
GEN-2006-026_GEN-2019-004 | 05 SOUTHWEST | 528552 | OIL_CENTER 3 | 115 | 6.2088 | 5.9929 | 0.2159
GEN-2006-026_GEN-2019-004 | 05 SOUTHWEST | 528574 | OXY_NHU_RCF3 | 115 | 15.3654 | 13.6618 | 1.7036
GEN-2006-026_GEN-2019-004 | 05 SOUTHWEST | 528589 | DRINKARD 3 | 115 | 7.6615 | 7.3376 | 0.3239
GEN-2006-026_GEN-2019-004 | 05 SOUTHWEST | 528605 | TARGA 3 | 115 | 8.1629 | 7.8547 | 0.3082
GEN-2006-026_GEN-2019-004 | 05 SOUTHWEST | 528622 | LE-SANANDRS2 | 69 | 5.2198 | 5.1147 | 0.1051
GEN-2006-026_GEN-2019-004 | 05 SOUTHWEST | 528630 | LE-BUCKEYE 2 | 69 | 3.765 | 3.7148 | 0.0502
GEN-2006-026_GEN-2019-004 | 05 SOUTHWEST | 528645 | LE-BAYWAPOI2 | 69 | 2.0739 | 2.0629 | 0.011
GEN-2006-026_GEN-2019-004 | 05 SOUTHWEST | 528650 | LE-SAUNDERS2 | 69 | 1.9446 | 1.9333 | 0.0113
GEN-2006-026_GEN-2019-004 | 05 SOUTHWEST | 528667 | LE-MHOON 2 | 69 | 4.35 | 4.2864 | 0.0636
GEN-2006-026_GEN-2019-004 | 05 SOUTHWEST | 528671 | LE-S_LOVITN2 | 69 | 3.5101 | 3.4688 | 0.0413
GEN-2006-026_GEN-2019-004 | 05 SOUTHWEST | 528678 | LE-DSYSOLAR2 | 69 | 5.4268 | 5.3351 | 0.0917
GEN-2006-026_GEN-2019-004 | 05 SOUTHWEST | 528683 | LE-MCDONALD2 | 69 | 2.2041 | 2.193 | 0.0111
GEN-2006-026_GEN-2019-004 | 05 SOUTHWEST | 528703 | LE-DENTN_TP2 | 69 | 2.5036 | 2.4854 | 0.0182
GEN-2006-026_GEN-2019-004 | 05 SOUTHWEST | 528707 | LE-DENTON 2 | 69 | 2.2163 | 2.202 | 0.0143
GEN-2006-026_GEN-2019-004 | 05 SOUTHWEST | 528714 | LE-FORT_SW 2 | 69 | 3.332 | 3.3133 | 0.0187
GEN-2006-026_GEN-2019-004 | 05 SOUTHWEST | 528759 | LE-TP51 2 | 69 | 2.3098 | 2.3009 | 0.0089
GEN-2006-026_GEN-2019-004 | 05 SOUTHWEST | 528774 | LE-ERF 2 | 69 | 4.8002 | 4.7429 | 0.0573
GEN-2006-026_GEN-2019-004 | 05 SOUTHWEST | 528779 | LE-TALLCOTN3 | 115 | 8.334 | 8.0556 | 0.2784
GEN-2006-026_GEN-2019-004 | 05 SOUTHWEST | 560022 | CRAWFISH_DR | 345 | 13.842 | 13.7944 | 0.0476
GEN-2006-026_GEN-2019-004 | 05 SOUTHWEST | 587990 | GEN-2016-121 | 115 | 13.5705 | 13.1008 | 0.4697
GEN-2006-026_GEN-2019-004 | 05 SOUTHWEST | 599960 | EPTNP-D6 | 230 | 9.402 | 8.9974 | 0.4046
GEN-2018-073 | 05 SOUTHWEST | 560022 | CRAWFISH_DR | 345 | 13.842 | 13.3171 | 0.5249
GEN-2018-073 | 05 SOUTHWEST | 515458 | BORDER 7 | 345 | 8.2517 | 8.242 | 0.0097
GEN-2018-073 | 05 SOUTHWEST | 525832 | TUCO_INT 7 | 345 | 14.0745 | 13.559 | 0.5155
GEN-2018-073 | 05 SOUTHWEST | 762216 | G17-151TAP | 345 | 8.5119 | 8.3647 | 0.1472
GEN-2018-073 | 05 SOUTHWEST | 763087 | GEN-2018-073 | 345 | 11.9423 | 11.4144 | 0.5279
GEN-2018-073 | 05 SOUTHWEST | 525830 | TUCO_INT 6 | 230 | 21.9895 | 21.604 | 0.3855
GEN-2018-073 | 05 SOUTHWEST | 525850 | ELK_CT1 | 345 | 13.9398 | 13.4349 | 0.5049
GEN-2018-073 | 05 SOUTHWEST | 526936 | YOAKUM_345 | 345 | 9.9314 | 9.9038 | 0.0276
GEN-2018-073 | 05 SOUTHWEST | 755000 | WWDBORDT | 345 | 12.2648 | 12.2552 | 0.0096
GEN-2018-073 | 05 SOUTHWEST | 762217 | GEN-2017-151 | 345 | 6.1754 | 6.1011 | 0.0743
GEN-2018-073 | 05 SOUTHWEST | 762467 | G18-015-TAP | 345 | 5.8242 | 5.802 | 0.0222
GEN-2018-073 | 05 SOUTHWEST | 511553 | CHISHOLM7 | 345 | 12.3397 | 12.3302 | 0.0095
GEN-2018-073 | 05 SOUTHWEST | 515375 | WWRDEHV7 | 345 | 22.3641 | 22.3621 | 0.002
GEN-2018-073 | 05 SOUTHWEST | 525213 | SWISHER 6 | 230 | 10.3853 | 10.3648 | 0.0205
GEN-2018-073 | 05 SOUTHWEST | 525531 | TOLK 6 | 230 | 31.4946 | 31.4549 | 0.0397
GEN-2018-073 | 05 SOUTHWEST | 525828 | TUCO_INT 3 | 115 | 19.3618 | 19.2602 | 0.1016
GEN-2018-073 | 05 SOUTHWEST | 525840 | ANTELOPE_1 6 | 230 | 21.8013 | 21.4226 | 0.3787
GEN-2018-073 | 05 SOUTHWEST | 525957 | HALE_WNDCL16 | 230 | 10.5196 | 10.4402 | 0.0794
GEN-2018-073 | 05 SOUTHWEST | 526161 | CARLISLE 6 | 230 | 10.473 | 10.4317 | 0.0413
GEN-2018-073 | 05 SOUTHWEST | 526337 | JONES 6 | 230 | 16.6076 | 16.5521 | 0.0555
GEN-2018-073 | 05 SOUTHWEST | 526935 | YOAKUM 6 | 230 | 19.6825 | 19.6564 | 0.0261
GEN-2018-073 | 05 SOUTHWEST | 527896 | HOBBS_INT 7 | 345 | 12.0143 | 12.0026 | 0.0117
GEN-2018-073 | 05 SOUTHWEST | 762460 | GEN-2018-015 | 345 | 5.812 | 5.7898 | 0.0222
GEN-2018-073 | 05 SOUTHWEST | 763215 | G18-092-TAP | 345 | 6.0024 | 5.9872 | 0.0152
GEN-2018-073 | 05 SOUTHWEST | 763516 | GEN-2019-011 | 345 | 9.2852 | 9.261 | 0.0242
GEN-2018-073 | 05 SOUTHWEST | 511456 | O.K.U.-7 | 345 | 6.3254 | 6.3168 | 0.0086
GEN-2018-073 | 05 SOUTHWEST | 511557 | CHISHOLM6 | 230 | 12.1566 | 12.1524 | 0.0042
GEN-2018-073 | 05 SOUTHWEST | 515376 | WWRDEHV4 | 138 | 24.8769 | 24.8761 | 0.0008
GEN-2018-073 | 05 SOUTHWEST | 515407 | TATONGA7 | 345 | 17.5658 | 17.5652 | 0.0006
GEN-2018-073 | 05 SOUTHWEST | 515554 | BVRCNTY7 | 345 | 15.3093 | 15.3084 | 0.0009
GEN-2018-073 | 05 SOUTHWEST | 515599 | G07621119-20 | 345 | 13.4849 | 13.4842 | 0.0007
GEN-2018-073 | 05 SOUTHWEST | 515852 | DGRASSE7 | 345 | 15.3179 | 15.3174 | 0.0005
GEN-2018-073 | 05 SOUTHWEST | 515961 | GUTHRIE7 | 345 | 12.8816 | 12.8809 | 0.0007
GEN-2018-073 | 05 SOUTHWEST | 516106 | BOBCAT 7 | 345 | 15.796 | 15.7951 | 0.0009
GEN-2018-073 | 05 SOUTHWEST | 524415 | AMA_SOUTH 6 | 230 | 13.6408 | 13.6368 | 0.004
GEN-2018-073 | 05 SOUTHWEST | 524909 | ROOSEVELT 6 | 230 | 9.709 | 9.7062 | 0.0028
GEN-2018-073 | 05 SOUTHWEST | 525212 | SWISHER 3 | 115 | 11.4972 | 11.4865 | 0.0107
GEN-2018-073 | 05 SOUTHWEST | 525454 | HALE_CNTY 3 | 115 | 10.1608 | 10.1506 | 0.0102
GEN-2018-073 | 05 SOUTHWEST | 525461 | NEWHART 6 | 230 | 10.9971 | 10.9855 | 0.0116
GEN-2018-073 | 05 SOUTHWEST | 525481 | PLANT_X 6 | 230 | 24.1838 | 24.1573 | 0.0265
GEN-2018-073 | 05 SOUTHWEST | 525549 | TOLK 7 | 345 | 15.0276 | 15.0155 | 0.0121
GEN-2018-073 | 05 SOUTHWEST | 525586 | NEEDMORE 6 | 230 | 11.0214 | 11.0164 | 0.005
GEN-2018-073 | 05 SOUTHWEST | 525637 | LAMB_CNTY 6 | 230 | 5.4027 | 5.4013 | 0.0014
GEN-2018-073 | 05 SOUTHWEST | 525780 | FLOYD_CNTY 3 | 115 | 6.2514 | 6.2452 | 0.0062
GEN-2018-073 | 05 SOUTHWEST | 525816 | TUCO_INT2 2 | 69 | 4.6524 | 4.6489 | 0.0035
GEN-2018-073 | 05 SOUTHWEST | 525826 | TUCO_INT 2 | 69 | 7.8538 | 7.8438 | 0.01
GEN-2018-073 | 05 SOUTHWEST | 526076 | STANTON_W 3 | 115 | 8.923 | 8.9084 | 0.0146
GEN-2018-073 | 05 SOUTHWEST | 526160 | CARLISLE 3 | 115 | 12.772 | 12.7466 | 0.0254
GEN-2018-073 | 05 SOUTHWEST | 526269 | LUBBCK_STH 6 | 230 | 15.0546 | 15.0068 | 0.0478
GEN-2018-073 | 05 SOUTHWEST | 526298 | LUBBCK_EST 3 | 115 | 14.4141 | 14.386 | 0.0281
GEN-2018-073 | 05 SOUTHWEST | 526299 | LUBBCK_EST 6 | 230 | 11.0462 | 11.0205 | 0.0257
GEN-2018-073 | 05 SOUTHWEST | 526460 | AMOCO_SS 6 | 230 | 10.1771 | 10.1639 | 0.0132
GEN-2018-073 | 05 SOUTHWEST | 526525 | WOLFFORTH 6 | 230 | 13.0516 | 13.0108 | 0.0408
GEN-2018-073 | 05 SOUTHWEST | 526677 | GRASSLAND 6 | 230 | 5.9735 | 5.9662 | 0.0073
GEN-2018-073 | 05 SOUTHWEST | 526934 | YOAKUM 3 | 115 | 19.2326 | 19.2217 | 0.0109
GEN-2018-073 | 05 SOUTHWEST | 527009 | BRU_SUB 6 | 230 | 15.6513 | 15.638 | 0.0133
GEN-2018-073 | 05 SOUTHWEST | 527028 | INK_BASIN 6 | 230 | 11.2413 | 11.2356 | 0.0057
GEN-2018-073 | 05 SOUTHWEST | 527149 | MUSTANG 6 | 230 | 17.9238 | 17.9121 | 0.0117
GEN-2018-073 | 05 SOUTHWEST | 527656 | CROSSROADS 7 | 345 | 11.539 | 11.5327 | 0.0063
GEN-2018-073 | 05 SOUTHWEST | 527894 | HOBBS_INT 6 | 230 | 19.4767 | 19.4675 | 0.0092
GEN-2018-073 | 05 SOUTHWEST | 527965 | KIOWA 7 | 345 | 8.82 | 8.815 | 0.005
GEN-2018-073 | 05 SOUTHWEST | 528027 | RDRUNNER 7 | 345 | 8.6815 | 8.6762 | 0.0053
GEN-2018-073 | 05 SOUTHWEST | 560035 | GRAPEVINE | 345 | 6.4589 | 6.4572 | 0.0017
GEN-2018-073 | 05 SOUTHWEST | 560078 | G16-037-TAP | 345 | 10.1427 | 10.1397 | 0.003
GEN-2018-073 | 05 SOUTHWEST | 762132 | GEN-2017-158 | 230 | 13.8646 | 13.8579 | 0.0067
GEN-2018-073 | 05 SOUTHWEST | 763208 | GEN-2018-092 | 345 | 5.809 | 5.795 | 0.014
GEN-2018-073 | 05 SOUTHWEST | 763241 | GEN-2018-097 | 230 | 24.4484 | 24.425 | 0.0234
GEN-2018-073 | 05 SOUTHWEST | 763527 | GEN-2019-012 | 345 | 19.3711 | 19.3695 | 0.0016
GEN-2018-073 | 05 SOUTHWEST | 511468 | L.E.S.-7 | 345 | 14.8644 | 14.8596 | 0.0048
GEN-2018-073 | 05 SOUTHWEST | 511490 | ELKCITY6 | 230 | 7.3607 | 7.3597 | 0.001
GEN-2018-073 | 05 SOUTHWEST | 511541 | SWEETWT6 | 230 | 8.8366 | 8.8348 | 0.0018
GEN-2018-073 | 05 SOUTHWEST | 511565 | OKLAUN HVDC7 | 345 | 6.3037 | 6.2951 | 0.0086
GEN-2018-073 | 05 SOUTHWEST | 514785 | WOODWRD4 | 138 | 13.1123 | 13.1121 | 0.0002
GEN-2018-073 | 05 SOUTHWEST | 514796 | IODINE-4 | 138 | 7.3201 | 7.32 | 0.0001
GEN-2018-073 | 05 SOUTHWEST | 515394 | KEENAN 4 | 138 | 8.9414 | 8.9413 | 0.0001
GEN-2018-073 | 05 SOUTHWEST | 515398 | OUSPRT 4 | 138 | 9.528 | 9.5279 | 0.0001
GEN-2018-073 | 05 SOUTHWEST | 515425 | WWDPST 4 | 138 | 17.7977 | 17.7974 | 0.0003
GEN-2018-073 | 05 SOUTHWEST | 515448 | CRSRDSW7 | 345 | 12.1468 | 12.1465 | 0.0003
GEN-2018-073 | 05 SOUTHWEST | 515497 | MATHWSN7 | 345 | 32.7952 | 32.7943 | 0.0009
GEN-2018-073 | 05 SOUTHWEST | 515582 | SLNGWND7 | 345 | 8.4766 | 8.4765 | 0.0001
GEN-2018-073 | 05 SOUTHWEST | 515585 | MAMTHPW7 | 345 | 13.5669 | 13.5665 | 0.0004
GEN-2018-073 | 05 SOUTHWEST | 515590 | PALDR2W7 | 345 | 12.8669 | 12.8663 | 0.0006
GEN-2018-073 | 05 SOUTHWEST | 515618 | BALKOW 7 | 345 | 12.5807 | 12.5801 | 0.0006
GEN-2018-073 | 05 SOUTHWEST | 515677 | BADGER 7 | 345 | 13.7821 | 13.7814 | 0.0007
GEN-2018-073 | 05 SOUTHWEST | 515800 | GRACMNT7 | 345 | 20.5087 | 20.5051 | 0.0036
GEN-2018-073 | 05 SOUTHWEST | 515825 | GRTWSRN7 | 345 | 9.0702 | 9.0699 | 0.0003
GEN-2018-073 | 05 SOUTHWEST | 515853 | DGRASSE4 | 138 | 17.0745 | 17.0744 | 0.0001
GEN-2018-073 | 05 SOUTHWEST | 515951 | PERSIMN7 | 345 | 11.0796 | 11.0791 | 0.0005
GEN-2018-073 | 05 SOUTHWEST | 516146 | 25MILE 7 | 345 | 11.1221 | 11.1217 | 0.0004
GEN-2018-073 | 05 SOUTHWEST | 523097 | HITCHLAND 7 | 345 | 14.9713 | 14.9704 | 0.0009
GEN-2018-073 | 05 SOUTHWEST | 523959 | POTTER_CO 6 | 230 | 22.4376 | 22.4305 | 0.0071
GEN-2018-073 | 05 SOUTHWEST | 523961 | POTTER_CO 7 | 345 | 11.6631 | 11.6599 | 0.0032
GEN-2018-073 | 05 SOUTHWEST | 524044 | NICHOLS 6 | 230 | 26.1237 | 26.1167 | 0.007
GEN-2018-073 | 05 SOUTHWEST | 524365 | RANDALL 6 | 230 | 14.5681 | 14.5645 | 0.0036
GEN-2018-073 | 05 SOUTHWEST | 524414 | AMA_SOUTH 3 | 115 | 16.9088 | 16.9064 | 0.0024
GEN-2018-073 | 05 SOUTHWEST | 524770 | PLSNT_HILL 6 | 230 | 6.517 | 6.5158 | 0.0012
GEN-2018-073 | 05 SOUTHWEST | 524875 | OASIS 6 | 230 | 7.8784 | 7.8767 | 0.0017
GEN-2018-073 | 05 SOUTHWEST | 524908 | ROOSEVELT 3 | 115 | 11.1454 | 11.1436 | 0.0018
GEN-2018-073 | 05 SOUTHWEST | 525192 | KRESS_INT 3 | 115 | 11.9205 | 11.9096 | 0.0109
GEN-2018-073 | 05 SOUTHWEST | 525326 | COX 3 | 115 | 6.2736 | 6.2692 | 0.0044
GEN-2018-073 | 05 SOUTHWEST | 525414 | LAMTON 3 | 115 | 7.6144 | 7.6111 | 0.0033
GEN-2018-073 | 05 SOUTHWEST | 525453 | HALE_CNTY 2 | 69 | 6.9062 | 6.9034 | 0.0028
GEN-2018-073 | 05 SOUTHWEST | 525460 | NEWHART 3 | 115 | 14.9423 | 14.9317 | 0.0106
GEN-2018-073 | 05 SOUTHWEST | 525480 | PLANT_X 3 | 115 | 19.2796 | 19.2685 | 0.0111
GEN-2018-073 | 05 SOUTHWEST | 525585 | BLUECLDPOI 6 | 230 | 11.0214 | 11.0164 | 0.005
GEN-2018-073 | 05 SOUTHWEST | 525636 | LAMB_CNTY 3 | 115 | 8.4389 | 8.4369 | 0.002
GEN-2018-073 | 05 SOUTHWEST | 525731 | SP-ABERNTHY2 | 69 | 3.0093 | 3.0078 | 0.0015
GEN-2018-073 | 05 SOUTHWEST | 525738 | HALECENTER 2 | 69 | 2.4566 | 2.4556 | 0.001
GEN-2018-073 | 05 SOUTHWEST | 525763 | CALLAHAN 3 | 115 | 5.5668 | 5.5623 | 0.0045
GEN-2018-073 | 05 SOUTHWEST | 525779 | FLOYD_CNTY 2 | 69 | 5.401 | 5.3983 | 0.0027
GEN-2018-073 | 05 SOUTHWEST | 525803 | BLANCO 3 | 115 | 5.0451 | 5.0416 | 0.0035
GEN-2018-073 | 05 SOUTHWEST | 525853 | LH-WIL&ELN+2 | 69 | 2.5404 | 2.5394 | 0.001
GEN-2018-073 | 05 SOUTHWEST | 525885 | SP-NEWDEAL 2 | 69 | 3.3073 | 3.3055 | 0.0018
GEN-2018-073 | 05 SOUTHWEST | 525926 | CROSBY 3 | 115 | 4.7129 | 4.7099 | 0.003
GEN-2018-073 | 05 SOUTHWEST | 526109 | SP-ERSKINE 3 | 115 | 10.9787 | 10.9589 | 0.0198
GEN-2018-073 | 05 SOUTHWEST | 526146 | INDIANA 3 | 115 | 9.3032 | 9.2878 | 0.0154
GEN-2018-073 | 05 SOUTHWEST | 526159 | CARLISLE 2 | 69 | 2.5568 | 2.5562 | 0.0006
GEN-2018-073 | 05 SOUTHWEST | 526162 | LP-DOUD_TP 3 | 115 | 11.325 | 11.3063 | 0.0187
GEN-2018-073 | 05 SOUTHWEST | 526192 | MURPHY 3 | 115 | 10.2503 | 10.2347 | 0.0156
GEN-2018-073 | 05 SOUTHWEST | 526268 | LUBBCK_STH 3 | 115 | 17.6482 | 17.611 | 0.0372
GEN-2018-073 | 05 SOUTHWEST | 526297 | LUBBCK_EST 2 | 69 | 7.8955 | 7.8905 | 0.005
GEN-2018-073 | 05 SOUTHWEST | 526435 | SUNDOWN 6 | 230 | 11.7438 | 11.7249 | 0.0189
GEN-2018-073 | 05 SOUTHWEST | 526524 | WOLFFORTH 3 | 115 | 11.2819 | 11.2671 | 0.0148
GEN-2018-073 | 05 SOUTHWEST | 526676 | GRASSLAND 3 | 115 | 6.8633 | 6.8583 | 0.005
GEN-2018-073 | 05 SOUTHWEST | 526679 | CIRRUS_WND 6 | 230 | 4.6792 | 4.6747 | 0.0045
GEN-2018-073 | 05 SOUTHWEST | 526784 | AMOCOWASSON6 | 230 | 15.6353 | 15.625 | 0.0103
GEN-2018-073 | 05 SOUTHWEST | 526792 | PRENTICE 3 | 115 | 6.0286 | 6.0272 | 0.0014
GEN-2018-073 | 05 SOUTHWEST | 526928 | PLAINS_INT 3 | 115 | 10.0196 | 10.0166 | 0.003
GEN-2018-073 | 05 SOUTHWEST | 527010 | OXYBRU 6 | 230 | 15.5052 | 15.4921 | 0.0131
GEN-2018-073 | 05 SOUTHWEST | 527011 | XTO_MAHONEY6 | 230 | 15.3578 | 15.3459 | 0.0119
GEN-2018-073 | 05 SOUTHWEST | 527027 | INK_BASIN 3 | 115 | 13.258 | 13.2552 | 0.0028
GEN-2018-073 | 05 SOUTHWEST | 527041 | ARCO_TP 3 | 115 | 13.6807 | 13.6769 | 0.0038
GEN-2018-073 | 05 SOUTHWEST | 527146 | MUSTANG 3 | 115 | 24.0628 | 24.0542 | 0.0086
GEN-2018-073 | 05 SOUTHWEST | 527151 | GS-MUSTANG 6 | 230 | 17.9238 | 17.9121 | 0.0117
GEN-2018-073 | 05 SOUTHWEST | 527194 | LG-PLSHILL 3 | 115 | 7.9741 | 7.9726 | 0.0015
GEN-2018-073 | 05 SOUTHWEST | 527276 | SEMINOLE 6 | 230 | 8.197 | 8.1948 | 0.0022
GEN-2018-073 | 05 SOUTHWEST | 527610 | SAGA_SCOL 7 | 345 | 10.2321 | 10.2274 | 0.0047
GEN-2018-073 | 05 SOUTHWEST | 527655 | RSVLT_CC_E 7 | 345 | 10.0154 | 10.0109 | 0.0045
GEN-2018-073 | 05 SOUTHWEST | 527802 | EDDY_CNTY 7 | 345 | 7.3273 | 7.3244 | 0.0029
GEN-2018-073 | 05 SOUTHWEST | 527867 | CUNNIGHM_S 6 | 230 | 17.5364 | 17.53 | 0.0064
GEN-2018-073 | 05 SOUTHWEST | 527891 | HOBBS_INT 3 | 115 | 33.0667 | 33.0598 | 0.0069
GEN-2018-073 | 05 SOUTHWEST | 527966 | KIOWA 3 | 115 | 17.1508 | 17.1458 | 0.005
GEN-2018-073 | 05 SOUTHWEST | 528015 | PHANTOM 7 | 345 | 5.675 | 5.6729 | 0.0021
GEN-2018-073 | 05 SOUTHWEST | 528025 | RDRUNNER 3 | 115 | 13.7957 | 13.7918 | 0.0039
GEN-2018-073 | 05 SOUTHWEST | 528185 | N_LOVING 7 | 345 | 6.5496 | 6.5469 | 0.0027
GEN-2018-073 | 05 SOUTHWEST | 528604 | ANDREWS 6 | 230 | 6.0764 | 6.0756 | 0.0008
GEN-2018-073 | 05 SOUTHWEST | 539801 | THISTLE7 | 345 | 16.6662 | 16.6661 | 0.0001
GEN-2018-073 | 05 SOUTHWEST | 585410 | GREAT_WESTRN | 345 | 9.7415 | 9.7411 | 0.0004
GEN-2018-073 | 05 SOUTHWEST | 585430 | PRSIMN_CRK1 | 345 | 11.7445 | 11.744 | 0.0005
GEN-2018-073 | 05 SOUTHWEST | 587230 | GEN-2016-037 | 345 | 9.6646 | 9.6619 | 0.0027
GEN-2018-073 | 05 SOUTHWEST | 588560 | GEN-2017-011 | 345 | 12.6206 | 12.62 | 0.0006
GEN-2018-073 | 05 SOUTHWEST | 588760 | GEN-2017-033 | 345 | 4.4427 | 4.4387 | 0.004
GEN-2018-073 | 05 SOUTHWEST | 599955 | PNM-DC6 | 230 | 9.709 | 9.7062 | 0.0028
GEN-2018-073 | 05 SOUTHWEST | 760498 | G17-146-TAP | 230 | 7.745 | 7.7433 | 0.0017
GEN-2018-073 | 05 SOUTHWEST | 763120 | GEN-2018-081 | 230 | 17.3907 | 17.3773 | 0.0134
GEN-2018-073 | 05 SOUTHWEST | 763186 | GEN-2018-089 | 230 | 10.6882 | 10.6773 | 0.0109
GEN-2018-073 | 05 SOUTHWEST | 763483 | GEN-2019-003 | 230 | 8.7401 | 8.7379 | 0.0022
GEN-2018-081 | 05 SOUTHWEST | 525481 | PLANT_X 6 | 230 | 24.1838 | 23.6782 | 0.5056
GEN-2018-081 | 05 SOUTHWEST | 525461 | NEWHART 6 | 230 | 10.9971 | 10.9692 | 0.0279
GEN-2018-081 | 05 SOUTHWEST | 525480 | PLANT_X 3 | 115 | 19.2796 | 19.1753 | 0.1043
GEN-2018-081 | 05 SOUTHWEST | 525531 | TOLK 6 | 230 | 31.4946 | 31.1734 | 0.3212
GEN-2018-081 | 05 SOUTHWEST | 526435 | SUNDOWN 6 | 230 | 11.7438 | 11.7246 | 0.0192
GEN-2018-081 | 05 SOUTHWEST | 760498 | G17-146-TAP | 230 | 7.745 | 7.7236 | 0.0214
GEN-2018-081 | 05 SOUTHWEST | 763120 | GEN-2018-081 | 230 | 17.3907 | 16.8812 | 0.5095
GEN-2018-081 | 05 SOUTHWEST | 523959 | POTTER_CO 6 | 230 | 22.4376 | 22.4208 | 0.0168
GEN-2018-081 | 05 SOUTHWEST | 524623 | DEAFSMITH 6 | 230 | 8.0257 | 8.0093 | 0.0164
GEN-2018-081 | 05 SOUTHWEST | 524909 | ROOSEVELT 6 | 230 | 9.709 | 9.6878 | 0.0212
GEN-2018-081 | 05 SOUTHWEST | 525019 | MULSHVLY_TP3 | 115 | 5.9489 | 5.941 | 0.0079
GEN-2018-081 | 05 SOUTHWEST | 525056 | BC-EARTH 3 | 115 | 8.2606 | 8.2467 | 0.0139
GEN-2018-081 | 05 SOUTHWEST | 525213 | SWISHER 6 | 230 | 10.3853 | 10.3715 | 0.0138
GEN-2018-081 | 05 SOUTHWEST | 525446 | RKYFORD_TP 3 | 115 | 10.1267 | 10.1013 | 0.0254
GEN-2018-081 | 05 SOUTHWEST | 525454 | HALE_CNTY 3 | 115 | 10.1608 | 10.1511 | 0.0097
GEN-2018-081 | 05 SOUTHWEST | 525460 | NEWHART 3 | 115 | 14.9423 | 14.917 | 0.0253
GEN-2018-081 | 05 SOUTHWEST | 525549 | TOLK 7 | 345 | 15.0276 | 14.9517 | 0.0759
GEN-2018-081 | 05 SOUTHWEST | 525586 | NEEDMORE 6 | 230 | 11.0214 | 10.9911 | 0.0303
GEN-2018-081 | 05 SOUTHWEST | 525636 | LAMB_CNTY 3 | 115 | 8.4389 | 8.4266 | 0.0123
GEN-2018-081 | 05 SOUTHWEST | 525637 | LAMB_CNTY 6 | 230 | 5.4027 | 5.3929 | 0.0098
GEN-2018-081 | 05 SOUTHWEST | 525830 | TUCO_INT 6 | 230 | 21.9895 | 21.9658 | 0.0237
GEN-2018-081 | 05 SOUTHWEST | 526434 | SUNDOWN 3 | 115 | 10.8603 | 10.8537 | 0.0066
GEN-2018-081 | 05 SOUTHWEST | 526460 | AMOCO_SS 6 | 230 | 10.1771 | 10.1644 | 0.0127
GEN-2018-081 | 05 SOUTHWEST | 526525 | WOLFFORTH 6 | 230 | 13.0516 | 13.0399 | 0.0117
GEN-2018-081 | 05 SOUTHWEST | 760494 | GEN-2017-146 | 230 | 7.4558 | 7.436 | 0.0198
GEN-2018-081 | 05 SOUTHWEST | 762132 | GEN-2017-158 | 230 | 13.8646 | 13.8099 | 0.0547
GEN-2018-081 | 05 SOUTHWEST | 763186 | GEN-2018-089 | 230 | 10.6882 | 10.6619 | 0.0263
GEN-2018-081 | 05 SOUTHWEST | 763241 | GEN-2018-097 | 230 | 24.4484 | 24.2583 | 0.1901
GEN-2018-081 | 05 SOUTHWEST | 523323 | MCDWL_CREEK6 | 230 | 8.9802 | 8.9782 | 0.002
GEN-2018-081 | 05 SOUTHWEST | 523869 | CHAN+TASCOS6 | 230 | 4.2464 | 4.2459 | 0.0005
GEN-2018-081 | 05 SOUTHWEST | 523961 | POTTER_CO 7 | 345 | 11.6631 | 11.656 | 0.0071
GEN-2018-081 | 05 SOUTHWEST | 523979 | HARRNG_EST 6 | 230 | 26.9856 | 26.9715 | 0.0141
GEN-2018-081 | 05 SOUTHWEST | 524010 | ROLLHILLS 6 | 230 | 20.2306 | 20.2204 | 0.0102
GEN-2018-081 | 05 SOUTHWEST | 524267 | BUSHLAND 6 | 230 | 10.1739 | 10.1662 | 0.0077
GEN-2018-081 | 05 SOUTHWEST | 524415 | AMA_SOUTH 6 | 230 | 13.6408 | 13.635 | 0.0058
GEN-2018-081 | 05 SOUTHWEST | 524619 | DFSMTH_EST 3 | 115 | 11.9939 | 11.9773 | 0.0166
GEN-2018-081 | 05 SOUTHWEST | 524622 | DFSMTH_WST 3 | 115 | 11.9945 | 11.9779 | 0.0166
GEN-2018-081 | 05 SOUTHWEST | 524746 | CASTRO_CNTY3 | 115 | 9.822 | 9.8105 | 0.0115
GEN-2018-081 | 05 SOUTHWEST | 524770 | PLSNT_HILL 6 | 230 | 6.517 | 6.508 | 0.009
GEN-2018-081 | 05 SOUTHWEST | 524875 | OASIS 6 | 230 | 7.8784 | 7.866 | 0.0124
GEN-2018-081 | 05 SOUTHWEST | 524908 | ROOSEVELT 3 | 115 | 11.1454 | 11.1316 | 0.0138
GEN-2018-081 | 05 SOUTHWEST | 525018 | MULESHVALLY3 | 115 | 5.5409 | 5.534 | 0.0069
GEN-2018-081 | 05 SOUTHWEST | 525028 | BAILEYCO 3 | 115 | 5.8021 | 5.7947 | 0.0074
GEN-2018-081 | 05 SOUTHWEST | 525050 | BC-KELLEY +3 | 115 | 7.782 | 7.7711 | 0.0109
GEN-2018-081 | 05 SOUTHWEST | 525124 | HART_INDUST3 | 115 | 7.4925 | 7.4854 | 0.0071
GEN-2018-081 | 05 SOUTHWEST | 525192 | KRESS_INT 3 | 115 | 11.9205 | 11.9099 | 0.0106
GEN-2018-081 | 05 SOUTHWEST | 525212 | SWISHER 3 | 115 | 11.4972 | 11.4877 | 0.0095
GEN-2018-081 | 05 SOUTHWEST | 525326 | COX 3 | 115 | 6.2736 | 6.271 | 0.0026
GEN-2018-081 | 05 SOUTHWEST | 525393 | ROCKYFORD 3 | 115 | 9.0431 | 9.0228 | 0.0203
GEN-2018-081 | 05 SOUTHWEST | 525414 | LAMTON 3 | 115 | 7.6144 | 7.6055 | 0.0089
GEN-2018-081 | 05 SOUTHWEST | 525440 | LC-S_OLTON+3 | 115 | 7.1982 | 7.1885 | 0.0097
GEN-2018-081 | 05 SOUTHWEST | 525453 | HALE_CNTY 2 | 69 | 6.9062 | 6.9035 | 0.0027
GEN-2018-081 | 05 SOUTHWEST | 525585 | BLUECLDPOI 6 | 230 | 11.0214 | 10.9911 | 0.0303
GEN-2018-081 | 05 SOUTHWEST | 525635 | LAMB_CNTY 2 | 69 | 5.8992 | 5.8955 | 0.0037
GEN-2018-081 | 05 SOUTHWEST | 525828 | TUCO_INT 3 | 115 | 19.3618 | 19.3504 | 0.0114
GEN-2018-081 | 05 SOUTHWEST | 525832 | TUCO_INT 7 | 345 | 14.0745 | 14.0658 | 0.0087
GEN-2018-081 | 05 SOUTHWEST | 525840 | ANTELOPE_1 6 | 230 | 21.8013 | 21.778 | 0.0233
GEN-2018-081 | 05 SOUTHWEST | 525957 | HALE_WNDCL16 | 230 | 10.5196 | 10.5148 | 0.0048
GEN-2018-081 | 05 SOUTHWEST | 526020 | HOCKLEY 3 | 115 | 5.426 | 5.4231 | 0.0029
GEN-2018-081 | 05 SOUTHWEST | 526036 | LC-OPDYKE 3 | 115 | 5.7143 | 5.7114 | 0.0029
GEN-2018-081 | 05 SOUTHWEST | 526161 | CARLISLE 6 | 230 | 10.473 | 10.4664 | 0.0066
GEN-2018-081 | 05 SOUTHWEST | 526269 | LUBBCK_STH 6 | 230 | 15.0546 | 15.0467 | 0.0079
GEN-2018-081 | 05 SOUTHWEST | 526337 | JONES 6 | 230 | 16.6076 | 16.5994 | 0.0082
GEN-2018-081 | 05 SOUTHWEST | 526424 | PACIFIC 3 | 115 | 9.1771 | 9.1726 | 0.0045
GEN-2018-081 | 05 SOUTHWEST | 526445 | AMOCO_TP 3 | 115 | 10.1845 | 10.1789 | 0.0056
GEN-2018-081 | 05 SOUTHWEST | 526524 | WOLFFORTH 3 | 115 | 11.2819 | 11.2782 | 0.0037
GEN-2018-081 | 05 SOUTHWEST | 526935 | YOAKUM 6 | 230 | 19.6825 | 19.6696 | 0.0129
GEN-2018-081 | 05 SOUTHWEST | 527656 | CROSSROADS 7 | 345 | 11.539 | 11.5264 | 0.0126
GEN-2018-081 | 05 SOUTHWEST | 599955 | PNM-DC6 | 230 | 9.709 | 9.6878 | 0.0212
GEN-2018-081 | 05 SOUTHWEST | 763483 | GEN-2019-003 | 230 | 8.7401 | 8.7233 | 0.0168
GEN-2018-081 | 05 SOUTHWEST | 523097 | HITCHLAND 7 | 345 | 14.9713 | 14.9702 | 0.0011
GEN-2018-081 | 05 SOUTHWEST | 523221 | XIT_INTG 6 | 230 | 3.1441 | 3.1438 | 0.0003
GEN-2018-081 | 05 SOUTHWEST | 523267 | PRINGLE 6 | 230 | 4.3435 | 4.3433 | 0.0002
GEN-2018-081 | 05 SOUTHWEST | 523309 | MOORE_CNTY 6 | 230 | 6.6813 | 6.6806 | 0.0007
GEN-2018-081 | 05 SOUTHWEST | 523322 | MCDWL_CREEK3 | 115 | 9.8376 | 9.8366 | 0.001
GEN-2018-081 | 05 SOUTHWEST | 523977 | HARRNG_WST 6 | 230 | 26.9856 | 26.9715 | 0.0141
GEN-2018-081 | 05 SOUTHWEST | 523978 | HARRNG_MID 6 | 230 | 26.9856 | 26.9715 | 0.0141
GEN-2018-081 | 05 SOUTHWEST | 524007 | ROLLHILLS 3 | 115 | 19.6592 | 19.6549 | 0.0043
GEN-2018-081 | 05 SOUTHWEST | 524044 | NICHOLS 6 | 230 | 26.1237 | 26.1107 | 0.013
GEN-2018-081 | 05 SOUTHWEST | 524266 | BUSHLAND 3 | 115 | 10.3324 | 10.3295 | 0.0029
GEN-2018-081 | 05 SOUTHWEST | 524290 | WILDOR2_JUS6 | 230 | 6.9783 | 6.9749 | 0.0034
GEN-2018-081 | 05 SOUTHWEST | 524296 | SPNSPUR_WND7 | 345 | 5.3278 | 5.3266 | 0.0012
GEN-2018-081 | 05 SOUTHWEST | 524365 | RANDALL 6 | 230 | 14.5681 | 14.5622 | 0.0059
GEN-2018-081 | 05 SOUTHWEST | 524414 | AMA_SOUTH 3 | 115 | 16.9088 | 16.9043 | 0.0045
GEN-2018-081 | 05 SOUTHWEST | 524630 | TIERABLANCA3 | 115 | 12.3344 | 12.3169 | 0.0175
GEN-2018-081 | 05 SOUTHWEST | 524694 | DS-#22 3 | 115 | 4.5966 | 4.5941 | 0.0025
GEN-2018-081 | 05 SOUTHWEST | 524734 | DS-#21 3 | 115 | 9.3056 | 9.2953 | 0.0103
GEN-2018-081 | 05 SOUTHWEST | 524745 | CASTRO_CNTY2 | 69 | 8.7963 | 8.7908 | 0.0055
GEN-2018-081 | 05 SOUTHWEST | 524757 | BETHEL_COL13 | 115 | 8.2391 | 8.2318 | 0.0073
GEN-2018-081 | 05 SOUTHWEST | 524768 | PLSNT_HILL 3 | 115 | 10.5272 | 10.5159 | 0.0113
GEN-2018-081 | 05 SOUTHWEST | 524822 | CURRY 3 | 115 | 11.4402 | 11.4255 | 0.0147
GEN-2018-081 | 05 SOUTHWEST | 524874 | OASIS 3 | 115 | 10.0542 | 10.0436 | 0.0106
GEN-2018-081 | 05 SOUTHWEST | 524885 | SN_JUAN_TAP6 | 230 | 4.8705 | 4.8684 | 0.0021
GEN-2018-081 | 05 SOUTHWEST | 524924 | PORTALES 3 | 115 | 7.5524 | 7.5463 | 0.0061
GEN-2018-081 | 05 SOUTHWEST | 525027 | BAILEYCO 2 | 69 | 5.2707 | 5.2671 | 0.0036
GEN-2018-081 | 05 SOUTHWEST | 525179 | TULIA_TP 3 | 115 | 6.4624 | 6.4599 | 0.0025
GEN-2018-081 | 05 SOUTHWEST | 525191 | KRESS_INT 2 | 69 | 4.4978 | 4.4969 | 0.0009
GEN-2018-081 | 05 SOUTHWEST | 525226 | KRS_RURL_TP3 | 115 | 6.4399 | 6.4369 | 0.003
GEN-2018-081 | 05 SOUTHWEST | 525272 | KISER 3 | 115 | 5.2683 | 5.2663 | 0.002
GEN-2018-081 | 05 SOUTHWEST | 525291 | PLAINVW_TP 2 | 69 | 6.4824 | 6.48 | 0.0024
GEN-2018-081 | 05 SOUTHWEST | 525298 | S_PLAINVEW 2 | 69 | 2.5852 | 2.5849 | 0.0003
GEN-2018-081 | 05 SOUTHWEST | 525325 | COX 2 | 69 | 3.4185 | 3.418 | 0.0005
GEN-2018-081 | 05 SOUTHWEST | 525413 | LAMTON 2 | 69 | 5.1693 | 5.1669 | 0.0024
GEN-2018-081 | 05 SOUTHWEST | 525432 | SP-HALFWAY+2 | 69 | 5.8641 | 5.8621 | 0.002
GEN-2018-081 | 05 SOUTHWEST | 525584 | BLUECLDCOL 6 | 230 | 10.4275 | 10.4005 | 0.027
GEN-2018-081 | 05 SOUTHWEST | 525613 | W_LITTLFLD 2 | 69 | 2.9684 | 2.9675 | 0.0009
GEN-2018-081 | 05 SOUTHWEST | 525620 | LTFLD_S&CTY2 | 69 | 4.1727 | 4.1709 | 0.0018
GEN-2018-081 | 05 SOUTHWEST | 525650 | LC-LTTLFLD+2 | 69 | 4.9319 | 4.9294 | 0.0025
GEN-2018-081 | 05 SOUTHWEST | 525687 | LC-LUMSCHAP2 | 69 | 4.6126 | 4.6103 | 0.0023
GEN-2018-081 | 05 SOUTHWEST | 525763 | CALLAHAN 3 | 115 | 5.5668 | 5.5653 | 0.0015
GEN-2018-081 | 05 SOUTHWEST | 525780 | FLOYD_CNTY 3 | 115 | 6.2514 | 6.2499 | 0.0015
GEN-2018-081 | 05 SOUTHWEST | 525816 | TUCO_INT2 2 | 69 | 4.6524 | 4.652 | 0.0004
GEN-2018-081 | 05 SOUTHWEST | 525826 | TUCO_INT 2 | 69 | 7.8538 | 7.8526 | 0.0012
GEN-2018-081 | 05 SOUTHWEST | 525850 | ELK_CT1 | 345 | 13.9398 | 13.9313 | 0.0085
GEN-2018-081 | 05 SOUTHWEST | 526019 | HOCKLEY 2 | 69 | 5.1105 | 5.109 | 0.0015
GEN-2018-081 | 05 SOUTHWEST | 526076 | STANTON_W 3 | 115 | 8.923 | 8.9208 | 0.0022
GEN-2018-081 | 05 SOUTHWEST | 526160 | CARLISLE 3 | 115 | 12.772 | 12.7676 | 0.0044
GEN-2018-081 | 05 SOUTHWEST | 526268 | LUBBCK_STH 3 | 115 | 17.6482 | 17.6422 | 0.006
GEN-2018-081 | 05 SOUTHWEST | 526298 | LUBBCK_EST 3 | 115 | 14.4141 | 14.4099 | 0.0042
GEN-2018-081 | 05 SOUTHWEST | 526299 | LUBBCK_EST 6 | 230 | 11.0462 | 11.0424 | 0.0038
GEN-2018-081 | 05 SOUTHWEST | 526361 | COCHRAN 3 | 115 | 6.4257 | 6.4239 | 0.0018
GEN-2018-081 | 05 SOUTHWEST | 526452 | AMOCO_CRYO 3 | 115 | 6.362 | 6.3598 | 0.0022
GEN-2018-081 | 05 SOUTHWEST | 526475 | YUMA_INT 3 | 115 | 10.7034 | 10.7002 | 0.0032
GEN-2018-081 | 05 SOUTHWEST | 526484 | LG-LEVELAND3 | 115 | 9.1775 | 9.1732 | 0.0043
GEN-2018-081 | 05 SOUTHWEST | 526677 | GRASSLAND 6 | 230 | 5.9735 | 5.9724 | 0.0011
GEN-2018-081 | 05 SOUTHWEST | 526736 | TERRY_CNTY 3 | 115 | 10.6679 | 10.6652 | 0.0027
GEN-2018-081 | 05 SOUTHWEST | 526934 | YOAKUM 3 | 115 | 19.2326 | 19.2269 | 0.0057
GEN-2018-081 | 05 SOUTHWEST | 526936 | YOAKUM_345 | 345 | 9.9314 | 9.9266 | 0.0048
GEN-2018-081 | 05 SOUTHWEST | 527009 | BRU_SUB 6 | 230 | 15.6513 | 15.6448 | 0.0065
GEN-2018-081 | 05 SOUTHWEST | 527028 | INK_BASIN 6 | 230 | 11.2413 | 11.2383 | 0.003
GEN-2018-081 | 05 SOUTHWEST | 527149 | MUSTANG 6 | 230 | 17.9238 | 17.918 | 0.0058
GEN-2018-081 | 05 SOUTHWEST | 527610 | SAGA_SCOL 7 | 345 | 10.2321 | 10.2227 | 0.0094
GEN-2018-081 | 05 SOUTHWEST | 527655 | RSVLT_CC_E 7 | 345 | 10.0154 | 10.0064 | 0.009
GEN-2018-081 | 05 SOUTHWEST | 527802 | EDDY_CNTY 7 | 345 | 7.3273 | 7.3244 | 0.0029
GEN-2018-081 | 05 SOUTHWEST | 527896 | HOBBS_INT 7 | 345 | 12.0143 | 12.0072 | 0.0071
GEN-2018-081 | 05 SOUTHWEST | 560022 | CRAWFISH_DR | 345 | 13.842 | 13.8338 | 0.0082
GEN-2018-081 | 05 SOUTHWEST | 560035 | GRAPEVINE | 345 | 6.4589 | 6.4578 | 0.0011
GEN-2018-081 | 05 SOUTHWEST | 511553 | CHISHOLM7 | 345 | 12.3397 | 12.3386 | 0.0011
GEN-2018-081 | 05 SOUTHWEST | 515458 | BORDER 7 | 345 | 8.2517 | 8.2511 | 0.0006
GEN-2018-081 | 05 SOUTHWEST | 515554 | BVRCNTY7 | 345 | 15.3093 | 15.3086 | 0.0007
GEN-2018-081 | 05 SOUTHWEST | 522800 | MU-TULIA 3 | 115 | 5.2034 | 5.2017 | 0.0017
GEN-2018-081 | 05 SOUTHWEST | 523095 | HITCHLAND 6 | 230 | 14.5761 | 14.5752 | 0.0009
GEN-2018-081 | 05 SOUTHWEST | 523101 | NOBLE_WND 7 | 345 | 14.9103 | 14.9092 | 0.0011
GEN-2018-081 | 05 SOUTHWEST | 523112 | NOVUS1 7 | 345 | 14.6716 | 14.6705 | 0.0011
GEN-2018-081 | 05 SOUTHWEST | 523220 | XIT_INTG 3 | 115 | 5.8284 | 5.828 | 0.0004
GEN-2018-081 | 05 SOUTHWEST | 523266 | PRINGLE 3 | 115 | 11.3365 | 11.3361 | 0.0004
GEN-2018-081 | 05 SOUTHWEST | 523308 | MOORE_E 3 | 115 | 10.3425 | 10.3417 | 0.0008
GEN-2018-081 | 05 SOUTHWEST | 523332 | EXELL_TP 3 | 115 | 7.627 | 7.6264 | 0.0006
GEN-2018-081 | 05 SOUTHWEST | 523339 | FAIN 3 | 115 | 8.4872 | 8.4865 | 0.0007
GEN-2018-081 | 05 SOUTHWEST | 523551 | HUTCHISON 6 | 230 | 7.288 | 7.2873 | 0.0007
GEN-2018-081 | 05 SOUTHWEST | 523771 | GRAPEVINE 6 | 230 | 5.9762 | 5.9759 | 0.0003
GEN-2018-081 | 05 SOUTHWEST | 523823 | CARPENTER 7 | 345 | 6.5781 | 6.578 | 0.0001
GEN-2018-081 | 05 SOUTHWEST | 524009 | CHERRY 3 | 115 | 18.7893 | 18.7853 | 0.004
GEN-2018-081 | 05 SOUTHWEST | 524043 | NICHOLS 3 | 115 | 30.649 | 30.6415 | 0.0075
GEN-2018-081 | 05 SOUTHWEST | 524106 | NORTHWEST 3 | 115 | 11.5491 | 11.5472 | 0.0019
GEN-2018-081 | 05 SOUTHWEST | 524136 | HASTINGS 3 | 115 | 14.3234 | 14.3211 | 0.0023
GEN-2018-081 | 05 SOUTHWEST | 524163 | EAST_PLANT 6 | 230 | 13.8955 | 13.8917 | 0.0038
GEN-2018-081 | 05 SOUTHWEST | 524243 | OUTPOST 3 | 115 | 10.275 | 10.2724 | 0.0026
GEN-2018-081 | 05 SOUTHWEST | 524276 | WILDOR_WND 6 | 230 | 5.2234 | 5.2216 | 0.0018
GEN-2018-081 | 05 SOUTHWEST | 524299 | SPNSPUR_COL7 | 345 | 5.3278 | 5.3266 | 0.0012
GEN-2018-081 | 05 SOUTHWEST | 524364 | RANDALL 3 | 115 | 21.0733 | 21.0656 | 0.0077
GEN-2018-081 | 05 SOUTHWEST | 524377 | FARMERS 3 | 115 | 15.4368 | 15.4329 | 0.0039
GEN-2018-081 | 05 SOUTHWEST | 524397 | ARROWHEAD 3 | 115 | 13.6793 | 13.6766 | 0.0027
GEN-2018-081 | 05 SOUTHWEST | 524404 | OWENSCORN 3 | 115 | 15.0594 | 15.0558 | 0.0036
GEN-2018-081 | 05 SOUTHWEST | 524502 | NORTON 3 | 115 | 2.9186 | 2.9184 | 0.0002
GEN-2018-081 | 05 SOUTHWEST | 524544 | SPRING_DRW 3 | 115 | 6.4069 | 6.4062 | 0.0007
GEN-2018-081 | 05 SOUTHWEST | 524567 | NE_HEREFORD3 | 115 | 9.9092 | 9.898 | 0.0112
GEN-2018-081 | 05 SOUTHWEST | 524575 | DS-#25+ 3 | 115 | 10.215 | 10.2035 | 0.0115
GEN-2018-081 | 05 SOUTHWEST | 524606 | HEREFORD 3 | 115 | 11.1394 | 11.1252 | 0.0142
GEN-2018-081 | 05 SOUTHWEST | 524669 | DS-#20 3 | 115 | 6.2762 | 6.2718 | 0.0044
GEN-2018-081 | 05 SOUTHWEST | 524688 | DS-#3 2 | 69 | 2.9614 | 2.9607 | 0.0007
GEN-2018-081 | 05 SOUTHWEST | 524721 | DS-#15&#19+2 | 69 | 3.5539 | 3.5531 | 0.0008
GEN-2018-081 | 05 SOUTHWEST | 524728 | DS-CASTRO 2 | 69 | 4.2749 | 4.2736 | 0.0013
GEN-2018-081 | 05 SOUTHWEST | 524764 | NORRIS_TP 3 | 115 | 11.4074 | 11.3928 | 0.0146
GEN-2018-081 | 05 SOUTHWEST | 524773 | E_CLOVIS 3 | 115 | 8.962 | 8.9534 | 0.0086
GEN-2018-081 | 05 SOUTHWEST | 524776 | N_CLOVIS_TP3 | 115 | 7.4744 | 7.4689 | 0.0055
GEN-2018-081 | 05 SOUTHWEST | 524797 | PERIMETER 3 | 115 | 6.5512 | 6.5468 | 0.0044
GEN-2018-081 | 05 SOUTHWEST | 524821 | CURRY 2 | 69 | 4.4284 | 4.4271 | 0.0013
GEN-2018-081 | 05 SOUTHWEST | 524831 | FE-HOLLAND 3 | 115 | 9.2431 | 9.2341 | 0.009
GEN-2018-081 | 05 SOUTHWEST | 524838 | FE-CLOVIS2+3 | 115 | 10.7942 | 10.7812 | 0.013
GEN-2018-081 | 05 SOUTHWEST | 524863 | FE-CHZPLT 3 | 115 | 8.0228 | 8.0158 | 0.007
GEN-2018-081 | 05 SOUTHWEST | 524889 | SN_JUAN_WND6 | 230 | 4.6556 | 4.6538 | 0.0018
GEN-2018-081 | 05 SOUTHWEST | 524923 | PORTALES 2 | 69 | 7.5604 | 7.5567 | 0.0037
GEN-2018-081 | 05 SOUTHWEST | 524935 | KILGORE 3 | 115 | 6.1488 | 6.1447 | 0.0041
GEN-2018-081 | 05 SOUTHWEST | 524977 | GREYHOUND 3 | 115 | 5.6862 | 5.6828 | 0.0034
GEN-2018-081 | 05 SOUTHWEST | 525008 | MULESH_CTY 2 | 69 | 4.2533 | 4.2509 | 0.0024
GEN-2018-081 | 05 SOUTHWEST | 525017 | EMULESH&VLY2 | 69 | 4.2591 | 4.2567 | 0.0024
GEN-2018-081 | 05 SOUTHWEST | 525023 | BC-BAIL_MTR2 | 69 | 5.2707 | 5.2671 | 0.0036
GEN-2018-081 | 05 SOUTHWEST | 525132 | LC-N_OLTON 2 | 69 | 3.0771 | 3.0762 | 0.0009
GEN-2018-081 | 05 SOUTHWEST | 525154 | HAPPY_INT 3 | 115 | 5.4569 | 5.4554 | 0.0015
GEN-2018-081 | 05 SOUTHWEST | 525203 | SW-KRESS 2 | 69 | 4.4978 | 4.4969 | 0.0009
GEN-2018-081 | 05 SOUTHWEST | 525224 | KRESS_RURL 2 | 69 | 2.5281 | 2.5278 | 0.0003
GEN-2018-081 | 05 SOUTHWEST | 525225 | KRESS_RURAL3 | 115 | 5.9704 | 5.9678 | 0.0026
GEN-2018-081 | 05 SOUTHWEST | 525257 | N_PLAINVEW 3 | 115 | 5.2521 | 5.2502 | 0.0019
GEN-2018-081 | 05 SOUTHWEST | 525271 | KISER 2 | 69 | 3.4985 | 3.498 | 0.0005
GEN-2018-081 | 05 SOUTHWEST | 525279 | WSTRIDGE_TP3 | 69 | 4.2644 | 4.2634 | 0.001
GEN-2018-081 | 05 SOUTHWEST | 525307 | E_PLAINVEW 2 | 69 | 2.4781 | 2.4778 | 0.0003
GEN-2018-081 | 05 SOUTHWEST | 525316 | LH-PROVDNCE2 | 69 | 3.4185 | 3.418 | 0.0005
GEN-2018-081 | 05 SOUTHWEST | 525339 | AIKEN_RURL 2 | 69 | 2.7745 | 2.7741 | 0.0004
GEN-2018-081 | 05 SOUTHWEST | 525404 | LC-OLTON 2 | 69 | 4.4829 | 4.4811 | 0.0018
GEN-2018-081 | 05 SOUTHWEST | 525425 | CORNER 2 | 69 | 3.6326 | 3.6319 | 0.0007
GEN-2018-081 | 05 SOUTHWEST | 525606 | AMHERST 2 | 69 | 2.3408 | 2.3403 | 0.0005
GEN-2018-081 | 05 SOUTHWEST | 525657 | W_ANTON_TP 2 | 69 | 4.1079 | 4.1061 | 0.0018
GEN-2018-081 | 05 SOUTHWEST | 525694 | HOBGOOD 2 | 69 | 3.4381 | 3.4369 | 0.0012
GEN-2018-081 | 05 SOUTHWEST | 525731 | SP-ABERNTHY2 | 69 | 3.0093 | 3.0091 | 0.0002
GEN-2018-081 | 05 SOUTHWEST | 525738 | HALECENTER 2 | 69 | 2.4566 | 2.4565 | 0.0001
GEN-2018-081 | 05 SOUTHWEST | 525745 | LH-HALECTR 2 | 69 | 2.4289 | 2.4288 | 0.0001
GEN-2018-081 | 05 SOUTHWEST | 525779 | FLOYD_CNTY 2 | 69 | 5.401 | 5.4003 | 0.0007
GEN-2018-081 | 05 SOUTHWEST | 525803 | BLANCO 3 | 115 | 5.0451 | 5.0444 | 0.0007
GEN-2018-081 | 05 SOUTHWEST | 525853 | LH-WIL&ELN+2 | 69 | 2.5404 | 2.5403 | 0.0001
GEN-2018-081 | 05 SOUTHWEST | 525885 | SP-NEWDEAL 2 | 69 | 3.3073 | 3.3071 | 0.0002
GEN-2018-081 | 05 SOUTHWEST | 525926 | CROSBY 3 | 115 | 4.7129 | 4.7124 | 0.0005
GEN-2018-081 | 05 SOUTHWEST | 526009 | LC-LEVLND#22 | 69 | 4.2645 | 4.2634 | 0.0011
GEN-2018-081 | 05 SOUTHWEST | 526012 | LOST_DRAW 3 | 115 | 5.5483 | 5.5474 | 0.0009
GEN-2018-081 | 05 SOUTHWEST | 526042 | COBLE 2 | 69 | 2.2615 | 2.2612 | 0.0003
GEN-2018-081 | 05 SOUTHWEST | 526048 | LVLNDCTY_TP2 | 69 | 4.2645 | 4.2634 | 0.0011
GEN-2018-081 | 05 SOUTHWEST | 526109 | SP-ERSKINE 3 | 115 | 10.9787 | 10.9754 | 0.0033
GEN-2018-081 | 05 SOUTHWEST | 526146 | INDIANA 3 | 115 | 9.3032 | 9.3008 | 0.0024
GEN-2018-081 | 05 SOUTHWEST | 526159 | CARLISLE 2 | 69 | 2.5568 | 2.5567 | 0.0001
GEN-2018-081 | 05 SOUTHWEST | 526162 | LP-DOUD_TP 3 | 115 | 11.325 | 11.3215 | 0.0035
GEN-2018-081 | 05 SOUTHWEST | 526192 | MURPHY 3 | 115 | 10.2503 | 10.2476 | 0.0027
GEN-2018-081 | 05 SOUTHWEST | 526213 | ALLEN 3 | 115 | 10.4502 | 10.4479 | 0.0023
GEN-2018-081 | 05 SOUTHWEST | 526267 | LUBBCK_STH 2 | 69 | 4.3104 | 4.3102 | 0.0002
GEN-2018-081 | 05 SOUTHWEST | 526297 | LUBBCK_EST 2 | 69 | 7.8955 | 7.8948 | 0.0007
GEN-2018-081 | 05 SOUTHWEST | 526360 | COCHRAN 2 | 69 | 5.6074 | 5.6066 | 0.0008
GEN-2018-081 | 05 SOUTHWEST | 526481 | SP-WOLF_TP 3 | 115 | 10.8642 | 10.8609 | 0.0033
GEN-2018-081 | 05 SOUTHWEST | 526491 | LG-CLAUENE 3 | 115 | 7.9267 | 7.9242 | 0.0025
GEN-2018-081 | 05 SOUTHWEST | 526602 | WOODROW 3 | 115 | 9.1323 | 9.1308 | 0.0015
GEN-2018-081 | 05 SOUTHWEST | 526676 | GRASSLAND 3 | 115 | 6.8633 | 6.8626 | 0.0007
GEN-2018-081 | 05 SOUTHWEST | 526679 | CIRRUS_WND 6 | 230 | 4.6792 | 4.6786 | 0.0006
GEN-2018-081 | 05 SOUTHWEST | 526735 | TERRY_CNTY 2 | 69 | 7.0347 | 7.034 | 0.0007
GEN-2018-081 | 05 SOUTHWEST | 526784 | AMOCOWASSON6 | 230 | 15.6353 | 15.6302 | 0.0051
GEN-2018-081 | 05 SOUTHWEST | 526792 | PRENTICE 3 | 115 | 6.0286 | 6.0279 | 0.0007
GEN-2018-081 | 05 SOUTHWEST | 526928 | PLAINS_INT 3 | 115 | 10.0196 | 10.0179 | 0.0017
GEN-2018-081 | 05 SOUTHWEST | 527010 | OXYBRU 6 | 230 | 15.5052 | 15.4987 | 0.0065
GEN-2018-081 | 05 SOUTHWEST | 527011 | XTO_MAHONEY6 | 230 | 15.3578 | 15.3519 | 0.0059
GEN-2018-081 | 05 SOUTHWEST | 527027 | INK_BASIN 3 | 115 | 13.258 | 13.2565 | 0.0015
GEN-2018-081 | 05 SOUTHWEST | 527041 | ARCO_TP 3 | 115 | 13.6807 | 13.6787 | 0.002
GEN-2018-081 | 05 SOUTHWEST | 527130 | DENVER_N 3 | 115 | 22.5277 | 22.5235 | 0.0042
GEN-2018-081 | 05 SOUTHWEST | 527146 | MUSTANG 3 | 115 | 24.0628 | 24.0584 | 0.0044
GEN-2018-081 | 05 SOUTHWEST | 527151 | GS-MUSTANG 6 | 230 | 17.9238 | 17.918 | 0.0058
GEN-2018-081 | 05 SOUTHWEST | 527194 | LG-PLSHILL 3 | 115 | 7.9741 | 7.9734 | 0.0007
GEN-2018-081 | 05 SOUTHWEST | 527257 | FLATLAND 3 | 115 | 6.6733 | 6.6727 | 0.0006
GEN-2018-081 | 05 SOUTHWEST | 527276 | SEMINOLE 6 | 230 | 8.197 | 8.1959 | 0.0011
GEN-2018-081 | 05 SOUTHWEST | 527483 | CHAVES_CNTY6 | 230 | 4.4929 | 4.4919 | 0.001
GEN-2018-081 | 05 SOUTHWEST | 527599 | SAGA_SDCOL 7 | 345 | 10.2321 | 10.2227 | 0.0094
GEN-2018-081 | 05 SOUTHWEST | 527654 | RSVLT_CC_W 7 | 345 | 8.7265 | 8.7198 | 0.0067
GEN-2018-081 | 05 SOUTHWEST | 527799 | EDDY_NORTH 6 | 230 | 9.402 | 9.3992 | 0.0028
GEN-2018-081 | 05 SOUTHWEST | 527894 | HOBBS_INT 6 | 230 | 19.4767 | 19.4708 | 0.0059
GEN-2018-081 | 05 SOUTHWEST | 527965 | KIOWA 7 | 345 | 8.82 | 8.8163 | 0.0037
GEN-2018-081 | 05 SOUTHWEST | 528027 | RDRUNNER 7 | 345 | 8.6815 | 8.678 | 0.0035
GEN-2018-081 | 05 SOUTHWEST | 576397 | G10014G11022 | 345 | 10.3812 | 10.3808 | 0.0004
GEN-2018-081 | 05 SOUTHWEST | 762216 | G17-151TAP | 345 | 8.5119 | 8.5096 | 0.0023
GEN-2018-081 | 05 SOUTHWEST | 763087 | GEN-2018-073 | 345 | 11.9423 | 11.9362 | 0.0061
GEN-2018-081 | 05 SOUTHWEST | 763516 | GEN-2019-011 | 345 | 9.2852 | 9.281 | 0.0042
GEN-2018-089 | 05 SOUTHWEST | 525461 | NEWHART 6 | 230 | 10.9971 | 10.6028 | 0.3943
GEN-2018-089 | 05 SOUTHWEST | 523959 | POTTER_CO 6 | 230 | 22.4376 | 22.3805 | 0.0571
GEN-2018-089 | 05 SOUTHWEST | 525213 | SWISHER 6 | 230 | 10.3853 | 10.2554 | 0.1299
GEN-2018-089 | 05 SOUTHWEST | 525460 | NEWHART 3 | 115 | 14.9423 | 14.7048 | 0.2375
GEN-2018-089 | 05 SOUTHWEST | 525481 | PLANT_X 6 | 230 | 24.1838 | 24.0767 | 0.1071
GEN-2018-089 | 05 SOUTHWEST | 763186 | GEN-2018-089 | 230 | 10.6882 | 10.2934 | 0.3948
GEN-2018-089 | 05 SOUTHWEST | 523323 | MCDWL_CREEK6 | 230 | 8.9802 | 8.9736 | 0.0066
GEN-2018-089 | 05 SOUTHWEST | 523869 | CHAN+TASCOS6 | 230 | 4.2464 | 4.2447 | 0.0017
GEN-2018-089 | 05 SOUTHWEST | 523961 | POTTER_CO 7 | 345 | 11.6631 | 11.6527 | 0.0104
GEN-2018-089 | 05 SOUTHWEST | 523979 | HARRNG_EST 6 | 230 | 26.9856 | 26.9326 | 0.053
GEN-2018-089 | 05 SOUTHWEST | 524010 | ROLLHILLS 6 | 230 | 20.2306 | 20.1942 | 0.0364
GEN-2018-089 | 05 SOUTHWEST | 524267 | BUSHLAND 6 | 230 | 10.1739 | 10.1617 | 0.0122
GEN-2018-089 | 05 SOUTHWEST | 524415 | AMA_SOUTH 6 | 230 | 13.6408 | 13.6135 | 0.0273
GEN-2018-089 | 05 SOUTHWEST | 524746 | CASTRO_CNTY3 | 115 | 9.822 | 9.793 | 0.029
GEN-2018-089 | 05 SOUTHWEST | 525124 | HART_INDUST3 | 115 | 7.4925 | 7.4476 | 0.0449
GEN-2018-089 | 05 SOUTHWEST | 525192 | KRESS_INT 3 | 115 | 11.9205 | 11.8521 | 0.0684
GEN-2018-089 | 05 SOUTHWEST | 525212 | SWISHER 3 | 115 | 11.4972 | 11.43 | 0.0672
GEN-2018-089 | 05 SOUTHWEST | 525480 | PLANT_X 3 | 115 | 19.2796 | 19.2293 | 0.0503
GEN-2018-089 | 05 SOUTHWEST | 525531 | TOLK 6 | 230 | 31.4946 | 31.4127 | 0.0819
GEN-2018-089 | 05 SOUTHWEST | 525830 | TUCO_INT 6 | 230 | 21.9895 | 21.9453 | 0.0442
GEN-2018-089 | 05 SOUTHWEST | 526435 | SUNDOWN 6 | 230 | 11.7438 | 11.7358 | 0.008
GEN-2018-089 | 05 SOUTHWEST | 760498 | G17-146-TAP | 230 | 7.745 | 7.7352 | 0.0098
GEN-2018-089 | 05 SOUTHWEST | 763120 | GEN-2018-081 | 230 | 17.3907 | 17.3362 | 0.0545
GEN-2018-089 | 05 SOUTHWEST | 523097 | HITCHLAND 7 | 345 | 14.9713 | 14.9691 | 0.0022
GEN-2018-089 | 05 SOUTHWEST | 523221 | XIT_INTG 6 | 230 | 3.1441 | 3.1433 | 0.0008
GEN-2018-089 | 05 SOUTHWEST | 523267 | PRINGLE 6 | 230 | 4.3435 | 4.3427 | 0.0008
GEN-2018-089 | 05 SOUTHWEST | 523309 | MOORE_CNTY 6 | 230 | 6.6813 | 6.679 | 0.0023
GEN-2018-089 | 05 SOUTHWEST | 523322 | MCDWL_CREEK3 | 115 | 9.8376 | 9.8342 | 0.0034
GEN-2018-089 | 05 SOUTHWEST | 523977 | HARRNG_WST 6 | 230 | 26.9856 | 26.9326 | 0.053
GEN-2018-089 | 05 SOUTHWEST | 523978 | HARRNG_MID 6 | 230 | 26.9856 | 26.9326 | 0.053
GEN-2018-089 | 05 SOUTHWEST | 524007 | ROLLHILLS 3 | 115 | 19.6592 | 19.6439 | 0.0153
GEN-2018-089 | 05 SOUTHWEST | 524044 | NICHOLS 6 | 230 | 26.1237 | 26.0746 | 0.0491
GEN-2018-089 | 05 SOUTHWEST | 524266 | BUSHLAND 3 | 115 | 10.3324 | 10.3263 | 0.0061
GEN-2018-089 | 05 SOUTHWEST | 524290 | WILDOR2_JUS6 | 230 | 6.9783 | 6.9729 | 0.0054
GEN-2018-089 | 05 SOUTHWEST | 524296 | SPNSPUR_WND7 | 345 | 5.3278 | 5.326 | 0.0018
GEN-2018-089 | 05 SOUTHWEST | 524365 | RANDALL 6 | 230 | 14.5681 | 14.5437 | 0.0244
GEN-2018-089 | 05 SOUTHWEST | 524414 | AMA_SOUTH 3 | 115 | 16.9088 | 16.8924 | 0.0164
GEN-2018-089 | 05 SOUTHWEST | 524623 | DEAFSMITH 6 | 230 | 8.0257 | 8.015 | 0.0107
GEN-2018-089 | 05 SOUTHWEST | 524694 | DS-#22 3 | 115 | 4.5966 | 4.5903 | 0.0063
GEN-2018-089 | 05 SOUTHWEST | 524734 | DS-#21 3 | 115 | 9.3056 | 9.2805 | 0.0251
GEN-2018-089 | 05 SOUTHWEST | 524745 | CASTRO_CNTY2 | 69 | 8.7963 | 8.7824 | 0.0139
GEN-2018-089 | 05 SOUTHWEST | 524757 | BETHEL_COL13 | 115 | 8.2391 | 8.2206 | 0.0185
GEN-2018-089 | 05 SOUTHWEST | 524909 | ROOSEVELT 6 | 230 | 9.709 | 9.7027 | 0.0063
GEN-2018-089 | 05 SOUTHWEST | 525019 | MULSHVLY_TP3 | 115 | 5.9489 | 5.9453 | 0.0036
GEN-2018-089 | 05 SOUTHWEST | 525050 | BC-KELLEY +3 | 115 | 7.782 | 7.7684 | 0.0136
GEN-2018-089 | 05 SOUTHWEST | 525056 | BC-EARTH 3 | 115 | 8.2606 | 8.2471 | 0.0135
GEN-2018-089 | 05 SOUTHWEST | 525179 | TULIA_TP 3 | 115 | 6.4624 | 6.4469 | 0.0155
GEN-2018-089 | 05 SOUTHWEST | 525191 | KRESS_INT 2 | 69 | 4.4978 | 4.492 | 0.0058
GEN-2018-089 | 05 SOUTHWEST | 525226 | KRS_RURL_TP3 | 115 | 6.4399 | 6.4231 | 0.0168
GEN-2018-089 | 05 SOUTHWEST | 525414 | LAMTON 3 | 115 | 7.6144 | 7.5928 | 0.0216
GEN-2018-089 | 05 SOUTHWEST | 525446 | RKYFORD_TP 3 | 115 | 10.1267 | 10.108 | 0.0187
GEN-2018-089 | 05 SOUTHWEST | 525454 | HALE_CNTY 3 | 115 | 10.1608 | 10.1343 | 0.0265
GEN-2018-089 | 05 SOUTHWEST | 525549 | TOLK 7 | 345 | 15.0276 | 15.0058 | 0.0218
GEN-2018-089 | 05 SOUTHWEST | 525586 | NEEDMORE 6 | 230 | 11.0214 | 11.0135 | 0.0079
GEN-2018-089 | 05 SOUTHWEST | 525636 | LAMB_CNTY 3 | 115 | 8.4389 | 8.4345 | 0.0044
GEN-2018-089 | 05 SOUTHWEST | 525637 | LAMB_CNTY 6 | 230 | 5.4027 | 5.3997 | 0.003
GEN-2018-089 | 05 SOUTHWEST | 525828 | TUCO_INT 3 | 115 | 19.3618 | 19.3394 | 0.0224
GEN-2018-089 | 05 SOUTHWEST | 525832 | TUCO_INT 7 | 345 | 14.0745 | 14.0599 | 0.0146
GEN-2018-089 | 05 SOUTHWEST | 525840 | ANTELOPE_1 6 | 230 | 21.8013 | 21.7578 | 0.0435
GEN-2018-089 | 05 SOUTHWEST | 525957 | HALE_WNDCL16 | 230 | 10.5196 | 10.5106 | 0.009
GEN-2018-089 | 05 SOUTHWEST | 526161 | CARLISLE 6 | 230 | 10.473 | 10.466 | 0.007
GEN-2018-089 | 05 SOUTHWEST | 526337 | JONES 6 | 230 | 16.6076 | 16.598 | 0.0096
GEN-2018-089 | 05 SOUTHWEST | 526434 | SUNDOWN 3 | 115 | 10.8603 | 10.8575 | 0.0028
GEN-2018-089 | 05 SOUTHWEST | 526460 | AMOCO_SS 6 | 230 | 10.1771 | 10.1718 | 0.0053
GEN-2018-089 | 05 SOUTHWEST | 526525 | WOLFFORTH 6 | 230 | 13.0516 | 13.0426 | 0.009
GEN-2018-089 | 05 SOUTHWEST | 560035 | GRAPEVINE | 345 | 6.4589 | 6.4572 | 0.0017
GEN-2018-089 | 05 SOUTHWEST | 760494 | GEN-2017-146 | 230 | 7.4558 | 7.4467 | 0.0091
GEN-2018-089 | 05 SOUTHWEST | 762132 | GEN-2017-158 | 230 | 13.8646 | 13.8508 | 0.0138
GEN-2018-089 | 05 SOUTHWEST | 763241 | GEN-2018-097 | 230 | 24.4484 | 24.4 | 0.0484
GEN-2018-089 | 05 SOUTHWEST | 511553 | CHISHOLM7 | 345 | 12.3397 | 12.3377 | 0.002
GEN-2018-089 | 05 SOUTHWEST | 515554 | BVRCNTY7 | 345 | 15.3093 | 15.3079 | 0.0014
GEN-2018-089 | 05 SOUTHWEST | 522800 | MU-TULIA 3 | 115 | 5.2034 | 5.1933 | 0.0101
GEN-2018-089 | 05 SOUTHWEST | 523095 | HITCHLAND 6 | 230 | 14.5761 | 14.5741 | 0.002
GEN-2018-089 | 05 SOUTHWEST | 523101 | NOBLE_WND 7 | 345 | 14.9103 | 14.9081 | 0.0022
GEN-2018-089 | 05 SOUTHWEST | 523112 | NOVUS1 7 | 345 | 14.6716 | 14.6695 | 0.0021
GEN-2018-089 | 05 SOUTHWEST | 523220 | XIT_INTG 3 | 115 | 5.8284 | 5.8272 | 0.0012
GEN-2018-089 | 05 SOUTHWEST | 523266 | PRINGLE 3 | 115 | 11.3365 | 11.3349 | 0.0016
GEN-2018-089 | 05 SOUTHWEST | 523308 | MOORE_E 3 | 115 | 10.3425 | 10.3398 | 0.0027
GEN-2018-089 | 05 SOUTHWEST | 523332 | EXELL_TP 3 | 115 | 7.627 | 7.625 | 0.002
GEN-2018-089 | 05 SOUTHWEST | 523339 | FAIN 3 | 115 | 8.4872 | 8.4847 | 0.0025
GEN-2018-089 | 05 SOUTHWEST | 523551 | HUTCHISON 6 | 230 | 7.288 | 7.2854 | 0.0026
GEN-2018-089 | 05 SOUTHWEST | 523771 | GRAPEVINE 6 | 230 | 5.9762 | 5.9751 | 0.0011
GEN-2018-089 | 05 SOUTHWEST | 523823 | CARPENTER 7 | 345 | 6.5781 | 6.5779 | 0.0002
GEN-2018-089 | 05 SOUTHWEST | 524009 | CHERRY 3 | 115 | 18.7893 | 18.7753 | 0.014
GEN-2018-089 | 05 SOUTHWEST | 524043 | NICHOLS 3 | 115 | 30.649 | 30.6218 | 0.0272
GEN-2018-089 | 05 SOUTHWEST | 524106 | NORTHWEST 3 | 115 | 11.5491 | 11.5427 | 0.0064
GEN-2018-089 | 05 SOUTHWEST | 524136 | HASTINGS 3 | 115 | 14.3234 | 14.315 | 0.0084
GEN-2018-089 | 05 SOUTHWEST | 524163 | EAST_PLANT 6 | 230 | 13.8955 | 13.8812 | 0.0143
GEN-2018-089 | 05 SOUTHWEST | 524243 | OUTPOST 3 | 115 | 10.275 | 10.269 | 0.006
GEN-2018-089 | 05 SOUTHWEST | 524276 | WILDOR_WND 6 | 230 | 5.2234 | 5.2206 | 0.0028
GEN-2018-089 | 05 SOUTHWEST | 524299 | SPNSPUR_COL7 | 345 | 5.3278 | 5.326 | 0.0018
GEN-2018-089 | 05 SOUTHWEST | 524364 | RANDALL 3 | 115 | 21.0733 | 21.0458 | 0.0275
GEN-2018-089 | 05 SOUTHWEST | 524377 | FARMERS 3 | 115 | 15.4368 | 15.4231 | 0.0137
GEN-2018-089 | 05 SOUTHWEST | 524397 | ARROWHEAD 3 | 115 | 13.6793 | 13.6695 | 0.0098
GEN-2018-089 | 05 SOUTHWEST | 524404 | OWENSCORN 3 | 115 | 15.0594 | 15.0464 | 0.013
GEN-2018-089 | 05 SOUTHWEST | 524544 | SPRING_DRW 3 | 115 | 6.4069 | 6.4045 | 0.0024
GEN-2018-089 | 05 SOUTHWEST | 524619 | DFSMTH_EST 3 | 115 | 11.9939 | 11.9796 | 0.0143
GEN-2018-089 | 05 SOUTHWEST | 524622 | DFSMTH_WST 3 | 115 | 11.9945 | 11.9802 | 0.0143
GEN-2018-089 | 05 SOUTHWEST | 524630 | TIERABLANCA3 | 115 | 12.3344 | 12.3191 | 0.0153
GEN-2018-089 | 05 SOUTHWEST | 524688 | DS-#3 2 | 69 | 2.9614 | 2.9598 | 0.0016
GEN-2018-089 | 05 SOUTHWEST | 524721 | DS-#15&#19+2 | 69 | 3.5539 | 3.5517 | 0.0022
GEN-2018-089 | 05 SOUTHWEST | 524728 | DS-CASTRO 2 | 69 | 4.2749 | 4.2716 | 0.0033
GEN-2018-089 | 05 SOUTHWEST | 524770 | PLSNT_HILL 6 | 230 | 6.517 | 6.5142 | 0.0028
GEN-2018-089 | 05 SOUTHWEST | 524875 | OASIS 6 | 230 | 7.8784 | 7.8746 | 0.0038
GEN-2018-089 | 05 SOUTHWEST | 524908 | ROOSEVELT 3 | 115 | 11.1454 | 11.1409 | 0.0045
GEN-2018-089 | 05 SOUTHWEST | 525018 | MULESHVALLY3 | 115 | 5.5409 | 5.5378 | 0.0031
GEN-2018-089 | 05 SOUTHWEST | 525028 | BAILEYCO 3 | 115 | 5.8021 | 5.7988 | 0.0033
GEN-2018-089 | 05 SOUTHWEST | 525154 | HAPPY_INT 3 | 115 | 5.4569 | 5.4479 | 0.009
GEN-2018-089 | 05 SOUTHWEST | 525203 | SW-KRESS 2 | 69 | 4.4978 | 4.492 | 0.0058
GEN-2018-089 | 05 SOUTHWEST | 525224 | KRESS_RURL 2 | 69 | 2.5281 | 2.5263 | 0.0018
GEN-2018-089 | 05 SOUTHWEST | 525225 | KRESS_RURAL3 | 115 | 5.9704 | 5.9559 | 0.0145
GEN-2018-089 | 05 SOUTHWEST | 525257 | N_PLAINVEW 3 | 115 | 5.2521 | 5.2435 | 0.0086
GEN-2018-089 | 05 SOUTHWEST | 525326 | COX 3 | 115 | 6.2736 | 6.2644 | 0.0092
GEN-2018-089 | 05 SOUTHWEST | 525393 | ROCKYFORD 3 | 115 | 9.0431 | 9.0282 | 0.0149
GEN-2018-089 | 05 SOUTHWEST | 525413 | LAMTON 2 | 69 | 5.1693 | 5.1634 | 0.0059
GEN-2018-089 | 05 SOUTHWEST | 525440 | LC-S_OLTON+3 | 115 | 7.1982 | 7.1831 | 0.0151
GEN-2018-089 | 05 SOUTHWEST | 525453 | HALE_CNTY 2 | 69 | 6.9062 | 6.899 | 0.0072
GEN-2018-089 | 05 SOUTHWEST | 525585 | BLUECLDPOI 6 | 230 | 11.0214 | 11.0135 | 0.0079
GEN-2018-089 | 05 SOUTHWEST | 525635 | LAMB_CNTY 2 | 69 | 5.8992 | 5.8978 | 0.0014
GEN-2018-089 | 05 SOUTHWEST | 525780 | FLOYD_CNTY 3 | 115 | 6.2514 | 6.2473 | 0.0041
GEN-2018-089 | 05 SOUTHWEST | 525816 | TUCO_INT2 2 | 69 | 4.6524 | 4.6516 | 0.0008
GEN-2018-089 | 05 SOUTHWEST | 525826 | TUCO_INT 2 | 69 | 7.8538 | 7.8515 | 0.0023
GEN-2018-089 | 05 SOUTHWEST | 525850 | ELK_CT1 | 345 | 13.9398 | 13.9255 | 0.0143
GEN-2018-089 | 05 SOUTHWEST | 526020 | HOCKLEY 3 | 115 | 5.426 | 5.4249 | 0.0011
GEN-2018-089 | 05 SOUTHWEST | 526036 | LC-OPDYKE 3 | 115 | 5.7143 | 5.7131 | 0.0012
GEN-2018-089 | 05 SOUTHWEST | 526076 | STANTON_W 3 | 115 | 8.923 | 8.9201 | 0.0029
GEN-2018-089 | 05 SOUTHWEST | 526160 | CARLISLE 3 | 115 | 12.772 | 12.7671 | 0.0049
GEN-2018-089 | 05 SOUTHWEST | 526269 | LUBBCK_STH 6 | 230 | 15.0546 | 15.0459 | 0.0087
GEN-2018-089 | 05 SOUTHWEST | 526298 | LUBBCK_EST 3 | 115 | 14.4141 | 14.4081 | 0.006
GEN-2018-089 | 05 SOUTHWEST | 526299 | LUBBCK_EST 6 | 230 | 11.0462 | 11.0416 | 0.0046
GEN-2018-089 | 05 SOUTHWEST | 526424 | PACIFIC 3 | 115 | 9.1771 | 9.1752 | 0.0019
GEN-2018-089 | 05 SOUTHWEST | 526445 | AMOCO_TP 3 | 115 | 10.1845 | 10.1821 | 0.0024
GEN-2018-089 | 05 SOUTHWEST | 526524 | WOLFFORTH 3 | 115 | 11.2819 | 11.2787 | 0.0032
GEN-2018-089 | 05 SOUTHWEST | 526677 | GRASSLAND 6 | 230 | 5.9735 | 5.9722 | 0.0013
GEN-2018-089 | 05 SOUTHWEST | 526935 | YOAKUM 6 | 230 | 19.6825 | 19.6769 | 0.0056
GEN-2018-089 | 05 SOUTHWEST | 526936 | YOAKUM_345 | 345 | 9.9314 | 9.9287 | 0.0027
GEN-2018-089 | 05 SOUTHWEST | 527656 | CROSSROADS 7 | 345 | 11.539 | 11.5349 | 0.0041
GEN-2018-089 | 05 SOUTHWEST | 560022 | CRAWFISH_DR | 345 | 13.842 | 13.8282 | 0.0138
GEN-2018-089 | 05 SOUTHWEST | 576397 | G10014G11022 | 345 | 10.3812 | 10.3803 | 0.0009
GEN-2018-089 | 05 SOUTHWEST | 599955 | PNM-DC6 | 230 | 9.709 | 9.7027 | 0.0063
GEN-2018-089 | 05 SOUTHWEST | 763483 | GEN-2019-003 | 230 | 8.7401 | 8.7351 | 0.005
GEN-2018-089 | 05 SOUTHWEST | 511557 | CHISHOLM6 | 230 | 12.1566 | 12.1553 | 0.0013
GEN-2018-089 | 05 SOUTHWEST | 515375 | WWRDEHV7 | 345 | 22.3641 | 22.363 | 0.0011
GEN-2018-089 | 05 SOUTHWEST | 515458 | BORDER 7 | 345 | 8.2517 | 8.2506 | 0.0011
GEN-2018-089 | 05 SOUTHWEST | 515590 | PALDR2W7 | 345 | 12.8669 | 12.8659 | 0.001
GEN-2018-089 | 05 SOUTHWEST | 515618 | BALKOW 7 | 345 | 12.5807 | 12.5798 | 0.0009
GEN-2018-089 | 05 SOUTHWEST | 515677 | BADGER 7 | 345 | 13.7821 | 13.7812 | 0.0009
GEN-2018-089 | 05 SOUTHWEST | 523093 | HITCHLAND 3 | 115 | 17.3358 | 17.3342 | 0.0016
GEN-2018-089 | 05 SOUTHWEST | 523103 | NOBLE_WND 3 | 115 | 10.6199 | 10.6196 | 0.0003
GEN-2018-089 | 05 SOUTHWEST | 523111 | NOVUS1 3 | 115 | 7.8432 | 7.843 | 0.0002
GEN-2018-089 | 05 SOUTHWEST | 523155 | OCHILTREE 6 | 230 | 4.265 | 4.2648 | 0.0002
GEN-2018-089 | 05 SOUTHWEST | 523177 | RB-SPURLCK+3 | 115 | 5.4905 | 5.4898 | 0.0007
GEN-2018-089 | 05 SOUTHWEST | 523186 | SPEARMAN 3 | 115 | 8.8127 | 8.812 | 0.0007
GEN-2018-089 | 05 SOUTHWEST | 523215 | GEN-2011-022 | 345 | 10.3812 | 10.3803 | 0.0009
GEN-2018-089 | 05 SOUTHWEST | 523217 | RB-KEMP 3 | 115 | 3.8222 | 3.8218 | 0.0004
GEN-2018-089 | 05 SOUTHWEST | 523228 | DALLAM 3 | 115 | 5.8608 | 5.8596 | 0.0012
GEN-2018-089 | 05 SOUTHWEST | 523256 | ETTER 3 | 115 | 5.4015 | 5.4007 | 0.0008
GEN-2018-089 | 05 SOUTHWEST | 523277 | VALERO 3 | 115 | 9.3729 | 9.3707 | 0.0022
GEN-2018-089 | 05 SOUTHWEST | 523304 | MOORE_W 3 | 115 | 10.3425 | 10.3398 | 0.0027
GEN-2018-089 | 05 SOUTHWEST | 523318 | DUMAS_19ST 3 | 115 | 5.8397 | 5.8387 | 0.001
GEN-2018-089 | 05 SOUTHWEST | 523325 | EXELL 3 | 115 | 6.1941 | 6.1928 | 0.0013
GEN-2018-089 | 05 SOUTHWEST | 523377 | RIVERVIEW 3 | 115 | 13.5172 | 13.5142 | 0.003
GEN-2018-089 | 05 SOUTHWEST | 523410 | CRMWA_#4 3 | 115 | 9.7322 | 9.7298 | 0.0024
GEN-2018-089 | 05 SOUTHWEST | 523478 | Q_RYTON_TP 3 | 115 | 11.9082 | 11.9072 | 0.001
GEN-2018-089 | 05 SOUTHWEST | 523544 | HUTCH_N 3 | 115 | 16.0441 | 16.0399 | 0.0042
GEN-2018-089 | 05 SOUTHWEST | 523546 | HUTCH_S 3 | 115 | 16.0441 | 16.0399 | 0.0042
GEN-2018-089 | 05 SOUTHWEST | 523770 | GRAPEVINE 3 | 115 | 7.9787 | 7.9778 | 0.0009
GEN-2018-089 | 05 SOUTHWEST | 523777 | WHEELER 6 | 230 | 6.7683 | 6.7675 | 0.0008
GEN-2018-089 | 05 SOUTHWEST | 523817 | MIDSTRM_TP 3 | 115 | 4.7119 | 4.7115 | 0.0004
GEN-2018-089 | 05 SOUTHWEST | 523853 | FINNEY 7 | 345 | 9.8362 | 9.8361 | 0.0001
GEN-2018-089 | 05 SOUTHWEST | 524016 | ASARCO 3 | 115 | 26.5107 | 26.4906 | 0.0201
GEN-2018-089 | 05 SOUTHWEST | 524018 | ASARCO_TP 3 | 115 | 28.6572 | 28.6336 | 0.0236
GEN-2018-089 | 05 SOUTHWEST | 524058 | WHITAKER 3 | 115 | 21.9266 | 21.9099 | 0.0167
GEN-2018-089 | 05 SOUTHWEST | 524072 | YARNELL_TP 3 | 115 | 7.9824 | 7.9808 | 0.0016
GEN-2018-089 | 05 SOUTHWEST | 524105 | NORTHWEST 2 | 69 | 6.3778 | 6.3766 | 0.0012
GEN-2018-089 | 05 SOUTHWEST | 524124 | BUSH 3 | 115 | 7.1605 | 7.1581 | 0.0024
GEN-2018-089 | 05 SOUTHWEST | 524162 | EAST_PLANT 3 | 115 | 22.9296 | 22.9074 | 0.0222
GEN-2018-089 | 05 SOUTHWEST | 524224 | MANHATTAN 3 | 115 | 17.2747 | 17.2596 | 0.0151
GEN-2018-089 | 05 SOUTHWEST | 524249 | SUNSET 3 | 115 | 11.7322 | 11.7252 | 0.007
GEN-2018-089 | 05 SOUTHWEST | 524322 | GEORGIA 3 | 115 | 16.8695 | 16.8531 | 0.0164
GEN-2018-089 | 05 SOUTHWEST | 524338 | SOUTHEAST 3 | 115 | 11.2307 | 11.2229 | 0.0078
GEN-2018-089 | 05 SOUTHWEST | 524341 | PRESTONWEST3 | 115 | 13.1302 | 13.1204 | 0.0098
GEN-2018-089 | 05 SOUTHWEST | 524345 | OSAGE 3 | 115 | 13.8304 | 13.8211 | 0.0093
GEN-2018-089 | 05 SOUTHWEST | 524387 | CRSE_HINDTP3 | 115 | 15.4475 | 15.4338 | 0.0137
GEN-2018-089 | 05 SOUTHWEST | 524522 | CANYON_E_TP3 | 115 | 5.853 | 5.8504 | 0.0026
GEN-2018-089 | 05 SOUTHWEST | 524530 | PALO_DURO 3 | 115 | 6.7455 | 6.7398 | 0.0057
GEN-2018-089 | 05 SOUTHWEST | 524560 | ARNOT 3 | 115 | 10.9349 | 10.9282 | 0.0067
GEN-2018-089 | 05 SOUTHWEST | 524567 | NE_HEREFORD3 | 115 | 9.9092 | 9.8995 | 0.0097
GEN-2018-089 | 05 SOUTHWEST | 524575 | DS-#25+ 3 | 115 | 10.215 | 10.2047 | 0.0103
GEN-2018-089 | 05 SOUTHWEST | 524606 | HEREFORD 3 | 115 | 11.1394 | 11.1272 | 0.0122
GEN-2018-089 | 05 SOUTHWEST | 524679 | DIMMIT_S_TP2 | 69 | 2.9182 | 2.9166 | 0.0016
GEN-2018-089 | 05 SOUTHWEST | 524768 | PLSNT_HILL 3 | 115 | 10.5272 | 10.5234 | 0.0038
GEN-2018-089 | 05 SOUTHWEST | 524822 | CURRY 3 | 115 | 11.4402 | 11.4348 | 0.0054
GEN-2018-089 | 05 SOUTHWEST | 524874 | OASIS 3 | 115 | 10.0542 | 10.0508 | 0.0034
GEN-2018-089 | 05 SOUTHWEST | 524885 | SN_JUAN_TAP6 | 230 | 4.8705 | 4.8698 | 0.0007
GEN-2018-089 | 05 SOUTHWEST | 524924 | PORTALES 3 | 115 | 7.5524 | 7.5504 | 0.002
GEN-2018-089 | 05 SOUTHWEST | 525027 | BAILEYCO 2 | 69 | 5.2707 | 5.2691 | 0.0016
GEN-2018-089 | 05 SOUTHWEST | 525116 | DS-#12 2 | 69 | 2.3738 | 2.3728 | 0.001
GEN-2018-089 | 05 SOUTHWEST | 525132 | LC-N_OLTON 2 | 69 | 3.0771 | 3.075 | 0.0021
GEN-2018-089 | 05 SOUTHWEST | 525153 | HAPPY_INT 2 | 69 | 5.1031 | 5.0984 | 0.0047
GEN-2018-089 | 05 SOUTHWEST | 525249 | LH-PLW&FNY+2 | 69 | 1.603 | 1.6023 | 0.0007
GEN-2018-089 | 05 SOUTHWEST | 525272 | KISER 3 | 115 | 5.2683 | 5.2599 | 0.0084
GEN-2018-089 | 05 SOUTHWEST | 525291 | PLAINVW_TP 2 | 69 | 6.4824 | 6.4759 | 0.0065
GEN-2018-089 | 05 SOUTHWEST | 525298 | S_PLAINVEW 2 | 69 | 2.5852 | 2.5842 | 0.001
GEN-2018-089 | 05 SOUTHWEST | 525325 | COX 2 | 69 | 3.4185 | 3.4168 | 0.0017
GEN-2018-089 | 05 SOUTHWEST | 525404 | LC-OLTON 2 | 69 | 4.4829 | 4.4785 | 0.0044
GEN-2018-089 | 05 SOUTHWEST | 525425 | CORNER 2 | 69 | 3.6326 | 3.6306 | 0.002
GEN-2018-089 | 05 SOUTHWEST | 525432 | SP-HALFWAY+2 | 69 | 5.8641 | 5.8588 | 0.0053
GEN-2018-089 | 05 SOUTHWEST | 525584 | BLUECLDCOL 6 | 230 | 10.4275 | 10.4204 | 0.0071
GEN-2018-089 | 05 SOUTHWEST | 525613 | W_LITTLFLD 2 | 69 | 2.9684 | 2.9681 | 0.0003
GEN-2018-089 | 05 SOUTHWEST | 525620 | LTFLD_S&CTY2 | 69 | 4.1727 | 4.172 | 0.0007
GEN-2018-089 | 05 SOUTHWEST | 525650 | LC-LTTLFLD+2 | 69 | 4.9319 | 4.931 | 0.0009
GEN-2018-089 | 05 SOUTHWEST | 525687 | LC-LUMSCHAP2 | 69 | 4.6126 | 4.6118 | 0.0008
GEN-2018-089 | 05 SOUTHWEST | 525731 | SP-ABERNTHY2 | 69 | 3.0093 | 3.0089 | 0.0004
GEN-2018-089 | 05 SOUTHWEST | 525738 | HALECENTER 2 | 69 | 2.4566 | 2.4564 | 0.0002
GEN-2018-089 | 05 SOUTHWEST | 525763 | CALLAHAN 3 | 115 | 5.5668 | 5.5626 | 0.0042
GEN-2018-089 | 05 SOUTHWEST | 525779 | FLOYD_CNTY 2 | 69 | 5.401 | 5.3992 | 0.0018
GEN-2018-089 | 05 SOUTHWEST | 525803 | BLANCO 3 | 115 | 5.0451 | 5.0432 | 0.0019
GEN-2018-089 | 05 SOUTHWEST | 525853 | LH-WIL&ELN+2 | 69 | 2.5404 | 2.5402 | 0.0002
GEN-2018-089 | 05 SOUTHWEST | 525885 | SP-NEWDEAL 2 | 69 | 3.3073 | 3.3069 | 0.0004
GEN-2018-089 | 05 SOUTHWEST | 525926 | CROSBY 3 | 115 | 4.7129 | 4.7117 | 0.0012
GEN-2018-089 | 05 SOUTHWEST | 526019 | HOCKLEY 2 | 69 | 5.1105 | 5.1099 | 0.0006
GEN-2018-089 | 05 SOUTHWEST | 526109 | SP-ERSKINE 3 | 115 | 10.9787 | 10.9748 | 0.0039
GEN-2018-089 | 05 SOUTHWEST | 526146 | INDIANA 3 | 115 | 9.3032 | 9.3002 | 0.003
GEN-2018-089 | 05 SOUTHWEST | 526159 | CARLISLE 2 | 69 | 2.5568 | 2.5567 | 0.0001
GEN-2018-089 | 05 SOUTHWEST | 526162 | LP-DOUD_TP 3 | 115 | 11.325 | 11.3213 | 0.0037
GEN-2018-089 | 05 SOUTHWEST | 526192 | MURPHY 3 | 115 | 10.2503 | 10.2473 | 0.003
GEN-2018-089 | 05 SOUTHWEST | 526268 | LUBBCK_STH 3 | 115 | 17.6482 | 17.641 | 0.0072
GEN-2018-089 | 05 SOUTHWEST | 526297 | LUBBCK_EST 2 | 69 | 7.8955 | 7.8944 | 0.0011
GEN-2018-089 | 05 SOUTHWEST | 526361 | COCHRAN 3 | 115 | 6.4257 | 6.4249 | 0.0008
GEN-2018-089 | 05 SOUTHWEST | 526452 | AMOCO_CRYO 3 | 115 | 6.362 | 6.361 | 0.001
GEN-2018-089 | 05 SOUTHWEST | 526475 | YUMA_INT 3 | 115 | 10.7034 | 10.7002 | 0.0032
GEN-2018-089 | 05 SOUTHWEST | 526484 | LG-LEVELAND3 | 115 | 9.1775 | 9.1756 | 0.0019
GEN-2018-089 | 05 SOUTHWEST | 526676 | GRASSLAND 3 | 115 | 6.8633 | 6.8624 | 0.0009
GEN-2018-089 | 05 SOUTHWEST | 526679 | CIRRUS_WND 6 | 230 | 4.6792 | 4.6784 | 0.0008
GEN-2018-089 | 05 SOUTHWEST | 526736 | TERRY_CNTY 3 | 115 | 10.6679 | 10.6665 | 0.0014
GEN-2018-089 | 05 SOUTHWEST | 526934 | YOAKUM 3 | 115 | 19.2326 | 19.23 | 0.0026
GEN-2018-089 | 05 SOUTHWEST | 527009 | BRU_SUB 6 | 230 | 15.6513 | 15.6484 | 0.0029
GEN-2018-089 | 05 SOUTHWEST | 527028 | INK_BASIN 6 | 230 | 11.2413 | 11.24 | 0.0013
GEN-2018-089 | 05 SOUTHWEST | 527149 | MUSTANG 6 | 230 | 17.9238 | 17.9212 | 0.0026
GEN-2018-089 | 05 SOUTHWEST | 527610 | SAGA_SCOL 7 | 345 | 10.2321 | 10.229 | 0.0031
GEN-2018-089 | 05 SOUTHWEST | 527655 | RSVLT_CC_E 7 | 345 | 10.0154 | 10.0125 | 0.0029
GEN-2018-089 | 05 SOUTHWEST | 527802 | EDDY_CNTY 7 | 345 | 7.3273 | 7.3262 | 0.0011
GEN-2018-089 | 05 SOUTHWEST | 527896 | HOBBS_INT 7 | 345 | 12.0143 | 12.0114 | 0.0029
GEN-2018-089 | 05 SOUTHWEST | 531512 | HARBNGR7 | 345 | 6.5579 | 6.5578 | 0.0001
GEN-2018-089 | 05 SOUTHWEST | 560078 | G16-037-TAP | 345 | 10.1427 | 10.1422 | 0.0005
GEN-2018-089 | 05 SOUTHWEST | 560577 | G06-44 | 115 | 7.5797 | 7.5796 | 0.0001
GEN-2018-089 | 05 SOUTHWEST | 576395 | GEN-2010-014 | 345 | 10.3812 | 10.3803 | 0.0009
GEN-2018-089 | 05 SOUTHWEST | 755000 | WWDBORDT | 345 | 12.2648 | 12.2628 | 0.002
GEN-2018-089 | 05 SOUTHWEST | 762216 | G17-151TAP | 345 | 8.5119 | 8.5081 | 0.0038
GEN-2018-089 | 05 SOUTHWEST | 763087 | GEN-2018-073 | 345 | 11.9423 | 11.9321 | 0.0102
GEN-2018-089 | 05 SOUTHWEST | 763516 | GEN-2019-011 | 345 | 9.2852 | 9.2828 | 0.0024
GEN-2018-089 | 05 SOUTHWEST | 763879 | GEN-2019-056 | 115 | 20.1117 | 20.0867 | 0.025
GEN-2018-092 | 05 SOUTHWEST | 763215 | G18-092-TAP | 345 | 6.0024 | 5.2188 | 0.7836
GEN-2018-092 | 05 SOUTHWEST | 511456 | O.K.U.-7 | 345 | 6.3254 | 5.8689 | 0.4565
GEN-2018-092 | 05 SOUTHWEST | 762467 | G18-015-TAP | 345 | 5.8242 | 5.3038 | 0.5204
GEN-2018-092 | 05 SOUTHWEST | 763208 | GEN-2018-092 | 345 | 5.809 | 5.0209 | 0.7881
GEN-2018-092 | 05 SOUTHWEST | 511468 | L.E.S.-7 | 345 | 14.8644 | 14.6614 | 0.203
GEN-2018-092 | 05 SOUTHWEST | 511565 | OKLAUN HVDC7 | 345 | 6.3037 | 5.8502 | 0.4535
GEN-2018-092 | 05 SOUTHWEST | 588760 | GEN-2017-033 | 345 | 4.4427 | 4.2247 | 0.218
GEN-2018-092 | 05 SOUTHWEST | 762216 | G17-151TAP | 345 | 8.5119 | 8.3344 | 0.1775
GEN-2018-092 | 05 SOUTHWEST | 762460 | GEN-2018-015 | 345 | 5.812 | 5.2938 | 0.5182
GEN-2018-092 | 05 SOUTHWEST | 511467 | L.E.S.-4 | 138 | 25.3857 | 25.2532 | 0.1325
GEN-2018-092 | 05 SOUTHWEST | 560022 | CRAWFISH_DR | 345 | 13.842 | 13.7094 | 0.1326
GEN-2018-092 | 05 SOUTHWEST | 587744 | G16-091-TAP | 345 | 16.3944 | 16.3187 | 0.0757
GEN-2018-092 | 05 SOUTHWEST | 760938 | G17-171-TAP | 345 | 12.0416 | 11.9488 | 0.0928
GEN-2018-092 | 05 SOUTHWEST | 762217 | GEN-2017-151 | 345 | 6.1754 | 6.0858 | 0.0896
GEN-2018-092 | 05 SOUTHWEST | 763318 | GEN-2018-115 | 345 | 14.5675 | 14.3728 | 0.1947
GEN-2018-092 | 05 SOUTHWEST | 511423 | FLE TAP4 | 138 | 8.7336 | 8.7266 | 0.007
GEN-2018-092 | 05 SOUTHWEST | 511437 | COMANC-4 | 138 | 18.3773 | 18.3179 | 0.0594
GEN-2018-092 | 05 SOUTHWEST | 511439 | LWSTAP 4 | 138 | 11.6423 | 11.6179 | 0.0244
GEN-2018-092 | 05 SOUTHWEST | 511466 | L.E.S.-2 | 69 | 16.4224 | 16.4008 | 0.0216
GEN-2018-092 | 05 SOUTHWEST | 511474 | SHERID4 | 138 | 12.4494 | 12.42 | 0.0294
GEN-2018-092 | 05 SOUTHWEST | 511486 | ELGINJT4 | 138 | 10.0413 | 10.0304 | 0.0109
GEN-2018-092 | 05 SOUTHWEST | 511494 | COMMTAP4 | 138 | 22.0417 | 21.9461 | 0.0956
GEN-2018-092 | 05 SOUTHWEST | 511568 | TERRYRD7 | 345 | 11.0146 | 10.9619 | 0.0527
GEN-2018-092 | 05 SOUTHWEST | 515458 | BORDER 7 | 345 | 8.2517 | 8.246 | 0.0057
GEN-2018-092 | 05 SOUTHWEST | 515800 | GRACMNT7 | 345 | 20.5087 | 20.4462 | 0.0625
GEN-2018-092 | 05 SOUTHWEST | 525832 | TUCO_INT 7 | 345 | 14.0745 | 13.9443 | 0.1302
GEN-2018-092 | 05 SOUTHWEST | 587740 | GEN-2016-091 | 345 | 11.1551 | 11.121 | 0.0341
GEN-2018-092 | 05 SOUTHWEST | 587770 | GEN-2016-095 | 345 | 11.4525 | 11.4162 | 0.0363
GEN-2018-092 | 05 SOUTHWEST | 760939 | GEN-2017-171 | 345 | 11.9683 | 11.8767 | 0.0916
GEN-2018-092 | 05 SOUTHWEST | 763087 | GEN-2018-073 | 345 | 11.9423 | 11.8447 | 0.0976
GEN-2018-092 | 05 SOUTHWEST | 511422 | FLETCHR4 | 138 | 7.9769 | 7.971 | 0.0059
GEN-2018-092 | 05 SOUTHWEST | 511431 | LWS S4 | 138 | 11.1592 | 11.1368 | 0.0224
GEN-2018-092 | 05 SOUTHWEST | 511436 | COMANC-2 | 69 | 9.2141 | 9.2098 | 0.0043
GEN-2018-092 | 05 SOUTHWEST | 511469 | LGORE-N2 | 69 | 7.9734 | 7.9686 | 0.0048
GEN-2018-092 | 05 SOUTHWEST | 511470 | LGORE-S2 | 69 | 6.9103 | 6.9065 | 0.0038
GEN-2018-092 | 05 SOUTHWEST | 511487 | ELGINJT2 | 69 | 8.5044 | 8.5006 | 0.0038
GEN-2018-092 | 05 SOUTHWEST | 511488 | 112GORE4 | 138 | 12.8136 | 12.7853 | 0.0283
GEN-2018-092 | 05 SOUTHWEST | 511512 | RPPAPER4 | 138 | 12.0656 | 12.0399 | 0.0257
GEN-2018-092 | 05 SOUTHWEST | 511537 | ARTVLTP4 | 138 | 11.828 | 11.8022 | 0.0258
GEN-2018-092 | 05 SOUTHWEST | 511563 | ELSWORTH 4 | 138 | 9.9666 | 9.9562 | 0.0104
GEN-2018-092 | 05 SOUTHWEST | 511571 | RUSHSPR7 | 345 | 7.0502 | 7.0321 | 0.0181
GEN-2018-092 | 05 SOUTHWEST | 514801 | MINCO 7 | 345 | 23.2915 | 23.2689 | 0.0226
GEN-2018-092 | 05 SOUTHWEST | 515136 | SUNNYSD7 | 345 | 12.0848 | 12.0693 | 0.0155
GEN-2018-092 | 05 SOUTHWEST | 515802 | GRACMNT4 | 138 | 37.8367 | 37.7896 | 0.0471
GEN-2018-092 | 05 SOUTHWEST | 525830 | TUCO_INT 6 | 230 | 21.9895 | 21.893 | 0.0965
GEN-2018-092 | 05 SOUTHWEST | 525850 | ELK_CT1 | 345 | 13.9398 | 13.8123 | 0.1275
GEN-2018-092 | 05 SOUTHWEST | 526936 | YOAKUM_345 | 345 | 9.9314 | 9.9246 | 0.0068
GEN-2018-092 | 05 SOUTHWEST | 529304 | OMDUNCN4 | 138 | 6.6263 | 6.6215 | 0.0048
GEN-2018-092 | 05 SOUTHWEST | 560078 | G16-037-TAP | 345 | 10.1427 | 10.1338 | 0.0089
GEN-2018-092 | 05 SOUTHWEST | 563269 | GEN-2015-093 | 345 | 10.8212 | 10.8045 | 0.0167
GEN-2018-092 | 05 SOUTHWEST | 587794 | G16-097-TAP | 138 | 11.1766 | 11.17 | 0.0066
GEN-2018-092 | 05 SOUTHWEST | 755000 | WWDBORDT | 345 | 12.2648 | 12.2562 | 0.0086
GEN-2018-097 | 05 SOUTHWEST | 525531 | TOLK 6 | 230 | 31.4946 | 31.2053 | 0.2893
GEN-2018-097 | 05 SOUTHWEST | 524909 | ROOSEVELT 6 | 230 | 9.709 | 9.6924 | 0.0166
GEN-2018-097 | 05 SOUTHWEST | 525481 | PLANT_X 6 | 230 | 24.1838 | 24.0762 | 0.1076
GEN-2018-097 | 05 SOUTHWEST | 525549 | TOLK 7 | 345 | 15.0276 | 14.9608 | 0.0668
GEN-2018-097 | 05 SOUTHWEST | 525586 | NEEDMORE 6 | 230 | 11.0214 | 10.9948 | 0.0266
GEN-2018-097 | 05 SOUTHWEST | 525637 | LAMB_CNTY 6 | 230 | 5.4027 | 5.3959 | 0.0068
GEN-2018-097 | 05 SOUTHWEST | 525830 | TUCO_INT 6 | 230 | 21.9895 | 21.9781 | 0.0114
GEN-2018-097 | 05 SOUTHWEST | 762132 | GEN-2017-158 | 230 | 13.8646 | 13.8153 | 0.0493
GEN-2018-097 | 05 SOUTHWEST | 763241 | GEN-2018-097 | 230 | 24.4484 | 24.1541 | 0.2943
GEN-2018-097 | 05 SOUTHWEST | 523961 | POTTER_CO 7 | 345 | 11.6631 | 11.6589 | 0.0042
GEN-2018-097 | 05 SOUTHWEST | 524770 | PLSNT_HILL 6 | 230 | 6.517 | 6.5103 | 0.0067
GEN-2018-097 | 05 SOUTHWEST | 524875 | OASIS 6 | 230 | 7.8784 | 7.8689 | 0.0095
GEN-2018-097 | 05 SOUTHWEST | 524908 | ROOSEVELT 3 | 115 | 11.1454 | 11.1357 | 0.0097
GEN-2018-097 | 05 SOUTHWEST | 525213 | SWISHER 6 | 230 | 10.3853 | 10.3812 | 0.0041
GEN-2018-097 | 05 SOUTHWEST | 525461 | NEWHART 6 | 230 | 10.9971 | 10.9901 | 0.007
GEN-2018-097 | 05 SOUTHWEST | 525480 | PLANT_X 3 | 115 | 19.2796 | 19.2531 | 0.0265
GEN-2018-097 | 05 SOUTHWEST | 525585 | BLUECLDPOI 6 | 230 | 11.0214 | 10.9948 | 0.0266
GEN-2018-097 | 05 SOUTHWEST | 525636 | LAMB_CNTY 3 | 115 | 8.4389 | 8.4327 | 0.0062
GEN-2018-097 | 05 SOUTHWEST | 525828 | TUCO_INT 3 | 115 | 19.3618 | 19.3571 | 0.0047
GEN-2018-097 | 05 SOUTHWEST | 525832 | TUCO_INT 7 | 345 | 14.0745 | 14.0702 | 0.0043
GEN-2018-097 | 05 SOUTHWEST | 525840 | ANTELOPE_1 6 | 230 | 21.8013 | 21.7901 | 0.0112
GEN-2018-097 | 05 SOUTHWEST | 525957 | HALE_WNDCL16 | 230 | 10.5196 | 10.5173 | 0.0023
GEN-2018-097 | 05 SOUTHWEST | 526161 | CARLISLE 6 | 230 | 10.473 | 10.4704 | 0.0026
GEN-2018-097 | 05 SOUTHWEST | 526337 | JONES 6 | 230 | 16.6076 | 16.6044 | 0.0032
GEN-2018-097 | 05 SOUTHWEST | 526435 | SUNDOWN 6 | 230 | 11.7438 | 11.7379 | 0.0059
GEN-2018-097 | 05 SOUTHWEST | 526935 | YOAKUM 6 | 230 | 19.6825 | 19.6753 | 0.0072
GEN-2018-097 | 05 SOUTHWEST | 527656 | CROSSROADS 7 | 345 | 11.539 | 11.5286 | 0.0104
GEN-2018-097 | 05 SOUTHWEST | 599955 | PNM-DC6 | 230 | 9.709 | 9.6924 | 0.0166
GEN-2018-097 | 05 SOUTHWEST | 760498 | G17-146-TAP | 230 | 7.745 | 7.7399 | 0.0051
GEN-2018-097 | 05 SOUTHWEST | 763120 | GEN-2018-081 | 230 | 17.3907 | 17.3359 | 0.0548
GEN-2018-097 | 05 SOUTHWEST | 763483 | GEN-2019-003 | 230 | 8.7401 | 8.7269 | 0.0132
GEN-2018-097 | 05 SOUTHWEST | 523097 | HITCHLAND 7 | 345 | 14.9713 | 14.9707 | 0.0006
GEN-2018-097 | 05 SOUTHWEST | 523959 | POTTER_CO 6 | 230 | 22.4376 | 22.4313 | 0.0063
GEN-2018-097 | 05 SOUTHWEST | 524296 | SPNSPUR_WND7 | 345 | 5.3278 | 5.3271 | 0.0007
GEN-2018-097 | 05 SOUTHWEST | 524415 | AMA_SOUTH 6 | 230 | 13.6408 | 13.6389 | 0.0019
GEN-2018-097 | 05 SOUTHWEST | 524623 | DEAFSMITH 6 | 230 | 8.0257 | 8.0215 | 0.0042
GEN-2018-097 | 05 SOUTHWEST | 524768 | PLSNT_HILL 3 | 115 | 10.5272 | 10.5195 | 0.0077
GEN-2018-097 | 05 SOUTHWEST | 524822 | CURRY 3 | 115 | 11.4402 | 11.4308 | 0.0094
GEN-2018-097 | 05 SOUTHWEST | 524874 | OASIS 3 | 115 | 10.0542 | 10.0467 | 0.0075
GEN-2018-097 | 05 SOUTHWEST | 524885 | SN_JUAN_TAP6 | 230 | 4.8705 | 4.8689 | 0.0016
GEN-2018-097 | 05 SOUTHWEST | 524924 | PORTALES 3 | 115 | 7.5524 | 7.5481 | 0.0043
GEN-2018-097 | 05 SOUTHWEST | 525019 | MULSHVLY_TP3 | 115 | 5.9489 | 5.9464 | 0.0025
GEN-2018-097 | 05 SOUTHWEST | 525056 | BC-EARTH 3 | 115 | 8.2606 | 8.2571 | 0.0035
GEN-2018-097 | 05 SOUTHWEST | 525212 | SWISHER 3 | 115 | 11.4972 | 11.4945 | 0.0027
GEN-2018-097 | 05 SOUTHWEST | 525446 | RKYFORD_TP 3 | 115 | 10.1267 | 10.1202 | 0.0065
GEN-2018-097 | 05 SOUTHWEST | 525454 | HALE_CNTY 3 | 115 | 10.1608 | 10.1581 | 0.0027
GEN-2018-097 | 05 SOUTHWEST | 525460 | NEWHART 3 | 115 | 14.9423 | 14.9358 | 0.0065
GEN-2018-097 | 05 SOUTHWEST | 525584 | BLUECLDCOL 6 | 230 | 10.4275 | 10.4038 | 0.0237
GEN-2018-097 | 05 SOUTHWEST | 525635 | LAMB_CNTY 2 | 69 | 5.8992 | 5.8973 | 0.0019
GEN-2018-097 | 05 SOUTHWEST | 525780 | FLOYD_CNTY 3 | 115 | 6.2514 | 6.2508 | 0.0006
GEN-2018-097 | 05 SOUTHWEST | 525816 | TUCO_INT2 2 | 69 | 4.6524 | 4.6522 | 0.0002
GEN-2018-097 | 05 SOUTHWEST | 525826 | TUCO_INT 2 | 69 | 7.8538 | 7.8533 | 0.0005
GEN-2018-097 | 05 SOUTHWEST | 525850 | ELK_CT1 | 345 | 13.9398 | 13.9355 | 0.0043
GEN-2018-097 | 05 SOUTHWEST | 526020 | HOCKLEY 3 | 115 | 5.426 | 5.4247 | 0.0013
GEN-2018-097 | 05 SOUTHWEST | 526076 | STANTON_W 3 | 115 | 8.923 | 8.9221 | 0.0009
GEN-2018-097 | 05 SOUTHWEST | 526160 | CARLISLE 3 | 115 | 12.772 | 12.7703 | 0.0017
GEN-2018-097 | 05 SOUTHWEST | 526269 | LUBBCK_STH 6 | 230 | 15.0546 | 15.0515 | 0.0031
GEN-2018-097 | 05 SOUTHWEST | 526298 | LUBBCK_EST 3 | 115 | 14.4141 | 14.4125 | 0.0016
GEN-2018-097 | 05 SOUTHWEST | 526299 | LUBBCK_EST 6 | 230 | 11.0462 | 11.0447 | 0.0015
GEN-2018-097 | 05 SOUTHWEST | 526434 | SUNDOWN 3 | 115 | 10.8603 | 10.8578 | 0.0025
GEN-2018-097 | 05 SOUTHWEST | 526460 | AMOCO_SS 6 | 230 | 10.1771 | 10.173 | 0.0041
GEN-2018-097 | 05 SOUTHWEST | 526525 | WOLFFORTH 6 | 230 | 13.0516 | 13.0475 | 0.0041
GEN-2018-097 | 05 SOUTHWEST | 526677 | GRASSLAND 6 | 230 | 5.9735 | 5.9731 | 0.0004
GEN-2018-097 | 05 SOUTHWEST | 526934 | YOAKUM 3 | 115 | 19.2326 | 19.2296 | 0.003
GEN-2018-097 | 05 SOUTHWEST | 526936 | YOAKUM_345 | 345 | 9.9314 | 9.9285 | 0.0029
GEN-2018-097 | 05 SOUTHWEST | 527009 | BRU_SUB 6 | 230 | 15.6513 | 15.6477 | 0.0036
GEN-2018-097 | 05 SOUTHWEST | 527028 | INK_BASIN 6 | 230 | 11.2413 | 11.2395 | 0.0018
GEN-2018-097 | 05 SOUTHWEST | 527149 | MUSTANG 6 | 230 | 17.9238 | 17.9206 | 0.0032
GEN-2018-097 | 05 SOUTHWEST | 527610 | SAGA_SCOL 7 | 345 | 10.2321 | 10.2244 | 0.0077
GEN-2018-097 | 05 SOUTHWEST | 527655 | RSVLT_CC_E 7 | 345 | 10.0154 | 10.0079 | 0.0075
GEN-2018-097 | 05 SOUTHWEST | 527802 | EDDY_CNTY 7 | 345 | 7.3273 | 7.3251 | 0.0022
GEN-2018-097 | 05 SOUTHWEST | 527896 | HOBBS_INT 7 | 345 | 12.0143 | 12.0091 | 0.0052
GEN-2018-097 | 05 SOUTHWEST | 560022 | CRAWFISH_DR | 345 | 13.842 | 13.8379 | 0.0041
GEN-2018-097 | 05 SOUTHWEST | 560035 | GRAPEVINE | 345 | 6.4589 | 6.4582 | 0.0007
GEN-2018-097 | 05 SOUTHWEST | 760494 | GEN-2017-146 | 230 | 7.4558 | 7.4511 | 0.0047
GEN-2018-097 | 05 SOUTHWEST | 763186 | GEN-2018-089 | 230 | 10.6882 | 10.6815 | 0.0067
GEN-2018-097 | 05 SOUTHWEST | 511553 | CHISHOLM7 | 345 | 12.3397 | 12.3391 | 0.0006
GEN-2018-097 | 05 SOUTHWEST | 515458 | BORDER 7 | 345 | 8.2517 | 8.2514 | 0.0003
GEN-2018-097 | 05 SOUTHWEST | 515554 | BVRCNTY7 | 345 | 15.3093 | 15.3089 | 0.0004
GEN-2018-097 | 05 SOUTHWEST | 523095 | HITCHLAND 6 | 230 | 14.5761 | 14.5757 | 0.0004
GEN-2018-097 | 05 SOUTHWEST | 523101 | NOBLE_WND 7 | 345 | 14.9103 | 14.9097 | 0.0006
GEN-2018-097 | 05 SOUTHWEST | 523112 | NOVUS1 7 | 345 | 14.6716 | 14.671 | 0.0006
GEN-2018-097 | 05 SOUTHWEST | 523323 | MCDWL_CREEK6 | 230 | 8.9802 | 8.9794 | 0.0008
GEN-2018-097 | 05 SOUTHWEST | 523823 | CARPENTER 7 | 345 | 6.5781 | 6.578 | 0.0001
GEN-2018-097 | 05 SOUTHWEST | 523869 | CHAN+TASCOS6 | 230 | 4.2464 | 4.2462 | 0.0002
GEN-2018-097 | 05 SOUTHWEST | 523979 | HARRNG_EST 6 | 230 | 26.9856 | 26.9806 | 0.005
GEN-2018-097 | 05 SOUTHWEST | 524010 | ROLLHILLS 6 | 230 | 20.2306 | 20.2269 | 0.0037
GEN-2018-097 | 05 SOUTHWEST | 524044 | NICHOLS 6 | 230 | 26.1237 | 26.1191 | 0.0046
GEN-2018-097 | 05 SOUTHWEST | 524267 | BUSHLAND 6 | 230 | 10.1739 | 10.1716 | 0.0023
GEN-2018-097 | 05 SOUTHWEST | 524299 | SPNSPUR_COL7 | 345 | 5.3278 | 5.3271 | 0.0007
GEN-2018-097 | 05 SOUTHWEST | 524365 | RANDALL 6 | 230 | 14.5681 | 14.5661 | 0.002
GEN-2018-097 | 05 SOUTHWEST | 524414 | AMA_SOUTH 3 | 115 | 16.9088 | 16.9073 | 0.0015
GEN-2018-097 | 05 SOUTHWEST | 524502 | NORTON 3 | 115 | 2.9186 | 2.9184 | 0.0002
GEN-2018-097 | 05 SOUTHWEST | 524619 | DFSMTH_EST 3 | 115 | 11.9939 | 11.9893 | 0.0046
GEN-2018-097 | 05 SOUTHWEST | 524622 | DFSMTH_WST 3 | 115 | 11.9945 | 11.9899 | 0.0046
GEN-2018-097 | 05 SOUTHWEST | 524669 | DS-#20 3 | 115 | 6.2762 | 6.2738 | 0.0024
GEN-2018-097 | 05 SOUTHWEST | 524746 | CASTRO_CNTY3 | 115 | 9.822 | 9.819 | 0.003
GEN-2018-097 | 05 SOUTHWEST | 524764 | NORRIS_TP 3 | 115 | 11.4074 | 11.3981 | 0.0093
GEN-2018-097 | 05 SOUTHWEST | 524773 | E_CLOVIS 3 | 115 | 8.962 | 8.9563 | 0.0057
GEN-2018-097 | 05 SOUTHWEST | 524776 | N_CLOVIS_TP3 | 115 | 7.4744 | 7.4706 | 0.0038
GEN-2018-097 | 05 SOUTHWEST | 524797 | PERIMETER 3 | 115 | 6.5512 | 6.5481 | 0.0031
GEN-2018-097 | 05 SOUTHWEST | 524821 | CURRY 2 | 69 | 4.4284 | 4.4275 | 0.0009
GEN-2018-097 | 05 SOUTHWEST | 524831 | FE-HOLLAND 3 | 115 | 9.2431 | 9.2371 | 0.006
GEN-2018-097 | 05 SOUTHWEST | 524838 | FE-CLOVIS2+3 | 115 | 10.7942 | 10.7859 | 0.0083
GEN-2018-097 | 05 SOUTHWEST | 524863 | FE-CHZPLT 3 | 115 | 8.0228 | 8.0181 | 0.0047
GEN-2018-097 | 05 SOUTHWEST | 524889 | SN_JUAN_WND6 | 230 | 4.6556 | 4.6542 | 0.0014
GEN-2018-097 | 05 SOUTHWEST | 524923 | PORTALES 2 | 69 | 7.5604 | 7.5578 | 0.0026
GEN-2018-097 | 05 SOUTHWEST | 524935 | KILGORE 3 | 115 | 6.1488 | 6.1459 | 0.0029
GEN-2018-097 | 05 SOUTHWEST | 524977 | GREYHOUND 3 | 115 | 5.6862 | 5.6838 | 0.0024
GEN-2018-097 | 05 SOUTHWEST | 525018 | MULESHVALLY3 | 115 | 5.5409 | 5.5387 | 0.0022
GEN-2018-097 | 05 SOUTHWEST | 525028 | BAILEYCO 3 | 115 | 5.8021 | 5.7997 | 0.0024
GEN-2018-097 | 05 SOUTHWEST | 525050 | BC-KELLEY +3 | 115 | 7.782 | 7.7792 | 0.0028
GEN-2018-097 | 05 SOUTHWEST | 525124 | HART_INDUST3 | 115 | 7.4925 | 7.4906 | 0.0019
GEN-2018-097 | 05 SOUTHWEST | 525192 | KRESS_INT 3 | 115 | 11.9205 | 11.9175 | 0.003
GEN-2018-097 | 05 SOUTHWEST | 525326 | COX 3 | 115 | 6.2736 | 6.2728 | 0.0008
GEN-2018-097 | 05 SOUTHWEST | 525393 | ROCKYFORD 3 | 115 | 9.0431 | 9.0379 | 0.0052
GEN-2018-097 | 05 SOUTHWEST | 525414 | LAMTON 3 | 115 | 7.6144 | 7.6121 | 0.0023
GEN-2018-097 | 05 SOUTHWEST | 525440 | LC-S_OLTON+3 | 115 | 7.1982 | 7.1957 | 0.0025
GEN-2018-097 | 05 SOUTHWEST | 525453 | HALE_CNTY 2 | 69 | 6.9062 | 6.9055 | 0.0007
GEN-2018-097 | 05 SOUTHWEST | 525613 | W_LITTLFLD 2 | 69 | 2.9684 | 2.968 | 0.0004
GEN-2018-097 | 05 SOUTHWEST | 525620 | LTFLD_S&CTY2 | 69 | 4.1727 | 4.1718 | 0.0009
GEN-2018-097 | 05 SOUTHWEST | 525650 | LC-LTTLFLD+2 | 69 | 4.9319 | 4.9306 | 0.0013
GEN-2018-097 | 05 SOUTHWEST | 525687 | LC-LUMSCHAP2 | 69 | 4.6126 | 4.6114 | 0.0012
GEN-2018-097 | 05 SOUTHWEST | 525731 | SP-ABERNTHY2 | 69 | 3.0093 | 3.0092 | 0.0001
GEN-2018-097 | 05 SOUTHWEST | 525738 | HALECENTER 2 | 69 | 2.4566 | 2.4565 | 0.0001
GEN-2018-097 | 05 SOUTHWEST | 525763 | CALLAHAN 3 | 115 | 5.5668 | 5.5663 | 0.0005
GEN-2018-097 | 05 SOUTHWEST | 525779 | FLOYD_CNTY 2 | 69 | 5.401 | 5.4008 | 0.0002
GEN-2018-097 | 05 SOUTHWEST | 525803 | BLANCO 3 | 115 | 5.0451 | 5.0449 | 0.0002
GEN-2018-097 | 05 SOUTHWEST | 525853 | LH-WIL&ELN+2 | 69 | 2.5404 | 2.5404 | 0
GEN-2018-097 | 05 SOUTHWEST | 525885 | SP-NEWDEAL 2 | 69 | 3.3073 | 3.3072 | 0.0001
GEN-2018-097 | 05 SOUTHWEST | 525926 | CROSBY 3 | 115 | 4.7129 | 4.7127 | 0.0002
GEN-2018-097 | 05 SOUTHWEST | 526019 | HOCKLEY 2 | 69 | 5.1105 | 5.1098 | 0.0007
GEN-2018-097 | 05 SOUTHWEST | 526036 | LC-OPDYKE 3 | 115 | 5.7143 | 5.713 | 0.0013
GEN-2018-097 | 05 SOUTHWEST | 526109 | SP-ERSKINE 3 | 115 | 10.9787 | 10.9774 | 0.0013
GEN-2018-097 | 05 SOUTHWEST | 526146 | INDIANA 3 | 115 | 9.3032 | 9.3023 | 0.0009
GEN-2018-097 | 05 SOUTHWEST | 526159 | CARLISLE 2 | 69 | 2.5568 | 2.5568 | 0
GEN-2018-097 | 05 SOUTHWEST | 526162 | LP-DOUD_TP 3 | 115 | 11.325 | 11.3236 | 0.0014
GEN-2018-097 | 05 SOUTHWEST | 526192 | MURPHY 3 | 115 | 10.2503 | 10.2493 | 0.001
GEN-2018-097 | 05 SOUTHWEST | 526268 | LUBBCK_STH 3 | 115 | 17.6482 | 17.6459 | 0.0023
GEN-2018-097 | 05 SOUTHWEST | 526297 | LUBBCK_EST 2 | 69 | 7.8955 | 7.8952 | 0.0003
GEN-2018-097 | 05 SOUTHWEST | 526424 | PACIFIC 3 | 115 | 9.1771 | 9.1754 | 0.0017
GEN-2018-097 | 05 SOUTHWEST | 526445 | AMOCO_TP 3 | 115 | 10.1845 | 10.1824 | 0.0021
GEN-2018-097 | 05 SOUTHWEST | 526524 | WOLFFORTH 3 | 115 | 11.2819 | 11.2805 | 0.0014
GEN-2018-097 | 05 SOUTHWEST | 526676 | GRASSLAND 3 | 115 | 6.8633 | 6.863 | 0.0003
GEN-2018-097 | 05 SOUTHWEST | 526679 | CIRRUS_WND 6 | 230 | 4.6792 | 4.679 | 0.0002
GEN-2018-097 | 05 SOUTHWEST | 526784 | AMOCOWASSON6 | 230 | 15.6353 | 15.6325 | 0.0028
GEN-2018-097 | 05 SOUTHWEST | 526792 | PRENTICE 3 | 115 | 6.0286 | 6.0283 | 0.0003
GEN-2018-097 | 05 SOUTHWEST | 526928 | PLAINS_INT 3 | 115 | 10.0196 | 10.0187 | 0.0009
GEN-2018-097 | 05 SOUTHWEST | 527010 | OXYBRU 6 | 230 | 15.5052 | 15.5016 | 0.0036
GEN-2018-097 | 05 SOUTHWEST | 527011 | XTO_MAHONEY6 | 230 | 15.3578 | 15.3545 | 0.0033
GEN-2018-097 | 05 SOUTHWEST | 527027 | INK_BASIN 3 | 115 | 13.258 | 13.2571 | 0.0009
GEN-2018-097 | 05 SOUTHWEST | 527041 | ARCO_TP 3 | 115 | 13.6807 | 13.6796 | 0.0011
GEN-2018-097 | 05 SOUTHWEST | 527146 | MUSTANG 3 | 115 | 24.0628 | 24.0604 | 0.0024
GEN-2018-097 | 05 SOUTHWEST | 527151 | GS-MUSTANG 6 | 230 | 17.9238 | 17.9206 | 0.0032
GEN-2018-097 | 05 SOUTHWEST | 527194 | LG-PLSHILL 3 | 115 | 7.9741 | 7.9737 | 0.0004
GEN-2018-097 | 05 SOUTHWEST | 527276 | SEMINOLE 6 | 230 | 8.197 | 8.1964 | 0.0006
GEN-2018-097 | 05 SOUTHWEST | 527483 | CHAVES_CNTY6 | 230 | 4.4929 | 4.4921 | 0.0008
GEN-2018-097 | 05 SOUTHWEST | 527599 | SAGA_SDCOL 7 | 345 | 10.2321 | 10.2244 | 0.0077
GEN-2018-097 | 05 SOUTHWEST | 527654 | RSVLT_CC_W 7 | 345 | 8.7265 | 8.721 | 0.0055
GEN-2018-097 | 05 SOUTHWEST | 527799 | EDDY_NORTH 6 | 230 | 9.402 | 9.3999 | 0.0021
GEN-2018-097 | 05 SOUTHWEST | 527894 | HOBBS_INT 6 | 230 | 19.4767 | 19.4726 | 0.0041
GEN-2018-097 | 05 SOUTHWEST | 527965 | KIOWA 7 | 345 | 8.82 | 8.8172 | 0.0028
GEN-2018-097 | 05 SOUTHWEST | 528027 | RDRUNNER 7 | 345 | 8.6815 | 8.6789 | 0.0026
GEN-2018-097 | 05 SOUTHWEST | 576397 | G10014G11022 | 345 | 10.3812 | 10.381 | 0.0002
GEN-2018-097 | 05 SOUTHWEST | 762216 | G17-151TAP | 345 | 8.5119 | 8.5108 | 0.0011
GEN-2018-097 | 05 SOUTHWEST | 763087 | GEN-2018-073 | 345 | 11.9423 | 11.9393 | 0.003
GEN-2018-097 | 05 SOUTHWEST | 763516 | GEN-2019-011 | 345 | 9.2852 | 9.2826 | 0.0026
GEN-2018-097 | 05 SOUTHWEST | 511557 | CHISHOLM6 | 230 | 12.1566 | 12.1563 | 0.0003
GEN-2018-097 | 05 SOUTHWEST | 515375 | WWRDEHV7 | 345 | 22.3641 | 22.3638 | 0.0003
GEN-2018-097 | 05 SOUTHWEST | 515590 | PALDR2W7 | 345 | 12.8669 | 12.8667 | 0.0002
GEN-2018-097 | 05 SOUTHWEST | 515618 | BALKOW 7 | 345 | 12.5807 | 12.5805 | 0.0002
GEN-2018-097 | 05 SOUTHWEST | 515677 | BADGER 7 | 345 | 13.7821 | 13.7819 | 0.0002
GEN-2018-097 | 05 SOUTHWEST | 523093 | HITCHLAND 3 | 115 | 17.3358 | 17.3355 | 0.0003
GEN-2018-097 | 05 SOUTHWEST | 523103 | NOBLE_WND 3 | 115 | 10.6199 | 10.6198 | 0.0001
GEN-2018-097 | 05 SOUTHWEST | 523111 | NOVUS1 3 | 115 | 7.8432 | 7.8431 | 0.0001
GEN-2018-097 | 05 SOUTHWEST | 523155 | OCHILTREE 6 | 230 | 4.265 | 4.265 | 0
GEN-2018-097 | 05 SOUTHWEST | 523215 | GEN-2011-022 | 345 | 10.3812 | 10.381 | 0.0002
GEN-2018-097 | 05 SOUTHWEST | 523221 | XIT_INTG 6 | 230 | 3.1441 | 3.144 | 0.0001
GEN-2018-097 | 05 SOUTHWEST | 523267 | PRINGLE 6 | 230 | 4.3435 | 4.3434 | 0.0001
GEN-2018-097 | 05 SOUTHWEST | 523309 | MOORE_CNTY 6 | 230 | 6.6813 | 6.681 | 0.0003
GEN-2018-097 | 05 SOUTHWEST | 523322 | MCDWL_CREEK3 | 115 | 9.8376 | 9.8373 | 0.0003
GEN-2018-097 | 05 SOUTHWEST | 523551 | HUTCHISON 6 | 230 | 7.288 | 7.2877 | 0.0003
GEN-2018-097 | 05 SOUTHWEST | 523771 | GRAPEVINE 6 | 230 | 5.9762 | 5.9761 | 0.0001
GEN-2018-097 | 05 SOUTHWEST | 523853 | FINNEY 7 | 345 | 9.8362 | 9.8361 | 0.0001
GEN-2018-097 | 05 SOUTHWEST | 523977 | HARRNG_WST 6 | 230 | 26.9856 | 26.9806 | 0.005
GEN-2018-097 | 05 SOUTHWEST | 523978 | HARRNG_MID 6 | 230 | 26.9856 | 26.9806 | 0.005
GEN-2018-097 | 05 SOUTHWEST | 524007 | ROLLHILLS 3 | 115 | 19.6592 | 19.6577 | 0.0015
GEN-2018-097 | 05 SOUTHWEST | 524043 | NICHOLS 3 | 115 | 30.649 | 30.6464 | 0.0026
GEN-2018-097 | 05 SOUTHWEST | 524266 | BUSHLAND 3 | 115 | 10.3324 | 10.3315 | 0.0009
GEN-2018-097 | 05 SOUTHWEST | 524290 | WILDOR2_JUS6 | 230 | 6.9783 | 6.9772 | 0.0011
GEN-2018-097 | 05 SOUTHWEST | 524364 | RANDALL 3 | 115 | 21.0733 | 21.0708 | 0.0025
GEN-2018-097 | 05 SOUTHWEST | 524377 | FARMERS 3 | 115 | 15.4368 | 15.4355 | 0.0013
GEN-2018-097 | 05 SOUTHWEST | 524397 | ARROWHEAD 3 | 115 | 13.6793 | 13.6784 | 0.0009
GEN-2018-097 | 05 SOUTHWEST | 524404 | OWENSCORN 3 | 115 | 15.0594 | 15.0582 | 0.0012
GEN-2018-097 | 05 SOUTHWEST | 524486 | CAPROCK 3 | 115 | 2.636 | 2.636 | 0
GEN-2018-097 | 05 SOUTHWEST | 524509 | FE-TUCMCARI3 | 115 | 2.391 | 2.3909 | 0.0001
GEN-2018-097 | 05 SOUTHWEST | 524544 | SPRING_DRW 3 | 115 | 6.4069 | 6.4067 | 0.0002
GEN-2018-097 | 05 SOUTHWEST | 524630 | TIERABLANCA3 | 115 | 12.3344 | 12.3295 | 0.0049
GEN-2018-097 | 05 SOUTHWEST | 524662 | PARMER_CO 3 | 115 | 5.4666 | 5.465 | 0.0016
GEN-2018-097 | 05 SOUTHWEST | 524694 | DS-#22 3 | 115 | 4.5966 | 4.596 | 0.0006
GEN-2018-097 | 05 SOUTHWEST | 524734 | DS-#21 3 | 115 | 9.3056 | 9.3029 | 0.0027
GEN-2018-097 | 05 SOUTHWEST | 524745 | CASTRO_CNTY2 | 69 | 8.7963 | 8.7949 | 0.0014
GEN-2018-097 | 05 SOUTHWEST | 524757 | BETHEL_COL13 | 115 | 8.2391 | 8.2372 | 0.0019
GEN-2018-097 | 05 SOUTHWEST | 524777 | N_CLOVIS 3 | 115 | 6.7428 | 6.7397 | 0.0031
GEN-2018-097 | 05 SOUTHWEST | 524783 | W_CLOVIS 2 | 69 | 2.4403 | 2.44 | 0.0003
GEN-2018-097 | 05 SOUTHWEST | 524790 | CANNON_TP 3 | 115 | 6.0058 | 6.0033 | 0.0025
GEN-2018-097 | 05 SOUTHWEST | 524801 | NORRIS 3 | 115 | 10.4115 | 10.4038 | 0.0077
GEN-2018-097 | 05 SOUTHWEST | 524808 | FE-CLVS_INT3 | 115 | 6.9498 | 6.9465 | 0.0033
GEN-2018-097 | 05 SOUTHWEST | 524846 | FARWELL 2 | 69 | 2.1357 | 2.1356 | 0.0001
GEN-2018-097 | 05 SOUTHWEST | 524929 | RO-PORT_MTR2 | 69 | 7.5604 | 7.5578 | 0.0026
GEN-2018-097 | 05 SOUTHWEST | 524934 | ZODIAC 2 | 69 | 5.5439 | 5.5425 | 0.0014
GEN-2018-097 | 05 SOUTHWEST | 524941 | PORTALES#1 2 | 69 | 5.7509 | 5.7494 | 0.0015
GEN-2018-097 | 05 SOUTHWEST | 524963 | S_PORTALES 3 | 115 | 5.7708 | 5.7682 | 0.0026
GEN-2018-097 | 05 SOUTHWEST | 525027 | BAILEYCO 2 | 69 | 5.2707 | 5.2695 | 0.0012
GEN-2018-097 | 05 SOUTHWEST | 525179 | TULIA_TP 3 | 115 | 6.4624 | 6.4617 | 0.0007
GEN-2018-097 | 05 SOUTHWEST | 525191 | KRESS_INT 2 | 69 | 4.4978 | 4.4975 | 0.0003
GEN-2018-097 | 05 SOUTHWEST | 525226 | KRS_RURL_TP3 | 115 | 6.4399 | 6.4391 | 0.0008
GEN-2018-097 | 05 SOUTHWEST | 525272 | KISER 3 | 115 | 5.2683 | 5.2677 | 0.0006
GEN-2018-097 | 05 SOUTHWEST | 525291 | PLAINVW_TP 2 | 69 | 6.4824 | 6.4817 | 0.0007
GEN-2018-097 | 05 SOUTHWEST | 525298 | S_PLAINVEW 2 | 69 | 2.5852 | 2.5851 | 0.0001
GEN-2018-097 | 05 SOUTHWEST | 525325 | COX 2 | 69 | 3.4185 | 3.4183 | 0.0002
GEN-2018-097 | 05 SOUTHWEST | 525351 | LH-AIKEN 2 | 69 | 2.1484 | 2.1484 | 0
GEN-2018-097 | 05 SOUTHWEST | 525413 | LAMTON 2 | 69 | 5.1693 | 5.1687 | 0.0006
GEN-2018-097 | 05 SOUTHWEST | 525432 | SP-HALFWAY+2 | 69 | 5.8641 | 5.8635 | 0.0006
GEN-2018-097 | 05 SOUTHWEST | 525606 | AMHERST 2 | 69 | 2.3408 | 2.3405 | 0.0003
GEN-2018-097 | 05 SOUTHWEST | 525657 | W_ANTON_TP 2 | 69 | 4.1079 | 4.107 | 0.0009
GEN-2018-097 | 05 SOUTHWEST | 525694 | HOBGOOD 2 | 69 | 3.4381 | 3.4375 | 0.0006
GEN-2018-097 | 05 SOUTHWEST | 525723 | CNTYLINE_TP2 | 69 | 2.2014 | 2.2014 | 0
GEN-2018-097 | 05 SOUTHWEST | 525745 | LH-HALECTR 2 | 69 | 2.4289 | 2.4289 | 0
GEN-2018-097 | 05 SOUTHWEST | 525790 | FLOYDADA_TP2 | 69 | 2.5171 | 2.517 | 0.0001
GEN-2018-097 | 05 SOUTHWEST | 525801 | LRNZ_MPT 3 | 115 | 5.0442 | 5.0439 | 0.0003
GEN-2018-097 | 05 SOUTHWEST | 525811 | LH-HARMONY 2 | 69 | 4.3124 | 4.3123 | 0.0001
GEN-2018-097 | 05 SOUTHWEST | 525860 | SP-BECTON +2 | 69 | 2.2545 | 2.2545 | 0
GEN-2018-097 | 05 SOUTHWEST | 525892 | MONROE 2 | 69 | 2.6475 | 2.6475 | 0
GEN-2018-097 | 05 SOUTHWEST | 525925 | CROSBY 2 | 69 | 4.7847 | 4.7846 | 0.0001
GEN-2018-097 | 05 SOUTHWEST | 526009 | LC-LEVLND#22 | 69 | 4.2645 | 4.264 | 0.0005
GEN-2018-097 | 05 SOUTHWEST | 526042 | COBLE 2 | 69 | 2.2615 | 2.2614 | 0.0001
GEN-2018-097 | 05 SOUTHWEST | 526048 | LVLNDCTY_TP2 | 69 | 4.2645 | 4.264 | 0.0005
GEN-2018-097 | 05 SOUTHWEST | 526130 | SP-CARLISLE2 | 69 | 2.1026 | 2.1025 | 0.0001
GEN-2018-097 | 05 SOUTHWEST | 526176 | LP-DOUD 3 | 115 | 8.8577 | 8.8569 | 0.0008
GEN-2018-097 | 05 SOUTHWEST | 526184 | SW_6878 2 | 69 | 2.1534 | 2.1534 | 0
GEN-2018-097 | 05 SOUTHWEST | 526195 | QUINCY 3 | 115 | 9.6342 | 9.6333 | 0.0009
GEN-2018-097 | 05 SOUTHWEST | 526213 | ALLEN 3 | 115 | 10.4502 | 10.4493 | 0.0009
GEN-2018-097 | 05 SOUTHWEST | 526267 | LUBBCK_STH 2 | 69 | 4.3104 | 4.3104 | 0
GEN-2018-097 | 05 SOUTHWEST | 526284 | PLANTERS 2 | 69 | 5.7109 | 5.7108 | 0.0001
GEN-2018-097 | 05 SOUTHWEST | 526310 | CLUTTER 2 | 69 | 5.3812 | 5.381 | 0.0002
GEN-2018-097 | 05 SOUTHWEST | 526361 | COCHRAN 3 | 115 | 6.4257 | 6.425 | 0.0007
GEN-2018-097 | 05 SOUTHWEST | 526452 | AMOCO_CRYO 3 | 115 | 6.362 | 6.3612 | 0.0008
GEN-2018-097 | 05 SOUTHWEST | 526475 | YUMA_INT 3 | 115 | 10.7034 | 10.7021 | 0.0013
GEN-2018-097 | 05 SOUTHWEST | 526481 | SP-WOLF_TP 3 | 115 | 10.8642 | 10.8629 | 0.0013
GEN-2018-097 | 05 SOUTHWEST | 526484 | LG-LEVELAND3 | 115 | 9.1775 | 9.1759 | 0.0016
GEN-2018-097 | 05 SOUTHWEST | 526562 | SLATON 2 | 69 | 2.4663 | 2.4663 | 0
GEN-2018-097 | 05 SOUTHWEST | 526602 | WOODROW 3 | 115 | 9.1323 | 9.1317 | 0.0006
GEN-2018-097 | 05 SOUTHWEST | 526656 | LYNN_CNTY 3 | 115 | 5.9373 | 5.9371 | 0.0002
GEN-2018-097 | 05 SOUTHWEST | 526694 | GRAHAM 3 | 115 | 2.8169 | 2.8169 | 0
GEN-2018-097 | 05 SOUTHWEST | 526736 | TERRY_CNTY 3 | 115 | 10.6679 | 10.6668 | 0.0011
GEN-2018-097 | 05 SOUTHWEST | 526944 | LG-PLAINS 3 | 115 | 7.9013 | 7.9008 | 0.0005
GEN-2018-097 | 05 SOUTHWEST | 527018 | BENNETT 3 | 115 | 13.7758 | 13.7747 | 0.0011
GEN-2018-097 | 05 SOUTHWEST | 527030 | ALRDCRTZ_TP3 | 115 | 12.2915 | 12.2908 | 0.0007
GEN-2018-097 | 05 SOUTHWEST | 527047 | OXY_WILRD1 3 | 115 | 10.8936 | 10.893 | 0.0006
GEN-2018-097 | 05 SOUTHWEST | 527062 | SHELL_CO2 3 | 115 | 16.7017 | 16.7003 | 0.0014
GEN-2018-097 | 05 SOUTHWEST | 527130 | DENVER_N 3 | 115 | 22.5277 | 22.5254 | 0.0023
GEN-2018-097 | 05 SOUTHWEST | 527136 | DENVER_S 3 | 115 | 22.5277 | 22.5254 | 0.0023
GEN-2018-097 | 05 SOUTHWEST | 527202 | SEAGRAVES 3 | 115 | 9.1786 | 9.1782 | 0.0004
GEN-2018-097 | 05 SOUTHWEST | 527275 | SEMINOLE 3 | 115 | 14.6609 | 14.6599 | 0.001
GEN-2018-097 | 05 SOUTHWEST | 527482 | CHAVES_CNTY3 | 115 | 7.0492 | 7.0483 | 0.0009
GEN-2018-097 | 05 SOUTHWEST | 527600 | SAGA_SMEAS 7 | 345 | 10.2321 | 10.2244 | 0.0077
GEN-2018-097 | 05 SOUTHWEST | 527666 | RSVLT_COL1 7 | 345 | 8.7265 | 8.721 | 0.0055
GEN-2018-097 | 05 SOUTHWEST | 527667 | RSVLT_COL2 7 | 345 | 8.7265 | 8.721 | 0.0055
GEN-2018-097 | 05 SOUTHWEST | 527793 | EDDY_STH 3 | 115 | 11.9559 | 11.9542 | 0.0017
GEN-2018-097 | 05 SOUTHWEST | 527798 | EDDY_NTH 3 | 115 | 11.9559 | 11.9542 | 0.0017
GEN-2018-097 | 05 SOUTHWEST | 527865 | CUNNIGHM_N 6 | 230 | 17.5364 | 17.5334 | 0.003
GEN-2018-097 | 05 SOUTHWEST | 527867 | CUNNIGHM_S 6 | 230 | 17.5364 | 17.5334 | 0.003
GEN-2018-097 | 05 SOUTHWEST | 527891 | HOBBS_INT 3 | 115 | 33.0667 | 33.0638 | 0.0029
GEN-2018-097 | 05 SOUTHWEST | 527966 | KIOWA 3 | 115 | 17.1508 | 17.1479 | 0.0029
GEN-2018-097 | 05 SOUTHWEST | 528015 | PHANTOM 7 | 345 | 5.675 | 5.6739 | 0.0011
GEN-2018-097 | 05 SOUTHWEST | 528025 | RDRUNNER 3 | 115 | 13.7957 | 13.7938 | 0.0019
GEN-2018-097 | 05 SOUTHWEST | 528095 | 7-RIVERS 6 | 230 | 6.3874 | 6.3865 | 0.0009
GEN-2018-097 | 05 SOUTHWEST | 528185 | N_LOVING 7 | 345 | 6.5496 | 6.5482 | 0.0014
GEN-2018-097 | 05 SOUTHWEST | 528325 | LE-WAITS 3 | 115 | 8.9967 | 8.9964 | 0.0003
GEN-2018-097 | 05 SOUTHWEST | 528604 | ANDREWS 6 | 230 | 6.0764 | 6.076 | 0.0004
GEN-2018-097 | 05 SOUTHWEST | 528626 | LE-PLNSINT 2 | 69 | 3.6375 | 3.6375 | 0
GEN-2018-097 | 05 SOUTHWEST | 531512 | HARBNGR7 | 345 | 6.5579 | 6.5579 | 0
GEN-2018-097 | 05 SOUTHWEST | 560078 | G16-037-TAP | 345 | 10.1427 | 10.1425 | 0.0002
GEN-2018-097 | 05 SOUTHWEST | 560577 | G06-44 | 115 | 7.5797 | 7.5797 | 0
GEN-2018-097 | 05 SOUTHWEST | 576395 | GEN-2010-014 | 345 | 10.3812 | 10.381 | 0.0002
GEN-2018-097 | 05 SOUTHWEST | 588460 | A16-008SUB | 115 | 13.258 | 13.2571 | 0.0009
GEN-2018-097 | 05 SOUTHWEST | 599960 | EPTNP-D6 | 230 | 9.402 | 9.3999 | 0.0021
GEN-2018-097 | 05 SOUTHWEST | 755000 | WWDBORDT | 345 | 12.2648 | 12.2642 | 0.0006
GEN-2018-097 | 05 SOUTHWEST | 761355 | GEN-2017-239 | 230 | 13.7988 | 13.7962 | 0.0026
GEN-2018-097 | 05 SOUTHWEST | 762217 | GEN-2017-151 | 345 | 6.1754 | 6.1748 | 0.0006
GEN-2018-097 | 05 SOUTHWEST | 762467 | G18-015-TAP | 345 | 5.8242 | 5.8241 | 0.0001
GEN-2018-099 | 05 SOUTHWEST | 525531 | TOLK 6 | 230 | 31.4946 | 30.7586 | 0.736
GEN-2018-099 | 05 SOUTHWEST | 524909 | ROOSEVELT 6 | 230 | 9.709 | 9.6664 | 0.0426
GEN-2018-099 | 05 SOUTHWEST | 525481 | PLANT_X 6 | 230 | 24.1838 | 23.9081 | 0.2757
GEN-2018-099 | 05 SOUTHWEST | 525549 | TOLK 7 | 345 | 15.0276 | 14.8562 | 0.1714
GEN-2018-099 | 05 SOUTHWEST | 525586 | NEEDMORE 6 | 230 | 11.0214 | 10.9531 | 0.0683
GEN-2018-099 | 05 SOUTHWEST | 525637 | LAMB_CNTY 6 | 230 | 5.4027 | 5.3853 | 0.0174
GEN-2018-099 | 05 SOUTHWEST | 525830 | TUCO_INT 6 | 230 | 21.9895 | 21.9602 | 0.0293
GEN-2018-099 | 05 SOUTHWEST | 762132 | GEN-2017-158 | 230 | 13.8646 | 13.0532 | 0.8114
GEN-2018-099 | 05 SOUTHWEST | 763241 | GEN-2018-097 | 230 | 24.4484 | 24.0115 | 0.4369
GEN-2018-099 | 05 SOUTHWEST | 523961 | POTTER_CO 7 | 345 | 11.6631 | 11.6523 | 0.0108
GEN-2018-099 | 05 SOUTHWEST | 524770 | PLSNT_HILL 6 | 230 | 6.517 | 6.4996 | 0.0174
GEN-2018-099 | 05 SOUTHWEST | 524875 | OASIS 6 | 230 | 7.8784 | 7.8539 | 0.0245
GEN-2018-099 | 05 SOUTHWEST | 524908 | ROOSEVELT 3 | 115 | 11.1454 | 11.1203 | 0.0251
GEN-2018-099 | 05 SOUTHWEST | 525213 | SWISHER 6 | 230 | 10.3853 | 10.3749 | 0.0104
GEN-2018-099 | 05 SOUTHWEST | 525461 | NEWHART 6 | 230 | 10.9971 | 10.979 | 0.0181
GEN-2018-099 | 05 SOUTHWEST | 525480 | PLANT_X 3 | 115 | 19.2796 | 19.2113 | 0.0683
GEN-2018-099 | 05 SOUTHWEST | 525585 | BLUECLDPOI 6 | 230 | 11.0214 | 10.9531 | 0.0683
GEN-2018-099 | 05 SOUTHWEST | 525636 | LAMB_CNTY 3 | 115 | 8.4389 | 8.4229 | 0.016
GEN-2018-099 | 05 SOUTHWEST | 525828 | TUCO_INT 3 | 115 | 19.3618 | 19.3498 | 0.012
GEN-2018-099 | 05 SOUTHWEST | 525832 | TUCO_INT 7 | 345 | 14.0745 | 14.0634 | 0.0111
GEN-2018-099 | 05 SOUTHWEST | 525840 | ANTELOPE_1 6 | 230 | 21.8013 | 21.7725 | 0.0288
GEN-2018-099 | 05 SOUTHWEST | 525957 | HALE_WNDCL16 | 230 | 10.5196 | 10.5136 | 0.006
GEN-2018-099 | 05 SOUTHWEST | 526161 | CARLISLE 6 | 230 | 10.473 | 10.4663 | 0.0067
GEN-2018-099 | 05 SOUTHWEST | 526337 | JONES 6 | 230 | 16.6076 | 16.5993 | 0.0083
GEN-2018-099 | 05 SOUTHWEST | 526435 | SUNDOWN 6 | 230 | 11.7438 | 11.7286 | 0.0152
GEN-2018-099 | 05 SOUTHWEST | 526935 | YOAKUM 6 | 230 | 19.6825 | 19.664 | 0.0185
GEN-2018-099 | 05 SOUTHWEST | 527656 | CROSSROADS 7 | 345 | 11.539 | 11.5123 | 0.0267
GEN-2018-099 | 05 SOUTHWEST | 599955 | PNM-DC6 | 230 | 9.709 | 9.6664 | 0.0426
GEN-2018-099 | 05 SOUTHWEST | 760498 | G17-146-TAP | 230 | 7.745 | 7.7319 | 0.0131
GEN-2018-099 | 05 SOUTHWEST | 763120 | GEN-2018-081 | 230 | 17.3907 | 17.2502 | 0.1405
GEN-2018-099 | 05 SOUTHWEST | 763483 | GEN-2019-003 | 230 | 8.7401 | 8.7061 | 0.034
GEN-2018-099 | 05 SOUTHWEST | 523097 | HITCHLAND 7 | 345 | 14.9713 | 14.9698 | 0.0015
GEN-2018-099 | 05 SOUTHWEST | 523959 | POTTER_CO 6 | 230 | 22.4376 | 22.4215 | 0.0161
GEN-2018-099 | 05 SOUTHWEST | 524296 | SPNSPUR_WND7 | 345 | 5.3278 | 5.3259 | 0.0019
GEN-2018-099 | 05 SOUTHWEST | 524415 | AMA_SOUTH 6 | 230 | 13.6408 | 13.6359 | 0.0049
GEN-2018-099 | 05 SOUTHWEST | 524623 | DEAFSMITH 6 | 230 | 8.0257 | 8.0149 | 0.0108
GEN-2018-099 | 05 SOUTHWEST | 524768 | PLSNT_HILL 3 | 115 | 10.5272 | 10.5074 | 0.0198
GEN-2018-099 | 05 SOUTHWEST | 524822 | CURRY 3 | 115 | 11.4402 | 11.4162 | 0.024
GEN-2018-099 | 05 SOUTHWEST | 524874 | OASIS 3 | 115 | 10.0542 | 10.0348 | 0.0194
GEN-2018-099 | 05 SOUTHWEST | 524885 | SN_JUAN_TAP6 | 230 | 4.8705 | 4.8664 | 0.0041
GEN-2018-099 | 05 SOUTHWEST | 524924 | PORTALES 3 | 115 | 7.5524 | 7.5413 | 0.0111
GEN-2018-099 | 05 SOUTHWEST | 525019 | MULSHVLY_TP3 | 115 | 5.9489 | 5.9424 | 0.0065
GEN-2018-099 | 05 SOUTHWEST | 525056 | BC-EARTH 3 | 115 | 8.2606 | 8.2515 | 0.0091
GEN-2018-099 | 05 SOUTHWEST | 525212 | SWISHER 3 | 115 | 11.4972 | 11.4902 | 0.007
GEN-2018-099 | 05 SOUTHWEST | 525446 | RKYFORD_TP 3 | 115 | 10.1267 | 10.1101 | 0.0166
GEN-2018-099 | 05 SOUTHWEST | 525454 | HALE_CNTY 3 | 115 | 10.1608 | 10.1537 | 0.0071
GEN-2018-099 | 05 SOUTHWEST | 525460 | NEWHART 3 | 115 | 14.9423 | 14.9255 | 0.0168
GEN-2018-099 | 05 SOUTHWEST | 525584 | BLUECLDCOL 6 | 230 | 10.4275 | 10.3665 | 0.061
GEN-2018-099 | 05 SOUTHWEST | 525635 | LAMB_CNTY 2 | 69 | 5.8992 | 5.8945 | 0.0047
GEN-2018-099 | 05 SOUTHWEST | 525780 | FLOYD_CNTY 3 | 115 | 6.2514 | 6.25 | 0.0014
GEN-2018-099 | 05 SOUTHWEST | 525816 | TUCO_INT2 2 | 69 | 4.6524 | 4.652 | 0.0004
GEN-2018-099 | 05 SOUTHWEST | 525826 | TUCO_INT 2 | 69 | 7.8538 | 7.8526 | 0.0012
GEN-2018-099 | 05 SOUTHWEST | 525850 | ELK_CT1 | 345 | 13.9398 | 13.9289 | 0.0109
GEN-2018-099 | 05 SOUTHWEST | 526020 | HOCKLEY 3 | 115 | 5.426 | 5.4227 | 0.0033
GEN-2018-099 | 05 SOUTHWEST | 526076 | STANTON_W 3 | 115 | 8.923 | 8.9208 | 0.0022
GEN-2018-099 | 05 SOUTHWEST | 526160 | CARLISLE 3 | 115 | 12.772 | 12.7676 | 0.0044
GEN-2018-099 | 05 SOUTHWEST | 526269 | LUBBCK_STH 6 | 230 | 15.0546 | 15.0467 | 0.0079
GEN-2018-099 | 05 SOUTHWEST | 526298 | LUBBCK_EST 3 | 115 | 14.4141 | 14.41 | 0.0041
GEN-2018-099 | 05 SOUTHWEST | 526299 | LUBBCK_EST 6 | 230 | 11.0462 | 11.0424 | 0.0038
GEN-2018-099 | 05 SOUTHWEST | 526434 | SUNDOWN 3 | 115 | 10.8603 | 10.8539 | 0.0064
GEN-2018-099 | 05 SOUTHWEST | 526460 | AMOCO_SS 6 | 230 | 10.1771 | 10.1666 | 0.0105
GEN-2018-099 | 05 SOUTHWEST | 526525 | WOLFFORTH 6 | 230 | 13.0516 | 13.0409 | 0.0107
GEN-2018-099 | 05 SOUTHWEST | 526677 | GRASSLAND 6 | 230 | 5.9735 | 5.9724 | 0.0011
GEN-2018-099 | 05 SOUTHWEST | 526934 | YOAKUM 3 | 115 | 19.2326 | 19.2249 | 0.0077
GEN-2018-099 | 05 SOUTHWEST | 526936 | YOAKUM_345 | 345 | 9.9314 | 9.9238 | 0.0076
GEN-2018-099 | 05 SOUTHWEST | 527009 | BRU_SUB 6 | 230 | 15.6513 | 15.642 | 0.0093
GEN-2018-099 | 05 SOUTHWEST | 527028 | INK_BASIN 6 | 230 | 11.2413 | 11.2367 | 0.0046
GEN-2018-099 | 05 SOUTHWEST | 527149 | MUSTANG 6 | 230 | 17.9238 | 17.9155 | 0.0083
GEN-2018-099 | 05 SOUTHWEST | 527610 | SAGA_SCOL 7 | 345 | 10.2321 | 10.2123 | 0.0198
GEN-2018-099 | 05 SOUTHWEST | 527655 | RSVLT_CC_E 7 | 345 | 10.0154 | 9.9961 | 0.0193
GEN-2018-099 | 05 SOUTHWEST | 527802 | EDDY_CNTY 7 | 345 | 7.3273 | 7.3216 | 0.0057
GEN-2018-099 | 05 SOUTHWEST | 527896 | HOBBS_INT 7 | 345 | 12.0143 | 12.0009 | 0.0134
GEN-2018-099 | 05 SOUTHWEST | 560022 | CRAWFISH_DR | 345 | 13.842 | 13.8315 | 0.0105
GEN-2018-099 | 05 SOUTHWEST | 560035 | GRAPEVINE | 345 | 6.4589 | 6.4572 | 0.0017
GEN-2018-099 | 05 SOUTHWEST | 760494 | GEN-2017-146 | 230 | 7.4558 | 7.4437 | 0.0121
GEN-2018-099 | 05 SOUTHWEST | 763186 | GEN-2018-089 | 230 | 10.6882 | 10.6711 | 0.0171
GEN-2018-099 | 05 SOUTHWEST | 511553 | CHISHOLM7 | 345 | 12.3397 | 12.3382 | 0.0015
GEN-2018-099 | 05 SOUTHWEST | 515458 | BORDER 7 | 345 | 8.2517 | 8.2509 | 0.0008
GEN-2018-099 | 05 SOUTHWEST | 515554 | BVRCNTY7 | 345 | 15.3093 | 15.3084 | 0.0009
GEN-2018-099 | 05 SOUTHWEST | 523095 | HITCHLAND 6 | 230 | 14.5761 | 14.575 | 0.0011
GEN-2018-099 | 05 SOUTHWEST | 523101 | NOBLE_WND 7 | 345 | 14.9103 | 14.9088 | 0.0015
GEN-2018-099 | 05 SOUTHWEST | 523112 | NOVUS1 7 | 345 | 14.6716 | 14.6702 | 0.0014
GEN-2018-099 | 05 SOUTHWEST | 523323 | MCDWL_CREEK6 | 230 | 8.9802 | 8.9783 | 0.0019
GEN-2018-099 | 05 SOUTHWEST | 523823 | CARPENTER 7 | 345 | 6.5781 | 6.578 | 0.0001
GEN-2018-099 | 05 SOUTHWEST | 523869 | CHAN+TASCOS6 | 230 | 4.2464 | 4.2459 | 0.0005
GEN-2018-099 | 05 SOUTHWEST | 523979 | HARRNG_EST 6 | 230 | 26.9856 | 26.9726 | 0.013
GEN-2018-099 | 05 SOUTHWEST | 524010 | ROLLHILLS 6 | 230 | 20.2306 | 20.2211 | 0.0095
GEN-2018-099 | 05 SOUTHWEST | 524044 | NICHOLS 6 | 230 | 26.1237 | 26.1118 | 0.0119
GEN-2018-099 | 05 SOUTHWEST | 524267 | BUSHLAND 6 | 230 | 10.1739 | 10.1679 | 0.006
GEN-2018-099 | 05 SOUTHWEST | 524299 | SPNSPUR_COL7 | 345 | 5.3278 | 5.3259 | 0.0019
GEN-2018-099 | 05 SOUTHWEST | 524365 | RANDALL 6 | 230 | 14.5681 | 14.563 | 0.0051
GEN-2018-099 | 05 SOUTHWEST | 524414 | AMA_SOUTH 3 | 115 | 16.9088 | 16.905 | 0.0038
GEN-2018-099 | 05 SOUTHWEST | 524502 | NORTON 3 | 115 | 2.9186 | 2.9182 | 0.0004
GEN-2018-099 | 05 SOUTHWEST | 524619 | DFSMTH_EST 3 | 115 | 11.9939 | 11.982 | 0.0119
GEN-2018-099 | 05 SOUTHWEST | 524622 | DFSMTH_WST 3 | 115 | 11.9945 | 11.9826 | 0.0119
GEN-2018-099 | 05 SOUTHWEST | 524669 | DS-#20 3 | 115 | 6.2762 | 6.27 | 0.0062
GEN-2018-099 | 05 SOUTHWEST | 524746 | CASTRO_CNTY3 | 115 | 9.822 | 9.8144 | 0.0076
GEN-2018-099 | 05 SOUTHWEST | 524764 | NORRIS_TP 3 | 115 | 11.4074 | 11.3836 | 0.0238
GEN-2018-099 | 05 SOUTHWEST | 524773 | E_CLOVIS 3 | 115 | 8.962 | 8.9475 | 0.0145
GEN-2018-099 | 05 SOUTHWEST | 524776 | N_CLOVIS_TP3 | 115 | 7.4744 | 7.4646 | 0.0098
GEN-2018-099 | 05 SOUTHWEST | 524797 | PERIMETER 3 | 115 | 6.5512 | 6.5432 | 0.008
GEN-2018-099 | 05 SOUTHWEST | 524821 | CURRY 2 | 69 | 4.4284 | 4.4262 | 0.0022
GEN-2018-099 | 05 SOUTHWEST | 524831 | FE-HOLLAND 3 | 115 | 9.2431 | 9.2277 | 0.0154
GEN-2018-099 | 05 SOUTHWEST | 524838 | FE-CLOVIS2+3 | 115 | 10.7942 | 10.7729 | 0.0213
GEN-2018-099 | 05 SOUTHWEST | 524863 | FE-CHZPLT 3 | 115 | 8.0228 | 8.0108 | 0.012
GEN-2018-099 | 05 SOUTHWEST | 524889 | SN_JUAN_WND6 | 230 | 4.6556 | 4.6521 | 0.0035
GEN-2018-099 | 05 SOUTHWEST | 524923 | PORTALES 2 | 69 | 7.5604 | 7.5537 | 0.0067
GEN-2018-099 | 05 SOUTHWEST | 524935 | KILGORE 3 | 115 | 6.1488 | 6.1414 | 0.0074
GEN-2018-099 | 05 SOUTHWEST | 524977 | GREYHOUND 3 | 115 | 5.6862 | 5.6799 | 0.0063
GEN-2018-099 | 05 SOUTHWEST | 525018 | MULESHVALLY3 | 115 | 5.5409 | 5.5353 | 0.0056
GEN-2018-099 | 05 SOUTHWEST | 525028 | BAILEYCO 3 | 115 | 5.8021 | 5.796 | 0.0061
GEN-2018-099 | 05 SOUTHWEST | 525050 | BC-KELLEY +3 | 115 | 7.782 | 7.7749 | 0.0071
GEN-2018-099 | 05 SOUTHWEST | 525124 | HART_INDUST3 | 115 | 7.4925 | 7.4877 | 0.0048
GEN-2018-099 | 05 SOUTHWEST | 525192 | KRESS_INT 3 | 115 | 11.9205 | 11.9128 | 0.0077
GEN-2018-099 | 05 SOUTHWEST | 525326 | COX 3 | 115 | 6.2736 | 6.2716 | 0.002
GEN-2018-099 | 05 SOUTHWEST | 525393 | ROCKYFORD 3 | 115 | 9.0431 | 9.0299 | 0.0132
GEN-2018-099 | 05 SOUTHWEST | 525414 | LAMTON 3 | 115 | 7.6144 | 7.6084 | 0.006
GEN-2018-099 | 05 SOUTHWEST | 525440 | LC-S_OLTON+3 | 115 | 7.1982 | 7.1918 | 0.0064
GEN-2018-099 | 05 SOUTHWEST | 525453 | HALE_CNTY 2 | 69 | 6.9062 | 6.9042 | 0.002
GEN-2018-099 | 05 SOUTHWEST | 525613 | W_LITTLFLD 2 | 69 | 2.9684 | 2.9673 | 0.0011
GEN-2018-099 | 05 SOUTHWEST | 525620 | LTFLD_S&CTY2 | 69 | 4.1727 | 4.1703 | 0.0024
GEN-2018-099 | 05 SOUTHWEST | 525650 | LC-LTTLFLD+2 | 69 | 4.9319 | 4.9286 | 0.0033
GEN-2018-099 | 05 SOUTHWEST | 525687 | LC-LUMSCHAP2 | 69 | 4.6126 | 4.6097 | 0.0029
GEN-2018-099 | 05 SOUTHWEST | 525731 | SP-ABERNTHY2 | 69 | 3.0093 | 3.0091 | 0.0002
GEN-2018-099 | 05 SOUTHWEST | 525738 | HALECENTER 2 | 69 | 2.4566 | 2.4564 | 0.0002
GEN-2018-099 | 05 SOUTHWEST | 525763 | CALLAHAN 3 | 115 | 5.5668 | 5.5656 | 0.0012
GEN-2018-099 | 05 SOUTHWEST | 525779 | FLOYD_CNTY 2 | 69 | 5.401 | 5.4004 | 0.0006
GEN-2018-099 | 05 SOUTHWEST | 525803 | BLANCO 3 | 115 | 5.0451 | 5.0445 | 0.0006
GEN-2018-099 | 05 SOUTHWEST | 525853 | LH-WIL&ELN+2 | 69 | 2.5404 | 2.5403 | 0.0001
GEN-2018-099 | 05 SOUTHWEST | 525885 | SP-NEWDEAL 2 | 69 | 3.3073 | 3.3071 | 0.0002
GEN-2018-099 | 05 SOUTHWEST | 525926 | CROSBY 3 | 115 | 4.7129 | 4.7124 | 0.0005
GEN-2018-099 | 05 SOUTHWEST | 526019 | HOCKLEY 2 | 69 | 5.1105 | 5.1087 | 0.0018
GEN-2018-099 | 05 SOUTHWEST | 526036 | LC-OPDYKE 3 | 115 | 5.7143 | 5.7111 | 0.0032
GEN-2018-099 | 05 SOUTHWEST | 526109 | SP-ERSKINE 3 | 115 | 10.9787 | 10.9754 | 0.0033
GEN-2018-099 | 05 SOUTHWEST | 526146 | INDIANA 3 | 115 | 9.3032 | 9.3008 | 0.0024
GEN-2018-099 | 05 SOUTHWEST | 526159 | CARLISLE 2 | 69 | 2.5568 | 2.5567 | 0.0001
GEN-2018-099 | 05 SOUTHWEST | 526162 | LP-DOUD_TP 3 | 115 | 11.325 | 11.3215 | 0.0035
GEN-2018-099 | 05 SOUTHWEST | 526192 | MURPHY 3 | 115 | 10.2503 | 10.2477 | 0.0026
GEN-2018-099 | 05 SOUTHWEST | 526268 | LUBBCK_STH 3 | 115 | 17.6482 | 17.6422 | 0.006
GEN-2018-099 | 05 SOUTHWEST | 526297 | LUBBCK_EST 2 | 69 | 7.8955 | 7.8948 | 0.0007
GEN-2018-099 | 05 SOUTHWEST | 526424 | PACIFIC 3 | 115 | 9.1771 | 9.1728 | 0.0043
GEN-2018-099 | 05 SOUTHWEST | 526445 | AMOCO_TP 3 | 115 | 10.1845 | 10.179 | 0.0055
GEN-2018-099 | 05 SOUTHWEST | 526524 | WOLFFORTH 3 | 115 | 11.2819 | 11.2783 | 0.0036
GEN-2018-099 | 05 SOUTHWEST | 526676 | GRASSLAND 3 | 115 | 6.8633 | 6.8626 | 0.0007
GEN-2018-099 | 05 SOUTHWEST | 526679 | CIRRUS_WND 6 | 230 | 4.6792 | 4.6786 | 0.0006
GEN-2018-099 | 05 SOUTHWEST | 526784 | AMOCOWASSON6 | 230 | 15.6353 | 15.628 | 0.0073
GEN-2018-099 | 05 SOUTHWEST | 526792 | PRENTICE 3 | 115 | 6.0286 | 6.0278 | 0.0008
GEN-2018-099 | 05 SOUTHWEST | 526928 | PLAINS_INT 3 | 115 | 10.0196 | 10.0174 | 0.0022
GEN-2018-099 | 05 SOUTHWEST | 527010 | OXYBRU 6 | 230 | 15.5052 | 15.496 | 0.0092
GEN-2018-099 | 05 SOUTHWEST | 527011 | XTO_MAHONEY6 | 230 | 15.3578 | 15.3494 | 0.0084
GEN-2018-099 | 05 SOUTHWEST | 527027 | INK_BASIN 3 | 115 | 13.258 | 13.2558 | 0.0022
GEN-2018-099 | 05 SOUTHWEST | 527041 | ARCO_TP 3 | 115 | 13.6807 | 13.678 | 0.0027
GEN-2018-099 | 05 SOUTHWEST | 527146 | MUSTANG 3 | 115 | 24.0628 | 24.0567 | 0.0061
GEN-2018-099 | 05 SOUTHWEST | 527151 | GS-MUSTANG 6 | 230 | 17.9238 | 17.9155 | 0.0083
GEN-2018-099 | 05 SOUTHWEST | 527194 | LG-PLSHILL 3 | 115 | 7.9741 | 7.9731 | 0.001
GEN-2018-099 | 05 SOUTHWEST | 527276 | SEMINOLE 6 | 230 | 8.197 | 8.1954 | 0.0016
GEN-2018-099 | 05 SOUTHWEST | 527483 | CHAVES_CNTY6 | 230 | 4.4929 | 4.4909 | 0.002
GEN-2018-099 | 05 SOUTHWEST | 527599 | SAGA_SDCOL 7 | 345 | 10.2321 | 10.2123 | 0.0198
GEN-2018-099 | 05 SOUTHWEST | 527654 | RSVLT_CC_W 7 | 345 | 8.7265 | 8.7123 | 0.0142
GEN-2018-099 | 05 SOUTHWEST | 527799 | EDDY_NORTH 6 | 230 | 9.402 | 9.3965 | 0.0055
GEN-2018-099 | 05 SOUTHWEST | 527894 | HOBBS_INT 6 | 230 | 19.4767 | 19.4662 | 0.0105
GEN-2018-099 | 05 SOUTHWEST | 527965 | KIOWA 7 | 345 | 8.82 | 8.8129 | 0.0071
GEN-2018-099 | 05 SOUTHWEST | 528027 | RDRUNNER 7 | 345 | 8.6815 | 8.6748 | 0.0067
GEN-2018-099 | 05 SOUTHWEST | 576397 | G10014G11022 | 345 | 10.3812 | 10.3806 | 0.0006
GEN-2018-099 | 05 SOUTHWEST | 762216 | G17-151TAP | 345 | 8.5119 | 8.509 | 0.0029
GEN-2018-099 | 05 SOUTHWEST | 763087 | GEN-2018-073 | 345 | 11.9423 | 11.9346 | 0.0077
GEN-2018-099 | 05 SOUTHWEST | 763516 | GEN-2019-011 | 345 | 9.2852 | 9.2785 | 0.0067
GEN-2018-099 | 05 SOUTHWEST | 511557 | CHISHOLM6 | 230 | 12.1566 | 12.1558 | 0.0008
GEN-2018-099 | 05 SOUTHWEST | 515375 | WWRDEHV7 | 345 | 22.3641 | 22.3633 | 0.0008
GEN-2018-099 | 05 SOUTHWEST | 515590 | PALDR2W7 | 345 | 12.8669 | 12.8663 | 0.0006
GEN-2018-099 | 05 SOUTHWEST | 515618 | BALKOW 7 | 345 | 12.5807 | 12.5801 | 0.0006
GEN-2018-099 | 05 SOUTHWEST | 515677 | BADGER 7 | 345 | 13.7821 | 13.7815 | 0.0006
GEN-2018-099 | 05 SOUTHWEST | 523093 | HITCHLAND 3 | 115 | 17.3358 | 17.3351 | 0.0007
GEN-2018-099 | 05 SOUTHWEST | 523103 | NOBLE_WND 3 | 115 | 10.6199 | 10.6197 | 0.0002
GEN-2018-099 | 05 SOUTHWEST | 523111 | NOVUS1 3 | 115 | 7.8432 | 7.8431 | 0.0001
GEN-2018-099 | 05 SOUTHWEST | 523155 | OCHILTREE 6 | 230 | 4.265 | 4.2649 | 0.0001
GEN-2018-099 | 05 SOUTHWEST | 523215 | GEN-2011-022 | 345 | 10.3812 | 10.3806 | 0.0006
GEN-2018-099 | 05 SOUTHWEST | 523221 | XIT_INTG 6 | 230 | 3.1441 | 3.1438 | 0.0003
GEN-2018-099 | 05 SOUTHWEST | 523267 | PRINGLE 6 | 230 | 4.3435 | 4.3433 | 0.0002
GEN-2018-099 | 05 SOUTHWEST | 523309 | MOORE_CNTY 6 | 230 | 6.6813 | 6.6806 | 0.0007
GEN-2018-099 | 05 SOUTHWEST | 523322 | MCDWL_CREEK3 | 115 | 9.8376 | 9.8367 | 0.0009
GEN-2018-099 | 05 SOUTHWEST | 523551 | HUTCHISON 6 | 230 | 7.288 | 7.2873 | 0.0007
GEN-2018-099 | 05 SOUTHWEST | 523771 | GRAPEVINE 6 | 230 | 5.9762 | 5.9759 | 0.0003
GEN-2018-099 | 05 SOUTHWEST | 523853 | FINNEY 7 | 345 | 9.8362 | 9.8361 | 0.0001
GEN-2018-099 | 05 SOUTHWEST | 523977 | HARRNG_WST 6 | 230 | 26.9856 | 26.9726 | 0.013
GEN-2018-099 | 05 SOUTHWEST | 523978 | HARRNG_MID 6 | 230 | 26.9856 | 26.9726 | 0.013
GEN-2018-099 | 05 SOUTHWEST | 524007 | ROLLHILLS 3 | 115 | 19.6592 | 19.6553 | 0.0039
GEN-2018-099 | 05 SOUTHWEST | 524043 | NICHOLS 3 | 115 | 30.649 | 30.6423 | 0.0067
GEN-2018-099 | 05 SOUTHWEST | 524266 | BUSHLAND 3 | 115 | 10.3324 | 10.3301 | 0.0023
GEN-2018-099 | 05 SOUTHWEST | 524290 | WILDOR2_JUS6 | 230 | 6.9783 | 6.9757 | 0.0026
GEN-2018-099 | 05 SOUTHWEST | 524364 | RANDALL 3 | 115 | 21.0733 | 21.0668 | 0.0065
GEN-2018-099 | 05 SOUTHWEST | 524377 | FARMERS 3 | 115 | 15.4368 | 15.4335 | 0.0033
GEN-2018-099 | 05 SOUTHWEST | 524397 | ARROWHEAD 3 | 115 | 13.6793 | 13.677 | 0.0023
GEN-2018-099 | 05 SOUTHWEST | 524404 | OWENSCORN 3 | 115 | 15.0594 | 15.0564 | 0.003
GEN-2018-099 | 05 SOUTHWEST | 524486 | CAPROCK 3 | 115 | 2.636 | 2.6358 | 0.0002
GEN-2018-099 | 05 SOUTHWEST | 524509 | FE-TUCMCARI3 | 115 | 2.391 | 2.3908 | 0.0002
GEN-2018-099 | 05 SOUTHWEST | 524544 | SPRING_DRW 3 | 115 | 6.4069 | 6.4064 | 0.0005
GEN-2018-099 | 05 SOUTHWEST | 524630 | TIERABLANCA3 | 115 | 12.3344 | 12.3218 | 0.0126
GEN-2018-099 | 05 SOUTHWEST | 524662 | PARMER_CO 3 | 115 | 5.4666 | 5.4626 | 0.004
GEN-2018-099 | 05 SOUTHWEST | 524694 | DS-#22 3 | 115 | 4.5966 | 4.595 | 0.0016
GEN-2018-099 | 05 SOUTHWEST | 524734 | DS-#21 3 | 115 | 9.3056 | 9.2987 | 0.0069
GEN-2018-099 | 05 SOUTHWEST | 524745 | CASTRO_CNTY2 | 69 | 8.7963 | 8.7926 | 0.0037
GEN-2018-099 | 05 SOUTHWEST | 524757 | BETHEL_COL13 | 115 | 8.2391 | 8.2342 | 0.0049
GEN-2018-099 | 05 SOUTHWEST | 524777 | N_CLOVIS 3 | 115 | 6.7428 | 6.7349 | 0.0079
GEN-2018-099 | 05 SOUTHWEST | 524783 | W_CLOVIS 2 | 69 | 2.4403 | 2.4396 | 0.0007
GEN-2018-099 | 05 SOUTHWEST | 524790 | CANNON_TP 3 | 115 | 6.0058 | 5.9993 | 0.0065
GEN-2018-099 | 05 SOUTHWEST | 524801 | NORRIS 3 | 115 | 10.4115 | 10.3917 | 0.0198
GEN-2018-099 | 05 SOUTHWEST | 524808 | FE-CLVS_INT3 | 115 | 6.9498 | 6.9413 | 0.0085
GEN-2018-099 | 05 SOUTHWEST | 524846 | FARWELL 2 | 69 | 2.1357 | 2.1353 | 0.0004
GEN-2018-099 | 05 SOUTHWEST | 524929 | RO-PORT_MTR2 | 69 | 7.5604 | 7.5537 | 0.0067
GEN-2018-099 | 05 SOUTHWEST | 524934 | ZODIAC 2 | 69 | 5.5439 | 5.5403 | 0.0036
GEN-2018-099 | 05 SOUTHWEST | 524941 | PORTALES#1 2 | 69 | 5.7509 | 5.747 | 0.0039
GEN-2018-099 | 05 SOUTHWEST | 524963 | S_PORTALES 3 | 115 | 5.7708 | 5.7643 | 0.0065
GEN-2018-099 | 05 SOUTHWEST | 525027 | BAILEYCO 2 | 69 | 5.2707 | 5.2677 | 0.003
GEN-2018-099 | 05 SOUTHWEST | 525179 | TULIA_TP 3 | 115 | 6.4624 | 6.4606 | 0.0018
GEN-2018-099 | 05 SOUTHWEST | 525191 | KRESS_INT 2 | 69 | 4.4978 | 4.4971 | 0.0007
GEN-2018-099 | 05 SOUTHWEST | 525226 | KRS_RURL_TP3 | 115 | 6.4399 | 6.4377 | 0.0022
GEN-2018-099 | 05 SOUTHWEST | 525272 | KISER 3 | 115 | 5.2683 | 5.2668 | 0.0015
GEN-2018-099 | 05 SOUTHWEST | 525291 | PLAINVW_TP 2 | 69 | 6.4824 | 6.4806 | 0.0018
GEN-2018-099 | 05 SOUTHWEST | 525298 | S_PLAINVEW 2 | 69 | 2.5852 | 2.585 | 0.0002
GEN-2018-099 | 05 SOUTHWEST | 525325 | COX 2 | 69 | 3.4185 | 3.4181 | 0.0004
GEN-2018-099 | 05 SOUTHWEST | 525351 | LH-AIKEN 2 | 69 | 2.1484 | 2.1483 | 0.0001
GEN-2018-099 | 05 SOUTHWEST | 525413 | LAMTON 2 | 69 | 5.1693 | 5.1677 | 0.0016
GEN-2018-099 | 05 SOUTHWEST | 525432 | SP-HALFWAY+2 | 69 | 5.8641 | 5.8626 | 0.0015
GEN-2018-099 | 05 SOUTHWEST | 525606 | AMHERST 2 | 69 | 2.3408 | 2.3401 | 0.0007
GEN-2018-099 | 05 SOUTHWEST | 525657 | W_ANTON_TP 2 | 69 | 4.1079 | 4.1056 | 0.0023
GEN-2018-099 | 05 SOUTHWEST | 525694 | HOBGOOD 2 | 69 | 3.4381 | 3.4366 | 0.0015
GEN-2018-099 | 05 SOUTHWEST | 525723 | CNTYLINE_TP2 | 69 | 2.2014 | 2.2013 | 0.0001
GEN-2018-099 | 05 SOUTHWEST | 525745 | LH-HALECTR 2 | 69 | 2.4289 | 2.4288 | 0.0001
GEN-2018-099 | 05 SOUTHWEST | 525790 | FLOYDADA_TP2 | 69 | 2.5171 | 2.5169 | 0.0002
GEN-2018-099 | 05 SOUTHWEST | 525801 | LRNZ_MPT 3 | 115 | 5.0442 | 5.0435 | 0.0007
GEN-2018-099 | 05 SOUTHWEST | 525811 | LH-HARMONY 2 | 69 | 4.3124 | 4.312 | 0.0004
GEN-2018-099 | 05 SOUTHWEST | 525860 | SP-BECTON +2 | 69 | 2.2545 | 2.2545 | 0
GEN-2018-099 | 05 SOUTHWEST | 525892 | MONROE 2 | 69 | 2.6475 | 2.6474 | 0.0001
GEN-2018-099 | 05 SOUTHWEST | 525925 | CROSBY 2 | 69 | 4.7847 | 4.7844 | 0.0003
GEN-2018-099 | 05 SOUTHWEST | 526009 | LC-LEVLND#22 | 69 | 4.2645 | 4.2633 | 0.0012
GEN-2018-099 | 05 SOUTHWEST | 526042 | COBLE 2 | 69 | 2.2615 | 2.2612 | 0.0003
GEN-2018-099 | 05 SOUTHWEST | 526048 | LVLNDCTY_TP2 | 69 | 4.2645 | 4.2633 | 0.0012
GEN-2018-099 | 05 SOUTHWEST | 526130 | SP-CARLISLE2 | 69 | 2.1026 | 2.1025 | 0.0001
GEN-2018-099 | 05 SOUTHWEST | 526176 | LP-DOUD 3 | 115 | 8.8577 | 8.8556 | 0.0021
GEN-2018-099 | 05 SOUTHWEST | 526184 | SW_6878 2 | 69 | 2.1534 | 2.1533 | 0.0001
GEN-2018-099 | 05 SOUTHWEST | 526195 | QUINCY 3 | 115 | 9.6342 | 9.6319 | 0.0023
GEN-2018-099 | 05 SOUTHWEST | 526213 | ALLEN 3 | 115 | 10.4502 | 10.4479 | 0.0023
GEN-2018-099 | 05 SOUTHWEST | 526267 | LUBBCK_STH 2 | 69 | 4.3104 | 4.3102 | 0.0002
GEN-2018-099 | 05 SOUTHWEST | 526284 | PLANTERS 2 | 69 | 5.7109 | 5.7106 | 0.0003
GEN-2018-099 | 05 SOUTHWEST | 526310 | CLUTTER 2 | 69 | 5.3812 | 5.3808 | 0.0004
GEN-2018-099 | 05 SOUTHWEST | 526361 | COCHRAN 3 | 115 | 6.4257 | 6.4239 | 0.0018
GEN-2018-099 | 05 SOUTHWEST | 526452 | AMOCO_CRYO 3 | 115 | 6.362 | 6.3599 | 0.0021
GEN-2018-099 | 05 SOUTHWEST | 526475 | YUMA_INT 3 | 115 | 10.7034 | 10.7002 | 0.0032
GEN-2018-099 | 05 SOUTHWEST | 526481 | SP-WOLF_TP 3 | 115 | 10.8642 | 10.8609 | 0.0033
GEN-2018-099 | 05 SOUTHWEST | 526484 | LG-LEVELAND3 | 115 | 9.1775 | 9.1733 | 0.0042
GEN-2018-099 | 05 SOUTHWEST | 526562 | SLATON 2 | 69 | 2.4663 | 2.4662 | 0.0001
GEN-2018-099 | 05 SOUTHWEST | 526602 | WOODROW 3 | 115 | 9.1323 | 9.1308 | 0.0015
GEN-2018-099 | 05 SOUTHWEST | 526656 | LYNN_CNTY 3 | 115 | 5.9373 | 5.9368 | 0.0005
GEN-2018-099 | 05 SOUTHWEST | 526694 | GRAHAM 3 | 115 | 2.8169 | 2.8168 | 0.0001
GEN-2018-099 | 05 SOUTHWEST | 526736 | TERRY_CNTY 3 | 115 | 10.6679 | 10.6651 | 0.0028
GEN-2018-099 | 05 SOUTHWEST | 526944 | LG-PLAINS 3 | 115 | 7.9013 | 7.8999 | 0.0014
GEN-2018-099 | 05 SOUTHWEST | 527018 | BENNETT 3 | 115 | 13.7758 | 13.7731 | 0.0027
GEN-2018-099 | 05 SOUTHWEST | 527030 | ALRDCRTZ_TP3 | 115 | 12.2915 | 12.2897 | 0.0018
GEN-2018-099 | 05 SOUTHWEST | 527047 | OXY_WILRD1 3 | 115 | 10.8936 | 10.892 | 0.0016
GEN-2018-099 | 05 SOUTHWEST | 527062 | SHELL_CO2 3 | 115 | 16.7017 | 16.6982 | 0.0035
GEN-2018-099 | 05 SOUTHWEST | 527130 | DENVER_N 3 | 115 | 22.5277 | 22.5219 | 0.0058
GEN-2018-099 | 05 SOUTHWEST | 527136 | DENVER_S 3 | 115 | 22.5277 | 22.5219 | 0.0058
GEN-2018-099 | 05 SOUTHWEST | 527202 | SEAGRAVES 3 | 115 | 9.1786 | 9.1774 | 0.0012
GEN-2018-099 | 05 SOUTHWEST | 527275 | SEMINOLE 3 | 115 | 14.6609 | 14.6585 | 0.0024
GEN-2018-099 | 05 SOUTHWEST | 527482 | CHAVES_CNTY3 | 115 | 7.0492 | 7.0469 | 0.0023
GEN-2018-099 | 05 SOUTHWEST | 527600 | SAGA_SMEAS 7 | 345 | 10.2321 | 10.2123 | 0.0198
GEN-2018-099 | 05 SOUTHWEST | 527666 | RSVLT_COL1 7 | 345 | 8.7265 | 8.7123 | 0.0142
GEN-2018-099 | 05 SOUTHWEST | 527667 | RSVLT_COL2 7 | 345 | 8.7265 | 8.7123 | 0.0142
GEN-2018-099 | 05 SOUTHWEST | 527793 | EDDY_STH 3 | 115 | 11.9559 | 11.9515 | 0.0044
GEN-2018-099 | 05 SOUTHWEST | 527798 | EDDY_NTH 3 | 115 | 11.9559 | 11.9515 | 0.0044
GEN-2018-099 | 05 SOUTHWEST | 527865 | CUNNIGHM_N 6 | 230 | 17.5364 | 17.5286 | 0.0078
GEN-2018-099 | 05 SOUTHWEST | 527867 | CUNNIGHM_S 6 | 230 | 17.5364 | 17.5286 | 0.0078
GEN-2018-099 | 05 SOUTHWEST | 527891 | HOBBS_INT 3 | 115 | 33.0667 | 33.0592 | 0.0075
GEN-2018-099 | 05 SOUTHWEST | 527966 | KIOWA 3 | 115 | 17.1508 | 17.1434 | 0.0074
GEN-2018-099 | 05 SOUTHWEST | 528015 | PHANTOM 7 | 345 | 5.675 | 5.6722 | 0.0028
GEN-2018-099 | 05 SOUTHWEST | 528025 | RDRUNNER 3 | 115 | 13.7957 | 13.7907 | 0.005
GEN-2018-099 | 05 SOUTHWEST | 528095 | 7-RIVERS 6 | 230 | 6.3874 | 6.3851 | 0.0023
GEN-2018-099 | 05 SOUTHWEST | 528185 | N_LOVING 7 | 345 | 6.5496 | 6.5458 | 0.0038
GEN-2018-099 | 05 SOUTHWEST | 528325 | LE-WAITS 3 | 115 | 8.9967 | 8.9959 | 0.0008
GEN-2018-099 | 05 SOUTHWEST | 528604 | ANDREWS 6 | 230 | 6.0764 | 6.0754 | 0.001
GEN-2018-099 | 05 SOUTHWEST | 528626 | LE-PLNSINT 2 | 69 | 3.6375 | 3.6374 | 0.0001
GEN-2018-099 | 05 SOUTHWEST | 531512 | HARBNGR7 | 345 | 6.5579 | 6.5578 | 0.0001
GEN-2018-099 | 05 SOUTHWEST | 560078 | G16-037-TAP | 345 | 10.1427 | 10.1423 | 0.0004
GEN-2018-099 | 05 SOUTHWEST | 560577 | G06-44 | 115 | 7.5797 | 7.5796 | 0.0001
GEN-2018-099 | 05 SOUTHWEST | 576395 | GEN-2010-014 | 345 | 10.3812 | 10.3806 | 0.0006
GEN-2018-099 | 05 SOUTHWEST | 588460 | A16-008SUB | 115 | 13.258 | 13.2558 | 0.0022
GEN-2018-099 | 05 SOUTHWEST | 599960 | EPTNP-D6 | 230 | 9.402 | 9.3965 | 0.0055
GEN-2018-099 | 05 SOUTHWEST | 755000 | WWDBORDT | 345 | 12.2648 | 12.2633 | 0.0015
GEN-2018-099 | 05 SOUTHWEST | 761355 | GEN-2017-239 | 230 | 13.7988 | 13.7922 | 0.0066
GEN-2018-099 | 05 SOUTHWEST | 762217 | GEN-2017-151 | 345 | 6.1754 | 6.1739 | 0.0015
GEN-2018-099 | 05 SOUTHWEST | 762467 | G18-015-TAP | 345 | 5.8242 | 5.8238 | 0.0004
GEN-2018-111 | 05 SOUTHWEST | 525531 | TOLK 6 | 230 | 31.4946 | 31.4946 | 0
GEN-2018-111 | 05 SOUTHWEST | 524909 | ROOSEVELT 6 | 230 | 9.709 | 9.709 | 0
GEN-2018-111 | 05 SOUTHWEST | 525481 | PLANT_X 6 | 230 | 24.1838 | 24.1838 | 0
GEN-2018-111 | 05 SOUTHWEST | 525549 | TOLK 7 | 345 | 15.0276 | 15.0276 | 0
GEN-2018-111 | 05 SOUTHWEST | 525586 | NEEDMORE 6 | 230 | 11.0214 | 11.0214 | 0
GEN-2018-111 | 05 SOUTHWEST | 525637 | LAMB_CNTY 6 | 230 | 5.4027 | 5.4027 | 0
GEN-2018-111 | 05 SOUTHWEST | 525830 | TUCO_INT 6 | 230 | 21.9895 | 21.9895 | 0
GEN-2018-111 | 05 SOUTHWEST | 762132 | GEN-2017-158 | 230 | 13.8646 | 13.8646 | 0
GEN-2018-111 | 05 SOUTHWEST | 763241 | GEN-2018-097 | 230 | 24.4484 | 24.4484 | 0
GEN-2018-111 | 05 SOUTHWEST | 523961 | POTTER_CO 7 | 345 | 11.6631 | 11.6631 | 0
GEN-2018-111 | 05 SOUTHWEST | 524770 | PLSNT_HILL 6 | 230 | 6.517 | 6.517 | 0
GEN-2018-111 | 05 SOUTHWEST | 524875 | OASIS 6 | 230 | 7.8784 | 7.8784 | 0
GEN-2018-111 | 05 SOUTHWEST | 524908 | ROOSEVELT 3 | 115 | 11.1454 | 11.1454 | 0
GEN-2018-111 | 05 SOUTHWEST | 525213 | SWISHER 6 | 230 | 10.3853 | 10.3853 | 0
GEN-2018-111 | 05 SOUTHWEST | 525461 | NEWHART 6 | 230 | 10.9971 | 10.9971 | 0
GEN-2018-111 | 05 SOUTHWEST | 525480 | PLANT_X 3 | 115 | 19.2796 | 19.2796 | 0
GEN-2018-111 | 05 SOUTHWEST | 525585 | BLUECLDPOI 6 | 230 | 11.0214 | 11.0214 | 0
GEN-2018-111 | 05 SOUTHWEST | 525636 | LAMB_CNTY 3 | 115 | 8.4389 | 8.4389 | 0
GEN-2018-111 | 05 SOUTHWEST | 525828 | TUCO_INT 3 | 115 | 19.3618 | 19.3618 | 0
GEN-2018-111 | 05 SOUTHWEST | 525832 | TUCO_INT 7 | 345 | 14.0745 | 14.0745 | 0
GEN-2018-111 | 05 SOUTHWEST | 525840 | ANTELOPE_1 6 | 230 | 21.8013 | 21.8013 | 0
GEN-2018-111 | 05 SOUTHWEST | 525957 | HALE_WNDCL16 | 230 | 10.5196 | 10.5196 | 0
GEN-2018-111 | 05 SOUTHWEST | 526161 | CARLISLE 6 | 230 | 10.473 | 10.473 | 0
GEN-2018-111 | 05 SOUTHWEST | 526337 | JONES 6 | 230 | 16.6076 | 16.6076 | 0
GEN-2018-111 | 05 SOUTHWEST | 526435 | SUNDOWN 6 | 230 | 11.7438 | 11.7438 | 0
GEN-2018-111 | 05 SOUTHWEST | 526935 | YOAKUM 6 | 230 | 19.6825 | 19.6825 | 0
GEN-2018-111 | 05 SOUTHWEST | 527656 | CROSSROADS 7 | 345 | 11.539 | 11.539 | 0
GEN-2018-111 | 05 SOUTHWEST | 599955 | PNM-DC6 | 230 | 9.709 | 9.709 | 0
GEN-2018-111 | 05 SOUTHWEST | 760498 | G17-146-TAP | 230 | 7.745 | 7.745 | 0
GEN-2018-111 | 05 SOUTHWEST | 763120 | GEN-2018-081 | 230 | 17.3907 | 17.3907 | 0
GEN-2018-111 | 05 SOUTHWEST | 763483 | GEN-2019-003 | 230 | 8.7401 | 8.7401 | 0
GEN-2018-111 | 05 SOUTHWEST | 523097 | HITCHLAND 7 | 345 | 14.9713 | 14.9713 | 0
GEN-2018-111 | 05 SOUTHWEST | 523959 | POTTER_CO 6 | 230 | 22.4376 | 22.4376 | 0
GEN-2018-111 | 05 SOUTHWEST | 524296 | SPNSPUR_WND7 | 345 | 5.3278 | 5.3278 | 0
GEN-2018-111 | 05 SOUTHWEST | 524415 | AMA_SOUTH 6 | 230 | 13.6408 | 13.6408 | 0
GEN-2018-111 | 05 SOUTHWEST | 524623 | DEAFSMITH 6 | 230 | 8.0257 | 8.0257 | 0
GEN-2018-111 | 05 SOUTHWEST | 524768 | PLSNT_HILL 3 | 115 | 10.5272 | 10.5272 | 0
GEN-2018-111 | 05 SOUTHWEST | 524822 | CURRY 3 | 115 | 11.4402 | 11.4402 | 0
GEN-2018-111 | 05 SOUTHWEST | 524874 | OASIS 3 | 115 | 10.0542 | 10.0542 | 0
GEN-2018-111 | 05 SOUTHWEST | 524885 | SN_JUAN_TAP6 | 230 | 4.8705 | 4.8705 | 0
GEN-2018-111 | 05 SOUTHWEST | 524924 | PORTALES 3 | 115 | 7.5524 | 7.5524 | 0
GEN-2018-111 | 05 SOUTHWEST | 525019 | MULSHVLY_TP3 | 115 | 5.9489 | 5.9489 | 0
GEN-2018-111 | 05 SOUTHWEST | 525056 | BC-EARTH 3 | 115 | 8.2606 | 8.2606 | 0
GEN-2018-111 | 05 SOUTHWEST | 525212 | SWISHER 3 | 115 | 11.4972 | 11.4972 | 0
GEN-2018-111 | 05 SOUTHWEST | 525446 | RKYFORD_TP 3 | 115 | 10.1267 | 10.1267 | 0
GEN-2018-111 | 05 SOUTHWEST | 525454 | HALE_CNTY 3 | 115 | 10.1608 | 10.1608 | 0
GEN-2018-111 | 05 SOUTHWEST | 525460 | NEWHART 3 | 115 | 14.9423 | 14.9423 | 0
GEN-2018-111 | 05 SOUTHWEST | 525584 | BLUECLDCOL 6 | 230 | 10.4275 | 10.4275 | 0
GEN-2018-111 | 05 SOUTHWEST | 525635 | LAMB_CNTY 2 | 69 | 5.8992 | 5.8992 | 0
GEN-2018-111 | 05 SOUTHWEST | 525780 | FLOYD_CNTY 3 | 115 | 6.2514 | 6.2514 | 0
GEN-2018-111 | 05 SOUTHWEST | 525816 | TUCO_INT2 2 | 69 | 4.6524 | 4.6524 | 0
GEN-2018-111 | 05 SOUTHWEST | 525826 | TUCO_INT 2 | 69 | 7.8538 | 7.8538 | 0
GEN-2018-111 | 05 SOUTHWEST | 525850 | ELK_CT1 | 345 | 13.9398 | 13.9398 | 0
GEN-2018-111 | 05 SOUTHWEST | 526020 | HOCKLEY 3 | 115 | 5.426 | 5.426 | 0
GEN-2018-111 | 05 SOUTHWEST | 526076 | STANTON_W 3 | 115 | 8.923 | 8.923 | 0
GEN-2018-111 | 05 SOUTHWEST | 526160 | CARLISLE 3 | 115 | 12.772 | 12.772 | 0
GEN-2018-111 | 05 SOUTHWEST | 526269 | LUBBCK_STH 6 | 230 | 15.0546 | 15.0546 | 0
GEN-2018-111 | 05 SOUTHWEST | 526298 | LUBBCK_EST 3 | 115 | 14.4141 | 14.4141 | 0
GEN-2018-111 | 05 SOUTHWEST | 526299 | LUBBCK_EST 6 | 230 | 11.0462 | 11.0462 | 0
GEN-2018-111 | 05 SOUTHWEST | 526434 | SUNDOWN 3 | 115 | 10.8603 | 10.8603 | 0
GEN-2018-111 | 05 SOUTHWEST | 526460 | AMOCO_SS 6 | 230 | 10.1771 | 10.1771 | 0
GEN-2018-111 | 05 SOUTHWEST | 526525 | WOLFFORTH 6 | 230 | 13.0516 | 13.0516 | 0
GEN-2018-111 | 05 SOUTHWEST | 526677 | GRASSLAND 6 | 230 | 5.9735 | 5.9735 | 0
GEN-2018-111 | 05 SOUTHWEST | 526934 | YOAKUM 3 | 115 | 19.2326 | 19.2326 | 0
GEN-2018-111 | 05 SOUTHWEST | 526936 | YOAKUM_345 | 345 | 9.9314 | 9.9314 | 0
GEN-2018-111 | 05 SOUTHWEST | 527009 | BRU_SUB 6 | 230 | 15.6513 | 15.6513 | 0
GEN-2018-111 | 05 SOUTHWEST | 527028 | INK_BASIN 6 | 230 | 11.2413 | 11.2413 | 0
GEN-2018-111 | 05 SOUTHWEST | 527149 | MUSTANG 6 | 230 | 17.9238 | 17.9238 | 0
GEN-2018-111 | 05 SOUTHWEST | 527610 | SAGA_SCOL 7 | 345 | 10.2321 | 10.2321 | 0
GEN-2018-111 | 05 SOUTHWEST | 527655 | RSVLT_CC_E 7 | 345 | 10.0154 | 10.0154 | 0
GEN-2018-111 | 05 SOUTHWEST | 527802 | EDDY_CNTY 7 | 345 | 7.3273 | 7.3273 | 0
GEN-2018-111 | 05 SOUTHWEST | 527896 | HOBBS_INT 7 | 345 | 12.0143 | 12.0143 | 0
GEN-2018-111 | 05 SOUTHWEST | 560022 | CRAWFISH_DR | 345 | 13.842 | 13.842 | 0
GEN-2018-111 | 05 SOUTHWEST | 560035 | GRAPEVINE | 345 | 6.4589 | 6.4589 | 0
GEN-2018-111 | 05 SOUTHWEST | 760494 | GEN-2017-146 | 230 | 7.4558 | 7.4558 | 0
GEN-2018-111 | 05 SOUTHWEST | 763186 | GEN-2018-089 | 230 | 10.6882 | 10.6882 | 0
GEN-2018-111 | 05 SOUTHWEST | 511553 | CHISHOLM7 | 345 | 12.3397 | 12.3397 | 0
GEN-2018-111 | 05 SOUTHWEST | 515458 | BORDER 7 | 345 | 8.2517 | 8.2517 | 0
GEN-2018-111 | 05 SOUTHWEST | 515554 | BVRCNTY7 | 345 | 15.3093 | 15.3093 | 0
GEN-2018-111 | 05 SOUTHWEST | 523095 | HITCHLAND 6 | 230 | 14.5761 | 14.5761 | 0
GEN-2018-111 | 05 SOUTHWEST | 523101 | NOBLE_WND 7 | 345 | 14.9103 | 14.9103 | 0
GEN-2018-111 | 05 SOUTHWEST | 523112 | NOVUS1 7 | 345 | 14.6716 | 14.6716 | 0
GEN-2018-111 | 05 SOUTHWEST | 523323 | MCDWL_CREEK6 | 230 | 8.9802 | 8.9802 | 0
GEN-2018-111 | 05 SOUTHWEST | 523823 | CARPENTER 7 | 345 | 6.5781 | 6.5781 | 0
GEN-2018-111 | 05 SOUTHWEST | 523869 | CHAN+TASCOS6 | 230 | 4.2464 | 4.2464 | 0
GEN-2018-111 | 05 SOUTHWEST | 523979 | HARRNG_EST 6 | 230 | 26.9856 | 26.9856 | 0
GEN-2018-111 | 05 SOUTHWEST | 524010 | ROLLHILLS 6 | 230 | 20.2306 | 20.2306 | 0
GEN-2018-111 | 05 SOUTHWEST | 524044 | NICHOLS 6 | 230 | 26.1237 | 26.1237 | 0
GEN-2018-111 | 05 SOUTHWEST | 524267 | BUSHLAND 6 | 230 | 10.1739 | 10.1739 | 0
GEN-2018-111 | 05 SOUTHWEST | 524299 | SPNSPUR_COL7 | 345 | 5.3278 | 5.3278 | 0
GEN-2018-111 | 05 SOUTHWEST | 524365 | RANDALL 6 | 230 | 14.5681 | 14.5681 | 0
GEN-2018-111 | 05 SOUTHWEST | 524414 | AMA_SOUTH 3 | 115 | 16.9088 | 16.9088 | 0
GEN-2018-111 | 05 SOUTHWEST | 524502 | NORTON 3 | 115 | 2.9186 | 2.9186 | 0
GEN-2018-111 | 05 SOUTHWEST | 524619 | DFSMTH_EST 3 | 115 | 11.9939 | 11.9939 | 0
GEN-2018-111 | 05 SOUTHWEST | 524622 | DFSMTH_WST 3 | 115 | 11.9945 | 11.9945 | 0
GEN-2018-111 | 05 SOUTHWEST | 524669 | DS-#20 3 | 115 | 6.2762 | 6.2762 | 0
GEN-2018-111 | 05 SOUTHWEST | 524746 | CASTRO_CNTY3 | 115 | 9.822 | 9.822 | 0
GEN-2018-111 | 05 SOUTHWEST | 524764 | NORRIS_TP 3 | 115 | 11.4074 | 11.4074 | 0
GEN-2018-111 | 05 SOUTHWEST | 524773 | E_CLOVIS 3 | 115 | 8.962 | 8.962 | 0
GEN-2018-111 | 05 SOUTHWEST | 524776 | N_CLOVIS_TP3 | 115 | 7.4744 | 7.4744 | 0
GEN-2018-111 | 05 SOUTHWEST | 524797 | PERIMETER 3 | 115 | 6.5512 | 6.5512 | 0
GEN-2018-111 | 05 SOUTHWEST | 524821 | CURRY 2 | 69 | 4.4284 | 4.4284 | 0
GEN-2018-111 | 05 SOUTHWEST | 524831 | FE-HOLLAND 3 | 115 | 9.2431 | 9.2431 | 0
GEN-2018-111 | 05 SOUTHWEST | 524838 | FE-CLOVIS2+3 | 115 | 10.7942 | 10.7942 | 0
GEN-2018-111 | 05 SOUTHWEST | 524863 | FE-CHZPLT 3 | 115 | 8.0228 | 8.0228 | 0
GEN-2018-111 | 05 SOUTHWEST | 524889 | SN_JUAN_WND6 | 230 | 4.6556 | 4.6556 | 0
GEN-2018-111 | 05 SOUTHWEST | 524923 | PORTALES 2 | 69 | 7.5604 | 7.5604 | 0
GEN-2018-111 | 05 SOUTHWEST | 524935 | KILGORE 3 | 115 | 6.1488 | 6.1488 | 0
GEN-2018-111 | 05 SOUTHWEST | 524977 | GREYHOUND 3 | 115 | 5.6862 | 5.6862 | 0
GEN-2018-111 | 05 SOUTHWEST | 525018 | MULESHVALLY3 | 115 | 5.5409 | 5.5409 | 0
GEN-2018-111 | 05 SOUTHWEST | 525028 | BAILEYCO 3 | 115 | 5.8021 | 5.8021 | 0
GEN-2018-111 | 05 SOUTHWEST | 525050 | BC-KELLEY +3 | 115 | 7.782 | 7.782 | 0
GEN-2018-111 | 05 SOUTHWEST | 525124 | HART_INDUST3 | 115 | 7.4925 | 7.4925 | 0
GEN-2018-111 | 05 SOUTHWEST | 525192 | KRESS_INT 3 | 115 | 11.9205 | 11.9205 | 0
GEN-2018-111 | 05 SOUTHWEST | 525326 | COX 3 | 115 | 6.2736 | 6.2736 | 0
GEN-2018-111 | 05 SOUTHWEST | 525393 | ROCKYFORD 3 | 115 | 9.0431 | 9.0431 | 0
GEN-2018-111 | 05 SOUTHWEST | 525414 | LAMTON 3 | 115 | 7.6144 | 7.6144 | 0
GEN-2018-111 | 05 SOUTHWEST | 525440 | LC-S_OLTON+3 | 115 | 7.1982 | 7.1982 | 0
GEN-2018-111 | 05 SOUTHWEST | 525453 | HALE_CNTY 2 | 69 | 6.9062 | 6.9062 | 0
GEN-2018-111 | 05 SOUTHWEST | 525613 | W_LITTLFLD 2 | 69 | 2.9684 | 2.9684 | 0
GEN-2018-111 | 05 SOUTHWEST | 525620 | LTFLD_S&CTY2 | 69 | 4.1727 | 4.1727 | 0
GEN-2018-111 | 05 SOUTHWEST | 525650 | LC-LTTLFLD+2 | 69 | 4.9319 | 4.9319 | 0
GEN-2018-111 | 05 SOUTHWEST | 525687 | LC-LUMSCHAP2 | 69 | 4.6126 | 4.6126 | 0
GEN-2018-111 | 05 SOUTHWEST | 525731 | SP-ABERNTHY2 | 69 | 3.0093 | 3.0093 | 0
GEN-2018-111 | 05 SOUTHWEST | 525738 | HALECENTER 2 | 69 | 2.4566 | 2.4566 | 0
GEN-2018-111 | 05 SOUTHWEST | 525763 | CALLAHAN 3 | 115 | 5.5668 | 5.5668 | 0
GEN-2018-111 | 05 SOUTHWEST | 525779 | FLOYD_CNTY 2 | 69 | 5.401 | 5.401 | 0
GEN-2018-111 | 05 SOUTHWEST | 525803 | BLANCO 3 | 115 | 5.0451 | 5.0451 | 0
GEN-2018-111 | 05 SOUTHWEST | 525853 | LH-WIL&ELN+2 | 69 | 2.5404 | 2.5404 | 0
GEN-2018-111 | 05 SOUTHWEST | 525885 | SP-NEWDEAL 2 | 69 | 3.3073 | 3.3073 | 0
GEN-2018-111 | 05 SOUTHWEST | 525926 | CROSBY 3 | 115 | 4.7129 | 4.7129 | 0
GEN-2018-111 | 05 SOUTHWEST | 526019 | HOCKLEY 2 | 69 | 5.1105 | 5.1105 | 0
GEN-2018-111 | 05 SOUTHWEST | 526036 | LC-OPDYKE 3 | 115 | 5.7143 | 5.7143 | 0
GEN-2018-111 | 05 SOUTHWEST | 526109 | SP-ERSKINE 3 | 115 | 10.9787 | 10.9787 | 0
GEN-2018-111 | 05 SOUTHWEST | 526146 | INDIANA 3 | 115 | 9.3032 | 9.3032 | 0
GEN-2018-111 | 05 SOUTHWEST | 526159 | CARLISLE 2 | 69 | 2.5568 | 2.5568 | 0
GEN-2018-111 | 05 SOUTHWEST | 526162 | LP-DOUD_TP 3 | 115 | 11.325 | 11.325 | 0
GEN-2018-111 | 05 SOUTHWEST | 526192 | MURPHY 3 | 115 | 10.2503 | 10.2503 | 0
GEN-2018-111 | 05 SOUTHWEST | 526268 | LUBBCK_STH 3 | 115 | 17.6482 | 17.6482 | 0
GEN-2018-111 | 05 SOUTHWEST | 526297 | LUBBCK_EST 2 | 69 | 7.8955 | 7.8955 | 0
GEN-2018-111 | 05 SOUTHWEST | 526424 | PACIFIC 3 | 115 | 9.1771 | 9.1771 | 0
GEN-2018-111 | 05 SOUTHWEST | 526445 | AMOCO_TP 3 | 115 | 10.1845 | 10.1845 | 0
GEN-2018-111 | 05 SOUTHWEST | 526524 | WOLFFORTH 3 | 115 | 11.2819 | 11.2819 | 0
GEN-2018-111 | 05 SOUTHWEST | 526676 | GRASSLAND 3 | 115 | 6.8633 | 6.8633 | 0
GEN-2018-111 | 05 SOUTHWEST | 526679 | CIRRUS_WND 6 | 230 | 4.6792 | 4.6792 | 0
GEN-2018-111 | 05 SOUTHWEST | 526784 | AMOCOWASSON6 | 230 | 15.6353 | 15.6353 | 0
GEN-2018-111 | 05 SOUTHWEST | 526792 | PRENTICE 3 | 115 | 6.0286 | 6.0286 | 0
GEN-2018-111 | 05 SOUTHWEST | 526928 | PLAINS_INT 3 | 115 | 10.0196 | 10.0196 | 0
GEN-2018-111 | 05 SOUTHWEST | 527010 | OXYBRU 6 | 230 | 15.5052 | 15.5052 | 0
GEN-2018-111 | 05 SOUTHWEST | 527011 | XTO_MAHONEY6 | 230 | 15.3578 | 15.3578 | 0
GEN-2018-111 | 05 SOUTHWEST | 527027 | INK_BASIN 3 | 115 | 13.258 | 13.258 | 0
GEN-2018-111 | 05 SOUTHWEST | 527041 | ARCO_TP 3 | 115 | 13.6807 | 13.6807 | 0
GEN-2018-111 | 05 SOUTHWEST | 527146 | MUSTANG 3 | 115 | 24.0628 | 24.0628 | 0
GEN-2018-111 | 05 SOUTHWEST | 527151 | GS-MUSTANG 6 | 230 | 17.9238 | 17.9238 | 0
GEN-2018-111 | 05 SOUTHWEST | 527194 | LG-PLSHILL 3 | 115 | 7.9741 | 7.9741 | 0
GEN-2018-111 | 05 SOUTHWEST | 527276 | SEMINOLE 6 | 230 | 8.197 | 8.197 | 0
GEN-2018-111 | 05 SOUTHWEST | 527483 | CHAVES_CNTY6 | 230 | 4.4929 | 4.4929 | 0
GEN-2018-111 | 05 SOUTHWEST | 527599 | SAGA_SDCOL 7 | 345 | 10.2321 | 10.2321 | 0
GEN-2018-111 | 05 SOUTHWEST | 527654 | RSVLT_CC_W 7 | 345 | 8.7265 | 8.7265 | 0
GEN-2018-111 | 05 SOUTHWEST | 527799 | EDDY_NORTH 6 | 230 | 9.402 | 9.402 | 0
GEN-2018-111 | 05 SOUTHWEST | 527894 | HOBBS_INT 6 | 230 | 19.4767 | 19.4767 | 0
GEN-2018-111 | 05 SOUTHWEST | 527965 | KIOWA 7 | 345 | 8.82 | 8.82 | 0
GEN-2018-111 | 05 SOUTHWEST | 528027 | RDRUNNER 7 | 345 | 8.6815 | 8.6815 | 0
GEN-2018-111 | 05 SOUTHWEST | 576397 | G10014G11022 | 345 | 10.3812 | 10.3812 | 0
GEN-2018-111 | 05 SOUTHWEST | 762216 | G17-151TAP | 345 | 8.5119 | 8.5119 | 0
GEN-2018-111 | 05 SOUTHWEST | 763087 | GEN-2018-073 | 345 | 11.9423 | 11.9423 | 0
GEN-2018-111 | 05 SOUTHWEST | 763516 | GEN-2019-011 | 345 | 9.2852 | 9.2852 | 0
GEN-2018-111 | 05 SOUTHWEST | 511557 | CHISHOLM6 | 230 | 12.1566 | 12.1566 | 0
GEN-2018-111 | 05 SOUTHWEST | 515375 | WWRDEHV7 | 345 | 22.3641 | 22.3641 | 0
GEN-2018-111 | 05 SOUTHWEST | 515590 | PALDR2W7 | 345 | 12.8669 | 12.8669 | 0
GEN-2018-111 | 05 SOUTHWEST | 515618 | BALKOW 7 | 345 | 12.5807 | 12.5807 | 0
GEN-2018-111 | 05 SOUTHWEST | 515677 | BADGER 7 | 345 | 13.7821 | 13.7821 | 0
GEN-2018-111 | 05 SOUTHWEST | 523093 | HITCHLAND 3 | 115 | 17.3358 | 17.3358 | 0
GEN-2018-111 | 05 SOUTHWEST | 523103 | NOBLE_WND 3 | 115 | 10.6199 | 10.6199 | 0
GEN-2018-111 | 05 SOUTHWEST | 523111 | NOVUS1 3 | 115 | 7.8432 | 7.8432 | 0
GEN-2018-111 | 05 SOUTHWEST | 523155 | OCHILTREE 6 | 230 | 4.265 | 4.265 | 0
GEN-2018-111 | 05 SOUTHWEST | 523215 | GEN-2011-022 | 345 | 10.3812 | 10.3812 | 0
GEN-2018-111 | 05 SOUTHWEST | 523221 | XIT_INTG 6 | 230 | 3.1441 | 3.1441 | 0
GEN-2018-111 | 05 SOUTHWEST | 523267 | PRINGLE 6 | 230 | 4.3435 | 4.3435 | 0
GEN-2018-111 | 05 SOUTHWEST | 523309 | MOORE_CNTY 6 | 230 | 6.6813 | 6.6813 | 0
GEN-2018-111 | 05 SOUTHWEST | 523322 | MCDWL_CREEK3 | 115 | 9.8376 | 9.8376 | 0
GEN-2018-111 | 05 SOUTHWEST | 523551 | HUTCHISON 6 | 230 | 7.288 | 7.288 | 0
GEN-2018-111 | 05 SOUTHWEST | 523771 | GRAPEVINE 6 | 230 | 5.9762 | 5.9762 | 0
GEN-2018-111 | 05 SOUTHWEST | 523853 | FINNEY 7 | 345 | 9.8362 | 9.8362 | 0
GEN-2018-111 | 05 SOUTHWEST | 523977 | HARRNG_WST 6 | 230 | 26.9856 | 26.9856 | 0
GEN-2018-111 | 05 SOUTHWEST | 523978 | HARRNG_MID 6 | 230 | 26.9856 | 26.9856 | 0
GEN-2018-111 | 05 SOUTHWEST | 524007 | ROLLHILLS 3 | 115 | 19.6592 | 19.6592 | 0
GEN-2018-111 | 05 SOUTHWEST | 524043 | NICHOLS 3 | 115 | 30.649 | 30.649 | 0
GEN-2018-111 | 05 SOUTHWEST | 524266 | BUSHLAND 3 | 115 | 10.3324 | 10.3324 | 0
GEN-2018-111 | 05 SOUTHWEST | 524290 | WILDOR2_JUS6 | 230 | 6.9783 | 6.9783 | 0
GEN-2018-111 | 05 SOUTHWEST | 524364 | RANDALL 3 | 115 | 21.0733 | 21.0733 | 0
GEN-2018-111 | 05 SOUTHWEST | 524377 | FARMERS 3 | 115 | 15.4368 | 15.4368 | 0
GEN-2018-111 | 05 SOUTHWEST | 524397 | ARROWHEAD 3 | 115 | 13.6793 | 13.6793 | 0
GEN-2018-111 | 05 SOUTHWEST | 524404 | OWENSCORN 3 | 115 | 15.0594 | 15.0594 | 0
GEN-2018-111 | 05 SOUTHWEST | 524486 | CAPROCK 3 | 115 | 2.636 | 2.636 | 0
GEN-2018-111 | 05 SOUTHWEST | 524509 | FE-TUCMCARI3 | 115 | 2.391 | 2.391 | 0
GEN-2018-111 | 05 SOUTHWEST | 524544 | SPRING_DRW 3 | 115 | 6.4069 | 6.4069 | 0
GEN-2018-111 | 05 SOUTHWEST | 524630 | TIERABLANCA3 | 115 | 12.3344 | 12.3344 | 0
GEN-2018-111 | 05 SOUTHWEST | 524662 | PARMER_CO 3 | 115 | 5.4666 | 5.4666 | 0
GEN-2018-111 | 05 SOUTHWEST | 524694 | DS-#22 3 | 115 | 4.5966 | 4.5966 | 0
GEN-2018-111 | 05 SOUTHWEST | 524734 | DS-#21 3 | 115 | 9.3056 | 9.3056 | 0
GEN-2018-111 | 05 SOUTHWEST | 524745 | CASTRO_CNTY2 | 69 | 8.7963 | 8.7963 | 0
GEN-2018-111 | 05 SOUTHWEST | 524757 | BETHEL_COL13 | 115 | 8.2391 | 8.2391 | 0
GEN-2018-111 | 05 SOUTHWEST | 524777 | N_CLOVIS 3 | 115 | 6.7428 | 6.7428 | 0
GEN-2018-111 | 05 SOUTHWEST | 524783 | W_CLOVIS 2 | 69 | 2.4403 | 2.4403 | 0
GEN-2018-111 | 05 SOUTHWEST | 524790 | CANNON_TP 3 | 115 | 6.0058 | 6.0058 | 0
GEN-2018-111 | 05 SOUTHWEST | 524801 | NORRIS 3 | 115 | 10.4115 | 10.4115 | 0
GEN-2018-111 | 05 SOUTHWEST | 524808 | FE-CLVS_INT3 | 115 | 6.9498 | 6.9498 | 0
GEN-2018-111 | 05 SOUTHWEST | 524846 | FARWELL 2 | 69 | 2.1357 | 2.1357 | 0
GEN-2018-111 | 05 SOUTHWEST | 524929 | RO-PORT_MTR2 | 69 | 7.5604 | 7.5604 | 0
GEN-2018-111 | 05 SOUTHWEST | 524934 | ZODIAC 2 | 69 | 5.5439 | 5.5439 | 0
GEN-2018-111 | 05 SOUTHWEST | 524941 | PORTALES#1 2 | 69 | 5.7509 | 5.7509 | 0
GEN-2018-111 | 05 SOUTHWEST | 524963 | S_PORTALES 3 | 115 | 5.7708 | 5.7708 | 0
GEN-2018-111 | 05 SOUTHWEST | 525027 | BAILEYCO 2 | 69 | 5.2707 | 5.2707 | 0
GEN-2018-111 | 05 SOUTHWEST | 525179 | TULIA_TP 3 | 115 | 6.4624 | 6.4624 | 0
GEN-2018-111 | 05 SOUTHWEST | 525191 | KRESS_INT 2 | 69 | 4.4978 | 4.4978 | 0
GEN-2018-111 | 05 SOUTHWEST | 525226 | KRS_RURL_TP3 | 115 | 6.4399 | 6.4399 | 0
GEN-2018-111 | 05 SOUTHWEST | 525272 | KISER 3 | 115 | 5.2683 | 5.2683 | 0
GEN-2018-111 | 05 SOUTHWEST | 525291 | PLAINVW_TP 2 | 69 | 6.4824 | 6.4824 | 0
GEN-2018-111 | 05 SOUTHWEST | 525298 | S_PLAINVEW 2 | 69 | 2.5852 | 2.5852 | 0
GEN-2018-111 | 05 SOUTHWEST | 525325 | COX 2 | 69 | 3.4185 | 3.4185 | 0
GEN-2018-111 | 05 SOUTHWEST | 525351 | LH-AIKEN 2 | 69 | 2.1484 | 2.1484 | 0
GEN-2018-111 | 05 SOUTHWEST | 525413 | LAMTON 2 | 69 | 5.1693 | 5.1693 | 0
GEN-2018-111 | 05 SOUTHWEST | 525432 | SP-HALFWAY+2 | 69 | 5.8641 | 5.8641 | 0
GEN-2018-111 | 05 SOUTHWEST | 525606 | AMHERST 2 | 69 | 2.3408 | 2.3408 | 0
GEN-2018-111 | 05 SOUTHWEST | 525657 | W_ANTON_TP 2 | 69 | 4.1079 | 4.1079 | 0
GEN-2018-111 | 05 SOUTHWEST | 525694 | HOBGOOD 2 | 69 | 3.4381 | 3.4381 | 0
GEN-2018-111 | 05 SOUTHWEST | 525723 | CNTYLINE_TP2 | 69 | 2.2014 | 2.2014 | 0
GEN-2018-111 | 05 SOUTHWEST | 525745 | LH-HALECTR 2 | 69 | 2.4289 | 2.4289 | 0
GEN-2018-111 | 05 SOUTHWEST | 525790 | FLOYDADA_TP2 | 69 | 2.5171 | 2.5171 | 0
GEN-2018-111 | 05 SOUTHWEST | 525801 | LRNZ_MPT 3 | 115 | 5.0442 | 5.0442 | 0
GEN-2018-111 | 05 SOUTHWEST | 525811 | LH-HARMONY 2 | 69 | 4.3124 | 4.3124 | 0
GEN-2018-111 | 05 SOUTHWEST | 525860 | SP-BECTON +2 | 69 | 2.2545 | 2.2545 | 0
GEN-2018-111 | 05 SOUTHWEST | 525892 | MONROE 2 | 69 | 2.6475 | 2.6475 | 0
GEN-2018-111 | 05 SOUTHWEST | 525925 | CROSBY 2 | 69 | 4.7847 | 4.7847 | 0
GEN-2018-111 | 05 SOUTHWEST | 526009 | LC-LEVLND#22 | 69 | 4.2645 | 4.2645 | 0
GEN-2018-111 | 05 SOUTHWEST | 526042 | COBLE 2 | 69 | 2.2615 | 2.2615 | 0
GEN-2018-111 | 05 SOUTHWEST | 526048 | LVLNDCTY_TP2 | 69 | 4.2645 | 4.2645 | 0
GEN-2018-111 | 05 SOUTHWEST | 526130 | SP-CARLISLE2 | 69 | 2.1026 | 2.1026 | 0
GEN-2018-111 | 05 SOUTHWEST | 526176 | LP-DOUD 3 | 115 | 8.8577 | 8.8577 | 0
GEN-2018-111 | 05 SOUTHWEST | 526184 | SW_6878 2 | 69 | 2.1534 | 2.1534 | 0
GEN-2018-111 | 05 SOUTHWEST | 526195 | QUINCY 3 | 115 | 9.6342 | 9.6342 | 0
GEN-2018-111 | 05 SOUTHWEST | 526213 | ALLEN 3 | 115 | 10.4502 | 10.4502 | 0
GEN-2018-111 | 05 SOUTHWEST | 526267 | LUBBCK_STH 2 | 69 | 4.3104 | 4.3104 | 0
GEN-2018-111 | 05 SOUTHWEST | 526284 | PLANTERS 2 | 69 | 5.7109 | 5.7109 | 0
GEN-2018-111 | 05 SOUTHWEST | 526310 | CLUTTER 2 | 69 | 5.3812 | 5.3812 | 0
GEN-2018-111 | 05 SOUTHWEST | 526361 | COCHRAN 3 | 115 | 6.4257 | 6.4257 | 0
GEN-2018-111 | 05 SOUTHWEST | 526452 | AMOCO_CRYO 3 | 115 | 6.362 | 6.362 | 0
GEN-2018-111 | 05 SOUTHWEST | 526475 | YUMA_INT 3 | 115 | 10.7034 | 10.7034 | 0
GEN-2018-111 | 05 SOUTHWEST | 526481 | SP-WOLF_TP 3 | 115 | 10.8642 | 10.8642 | 0
GEN-2018-111 | 05 SOUTHWEST | 526484 | LG-LEVELAND3 | 115 | 9.1775 | 9.1775 | 0
GEN-2018-111 | 05 SOUTHWEST | 526562 | SLATON 2 | 69 | 2.4663 | 2.4663 | 0
GEN-2018-111 | 05 SOUTHWEST | 526602 | WOODROW 3 | 115 | 9.1323 | 9.1323 | 0
GEN-2018-111 | 05 SOUTHWEST | 526656 | LYNN_CNTY 3 | 115 | 5.9373 | 5.9373 | 0
GEN-2018-111 | 05 SOUTHWEST | 526694 | GRAHAM 3 | 115 | 2.8169 | 2.8169 | 0
GEN-2018-111 | 05 SOUTHWEST | 526736 | TERRY_CNTY 3 | 115 | 10.6679 | 10.6679 | 0
GEN-2018-111 | 05 SOUTHWEST | 526944 | LG-PLAINS 3 | 115 | 7.9013 | 7.9013 | 0
GEN-2018-111 | 05 SOUTHWEST | 527018 | BENNETT 3 | 115 | 13.7758 | 13.7758 | 0
GEN-2018-111 | 05 SOUTHWEST | 527030 | ALRDCRTZ_TP3 | 115 | 12.2915 | 12.2915 | 0
GEN-2018-111 | 05 SOUTHWEST | 527047 | OXY_WILRD1 3 | 115 | 10.8936 | 10.8936 | 0
GEN-2018-111 | 05 SOUTHWEST | 527062 | SHELL_CO2 3 | 115 | 16.7017 | 16.7017 | 0
GEN-2018-111 | 05 SOUTHWEST | 527130 | DENVER_N 3 | 115 | 22.5277 | 22.5277 | 0
GEN-2018-111 | 05 SOUTHWEST | 527136 | DENVER_S 3 | 115 | 22.5277 | 22.5277 | 0
GEN-2018-111 | 05 SOUTHWEST | 527202 | SEAGRAVES 3 | 115 | 9.1786 | 9.1786 | 0
GEN-2018-111 | 05 SOUTHWEST | 527275 | SEMINOLE 3 | 115 | 14.6609 | 14.6609 | 0
GEN-2018-111 | 05 SOUTHWEST | 527482 | CHAVES_CNTY3 | 115 | 7.0492 | 7.0492 | 0
GEN-2018-111 | 05 SOUTHWEST | 527600 | SAGA_SMEAS 7 | 345 | 10.2321 | 10.2321 | 0
GEN-2018-111 | 05 SOUTHWEST | 527666 | RSVLT_COL1 7 | 345 | 8.7265 | 8.7265 | 0
GEN-2018-111 | 05 SOUTHWEST | 527667 | RSVLT_COL2 7 | 345 | 8.7265 | 8.7265 | 0
GEN-2018-111 | 05 SOUTHWEST | 527793 | EDDY_STH 3 | 115 | 11.9559 | 11.9559 | 0
GEN-2018-111 | 05 SOUTHWEST | 527798 | EDDY_NTH 3 | 115 | 11.9559 | 11.9559 | 0
GEN-2018-111 | 05 SOUTHWEST | 527865 | CUNNIGHM_N 6 | 230 | 17.5364 | 17.5364 | 0
GEN-2018-111 | 05 SOUTHWEST | 527867 | CUNNIGHM_S 6 | 230 | 17.5364 | 17.5364 | 0
GEN-2018-111 | 05 SOUTHWEST | 527891 | HOBBS_INT 3 | 115 | 33.0667 | 33.0667 | 0
GEN-2018-111 | 05 SOUTHWEST | 527966 | KIOWA 3 | 115 | 17.1508 | 17.1508 | 0
GEN-2018-111 | 05 SOUTHWEST | 528015 | PHANTOM 7 | 345 | 5.675 | 5.675 | 0
GEN-2018-111 | 05 SOUTHWEST | 528025 | RDRUNNER 3 | 115 | 13.7957 | 13.7957 | 0
GEN-2018-111 | 05 SOUTHWEST | 528095 | 7-RIVERS 6 | 230 | 6.3874 | 6.3874 | 0
GEN-2018-111 | 05 SOUTHWEST | 528185 | N_LOVING 7 | 345 | 6.5496 | 6.5496 | 0
GEN-2018-111 | 05 SOUTHWEST | 528325 | LE-WAITS 3 | 115 | 8.9967 | 8.9967 | 0
GEN-2018-111 | 05 SOUTHWEST | 528604 | ANDREWS 6 | 230 | 6.0764 | 6.0764 | 0
GEN-2018-111 | 05 SOUTHWEST | 528626 | LE-PLNSINT 2 | 69 | 3.6375 | 3.6375 | 0
GEN-2018-111 | 05 SOUTHWEST | 531512 | HARBNGR7 | 345 | 6.5579 | 6.5579 | 0
GEN-2018-111 | 05 SOUTHWEST | 560078 | G16-037-TAP | 345 | 10.1427 | 10.1427 | 0
GEN-2018-111 | 05 SOUTHWEST | 560577 | G06-44 | 115 | 7.5797 | 7.5797 | 0
GEN-2018-111 | 05 SOUTHWEST | 576395 | GEN-2010-014 | 345 | 10.3812 | 10.3812 | 0
GEN-2018-111 | 05 SOUTHWEST | 588460 | A16-008SUB | 115 | 13.258 | 13.258 | 0
GEN-2018-111 | 05 SOUTHWEST | 599960 | EPTNP-D6 | 230 | 9.402 | 9.402 | 0
GEN-2018-111 | 05 SOUTHWEST | 755000 | WWDBORDT | 345 | 12.2648 | 12.2648 | 0
GEN-2018-111 | 05 SOUTHWEST | 761355 | GEN-2017-239 | 230 | 13.7988 | 13.7988 | 0
GEN-2018-111 | 05 SOUTHWEST | 762217 | GEN-2017-151 | 345 | 6.1754 | 6.1754 | 0
GEN-2018-111 | 05 SOUTHWEST | 762467 | G18-015-TAP | 345 | 5.8242 | 5.8242 | 0
GEN-2018-112 | 05 SOUTHWEST | 525531 | TOLK 6 | 230 | 31.4946 | 31.1042 | 0.3904
GEN-2018-112 | 05 SOUTHWEST | 524909 | ROOSEVELT 6 | 230 | 9.709 | 9.6865 | 0.0225
GEN-2018-112 | 05 SOUTHWEST | 525481 | PLANT_X 6 | 230 | 24.1838 | 24.0383 | 0.1455
GEN-2018-112 | 05 SOUTHWEST | 525549 | TOLK 7 | 345 | 15.0276 | 14.9373 | 0.0903
GEN-2018-112 | 05 SOUTHWEST | 525586 | NEEDMORE 6 | 230 | 11.0214 | 10.9854 | 0.036
GEN-2018-112 | 05 SOUTHWEST | 525637 | LAMB_CNTY 6 | 230 | 5.4027 | 5.3935 | 0.0092
GEN-2018-112 | 05 SOUTHWEST | 525830 | TUCO_INT 6 | 230 | 21.9895 | 21.9741 | 0.0154
GEN-2018-112 | 05 SOUTHWEST | 762132 | GEN-2017-158 | 230 | 13.8646 | 13.798 | 0.0666
GEN-2018-112 | 05 SOUTHWEST | 763241 | GEN-2018-097 | 230 | 24.4484 | 24.0516 | 0.3968
GEN-2018-112 | 05 SOUTHWEST | 523961 | POTTER_CO 7 | 345 | 11.6631 | 11.6575 | 0.0056
GEN-2018-112 | 05 SOUTHWEST | 524770 | PLSNT_HILL 6 | 230 | 6.517 | 6.5079 | 0.0091
GEN-2018-112 | 05 SOUTHWEST | 524875 | OASIS 6 | 230 | 7.8784 | 7.8655 | 0.0129
GEN-2018-112 | 05 SOUTHWEST | 524908 | ROOSEVELT 3 | 115 | 11.1454 | 11.1322 | 0.0132
GEN-2018-112 | 05 SOUTHWEST | 525213 | SWISHER 6 | 230 | 10.3853 | 10.3798 | 0.0055
GEN-2018-112 | 05 SOUTHWEST | 525461 | NEWHART 6 | 230 | 10.9971 | 10.9876 | 0.0095
GEN-2018-112 | 05 SOUTHWEST | 525480 | PLANT_X 3 | 115 | 19.2796 | 19.2437 | 0.0359
GEN-2018-112 | 05 SOUTHWEST | 525585 | BLUECLDPOI 6 | 230 | 11.0214 | 10.9854 | 0.036
GEN-2018-112 | 05 SOUTHWEST | 525636 | LAMB_CNTY 3 | 115 | 8.4389 | 8.4305 | 0.0084
GEN-2018-112 | 05 SOUTHWEST | 525828 | TUCO_INT 3 | 115 | 19.3618 | 19.3555 | 0.0063
GEN-2018-112 | 05 SOUTHWEST | 525832 | TUCO_INT 7 | 345 | 14.0745 | 14.0687 | 0.0058
GEN-2018-112 | 05 SOUTHWEST | 525840 | ANTELOPE_1 6 | 230 | 21.8013 | 21.7861 | 0.0152
GEN-2018-112 | 05 SOUTHWEST | 525957 | HALE_WNDCL16 | 230 | 10.5196 | 10.5165 | 0.0031
GEN-2018-112 | 05 SOUTHWEST | 526161 | CARLISLE 6 | 230 | 10.473 | 10.4695 | 0.0035
GEN-2018-112 | 05 SOUTHWEST | 526337 | JONES 6 | 230 | 16.6076 | 16.6032 | 0.0044
GEN-2018-112 | 05 SOUTHWEST | 526435 | SUNDOWN 6 | 230 | 11.7438 | 11.7358 | 0.008
GEN-2018-112 | 05 SOUTHWEST | 526935 | YOAKUM 6 | 230 | 19.6825 | 19.6728 | 0.0097
GEN-2018-112 | 05 SOUTHWEST | 527656 | CROSSROADS 7 | 345 | 11.539 | 11.525 | 0.014
GEN-2018-112 | 05 SOUTHWEST | 599955 | PNM-DC6 | 230 | 9.709 | 9.6865 | 0.0225
GEN-2018-112 | 05 SOUTHWEST | 760498 | G17-146-TAP | 230 | 7.745 | 7.7381 | 0.0069
GEN-2018-112 | 05 SOUTHWEST | 763120 | GEN-2018-081 | 230 | 17.3907 | 17.3166 | 0.0741
GEN-2018-112 | 05 SOUTHWEST | 763483 | GEN-2019-003 | 230 | 8.7401 | 8.7222 | 0.0179
GEN-2018-112 | 05 SOUTHWEST | 523097 | HITCHLAND 7 | 345 | 14.9713 | 14.9705 | 0.0008
GEN-2018-112 | 05 SOUTHWEST | 523959 | POTTER_CO 6 | 230 | 22.4376 | 22.4291 | 0.0085
GEN-2018-112 | 05 SOUTHWEST | 524296 | SPNSPUR_WND7 | 345 | 5.3278 | 5.3268 | 0.001
GEN-2018-112 | 05 SOUTHWEST | 524415 | AMA_SOUTH 6 | 230 | 13.6408 | 13.6382 | 0.0026
GEN-2018-112 | 05 SOUTHWEST | 524623 | DEAFSMITH 6 | 230 | 8.0257 | 8.02 | 0.0057
GEN-2018-112 | 05 SOUTHWEST | 524768 | PLSNT_HILL 3 | 115 | 10.5272 | 10.5168 | 0.0104
GEN-2018-112 | 05 SOUTHWEST | 524822 | CURRY 3 | 115 | 11.4402 | 11.4276 | 0.0126
GEN-2018-112 | 05 SOUTHWEST | 524874 | OASIS 3 | 115 | 10.0542 | 10.044 | 0.0102
GEN-2018-112 | 05 SOUTHWEST | 524885 | SN_JUAN_TAP6 | 230 | 4.8705 | 4.8684 | 0.0021
GEN-2018-112 | 05 SOUTHWEST | 524924 | PORTALES 3 | 115 | 7.5524 | 7.5466 | 0.0058
GEN-2018-112 | 05 SOUTHWEST | 525019 | MULSHVLY_TP3 | 115 | 5.9489 | 5.9455 | 0.0034
GEN-2018-112 | 05 SOUTHWEST | 525056 | BC-EARTH 3 | 115 | 8.2606 | 8.2558 | 0.0048
GEN-2018-112 | 05 SOUTHWEST | 525212 | SWISHER 3 | 115 | 11.4972 | 11.4935 | 0.0037
GEN-2018-112 | 05 SOUTHWEST | 525446 | RKYFORD_TP 3 | 115 | 10.1267 | 10.118 | 0.0087
GEN-2018-112 | 05 SOUTHWEST | 525454 | HALE_CNTY 3 | 115 | 10.1608 | 10.1571 | 0.0037
GEN-2018-112 | 05 SOUTHWEST | 525460 | NEWHART 3 | 115 | 14.9423 | 14.9334 | 0.0089
GEN-2018-112 | 05 SOUTHWEST | 525584 | BLUECLDCOL 6 | 230 | 10.4275 | 10.3954 | 0.0321
GEN-2018-112 | 05 SOUTHWEST | 525635 | LAMB_CNTY 2 | 69 | 5.8992 | 5.8967 | 0.0025
GEN-2018-112 | 05 SOUTHWEST | 525780 | FLOYD_CNTY 3 | 115 | 6.2514 | 6.2507 | 0.0007
GEN-2018-112 | 05 SOUTHWEST | 525816 | TUCO_INT2 2 | 69 | 4.6524 | 4.6522 | 0.0002
GEN-2018-112 | 05 SOUTHWEST | 525826 | TUCO_INT 2 | 69 | 7.8538 | 7.8531 | 0.0007
GEN-2018-112 | 05 SOUTHWEST | 525850 | ELK_CT1 | 345 | 13.9398 | 13.934 | 0.0058
GEN-2018-112 | 05 SOUTHWEST | 526020 | HOCKLEY 3 | 115 | 5.426 | 5.4243 | 0.0017
GEN-2018-112 | 05 SOUTHWEST | 526076 | STANTON_W 3 | 115 | 8.923 | 8.9218 | 0.0012
GEN-2018-112 | 05 SOUTHWEST | 526160 | CARLISLE 3 | 115 | 12.772 | 12.7697 | 0.0023
GEN-2018-112 | 05 SOUTHWEST | 526269 | LUBBCK_STH 6 | 230 | 15.0546 | 15.0505 | 0.0041
GEN-2018-112 | 05 SOUTHWEST | 526298 | LUBBCK_EST 3 | 115 | 14.4141 | 14.4119 | 0.0022
GEN-2018-112 | 05 SOUTHWEST | 526299 | LUBBCK_EST 6 | 230 | 11.0462 | 11.0442 | 0.002
GEN-2018-112 | 05 SOUTHWEST | 526434 | SUNDOWN 3 | 115 | 10.8603 | 10.857 | 0.0033
GEN-2018-112 | 05 SOUTHWEST | 526460 | AMOCO_SS 6 | 230 | 10.1771 | 10.1716 | 0.0055
GEN-2018-112 | 05 SOUTHWEST | 526525 | WOLFFORTH 6 | 230 | 13.0516 | 13.046 | 0.0056
GEN-2018-112 | 05 SOUTHWEST | 526677 | GRASSLAND 6 | 230 | 5.9735 | 5.9729 | 0.0006
GEN-2018-112 | 05 SOUTHWEST | 526934 | YOAKUM 3 | 115 | 19.2326 | 19.2286 | 0.004
GEN-2018-112 | 05 SOUTHWEST | 526936 | YOAKUM_345 | 345 | 9.9314 | 9.9274 | 0.004
GEN-2018-112 | 05 SOUTHWEST | 527009 | BRU_SUB 6 | 230 | 15.6513 | 15.6464 | 0.0049
GEN-2018-112 | 05 SOUTHWEST | 527028 | INK_BASIN 6 | 230 | 11.2413 | 11.2389 | 0.0024
GEN-2018-112 | 05 SOUTHWEST | 527149 | MUSTANG 6 | 230 | 17.9238 | 17.9194 | 0.0044
GEN-2018-112 | 05 SOUTHWEST | 527610 | SAGA_SCOL 7 | 345 | 10.2321 | 10.2216 | 0.0105
GEN-2018-112 | 05 SOUTHWEST | 527655 | RSVLT_CC_E 7 | 345 | 10.0154 | 10.0053 | 0.0101
GEN-2018-112 | 05 SOUTHWEST | 527802 | EDDY_CNTY 7 | 345 | 7.3273 | 7.3243 | 0.003
GEN-2018-112 | 05 SOUTHWEST | 527896 | HOBBS_INT 7 | 345 | 12.0143 | 12.0072 | 0.0071
GEN-2018-112 | 05 SOUTHWEST | 560022 | CRAWFISH_DR | 345 | 13.842 | 13.8365 | 0.0055
GEN-2018-112 | 05 SOUTHWEST | 560035 | GRAPEVINE | 345 | 6.4589 | 6.458 | 0.0009
GEN-2018-112 | 05 SOUTHWEST | 760494 | GEN-2017-146 | 230 | 7.4558 | 7.4494 | 0.0064
GEN-2018-112 | 05 SOUTHWEST | 763186 | GEN-2018-089 | 230 | 10.6882 | 10.6792 | 0.009
GEN-2018-112 | 05 SOUTHWEST | 511553 | CHISHOLM7 | 345 | 12.3397 | 12.3389 | 0.0008
GEN-2018-112 | 05 SOUTHWEST | 515458 | BORDER 7 | 345 | 8.2517 | 8.2513 | 0.0004
GEN-2018-112 | 05 SOUTHWEST | 515554 | BVRCNTY7 | 345 | 15.3093 | 15.3088 | 0.0005
GEN-2018-112 | 05 SOUTHWEST | 523095 | HITCHLAND 6 | 230 | 14.5761 | 14.5755 | 0.0006
GEN-2018-112 | 05 SOUTHWEST | 523101 | NOBLE_WND 7 | 345 | 14.9103 | 14.9095 | 0.0008
GEN-2018-112 | 05 SOUTHWEST | 523112 | NOVUS1 7 | 345 | 14.6716 | 14.6708 | 0.0008
GEN-2018-112 | 05 SOUTHWEST | 523323 | MCDWL_CREEK6 | 230 | 8.9802 | 8.9792 | 0.001
GEN-2018-112 | 05 SOUTHWEST | 523823 | CARPENTER 7 | 345 | 6.5781 | 6.578 | 0.0001
GEN-2018-112 | 05 SOUTHWEST | 523869 | CHAN+TASCOS6 | 230 | 4.2464 | 4.2461 | 0.0003
GEN-2018-112 | 05 SOUTHWEST | 523979 | HARRNG_EST 6 | 230 | 26.9856 | 26.9788 | 0.0068
GEN-2018-112 | 05 SOUTHWEST | 524010 | ROLLHILLS 6 | 230 | 20.2306 | 20.2256 | 0.005
GEN-2018-112 | 05 SOUTHWEST | 524044 | NICHOLS 6 | 230 | 26.1237 | 26.1174 | 0.0063
GEN-2018-112 | 05 SOUTHWEST | 524267 | BUSHLAND 6 | 230 | 10.1739 | 10.1708 | 0.0031
GEN-2018-112 | 05 SOUTHWEST | 524299 | SPNSPUR_COL7 | 345 | 5.3278 | 5.3268 | 0.001
GEN-2018-112 | 05 SOUTHWEST | 524365 | RANDALL 6 | 230 | 14.5681 | 14.5654 | 0.0027
GEN-2018-112 | 05 SOUTHWEST | 524414 | AMA_SOUTH 3 | 115 | 16.9088 | 16.9068 | 0.002
GEN-2018-112 | 05 SOUTHWEST | 524502 | NORTON 3 | 115 | 2.9186 | 2.9184 | 0.0002
GEN-2018-112 | 05 SOUTHWEST | 524619 | DFSMTH_EST 3 | 115 | 11.9939 | 11.9877 | 0.0062
GEN-2018-112 | 05 SOUTHWEST | 524622 | DFSMTH_WST 3 | 115 | 11.9945 | 11.9883 | 0.0062
GEN-2018-112 | 05 SOUTHWEST | 524669 | DS-#20 3 | 115 | 6.2762 | 6.273 | 0.0032
GEN-2018-112 | 05 SOUTHWEST | 524746 | CASTRO_CNTY3 | 115 | 9.822 | 9.818 | 0.004
GEN-2018-112 | 05 SOUTHWEST | 524764 | NORRIS_TP 3 | 115 | 11.4074 | 11.3949 | 0.0125
GEN-2018-112 | 05 SOUTHWEST | 524773 | E_CLOVIS 3 | 115 | 8.962 | 8.9543 | 0.0077
GEN-2018-112 | 05 SOUTHWEST | 524776 | N_CLOVIS_TP3 | 115 | 7.4744 | 7.4693 | 0.0051
GEN-2018-112 | 05 SOUTHWEST | 524797 | PERIMETER 3 | 115 | 6.5512 | 6.547 | 0.0042
GEN-2018-112 | 05 SOUTHWEST | 524821 | CURRY 2 | 69 | 4.4284 | 4.4272 | 0.0012
GEN-2018-112 | 05 SOUTHWEST | 524831 | FE-HOLLAND 3 | 115 | 9.2431 | 9.235 | 0.0081
GEN-2018-112 | 05 SOUTHWEST | 524838 | FE-CLOVIS2+3 | 115 | 10.7942 | 10.783 | 0.0112
GEN-2018-112 | 05 SOUTHWEST | 524863 | FE-CHZPLT 3 | 115 | 8.0228 | 8.0165 | 0.0063
GEN-2018-112 | 05 SOUTHWEST | 524889 | SN_JUAN_WND6 | 230 | 4.6556 | 4.6537 | 0.0019
GEN-2018-112 | 05 SOUTHWEST | 524923 | PORTALES 2 | 69 | 7.5604 | 7.5569 | 0.0035
GEN-2018-112 | 05 SOUTHWEST | 524935 | KILGORE 3 | 115 | 6.1488 | 6.1449 | 0.0039
GEN-2018-112 | 05 SOUTHWEST | 524977 | GREYHOUND 3 | 115 | 5.6862 | 5.6829 | 0.0033
GEN-2018-112 | 05 SOUTHWEST | 525018 | MULESHVALLY3 | 115 | 5.5409 | 5.538 | 0.0029
GEN-2018-112 | 05 SOUTHWEST | 525028 | BAILEYCO 3 | 115 | 5.8021 | 5.7989 | 0.0032
GEN-2018-112 | 05 SOUTHWEST | 525050 | BC-KELLEY +3 | 115 | 7.782 | 7.7782 | 0.0038
GEN-2018-112 | 05 SOUTHWEST | 525124 | HART_INDUST3 | 115 | 7.4925 | 7.49 | 0.0025
GEN-2018-112 | 05 SOUTHWEST | 525192 | KRESS_INT 3 | 115 | 11.9205 | 11.9164 | 0.0041
GEN-2018-112 | 05 SOUTHWEST | 525326 | COX 3 | 115 | 6.2736 | 6.2725 | 0.0011
GEN-2018-112 | 05 SOUTHWEST | 525393 | ROCKYFORD 3 | 115 | 9.0431 | 9.0361 | 0.007
GEN-2018-112 | 05 SOUTHWEST | 525414 | LAMTON 3 | 115 | 7.6144 | 7.6113 | 0.0031
GEN-2018-112 | 05 SOUTHWEST | 525440 | LC-S_OLTON+3 | 115 | 7.1982 | 7.1948 | 0.0034
GEN-2018-112 | 05 SOUTHWEST | 525453 | HALE_CNTY 2 | 69 | 6.9062 | 6.9052 | 0.001
GEN-2018-112 | 05 SOUTHWEST | 525613 | W_LITTLFLD 2 | 69 | 2.9684 | 2.9678 | 0.0006
GEN-2018-112 | 05 SOUTHWEST | 525620 | LTFLD_S&CTY2 | 69 | 4.1727 | 4.1714 | 0.0013
GEN-2018-112 | 05 SOUTHWEST | 525650 | LC-LTTLFLD+2 | 69 | 4.9319 | 4.9302 | 0.0017
GEN-2018-112 | 05 SOUTHWEST | 525687 | LC-LUMSCHAP2 | 69 | 4.6126 | 4.611 | 0.0016
GEN-2018-112 | 05 SOUTHWEST | 525731 | SP-ABERNTHY2 | 69 | 3.0093 | 3.0092 | 0.0001
GEN-2018-112 | 05 SOUTHWEST | 525738 | HALECENTER 2 | 69 | 2.4566 | 2.4565 | 0.0001
GEN-2018-112 | 05 SOUTHWEST | 525763 | CALLAHAN 3 | 115 | 5.5668 | 5.5661 | 0.0007
GEN-2018-112 | 05 SOUTHWEST | 525779 | FLOYD_CNTY 2 | 69 | 5.401 | 5.4007 | 0.0003
GEN-2018-112 | 05 SOUTHWEST | 525803 | BLANCO 3 | 115 | 5.0451 | 5.0448 | 0.0003
GEN-2018-112 | 05 SOUTHWEST | 525853 | LH-WIL&ELN+2 | 69 | 2.5404 | 2.5404 | 0
GEN-2018-112 | 05 SOUTHWEST | 525885 | SP-NEWDEAL 2 | 69 | 3.3073 | 3.3072 | 0.0001
GEN-2018-112 | 05 SOUTHWEST | 525926 | CROSBY 3 | 115 | 4.7129 | 4.7127 | 0.0002
GEN-2018-112 | 05 SOUTHWEST | 526019 | HOCKLEY 2 | 69 | 5.1105 | 5.1096 | 0.0009
GEN-2018-112 | 05 SOUTHWEST | 526036 | LC-OPDYKE 3 | 115 | 5.7143 | 5.7126 | 0.0017
GEN-2018-112 | 05 SOUTHWEST | 526109 | SP-ERSKINE 3 | 115 | 10.9787 | 10.9769 | 0.0018
GEN-2018-112 | 05 SOUTHWEST | 526146 | INDIANA 3 | 115 | 9.3032 | 9.3019 | 0.0013
GEN-2018-112 | 05 SOUTHWEST | 526159 | CARLISLE 2 | 69 | 2.5568 | 2.5568 | 0
GEN-2018-112 | 05 SOUTHWEST | 526162 | LP-DOUD_TP 3 | 115 | 11.325 | 11.3231 | 0.0019
GEN-2018-112 | 05 SOUTHWEST | 526192 | MURPHY 3 | 115 | 10.2503 | 10.2489 | 0.0014
GEN-2018-112 | 05 SOUTHWEST | 526268 | LUBBCK_STH 3 | 115 | 17.6482 | 17.645 | 0.0032
GEN-2018-112 | 05 SOUTHWEST | 526297 | LUBBCK_EST 2 | 69 | 7.8955 | 7.8951 | 0.0004
GEN-2018-112 | 05 SOUTHWEST | 526424 | PACIFIC 3 | 115 | 9.1771 | 9.1748 | 0.0023
GEN-2018-112 | 05 SOUTHWEST | 526445 | AMOCO_TP 3 | 115 | 10.1845 | 10.1816 | 0.0029
GEN-2018-112 | 05 SOUTHWEST | 526524 | WOLFFORTH 3 | 115 | 11.2819 | 11.28 | 0.0019
GEN-2018-112 | 05 SOUTHWEST | 526676 | GRASSLAND 3 | 115 | 6.8633 | 6.8629 | 0.0004
GEN-2018-112 | 05 SOUTHWEST | 526679 | CIRRUS_WND 6 | 230 | 4.6792 | 4.6789 | 0.0003
GEN-2018-112 | 05 SOUTHWEST | 526784 | AMOCOWASSON6 | 230 | 15.6353 | 15.6315 | 0.0038
GEN-2018-112 | 05 SOUTHWEST | 526792 | PRENTICE 3 | 115 | 6.0286 | 6.0282 | 0.0004
GEN-2018-112 | 05 SOUTHWEST | 526928 | PLAINS_INT 3 | 115 | 10.0196 | 10.0184 | 0.0012
GEN-2018-112 | 05 SOUTHWEST | 527010 | OXYBRU 6 | 230 | 15.5052 | 15.5003 | 0.0049
GEN-2018-112 | 05 SOUTHWEST | 527011 | XTO_MAHONEY6 | 230 | 15.3578 | 15.3533 | 0.0045
GEN-2018-112 | 05 SOUTHWEST | 527027 | INK_BASIN 3 | 115 | 13.258 | 13.2568 | 0.0012
GEN-2018-112 | 05 SOUTHWEST | 527041 | ARCO_TP 3 | 115 | 13.6807 | 13.6793 | 0.0014
GEN-2018-112 | 05 SOUTHWEST | 527146 | MUSTANG 3 | 115 | 24.0628 | 24.0596 | 0.0032
GEN-2018-112 | 05 SOUTHWEST | 527151 | GS-MUSTANG 6 | 230 | 17.9238 | 17.9194 | 0.0044
GEN-2018-112 | 05 SOUTHWEST | 527194 | LG-PLSHILL 3 | 115 | 7.9741 | 7.9736 | 0.0005
GEN-2018-112 | 05 SOUTHWEST | 527276 | SEMINOLE 6 | 230 | 8.197 | 8.1962 | 0.0008
GEN-2018-112 | 05 SOUTHWEST | 527483 | CHAVES_CNTY6 | 230 | 4.4929 | 4.4919 | 0.001
GEN-2018-112 | 05 SOUTHWEST | 527599 | SAGA_SDCOL 7 | 345 | 10.2321 | 10.2216 | 0.0105
GEN-2018-112 | 05 SOUTHWEST | 527654 | RSVLT_CC_W 7 | 345 | 8.7265 | 8.719 | 0.0075
GEN-2018-112 | 05 SOUTHWEST | 527799 | EDDY_NORTH 6 | 230 | 9.402 | 9.3991 | 0.0029
GEN-2018-112 | 05 SOUTHWEST | 527894 | HOBBS_INT 6 | 230 | 19.4767 | 19.4712 | 0.0055
GEN-2018-112 | 05 SOUTHWEST | 527965 | KIOWA 7 | 345 | 8.82 | 8.8162 | 0.0038
GEN-2018-112 | 05 SOUTHWEST | 528027 | RDRUNNER 7 | 345 | 8.6815 | 8.678 | 0.0035
GEN-2018-112 | 05 SOUTHWEST | 576397 | G10014G11022 | 345 | 10.3812 | 10.3809 | 0.0003
GEN-2018-112 | 05 SOUTHWEST | 762216 | G17-151TAP | 345 | 8.5119 | 8.5104 | 0.0015
GEN-2018-112 | 05 SOUTHWEST | 763087 | GEN-2018-073 | 345 | 11.9423 | 11.9382 | 0.0041
GEN-2018-112 | 05 SOUTHWEST | 763516 | GEN-2019-011 | 345 | 9.2852 | 9.2817 | 0.0035
GEN-2018-112 | 05 SOUTHWEST | 511557 | CHISHOLM6 | 230 | 12.1566 | 12.1562 | 0.0004
GEN-2018-112 | 05 SOUTHWEST | 515375 | WWRDEHV7 | 345 | 22.3641 | 22.3637 | 0.0004
GEN-2018-112 | 05 SOUTHWEST | 515590 | PALDR2W7 | 345 | 12.8669 | 12.8666 | 0.0003
GEN-2018-112 | 05 SOUTHWEST | 515618 | BALKOW 7 | 345 | 12.5807 | 12.5804 | 0.0003
GEN-2018-112 | 05 SOUTHWEST | 515677 | BADGER 7 | 345 | 13.7821 | 13.7818 | 0.0003
GEN-2018-112 | 05 SOUTHWEST | 523093 | HITCHLAND 3 | 115 | 17.3358 | 17.3354 | 0.0004
GEN-2018-112 | 05 SOUTHWEST | 523103 | NOBLE_WND 3 | 115 | 10.6199 | 10.6198 | 0.0001
GEN-2018-112 | 05 SOUTHWEST | 523111 | NOVUS1 3 | 115 | 7.8432 | 7.8431 | 0.0001
GEN-2018-112 | 05 SOUTHWEST | 523155 | OCHILTREE 6 | 230 | 4.265 | 4.2649 | 0.0001
GEN-2018-112 | 05 SOUTHWEST | 523215 | GEN-2011-022 | 345 | 10.3812 | 10.3809 | 0.0003
GEN-2018-112 | 05 SOUTHWEST | 523221 | XIT_INTG 6 | 230 | 3.1441 | 3.1439 | 0.0002
GEN-2018-112 | 05 SOUTHWEST | 523267 | PRINGLE 6 | 230 | 4.3435 | 4.3434 | 0.0001
GEN-2018-112 | 05 SOUTHWEST | 523309 | MOORE_CNTY 6 | 230 | 6.6813 | 6.6809 | 0.0004
GEN-2018-112 | 05 SOUTHWEST | 523322 | MCDWL_CREEK3 | 115 | 9.8376 | 9.8371 | 0.0005
GEN-2018-112 | 05 SOUTHWEST | 523551 | HUTCHISON 6 | 230 | 7.288 | 7.2876 | 0.0004
GEN-2018-112 | 05 SOUTHWEST | 523771 | GRAPEVINE 6 | 230 | 5.9762 | 5.9761 | 0.0001
GEN-2018-112 | 05 SOUTHWEST | 523853 | FINNEY 7 | 345 | 9.8362 | 9.8361 | 0.0001
GEN-2018-112 | 05 SOUTHWEST | 523977 | HARRNG_WST 6 | 230 | 26.9856 | 26.9788 | 0.0068
GEN-2018-112 | 05 SOUTHWEST | 523978 | HARRNG_MID 6 | 230 | 26.9856 | 26.9788 | 0.0068
GEN-2018-112 | 05 SOUTHWEST | 524007 | ROLLHILLS 3 | 115 | 19.6592 | 19.6572 | 0.002
GEN-2018-112 | 05 SOUTHWEST | 524043 | NICHOLS 3 | 115 | 30.649 | 30.6455 | 0.0035
GEN-2018-112 | 05 SOUTHWEST | 524266 | BUSHLAND 3 | 115 | 10.3324 | 10.3312 | 0.0012
GEN-2018-112 | 05 SOUTHWEST | 524290 | WILDOR2_JUS6 | 230 | 6.9783 | 6.9769 | 0.0014
GEN-2018-112 | 05 SOUTHWEST | 524364 | RANDALL 3 | 115 | 21.0733 | 21.0699 | 0.0034
GEN-2018-112 | 05 SOUTHWEST | 524377 | FARMERS 3 | 115 | 15.4368 | 15.4351 | 0.0017
GEN-2018-112 | 05 SOUTHWEST | 524397 | ARROWHEAD 3 | 115 | 13.6793 | 13.6781 | 0.0012
GEN-2018-112 | 05 SOUTHWEST | 524404 | OWENSCORN 3 | 115 | 15.0594 | 15.0578 | 0.0016
GEN-2018-112 | 05 SOUTHWEST | 524486 | CAPROCK 3 | 115 | 2.636 | 2.6359 | 0.0001
GEN-2018-112 | 05 SOUTHWEST | 524509 | FE-TUCMCARI3 | 115 | 2.391 | 2.3909 | 0.0001
GEN-2018-112 | 05 SOUTHWEST | 524544 | SPRING_DRW 3 | 115 | 6.4069 | 6.4066 | 0.0003
GEN-2018-112 | 05 SOUTHWEST | 524630 | TIERABLANCA3 | 115 | 12.3344 | 12.3278 | 0.0066
GEN-2018-112 | 05 SOUTHWEST | 524662 | PARMER_CO 3 | 115 | 5.4666 | 5.4645 | 0.0021
GEN-2018-112 | 05 SOUTHWEST | 524694 | DS-#22 3 | 115 | 4.5966 | 4.5957 | 0.0009
GEN-2018-112 | 05 SOUTHWEST | 524734 | DS-#21 3 | 115 | 9.3056 | 9.3019 | 0.0037
GEN-2018-112 | 05 SOUTHWEST | 524745 | CASTRO_CNTY2 | 69 | 8.7963 | 8.7944 | 0.0019
GEN-2018-112 | 05 SOUTHWEST | 524757 | BETHEL_COL13 | 115 | 8.2391 | 8.2365 | 0.0026
GEN-2018-112 | 05 SOUTHWEST | 524777 | N_CLOVIS 3 | 115 | 6.7428 | 6.7386 | 0.0042
GEN-2018-112 | 05 SOUTHWEST | 524783 | W_CLOVIS 2 | 69 | 2.4403 | 2.44 | 0.0003
GEN-2018-112 | 05 SOUTHWEST | 524790 | CANNON_TP 3 | 115 | 6.0058 | 6.0024 | 0.0034
GEN-2018-112 | 05 SOUTHWEST | 524801 | NORRIS 3 | 115 | 10.4115 | 10.4011 | 0.0104
GEN-2018-112 | 05 SOUTHWEST | 524808 | FE-CLVS_INT3 | 115 | 6.9498 | 6.9453 | 0.0045
GEN-2018-112 | 05 SOUTHWEST | 524846 | FARWELL 2 | 69 | 2.1357 | 2.1355 | 0.0002
GEN-2018-112 | 05 SOUTHWEST | 524929 | RO-PORT_MTR2 | 69 | 7.5604 | 7.5569 | 0.0035
GEN-2018-112 | 05 SOUTHWEST | 524934 | ZODIAC 2 | 69 | 5.5439 | 5.542 | 0.0019
GEN-2018-112 | 05 SOUTHWEST | 524941 | PORTALES#1 2 | 69 | 5.7509 | 5.7489 | 0.002
GEN-2018-112 | 05 SOUTHWEST | 524963 | S_PORTALES 3 | 115 | 5.7708 | 5.7673 | 0.0035
GEN-2018-112 | 05 SOUTHWEST | 525027 | BAILEYCO 2 | 69 | 5.2707 | 5.2691 | 0.0016
GEN-2018-112 | 05 SOUTHWEST | 525179 | TULIA_TP 3 | 115 | 6.4624 | 6.4614 | 0.001
GEN-2018-112 | 05 SOUTHWEST | 525191 | KRESS_INT 2 | 69 | 4.4978 | 4.4974 | 0.0004
GEN-2018-112 | 05 SOUTHWEST | 525226 | KRS_RURL_TP3 | 115 | 6.4399 | 6.4388 | 0.0011
GEN-2018-112 | 05 SOUTHWEST | 525272 | KISER 3 | 115 | 5.2683 | 5.2675 | 0.0008
GEN-2018-112 | 05 SOUTHWEST | 525291 | PLAINVW_TP 2 | 69 | 6.4824 | 6.4814 | 0.001
GEN-2018-112 | 05 SOUTHWEST | 525298 | S_PLAINVEW 2 | 69 | 2.5852 | 2.5851 | 0.0001
GEN-2018-112 | 05 SOUTHWEST | 525325 | COX 2 | 69 | 3.4185 | 3.4183 | 0.0002
GEN-2018-112 | 05 SOUTHWEST | 525351 | LH-AIKEN 2 | 69 | 2.1484 | 2.1484 | 0
GEN-2018-112 | 05 SOUTHWEST | 525413 | LAMTON 2 | 69 | 5.1693 | 5.1685 | 0.0008
GEN-2018-112 | 05 SOUTHWEST | 525432 | SP-HALFWAY+2 | 69 | 5.8641 | 5.8633 | 0.0008
GEN-2018-112 | 05 SOUTHWEST | 525606 | AMHERST 2 | 69 | 2.3408 | 2.3404 | 0.0004
GEN-2018-112 | 05 SOUTHWEST | 525657 | W_ANTON_TP 2 | 69 | 4.1079 | 4.1067 | 0.0012
GEN-2018-112 | 05 SOUTHWEST | 525694 | HOBGOOD 2 | 69 | 3.4381 | 3.4373 | 0.0008
GEN-2018-112 | 05 SOUTHWEST | 525723 | CNTYLINE_TP2 | 69 | 2.2014 | 2.2014 | 0
GEN-2018-112 | 05 SOUTHWEST | 525745 | LH-HALECTR 2 | 69 | 2.4289 | 2.4289 | 0
GEN-2018-112 | 05 SOUTHWEST | 525790 | FLOYDADA_TP2 | 69 | 2.5171 | 2.517 | 0.0001
GEN-2018-112 | 05 SOUTHWEST | 525801 | LRNZ_MPT 3 | 115 | 5.0442 | 5.0438 | 0.0004
GEN-2018-112 | 05 SOUTHWEST | 525811 | LH-HARMONY 2 | 69 | 4.3124 | 4.3122 | 0.0002
GEN-2018-112 | 05 SOUTHWEST | 525860 | SP-BECTON +2 | 69 | 2.2545 | 2.2545 | 0
GEN-2018-112 | 05 SOUTHWEST | 525892 | MONROE 2 | 69 | 2.6475 | 2.6475 | 0
GEN-2018-112 | 05 SOUTHWEST | 525925 | CROSBY 2 | 69 | 4.7847 | 4.7845 | 0.0002
GEN-2018-112 | 05 SOUTHWEST | 526009 | LC-LEVLND#22 | 69 | 4.2645 | 4.2638 | 0.0007
GEN-2018-112 | 05 SOUTHWEST | 526042 | COBLE 2 | 69 | 2.2615 | 2.2613 | 0.0002
GEN-2018-112 | 05 SOUTHWEST | 526048 | LVLNDCTY_TP2 | 69 | 4.2645 | 4.2638 | 0.0007
GEN-2018-112 | 05 SOUTHWEST | 526130 | SP-CARLISLE2 | 69 | 2.1026 | 2.1025 | 0.0001
GEN-2018-112 | 05 SOUTHWEST | 526176 | LP-DOUD 3 | 115 | 8.8577 | 8.8566 | 0.0011
GEN-2018-112 | 05 SOUTHWEST | 526184 | SW_6878 2 | 69 | 2.1534 | 2.1534 | 0
GEN-2018-112 | 05 SOUTHWEST | 526195 | QUINCY 3 | 115 | 9.6342 | 9.633 | 0.0012
GEN-2018-112 | 05 SOUTHWEST | 526213 | ALLEN 3 | 115 | 10.4502 | 10.449 | 0.0012
GEN-2018-112 | 05 SOUTHWEST | 526267 | LUBBCK_STH 2 | 69 | 4.3104 | 4.3103 | 0.0001
GEN-2018-112 | 05 SOUTHWEST | 526284 | PLANTERS 2 | 69 | 5.7109 | 5.7107 | 0.0002
GEN-2018-112 | 05 SOUTHWEST | 526310 | CLUTTER 2 | 69 | 5.3812 | 5.381 | 0.0002
GEN-2018-112 | 05 SOUTHWEST | 526361 | COCHRAN 3 | 115 | 6.4257 | 6.4247 | 0.001
GEN-2018-112 | 05 SOUTHWEST | 526452 | AMOCO_CRYO 3 | 115 | 6.362 | 6.3609 | 0.0011
GEN-2018-112 | 05 SOUTHWEST | 526475 | YUMA_INT 3 | 115 | 10.7034 | 10.7017 | 0.0017
GEN-2018-112 | 05 SOUTHWEST | 526481 | SP-WOLF_TP 3 | 115 | 10.8642 | 10.8625 | 0.0017
GEN-2018-112 | 05 SOUTHWEST | 526484 | LG-LEVELAND3 | 115 | 9.1775 | 9.1753 | 0.0022
GEN-2018-112 | 05 SOUTHWEST | 526562 | SLATON 2 | 69 | 2.4663 | 2.4663 | 0
GEN-2018-112 | 05 SOUTHWEST | 526602 | WOODROW 3 | 115 | 9.1323 | 9.1315 | 0.0008
GEN-2018-112 | 05 SOUTHWEST | 526656 | LYNN_CNTY 3 | 115 | 5.9373 | 5.937 | 0.0003
GEN-2018-112 | 05 SOUTHWEST | 526694 | GRAHAM 3 | 115 | 2.8169 | 2.8168 | 0.0001
GEN-2018-112 | 05 SOUTHWEST | 526736 | TERRY_CNTY 3 | 115 | 10.6679 | 10.6664 | 0.0015
GEN-2018-112 | 05 SOUTHWEST | 526944 | LG-PLAINS 3 | 115 | 7.9013 | 7.9006 | 0.0007
GEN-2018-112 | 05 SOUTHWEST | 527018 | BENNETT 3 | 115 | 13.7758 | 13.7744 | 0.0014
GEN-2018-112 | 05 SOUTHWEST | 527030 | ALRDCRTZ_TP3 | 115 | 12.2915 | 12.2905 | 0.001
GEN-2018-112 | 05 SOUTHWEST | 527047 | OXY_WILRD1 3 | 115 | 10.8936 | 10.8927 | 0.0009
GEN-2018-112 | 05 SOUTHWEST | 527062 | SHELL_CO2 3 | 115 | 16.7017 | 16.6998 | 0.0019
GEN-2018-112 | 05 SOUTHWEST | 527130 | DENVER_N 3 | 115 | 22.5277 | 22.5246 | 0.0031
GEN-2018-112 | 05 SOUTHWEST | 527136 | DENVER_S 3 | 115 | 22.5277 | 22.5246 | 0.0031
GEN-2018-112 | 05 SOUTHWEST | 527202 | SEAGRAVES 3 | 115 | 9.1786 | 9.178 | 0.0006
GEN-2018-112 | 05 SOUTHWEST | 527275 | SEMINOLE 3 | 115 | 14.6609 | 14.6596 | 0.0013
GEN-2018-112 | 05 SOUTHWEST | 527482 | CHAVES_CNTY3 | 115 | 7.0492 | 7.048 | 0.0012
GEN-2018-112 | 05 SOUTHWEST | 527600 | SAGA_SMEAS 7 | 345 | 10.2321 | 10.2216 | 0.0105
GEN-2018-112 | 05 SOUTHWEST | 527666 | RSVLT_COL1 7 | 345 | 8.7265 | 8.719 | 0.0075
GEN-2018-112 | 05 SOUTHWEST | 527667 | RSVLT_COL2 7 | 345 | 8.7265 | 8.719 | 0.0075
GEN-2018-112 | 05 SOUTHWEST | 527793 | EDDY_STH 3 | 115 | 11.9559 | 11.9536 | 0.0023
GEN-2018-112 | 05 SOUTHWEST | 527798 | EDDY_NTH 3 | 115 | 11.9559 | 11.9536 | 0.0023
GEN-2018-112 | 05 SOUTHWEST | 527865 | CUNNIGHM_N 6 | 230 | 17.5364 | 17.5323 | 0.0041
GEN-2018-112 | 05 SOUTHWEST | 527867 | CUNNIGHM_S 6 | 230 | 17.5364 | 17.5323 | 0.0041
GEN-2018-112 | 05 SOUTHWEST | 527891 | HOBBS_INT 3 | 115 | 33.0667 | 33.0627 | 0.004
GEN-2018-112 | 05 SOUTHWEST | 527966 | KIOWA 3 | 115 | 17.1508 | 17.1469 | 0.0039
GEN-2018-112 | 05 SOUTHWEST | 528015 | PHANTOM 7 | 345 | 5.675 | 5.6735 | 0.0015
GEN-2018-112 | 05 SOUTHWEST | 528025 | RDRUNNER 3 | 115 | 13.7957 | 13.7931 | 0.0026
GEN-2018-112 | 05 SOUTHWEST | 528095 | 7-RIVERS 6 | 230 | 6.3874 | 6.3862 | 0.0012
GEN-2018-112 | 05 SOUTHWEST | 528185 | N_LOVING 7 | 345 | 6.5496 | 6.5476 | 0.002
GEN-2018-112 | 05 SOUTHWEST | 528325 | LE-WAITS 3 | 115 | 8.9967 | 8.9963 | 0.0004
GEN-2018-112 | 05 SOUTHWEST | 528604 | ANDREWS 6 | 230 | 6.0764 | 6.0759 | 0.0005
GEN-2018-112 | 05 SOUTHWEST | 528626 | LE-PLNSINT 2 | 69 | 3.6375 | 3.6374 | 0.0001
GEN-2018-112 | 05 SOUTHWEST | 531512 | HARBNGR7 | 345 | 6.5579 | 6.5579 | 0
GEN-2018-112 | 05 SOUTHWEST | 560078 | G16-037-TAP | 345 | 10.1427 | 10.1425 | 0.0002
GEN-2018-112 | 05 SOUTHWEST | 560577 | G06-44 | 115 | 7.5797 | 7.5797 | 0
GEN-2018-112 | 05 SOUTHWEST | 576395 | GEN-2010-014 | 345 | 10.3812 | 10.3809 | 0.0003
GEN-2018-112 | 05 SOUTHWEST | 588460 | A16-008SUB | 115 | 13.258 | 13.2568 | 0.0012
GEN-2018-112 | 05 SOUTHWEST | 599960 | EPTNP-D6 | 230 | 9.402 | 9.3991 | 0.0029
GEN-2018-112 | 05 SOUTHWEST | 755000 | WWDBORDT | 345 | 12.2648 | 12.264 | 0.0008
GEN-2018-112 | 05 SOUTHWEST | 761355 | GEN-2017-239 | 230 | 13.7988 | 13.7953 | 0.0035
GEN-2018-112 | 05 SOUTHWEST | 762217 | GEN-2017-151 | 345 | 6.1754 | 6.1746 | 0.0008
GEN-2018-112 | 05 SOUTHWEST | 762467 | G18-015-TAP | 345 | 5.8242 | 5.824 | 0.0002
GEN-2018-124 | 05 SOUTHWEST | 525531 | TOLK 6 | 230 | 31.4946 | 31.1345 | 0.3601
GEN-2018-124 | 05 SOUTHWEST | 524909 | ROOSEVELT 6 | 230 | 9.709 | 9.6883 | 0.0207
GEN-2018-124 | 05 SOUTHWEST | 525481 | PLANT_X 6 | 230 | 24.1838 | 24.0496 | 0.1342
GEN-2018-124 | 05 SOUTHWEST | 525549 | TOLK 7 | 345 | 15.0276 | 14.9444 | 0.0832
GEN-2018-124 | 05 SOUTHWEST | 525586 | NEEDMORE 6 | 230 | 11.0214 | 10.9882 | 0.0332
GEN-2018-124 | 05 SOUTHWEST | 525637 | LAMB_CNTY 6 | 230 | 5.4027 | 5.3942 | 0.0085
GEN-2018-124 | 05 SOUTHWEST | 525830 | TUCO_INT 6 | 230 | 21.9895 | 21.9753 | 0.0142
GEN-2018-124 | 05 SOUTHWEST | 762132 | GEN-2017-158 | 230 | 13.8646 | 13.8032 | 0.0614
GEN-2018-124 | 05 SOUTHWEST | 763241 | GEN-2018-097 | 230 | 24.4484 | 24.0824 | 0.366
GEN-2018-124 | 05 SOUTHWEST | 523961 | POTTER_CO 7 | 345 | 11.6631 | 11.6579 | 0.0052
GEN-2018-124 | 05 SOUTHWEST | 524770 | PLSNT_HILL 6 | 230 | 6.517 | 6.5086 | 0.0084
GEN-2018-124 | 05 SOUTHWEST | 524875 | OASIS 6 | 230 | 7.8784 | 7.8665 | 0.0119
GEN-2018-124 | 05 SOUTHWEST | 524908 | ROOSEVELT 3 | 115 | 11.1454 | 11.1333 | 0.0121
GEN-2018-124 | 05 SOUTHWEST | 525213 | SWISHER 6 | 230 | 10.3853 | 10.3802 | 0.0051
GEN-2018-124 | 05 SOUTHWEST | 525461 | NEWHART 6 | 230 | 10.9971 | 10.9883 | 0.0088
GEN-2018-124 | 05 SOUTHWEST | 525480 | PLANT_X 3 | 115 | 19.2796 | 19.2465 | 0.0331
GEN-2018-124 | 05 SOUTHWEST | 525585 | BLUECLDPOI 6 | 230 | 11.0214 | 10.9882 | 0.0332
GEN-2018-124 | 05 SOUTHWEST | 525636 | LAMB_CNTY 3 | 115 | 8.4389 | 8.4312 | 0.0077
GEN-2018-124 | 05 SOUTHWEST | 525828 | TUCO_INT 3 | 115 | 19.3618 | 19.356 | 0.0058
GEN-2018-124 | 05 SOUTHWEST | 525832 | TUCO_INT 7 | 345 | 14.0745 | 14.0691 | 0.0054
GEN-2018-124 | 05 SOUTHWEST | 525840 | ANTELOPE_1 6 | 230 | 21.8013 | 21.7873 | 0.014
GEN-2018-124 | 05 SOUTHWEST | 525957 | HALE_WNDCL16 | 230 | 10.5196 | 10.5167 | 0.0029
GEN-2018-124 | 05 SOUTHWEST | 526161 | CARLISLE 6 | 230 | 10.473 | 10.4698 | 0.0032
GEN-2018-124 | 05 SOUTHWEST | 526337 | JONES 6 | 230 | 16.6076 | 16.6036 | 0.004
GEN-2018-124 | 05 SOUTHWEST | 526435 | SUNDOWN 6 | 230 | 11.7438 | 11.7364 | 0.0074
GEN-2018-124 | 05 SOUTHWEST | 526935 | YOAKUM 6 | 230 | 19.6825 | 19.6735 | 0.009
GEN-2018-124 | 05 SOUTHWEST | 527656 | CROSSROADS 7 | 345 | 11.539 | 11.526 | 0.013
GEN-2018-124 | 05 SOUTHWEST | 599955 | PNM-DC6 | 230 | 9.709 | 9.6883 | 0.0207
GEN-2018-124 | 05 SOUTHWEST | 760498 | G17-146-TAP | 230 | 7.745 | 7.7387 | 0.0063
GEN-2018-124 | 05 SOUTHWEST | 763120 | GEN-2018-081 | 230 | 17.3907 | 17.3224 | 0.0683
GEN-2018-124 | 05 SOUTHWEST | 763483 | GEN-2019-003 | 230 | 8.7401 | 8.7236 | 0.0165
GEN-2018-124 | 05 SOUTHWEST | 523097 | HITCHLAND 7 | 345 | 14.9713 | 14.9706 | 0.0007
GEN-2018-124 | 05 SOUTHWEST | 523959 | POTTER_CO 6 | 230 | 22.4376 | 22.4297 | 0.0079
GEN-2018-124 | 05 SOUTHWEST | 524296 | SPNSPUR_WND7 | 345 | 5.3278 | 5.3269 | 0.0009
GEN-2018-124 | 05 SOUTHWEST | 524415 | AMA_SOUTH 6 | 230 | 13.6408 | 13.6384 | 0.0024
GEN-2018-124 | 05 SOUTHWEST | 524623 | DEAFSMITH 6 | 230 | 8.0257 | 8.0205 | 0.0052
GEN-2018-124 | 05 SOUTHWEST | 524768 | PLSNT_HILL 3 | 115 | 10.5272 | 10.5176 | 0.0096
GEN-2018-124 | 05 SOUTHWEST | 524822 | CURRY 3 | 115 | 11.4402 | 11.4285 | 0.0117
GEN-2018-124 | 05 SOUTHWEST | 524874 | OASIS 3 | 115 | 10.0542 | 10.0448 | 0.0094
GEN-2018-124 | 05 SOUTHWEST | 524885 | SN_JUAN_TAP6 | 230 | 4.8705 | 4.8685 | 0.002
GEN-2018-124 | 05 SOUTHWEST | 524924 | PORTALES 3 | 115 | 7.5524 | 7.547 | 0.0054
GEN-2018-124 | 05 SOUTHWEST | 525019 | MULSHVLY_TP3 | 115 | 5.9489 | 5.9458 | 0.0031
GEN-2018-124 | 05 SOUTHWEST | 525056 | BC-EARTH 3 | 115 | 8.2606 | 8.2562 | 0.0044
GEN-2018-124 | 05 SOUTHWEST | 525212 | SWISHER 3 | 115 | 11.4972 | 11.4938 | 0.0034
GEN-2018-124 | 05 SOUTHWEST | 525446 | RKYFORD_TP 3 | 115 | 10.1267 | 10.1186 | 0.0081
GEN-2018-124 | 05 SOUTHWEST | 525454 | HALE_CNTY 3 | 115 | 10.1608 | 10.1574 | 0.0034
GEN-2018-124 | 05 SOUTHWEST | 525460 | NEWHART 3 | 115 | 14.9423 | 14.9341 | 0.0082
GEN-2018-124 | 05 SOUTHWEST | 525584 | BLUECLDCOL 6 | 230 | 10.4275 | 10.3979 | 0.0296
GEN-2018-124 | 05 SOUTHWEST | 525635 | LAMB_CNTY 2 | 69 | 5.8992 | 5.8969 | 0.0023
GEN-2018-124 | 05 SOUTHWEST | 525780 | FLOYD_CNTY 3 | 115 | 6.2514 | 6.2507 | 0.0007
GEN-2018-124 | 05 SOUTHWEST | 525816 | TUCO_INT2 2 | 69 | 4.6524 | 4.6522 | 0.0002
GEN-2018-124 | 05 SOUTHWEST | 525826 | TUCO_INT 2 | 69 | 7.8538 | 7.8532 | 0.0006
GEN-2018-124 | 05 SOUTHWEST | 525850 | ELK_CT1 | 345 | 13.9398 | 13.9345 | 0.0053
GEN-2018-124 | 05 SOUTHWEST | 526020 | HOCKLEY 3 | 115 | 5.426 | 5.4244 | 0.0016
GEN-2018-124 | 05 SOUTHWEST | 526076 | STANTON_W 3 | 115 | 8.923 | 8.9219 | 0.0011
GEN-2018-124 | 05 SOUTHWEST | 526160 | CARLISLE 3 | 115 | 12.772 | 12.7699 | 0.0021
GEN-2018-124 | 05 SOUTHWEST | 526269 | LUBBCK_STH 6 | 230 | 15.0546 | 15.0508 | 0.0038
GEN-2018-124 | 05 SOUTHWEST | 526298 | LUBBCK_EST 3 | 115 | 14.4141 | 14.4121 | 0.002
GEN-2018-124 | 05 SOUTHWEST | 526299 | LUBBCK_EST 6 | 230 | 11.0462 | 11.0443 | 0.0019
GEN-2018-124 | 05 SOUTHWEST | 526434 | SUNDOWN 3 | 115 | 10.8603 | 10.8572 | 0.0031
GEN-2018-124 | 05 SOUTHWEST | 526460 | AMOCO_SS 6 | 230 | 10.1771 | 10.172 | 0.0051
GEN-2018-124 | 05 SOUTHWEST | 526525 | WOLFFORTH 6 | 230 | 13.0516 | 13.0464 | 0.0052
GEN-2018-124 | 05 SOUTHWEST | 526677 | GRASSLAND 6 | 230 | 5.9735 | 5.973 | 0.0005
GEN-2018-124 | 05 SOUTHWEST | 526934 | YOAKUM 3 | 115 | 19.2326 | 19.2289 | 0.0037
GEN-2018-124 | 05 SOUTHWEST | 526936 | YOAKUM_345 | 345 | 9.9314 | 9.9277 | 0.0037
GEN-2018-124 | 05 SOUTHWEST | 527009 | BRU_SUB 6 | 230 | 15.6513 | 15.6468 | 0.0045
GEN-2018-124 | 05 SOUTHWEST | 527028 | INK_BASIN 6 | 230 | 11.2413 | 11.2391 | 0.0022
GEN-2018-124 | 05 SOUTHWEST | 527149 | MUSTANG 6 | 230 | 17.9238 | 17.9198 | 0.004
GEN-2018-124 | 05 SOUTHWEST | 527610 | SAGA_SCOL 7 | 345 | 10.2321 | 10.2225 | 0.0096
GEN-2018-124 | 05 SOUTHWEST | 527655 | RSVLT_CC_E 7 | 345 | 10.0154 | 10.0061 | 0.0093
GEN-2018-124 | 05 SOUTHWEST | 527802 | EDDY_CNTY 7 | 345 | 7.3273 | 7.3245 | 0.0028
GEN-2018-124 | 05 SOUTHWEST | 527896 | HOBBS_INT 7 | 345 | 12.0143 | 12.0078 | 0.0065
GEN-2018-124 | 05 SOUTHWEST | 560022 | CRAWFISH_DR | 345 | 13.842 | 13.8369 | 0.0051
GEN-2018-124 | 05 SOUTHWEST | 560035 | GRAPEVINE | 345 | 6.4589 | 6.4581 | 0.0008
GEN-2018-124 | 05 SOUTHWEST | 760494 | GEN-2017-146 | 230 | 7.4558 | 7.4499 | 0.0059
GEN-2018-124 | 05 SOUTHWEST | 763186 | GEN-2018-089 | 230 | 10.6882 | 10.6799 | 0.0083
GEN-2018-124 | 05 SOUTHWEST | 511553 | CHISHOLM7 | 345 | 12.3397 | 12.339 | 0.0007
GEN-2018-124 | 05 SOUTHWEST | 515458 | BORDER 7 | 345 | 8.2517 | 8.2513 | 0.0004
GEN-2018-124 | 05 SOUTHWEST | 515554 | BVRCNTY7 | 345 | 15.3093 | 15.3088 | 0.0005
GEN-2018-124 | 05 SOUTHWEST | 523095 | HITCHLAND 6 | 230 | 14.5761 | 14.5756 | 0.0005
GEN-2018-124 | 05 SOUTHWEST | 523101 | NOBLE_WND 7 | 345 | 14.9103 | 14.9096 | 0.0007
GEN-2018-124 | 05 SOUTHWEST | 523112 | NOVUS1 7 | 345 | 14.6716 | 14.6709 | 0.0007
GEN-2018-124 | 05 SOUTHWEST | 523323 | MCDWL_CREEK6 | 230 | 8.9802 | 8.9792 | 0.001
GEN-2018-124 | 05 SOUTHWEST | 523823 | CARPENTER 7 | 345 | 6.5781 | 6.578 | 0.0001
GEN-2018-124 | 05 SOUTHWEST | 523869 | CHAN+TASCOS6 | 230 | 4.2464 | 4.2462 | 0.0002
GEN-2018-124 | 05 SOUTHWEST | 523979 | HARRNG_EST 6 | 230 | 26.9856 | 26.9793 | 0.0063
GEN-2018-124 | 05 SOUTHWEST | 524010 | ROLLHILLS 6 | 230 | 20.2306 | 20.226 | 0.0046
GEN-2018-124 | 05 SOUTHWEST | 524044 | NICHOLS 6 | 230 | 26.1237 | 26.1179 | 0.0058
GEN-2018-124 | 05 SOUTHWEST | 524267 | BUSHLAND 6 | 230 | 10.1739 | 10.171 | 0.0029
GEN-2018-124 | 05 SOUTHWEST | 524299 | SPNSPUR_COL7 | 345 | 5.3278 | 5.3269 | 0.0009
GEN-2018-124 | 05 SOUTHWEST | 524365 | RANDALL 6 | 230 | 14.5681 | 14.5656 | 0.0025
GEN-2018-124 | 05 SOUTHWEST | 524414 | AMA_SOUTH 3 | 115 | 16.9088 | 16.907 | 0.0018
GEN-2018-124 | 05 SOUTHWEST | 524502 | NORTON 3 | 115 | 2.9186 | 2.9184 | 0.0002
GEN-2018-124 | 05 SOUTHWEST | 524619 | DFSMTH_EST 3 | 115 | 11.9939 | 11.9881 | 0.0058
GEN-2018-124 | 05 SOUTHWEST | 524622 | DFSMTH_WST 3 | 115 | 11.9945 | 11.9887 | 0.0058
GEN-2018-124 | 05 SOUTHWEST | 524669 | DS-#20 3 | 115 | 6.2762 | 6.2732 | 0.003
GEN-2018-124 | 05 SOUTHWEST | 524746 | CASTRO_CNTY3 | 115 | 9.822 | 9.8183 | 0.0037
GEN-2018-124 | 05 SOUTHWEST | 524764 | NORRIS_TP 3 | 115 | 11.4074 | 11.3958 | 0.0116
GEN-2018-124 | 05 SOUTHWEST | 524773 | E_CLOVIS 3 | 115 | 8.962 | 8.9549 | 0.0071
GEN-2018-124 | 05 SOUTHWEST | 524776 | N_CLOVIS_TP3 | 115 | 7.4744 | 7.4697 | 0.0047
GEN-2018-124 | 05 SOUTHWEST | 524797 | PERIMETER 3 | 115 | 6.5512 | 6.5473 | 0.0039
GEN-2018-124 | 05 SOUTHWEST | 524821 | CURRY 2 | 69 | 4.4284 | 4.4273 | 0.0011
GEN-2018-124 | 05 SOUTHWEST | 524831 | FE-HOLLAND 3 | 115 | 9.2431 | 9.2356 | 0.0075
GEN-2018-124 | 05 SOUTHWEST | 524838 | FE-CLOVIS2+3 | 115 | 10.7942 | 10.7838 | 0.0104
GEN-2018-124 | 05 SOUTHWEST | 524863 | FE-CHZPLT 3 | 115 | 8.0228 | 8.017 | 0.0058
GEN-2018-124 | 05 SOUTHWEST | 524889 | SN_JUAN_WND6 | 230 | 4.6556 | 4.6539 | 0.0017
GEN-2018-124 | 05 SOUTHWEST | 524923 | PORTALES 2 | 69 | 7.5604 | 7.5571 | 0.0033
GEN-2018-124 | 05 SOUTHWEST | 524935 | KILGORE 3 | 115 | 6.1488 | 6.1452 | 0.0036
GEN-2018-124 | 05 SOUTHWEST | 524977 | GREYHOUND 3 | 115 | 5.6862 | 5.6832 | 0.003
GEN-2018-124 | 05 SOUTHWEST | 525018 | MULESHVALLY3 | 115 | 5.5409 | 5.5382 | 0.0027
GEN-2018-124 | 05 SOUTHWEST | 525028 | BAILEYCO 3 | 115 | 5.8021 | 5.7991 | 0.003
GEN-2018-124 | 05 SOUTHWEST | 525050 | BC-KELLEY +3 | 115 | 7.782 | 7.7785 | 0.0035
GEN-2018-124 | 05 SOUTHWEST | 525124 | HART_INDUST3 | 115 | 7.4925 | 7.4902 | 0.0023
GEN-2018-124 | 05 SOUTHWEST | 525192 | KRESS_INT 3 | 115 | 11.9205 | 11.9167 | 0.0038
GEN-2018-124 | 05 SOUTHWEST | 525326 | COX 3 | 115 | 6.2736 | 6.2726 | 0.001
GEN-2018-124 | 05 SOUTHWEST | 525393 | ROCKYFORD 3 | 115 | 9.0431 | 9.0366 | 0.0065
GEN-2018-124 | 05 SOUTHWEST | 525414 | LAMTON 3 | 115 | 7.6144 | 7.6115 | 0.0029
GEN-2018-124 | 05 SOUTHWEST | 525440 | LC-S_OLTON+3 | 115 | 7.1982 | 7.1951 | 0.0031
GEN-2018-124 | 05 SOUTHWEST | 525453 | HALE_CNTY 2 | 69 | 6.9062 | 6.9053 | 0.0009
GEN-2018-124 | 05 SOUTHWEST | 525613 | W_LITTLFLD 2 | 69 | 2.9684 | 2.9679 | 0.0005
GEN-2018-124 | 05 SOUTHWEST | 525620 | LTFLD_S&CTY2 | 69 | 4.1727 | 4.1715 | 0.0012
GEN-2018-124 | 05 SOUTHWEST | 525650 | LC-LTTLFLD+2 | 69 | 4.9319 | 4.9303 | 0.0016
GEN-2018-124 | 05 SOUTHWEST | 525687 | LC-LUMSCHAP2 | 69 | 4.6126 | 4.6112 | 0.0014
GEN-2018-124 | 05 SOUTHWEST | 525731 | SP-ABERNTHY2 | 69 | 3.0093 | 3.0092 | 0.0001
GEN-2018-124 | 05 SOUTHWEST | 525738 | HALECENTER 2 | 69 | 2.4566 | 2.4565 | 0.0001
GEN-2018-124 | 05 SOUTHWEST | 525763 | CALLAHAN 3 | 115 | 5.5668 | 5.5662 | 0.0006
GEN-2018-124 | 05 SOUTHWEST | 525779 | FLOYD_CNTY 2 | 69 | 5.401 | 5.4007 | 0.0003
GEN-2018-124 | 05 SOUTHWEST | 525803 | BLANCO 3 | 115 | 5.0451 | 5.0448 | 0.0003
GEN-2018-124 | 05 SOUTHWEST | 525853 | LH-WIL&ELN+2 | 69 | 2.5404 | 2.5404 | 0
GEN-2018-124 | 05 SOUTHWEST | 525885 | SP-NEWDEAL 2 | 69 | 3.3073 | 3.3072 | 0.0001
GEN-2018-124 | 05 SOUTHWEST | 525926 | CROSBY 3 | 115 | 4.7129 | 4.7127 | 0.0002
GEN-2018-124 | 05 SOUTHWEST | 526019 | HOCKLEY 2 | 69 | 5.1105 | 5.1096 | 0.0009
GEN-2018-124 | 05 SOUTHWEST | 526036 | LC-OPDYKE 3 | 115 | 5.7143 | 5.7127 | 0.0016
GEN-2018-124 | 05 SOUTHWEST | 526109 | SP-ERSKINE 3 | 115 | 10.9787 | 10.977 | 0.0017
GEN-2018-124 | 05 SOUTHWEST | 526146 | INDIANA 3 | 115 | 9.3032 | 9.302 | 0.0012
GEN-2018-124 | 05 SOUTHWEST | 526159 | CARLISLE 2 | 69 | 2.5568 | 2.5568 | 0
GEN-2018-124 | 05 SOUTHWEST | 526162 | LP-DOUD_TP 3 | 115 | 11.325 | 11.3233 | 0.0017
GEN-2018-124 | 05 SOUTHWEST | 526192 | MURPHY 3 | 115 | 10.2503 | 10.249 | 0.0013
GEN-2018-124 | 05 SOUTHWEST | 526268 | LUBBCK_STH 3 | 115 | 17.6482 | 17.6453 | 0.0029
GEN-2018-124 | 05 SOUTHWEST | 526297 | LUBBCK_EST 2 | 69 | 7.8955 | 7.8952 | 0.0003
GEN-2018-124 | 05 SOUTHWEST | 526424 | PACIFIC 3 | 115 | 9.1771 | 9.175 | 0.0021
GEN-2018-124 | 05 SOUTHWEST | 526445 | AMOCO_TP 3 | 115 | 10.1845 | 10.1818 | 0.0027
GEN-2018-124 | 05 SOUTHWEST | 526524 | WOLFFORTH 3 | 115 | 11.2819 | 11.2801 | 0.0018
GEN-2018-124 | 05 SOUTHWEST | 526676 | GRASSLAND 3 | 115 | 6.8633 | 6.863 | 0.0003
GEN-2018-124 | 05 SOUTHWEST | 526679 | CIRRUS_WND 6 | 230 | 4.6792 | 4.6789 | 0.0003
GEN-2018-124 | 05 SOUTHWEST | 526784 | AMOCOWASSON6 | 230 | 15.6353 | 15.6317 | 0.0036
GEN-2018-124 | 05 SOUTHWEST | 526792 | PRENTICE 3 | 115 | 6.0286 | 6.0282 | 0.0004
GEN-2018-124 | 05 SOUTHWEST | 526928 | PLAINS_INT 3 | 115 | 10.0196 | 10.0185 | 0.0011
GEN-2018-124 | 05 SOUTHWEST | 527010 | OXYBRU 6 | 230 | 15.5052 | 15.5007 | 0.0045
GEN-2018-124 | 05 SOUTHWEST | 527011 | XTO_MAHONEY6 | 230 | 15.3578 | 15.3537 | 0.0041
GEN-2018-124 | 05 SOUTHWEST | 527027 | INK_BASIN 3 | 115 | 13.258 | 13.2569 | 0.0011
GEN-2018-124 | 05 SOUTHWEST | 527041 | ARCO_TP 3 | 115 | 13.6807 | 13.6794 | 0.0013
GEN-2018-124 | 05 SOUTHWEST | 527146 | MUSTANG 3 | 115 | 24.0628 | 24.0599 | 0.0029
GEN-2018-124 | 05 SOUTHWEST | 527151 | GS-MUSTANG 6 | 230 | 17.9238 | 17.9198 | 0.004
GEN-2018-124 | 05 SOUTHWEST | 527194 | LG-PLSHILL 3 | 115 | 7.9741 | 7.9736 | 0.0005
GEN-2018-124 | 05 SOUTHWEST | 527276 | SEMINOLE 6 | 230 | 8.197 | 8.1963 | 0.0007
GEN-2018-124 | 05 SOUTHWEST | 527483 | CHAVES_CNTY6 | 230 | 4.4929 | 4.4919 | 0.001
GEN-2018-124 | 05 SOUTHWEST | 527599 | SAGA_SDCOL 7 | 345 | 10.2321 | 10.2225 | 0.0096
GEN-2018-124 | 05 SOUTHWEST | 527654 | RSVLT_CC_W 7 | 345 | 8.7265 | 8.7196 | 0.0069
GEN-2018-124 | 05 SOUTHWEST | 527799 | EDDY_NORTH 6 | 230 | 9.402 | 9.3993 | 0.0027
GEN-2018-124 | 05 SOUTHWEST | 527894 | HOBBS_INT 6 | 230 | 19.4767 | 19.4716 | 0.0051
GEN-2018-124 | 05 SOUTHWEST | 527965 | KIOWA 7 | 345 | 8.82 | 8.8165 | 0.0035
GEN-2018-124 | 05 SOUTHWEST | 528027 | RDRUNNER 7 | 345 | 8.6815 | 8.6783 | 0.0032
GEN-2018-124 | 05 SOUTHWEST | 576397 | G10014G11022 | 345 | 10.3812 | 10.3809 | 0.0003
GEN-2018-124 | 05 SOUTHWEST | 762216 | G17-151TAP | 345 | 8.5119 | 8.5105 | 0.0014
GEN-2018-124 | 05 SOUTHWEST | 763087 | GEN-2018-073 | 345 | 11.9423 | 11.9385 | 0.0038
GEN-2018-124 | 05 SOUTHWEST | 763516 | GEN-2019-011 | 345 | 9.2852 | 9.282 | 0.0032
GEN-2018-124 | 05 SOUTHWEST | 511557 | CHISHOLM6 | 230 | 12.1566 | 12.1562 | 0.0004
GEN-2018-124 | 05 SOUTHWEST | 515375 | WWRDEHV7 | 345 | 22.3641 | 22.3637 | 0.0004
GEN-2018-124 | 05 SOUTHWEST | 515590 | PALDR2W7 | 345 | 12.8669 | 12.8666 | 0.0003
GEN-2018-124 | 05 SOUTHWEST | 515618 | BALKOW 7 | 345 | 12.5807 | 12.5804 | 0.0003
GEN-2018-124 | 05 SOUTHWEST | 515677 | BADGER 7 | 345 | 13.7821 | 13.7818 | 0.0003
GEN-2018-124 | 05 SOUTHWEST | 523093 | HITCHLAND 3 | 115 | 17.3358 | 17.3354 | 0.0004
GEN-2018-124 | 05 SOUTHWEST | 523103 | NOBLE_WND 3 | 115 | 10.6199 | 10.6198 | 0.0001
GEN-2018-124 | 05 SOUTHWEST | 523111 | NOVUS1 3 | 115 | 7.8432 | 7.8431 | 0.0001
GEN-2018-124 | 05 SOUTHWEST | 523155 | OCHILTREE 6 | 230 | 4.265 | 4.2649 | 0.0001
GEN-2018-124 | 05 SOUTHWEST | 523215 | GEN-2011-022 | 345 | 10.3812 | 10.3809 | 0.0003
GEN-2018-124 | 05 SOUTHWEST | 523221 | XIT_INTG 6 | 230 | 3.1441 | 3.1439 | 0.0002
GEN-2018-124 | 05 SOUTHWEST | 523267 | PRINGLE 6 | 230 | 4.3435 | 4.3434 | 0.0001
GEN-2018-124 | 05 SOUTHWEST | 523309 | MOORE_CNTY 6 | 230 | 6.6813 | 6.6809 | 0.0004
GEN-2018-124 | 05 SOUTHWEST | 523322 | MCDWL_CREEK3 | 115 | 9.8376 | 9.8372 | 0.0004
GEN-2018-124 | 05 SOUTHWEST | 523551 | HUTCHISON 6 | 230 | 7.288 | 7.2877 | 0.0003
GEN-2018-124 | 05 SOUTHWEST | 523771 | GRAPEVINE 6 | 230 | 5.9762 | 5.9761 | 0.0001
GEN-2018-124 | 05 SOUTHWEST | 523853 | FINNEY 7 | 345 | 9.8362 | 9.8361 | 0.0001
GEN-2018-124 | 05 SOUTHWEST | 523977 | HARRNG_WST 6 | 230 | 26.9856 | 26.9793 | 0.0063
GEN-2018-124 | 05 SOUTHWEST | 523978 | HARRNG_MID 6 | 230 | 26.9856 | 26.9793 | 0.0063
GEN-2018-124 | 05 SOUTHWEST | 524007 | ROLLHILLS 3 | 115 | 19.6592 | 19.6573 | 0.0019
GEN-2018-124 | 05 SOUTHWEST | 524043 | NICHOLS 3 | 115 | 30.649 | 30.6457 | 0.0033
GEN-2018-124 | 05 SOUTHWEST | 524266 | BUSHLAND 3 | 115 | 10.3324 | 10.3313 | 0.0011
GEN-2018-124 | 05 SOUTHWEST | 524290 | WILDOR2_JUS6 | 230 | 6.9783 | 6.977 | 0.0013
GEN-2018-124 | 05 SOUTHWEST | 524364 | RANDALL 3 | 115 | 21.0733 | 21.0701 | 0.0032
GEN-2018-124 | 05 SOUTHWEST | 524377 | FARMERS 3 | 115 | 15.4368 | 15.4352 | 0.0016
GEN-2018-124 | 05 SOUTHWEST | 524397 | ARROWHEAD 3 | 115 | 13.6793 | 13.6782 | 0.0011
GEN-2018-124 | 05 SOUTHWEST | 524404 | OWENSCORN 3 | 115 | 15.0594 | 15.0579 | 0.0015
GEN-2018-124 | 05 SOUTHWEST | 524486 | CAPROCK 3 | 115 | 2.636 | 2.6359 | 0.0001
GEN-2018-124 | 05 SOUTHWEST | 524509 | FE-TUCMCARI3 | 115 | 2.391 | 2.3909 | 0.0001
GEN-2018-124 | 05 SOUTHWEST | 524544 | SPRING_DRW 3 | 115 | 6.4069 | 6.4066 | 0.0003
GEN-2018-124 | 05 SOUTHWEST | 524630 | TIERABLANCA3 | 115 | 12.3344 | 12.3283 | 0.0061
GEN-2018-124 | 05 SOUTHWEST | 524662 | PARMER_CO 3 | 115 | 5.4666 | 5.4646 | 0.002
GEN-2018-124 | 05 SOUTHWEST | 524694 | DS-#22 3 | 115 | 4.5966 | 4.5958 | 0.0008
GEN-2018-124 | 05 SOUTHWEST | 524734 | DS-#21 3 | 115 | 9.3056 | 9.3022 | 0.0034
GEN-2018-124 | 05 SOUTHWEST | 524745 | CASTRO_CNTY2 | 69 | 8.7963 | 8.7945 | 0.0018
GEN-2018-124 | 05 SOUTHWEST | 524757 | BETHEL_COL13 | 115 | 8.2391 | 8.2367 | 0.0024
GEN-2018-124 | 05 SOUTHWEST | 524777 | N_CLOVIS 3 | 115 | 6.7428 | 6.739 | 0.0038
GEN-2018-124 | 05 SOUTHWEST | 524783 | W_CLOVIS 2 | 69 | 2.4403 | 2.44 | 0.0003
GEN-2018-124 | 05 SOUTHWEST | 524790 | CANNON_TP 3 | 115 | 6.0058 | 6.0027 | 0.0031
GEN-2018-124 | 05 SOUTHWEST | 524801 | NORRIS 3 | 115 | 10.4115 | 10.4019 | 0.0096
GEN-2018-124 | 05 SOUTHWEST | 524808 | FE-CLVS_INT3 | 115 | 6.9498 | 6.9457 | 0.0041
GEN-2018-124 | 05 SOUTHWEST | 524846 | FARWELL 2 | 69 | 2.1357 | 2.1355 | 0.0002
GEN-2018-124 | 05 SOUTHWEST | 524929 | RO-PORT_MTR2 | 69 | 7.5604 | 7.5571 | 0.0033
GEN-2018-124 | 05 SOUTHWEST | 524934 | ZODIAC 2 | 69 | 5.5439 | 5.5421 | 0.0018
GEN-2018-124 | 05 SOUTHWEST | 524941 | PORTALES#1 2 | 69 | 5.7509 | 5.749 | 0.0019
GEN-2018-124 | 05 SOUTHWEST | 524963 | S_PORTALES 3 | 115 | 5.7708 | 5.7676 | 0.0032
GEN-2018-124 | 05 SOUTHWEST | 525027 | BAILEYCO 2 | 69 | 5.2707 | 5.2693 | 0.0014
GEN-2018-124 | 05 SOUTHWEST | 525179 | TULIA_TP 3 | 115 | 6.4624 | 6.4615 | 0.0009
GEN-2018-124 | 05 SOUTHWEST | 525191 | KRESS_INT 2 | 69 | 4.4978 | 4.4975 | 0.0003
GEN-2018-124 | 05 SOUTHWEST | 525226 | KRS_RURL_TP3 | 115 | 6.4399 | 6.4389 | 0.001
GEN-2018-124 | 05 SOUTHWEST | 525272 | KISER 3 | 115 | 5.2683 | 5.2676 | 0.0007
GEN-2018-124 | 05 SOUTHWEST | 525291 | PLAINVW_TP 2 | 69 | 6.4824 | 6.4815 | 0.0009
GEN-2018-124 | 05 SOUTHWEST | 525298 | S_PLAINVEW 2 | 69 | 2.5852 | 2.5851 | 0.0001
GEN-2018-124 | 05 SOUTHWEST | 525325 | COX 2 | 69 | 3.4185 | 3.4183 | 0.0002
GEN-2018-124 | 05 SOUTHWEST | 525351 | LH-AIKEN 2 | 69 | 2.1484 | 2.1484 | 0
GEN-2018-124 | 05 SOUTHWEST | 525413 | LAMTON 2 | 69 | 5.1693 | 5.1685 | 0.0008
GEN-2018-124 | 05 SOUTHWEST | 525432 | SP-HALFWAY+2 | 69 | 5.8641 | 5.8634 | 0.0007
GEN-2018-124 | 05 SOUTHWEST | 525606 | AMHERST 2 | 69 | 2.3408 | 2.3405 | 0.0003
GEN-2018-124 | 05 SOUTHWEST | 525657 | W_ANTON_TP 2 | 69 | 4.1079 | 4.1068 | 0.0011
GEN-2018-124 | 05 SOUTHWEST | 525694 | HOBGOOD 2 | 69 | 3.4381 | 3.4374 | 0.0007
GEN-2018-124 | 05 SOUTHWEST | 525723 | CNTYLINE_TP2 | 69 | 2.2014 | 2.2014 | 0
GEN-2018-124 | 05 SOUTHWEST | 525745 | LH-HALECTR 2 | 69 | 2.4289 | 2.4289 | 0
GEN-2018-124 | 05 SOUTHWEST | 525790 | FLOYDADA_TP2 | 69 | 2.5171 | 2.517 | 0.0001
GEN-2018-124 | 05 SOUTHWEST | 525801 | LRNZ_MPT 3 | 115 | 5.0442 | 5.0439 | 0.0003
GEN-2018-124 | 05 SOUTHWEST | 525811 | LH-HARMONY 2 | 69 | 4.3124 | 4.3122 | 0.0002
GEN-2018-124 | 05 SOUTHWEST | 525860 | SP-BECTON +2 | 69 | 2.2545 | 2.2545 | 0
GEN-2018-124 | 05 SOUTHWEST | 525892 | MONROE 2 | 69 | 2.6475 | 2.6475 | 0
GEN-2018-124 | 05 SOUTHWEST | 525925 | CROSBY 2 | 69 | 4.7847 | 4.7846 | 0.0001
GEN-2018-124 | 05 SOUTHWEST | 526009 | LC-LEVLND#22 | 69 | 4.2645 | 4.2639 | 0.0006
GEN-2018-124 | 05 SOUTHWEST | 526042 | COBLE 2 | 69 | 2.2615 | 2.2613 | 0.0002
GEN-2018-124 | 05 SOUTHWEST | 526048 | LVLNDCTY_TP2 | 69 | 4.2645 | 4.2639 | 0.0006
GEN-2018-124 | 05 SOUTHWEST | 526130 | SP-CARLISLE2 | 69 | 2.1026 | 2.1025 | 0.0001
GEN-2018-124 | 05 SOUTHWEST | 526176 | LP-DOUD 3 | 115 | 8.8577 | 8.8567 | 0.001
GEN-2018-124 | 05 SOUTHWEST | 526184 | SW_6878 2 | 69 | 2.1534 | 2.1534 | 0
GEN-2018-124 | 05 SOUTHWEST | 526195 | QUINCY 3 | 115 | 9.6342 | 9.6331 | 0.0011
GEN-2018-124 | 05 SOUTHWEST | 526213 | ALLEN 3 | 115 | 10.4502 | 10.4491 | 0.0011
GEN-2018-124 | 05 SOUTHWEST | 526267 | LUBBCK_STH 2 | 69 | 4.3104 | 4.3103 | 0.0001
GEN-2018-124 | 05 SOUTHWEST | 526284 | PLANTERS 2 | 69 | 5.7109 | 5.7108 | 0.0001
GEN-2018-124 | 05 SOUTHWEST | 526310 | CLUTTER 2 | 69 | 5.3812 | 5.381 | 0.0002
GEN-2018-124 | 05 SOUTHWEST | 526361 | COCHRAN 3 | 115 | 6.4257 | 6.4248 | 0.0009
GEN-2018-124 | 05 SOUTHWEST | 526452 | AMOCO_CRYO 3 | 115 | 6.362 | 6.361 | 0.001
GEN-2018-124 | 05 SOUTHWEST | 526475 | YUMA_INT 3 | 115 | 10.7034 | 10.7018 | 0.0016
GEN-2018-124 | 05 SOUTHWEST | 526481 | SP-WOLF_TP 3 | 115 | 10.8642 | 10.8626 | 0.0016
GEN-2018-124 | 05 SOUTHWEST | 526484 | LG-LEVELAND3 | 115 | 9.1775 | 9.1755 | 0.002
GEN-2018-124 | 05 SOUTHWEST | 526562 | SLATON 2 | 69 | 2.4663 | 2.4663 | 0
GEN-2018-124 | 05 SOUTHWEST | 526602 | WOODROW 3 | 115 | 9.1323 | 9.1316 | 0.0007
GEN-2018-124 | 05 SOUTHWEST | 526656 | LYNN_CNTY 3 | 115 | 5.9373 | 5.937 | 0.0003
GEN-2018-124 | 05 SOUTHWEST | 526694 | GRAHAM 3 | 115 | 2.8169 | 2.8168 | 0.0001
GEN-2018-124 | 05 SOUTHWEST | 526736 | TERRY_CNTY 3 | 115 | 10.6679 | 10.6665 | 0.0014
GEN-2018-124 | 05 SOUTHWEST | 526944 | LG-PLAINS 3 | 115 | 7.9013 | 7.9006 | 0.0007
GEN-2018-124 | 05 SOUTHWEST | 527018 | BENNETT 3 | 115 | 13.7758 | 13.7745 | 0.0013
GEN-2018-124 | 05 SOUTHWEST | 527030 | ALRDCRTZ_TP3 | 115 | 12.2915 | 12.2906 | 0.0009
GEN-2018-124 | 05 SOUTHWEST | 527047 | OXY_WILRD1 3 | 115 | 10.8936 | 10.8928 | 0.0008
GEN-2018-124 | 05 SOUTHWEST | 527062 | SHELL_CO2 3 | 115 | 16.7017 | 16.7 | 0.0017
GEN-2018-124 | 05 SOUTHWEST | 527130 | DENVER_N 3 | 115 | 22.5277 | 22.5249 | 0.0028
GEN-2018-124 | 05 SOUTHWEST | 527136 | DENVER_S 3 | 115 | 22.5277 | 22.5249 | 0.0028
GEN-2018-124 | 05 SOUTHWEST | 527202 | SEAGRAVES 3 | 115 | 9.1786 | 9.178 | 0.0006
GEN-2018-124 | 05 SOUTHWEST | 527275 | SEMINOLE 3 | 115 | 14.6609 | 14.6597 | 0.0012
GEN-2018-124 | 05 SOUTHWEST | 527482 | CHAVES_CNTY3 | 115 | 7.0492 | 7.0481 | 0.0011
GEN-2018-124 | 05 SOUTHWEST | 527600 | SAGA_SMEAS 7 | 345 | 10.2321 | 10.2225 | 0.0096
GEN-2018-124 | 05 SOUTHWEST | 527666 | RSVLT_COL1 7 | 345 | 8.7265 | 8.7196 | 0.0069
GEN-2018-124 | 05 SOUTHWEST | 527667 | RSVLT_COL2 7 | 345 | 8.7265 | 8.7196 | 0.0069
GEN-2018-124 | 05 SOUTHWEST | 527793 | EDDY_STH 3 | 115 | 11.9559 | 11.9537 | 0.0022
GEN-2018-124 | 05 SOUTHWEST | 527798 | EDDY_NTH 3 | 115 | 11.9559 | 11.9537 | 0.0022
GEN-2018-124 | 05 SOUTHWEST | 527865 | CUNNIGHM_N 6 | 230 | 17.5364 | 17.5327 | 0.0037
GEN-2018-124 | 05 SOUTHWEST | 527867 | CUNNIGHM_S 6 | 230 | 17.5364 | 17.5327 | 0.0037
GEN-2018-124 | 05 SOUTHWEST | 527891 | HOBBS_INT 3 | 115 | 33.0667 | 33.063 | 0.0037
GEN-2018-124 | 05 SOUTHWEST | 527966 | KIOWA 3 | 115 | 17.1508 | 17.1472 | 0.0036
GEN-2018-124 | 05 SOUTHWEST | 528015 | PHANTOM 7 | 345 | 5.675 | 5.6736 | 0.0014
GEN-2018-124 | 05 SOUTHWEST | 528025 | RDRUNNER 3 | 115 | 13.7957 | 13.7933 | 0.0024
GEN-2018-124 | 05 SOUTHWEST | 528095 | 7-RIVERS 6 | 230 | 6.3874 | 6.3863 | 0.0011
GEN-2018-124 | 05 SOUTHWEST | 528185 | N_LOVING 7 | 345 | 6.5496 | 6.5478 | 0.0018
GEN-2018-124 | 05 SOUTHWEST | 528325 | LE-WAITS 3 | 115 | 8.9967 | 8.9963 | 0.0004
GEN-2018-124 | 05 SOUTHWEST | 528604 | ANDREWS 6 | 230 | 6.0764 | 6.076 | 0.0004
GEN-2018-124 | 05 SOUTHWEST | 528626 | LE-PLNSINT 2 | 69 | 3.6375 | 3.6374 | 0.0001
GEN-2018-124 | 05 SOUTHWEST | 531512 | HARBNGR7 | 345 | 6.5579 | 6.5579 | 0
GEN-2018-124 | 05 SOUTHWEST | 560078 | G16-037-TAP | 345 | 10.1427 | 10.1425 | 0.0002
GEN-2018-124 | 05 SOUTHWEST | 560577 | G06-44 | 115 | 7.5797 | 7.5797 | 0
GEN-2018-124 | 05 SOUTHWEST | 576395 | GEN-2010-014 | 345 | 10.3812 | 10.3809 | 0.0003
GEN-2018-124 | 05 SOUTHWEST | 588460 | A16-008SUB | 115 | 13.258 | 13.2569 | 0.0011
GEN-2018-124 | 05 SOUTHWEST | 599960 | EPTNP-D6 | 230 | 9.402 | 9.3993 | 0.0027
GEN-2018-124 | 05 SOUTHWEST | 755000 | WWDBORDT | 345 | 12.2648 | 12.2641 | 0.0007
GEN-2018-124 | 05 SOUTHWEST | 761355 | GEN-2017-239 | 230 | 13.7988 | 13.7956 | 0.0032
GEN-2018-124 | 05 SOUTHWEST | 762217 | GEN-2017-151 | 345 | 6.1754 | 6.1747 | 0.0007
GEN-2018-124 | 05 SOUTHWEST | 762467 | G18-015-TAP | 345 | 5.8242 | 5.824 | 0.0002
GEN-2019-003 | 05 SOUTHWEST | 524909 | ROOSEVELT 6 | 230 | 9.709 | 9.3064 | 0.4026
GEN-2019-003 | 05 SOUTHWEST | 524770 | PLSNT_HILL 6 | 230 | 6.517 | 6.358 | 0.159
GEN-2019-003 | 05 SOUTHWEST | 524875 | OASIS 6 | 230 | 7.8784 | 7.654 | 0.2244
GEN-2019-003 | 05 SOUTHWEST | 524908 | ROOSEVELT 3 | 115 | 11.1454 | 10.9306 | 0.2148
GEN-2019-003 | 05 SOUTHWEST | 525531 | TOLK 6 | 230 | 31.4946 | 31.2438 | 0.2508
GEN-2019-003 | 05 SOUTHWEST | 599955 | PNM-DC6 | 230 | 9.709 | 9.3064 | 0.4026
GEN-2019-003 | 05 SOUTHWEST | 763483 | GEN-2019-003 | 230 | 8.7401 | 8.3344 | 0.4057
GEN-2019-003 | 05 SOUTHWEST | 524768 | PLSNT_HILL 3 | 115 | 10.5272 | 10.363 | 0.1642
GEN-2019-003 | 05 SOUTHWEST | 524822 | CURRY 3 | 115 | 11.4402 | 11.2569 | 0.1833
GEN-2019-003 | 05 SOUTHWEST | 524874 | OASIS 3 | 115 | 10.0542 | 9.886 | 0.1682
GEN-2019-003 | 05 SOUTHWEST | 524885 | SN_JUAN_TAP6 | 230 | 4.8705 | 4.8395 | 0.031
GEN-2019-003 | 05 SOUTHWEST | 524924 | PORTALES 3 | 115 | 7.5524 | 7.4549 | 0.0975
GEN-2019-003 | 05 SOUTHWEST | 525481 | PLANT_X 6 | 230 | 24.1838 | 24.0769 | 0.1069
GEN-2019-003 | 05 SOUTHWEST | 525549 | TOLK 7 | 345 | 15.0276 | 14.9674 | 0.0602
GEN-2019-003 | 05 SOUTHWEST | 525586 | NEEDMORE 6 | 230 | 11.0214 | 10.998 | 0.0234
GEN-2019-003 | 05 SOUTHWEST | 525637 | LAMB_CNTY 6 | 230 | 5.4027 | 5.3963 | 0.0064
GEN-2019-003 | 05 SOUTHWEST | 525830 | TUCO_INT 6 | 230 | 21.9895 | 21.9776 | 0.0119
GEN-2019-003 | 05 SOUTHWEST | 762132 | GEN-2017-158 | 230 | 13.8646 | 13.8219 | 0.0427
GEN-2019-003 | 05 SOUTHWEST | 763241 | GEN-2018-097 | 230 | 24.4484 | 24.3 | 0.1484
GEN-2019-003 | 05 SOUTHWEST | 523961 | POTTER_CO 7 | 345 | 11.6631 | 11.6587 | 0.0044
GEN-2019-003 | 05 SOUTHWEST | 524502 | NORTON 3 | 115 | 2.9186 | 2.9156 | 0.003
GEN-2019-003 | 05 SOUTHWEST | 524669 | DS-#20 3 | 115 | 6.2762 | 6.2384 | 0.0378
GEN-2019-003 | 05 SOUTHWEST | 524764 | NORRIS_TP 3 | 115 | 11.4074 | 11.2251 | 0.1823
GEN-2019-003 | 05 SOUTHWEST | 524773 | E_CLOVIS 3 | 115 | 8.962 | 8.8453 | 0.1167
GEN-2019-003 | 05 SOUTHWEST | 524776 | N_CLOVIS_TP3 | 115 | 7.4744 | 7.3912 | 0.0832
GEN-2019-003 | 05 SOUTHWEST | 524797 | PERIMETER 3 | 115 | 6.5512 | 6.4819 | 0.0693
GEN-2019-003 | 05 SOUTHWEST | 524821 | CURRY 2 | 69 | 4.4284 | 4.4119 | 0.0165
GEN-2019-003 | 05 SOUTHWEST | 524831 | FE-HOLLAND 3 | 115 | 9.2431 | 9.1186 | 0.1245
GEN-2019-003 | 05 SOUTHWEST | 524838 | FE-CLOVIS2+3 | 115 | 10.7942 | 10.6301 | 0.1641
GEN-2019-003 | 05 SOUTHWEST | 524863 | FE-CHZPLT 3 | 115 | 8.0228 | 7.9238 | 0.099
GEN-2019-003 | 05 SOUTHWEST | 524889 | SN_JUAN_WND6 | 230 | 4.6556 | 4.6284 | 0.0272
GEN-2019-003 | 05 SOUTHWEST | 524923 | PORTALES 2 | 69 | 7.5604 | 7.5019 | 0.0585
GEN-2019-003 | 05 SOUTHWEST | 524935 | KILGORE 3 | 115 | 6.1488 | 6.0839 | 0.0649
GEN-2019-003 | 05 SOUTHWEST | 524977 | GREYHOUND 3 | 115 | 5.6862 | 5.6307 | 0.0555
GEN-2019-003 | 05 SOUTHWEST | 525028 | BAILEYCO 3 | 115 | 5.8021 | 5.7901 | 0.012
GEN-2019-003 | 05 SOUTHWEST | 525213 | SWISHER 6 | 230 | 10.3853 | 10.3805 | 0.0048
GEN-2019-003 | 05 SOUTHWEST | 525461 | NEWHART 6 | 230 | 10.9971 | 10.9889 | 0.0082
GEN-2019-003 | 05 SOUTHWEST | 525480 | PLANT_X 3 | 115 | 19.2796 | 19.2397 | 0.0399
GEN-2019-003 | 05 SOUTHWEST | 525585 | BLUECLDPOI 6 | 230 | 11.0214 | 10.998 | 0.0234
GEN-2019-003 | 05 SOUTHWEST | 525636 | LAMB_CNTY 3 | 115 | 8.4389 | 8.4323 | 0.0066
GEN-2019-003 | 05 SOUTHWEST | 525828 | TUCO_INT 3 | 115 | 19.3618 | 19.3567 | 0.0051
GEN-2019-003 | 05 SOUTHWEST | 525832 | TUCO_INT 7 | 345 | 14.0745 | 14.0699 | 0.0046
GEN-2019-003 | 05 SOUTHWEST | 525840 | ANTELOPE_1 6 | 230 | 21.8013 | 21.7896 | 0.0117
GEN-2019-003 | 05 SOUTHWEST | 525957 | HALE_WNDCL16 | 230 | 10.5196 | 10.5172 | 0.0024
GEN-2019-003 | 05 SOUTHWEST | 526161 | CARLISLE 6 | 230 | 10.473 | 10.4703 | 0.0027
GEN-2019-003 | 05 SOUTHWEST | 526337 | JONES 6 | 230 | 16.6076 | 16.6042 | 0.0034
GEN-2019-003 | 05 SOUTHWEST | 526435 | SUNDOWN 6 | 230 | 11.7438 | 11.7376 | 0.0062
GEN-2019-003 | 05 SOUTHWEST | 526935 | YOAKUM 6 | 230 | 19.6825 | 19.6741 | 0.0084
GEN-2019-003 | 05 SOUTHWEST | 527483 | CHAVES_CNTY6 | 230 | 4.4929 | 4.4841 | 0.0088
GEN-2019-003 | 05 SOUTHWEST | 527656 | CROSSROADS 7 | 345 | 11.539 | 11.5267 | 0.0123
GEN-2019-003 | 05 SOUTHWEST | 760498 | G17-146-TAP | 230 | 7.745 | 7.7367 | 0.0083
GEN-2019-003 | 05 SOUTHWEST | 763120 | GEN-2018-081 | 230 | 17.3907 | 17.3363 | 0.0544
GEN-2019-003 | 05 SOUTHWEST | 523097 | HITCHLAND 7 | 345 | 14.9713 | 14.9707 | 0.0006
GEN-2019-003 | 05 SOUTHWEST | 523959 | POTTER_CO 6 | 230 | 22.4376 | 22.4293 | 0.0083
GEN-2019-003 | 05 SOUTHWEST | 524296 | SPNSPUR_WND7 | 345 | 5.3278 | 5.327 | 0.0008
GEN-2019-003 | 05 SOUTHWEST | 524415 | AMA_SOUTH 6 | 230 | 13.6408 | 13.6382 | 0.0026
GEN-2019-003 | 05 SOUTHWEST | 524486 | CAPROCK 3 | 115 | 2.636 | 2.6342 | 0.0018
GEN-2019-003 | 05 SOUTHWEST | 524509 | FE-TUCMCARI3 | 115 | 2.391 | 2.3894 | 0.0016
GEN-2019-003 | 05 SOUTHWEST | 524623 | DEAFSMITH 6 | 230 | 8.0257 | 8.0172 | 0.0085
GEN-2019-003 | 05 SOUTHWEST | 524662 | PARMER_CO 3 | 115 | 5.4666 | 5.4472 | 0.0194
GEN-2019-003 | 05 SOUTHWEST | 524777 | N_CLOVIS 3 | 115 | 6.7428 | 6.6749 | 0.0679
GEN-2019-003 | 05 SOUTHWEST | 524783 | W_CLOVIS 2 | 69 | 2.4403 | 2.4352 | 0.0051
GEN-2019-003 | 05 SOUTHWEST | 524790 | CANNON_TP 3 | 115 | 6.0058 | 5.9497 | 0.0561
GEN-2019-003 | 05 SOUTHWEST | 524801 | NORRIS 3 | 115 | 10.4115 | 10.2591 | 0.1524
GEN-2019-003 | 05 SOUTHWEST | 524808 | FE-CLVS_INT3 | 115 | 6.9498 | 6.8779 | 0.0719
GEN-2019-003 | 05 SOUTHWEST | 524846 | FARWELL 2 | 69 | 2.1357 | 2.1318 | 0.0039
GEN-2019-003 | 05 SOUTHWEST | 524929 | RO-PORT_MTR2 | 69 | 7.5604 | 7.5019 | 0.0585
GEN-2019-003 | 05 SOUTHWEST | 524934 | ZODIAC 2 | 69 | 5.5439 | 5.512 | 0.0319
GEN-2019-003 | 05 SOUTHWEST | 524941 | PORTALES#1 2 | 69 | 5.7509 | 5.7167 | 0.0342
GEN-2019-003 | 05 SOUTHWEST | 524963 | S_PORTALES 3 | 115 | 5.7708 | 5.7136 | 0.0572
GEN-2019-003 | 05 SOUTHWEST | 525019 | MULSHVLY_TP3 | 115 | 5.9489 | 5.937 | 0.0119
GEN-2019-003 | 05 SOUTHWEST | 525027 | BAILEYCO 2 | 69 | 5.2707 | 5.2648 | 0.0059
GEN-2019-003 | 05 SOUTHWEST | 525056 | BC-EARTH 3 | 115 | 8.2606 | 8.255 | 0.0056
GEN-2019-003 | 05 SOUTHWEST | 525212 | SWISHER 3 | 115 | 11.4972 | 11.4938 | 0.0034
GEN-2019-003 | 05 SOUTHWEST | 525446 | RKYFORD_TP 3 | 115 | 10.1267 | 10.1171 | 0.0096
GEN-2019-003 | 05 SOUTHWEST | 525454 | HALE_CNTY 3 | 115 | 10.1608 | 10.1572 | 0.0036
GEN-2019-003 | 05 SOUTHWEST | 525460 | NEWHART 3 | 115 | 14.9423 | 14.9339 | 0.0084
GEN-2019-003 | 05 SOUTHWEST | 525584 | BLUECLDCOL 6 | 230 | 10.4275 | 10.4066 | 0.0209
GEN-2019-003 | 05 SOUTHWEST | 525635 | LAMB_CNTY 2 | 69 | 5.8992 | 5.8972 | 0.002
GEN-2019-003 | 05 SOUTHWEST | 525780 | FLOYD_CNTY 3 | 115 | 6.2514 | 6.2508 | 0.0006
GEN-2019-003 | 05 SOUTHWEST | 525816 | TUCO_INT2 2 | 69 | 4.6524 | 4.6522 | 0.0002
GEN-2019-003 | 05 SOUTHWEST | 525826 | TUCO_INT 2 | 69 | 7.8538 | 7.8532 | 0.0006
GEN-2019-003 | 05 SOUTHWEST | 525850 | ELK_CT1 | 345 | 13.9398 | 13.9352 | 0.0046
GEN-2019-003 | 05 SOUTHWEST | 526020 | HOCKLEY 3 | 115 | 5.426 | 5.4246 | 0.0014
GEN-2019-003 | 05 SOUTHWEST | 526076 | STANTON_W 3 | 115 | 8.923 | 8.9221 | 0.0009
GEN-2019-003 | 05 SOUTHWEST | 526160 | CARLISLE 3 | 115 | 12.772 | 12.7702 | 0.0018
GEN-2019-003 | 05 SOUTHWEST | 526269 | LUBBCK_STH 6 | 230 | 15.0546 | 15.0514 | 0.0032
GEN-2019-003 | 05 SOUTHWEST | 526298 | LUBBCK_EST 3 | 115 | 14.4141 | 14.4123 | 0.0018
GEN-2019-003 | 05 SOUTHWEST | 526299 | LUBBCK_EST 6 | 230 | 11.0462 | 11.0446 | 0.0016
GEN-2019-003 | 05 SOUTHWEST | 526434 | SUNDOWN 3 | 115 | 10.8603 | 10.8577 | 0.0026
GEN-2019-003 | 05 SOUTHWEST | 526460 | AMOCO_SS 6 | 230 | 10.1771 | 10.1728 | 0.0043
GEN-2019-003 | 05 SOUTHWEST | 526525 | WOLFFORTH 6 | 230 | 13.0516 | 13.0472 | 0.0044
GEN-2019-003 | 05 SOUTHWEST | 526677 | GRASSLAND 6 | 230 | 5.9735 | 5.973 | 0.0005
GEN-2019-003 | 05 SOUTHWEST | 526934 | YOAKUM 3 | 115 | 19.2326 | 19.2291 | 0.0035
GEN-2019-003 | 05 SOUTHWEST | 526936 | YOAKUM_345 | 345 | 9.9314 | 9.9275 | 0.0039
GEN-2019-003 | 05 SOUTHWEST | 527009 | BRU_SUB 6 | 230 | 15.6513 | 15.647 | 0.0043
GEN-2019-003 | 05 SOUTHWEST | 527028 | INK_BASIN 6 | 230 | 11.2413 | 11.2389 | 0.0024
GEN-2019-003 | 05 SOUTHWEST | 527149 | MUSTANG 6 | 230 | 17.9238 | 17.92 | 0.0038
GEN-2019-003 | 05 SOUTHWEST | 527482 | CHAVES_CNTY3 | 115 | 7.0492 | 7.0397 | 0.0095
GEN-2019-003 | 05 SOUTHWEST | 527610 | SAGA_SCOL 7 | 345 | 10.2321 | 10.2229 | 0.0092
GEN-2019-003 | 05 SOUTHWEST | 527655 | RSVLT_CC_E 7 | 345 | 10.0154 | 10.0065 | 0.0089
GEN-2019-003 | 05 SOUTHWEST | 527799 | EDDY_NORTH 6 | 230 | 9.402 | 9.3943 | 0.0077
GEN-2019-003 | 05 SOUTHWEST | 527802 | EDDY_CNTY 7 | 345 | 7.3273 | 7.3223 | 0.005
GEN-2019-003 | 05 SOUTHWEST | 527896 | HOBBS_INT 7 | 345 | 12.0143 | 12.0061 | 0.0082
GEN-2019-003 | 05 SOUTHWEST | 560022 | CRAWFISH_DR | 345 | 13.842 | 13.8376 | 0.0044
GEN-2019-003 | 05 SOUTHWEST | 560035 | GRAPEVINE | 345 | 6.4589 | 6.4582 | 0.0007
GEN-2019-003 | 05 SOUTHWEST | 760494 | GEN-2017-146 | 230 | 7.4558 | 7.4481 | 0.0077
GEN-2019-003 | 05 SOUTHWEST | 763186 | GEN-2018-089 | 230 | 10.6882 | 10.6804 | 0.0078
GEN-2019-003 | 05 SOUTHWEST | 511553 | CHISHOLM7 | 345 | 12.3397 | 12.3391 | 0.0006
GEN-2019-003 | 05 SOUTHWEST | 515458 | BORDER 7 | 345 | 8.2517 | 8.2514 | 0.0003
GEN-2019-003 | 05 SOUTHWEST | 515554 | BVRCNTY7 | 345 | 15.3093 | 15.3089 | 0.0004
GEN-2019-003 | 05 SOUTHWEST | 523095 | HITCHLAND 6 | 230 | 14.5761 | 14.5756 | 0.0005
GEN-2019-003 | 05 SOUTHWEST | 523101 | NOBLE_WND 7 | 345 | 14.9103 | 14.9096 | 0.0007
GEN-2019-003 | 05 SOUTHWEST | 523112 | NOVUS1 7 | 345 | 14.6716 | 14.6709 | 0.0007
GEN-2019-003 | 05 SOUTHWEST | 523323 | MCDWL_CREEK6 | 230 | 8.9802 | 8.9792 | 0.001
GEN-2019-003 | 05 SOUTHWEST | 523823 | CARPENTER 7 | 345 | 6.5781 | 6.578 | 0.0001
GEN-2019-003 | 05 SOUTHWEST | 523869 | CHAN+TASCOS6 | 230 | 4.2464 | 4.2462 | 0.0002
GEN-2019-003 | 05 SOUTHWEST | 523979 | HARRNG_EST 6 | 230 | 26.9856 | 26.9787 | 0.0069
GEN-2019-003 | 05 SOUTHWEST | 524010 | ROLLHILLS 6 | 230 | 20.2306 | 20.2256 | 0.005
GEN-2019-003 | 05 SOUTHWEST | 524044 | NICHOLS 6 | 230 | 26.1237 | 26.1174 | 0.0063
GEN-2019-003 | 05 SOUTHWEST | 524267 | BUSHLAND 6 | 230 | 10.1739 | 10.17 | 0.0039
GEN-2019-003 | 05 SOUTHWEST | 524299 | SPNSPUR_COL7 | 345 | 5.3278 | 5.327 | 0.0008
GEN-2019-003 | 05 SOUTHWEST | 524365 | RANDALL 6 | 230 | 14.5681 | 14.5653 | 0.0028
GEN-2019-003 | 05 SOUTHWEST | 524414 | AMA_SOUTH 3 | 115 | 16.9088 | 16.9066 | 0.0022
GEN-2019-003 | 05 SOUTHWEST | 524472 | LOPEZ 3 | 115 | 2.2613 | 2.2599 | 0.0014
GEN-2019-003 | 05 SOUTHWEST | 524619 | DFSMTH_EST 3 | 115 | 11.9939 | 11.9802 | 0.0137
GEN-2019-003 | 05 SOUTHWEST | 524622 | DFSMTH_WST 3 | 115 | 11.9945 | 11.9808 | 0.0137
GEN-2019-003 | 05 SOUTHWEST | 524664 | DS-#24 +3 | 115 | 5.4393 | 5.4214 | 0.0179
GEN-2019-003 | 05 SOUTHWEST | 524746 | CASTRO_CNTY3 | 115 | 9.822 | 9.8167 | 0.0053
GEN-2019-003 | 05 SOUTHWEST | 524784 | W_CLOVIS 3 | 115 | 6.3275 | 6.2667 | 0.0608
GEN-2019-003 | 05 SOUTHWEST | 524794 | CANNONAFB 3 | 115 | 5.6335 | 5.5841 | 0.0494
GEN-2019-003 | 05 SOUTHWEST | 524853 | DS-#10 +2 | 69 | 1.7522 | 1.7516 | 0.0006
GEN-2019-003 | 05 SOUTHWEST | 524948 | PORTALES#2 2 | 69 | 4.8607 | 4.8362 | 0.0245
GEN-2019-003 | 05 SOUTHWEST | 524962 | S_PORTALES 2 | 69 | 4.3137 | 4.2944 | 0.0193
GEN-2019-003 | 05 SOUTHWEST | 525008 | MULESH_CTY 2 | 69 | 4.2533 | 4.2495 | 0.0038
GEN-2019-003 | 05 SOUTHWEST | 525017 | EMULESH&VLY2 | 69 | 4.2591 | 4.2552 | 0.0039
GEN-2019-003 | 05 SOUTHWEST | 525018 | MULESHVALLY3 | 115 | 5.5409 | 5.5305 | 0.0104
GEN-2019-003 | 05 SOUTHWEST | 525023 | BC-BAIL_MTR2 | 69 | 5.2707 | 5.2648 | 0.0059
GEN-2019-003 | 05 SOUTHWEST | 525050 | BC-KELLEY +3 | 115 | 7.782 | 7.7774 | 0.0046
GEN-2019-003 | 05 SOUTHWEST | 525124 | HART_INDUST3 | 115 | 7.4925 | 7.49 | 0.0025
GEN-2019-003 | 05 SOUTHWEST | 525192 | KRESS_INT 3 | 115 | 11.9205 | 11.9167 | 0.0038
GEN-2019-003 | 05 SOUTHWEST | 525326 | COX 3 | 115 | 6.2736 | 6.2726 | 0.001
GEN-2019-003 | 05 SOUTHWEST | 525393 | ROCKYFORD 3 | 115 | 9.0431 | 9.0355 | 0.0076
GEN-2019-003 | 05 SOUTHWEST | 525414 | LAMTON 3 | 115 | 7.6144 | 7.6112 | 0.0032
GEN-2019-003 | 05 SOUTHWEST | 525440 | LC-S_OLTON+3 | 115 | 7.1982 | 7.1946 | 0.0036
GEN-2019-003 | 05 SOUTHWEST | 525453 | HALE_CNTY 2 | 69 | 6.9062 | 6.9052 | 0.001
GEN-2019-003 | 05 SOUTHWEST | 525613 | W_LITTLFLD 2 | 69 | 2.9684 | 2.968 | 0.0004
GEN-2019-003 | 05 SOUTHWEST | 525620 | LTFLD_S&CTY2 | 69 | 4.1727 | 4.1717 | 0.001
GEN-2019-003 | 05 SOUTHWEST | 525650 | LC-LTTLFLD+2 | 69 | 4.9319 | 4.9305 | 0.0014
GEN-2019-003 | 05 SOUTHWEST | 525687 | LC-LUMSCHAP2 | 69 | 4.6126 | 4.6114 | 0.0012
GEN-2019-003 | 05 SOUTHWEST | 525731 | SP-ABERNTHY2 | 69 | 3.0093 | 3.0092 | 0.0001
GEN-2019-003 | 05 SOUTHWEST | 525738 | HALECENTER 2 | 69 | 2.4566 | 2.4565 | 0.0001
GEN-2019-003 | 05 SOUTHWEST | 525763 | CALLAHAN 3 | 115 | 5.5668 | 5.5662 | 0.0006
GEN-2019-003 | 05 SOUTHWEST | 525779 | FLOYD_CNTY 2 | 69 | 5.401 | 5.4008 | 0.0002
GEN-2019-003 | 05 SOUTHWEST | 525803 | BLANCO 3 | 115 | 5.0451 | 5.0448 | 0.0003
GEN-2019-003 | 05 SOUTHWEST | 525853 | LH-WIL&ELN+2 | 69 | 2.5404 | 2.5404 | 0
GEN-2019-003 | 05 SOUTHWEST | 525885 | SP-NEWDEAL 2 | 69 | 3.3073 | 3.3072 | 0.0001
GEN-2019-003 | 05 SOUTHWEST | 525926 | CROSBY 3 | 115 | 4.7129 | 4.7127 | 0.0002
GEN-2019-003 | 05 SOUTHWEST | 526019 | HOCKLEY 2 | 69 | 5.1105 | 5.1098 | 0.0007
GEN-2019-003 | 05 SOUTHWEST | 526036 | LC-OPDYKE 3 | 115 | 5.7143 | 5.7129 | 0.0014
GEN-2019-003 | 05 SOUTHWEST | 526109 | SP-ERSKINE 3 | 115 | 10.9787 | 10.9773 | 0.0014
GEN-2019-003 | 05 SOUTHWEST | 526146 | INDIANA 3 | 115 | 9.3032 | 9.3022 | 0.001
GEN-2019-003 | 05 SOUTHWEST | 526159 | CARLISLE 2 | 69 | 2.5568 | 2.5568 | 0
GEN-2019-003 | 05 SOUTHWEST | 526162 | LP-DOUD_TP 3 | 115 | 11.325 | 11.3235 | 0.0015
GEN-2019-003 | 05 SOUTHWEST | 526192 | MURPHY 3 | 115 | 10.2503 | 10.2492 | 0.0011
GEN-2019-003 | 05 SOUTHWEST | 526268 | LUBBCK_STH 3 | 115 | 17.6482 | 17.6457 | 0.0025
GEN-2019-003 | 05 SOUTHWEST | 526297 | LUBBCK_EST 2 | 69 | 7.8955 | 7.8952 | 0.0003
GEN-2019-003 | 05 SOUTHWEST | 526424 | PACIFIC 3 | 115 | 9.1771 | 9.1753 | 0.0018
GEN-2019-003 | 05 SOUTHWEST | 526445 | AMOCO_TP 3 | 115 | 10.1845 | 10.1822 | 0.0023
GEN-2019-003 | 05 SOUTHWEST | 526524 | WOLFFORTH 3 | 115 | 11.2819 | 11.2804 | 0.0015
GEN-2019-003 | 05 SOUTHWEST | 526676 | GRASSLAND 3 | 115 | 6.8633 | 6.863 | 0.0003
GEN-2019-003 | 05 SOUTHWEST | 526679 | CIRRUS_WND 6 | 230 | 4.6792 | 4.679 | 0.0002
GEN-2019-003 | 05 SOUTHWEST | 526784 | AMOCOWASSON6 | 230 | 15.6353 | 15.6319 | 0.0034
GEN-2019-003 | 05 SOUTHWEST | 526792 | PRENTICE 3 | 115 | 6.0286 | 6.0283 | 0.0003
GEN-2019-003 | 05 SOUTHWEST | 526928 | PLAINS_INT 3 | 115 | 10.0196 | 10.0186 | 0.001
GEN-2019-003 | 05 SOUTHWEST | 527010 | OXYBRU 6 | 230 | 15.5052 | 15.5009 | 0.0043
GEN-2019-003 | 05 SOUTHWEST | 527011 | XTO_MAHONEY6 | 230 | 15.3578 | 15.3539 | 0.0039
GEN-2019-003 | 05 SOUTHWEST | 527027 | INK_BASIN 3 | 115 | 13.258 | 13.2568 | 0.0012
GEN-2019-003 | 05 SOUTHWEST | 527041 | ARCO_TP 3 | 115 | 13.6807 | 13.6794 | 0.0013
GEN-2019-003 | 05 SOUTHWEST | 527146 | MUSTANG 3 | 115 | 24.0628 | 24.0599 | 0.0029
GEN-2019-003 | 05 SOUTHWEST | 527151 | GS-MUSTANG 6 | 230 | 17.9238 | 17.92 | 0.0038
GEN-2019-003 | 05 SOUTHWEST | 527194 | LG-PLSHILL 3 | 115 | 7.9741 | 7.9737 | 0.0004
GEN-2019-003 | 05 SOUTHWEST | 527276 | SEMINOLE 6 | 230 | 8.197 | 8.1963 | 0.0007
GEN-2019-003 | 05 SOUTHWEST | 527455 | RSWL_SLRCOL3 | 115 | 6.9796 | 6.9703 | 0.0093
GEN-2019-003 | 05 SOUTHWEST | 527470 | CHVS_SLRCOL3 | 115 | 6.816 | 6.8071 | 0.0089
GEN-2019-003 | 05 SOUTHWEST | 527501 | URTON 3 | 115 | 5.8725 | 5.8662 | 0.0063
GEN-2019-003 | 05 SOUTHWEST | 527509 | PRICE_TAP 3 | 115 | 5.4519 | 5.4463 | 0.0056
GEN-2019-003 | 05 SOUTHWEST | 527546 | SAMSON 3 | 115 | 5.515 | 5.5095 | 0.0055
GEN-2019-003 | 05 SOUTHWEST | 527599 | SAGA_SDCOL 7 | 345 | 10.2321 | 10.2229 | 0.0092
GEN-2019-003 | 05 SOUTHWEST | 527654 | RSVLT_CC_W 7 | 345 | 8.7265 | 8.72 | 0.0065
GEN-2019-003 | 05 SOUTHWEST | 527793 | EDDY_STH 3 | 115 | 11.9559 | 11.9494 | 0.0065
GEN-2019-003 | 05 SOUTHWEST | 527798 | EDDY_NTH 3 | 115 | 11.9559 | 11.9494 | 0.0065
GEN-2019-003 | 05 SOUTHWEST | 527865 | CUNNIGHM_N 6 | 230 | 17.5364 | 17.5304 | 0.006
GEN-2019-003 | 05 SOUTHWEST | 527894 | HOBBS_INT 6 | 230 | 19.4767 | 19.4693 | 0.0074
GEN-2019-003 | 05 SOUTHWEST | 527965 | KIOWA 7 | 345 | 8.82 | 8.8146 | 0.0054
GEN-2019-003 | 05 SOUTHWEST | 528027 | RDRUNNER 7 | 345 | 8.6815 | 8.677 | 0.0045
GEN-2019-003 | 05 SOUTHWEST | 528095 | 7-RIVERS 6 | 230 | 6.3874 | 6.3846 | 0.0028
GEN-2019-003 | 05 SOUTHWEST | 560756 | CEILO-TAP-N | 115 | 0.4601 | 0.4601 | 0
GEN-2019-003 | 05 SOUTHWEST | 576397 | G10014G11022 | 345 | 10.3812 | 10.381 | 0.0002
GEN-2019-003 | 05 SOUTHWEST | 583280 | A12-02&13-05 | 115 | 1.0409 | 1.0403 | 0.0006
GEN-2019-003 | 05 SOUTHWEST | 599960 | EPTNP-D6 | 230 | 9.402 | 9.3943 | 0.0077
GEN-2019-003 | 05 SOUTHWEST | 762216 | G17-151TAP | 345 | 8.5119 | 8.5107 | 0.0012
GEN-2019-003 | 05 SOUTHWEST | 763087 | GEN-2018-073 | 345 | 11.9423 | 11.9391 | 0.0032
GEN-2019-003 | 05 SOUTHWEST | 763516 | GEN-2019-011 | 345 | 9.2852 | 9.2818 | 0.0034
GEN-2019-011 | 05 SOUTHWEST | 526936 | YOAKUM_345 | 345 | 9.9314 | 9.9314 | 0
GEN-2019-011 | 05 SOUTHWEST | 525832 | TUCO_INT 7 | 345 | 14.0745 | 14.0745 | 0
GEN-2019-011 | 05 SOUTHWEST | 526935 | YOAKUM 6 | 230 | 19.6825 | 19.6825 | 0
GEN-2019-011 | 05 SOUTHWEST | 527896 | HOBBS_INT 7 | 345 | 12.0143 | 12.0143 | 0
GEN-2019-011 | 05 SOUTHWEST | 763516 | GEN-2019-011 | 345 | 9.2852 | 9.2852 | 0
GEN-2019-011 | 05 SOUTHWEST | 525586 | NEEDMORE 6 | 230 | 11.0214 | 11.0214 | 0
GEN-2019-011 | 05 SOUTHWEST | 525830 | TUCO_INT 6 | 230 | 21.9895 | 21.9895 | 0
GEN-2019-011 | 05 SOUTHWEST | 525850 | ELK_CT1 | 345 | 13.9398 | 13.9398 | 0
GEN-2019-011 | 05 SOUTHWEST | 526460 | AMOCO_SS 6 | 230 | 10.1771 | 10.1771 | 0
GEN-2019-011 | 05 SOUTHWEST | 526934 | YOAKUM 3 | 115 | 19.2326 | 19.2326 | 0
GEN-2019-011 | 05 SOUTHWEST | 527009 | BRU_SUB 6 | 230 | 15.6513 | 15.6513 | 0
GEN-2019-011 | 05 SOUTHWEST | 527028 | INK_BASIN 6 | 230 | 11.2413 | 11.2413 | 0
GEN-2019-011 | 05 SOUTHWEST | 527149 | MUSTANG 6 | 230 | 17.9238 | 17.9238 | 0
GEN-2019-011 | 05 SOUTHWEST | 527656 | CROSSROADS 7 | 345 | 11.539 | 11.539 | 0
GEN-2019-011 | 05 SOUTHWEST | 527894 | HOBBS_INT 6 | 230 | 19.4767 | 19.4767 | 0
GEN-2019-011 | 05 SOUTHWEST | 527965 | KIOWA 7 | 345 | 8.82 | 8.82 | 0
GEN-2019-011 | 05 SOUTHWEST | 528027 | RDRUNNER 7 | 345 | 8.6815 | 8.6815 | 0
GEN-2019-011 | 05 SOUTHWEST | 560022 | CRAWFISH_DR | 345 | 13.842 | 13.842 | 0
GEN-2019-011 | 05 SOUTHWEST | 515458 | BORDER 7 | 345 | 8.2517 | 8.2517 | 0
GEN-2019-011 | 05 SOUTHWEST | 525213 | SWISHER 6 | 230 | 10.3853 | 10.3853 | 0
GEN-2019-011 | 05 SOUTHWEST | 525531 | TOLK 6 | 230 | 31.4946 | 31.4946 | 0
GEN-2019-011 | 05 SOUTHWEST | 525549 | TOLK 7 | 345 | 15.0276 | 15.0276 | 0
GEN-2019-011 | 05 SOUTHWEST | 525585 | BLUECLDPOI 6 | 230 | 11.0214 | 11.0214 | 0
GEN-2019-011 | 05 SOUTHWEST | 525828 | TUCO_INT 3 | 115 | 19.3618 | 19.3618 | 0
GEN-2019-011 | 05 SOUTHWEST | 525840 | ANTELOPE_1 6 | 230 | 21.8013 | 21.8013 | 0
GEN-2019-011 | 05 SOUTHWEST | 525957 | HALE_WNDCL16 | 230 | 10.5196 | 10.5196 | 0
GEN-2019-011 | 05 SOUTHWEST | 526161 | CARLISLE 6 | 230 | 10.473 | 10.473 | 0
GEN-2019-011 | 05 SOUTHWEST | 526337 | JONES 6 | 230 | 16.6076 | 16.6076 | 0
GEN-2019-011 | 05 SOUTHWEST | 526435 | SUNDOWN 6 | 230 | 11.7438 | 11.7438 | 0
GEN-2019-011 | 05 SOUTHWEST | 526784 | AMOCOWASSON6 | 230 | 15.6353 | 15.6353 | 0
GEN-2019-011 | 05 SOUTHWEST | 526792 | PRENTICE 3 | 115 | 6.0286 | 6.0286 | 0
GEN-2019-011 | 05 SOUTHWEST | 526928 | PLAINS_INT 3 | 115 | 10.0196 | 10.0196 | 0
GEN-2019-011 | 05 SOUTHWEST | 527010 | OXYBRU 6 | 230 | 15.5052 | 15.5052 | 0
GEN-2019-011 | 05 SOUTHWEST | 527011 | XTO_MAHONEY6 | 230 | 15.3578 | 15.3578 | 0
GEN-2019-011 | 05 SOUTHWEST | 527027 | INK_BASIN 3 | 115 | 13.258 | 13.258 | 0
GEN-2019-011 | 05 SOUTHWEST | 527041 | ARCO_TP 3 | 115 | 13.6807 | 13.6807 | 0
GEN-2019-011 | 05 SOUTHWEST | 527146 | MUSTANG 3 | 115 | 24.0628 | 24.0628 | 0
GEN-2019-011 | 05 SOUTHWEST | 527151 | GS-MUSTANG 6 | 230 | 17.9238 | 17.9238 | 0
GEN-2019-011 | 05 SOUTHWEST | 527194 | LG-PLSHILL 3 | 115 | 7.9741 | 7.9741 | 0
GEN-2019-011 | 05 SOUTHWEST | 527276 | SEMINOLE 6 | 230 | 8.197 | 8.197 | 0
GEN-2019-011 | 05 SOUTHWEST | 527610 | SAGA_SCOL 7 | 345 | 10.2321 | 10.2321 | 0
GEN-2019-011 | 05 SOUTHWEST | 527655 | RSVLT_CC_E 7 | 345 | 10.0154 | 10.0154 | 0
GEN-2019-011 | 05 SOUTHWEST | 527802 | EDDY_CNTY 7 | 345 | 7.3273 | 7.3273 | 0
GEN-2019-011 | 05 SOUTHWEST | 527867 | CUNNIGHM_S 6 | 230 | 17.5364 | 17.5364 | 0
GEN-2019-011 | 05 SOUTHWEST | 527891 | HOBBS_INT 3 | 115 | 33.0667 | 33.0667 | 0
GEN-2019-011 | 05 SOUTHWEST | 527966 | KIOWA 3 | 115 | 17.1508 | 17.1508 | 0
GEN-2019-011 | 05 SOUTHWEST | 528015 | PHANTOM 7 | 345 | 5.675 | 5.675 | 0
GEN-2019-011 | 05 SOUTHWEST | 528025 | RDRUNNER 3 | 115 | 13.7957 | 13.7957 | 0
GEN-2019-011 | 05 SOUTHWEST | 528185 | N_LOVING 7 | 345 | 6.5496 | 6.5496 | 0
GEN-2019-011 | 05 SOUTHWEST | 528604 | ANDREWS 6 | 230 | 6.0764 | 6.0764 | 0
GEN-2019-011 | 05 SOUTHWEST | 762216 | G17-151TAP | 345 | 8.5119 | 8.5119 | 0
GEN-2019-011 | 05 SOUTHWEST | 763087 | GEN-2018-073 | 345 | 11.9423 | 11.9423 | 0
GEN-2019-011 | 05 SOUTHWEST | 523961 | POTTER_CO 7 | 345 | 11.6631 | 11.6631 | 0
GEN-2019-011 | 05 SOUTHWEST | 524415 | AMA_SOUTH 6 | 230 | 13.6408 | 13.6408 | 0
GEN-2019-011 | 05 SOUTHWEST | 524909 | ROOSEVELT 6 | 230 | 9.709 | 9.709 | 0
GEN-2019-011 | 05 SOUTHWEST | 525212 | SWISHER 3 | 115 | 11.4972 | 11.4972 | 0
GEN-2019-011 | 05 SOUTHWEST | 525454 | HALE_CNTY 3 | 115 | 10.1608 | 10.1608 | 0
GEN-2019-011 | 05 SOUTHWEST | 525461 | NEWHART 6 | 230 | 10.9971 | 10.9971 | 0
GEN-2019-011 | 05 SOUTHWEST | 525481 | PLANT_X 6 | 230 | 24.1838 | 24.1838 | 0
GEN-2019-011 | 05 SOUTHWEST | 525584 | BLUECLDCOL 6 | 230 | 10.4275 | 10.4275 | 0
GEN-2019-011 | 05 SOUTHWEST | 525637 | LAMB_CNTY 6 | 230 | 5.4027 | 5.4027 | 0
GEN-2019-011 | 05 SOUTHWEST | 525780 | FLOYD_CNTY 3 | 115 | 6.2514 | 6.2514 | 0
GEN-2019-011 | 05 SOUTHWEST | 525816 | TUCO_INT2 2 | 69 | 4.6524 | 4.6524 | 0
GEN-2019-011 | 05 SOUTHWEST | 525826 | TUCO_INT 2 | 69 | 7.8538 | 7.8538 | 0
GEN-2019-011 | 05 SOUTHWEST | 526076 | STANTON_W 3 | 115 | 8.923 | 8.923 | 0
GEN-2019-011 | 05 SOUTHWEST | 526160 | CARLISLE 3 | 115 | 12.772 | 12.772 | 0
GEN-2019-011 | 05 SOUTHWEST | 526269 | LUBBCK_STH 6 | 230 | 15.0546 | 15.0546 | 0
GEN-2019-011 | 05 SOUTHWEST | 526298 | LUBBCK_EST 3 | 115 | 14.4141 | 14.4141 | 0
GEN-2019-011 | 05 SOUTHWEST | 526299 | LUBBCK_EST 6 | 230 | 11.0462 | 11.0462 | 0
GEN-2019-011 | 05 SOUTHWEST | 526434 | SUNDOWN 3 | 115 | 10.8603 | 10.8603 | 0
GEN-2019-011 | 05 SOUTHWEST | 526525 | WOLFFORTH 6 | 230 | 13.0516 | 13.0516 | 0
GEN-2019-011 | 05 SOUTHWEST | 526677 | GRASSLAND 6 | 230 | 5.9735 | 5.9735 | 0
GEN-2019-011 | 05 SOUTHWEST | 526736 | TERRY_CNTY 3 | 115 | 10.6679 | 10.6679 | 0
GEN-2019-011 | 05 SOUTHWEST | 526944 | LG-PLAINS 3 | 115 | 7.9013 | 7.9013 | 0
GEN-2019-011 | 05 SOUTHWEST | 527018 | BENNETT 3 | 115 | 13.7758 | 13.7758 | 0
GEN-2019-011 | 05 SOUTHWEST | 527030 | ALRDCRTZ_TP3 | 115 | 12.2915 | 12.2915 | 0
GEN-2019-011 | 05 SOUTHWEST | 527047 | OXY_WILRD1 3 | 115 | 10.8936 | 10.8936 | 0
GEN-2019-011 | 05 SOUTHWEST | 527062 | SHELL_CO2 3 | 115 | 16.7017 | 16.7017 | 0
GEN-2019-011 | 05 SOUTHWEST | 527130 | DENVER_N 3 | 115 | 22.5277 | 22.5277 | 0
GEN-2019-011 | 05 SOUTHWEST | 527136 | DENVER_S 3 | 115 | 22.5277 | 22.5277 | 0
GEN-2019-011 | 05 SOUTHWEST | 527202 | SEAGRAVES 3 | 115 | 9.1786 | 9.1786 | 0
GEN-2019-011 | 05 SOUTHWEST | 527275 | SEMINOLE 3 | 115 | 14.6609 | 14.6609 | 0
GEN-2019-011 | 05 SOUTHWEST | 527599 | SAGA_SDCOL 7 | 345 | 10.2321 | 10.2321 | 0
GEN-2019-011 | 05 SOUTHWEST | 527654 | RSVLT_CC_W 7 | 345 | 8.7265 | 8.7265 | 0
GEN-2019-011 | 05 SOUTHWEST | 527799 | EDDY_NORTH 6 | 230 | 9.402 | 9.402 | 0
GEN-2019-011 | 05 SOUTHWEST | 527864 | CUNNINHAM 3 | 115 | 28.6112 | 28.6112 | 0
GEN-2019-011 | 05 SOUTHWEST | 527865 | CUNNIGHM_N 6 | 230 | 17.5364 | 17.5364 | 0
GEN-2019-011 | 05 SOUTHWEST | 527962 | POTASH_JCT 3 | 115 | 17.1771 | 17.1771 | 0
GEN-2019-011 | 05 SOUTHWEST | 528013 | PHANTOM 3 | 115 | 13.0934 | 13.0934 | 0
GEN-2019-011 | 05 SOUTHWEST | 528018 | RED_BLUFF 3 | 115 | 10.2086 | 10.2086 | 0
GEN-2019-011 | 05 SOUTHWEST | 528024 | RR_SVC_HV 3 | 115 | 13.7957 | 13.7957 | 0
GEN-2019-011 | 05 SOUTHWEST | 528040 | BATTLE_AXE 3 | 115 | 3.2123 | 3.2123 | 0
GEN-2019-011 | 05 SOUTHWEST | 528182 | NORTH_LOVNG3 | 115 | 12.4183 | 12.4183 | 0
GEN-2019-011 | 05 SOUTHWEST | 528223 | CHINA_DRAW 7 | 345 | 5.8229 | 5.8229 | 0
GEN-2019-011 | 05 SOUTHWEST | 528230 | AGAVE_RHILL3 | 115 | 12.3643 | 12.3643 | 0
GEN-2019-011 | 05 SOUTHWEST | 528231 | AGAVE_RHIL23 | 115 | 11.6311 | 11.6311 | 0
GEN-2019-011 | 05 SOUTHWEST | 528239 | CUSTERMTN 3 | 115 | 7.7101 | 7.7101 | 0
GEN-2019-011 | 05 SOUTHWEST | 528325 | LE-WAITS 3 | 115 | 8.9967 | 8.9967 | 0
GEN-2019-011 | 05 SOUTHWEST | 528333 | LE-WEST_SUB3 | 115 | 8.9508 | 8.9508 | 0
GEN-2019-011 | 05 SOUTHWEST | 528355 | MADDOX 3 | 115 | 27.5212 | 27.5212 | 0
GEN-2019-011 | 05 SOUTHWEST | 528433 | BENSING 3 | 115 | 8.0843 | 8.0843 | 0
GEN-2019-011 | 05 SOUTHWEST | 528434 | MILLEN_TPW 3 | 115 | 11.851 | 11.851 | 0
GEN-2019-011 | 05 SOUTHWEST | 528602 | ANDREWS 3 | 115 | 9.8058 | 9.8058 | 0
GEN-2019-011 | 05 SOUTHWEST | 528626 | LE-PLNSINT 2 | 69 | 3.6375 | 3.6375 | 0
GEN-2019-011 | 05 SOUTHWEST | 587990 | GEN-2016-121 | 115 | 13.5705 | 13.5705 | 0
GEN-2019-011 | 05 SOUTHWEST | 588460 | A16-008SUB | 115 | 13.258 | 13.258 | 0
GEN-2019-011 | 05 SOUTHWEST | 755000 | WWDBORDT | 345 | 12.2648 | 12.2648 | 0
GEN-2019-011 | 05 SOUTHWEST | 761355 | GEN-2017-239 | 230 | 13.7988 | 13.7988 | 0
GEN-2019-011 | 05 SOUTHWEST | 762132 | GEN-2017-158 | 230 | 13.8646 | 13.8646 | 0
GEN-2019-011 | 05 SOUTHWEST | 762217 | GEN-2017-151 | 345 | 6.1754 | 6.1754 | 0
GEN-2019-011 | 05 SOUTHWEST | 762467 | G18-015-TAP | 345 | 5.8242 | 5.8242 | 0
GEN-2019-011 | 05 SOUTHWEST | 763241 | GEN-2018-097 | 230 | 24.4484 | 24.4484 | 0
GEN-2019-011 | 05 SOUTHWEST | 511553 | CHISHOLM7 | 345 | 12.3397 | 12.3397 | 0
GEN-2019-011 | 05 SOUTHWEST | 515375 | WWRDEHV7 | 345 | 22.3641 | 22.3641 | 0
GEN-2019-011 | 05 SOUTHWEST | 523097 | HITCHLAND 7 | 345 | 14.9713 | 14.9713 | 0
GEN-2019-011 | 05 SOUTHWEST | 523959 | POTTER_CO 6 | 230 | 22.4376 | 22.4376 | 0
GEN-2019-011 | 05 SOUTHWEST | 524044 | NICHOLS 6 | 230 | 26.1237 | 26.1237 | 0
GEN-2019-011 | 05 SOUTHWEST | 524296 | SPNSPUR_WND7 | 345 | 5.3278 | 5.3278 | 0
GEN-2019-011 | 05 SOUTHWEST | 524365 | RANDALL 6 | 230 | 14.5681 | 14.5681 | 0
GEN-2019-011 | 05 SOUTHWEST | 524414 | AMA_SOUTH 3 | 115 | 16.9088 | 16.9088 | 0
GEN-2019-011 | 05 SOUTHWEST | 524770 | PLSNT_HILL 6 | 230 | 6.517 | 6.517 | 0
GEN-2019-011 | 05 SOUTHWEST | 524875 | OASIS 6 | 230 | 7.8784 | 7.8784 | 0
GEN-2019-011 | 05 SOUTHWEST | 524908 | ROOSEVELT 3 | 115 | 11.1454 | 11.1454 | 0
GEN-2019-011 | 05 SOUTHWEST | 525192 | KRESS_INT 3 | 115 | 11.9205 | 11.9205 | 0
GEN-2019-011 | 05 SOUTHWEST | 525326 | COX 3 | 115 | 6.2736 | 6.2736 | 0
GEN-2019-011 | 05 SOUTHWEST | 525414 | LAMTON 3 | 115 | 7.6144 | 7.6144 | 0
GEN-2019-011 | 05 SOUTHWEST | 525453 | HALE_CNTY 2 | 69 | 6.9062 | 6.9062 | 0
GEN-2019-011 | 05 SOUTHWEST | 525460 | NEWHART 3 | 115 | 14.9423 | 14.9423 | 0
GEN-2019-011 | 05 SOUTHWEST | 525480 | PLANT_X 3 | 115 | 19.2796 | 19.2796 | 0
GEN-2019-011 | 05 SOUTHWEST | 525636 | LAMB_CNTY 3 | 115 | 8.4389 | 8.4389 | 0
GEN-2019-011 | 05 SOUTHWEST | 525731 | SP-ABERNTHY2 | 69 | 3.0093 | 3.0093 | 0
GEN-2019-011 | 05 SOUTHWEST | 525738 | HALECENTER 2 | 69 | 2.4566 | 2.4566 | 0
GEN-2019-011 | 05 SOUTHWEST | 525763 | CALLAHAN 3 | 115 | 5.5668 | 5.5668 | 0
GEN-2019-011 | 05 SOUTHWEST | 525779 | FLOYD_CNTY 2 | 69 | 5.401 | 5.401 | 0
GEN-2019-011 | 05 SOUTHWEST | 525803 | BLANCO 3 | 115 | 5.0451 | 5.0451 | 0
GEN-2019-011 | 05 SOUTHWEST | 525853 | LH-WIL&ELN+2 | 69 | 2.5404 | 2.5404 | 0
GEN-2019-011 | 05 SOUTHWEST | 525885 | SP-NEWDEAL 2 | 69 | 3.3073 | 3.3073 | 0
GEN-2019-011 | 05 SOUTHWEST | 525926 | CROSBY 3 | 115 | 4.7129 | 4.7129 | 0
GEN-2019-011 | 05 SOUTHWEST | 526036 | LC-OPDYKE 3 | 115 | 5.7143 | 5.7143 | 0
GEN-2019-011 | 05 SOUTHWEST | 526109 | SP-ERSKINE 3 | 115 | 10.9787 | 10.9787 | 0
GEN-2019-011 | 05 SOUTHWEST | 526146 | INDIANA 3 | 115 | 9.3032 | 9.3032 | 0
GEN-2019-011 | 05 SOUTHWEST | 526159 | CARLISLE 2 | 69 | 2.5568 | 2.5568 | 0
GEN-2019-011 | 05 SOUTHWEST | 526162 | LP-DOUD_TP 3 | 115 | 11.325 | 11.325 | 0
GEN-2019-011 | 05 SOUTHWEST | 526192 | MURPHY 3 | 115 | 10.2503 | 10.2503 | 0
GEN-2019-011 | 05 SOUTHWEST | 526268 | LUBBCK_STH 3 | 115 | 17.6482 | 17.6482 | 0
GEN-2019-011 | 05 SOUTHWEST | 526297 | LUBBCK_EST 2 | 69 | 7.8955 | 7.8955 | 0
GEN-2019-011 | 05 SOUTHWEST | 526350 | LEHMAN_TP 3 | 115 | 5.4556 | 5.4556 | 0
GEN-2019-011 | 05 SOUTHWEST | 526424 | PACIFIC 3 | 115 | 9.1771 | 9.1771 | 0
GEN-2019-011 | 05 SOUTHWEST | 526445 | AMOCO_TP 3 | 115 | 10.1845 | 10.1845 | 0
GEN-2019-011 | 05 SOUTHWEST | 526491 | LG-CLAUENE 3 | 115 | 7.9267 | 7.9267 | 0
GEN-2019-011 | 05 SOUTHWEST | 526524 | WOLFFORTH 3 | 115 | 11.2819 | 11.2819 | 0
GEN-2019-011 | 05 SOUTHWEST | 526676 | GRASSLAND 3 | 115 | 6.8633 | 6.8633 | 0
GEN-2019-011 | 05 SOUTHWEST | 526679 | CIRRUS_WND 6 | 230 | 4.6792 | 4.6792 | 0
GEN-2019-011 | 05 SOUTHWEST | 526735 | TERRY_CNTY 2 | 69 | 7.0347 | 7.0347 | 0
GEN-2019-011 | 05 SOUTHWEST | 527024 | ALLRED_SUB 3 | 115 | 10.7765 | 10.7765 | 0
GEN-2019-011 | 05 SOUTHWEST | 527033 | XTO_CORNEL+3 | 115 | 12.4096 | 12.4096 | 0
GEN-2019-011 | 05 SOUTHWEST | 527036 | SHELL_C2 3 | 115 | 14.8515 | 14.8515 | 0
GEN-2019-011 | 05 SOUTHWEST | 527051 | ODC_TP 3 | 115 | 13.7922 | 13.7922 | 0
GEN-2019-011 | 05 SOUTHWEST | 527080 | EL_PASO 3 | 115 | 16.4487 | 16.4487 | 0
GEN-2019-011 | 05 SOUTHWEST | 527105 | SAN_ANDS_TP3 | 115 | 17.3939 | 17.3939 | 0
GEN-2019-011 | 05 SOUTHWEST | 527125 | DENVER_CTY 2 | 69 | 8.7911 | 8.7911 | 0
GEN-2019-011 | 05 SOUTHWEST | 527201 | SEAGRAVES 2 | 69 | 5.5462 | 5.5462 | 0
GEN-2019-011 | 05 SOUTHWEST | 527238 | ROZ 3 | 115 | 11.2923 | 11.2923 | 0
GEN-2019-011 | 05 SOUTHWEST | 527242 | AMERADA 3 | 115 | 11.4487 | 11.4487 | 0
GEN-2019-011 | 05 SOUTHWEST | 527257 | FLATLAND 3 | 115 | 6.6733 | 6.6733 | 0
GEN-2019-011 | 05 SOUTHWEST | 527286 | HIGGEAST 3 | 115 | 10.2075 | 10.2075 | 0
GEN-2019-011 | 05 SOUTHWEST | 527322 | GAINES 3 | 115 | 9.4721 | 9.4721 | 0
GEN-2019-011 | 05 SOUTHWEST | 527340 | DOSS 3 | 115 | 8.061 | 8.061 | 0
GEN-2019-011 | 05 SOUTHWEST | 527363 | HIGG 3 | 115 | 10.3839 | 10.3839 | 0
GEN-2019-011 | 05 SOUTHWEST | 527483 | CHAVES_CNTY6 | 230 | 4.4929 | 4.4929 | 0
GEN-2019-011 | 05 SOUTHWEST | 527600 | SAGA_SMEAS 7 | 345 | 10.2321 | 10.2321 | 0
GEN-2019-011 | 05 SOUTHWEST | 527666 | RSVLT_COL1 7 | 345 | 8.7265 | 8.7265 | 0
GEN-2019-011 | 05 SOUTHWEST | 527667 | RSVLT_COL2 7 | 345 | 8.7265 | 8.7265 | 0
GEN-2019-011 | 05 SOUTHWEST | 527793 | EDDY_STH 3 | 115 | 11.9559 | 11.9559 | 0
GEN-2019-011 | 05 SOUTHWEST | 527798 | EDDY_NTH 3 | 115 | 11.9559 | 11.9559 | 0
GEN-2019-011 | 05 SOUTHWEST | 527930 | PCA 3 | 115 | 11.9796 | 11.9796 | 0
GEN-2019-011 | 05 SOUTHWEST | 527961 | POTASH_JCT 2 | 69 | 9.8622 | 9.8622 | 0
GEN-2019-011 | 05 SOUTHWEST | 527963 | POTASH_JCT 6 | 230 | 7.464 | 7.464 | 0
GEN-2019-011 | 05 SOUTHWEST | 527999 | INTREPDW_TP3 | 115 | 13.9612 | 13.9612 | 0
GEN-2019-011 | 05 SOUTHWEST | 528016 | SAND_DUNES 3 | 115 | 7.446 | 7.446 | 0
GEN-2019-011 | 05 SOUTHWEST | 528020 | BOPCO_PKRLK3 | 115 | 12.8865 | 12.8865 | 0
GEN-2019-011 | 05 SOUTHWEST | 528095 | 7-RIVERS 6 | 230 | 6.3874 | 6.3874 | 0
GEN-2019-011 | 05 SOUTHWEST | 528160 | CARLSBAD 3 | 115 | 11.3979 | 11.3979 | 0
GEN-2019-011 | 05 SOUTHWEST | 528192 | SOUTH_LOVNG3 | 115 | 9.379 | 9.379 | 0
GEN-2019-011 | 05 SOUTHWEST | 528193 | BLACKRIVER 3 | 115 | 10.2994 | 10.2994 | 0
GEN-2019-011 | 05 SOUTHWEST | 528194 | MALAGABEND 3 | 115 | 7.8968 | 7.8968 | 0
GEN-2019-011 | 05 SOUTHWEST | 528195 | AGAVE_PDURO3 | 115 | 8.0375 | 8.0375 | 0
GEN-2019-011 | 05 SOUTHWEST | 528222 | CHINA_DRAW 3 | 115 | 10.9978 | 10.9978 | 0
GEN-2019-011 | 05 SOUTHWEST | 528226 | HOPI_SUB 3 | 115 | 7.3063 | 7.3063 | 0
GEN-2019-011 | 05 SOUTHWEST | 528228 | WOOD_DRAW 3 | 115 | 8.2129 | 8.2129 | 0
GEN-2019-011 | 05 SOUTHWEST | 528232 | OCHOA 3 | 115 | 11.687 | 11.687 | 0
GEN-2019-011 | 05 SOUTHWEST | 528235 | WOLFCAMP_TP3 | 115 | 12.1779 | 12.1779 | 0
GEN-2019-011 | 05 SOUTHWEST | 528240 | PONDEROSA 3 | 115 | 4.0499 | 4.0499 | 0
GEN-2019-011 | 05 SOUTHWEST | 528334 | LE-NRTH_INT3 | 115 | 8.8908 | 8.8908 | 0
GEN-2019-011 | 05 SOUTHWEST | 528348 | BUCKEYE_TP 3 | 115 | 8.2953 | 8.2953 | 0
GEN-2019-011 | 05 SOUTHWEST | 528353 | MADDOXG23 3 | 115 | 27.5212 | 27.5212 | 0
GEN-2019-011 | 05 SOUTHWEST | 528392 | PEARLE 3 | 115 | 6.3678 | 6.3678 | 0
GEN-2019-011 | 05 SOUTHWEST | 528394 | QUAHADA 3 | 115 | 8.071 | 8.071 | 0
GEN-2019-011 | 05 SOUTHWEST | 528435 | MILLEN 3 | 115 | 11.851 | 11.851 | 0
GEN-2019-011 | 05 SOUTHWEST | 528436 | MILLEN_TPE 3 | 115 | 11.851 | 11.851 | 0
GEN-2019-011 | 05 SOUTHWEST | 528491 | MONUMENT 3 | 115 | 15.8502 | 15.8502 | 0
GEN-2019-011 | 05 SOUTHWEST | 528540 | WHITTEN 3 | 115 | 7.6829 | 7.6829 | 0
GEN-2019-011 | 05 SOUTHWEST | 528568 | MONUMNT_TP 3 | 115 | 10.3926 | 10.3926 | 0
GEN-2019-011 | 05 SOUTHWEST | 528603 | NA_ENRICH 3 | 115 | 9.7292 | 9.7292 | 0
GEN-2019-011 | 05 SOUTHWEST | 528617 | LE-WAITS 2 | 69 | 3.5458 | 3.5458 | 0
GEN-2019-011 | 05 SOUTHWEST | 528709 | LE-PLNSGOAB2 | 69 | 2.8019 | 2.8019 | 0
GEN-2019-011 | 05 SOUTHWEST | 560035 | GRAPEVINE | 345 | 6.4589 | 6.4589 | 0
GEN-2019-011 | 05 SOUTHWEST | 599955 | PNM-DC6 | 230 | 9.709 | 9.709 | 0
GEN-2019-011 | 05 SOUTHWEST | 599960 | EPTNP-D6 | 230 | 9.402 | 9.402 | 0
GEN-2019-011 | 05 SOUTHWEST | 760498 | G17-146-TAP | 230 | 7.745 | 7.745 | 0
GEN-2019-011 | 05 SOUTHWEST | 762442 | G18-004-TAP | 115 | 23.6999 | 23.6999 | 0
GEN-2019-011 | 05 SOUTHWEST | 762460 | GEN-2018-015 | 345 | 5.812 | 5.812 | 0
GEN-2019-011 | 05 SOUTHWEST | 763120 | GEN-2018-081 | 230 | 17.3907 | 17.3907 | 0
GEN-2019-011 | 05 SOUTHWEST | 763186 | GEN-2018-089 | 230 | 10.6882 | 10.6882 | 0
GEN-2019-011 | 05 SOUTHWEST | 763215 | G18-092-TAP | 345 | 6.0024 | 6.0024 | 0
GEN-2019-011 | 05 SOUTHWEST | 763483 | GEN-2019-003 | 230 | 8.7401 | 8.7401 | 0
GEN-2019-021 | 05 SOUTHWEST | 524909 | ROOSEVELT 6 | 230 | 9.709 | 9.5575 | 0.1515
GEN-2019-021 | 05 SOUTHWEST | 524770 | PLSNT_HILL 6 | 230 | 6.517 | 6.4578 | 0.0592
GEN-2019-021 | 05 SOUTHWEST | 524875 | OASIS 6 | 230 | 7.8784 | 7.7947 | 0.0837
GEN-2019-021 | 05 SOUTHWEST | 524908 | ROOSEVELT 3 | 115 | 11.1454 | 11.0657 | 0.0797
GEN-2019-021 | 05 SOUTHWEST | 525531 | TOLK 6 | 230 | 31.4946 | 31.4022 | 0.0924
GEN-2019-021 | 05 SOUTHWEST | 599955 | PNM-DC6 | 230 | 9.709 | 9.5575 | 0.1515
GEN-2019-021 | 05 SOUTHWEST | 763483 | GEN-2019-003 | 230 | 8.7401 | 8.587 | 0.1531
GEN-2019-021 | 05 SOUTHWEST | 524768 | PLSNT_HILL 3 | 115 | 10.5272 | 10.4665 | 0.0607
GEN-2019-021 | 05 SOUTHWEST | 524822 | CURRY 3 | 115 | 11.4402 | 11.3723 | 0.0679
GEN-2019-021 | 05 SOUTHWEST | 524874 | OASIS 3 | 115 | 10.0542 | 9.9919 | 0.0623
GEN-2019-021 | 05 SOUTHWEST | 524885 | SN_JUAN_TAP6 | 230 | 4.8705 | 4.8591 | 0.0114
GEN-2019-021 | 05 SOUTHWEST | 524924 | PORTALES 3 | 115 | 7.5524 | 7.5164 | 0.036
GEN-2019-021 | 05 SOUTHWEST | 525481 | PLANT_X 6 | 230 | 24.1838 | 24.1445 | 0.0393
GEN-2019-021 | 05 SOUTHWEST | 525549 | TOLK 7 | 345 | 15.0276 | 15.0055 | 0.0221
GEN-2019-021 | 05 SOUTHWEST | 525586 | NEEDMORE 6 | 230 | 11.0214 | 11.0129 | 0.0085
GEN-2019-021 | 05 SOUTHWEST | 525637 | LAMB_CNTY 6 | 230 | 5.4027 | 5.4003 | 0.0024
GEN-2019-021 | 05 SOUTHWEST | 525830 | TUCO_INT 6 | 230 | 21.9895 | 21.9852 | 0.0043
GEN-2019-021 | 05 SOUTHWEST | 762132 | GEN-2017-158 | 230 | 13.8646 | 13.8489 | 0.0157
GEN-2019-021 | 05 SOUTHWEST | 763241 | GEN-2018-097 | 230 | 24.4484 | 24.3938 | 0.0546
GEN-2019-021 | 05 SOUTHWEST | 523961 | POTTER_CO 7 | 345 | 11.6631 | 11.6615 | 0.0016
GEN-2019-021 | 05 SOUTHWEST | 524502 | NORTON 3 | 115 | 2.9186 | 2.9175 | 0.0011
GEN-2019-021 | 05 SOUTHWEST | 524669 | DS-#20 3 | 115 | 6.2762 | 6.2623 | 0.0139
GEN-2019-021 | 05 SOUTHWEST | 524764 | NORRIS_TP 3 | 115 | 11.4074 | 11.3399 | 0.0675
GEN-2019-021 | 05 SOUTHWEST | 524773 | E_CLOVIS 3 | 115 | 8.962 | 8.9189 | 0.0431
GEN-2019-021 | 05 SOUTHWEST | 524776 | N_CLOVIS_TP3 | 115 | 7.4744 | 7.4437 | 0.0307
GEN-2019-021 | 05 SOUTHWEST | 524797 | PERIMETER 3 | 115 | 6.5512 | 6.5256 | 0.0256
GEN-2019-021 | 05 SOUTHWEST | 524821 | CURRY 2 | 69 | 4.4284 | 4.4223 | 0.0061
GEN-2019-021 | 05 SOUTHWEST | 524831 | FE-HOLLAND 3 | 115 | 9.2431 | 9.1971 | 0.046
GEN-2019-021 | 05 SOUTHWEST | 524838 | FE-CLOVIS2+3 | 115 | 10.7942 | 10.7335 | 0.0607
GEN-2019-021 | 05 SOUTHWEST | 524863 | FE-CHZPLT 3 | 115 | 8.0228 | 7.9862 | 0.0366
GEN-2019-021 | 05 SOUTHWEST | 524889 | SN_JUAN_WND6 | 230 | 4.6556 | 4.6456 | 0.01
GEN-2019-021 | 05 SOUTHWEST | 524923 | PORTALES 2 | 69 | 7.5604 | 7.5388 | 0.0216
GEN-2019-021 | 05 SOUTHWEST | 524935 | KILGORE 3 | 115 | 6.1488 | 6.1248 | 0.024
GEN-2019-021 | 05 SOUTHWEST | 524977 | GREYHOUND 3 | 115 | 5.6862 | 5.6657 | 0.0205
GEN-2019-021 | 05 SOUTHWEST | 525028 | BAILEYCO 3 | 115 | 5.8021 | 5.7977 | 0.0044
GEN-2019-021 | 05 SOUTHWEST | 525213 | SWISHER 6 | 230 | 10.3853 | 10.3835 | 0.0018
GEN-2019-021 | 05 SOUTHWEST | 525461 | NEWHART 6 | 230 | 10.9971 | 10.9941 | 0.003
GEN-2019-021 | 05 SOUTHWEST | 525480 | PLANT_X 3 | 115 | 19.2796 | 19.265 | 0.0146
GEN-2019-021 | 05 SOUTHWEST | 525585 | BLUECLDPOI 6 | 230 | 11.0214 | 11.0129 | 0.0085
GEN-2019-021 | 05 SOUTHWEST | 525636 | LAMB_CNTY 3 | 115 | 8.4389 | 8.4365 | 0.0024
GEN-2019-021 | 05 SOUTHWEST | 525828 | TUCO_INT 3 | 115 | 19.3618 | 19.36 | 0.0018
GEN-2019-021 | 05 SOUTHWEST | 525832 | TUCO_INT 7 | 345 | 14.0745 | 14.0728 | 0.0017
GEN-2019-021 | 05 SOUTHWEST | 525840 | ANTELOPE_1 6 | 230 | 21.8013 | 21.797 | 0.0043
GEN-2019-021 | 05 SOUTHWEST | 525957 | HALE_WNDCL16 | 230 | 10.5196 | 10.5187 | 0.0009
GEN-2019-021 | 05 SOUTHWEST | 526161 | CARLISLE 6 | 230 | 10.473 | 10.472 | 0.001
GEN-2019-021 | 05 SOUTHWEST | 526337 | JONES 6 | 230 | 16.6076 | 16.6063 | 0.0013
GEN-2019-021 | 05 SOUTHWEST | 526435 | SUNDOWN 6 | 230 | 11.7438 | 11.7415 | 0.0023
GEN-2019-021 | 05 SOUTHWEST | 526935 | YOAKUM 6 | 230 | 19.6825 | 19.6794 | 0.0031
GEN-2019-021 | 05 SOUTHWEST | 527483 | CHAVES_CNTY6 | 230 | 4.4929 | 4.4897 | 0.0032
GEN-2019-021 | 05 SOUTHWEST | 527656 | CROSSROADS 7 | 345 | 11.539 | 11.5345 | 0.0045
GEN-2019-021 | 05 SOUTHWEST | 760498 | G17-146-TAP | 230 | 7.745 | 7.742 | 0.003
GEN-2019-021 | 05 SOUTHWEST | 763120 | GEN-2018-081 | 230 | 17.3907 | 17.3708 | 0.0199
GEN-2019-021 | 05 SOUTHWEST | 523097 | HITCHLAND 7 | 345 | 14.9713 | 14.9711 | 0.0002
GEN-2019-021 | 05 SOUTHWEST | 523959 | POTTER_CO 6 | 230 | 22.4376 | 22.4345 | 0.0031
GEN-2019-021 | 05 SOUTHWEST | 524296 | SPNSPUR_WND7 | 345 | 5.3278 | 5.3275 | 0.0003
GEN-2019-021 | 05 SOUTHWEST | 524415 | AMA_SOUTH 6 | 230 | 13.6408 | 13.6398 | 0.001
GEN-2019-021 | 05 SOUTHWEST | 524486 | CAPROCK 3 | 115 | 2.636 | 2.6354 | 0.0006
GEN-2019-021 | 05 SOUTHWEST | 524509 | FE-TUCMCARI3 | 115 | 2.391 | 2.3904 | 0.0006
GEN-2019-021 | 05 SOUTHWEST | 524623 | DEAFSMITH 6 | 230 | 8.0257 | 8.0226 | 0.0031
GEN-2019-021 | 05 SOUTHWEST | 524662 | PARMER_CO 3 | 115 | 5.4666 | 5.4595 | 0.0071
GEN-2019-021 | 05 SOUTHWEST | 524777 | N_CLOVIS 3 | 115 | 6.7428 | 6.7178 | 0.025
GEN-2019-021 | 05 SOUTHWEST | 524783 | W_CLOVIS 2 | 69 | 2.4403 | 2.4384 | 0.0019
GEN-2019-021 | 05 SOUTHWEST | 524790 | CANNON_TP 3 | 115 | 6.0058 | 5.9851 | 0.0207
GEN-2019-021 | 05 SOUTHWEST | 524801 | NORRIS 3 | 115 | 10.4115 | 10.3551 | 0.0564
GEN-2019-021 | 05 SOUTHWEST | 524808 | FE-CLVS_INT3 | 115 | 6.9498 | 6.9233 | 0.0265
GEN-2019-021 | 05 SOUTHWEST | 524846 | FARWELL 2 | 69 | 2.1357 | 2.1343 | 0.0014
GEN-2019-021 | 05 SOUTHWEST | 524929 | RO-PORT_MTR2 | 69 | 7.5604 | 7.5388 | 0.0216
GEN-2019-021 | 05 SOUTHWEST | 524934 | ZODIAC 2 | 69 | 5.5439 | 5.5322 | 0.0117
GEN-2019-021 | 05 SOUTHWEST | 524941 | PORTALES#1 2 | 69 | 5.7509 | 5.7383 | 0.0126
GEN-2019-021 | 05 SOUTHWEST | 524963 | S_PORTALES 3 | 115 | 5.7708 | 5.7497 | 0.0211
GEN-2019-021 | 05 SOUTHWEST | 525019 | MULSHVLY_TP3 | 115 | 5.9489 | 5.9445 | 0.0044
GEN-2019-021 | 05 SOUTHWEST | 525027 | BAILEYCO 2 | 69 | 5.2707 | 5.2686 | 0.0021
GEN-2019-021 | 05 SOUTHWEST | 525056 | BC-EARTH 3 | 115 | 8.2606 | 8.2585 | 0.0021
GEN-2019-021 | 05 SOUTHWEST | 525212 | SWISHER 3 | 115 | 11.4972 | 11.496 | 0.0012
GEN-2019-021 | 05 SOUTHWEST | 525446 | RKYFORD_TP 3 | 115 | 10.1267 | 10.1232 | 0.0035
GEN-2019-021 | 05 SOUTHWEST | 525454 | HALE_CNTY 3 | 115 | 10.1608 | 10.1595 | 0.0013
GEN-2019-021 | 05 SOUTHWEST | 525460 | NEWHART 3 | 115 | 14.9423 | 14.9392 | 0.0031
GEN-2019-021 | 05 SOUTHWEST | 525584 | BLUECLDCOL 6 | 230 | 10.4275 | 10.4199 | 0.0076
GEN-2019-021 | 05 SOUTHWEST | 525635 | LAMB_CNTY 2 | 69 | 5.8992 | 5.8984 | 0.0008
GEN-2019-021 | 05 SOUTHWEST | 525780 | FLOYD_CNTY 3 | 115 | 6.2514 | 6.2511 | 0.0003
GEN-2019-021 | 05 SOUTHWEST | 525816 | TUCO_INT2 2 | 69 | 4.6524 | 4.6523 | 0.0001
GEN-2019-021 | 05 SOUTHWEST | 525826 | TUCO_INT 2 | 69 | 7.8538 | 7.8536 | 0.0002
GEN-2019-021 | 05 SOUTHWEST | 525850 | ELK_CT1 | 345 | 13.9398 | 13.9381 | 0.0017
GEN-2019-021 | 05 SOUTHWEST | 526020 | HOCKLEY 3 | 115 | 5.426 | 5.4255 | 0.0005
GEN-2019-021 | 05 SOUTHWEST | 526076 | STANTON_W 3 | 115 | 8.923 | 8.9227 | 0.0003
GEN-2019-021 | 05 SOUTHWEST | 526160 | CARLISLE 3 | 115 | 12.772 | 12.7714 | 0.0006
GEN-2019-021 | 05 SOUTHWEST | 526269 | LUBBCK_STH 6 | 230 | 15.0546 | 15.0534 | 0.0012
GEN-2019-021 | 05 SOUTHWEST | 526298 | LUBBCK_EST 3 | 115 | 14.4141 | 14.4135 | 0.0006
GEN-2019-021 | 05 SOUTHWEST | 526299 | LUBBCK_EST 6 | 230 | 11.0462 | 11.0456 | 0.0006
GEN-2019-021 | 05 SOUTHWEST | 526434 | SUNDOWN 3 | 115 | 10.8603 | 10.8594 | 0.0009
GEN-2019-021 | 05 SOUTHWEST | 526460 | AMOCO_SS 6 | 230 | 10.1771 | 10.1755 | 0.0016
GEN-2019-021 | 05 SOUTHWEST | 526525 | WOLFFORTH 6 | 230 | 13.0516 | 13.05 | 0.0016
GEN-2019-021 | 05 SOUTHWEST | 526677 | GRASSLAND 6 | 230 | 5.9735 | 5.9733 | 0.0002
GEN-2019-021 | 05 SOUTHWEST | 526934 | YOAKUM 3 | 115 | 19.2326 | 19.2313 | 0.0013
GEN-2019-021 | 05 SOUTHWEST | 526936 | YOAKUM_345 | 345 | 9.9314 | 9.93 | 0.0014
GEN-2019-021 | 05 SOUTHWEST | 527009 | BRU_SUB 6 | 230 | 15.6513 | 15.6497 | 0.0016
GEN-2019-021 | 05 SOUTHWEST | 527028 | INK_BASIN 6 | 230 | 11.2413 | 11.2404 | 0.0009
GEN-2019-021 | 05 SOUTHWEST | 527149 | MUSTANG 6 | 230 | 17.9238 | 17.9224 | 0.0014
GEN-2019-021 | 05 SOUTHWEST | 527482 | CHAVES_CNTY3 | 115 | 7.0492 | 7.0457 | 0.0035
GEN-2019-021 | 05 SOUTHWEST | 527610 | SAGA_SCOL 7 | 345 | 10.2321 | 10.2287 | 0.0034
GEN-2019-021 | 05 SOUTHWEST | 527655 | RSVLT_CC_E 7 | 345 | 10.0154 | 10.0122 | 0.0032
GEN-2019-021 | 05 SOUTHWEST | 527799 | EDDY_NORTH 6 | 230 | 9.402 | 9.3992 | 0.0028
GEN-2019-021 | 05 SOUTHWEST | 527802 | EDDY_CNTY 7 | 345 | 7.3273 | 7.3254 | 0.0019
GEN-2019-021 | 05 SOUTHWEST | 527896 | HOBBS_INT 7 | 345 | 12.0143 | 12.0113 | 0.003
GEN-2019-021 | 05 SOUTHWEST | 560022 | CRAWFISH_DR | 345 | 13.842 | 13.8404 | 0.0016
GEN-2019-021 | 05 SOUTHWEST | 560035 | GRAPEVINE | 345 | 6.4589 | 6.4586 | 0.0003
GEN-2019-021 | 05 SOUTHWEST | 760494 | GEN-2017-146 | 230 | 7.4558 | 7.453 | 0.0028
GEN-2019-021 | 05 SOUTHWEST | 763186 | GEN-2018-089 | 230 | 10.6882 | 10.6853 | 0.0029
GEN-2019-021 | 05 SOUTHWEST | 511553 | CHISHOLM7 | 345 | 12.3397 | 12.3395 | 0.0002
GEN-2019-021 | 05 SOUTHWEST | 515458 | BORDER 7 | 345 | 8.2517 | 8.2516 | 0.0001
GEN-2019-021 | 05 SOUTHWEST | 515554 | BVRCNTY7 | 345 | 15.3093 | 15.3092 | 0.0001
GEN-2019-021 | 05 SOUTHWEST | 523095 | HITCHLAND 6 | 230 | 14.5761 | 14.5759 | 0.0002
GEN-2019-021 | 05 SOUTHWEST | 523101 | NOBLE_WND 7 | 345 | 14.9103 | 14.91 | 0.0003
GEN-2019-021 | 05 SOUTHWEST | 523112 | NOVUS1 7 | 345 | 14.6716 | 14.6713 | 0.0003
GEN-2019-021 | 05 SOUTHWEST | 523323 | MCDWL_CREEK6 | 230 | 8.9802 | 8.9798 | 0.0004
GEN-2019-021 | 05 SOUTHWEST | 523823 | CARPENTER 7 | 345 | 6.5781 | 6.5781 | 0
GEN-2019-021 | 05 SOUTHWEST | 523869 | CHAN+TASCOS6 | 230 | 4.2464 | 4.2463 | 0.0001
GEN-2019-021 | 05 SOUTHWEST | 523979 | HARRNG_EST 6 | 230 | 26.9856 | 26.9831 | 0.0025
GEN-2019-021 | 05 SOUTHWEST | 524010 | ROLLHILLS 6 | 230 | 20.2306 | 20.2288 | 0.0018
GEN-2019-021 | 05 SOUTHWEST | 524044 | NICHOLS 6 | 230 | 26.1237 | 26.1214 | 0.0023
GEN-2019-021 | 05 SOUTHWEST | 524267 | BUSHLAND 6 | 230 | 10.1739 | 10.1725 | 0.0014
GEN-2019-021 | 05 SOUTHWEST | 524299 | SPNSPUR_COL7 | 345 | 5.3278 | 5.3275 | 0.0003
GEN-2019-021 | 05 SOUTHWEST | 524365 | RANDALL 6 | 230 | 14.5681 | 14.567 | 0.0011
GEN-2019-021 | 05 SOUTHWEST | 524414 | AMA_SOUTH 3 | 115 | 16.9088 | 16.908 | 0.0008
GEN-2019-021 | 05 SOUTHWEST | 524472 | LOPEZ 3 | 115 | 2.2613 | 2.2608 | 0.0005
GEN-2019-021 | 05 SOUTHWEST | 524619 | DFSMTH_EST 3 | 115 | 11.9939 | 11.9889 | 0.005
GEN-2019-021 | 05 SOUTHWEST | 524622 | DFSMTH_WST 3 | 115 | 11.9945 | 11.9895 | 0.005
GEN-2019-021 | 05 SOUTHWEST | 524664 | DS-#24 +3 | 115 | 5.4393 | 5.4328 | 0.0065
GEN-2019-021 | 05 SOUTHWEST | 524746 | CASTRO_CNTY3 | 115 | 9.822 | 9.8201 | 0.0019
GEN-2019-021 | 05 SOUTHWEST | 524784 | W_CLOVIS 3 | 115 | 6.3275 | 6.3051 | 0.0224
GEN-2019-021 | 05 SOUTHWEST | 524794 | CANNONAFB 3 | 115 | 5.6335 | 5.6153 | 0.0182
GEN-2019-021 | 05 SOUTHWEST | 524853 | DS-#10 +2 | 69 | 1.7522 | 1.752 | 0.0002
GEN-2019-021 | 05 SOUTHWEST | 524948 | PORTALES#2 2 | 69 | 4.8607 | 4.8517 | 0.009
GEN-2019-021 | 05 SOUTHWEST | 524962 | S_PORTALES 2 | 69 | 4.3137 | 4.3066 | 0.0071
GEN-2019-021 | 05 SOUTHWEST | 525008 | MULESH_CTY 2 | 69 | 4.2533 | 4.2519 | 0.0014
GEN-2019-021 | 05 SOUTHWEST | 525017 | EMULESH&VLY2 | 69 | 4.2591 | 4.2577 | 0.0014
GEN-2019-021 | 05 SOUTHWEST | 525018 | MULESHVALLY3 | 115 | 5.5409 | 5.5371 | 0.0038
GEN-2019-021 | 05 SOUTHWEST | 525023 | BC-BAIL_MTR2 | 69 | 5.2707 | 5.2686 | 0.0021
GEN-2019-021 | 05 SOUTHWEST | 525050 | BC-KELLEY +3 | 115 | 7.782 | 7.7803 | 0.0017
GEN-2019-021 | 05 SOUTHWEST | 525124 | HART_INDUST3 | 115 | 7.4925 | 7.4916 | 0.0009
GEN-2019-021 | 05 SOUTHWEST | 525192 | KRESS_INT 3 | 115 | 11.9205 | 11.9191 | 0.0014
GEN-2019-021 | 05 SOUTHWEST | 525326 | COX 3 | 115 | 6.2736 | 6.2733 | 0.0003
GEN-2019-021 | 05 SOUTHWEST | 525393 | ROCKYFORD 3 | 115 | 9.0431 | 9.0403 | 0.0028
GEN-2019-021 | 05 SOUTHWEST | 525414 | LAMTON 3 | 115 | 7.6144 | 7.6132 | 0.0012
GEN-2019-021 | 05 SOUTHWEST | 525440 | LC-S_OLTON+3 | 115 | 7.1982 | 7.1969 | 0.0013
GEN-2019-021 | 05 SOUTHWEST | 525453 | HALE_CNTY 2 | 69 | 6.9062 | 6.9059 | 0.0003
GEN-2019-021 | 05 SOUTHWEST | 525613 | W_LITTLFLD 2 | 69 | 2.9684 | 2.9683 | 0.0001
GEN-2019-021 | 05 SOUTHWEST | 525620 | LTFLD_S&CTY2 | 69 | 4.1727 | 4.1723 | 0.0004
GEN-2019-021 | 05 SOUTHWEST | 525650 | LC-LTTLFLD+2 | 69 | 4.9319 | 4.9314 | 0.0005
GEN-2019-021 | 05 SOUTHWEST | 525687 | LC-LUMSCHAP2 | 69 | 4.6126 | 4.6121 | 0.0005
GEN-2019-021 | 05 SOUTHWEST | 525731 | SP-ABERNTHY2 | 69 | 3.0093 | 3.0092 | 0.0001
GEN-2019-021 | 05 SOUTHWEST | 525738 | HALECENTER 2 | 69 | 2.4566 | 2.4565 | 0.0001
GEN-2019-021 | 05 SOUTHWEST | 525763 | CALLAHAN 3 | 115 | 5.5668 | 5.5665 | 0.0003
GEN-2019-021 | 05 SOUTHWEST | 525779 | FLOYD_CNTY 2 | 69 | 5.401 | 5.4009 | 0.0001
GEN-2019-021 | 05 SOUTHWEST | 525803 | BLANCO 3 | 115 | 5.0451 | 5.045 | 0.0001
GEN-2019-021 | 05 SOUTHWEST | 525853 | LH-WIL&ELN+2 | 69 | 2.5404 | 2.5404 | 0
GEN-2019-021 | 05 SOUTHWEST | 525885 | SP-NEWDEAL 2 | 69 | 3.3073 | 3.3073 | 0
GEN-2019-021 | 05 SOUTHWEST | 525926 | CROSBY 3 | 115 | 4.7129 | 4.7129 | 0
GEN-2019-021 | 05 SOUTHWEST | 526019 | HOCKLEY 2 | 69 | 5.1105 | 5.1102 | 0.0003
GEN-2019-021 | 05 SOUTHWEST | 526036 | LC-OPDYKE 3 | 115 | 5.7143 | 5.7138 | 0.0005
GEN-2019-021 | 05 SOUTHWEST | 526109 | SP-ERSKINE 3 | 115 | 10.9787 | 10.9782 | 0.0005
GEN-2019-021 | 05 SOUTHWEST | 526146 | INDIANA 3 | 115 | 9.3032 | 9.3028 | 0.0004
GEN-2019-021 | 05 SOUTHWEST | 526159 | CARLISLE 2 | 69 | 2.5568 | 2.5568 | 0
GEN-2019-021 | 05 SOUTHWEST | 526162 | LP-DOUD_TP 3 | 115 | 11.325 | 11.3245 | 0.0005
GEN-2019-021 | 05 SOUTHWEST | 526192 | MURPHY 3 | 115 | 10.2503 | 10.2499 | 0.0004
GEN-2019-021 | 05 SOUTHWEST | 526268 | LUBBCK_STH 3 | 115 | 17.6482 | 17.6473 | 0.0009
GEN-2019-021 | 05 SOUTHWEST | 526297 | LUBBCK_EST 2 | 69 | 7.8955 | 7.8954 | 0.0001
GEN-2019-021 | 05 SOUTHWEST | 526424 | PACIFIC 3 | 115 | 9.1771 | 9.1764 | 0.0007
GEN-2019-021 | 05 SOUTHWEST | 526445 | AMOCO_TP 3 | 115 | 10.1845 | 10.1836 | 0.0009
GEN-2019-021 | 05 SOUTHWEST | 526524 | WOLFFORTH 3 | 115 | 11.2819 | 11.2813 | 0.0006
GEN-2019-021 | 05 SOUTHWEST | 526676 | GRASSLAND 3 | 115 | 6.8633 | 6.8632 | 0.0001
GEN-2019-021 | 05 SOUTHWEST | 526679 | CIRRUS_WND 6 | 230 | 4.6792 | 4.6791 | 0.0001
GEN-2019-021 | 05 SOUTHWEST | 526784 | AMOCOWASSON6 | 230 | 15.6353 | 15.6341 | 0.0012
GEN-2019-021 | 05 SOUTHWEST | 526792 | PRENTICE 3 | 115 | 6.0286 | 6.0285 | 0.0001
GEN-2019-021 | 05 SOUTHWEST | 526928 | PLAINS_INT 3 | 115 | 10.0196 | 10.0192 | 0.0004
GEN-2019-021 | 05 SOUTHWEST | 527010 | OXYBRU 6 | 230 | 15.5052 | 15.5036 | 0.0016
GEN-2019-021 | 05 SOUTHWEST | 527011 | XTO_MAHONEY6 | 230 | 15.3578 | 15.3563 | 0.0015
GEN-2019-021 | 05 SOUTHWEST | 527027 | INK_BASIN 3 | 115 | 13.258 | 13.2576 | 0.0004
GEN-2019-021 | 05 SOUTHWEST | 527041 | ARCO_TP 3 | 115 | 13.6807 | 13.6802 | 0.0005
GEN-2019-021 | 05 SOUTHWEST | 527146 | MUSTANG 3 | 115 | 24.0628 | 24.0618 | 0.001
GEN-2019-021 | 05 SOUTHWEST | 527151 | GS-MUSTANG 6 | 230 | 17.9238 | 17.9224 | 0.0014
GEN-2019-021 | 05 SOUTHWEST | 527194 | LG-PLSHILL 3 | 115 | 7.9741 | 7.9739 | 0.0002
GEN-2019-021 | 05 SOUTHWEST | 527276 | SEMINOLE 6 | 230 | 8.197 | 8.1968 | 0.0002
GEN-2019-021 | 05 SOUTHWEST | 527455 | RSWL_SLRCOL3 | 115 | 6.9796 | 6.9762 | 0.0034
GEN-2019-021 | 05 SOUTHWEST | 527470 | CHVS_SLRCOL3 | 115 | 6.816 | 6.8127 | 0.0033
GEN-2019-021 | 05 SOUTHWEST | 527501 | URTON 3 | 115 | 5.8725 | 5.8702 | 0.0023
GEN-2019-021 | 05 SOUTHWEST | 527509 | PRICE_TAP 3 | 115 | 5.4519 | 5.4498 | 0.0021
GEN-2019-021 | 05 SOUTHWEST | 527546 | SAMSON 3 | 115 | 5.515 | 5.513 | 0.002
GEN-2019-021 | 05 SOUTHWEST | 527599 | SAGA_SDCOL 7 | 345 | 10.2321 | 10.2287 | 0.0034
GEN-2019-021 | 05 SOUTHWEST | 527654 | RSVLT_CC_W 7 | 345 | 8.7265 | 8.7241 | 0.0024
GEN-2019-021 | 05 SOUTHWEST | 527793 | EDDY_STH 3 | 115 | 11.9559 | 11.9535 | 0.0024
GEN-2019-021 | 05 SOUTHWEST | 527798 | EDDY_NTH 3 | 115 | 11.9559 | 11.9535 | 0.0024
GEN-2019-021 | 05 SOUTHWEST | 527865 | CUNNIGHM_N 6 | 230 | 17.5364 | 17.5342 | 0.0022
GEN-2019-021 | 05 SOUTHWEST | 527894 | HOBBS_INT 6 | 230 | 19.4767 | 19.474 | 0.0027
GEN-2019-021 | 05 SOUTHWEST | 527965 | KIOWA 7 | 345 | 8.82 | 8.818 | 0.002
GEN-2019-021 | 05 SOUTHWEST | 528027 | RDRUNNER 7 | 345 | 8.6815 | 8.6799 | 0.0016
GEN-2019-021 | 05 SOUTHWEST | 528095 | 7-RIVERS 6 | 230 | 6.3874 | 6.3864 | 0.001
GEN-2019-021 | 05 SOUTHWEST | 560756 | CEILO-TAP-N | 115 | 0.4601 | 0.4601 | 0
GEN-2019-021 | 05 SOUTHWEST | 576397 | G10014G11022 | 345 | 10.3812 | 10.3811 | 0.0001
GEN-2019-021 | 05 SOUTHWEST | 583280 | A12-02&13-05 | 115 | 1.0409 | 1.0407 | 0.0002
GEN-2019-021 | 05 SOUTHWEST | 599960 | EPTNP-D6 | 230 | 9.402 | 9.3992 | 0.0028
GEN-2019-021 | 05 SOUTHWEST | 762216 | G17-151TAP | 345 | 8.5119 | 8.5114 | 0.0005
GEN-2019-021 | 05 SOUTHWEST | 763087 | GEN-2018-073 | 345 | 11.9423 | 11.9411 | 0.0012
GEN-2019-021 | 05 SOUTHWEST | 763516 | GEN-2019-011 | 345 | 9.2852 | 9.2839 | 0.0013
GEN-2019-056 | 05 SOUTHWEST | 524364 | RANDALL 3 | 115 | 21.0733 | 21.0733 | 0
GEN-2019-056 | 05 SOUTHWEST | 524224 | MANHATTAN 3 | 115 | 17.2747 | 17.2747 | 0
GEN-2019-056 | 05 SOUTHWEST | 524322 | GEORGIA 3 | 115 | 16.8695 | 16.8695 | 0
GEN-2019-056 | 05 SOUTHWEST | 524338 | SOUTHEAST 3 | 115 | 11.2307 | 11.2307 | 0
GEN-2019-056 | 05 SOUTHWEST | 524365 | RANDALL 6 | 230 | 14.5681 | 14.5681 | 0
GEN-2019-056 | 05 SOUTHWEST | 524522 | CANYON_E_TP3 | 115 | 5.853 | 5.853 | 0
GEN-2019-056 | 05 SOUTHWEST | 524530 | PALO_DURO 3 | 115 | 6.7455 | 6.7455 | 0
GEN-2019-056 | 05 SOUTHWEST | 763879 | GEN-2019-056 | 115 | 20.1117 | 20.1117 | 0
GEN-2019-056 | 05 SOUTHWEST | 523978 | HARRNG_MID 6 | 230 | 26.9856 | 26.9856 | 0
GEN-2019-056 | 05 SOUTHWEST | 524162 | EAST_PLANT 3 | 115 | 22.9296 | 22.9296 | 0
GEN-2019-056 | 05 SOUTHWEST | 524321 | GEORGIA 2 | 69 | 6.6966 | 6.6966 | 0
GEN-2019-056 | 05 SOUTHWEST | 524325 | WESTERN 3 | 115 | 15.8226 | 15.8226 | 0
GEN-2019-056 | 05 SOUTHWEST | 524331 | PULLMAN 3 | 115 | 7.2077 | 7.2077 | 0
GEN-2019-056 | 05 SOUTHWEST | 524387 | CRSE_HINDTP3 | 115 | 15.4475 | 15.4475 | 0
GEN-2019-056 | 05 SOUTHWEST | 524415 | AMA_SOUTH 6 | 230 | 13.6408 | 13.6408 | 0
GEN-2019-056 | 05 SOUTHWEST | 524520 | HUNSLEY 3 | 115 | 5.6704 | 5.6704 | 0
GEN-2019-056 | 05 SOUTHWEST | 524523 | CANYON_EAST3 | 115 | 5.4025 | 5.4025 | 0
GEN-2019-056 | 05 SOUTHWEST | 525154 | HAPPY_INT 3 | 115 | 5.4569 | 5.4569 | 0
GEN-2019-056 | 05 SOUTHWEST | 587570 | ASGI1604 | 115 | 6.7455 | 6.7455 | 0
GEN-2019-056 | 05 SOUTHWEST | 523977 | HARRNG_WST 6 | 230 | 26.9856 | 26.9856 | 0
GEN-2019-056 | 05 SOUTHWEST | 523979 | HARRNG_EST 6 | 230 | 26.9856 | 26.9856 | 0
GEN-2019-056 | 05 SOUTHWEST | 524044 | NICHOLS 6 | 230 | 26.1237 | 26.1237 | 0
GEN-2019-056 | 05 SOUTHWEST | 524058 | WHITAKER 3 | 115 | 21.9266 | 21.9266 | 0
GEN-2019-056 | 05 SOUTHWEST | 524136 | HASTINGS 3 | 115 | 14.3234 | 14.3234 | 0
GEN-2019-056 | 05 SOUTHWEST | 524161 | EAST_PLANT 2 | 69 | 8.8539 | 8.8539 | 0
GEN-2019-056 | 05 SOUTHWEST | 524163 | EAST_PLANT 6 | 230 | 13.8955 | 13.8955 | 0
GEN-2019-056 | 05 SOUTHWEST | 524185 | PIERCE_TP 3 | 115 | 19.0664 | 19.0664 | 0
GEN-2019-056 | 05 SOUTHWEST | 524209 | LAWRENPRK1 2 | 69 | 6.5611 | 6.5611 | 0
GEN-2019-056 | 05 SOUTHWEST | 524281 | 34TH_ST_TP 3 | 115 | 15.4906 | 15.4906 | 0
GEN-2019-056 | 05 SOUTHWEST | 524377 | FARMERS 3 | 115 | 15.4368 | 15.4368 | 0
GEN-2019-056 | 05 SOUTHWEST | 524388 | CROUSE_HIND3 | 115 | 13.5165 | 13.5165 | 0
GEN-2019-056 | 05 SOUTHWEST | 524414 | AMA_SOUTH 3 | 115 | 16.9088 | 16.9088 | 0
GEN-2019-056 | 05 SOUTHWEST | 524516 | CANYON_WEST3 | 115 | 5.5422 | 5.5422 | 0
GEN-2019-056 | 05 SOUTHWEST | 525153 | HAPPY_INT 2 | 69 | 5.1031 | 5.1031 | 0
GEN-2019-056 | 05 SOUTHWEST | 525179 | TULIA_TP 3 | 115 | 6.4624 | 6.4624 | 0
GEN-2019-056 | 05 SOUTHWEST | 525213 | SWISHER 6 | 230 | 10.3853 | 10.3853 | 0
GEN-2019-056 | 05 SOUTHWEST | 522800 | MU-TULIA 3 | 115 | 5.2034 | 5.2034 | 0
GEN-2019-056 | 05 SOUTHWEST | 523267 | PRINGLE 6 | 230 | 4.3435 | 4.3435 | 0
GEN-2019-056 | 05 SOUTHWEST | 523551 | HUTCHISON 6 | 230 | 7.288 | 7.288 | 0
GEN-2019-056 | 05 SOUTHWEST | 523771 | GRAPEVINE 6 | 230 | 5.9762 | 5.9762 | 0
GEN-2019-056 | 05 SOUTHWEST | 523959 | POTTER_CO 6 | 230 | 22.4376 | 22.4376 | 0
GEN-2019-056 | 05 SOUTHWEST | 524007 | ROLLHILLS 3 | 115 | 19.6592 | 19.6592 | 0
GEN-2019-056 | 05 SOUTHWEST | 524010 | ROLLHILLS 6 | 230 | 20.2306 | 20.2306 | 0
GEN-2019-056 | 05 SOUTHWEST | 524043 | NICHOLS 3 | 115 | 30.649 | 30.649 | 0
GEN-2019-056 | 05 SOUTHWEST | 524142 | VANBUREN#1 2 | 69 | 5.6241 | 5.6241 | 0
GEN-2019-056 | 05 SOUTHWEST | 524149 | VANBUREN#2 2 | 69 | 6.5947 | 6.5947 | 0
GEN-2019-056 | 05 SOUTHWEST | 524192 | PIERCE 3 | 115 | 12.9787 | 12.9787 | 0
GEN-2019-056 | 05 SOUTHWEST | 524216 | LAWRENPRK2 2 | 69 | 6.5611 | 6.5611 | 0
GEN-2019-056 | 05 SOUTHWEST | 524282 | 34TH_ST 3 | 115 | 12.5992 | 12.5992 | 0
GEN-2019-056 | 05 SOUTHWEST | 524306 | COULTER 3 | 115 | 15.738 | 15.738 | 0
GEN-2019-056 | 05 SOUTHWEST | 524345 | OSAGE 3 | 115 | 13.8304 | 13.8304 | 0
GEN-2019-056 | 05 SOUTHWEST | 524397 | ARROWHEAD 3 | 115 | 13.6793 | 13.6793 | 0
GEN-2019-056 | 05 SOUTHWEST | 524404 | OWENSCORN 3 | 115 | 15.0594 | 15.0594 | 0
GEN-2019-056 | 05 SOUTHWEST | 524544 | SPRING_DRW 3 | 115 | 6.4069 | 6.4069 | 0
GEN-2019-056 | 05 SOUTHWEST | 524590 | DAWN 3 | 115 | 6.1533 | 6.1533 | 0
GEN-2019-056 | 05 SOUTHWEST | 525143 | HAPPY_CTYTP2 | 69 | 4.5453 | 4.5453 | 0
GEN-2019-056 | 05 SOUTHWEST | 525192 | KRESS_INT 3 | 115 | 11.9205 | 11.9205 | 0
GEN-2019-056 | 05 SOUTHWEST | 525212 | SWISHER 3 | 115 | 11.4972 | 11.4972 | 0
GEN-2019-056 | 05 SOUTHWEST | 525461 | NEWHART 6 | 230 | 10.9971 | 10.9971 | 0
GEN-2019-056 | 05 SOUTHWEST | 525830 | TUCO_INT 6 | 230 | 21.9895 | 21.9895 | 0
GEN-2019-056 | 05 SOUTHWEST | 523266 | PRINGLE 3 | 115 | 11.3365 | 11.3365 | 0
GEN-2019-056 | 05 SOUTHWEST | 523323 | MCDWL_CREEK6 | 230 | 8.9802 | 8.9802 | 0
GEN-2019-056 | 05 SOUTHWEST | 523339 | FAIN 3 | 115 | 8.4872 | 8.4872 | 0
GEN-2019-056 | 05 SOUTHWEST | 523410 | CRMWA_#4 3 | 115 | 9.7322 | 9.7322 | 0
GEN-2019-056 | 05 SOUTHWEST | 523544 | HUTCH_N 3 | 115 | 16.0441 | 16.0441 | 0
GEN-2019-056 | 05 SOUTHWEST | 523546 | HUTCH_S 3 | 115 | 16.0441 | 16.0441 | 0
GEN-2019-056 | 05 SOUTHWEST | 523770 | GRAPEVINE 3 | 115 | 7.9787 | 7.9787 | 0
GEN-2019-056 | 05 SOUTHWEST | 523777 | WHEELER 6 | 230 | 6.7683 | 6.7683 | 0
GEN-2019-056 | 05 SOUTHWEST | 523817 | MIDSTRM_TP 3 | 115 | 4.7119 | 4.7119 | 0
GEN-2019-056 | 05 SOUTHWEST | 523869 | CHAN+TASCOS6 | 230 | 4.2464 | 4.2464 | 0
GEN-2019-056 | 05 SOUTHWEST | 523961 | POTTER_CO 7 | 345 | 11.6631 | 11.6631 | 0
GEN-2019-056 | 05 SOUTHWEST | 524009 | CHERRY 3 | 115 | 18.7893 | 18.7893 | 0
GEN-2019-056 | 05 SOUTHWEST | 524016 | ASARCO 3 | 115 | 26.5107 | 26.5107 | 0
GEN-2019-056 | 05 SOUTHWEST | 524018 | ASARCO_TP 3 | 115 | 28.6572 | 28.6572 | 0
GEN-2019-056 | 05 SOUTHWEST | 524072 | YARNELL_TP 3 | 115 | 7.9824 | 7.9824 | 0
GEN-2019-056 | 05 SOUTHWEST | 524106 | NORTHWEST 3 | 115 | 11.5491 | 11.5491 | 0
GEN-2019-056 | 05 SOUTHWEST | 524200 | SONCY 2 | 69 | 6.3757 | 6.3757 | 0
GEN-2019-056 | 05 SOUTHWEST | 524256 | PUCKETT 3 | 115 | 12.8531 | 12.8531 | 0
GEN-2019-056 | 05 SOUTHWEST | 524267 | BUSHLAND 6 | 230 | 10.1739 | 10.1739 | 0
GEN-2019-056 | 05 SOUTHWEST | 524300 | HILLSIDE 3 | 115 | 13.0381 | 13.0381 | 0
GEN-2019-056 | 05 SOUTHWEST | 524305 | COULTER 2 | 69 | 4.2906 | 4.2906 | 0
GEN-2019-056 | 05 SOUTHWEST | 524341 | PRESTONWEST3 | 115 | 13.1302 | 13.1302 | 0
GEN-2019-056 | 05 SOUTHWEST | 524425 | ESTACADO_TP3 | 115 | 13.5484 | 13.5484 | 0
GEN-2019-056 | 05 SOUTHWEST | 524597 | PANDAHFD 3 | 115 | 8.8233 | 8.8233 | 0
GEN-2019-056 | 05 SOUTHWEST | 525136 | HAPPY_CTY 2 | 69 | 2.6255 | 2.6255 | 0
GEN-2019-056 | 05 SOUTHWEST | 525164 | SHAMRCK_PMP2 | 69 | 3.2753 | 3.2753 | 0
GEN-2019-056 | 05 SOUTHWEST | 525191 | KRESS_INT 2 | 69 | 4.4978 | 4.4978 | 0
GEN-2019-056 | 05 SOUTHWEST | 525226 | KRS_RURL_TP3 | 115 | 6.4399 | 6.4399 | 0
GEN-2019-056 | 05 SOUTHWEST | 525454 | HALE_CNTY 3 | 115 | 10.1608 | 10.1608 | 0
GEN-2019-056 | 05 SOUTHWEST | 525460 | NEWHART 3 | 115 | 14.9423 | 14.9423 | 0
GEN-2019-056 | 05 SOUTHWEST | 525481 | PLANT_X 6 | 230 | 24.1838 | 24.1838 | 0
GEN-2019-056 | 05 SOUTHWEST | 525531 | TOLK 6 | 230 | 31.4946 | 31.4946 | 0
GEN-2019-056 | 05 SOUTHWEST | 525828 | TUCO_INT 3 | 115 | 19.3618 | 19.3618 | 0
GEN-2019-056 | 05 SOUTHWEST | 525832 | TUCO_INT 7 | 345 | 14.0745 | 14.0745 | 0
GEN-2019-056 | 05 SOUTHWEST | 525840 | ANTELOPE_1 6 | 230 | 21.8013 | 21.8013 | 0
GEN-2019-056 | 05 SOUTHWEST | 525957 | HALE_WNDCL16 | 230 | 10.5196 | 10.5196 | 0
GEN-2019-056 | 05 SOUTHWEST | 526161 | CARLISLE 6 | 230 | 10.473 | 10.473 | 0
GEN-2019-056 | 05 SOUTHWEST | 526337 | JONES 6 | 230 | 16.6076 | 16.6076 | 0
GEN-2019-056 | 05 SOUTHWEST | 763186 | GEN-2018-089 | 230 | 10.6882 | 10.6882 | 0
GEN-2019-074 | 05 SOUTHWEST | 525481 | PLANT_X 6 | 230 | 24.1838 | 24.1838 | 0
GEN-2019-074 | 05 SOUTHWEST | 525461 | NEWHART 6 | 230 | 10.9971 | 10.9971 | 0
GEN-2019-074 | 05 SOUTHWEST | 525480 | PLANT_X 3 | 115 | 19.2796 | 19.2796 | 0
GEN-2019-074 | 05 SOUTHWEST | 525531 | TOLK 6 | 230 | 31.4946 | 31.4946 | 0
GEN-2019-074 | 05 SOUTHWEST | 526435 | SUNDOWN 6 | 230 | 11.7438 | 11.7438 | 0
GEN-2019-074 | 05 SOUTHWEST | 760498 | G17-146-TAP | 230 | 7.745 | 7.745 | 0
GEN-2019-074 | 05 SOUTHWEST | 763120 | GEN-2018-081 | 230 | 17.3907 | 17.3907 | 0
GEN-2019-074 | 05 SOUTHWEST | 523959 | POTTER_CO 6 | 230 | 22.4376 | 22.4376 | 0
GEN-2019-074 | 05 SOUTHWEST | 524623 | DEAFSMITH 6 | 230 | 8.0257 | 8.0257 | 0
GEN-2019-074 | 05 SOUTHWEST | 524909 | ROOSEVELT 6 | 230 | 9.709 | 9.709 | 0
GEN-2019-074 | 05 SOUTHWEST | 525019 | MULSHVLY_TP3 | 115 | 5.9489 | 5.9489 | 0
GEN-2019-074 | 05 SOUTHWEST | 525056 | BC-EARTH 3 | 115 | 8.2606 | 8.2606 | 0
GEN-2019-074 | 05 SOUTHWEST | 525213 | SWISHER 6 | 230 | 10.3853 | 10.3853 | 0
GEN-2019-074 | 05 SOUTHWEST | 525446 | RKYFORD_TP 3 | 115 | 10.1267 | 10.1267 | 0
GEN-2019-074 | 05 SOUTHWEST | 525454 | HALE_CNTY 3 | 115 | 10.1608 | 10.1608 | 0
GEN-2019-074 | 05 SOUTHWEST | 525460 | NEWHART 3 | 115 | 14.9423 | 14.9423 | 0
GEN-2019-074 | 05 SOUTHWEST | 525549 | TOLK 7 | 345 | 15.0276 | 15.0276 | 0
GEN-2019-074 | 05 SOUTHWEST | 525586 | NEEDMORE 6 | 230 | 11.0214 | 11.0214 | 0
GEN-2019-074 | 05 SOUTHWEST | 525636 | LAMB_CNTY 3 | 115 | 8.4389 | 8.4389 | 0
GEN-2019-074 | 05 SOUTHWEST | 525637 | LAMB_CNTY 6 | 230 | 5.4027 | 5.4027 | 0
GEN-2019-074 | 05 SOUTHWEST | 525830 | TUCO_INT 6 | 230 | 21.9895 | 21.9895 | 0
GEN-2019-074 | 05 SOUTHWEST | 526434 | SUNDOWN 3 | 115 | 10.8603 | 10.8603 | 0
GEN-2019-074 | 05 SOUTHWEST | 526460 | AMOCO_SS 6 | 230 | 10.1771 | 10.1771 | 0
GEN-2019-074 | 05 SOUTHWEST | 526525 | WOLFFORTH 6 | 230 | 13.0516 | 13.0516 | 0
GEN-2019-074 | 05 SOUTHWEST | 760494 | GEN-2017-146 | 230 | 7.4558 | 7.4558 | 0
GEN-2019-074 | 05 SOUTHWEST | 762132 | GEN-2017-158 | 230 | 13.8646 | 13.8646 | 0
GEN-2019-074 | 05 SOUTHWEST | 763186 | GEN-2018-089 | 230 | 10.6882 | 10.6882 | 0
GEN-2019-074 | 05 SOUTHWEST | 763241 | GEN-2018-097 | 230 | 24.4484 | 24.4484 | 0
GEN-2019-074 | 05 SOUTHWEST | 523323 | MCDWL_CREEK6 | 230 | 8.9802 | 8.9802 | 0
GEN-2019-074 | 05 SOUTHWEST | 523869 | CHAN+TASCOS6 | 230 | 4.2464 | 4.2464 | 0
GEN-2019-074 | 05 SOUTHWEST | 523961 | POTTER_CO 7 | 345 | 11.6631 | 11.6631 | 0
GEN-2019-074 | 05 SOUTHWEST | 523979 | HARRNG_EST 6 | 230 | 26.9856 | 26.9856 | 0
GEN-2019-074 | 05 SOUTHWEST | 524010 | ROLLHILLS 6 | 230 | 20.2306 | 20.2306 | 0
GEN-2019-074 | 05 SOUTHWEST | 524267 | BUSHLAND 6 | 230 | 10.1739 | 10.1739 | 0
GEN-2019-074 | 05 SOUTHWEST | 524415 | AMA_SOUTH 6 | 230 | 13.6408 | 13.6408 | 0
GEN-2019-074 | 05 SOUTHWEST | 524619 | DFSMTH_EST 3 | 115 | 11.9939 | 11.9939 | 0
GEN-2019-074 | 05 SOUTHWEST | 524622 | DFSMTH_WST 3 | 115 | 11.9945 | 11.9945 | 0
GEN-2019-074 | 05 SOUTHWEST | 524746 | CASTRO_CNTY3 | 115 | 9.822 | 9.822 | 0
GEN-2019-074 | 05 SOUTHWEST | 524770 | PLSNT_HILL 6 | 230 | 6.517 | 6.517 | 0
GEN-2019-074 | 05 SOUTHWEST | 524875 | OASIS 6 | 230 | 7.8784 | 7.8784 | 0
GEN-2019-074 | 05 SOUTHWEST | 524908 | ROOSEVELT 3 | 115 | 11.1454 | 11.1454 | 0
GEN-2019-074 | 05 SOUTHWEST | 525018 | MULESHVALLY3 | 115 | 5.5409 | 5.5409 | 0
GEN-2019-074 | 05 SOUTHWEST | 525028 | BAILEYCO 3 | 115 | 5.8021 | 5.8021 | 0
GEN-2019-074 | 05 SOUTHWEST | 525050 | BC-KELLEY +3 | 115 | 7.782 | 7.782 | 0
GEN-2019-074 | 05 SOUTHWEST | 525124 | HART_INDUST3 | 115 | 7.4925 | 7.4925 | 0
GEN-2019-074 | 05 SOUTHWEST | 525192 | KRESS_INT 3 | 115 | 11.9205 | 11.9205 | 0
GEN-2019-074 | 05 SOUTHWEST | 525212 | SWISHER 3 | 115 | 11.4972 | 11.4972 | 0
GEN-2019-074 | 05 SOUTHWEST | 525326 | COX 3 | 115 | 6.2736 | 6.2736 | 0
GEN-2019-074 | 05 SOUTHWEST | 525393 | ROCKYFORD 3 | 115 | 9.0431 | 9.0431 | 0
GEN-2019-074 | 05 SOUTHWEST | 525414 | LAMTON 3 | 115 | 7.6144 | 7.6144 | 0
GEN-2019-074 | 05 SOUTHWEST | 525440 | LC-S_OLTON+3 | 115 | 7.1982 | 7.1982 | 0
GEN-2019-074 | 05 SOUTHWEST | 525453 | HALE_CNTY 2 | 69 | 6.9062 | 6.9062 | 0
GEN-2019-074 | 05 SOUTHWEST | 525585 | BLUECLDPOI 6 | 230 | 11.0214 | 11.0214 | 0
GEN-2019-074 | 05 SOUTHWEST | 525635 | LAMB_CNTY 2 | 69 | 5.8992 | 5.8992 | 0
GEN-2019-074 | 05 SOUTHWEST | 525828 | TUCO_INT 3 | 115 | 19.3618 | 19.3618 | 0
GEN-2019-074 | 05 SOUTHWEST | 525832 | TUCO_INT 7 | 345 | 14.0745 | 14.0745 | 0
GEN-2019-074 | 05 SOUTHWEST | 525840 | ANTELOPE_1 6 | 230 | 21.8013 | 21.8013 | 0
GEN-2019-074 | 05 SOUTHWEST | 525957 | HALE_WNDCL16 | 230 | 10.5196 | 10.5196 | 0
GEN-2019-074 | 05 SOUTHWEST | 526020 | HOCKLEY 3 | 115 | 5.426 | 5.426 | 0
GEN-2019-074 | 05 SOUTHWEST | 526036 | LC-OPDYKE 3 | 115 | 5.7143 | 5.7143 | 0
GEN-2019-074 | 05 SOUTHWEST | 526161 | CARLISLE 6 | 230 | 10.473 | 10.473 | 0
GEN-2019-074 | 05 SOUTHWEST | 526269 | LUBBCK_STH 6 | 230 | 15.0546 | 15.0546 | 0
GEN-2019-074 | 05 SOUTHWEST | 526337 | JONES 6 | 230 | 16.6076 | 16.6076 | 0
GEN-2019-074 | 05 SOUTHWEST | 526424 | PACIFIC 3 | 115 | 9.1771 | 9.1771 | 0
GEN-2019-074 | 05 SOUTHWEST | 526445 | AMOCO_TP 3 | 115 | 10.1845 | 10.1845 | 0
GEN-2019-074 | 05 SOUTHWEST | 526524 | WOLFFORTH 3 | 115 | 11.2819 | 11.2819 | 0
GEN-2019-074 | 05 SOUTHWEST | 526935 | YOAKUM 6 | 230 | 19.6825 | 19.6825 | 0
GEN-2019-074 | 05 SOUTHWEST | 527656 | CROSSROADS 7 | 345 | 11.539 | 11.539 | 0
GEN-2019-074 | 05 SOUTHWEST | 599955 | PNM-DC6 | 230 | 9.709 | 9.709 | 0
GEN-2019-074 | 05 SOUTHWEST | 763483 | GEN-2019-003 | 230 | 8.7401 | 8.7401 | 0
GEN-2019-074 | 05 SOUTHWEST | 523097 | HITCHLAND 7 | 345 | 14.9713 | 14.9713 | 0
GEN-2019-074 | 05 SOUTHWEST | 523221 | XIT_INTG 6 | 230 | 3.1441 | 3.1441 | 0
GEN-2019-074 | 05 SOUTHWEST | 523267 | PRINGLE 6 | 230 | 4.3435 | 4.3435 | 0
GEN-2019-074 | 05 SOUTHWEST | 523309 | MOORE_CNTY 6 | 230 | 6.6813 | 6.6813 | 0
GEN-2019-074 | 05 SOUTHWEST | 523322 | MCDWL_CREEK3 | 115 | 9.8376 | 9.8376 | 0
GEN-2019-074 | 05 SOUTHWEST | 523977 | HARRNG_WST 6 | 230 | 26.9856 | 26.9856 | 0
GEN-2019-074 | 05 SOUTHWEST | 523978 | HARRNG_MID 6 | 230 | 26.9856 | 26.9856 | 0
GEN-2019-074 | 05 SOUTHWEST | 524007 | ROLLHILLS 3 | 115 | 19.6592 | 19.6592 | 0
GEN-2019-074 | 05 SOUTHWEST | 524044 | NICHOLS 6 | 230 | 26.1237 | 26.1237 | 0
GEN-2019-074 | 05 SOUTHWEST | 524266 | BUSHLAND 3 | 115 | 10.3324 | 10.3324 | 0
GEN-2019-074 | 05 SOUTHWEST | 524290 | WILDOR2_JUS6 | 230 | 6.9783 | 6.9783 | 0
GEN-2019-074 | 05 SOUTHWEST | 524296 | SPNSPUR_WND7 | 345 | 5.3278 | 5.3278 | 0
GEN-2019-074 | 05 SOUTHWEST | 524365 | RANDALL 6 | 230 | 14.5681 | 14.5681 | 0
GEN-2019-074 | 05 SOUTHWEST | 524414 | AMA_SOUTH 3 | 115 | 16.9088 | 16.9088 | 0
GEN-2019-074 | 05 SOUTHWEST | 524630 | TIERABLANCA3 | 115 | 12.3344 | 12.3344 | 0
GEN-2019-074 | 05 SOUTHWEST | 524694 | DS-#22 3 | 115 | 4.5966 | 4.5966 | 0
GEN-2019-074 | 05 SOUTHWEST | 524734 | DS-#21 3 | 115 | 9.3056 | 9.3056 | 0
GEN-2019-074 | 05 SOUTHWEST | 524745 | CASTRO_CNTY2 | 69 | 8.7963 | 8.7963 | 0
GEN-2019-074 | 05 SOUTHWEST | 524757 | BETHEL_COL13 | 115 | 8.2391 | 8.2391 | 0
GEN-2019-074 | 05 SOUTHWEST | 524768 | PLSNT_HILL 3 | 115 | 10.5272 | 10.5272 | 0
GEN-2019-074 | 05 SOUTHWEST | 524822 | CURRY 3 | 115 | 11.4402 | 11.4402 | 0
GEN-2019-074 | 05 SOUTHWEST | 524874 | OASIS 3 | 115 | 10.0542 | 10.0542 | 0
GEN-2019-074 | 05 SOUTHWEST | 524885 | SN_JUAN_TAP6 | 230 | 4.8705 | 4.8705 | 0
GEN-2019-074 | 05 SOUTHWEST | 524924 | PORTALES 3 | 115 | 7.5524 | 7.5524 | 0
GEN-2019-074 | 05 SOUTHWEST | 525027 | BAILEYCO 2 | 69 | 5.2707 | 5.2707 | 0
GEN-2019-074 | 05 SOUTHWEST | 525179 | TULIA_TP 3 | 115 | 6.4624 | 6.4624 | 0
GEN-2019-074 | 05 SOUTHWEST | 525191 | KRESS_INT 2 | 69 | 4.4978 | 4.4978 | 0
GEN-2019-074 | 05 SOUTHWEST | 525226 | KRS_RURL_TP3 | 115 | 6.4399 | 6.4399 | 0
GEN-2019-074 | 05 SOUTHWEST | 525272 | KISER 3 | 115 | 5.2683 | 5.2683 | 0
GEN-2019-074 | 05 SOUTHWEST | 525291 | PLAINVW_TP 2 | 69 | 6.4824 | 6.4824 | 0
GEN-2019-074 | 05 SOUTHWEST | 525298 | S_PLAINVEW 2 | 69 | 2.5852 | 2.5852 | 0
GEN-2019-074 | 05 SOUTHWEST | 525325 | COX 2 | 69 | 3.4185 | 3.4185 | 0
GEN-2019-074 | 05 SOUTHWEST | 525413 | LAMTON 2 | 69 | 5.1693 | 5.1693 | 0
GEN-2019-074 | 05 SOUTHWEST | 525432 | SP-HALFWAY+2 | 69 | 5.8641 | 5.8641 | 0
GEN-2019-074 | 05 SOUTHWEST | 525584 | BLUECLDCOL 6 | 230 | 10.4275 | 10.4275 | 0
GEN-2019-074 | 05 SOUTHWEST | 525613 | W_LITTLFLD 2 | 69 | 2.9684 | 2.9684 | 0
GEN-2019-074 | 05 SOUTHWEST | 525620 | LTFLD_S&CTY2 | 69 | 4.1727 | 4.1727 | 0
GEN-2019-074 | 05 SOUTHWEST | 525650 | LC-LTTLFLD+2 | 69 | 4.9319 | 4.9319 | 0
GEN-2019-074 | 05 SOUTHWEST | 525687 | LC-LUMSCHAP2 | 69 | 4.6126 | 4.6126 | 0
GEN-2019-074 | 05 SOUTHWEST | 525763 | CALLAHAN 3 | 115 | 5.5668 | 5.5668 | 0
GEN-2019-074 | 05 SOUTHWEST | 525780 | FLOYD_CNTY 3 | 115 | 6.2514 | 6.2514 | 0
GEN-2019-074 | 05 SOUTHWEST | 525816 | TUCO_INT2 2 | 69 | 4.6524 | 4.6524 | 0
GEN-2019-074 | 05 SOUTHWEST | 525826 | TUCO_INT 2 | 69 | 7.8538 | 7.8538 | 0
GEN-2019-074 | 05 SOUTHWEST | 525850 | ELK_CT1 | 345 | 13.9398 | 13.9398 | 0
GEN-2019-074 | 05 SOUTHWEST | 526019 | HOCKLEY 2 | 69 | 5.1105 | 5.1105 | 0
GEN-2019-074 | 05 SOUTHWEST | 526076 | STANTON_W 3 | 115 | 8.923 | 8.923 | 0
GEN-2019-074 | 05 SOUTHWEST | 526160 | CARLISLE 3 | 115 | 12.772 | 12.772 | 0
GEN-2019-074 | 05 SOUTHWEST | 526268 | LUBBCK_STH 3 | 115 | 17.6482 | 17.6482 | 0
GEN-2019-074 | 05 SOUTHWEST | 526298 | LUBBCK_EST 3 | 115 | 14.4141 | 14.4141 | 0
GEN-2019-074 | 05 SOUTHWEST | 526299 | LUBBCK_EST 6 | 230 | 11.0462 | 11.0462 | 0
GEN-2019-074 | 05 SOUTHWEST | 526361 | COCHRAN 3 | 115 | 6.4257 | 6.4257 | 0
GEN-2019-074 | 05 SOUTHWEST | 526452 | AMOCO_CRYO 3 | 115 | 6.362 | 6.362 | 0
GEN-2019-074 | 05 SOUTHWEST | 526475 | YUMA_INT 3 | 115 | 10.7034 | 10.7034 | 0
GEN-2019-074 | 05 SOUTHWEST | 526484 | LG-LEVELAND3 | 115 | 9.1775 | 9.1775 | 0
GEN-2019-074 | 05 SOUTHWEST | 526677 | GRASSLAND 6 | 230 | 5.9735 | 5.9735 | 0
GEN-2019-074 | 05 SOUTHWEST | 526736 | TERRY_CNTY 3 | 115 | 10.6679 | 10.6679 | 0
GEN-2019-074 | 05 SOUTHWEST | 526934 | YOAKUM 3 | 115 | 19.2326 | 19.2326 | 0
GEN-2019-074 | 05 SOUTHWEST | 526936 | YOAKUM_345 | 345 | 9.9314 | 9.9314 | 0
GEN-2019-074 | 05 SOUTHWEST | 527009 | BRU_SUB 6 | 230 | 15.6513 | 15.6513 | 0
GEN-2019-074 | 05 SOUTHWEST | 527028 | INK_BASIN 6 | 230 | 11.2413 | 11.2413 | 0
GEN-2019-074 | 05 SOUTHWEST | 527149 | MUSTANG 6 | 230 | 17.9238 | 17.9238 | 0
GEN-2019-074 | 05 SOUTHWEST | 527610 | SAGA_SCOL 7 | 345 | 10.2321 | 10.2321 | 0
GEN-2019-074 | 05 SOUTHWEST | 527655 | RSVLT_CC_E 7 | 345 | 10.0154 | 10.0154 | 0
GEN-2019-074 | 05 SOUTHWEST | 527802 | EDDY_CNTY 7 | 345 | 7.3273 | 7.3273 | 0
GEN-2019-074 | 05 SOUTHWEST | 527896 | HOBBS_INT 7 | 345 | 12.0143 | 12.0143 | 0
GEN-2019-074 | 05 SOUTHWEST | 560022 | CRAWFISH_DR | 345 | 13.842 | 13.842 | 0
GEN-2019-074 | 05 SOUTHWEST | 560035 | GRAPEVINE | 345 | 6.4589 | 6.4589 | 0
GEN-2019-074 | 05 SOUTHWEST | 511553 | CHISHOLM7 | 345 | 12.3397 | 12.3397 | 0
GEN-2019-074 | 05 SOUTHWEST | 515458 | BORDER 7 | 345 | 8.2517 | 8.2517 | 0
GEN-2019-074 | 05 SOUTHWEST | 515554 | BVRCNTY7 | 345 | 15.3093 | 15.3093 | 0
GEN-2019-074 | 05 SOUTHWEST | 522800 | MU-TULIA 3 | 115 | 5.2034 | 5.2034 | 0
GEN-2019-074 | 05 SOUTHWEST | 523095 | HITCHLAND 6 | 230 | 14.5761 | 14.5761 | 0
GEN-2019-074 | 05 SOUTHWEST | 523101 | NOBLE_WND 7 | 345 | 14.9103 | 14.9103 | 0
GEN-2019-074 | 05 SOUTHWEST | 523112 | NOVUS1 7 | 345 | 14.6716 | 14.6716 | 0
GEN-2019-074 | 05 SOUTHWEST | 523220 | XIT_INTG 3 | 115 | 5.8284 | 5.8284 | 0
GEN-2019-074 | 05 SOUTHWEST | 523266 | PRINGLE 3 | 115 | 11.3365 | 11.3365 | 0
GEN-2019-074 | 05 SOUTHWEST | 523308 | MOORE_E 3 | 115 | 10.3425 | 10.3425 | 0
GEN-2019-074 | 05 SOUTHWEST | 523332 | EXELL_TP 3 | 115 | 7.627 | 7.627 | 0
GEN-2019-074 | 05 SOUTHWEST | 523339 | FAIN 3 | 115 | 8.4872 | 8.4872 | 0
GEN-2019-074 | 05 SOUTHWEST | 523551 | HUTCHISON 6 | 230 | 7.288 | 7.288 | 0
GEN-2019-074 | 05 SOUTHWEST | 523771 | GRAPEVINE 6 | 230 | 5.9762 | 5.9762 | 0
GEN-2019-074 | 05 SOUTHWEST | 523823 | CARPENTER 7 | 345 | 6.5781 | 6.5781 | 0
GEN-2019-074 | 05 SOUTHWEST | 524009 | CHERRY 3 | 115 | 18.7893 | 18.7893 | 0
GEN-2019-074 | 05 SOUTHWEST | 524043 | NICHOLS 3 | 115 | 30.649 | 30.649 | 0
GEN-2019-074 | 05 SOUTHWEST | 524106 | NORTHWEST 3 | 115 | 11.5491 | 11.5491 | 0
GEN-2019-074 | 05 SOUTHWEST | 524136 | HASTINGS 3 | 115 | 14.3234 | 14.3234 | 0
GEN-2019-074 | 05 SOUTHWEST | 524163 | EAST_PLANT 6 | 230 | 13.8955 | 13.8955 | 0
GEN-2019-074 | 05 SOUTHWEST | 524243 | OUTPOST 3 | 115 | 10.275 | 10.275 | 0
GEN-2019-074 | 05 SOUTHWEST | 524276 | WILDOR_WND 6 | 230 | 5.2234 | 5.2234 | 0
GEN-2019-074 | 05 SOUTHWEST | 524299 | SPNSPUR_COL7 | 345 | 5.3278 | 5.3278 | 0
GEN-2019-074 | 05 SOUTHWEST | 524364 | RANDALL 3 | 115 | 21.0733 | 21.0733 | 0
GEN-2019-074 | 05 SOUTHWEST | 524377 | FARMERS 3 | 115 | 15.4368 | 15.4368 | 0
GEN-2019-074 | 05 SOUTHWEST | 524397 | ARROWHEAD 3 | 115 | 13.6793 | 13.6793 | 0
GEN-2019-074 | 05 SOUTHWEST | 524404 | OWENSCORN 3 | 115 | 15.0594 | 15.0594 | 0
GEN-2019-074 | 05 SOUTHWEST | 524502 | NORTON 3 | 115 | 2.9186 | 2.9186 | 0
GEN-2019-074 | 05 SOUTHWEST | 524544 | SPRING_DRW 3 | 115 | 6.4069 | 6.4069 | 0
GEN-2019-074 | 05 SOUTHWEST | 524567 | NE_HEREFORD3 | 115 | 9.9092 | 9.9092 | 0
GEN-2019-074 | 05 SOUTHWEST | 524575 | DS-#25+ 3 | 115 | 10.215 | 10.215 | 0
GEN-2019-074 | 05 SOUTHWEST | 524606 | HEREFORD 3 | 115 | 11.1394 | 11.1394 | 0
GEN-2019-074 | 05 SOUTHWEST | 524669 | DS-#20 3 | 115 | 6.2762 | 6.2762 | 0
GEN-2019-074 | 05 SOUTHWEST | 524688 | DS-#3 2 | 69 | 2.9614 | 2.9614 | 0
GEN-2019-074 | 05 SOUTHWEST | 524721 | DS-#15&#19+2 | 69 | 3.5539 | 3.5539 | 0
GEN-2019-074 | 05 SOUTHWEST | 524728 | DS-CASTRO 2 | 69 | 4.2749 | 4.2749 | 0
GEN-2019-074 | 05 SOUTHWEST | 524764 | NORRIS_TP 3 | 115 | 11.4074 | 11.4074 | 0
GEN-2019-074 | 05 SOUTHWEST | 524773 | E_CLOVIS 3 | 115 | 8.962 | 8.962 | 0
GEN-2019-074 | 05 SOUTHWEST | 524776 | N_CLOVIS_TP3 | 115 | 7.4744 | 7.4744 | 0
GEN-2019-074 | 05 SOUTHWEST | 524797 | PERIMETER 3 | 115 | 6.5512 | 6.5512 | 0
GEN-2019-074 | 05 SOUTHWEST | 524821 | CURRY 2 | 69 | 4.4284 | 4.4284 | 0
GEN-2019-074 | 05 SOUTHWEST | 524831 | FE-HOLLAND 3 | 115 | 9.2431 | 9.2431 | 0
GEN-2019-074 | 05 SOUTHWEST | 524838 | FE-CLOVIS2+3 | 115 | 10.7942 | 10.7942 | 0
GEN-2019-074 | 05 SOUTHWEST | 524863 | FE-CHZPLT 3 | 115 | 8.0228 | 8.0228 | 0
GEN-2019-074 | 05 SOUTHWEST | 524889 | SN_JUAN_WND6 | 230 | 4.6556 | 4.6556 | 0
GEN-2019-074 | 05 SOUTHWEST | 524923 | PORTALES 2 | 69 | 7.5604 | 7.5604 | 0
GEN-2019-074 | 05 SOUTHWEST | 524935 | KILGORE 3 | 115 | 6.1488 | 6.1488 | 0
GEN-2019-074 | 05 SOUTHWEST | 524977 | GREYHOUND 3 | 115 | 5.6862 | 5.6862 | 0
GEN-2019-074 | 05 SOUTHWEST | 525008 | MULESH_CTY 2 | 69 | 4.2533 | 4.2533 | 0
GEN-2019-074 | 05 SOUTHWEST | 525017 | EMULESH&VLY2 | 69 | 4.2591 | 4.2591 | 0
GEN-2019-074 | 05 SOUTHWEST | 525023 | BC-BAIL_MTR2 | 69 | 5.2707 | 5.2707 | 0
GEN-2019-074 | 05 SOUTHWEST | 525132 | LC-N_OLTON 2 | 69 | 3.0771 | 3.0771 | 0
GEN-2019-074 | 05 SOUTHWEST | 525154 | HAPPY_INT 3 | 115 | 5.4569 | 5.4569 | 0
GEN-2019-074 | 05 SOUTHWEST | 525203 | SW-KRESS 2 | 69 | 4.4978 | 4.4978 | 0
GEN-2019-074 | 05 SOUTHWEST | 525224 | KRESS_RURL 2 | 69 | 2.5281 | 2.5281 | 0
GEN-2019-074 | 05 SOUTHWEST | 525225 | KRESS_RURAL3 | 115 | 5.9704 | 5.9704 | 0
GEN-2019-074 | 05 SOUTHWEST | 525257 | N_PLAINVEW 3 | 115 | 5.2521 | 5.2521 | 0
GEN-2019-074 | 05 SOUTHWEST | 525271 | KISER 2 | 69 | 3.4985 | 3.4985 | 0
GEN-2019-074 | 05 SOUTHWEST | 525279 | WSTRIDGE_TP3 | 69 | 4.2644 | 4.2644 | 0
GEN-2019-074 | 05 SOUTHWEST | 525307 | E_PLAINVEW 2 | 69 | 2.4781 | 2.4781 | 0
GEN-2019-074 | 05 SOUTHWEST | 525316 | LH-PROVDNCE2 | 69 | 3.4185 | 3.4185 | 0
GEN-2019-074 | 05 SOUTHWEST | 525339 | AIKEN_RURL 2 | 69 | 2.7745 | 2.7745 | 0
GEN-2019-074 | 05 SOUTHWEST | 525404 | LC-OLTON 2 | 69 | 4.4829 | 4.4829 | 0
GEN-2019-074 | 05 SOUTHWEST | 525425 | CORNER 2 | 69 | 3.6326 | 3.6326 | 0
GEN-2019-074 | 05 SOUTHWEST | 525606 | AMHERST 2 | 69 | 2.3408 | 2.3408 | 0
GEN-2019-074 | 05 SOUTHWEST | 525657 | W_ANTON_TP 2 | 69 | 4.1079 | 4.1079 | 0
GEN-2019-074 | 05 SOUTHWEST | 525694 | HOBGOOD 2 | 69 | 3.4381 | 3.4381 | 0
GEN-2019-074 | 05 SOUTHWEST | 525731 | SP-ABERNTHY2 | 69 | 3.0093 | 3.0093 | 0
GEN-2019-074 | 05 SOUTHWEST | 525738 | HALECENTER 2 | 69 | 2.4566 | 2.4566 | 0
GEN-2019-074 | 05 SOUTHWEST | 525745 | LH-HALECTR 2 | 69 | 2.4289 | 2.4289 | 0
GEN-2019-074 | 05 SOUTHWEST | 525779 | FLOYD_CNTY 2 | 69 | 5.401 | 5.401 | 0
GEN-2019-074 | 05 SOUTHWEST | 525803 | BLANCO 3 | 115 | 5.0451 | 5.0451 | 0
GEN-2019-074 | 05 SOUTHWEST | 525853 | LH-WIL&ELN+2 | 69 | 2.5404 | 2.5404 | 0
GEN-2019-074 | 05 SOUTHWEST | 525885 | SP-NEWDEAL 2 | 69 | 3.3073 | 3.3073 | 0
GEN-2019-074 | 05 SOUTHWEST | 525926 | CROSBY 3 | 115 | 4.7129 | 4.7129 | 0
GEN-2019-074 | 05 SOUTHWEST | 526009 | LC-LEVLND#22 | 69 | 4.2645 | 4.2645 | 0
GEN-2019-074 | 05 SOUTHWEST | 526012 | LOST_DRAW 3 | 115 | 5.5483 | 5.5483 | 0
GEN-2019-074 | 05 SOUTHWEST | 526042 | COBLE 2 | 69 | 2.2615 | 2.2615 | 0
GEN-2019-074 | 05 SOUTHWEST | 526048 | LVLNDCTY_TP2 | 69 | 4.2645 | 4.2645 | 0
GEN-2019-074 | 05 SOUTHWEST | 526109 | SP-ERSKINE 3 | 115 | 10.9787 | 10.9787 | 0
GEN-2019-074 | 05 SOUTHWEST | 526146 | INDIANA 3 | 115 | 9.3032 | 9.3032 | 0
GEN-2019-074 | 05 SOUTHWEST | 526159 | CARLISLE 2 | 69 | 2.5568 | 2.5568 | 0
GEN-2019-074 | 05 SOUTHWEST | 526162 | LP-DOUD_TP 3 | 115 | 11.325 | 11.325 | 0
GEN-2019-074 | 05 SOUTHWEST | 526192 | MURPHY 3 | 115 | 10.2503 | 10.2503 | 0
GEN-2019-074 | 05 SOUTHWEST | 526213 | ALLEN 3 | 115 | 10.4502 | 10.4502 | 0
GEN-2019-074 | 05 SOUTHWEST | 526267 | LUBBCK_STH 2 | 69 | 4.3104 | 4.3104 | 0
GEN-2019-074 | 05 SOUTHWEST | 526297 | LUBBCK_EST 2 | 69 | 7.8955 | 7.8955 | 0
GEN-2019-074 | 05 SOUTHWEST | 526360 | COCHRAN 2 | 69 | 5.6074 | 5.6074 | 0
GEN-2019-074 | 05 SOUTHWEST | 526481 | SP-WOLF_TP 3 | 115 | 10.8642 | 10.8642 | 0
GEN-2019-074 | 05 SOUTHWEST | 526491 | LG-CLAUENE 3 | 115 | 7.9267 | 7.9267 | 0
GEN-2019-074 | 05 SOUTHWEST | 526602 | WOODROW 3 | 115 | 9.1323 | 9.1323 | 0
GEN-2019-074 | 05 SOUTHWEST | 526676 | GRASSLAND 3 | 115 | 6.8633 | 6.8633 | 0
GEN-2019-074 | 05 SOUTHWEST | 526679 | CIRRUS_WND 6 | 230 | 4.6792 | 4.6792 | 0
GEN-2019-074 | 05 SOUTHWEST | 526735 | TERRY_CNTY 2 | 69 | 7.0347 | 7.0347 | 0
GEN-2019-074 | 05 SOUTHWEST | 526784 | AMOCOWASSON6 | 230 | 15.6353 | 15.6353 | 0
GEN-2019-074 | 05 SOUTHWEST | 526792 | PRENTICE 3 | 115 | 6.0286 | 6.0286 | 0
GEN-2019-074 | 05 SOUTHWEST | 526928 | PLAINS_INT 3 | 115 | 10.0196 | 10.0196 | 0
GEN-2019-074 | 05 SOUTHWEST | 527010 | OXYBRU 6 | 230 | 15.5052 | 15.5052 | 0
GEN-2019-074 | 05 SOUTHWEST | 527011 | XTO_MAHONEY6 | 230 | 15.3578 | 15.3578 | 0
GEN-2019-074 | 05 SOUTHWEST | 527027 | INK_BASIN 3 | 115 | 13.258 | 13.258 | 0
GEN-2019-074 | 05 SOUTHWEST | 527041 | ARCO_TP 3 | 115 | 13.6807 | 13.6807 | 0
GEN-2019-074 | 05 SOUTHWEST | 527130 | DENVER_N 3 | 115 | 22.5277 | 22.5277 | 0
GEN-2019-074 | 05 SOUTHWEST | 527146 | MUSTANG 3 | 115 | 24.0628 | 24.0628 | 0
GEN-2019-074 | 05 SOUTHWEST | 527151 | GS-MUSTANG 6 | 230 | 17.9238 | 17.9238 | 0
GEN-2019-074 | 05 SOUTHWEST | 527194 | LG-PLSHILL 3 | 115 | 7.9741 | 7.9741 | 0
GEN-2019-074 | 05 SOUTHWEST | 527257 | FLATLAND 3 | 115 | 6.6733 | 6.6733 | 0
GEN-2019-074 | 05 SOUTHWEST | 527276 | SEMINOLE 6 | 230 | 8.197 | 8.197 | 0
GEN-2019-074 | 05 SOUTHWEST | 527483 | CHAVES_CNTY6 | 230 | 4.4929 | 4.4929 | 0
GEN-2019-074 | 05 SOUTHWEST | 527599 | SAGA_SDCOL 7 | 345 | 10.2321 | 10.2321 | 0
GEN-2019-074 | 05 SOUTHWEST | 527654 | RSVLT_CC_W 7 | 345 | 8.7265 | 8.7265 | 0
GEN-2019-074 | 05 SOUTHWEST | 527799 | EDDY_NORTH 6 | 230 | 9.402 | 9.402 | 0
GEN-2019-074 | 05 SOUTHWEST | 527894 | HOBBS_INT 6 | 230 | 19.4767 | 19.4767 | 0
GEN-2019-074 | 05 SOUTHWEST | 527965 | KIOWA 7 | 345 | 8.82 | 8.82 | 0
GEN-2019-074 | 05 SOUTHWEST | 528027 | RDRUNNER 7 | 345 | 8.6815 | 8.6815 | 0
GEN-2019-074 | 05 SOUTHWEST | 576397 | G10014G11022 | 345 | 10.3812 | 10.3812 | 0
GEN-2019-074 | 05 SOUTHWEST | 762216 | G17-151TAP | 345 | 8.5119 | 8.5119 | 0
GEN-2019-074 | 05 SOUTHWEST | 763087 | GEN-2018-073 | 345 | 11.9423 | 11.9423 | 0
GEN-2019-074 | 05 SOUTHWEST | 763516 | GEN-2019-011 | 345 | 9.2852 | 9.2852 | 0

## SCRCCT
Study | Case Type | Region Name | Season Year | Season | Contingency Type | Contingency Definition | SCR | Critical_Clearing_Time | POI Bus | Stability Margin | Pg Out | Pg Rated
18021901 | TC | North | 23 | SP | base | N/A | 4.0901 | 0.1443 | GEN-2018-067 | 44.2722 | 128.9 | 149.5
18021901 | TC | North | 23 | SP | base | N/A | 4.0901 | 0.1341 | GEN-2018-067 | 34.1284 | 126.1 | 133.3
18021901 | TC | North | 23 | SP | base | N/A | 4.6089 | 0.1715 | GEN-2018-069 | 71.5215 | 125 | 123.5
18021901 | TC | North | 23 | SP | base | N/A | 4.6089 | 0.2848 | GEN-2019-023 | 184.7975 | 75.62 | 122.1
18021901 | TC | North | 23 | SP | base | N/A | 4.6089 | 5.009 | GEN-2019-023 | 4908.9774 | 34.38 | 59.5
18021901 | TC | North | 26 | L | base | N/A | 3.4783 | 0.145 | GEN-2018-067 | 44.9856 | 128.9 | 149.5
18021901 | TC | North | 26 | L | base | N/A | 3.4783 | 0.1349 | GEN-2018-067 | 34.9018 | 126.1 | 133.3
18021901 | TC | North | 26 | L | base | N/A | 4.0383 | 0.1727 | GEN-2018-069 | 72.6567 | 125 | 123.5
18021901 | TC | North | 26 | L | base | N/A | 4.0383 | 0.2614 | GEN-2019-023 | 161.3639 | 110 | 122.1
18021901 | TC | North | 26 | L | contingency149.sav | 655940-655941 | 2.7853 | 0 | GEN-2019-023 | 0 | 0 | 0
18021901 | TC | North | 26 | L | contingency149.sav | 655940-655941 | 116.5089 | 0 | GEN-2018-070 | 0 | 0 | 0
18021901 | TC | North | 26 | L | contingency149.sav | 655940-655941 | 18.8016 | 0 | GEN-2018-074 | 0 | 0 | 0
18021901 | TC | North | 26 | SP | base | N/A | 4.0968 | 0.1442 | GEN-2018-067 | 44.2146 | 128.9 | 149.5
18021901 | TC | North | 26 | SP | base | N/A | 4.0968 | 0.1341 | GEN-2018-067 | 34.0748 | 126.1 | 133.3
18021901 | TC | North | 26 | SP | base | N/A | 4.6404 | 0.1713 | GEN-2018-069 | 71.3203 | 125 | 123.5
18021901 | TC | North | 26 | SP | base | N/A | 4.6404 | 0.2838 | GEN-2019-023 | 183.7969 | 75.62 | 122.1
18021901 | TC | North | 26 | SP | base | N/A | 4.6404 | 5.6001 | GEN-2019-023 | 5500.1046 | 34.38 | 59.5
18021901 | TC | North | 26 | WP | base | N/A | 4.1004 | 0.144 | GEN-2018-067 | 44.029 | 128.9 | 149.5
18021901 | TC | North | 26 | WP | base | N/A | 4.1004 | 0.1339 | GEN-2018-067 | 33.9006 | 126.1 | 133.3
18021901 | TC | North | 26 | WP | base | N/A | 4.6946 | 0.1713 | GEN-2018-069 | 71.2868 | 125 | 123.5
18021901 | TC | North | 26 | WP | base | N/A | 4.6946 | 0.2839 | GEN-2019-023 | 183.8634 | 75.62 | 122.1
18021901 | TC | North | 26 | WP | base | N/A | 4.6946 | 5.1933 | GEN-2019-023 | 5093.3435 | 34.38 | 59.5
18021901 | TC | Nebraska | 23 | SP | base | N/A | 4.2157 | 0.7281 | GEN-2018-065 | 628.0702 | 19.8 | 22.9
18021901 | TC | Nebraska | 23 | SP | base | N/A | 4.2157 | 0.2027 | GEN-2018-068 | 102.6816 | 151.2 | 171.5
18021901 | TC | Nebraska | 23 | SP | base | N/A | 4.2157 | 0.2027 | GEN-2018-068 | 102.6816 | 151.2 | 171.5
18021901 | TC | Nebraska | 23 | SP | base | N/A | 4.2157 | 0.1077 | GEN-2018-131 | 7.7164 | 221.4 | 251.1
18021901 | TC | Nebraska | 23 | SP | base | N/A | 4.2157 | 0.1228 | GEN-2018-132 | 22.7819 | 201.6 | 226.8
18021901 | TC | Nebraska | 23 | SP | base | N/A | 17.5256 | 0.0711 | GEN-2018-125 | -28.8916 | 231 | 259.1
18021901 | TC | Nebraska | 23 | SP | base | N/A | 5.2861 | 0.1543 | GEN-2019-033 | 54.3038 | 182 | 198.4
18021901 | TC | Nebraska | 23 | SP | contingency94.sav | 640124-763718 | 1.8189 | 0.3788 | GEN-2019-039 | 278.7806 | 174.5 | 206.6
18021901 | TC | Nebraska | 23 | SP | contingency129.sav | 640226-763982 | 4.8299 | 0.2357 | GEN-2018-083 | 135.7023 | 125 | 141
18021901 | TC | Nebraska | 23 | SP | contingency129.sav | 640226-763982 | 4.8299 | 0.2357 | GEN-2018-083 | 135.7023 | 125 | 141
18021901 | TC | Nebraska | 23 | SP | contingency129.sav | 640226-763982 | 4.8299 | 17.5539 | GEN-2019-069 | 17453.869 | 100 | 113.4
18021901 | TC | Nebraska | 23 | SP | contingency129.sav | 640226-763982 | 4.8299 | 24.3399 | GEN-2019-070 | 24239.9059 | 50 | 58.8
18021901 | TC | Nebraska | 23 | SP | contingency162.sav | 640342-763982 | 5.971 | 0.2336 | GEN-2018-083 | 133.5545 | 125 | 141
18021901 | TC | Nebraska | 23 | SP | contingency162.sav | 640342-763982 | 5.971 | 0.2336 | GEN-2018-083 | 133.5545 | 125 | 141
18021901 | TC | Nebraska | 23 | SP | contingency162.sav | 640342-763982 | 5.971 | 16.9869 | GEN-2019-069 | 16886.8766 | 100 | 113.4
18021901 | TC | Nebraska | 23 | SP | contingency162.sav | 640342-763982 | 5.971 | 23.5738 | GEN-2019-070 | 23473.8152 | 50 | 58.8
18021901 | TC | Nebraska | 26 | L | base | 640226-640520 | 3.7772 | 0.7307 | GEN-2018-065 | 630.7346 | 19.8 | 22.9
18021901 | TC | Nebraska | 26 | L | base | 640226-640520 | 3.7772 | 0.2033 | GEN-2018-068 | 103.3435 | 151.2 | 171.5
18021901 | TC | Nebraska | 26 | L | base | 640226-640520 | 3.7772 | 0.2033 | GEN-2018-068 | 103.3435 | 151.2 | 171.5
18021901 | TC | Nebraska | 26 | L | base | 640226-640520 | 13.1412 | 0.071 | GEN-2018-125 | -28.978 | 231 | 259.1
18021901 | TC | Nebraska | 26 | L | contingency130.sav | 640226-763982 | 4.4302 | 0.236 | GEN-2018-083 | 136.0428 | 125 | 141
18021901 | TC | Nebraska | 26 | L | contingency130.sav | 640226-763982 | 4.4302 | 0.236 | GEN-2018-083 | 136.0428 | 125 | 141
18021901 | TC | Nebraska | 26 | L | contingency163.sav | 640342-763982 | 5.1322 | 0.234 | GEN-2018-083 | 134.0182 | 125 | 141
18021901 | TC | Nebraska | 26 | L | contingency163.sav | 640342-763982 | 5.1322 | 0.234 | GEN-2018-083 | 134.0182 | 125 | 141
18021901 | TC | Nebraska | 26 | SP | base | 640226-640520 | 4.2306 | 0.7286 | GEN-2018-065 | 628.5968 | 19.8 | 22.9
18021901 | TC | Nebraska | 26 | SP | base | 640226-640520 | 4.2306 | 0.2028 | GEN-2018-068 | 102.7769 | 151.2 | 171.5
18021901 | TC | Nebraska | 26 | SP | base | 640226-640520 | 4.2306 | 0.2028 | GEN-2018-068 | 102.7769 | 151.2 | 171.5
18021901 | TC | Nebraska | 26 | SP | base | 640226-640520 | 4.2306 | 0.1078 | GEN-2018-131 | 7.8249 | 221.4 | 251.1
18021901 | TC | Nebraska | 26 | SP | base | 640226-640520 | 4.2306 | 0.123 | GEN-2018-132 | 23.0196 | 201.6 | 226.8
18021901 | TC | Nebraska | 26 | SP | base | 640226-640520 | 17.8864 | 0.0712 | GEN-2018-125 | -28.7615 | 231 | 259.1
18021901 | TC | Nebraska | 26 | SP | base | 640226-640520 | 5.3855 | 0.1536 | GEN-2019-033 | 53.6016 | 182 | 198.4
18021901 | TC | Nebraska | 26 | SP | contingency94.sav | 640124-763718 | 1.8189 | 0.3788 | GEN-2019-039 | 278.76 | 174.5 | 206.6
18021901 | TC | Nebraska | 26 | SP | contingency130.sav | 640226-763982 | 4.843 | 0.2356 | GEN-2018-083 | 135.6275 | 125 | 141
18021901 | TC | Nebraska | 26 | SP | contingency130.sav | 640226-763982 | 4.843 | 0.2356 | GEN-2018-083 | 135.6275 | 125 | 141
18021901 | TC | Nebraska | 26 | SP | contingency130.sav | 640226-763982 | 4.843 | 17.53 | GEN-2019-069 | 17429.9695 | 100 | 113.4
18021901 | TC | Nebraska | 26 | SP | contingency130.sav | 640226-763982 | 4.843 | 24.3134 | GEN-2019-070 | 24213.418 | 50 | 58.8
18021901 | TC | Nebraska | 26 | SP | contingency163.sav | 640342-763982 | 5.9864 | 0.2336 | GEN-2018-083 | 133.5516 | 125 | 141
18021901 | TC | Nebraska | 26 | SP | contingency163.sav | 640342-763982 | 5.9864 | 0.2336 | GEN-2018-083 | 133.5516 | 125 | 141
18021901 | TC | Nebraska | 26 | SP | contingency163.sav | 640342-763982 | 5.9864 | 16.9881 | GEN-2019-069 | 16888.0834 | 100 | 113.4
18021901 | TC | Nebraska | 26 | SP | contingency163.sav | 640342-763982 | 5.9864 | 23.5751 | GEN-2019-070 | 23475.0694 | 50 | 58.8
18021901 | TC | Nebraska | 26 | WP | base | 640226-640520 | 4.1425 | 0.7292 | GEN-2018-065 | 629.2181 | 19.8 | 22.9
18021901 | TC | Nebraska | 26 | WP | base | 640226-640520 | 4.1425 | 0.2032 | GEN-2018-068 | 103.2476 | 151.2 | 171.5
18021901 | TC | Nebraska | 26 | WP | base | 640226-640520 | 4.1425 | 0.2032 | GEN-2018-068 | 103.2476 | 151.2 | 171.5
18021901 | TC | Nebraska | 26 | WP | base | 640226-640520 | 4.1425 | 0.1083 | GEN-2018-131 | 8.2595 | 221.4 | 251.1
18021901 | TC | Nebraska | 26 | WP | base | 640226-640520 | 4.1425 | 0.1239 | GEN-2018-132 | 23.8961 | 201.6 | 226.8
18021901 | TC | Nebraska | 26 | WP | base | 640226-640520 | 17.3884 | 0.071 | GEN-2018-125 | -29.0478 | 231 | 259.1
18021901 | TC | Nebraska | 26 | WP | base | 640226-640520 | 5.2821 | 0.1556 | GEN-2019-033 | 55.6124 | 182 | 198.4
18021901 | TC | Nebraska | 26 | WP | contingency94.sav | 640124-763718 | 1.7638 | 0.3849 | GEN-2019-039 | 284.9403 | 174.5 | 206.6
18021901 | TC | Nebraska | 26 | WP | contingency129.sav | 640226-640520 | 5.3813 | 0 | GEN-2018-083 | 0 | 0 | 0
18021901 | TC | Nebraska | 26 | WP | contingency129.sav | 640226-640520 | 5.3813 | 0 | GEN-2018-083 | 0 | 0 | 0
18021901 | TC | Nebraska | 26 | WP | contingency129.sav | 640226-640520 | 5.3813 | 0 | GEN-2019-069 | 0 | 0 | 0
18021901 | TC | Nebraska | 26 | WP | contingency129.sav | 640226-640520 | 5.3813 | 0 | GEN-2019-070 | 0 | 0 | 0
18021901 | TC | Nebraska | 26 | WP | contingency129.sav | 640226-640520 | 53.1379 | 0 | GEN-2018-090 | 0 | 0 | 0
18021901 | TC | Nebraska | 26 | WP | contingency129.sav | 640226-640520 | 18.6776 | 0 | GEN-2019-009 | 0 | 0 | 0
18021901 | TC | Nebraska | 26 | WP | contingency129.sav | 640226-640520 | 4.5504 | 0 | GEN-2019-029 | 0 | 0 | 0
18021901 | TC | Nebraska | 26 | WP | contingency129.sav | 640226-640520 | 4.9445 | 0 | GEN-2019-039 | 0 | 0 | 0
18021901 | TC | Nebraska | 26 | WP | contingency129.sav | 640226-640520 | 70.4823 | 0 | GEN-2019-041 | 0 | 0 | 0
18021901 | TC | Nebraska | 26 | WP | contingency129.sav | 640226-640520 | 70.4823 | 0 | GEN-2019-041 | 0 | 0 | 0
18021901 | TC | Nebraska | 26 | WP | contingency130.sav | 640226-763982 | 4.6611 | 0.2356 | GEN-2018-083 | 135.5551 | 125 | 141
18021901 | TC | Nebraska | 26 | WP | contingency130.sav | 640226-763982 | 4.6611 | 0.2356 | GEN-2018-083 | 135.5551 | 125 | 141
18021901 | TC | Nebraska | 26 | WP | contingency130.sav | 640226-763982 | 4.6611 | 17.6302 | GEN-2019-069 | 17530.2153 | 100 | 113.4
18021901 | TC | Nebraska | 26 | WP | contingency130.sav | 640226-763982 | 4.6611 | 24.4618 | GEN-2019-070 | 24361.7948 | 50 | 58.8
18021901 | TC | Nebraska | 26 | WP | contingency143.sav | 640252-763666 | 8.8571 | 0 | GEN-2018-083 | 0 | 0 | 0
18021901 | TC | Nebraska | 26 | WP | contingency143.sav | 640252-763666 | 8.8571 | 0 | GEN-2018-083 | 0 | 0 | 0
18021901 | TC | Nebraska | 26 | WP | contingency143.sav | 640252-763666 | 8.8571 | 0 | GEN-2019-069 | 0 | 0 | 0
18021901 | TC | Nebraska | 26 | WP | contingency143.sav | 640252-763666 | 8.8571 | 0 | GEN-2019-070 | 0 | 0 | 0
18021901 | TC | Nebraska | 26 | WP | contingency143.sav | 640252-763666 | 60.1628 | 0 | GEN-2018-090 | 0 | 0 | 0
18021901 | TC | Nebraska | 26 | WP | contingency143.sav | 640252-763666 | 19.692 | 0 | GEN-2019-009 | 0 | 0 | 0
18021901 | TC | Nebraska | 26 | WP | contingency143.sav | 640252-763666 | 6.7635 | 0 | GEN-2019-029 | 0 | 0 | 0
18021901 | TC | Nebraska | 26 | WP | contingency143.sav | 640252-763666 | 7.7584 | 0 | GEN-2019-039 | 0 | 0 | 0
18021901 | TC | Nebraska | 26 | WP | contingency143.sav | 640252-763666 | 77.0972 | 0 | GEN-2019-041 | 0 | 0 | 0
18021901 | TC | Nebraska | 26 | WP | contingency143.sav | 640252-763666 | 77.0972 | 0 | GEN-2019-041 | 0 | 0 | 0
18021901 | TC | Nebraska | 26 | WP | contingency163.sav | 640342-763982 | 5.8896 | 0.2335 | GEN-2018-083 | 133.5212 | 125 | 141
18021901 | TC | Nebraska | 26 | WP | contingency163.sav | 640342-763982 | 5.8896 | 0.2335 | GEN-2018-083 | 133.5212 | 125 | 141
18021901 | TC | Nebraska | 26 | WP | contingency163.sav | 640342-763982 | 5.8896 | 16.9324 | GEN-2019-069 | 16832.3812 | 100 | 113.4
18021901 | TC | Nebraska | 26 | WP | contingency163.sav | 640342-763982 | 5.8896 | 23.5098 | GEN-2019-070 | 23409.7692 | 50 | 58.8
18021901 | TC | Central | 23 | SP | base | N/A | 29.04 | 0.0766 | GEN-2018-128 | -23.3963 | 200.22 | 230.8
18021901 | TC | Central | 23 | SP | contingency68.sav | 539666-539689 | 5.781 | 69.1765 | GEN-2018-116 | 69076.4825 | 2.41 | 3.1
18021901 | TC | Central | 23 | SP | contingency68.sav | 539666-539689 | 5.781 | 24.3493 | GEN-2018-116 | 24249.3245 | 147.59 | 192.9
18021901 | TC | Central | 23 | SP | contingency68.sav | 539666-539689 | 5.781 | 8.478 | GEN-2019-051 | 8377.9588 | 40 | 63
18021901 | TC | Central | 23 | SP | contingency72.sav | 539678-539681 | 5.1211 | 291.3821 | GEN-2018-116 | 291282.1301 | 2.41 | 3.1
18021901 | TC | Central | 23 | SP | contingency72.sav | 539678-539681 | 5.1211 | 0.0475 | GEN-2018-116 | -52.4598 | 147.59 | 192.9
18021901 | TC | Central | 23 | SP | contingency72.sav | 539678-539681 | 5.1211 | 19.9619 | GEN-2019-051 | 19861.9336 | 40 | 63
18021901 | TC | Central | 23 | SP | contingency117.sav | 300101-547478 | 5.3438 | 210.2953 | GEN-2019-016 | 210195.3168 | 200 | 220.2
18021901 | TC | Central | 23 | SP | contingency265.sav | 539679-763862 | 4.1704 | 50.2934 | GEN-2019-054 | 50193.4088 | 2.78 | 3.1
18021901 | TC | Central | 23 | SP | contingency265.sav | 539679-763862 | 4.1704 | 7.205 | GEN-2019-054 | 7105.0388 | 147.22 | 192.9
18021901 | TC | Central | 23 | SP | contingency266.sav | 539681-539661 | 5.0555 | 457.3978 | GEN-2018-116 | 457297.8476 | 2.41 | 3.1
18021901 | TC | Central | 23 | SP | contingency266.sav | 539681-539661 | 5.0555 | 0.0476 | GEN-2018-116 | -52.3658 | 147.59 | 192.9
18021901 | TC | Central | 23 | SP | contingency266.sav | 539681-539661 | 5.0555 | 18.2285 | GEN-2019-051 | 18128.5169 | 40 | 63
18021901 | TC | Central | 23 | SP | contingency268.sav | 539689-539661 | 5.7442 | 65.2026 | GEN-2018-116 | 65102.5623 | 2.41 | 3.1
18021901 | TC | Central | 23 | SP | contingency268.sav | 539689-539661 | 5.7442 | 19.0857 | GEN-2018-116 | 18985.6803 | 147.59 | 192.9
18021901 | TC | Central | 23 | SP | contingency268.sav | 539689-539661 | 5.7442 | 8.1593 | GEN-2019-051 | 8059.281 | 40 | 63
18021901 | TC | Central | 23 | SP | contingency270.sav | 539695-763850 | 5.2392 | 4.0865 | GEN-2019-053 | 3986.5419 | 50 | 77
18021901 | TC | Central | 23 | SP | contingency270.sav | 539695-763850 | 5.2392 | 45.0331 | GEN-2019-055 | 44933.128 | 2.45 | 3.1
18021901 | TC | Central | 23 | SP | contingency270.sav | 539695-763850 | 5.2392 | 5.5178 | GEN-2019-055 | 5417.8271 | 147.55 | 189.6
18021901 | TC | Central | 23 | SP | contingency383.sav | 532796-532782(1):532796-532782(2) | 3.2583 | 56.4572 | GEN-2018-116 | 56357.1738 | 2.41 | 3.1
18021901 | TC | Central | 23 | SP | contingency383.sav | 532796-532782(1):532796-532782(2) | 3.2583 | 12.5109 | GEN-2018-116 | 12410.9254 | 147.59 | 192.9
18021901 | TC | Central | 23 | SP | contingency383.sav | 532796-532782(1):532796-532782(2) | 3.2583 | 6.3167 | GEN-2019-051 | 6216.7385 | 40 | 63
18021901 | TC | Central | 26 | L | base | N/A | 25.0595 | 0.0773 | GEN-2018-128 | -22.7166 | 200.22 | 230.8
18021901 | TC | Central | 26 | SP | base | N/A | 29.5538 | 0.1001 | GEN-2018-128 | 0.1323 | 200.22 | 230.8
18021901 | TC | Central | 26 | SP | contingency68.sav | 539666-539689 | 5.8222 | 68.2899 | GEN-2018-116 | 68189.8838 | 2.41 | 3.1
18021901 | TC | Central | 26 | SP | contingency68.sav | 539666-539689 | 5.8222 | 22.4632 | GEN-2018-116 | 22363.1874 | 147.59 | 192.9
18021901 | TC | Central | 26 | SP | contingency68.sav | 539666-539689 | 5.8222 | 7.7253 | GEN-2019-051 | 7625.3471 | 40 | 63
18021901 | TC | Central | 26 | SP | contingency72.sav | 539678-539681 | 5.148 | 353.5421 | GEN-2018-116 | 353442.0852 | 2.41 | 3.1
18021901 | TC | Central | 26 | SP | contingency72.sav | 539678-539681 | 5.148 | 0.0472 | GEN-2018-116 | -52.7786 | 147.59 | 192.9
18021901 | TC | Central | 26 | SP | contingency72.sav | 539678-539681 | 5.148 | 18.3894 | GEN-2019-051 | 18289.3518 | 40 | 63
18021901 | TC | Central | 26 | SP | contingency117.sav | 300101-547478 | 5.3322 | 214.0867 | GEN-2019-016 | 213986.6621 | 200 | 220.2
18021901 | TC | Central | 26 | SP | contingency265.sav | 539679-763862 | 4.2092 | 49.8197 | GEN-2019-054 | 49719.6524 | 2.78 | 3.1
18021901 | TC | Central | 26 | SP | contingency265.sav | 539679-763862 | 4.2092 | 7.0518 | GEN-2019-054 | 6951.7554 | 147.22 | 192.9
18021901 | TC | Central | 26 | SP | contingency266.sav | 539681-539661 | 5.0809 | 346.3486 | GEN-2018-116 | 346248.5824 | 2.41 | 3.1
18021901 | TC | Central | 26 | SP | contingency266.sav | 539681-539661 | 5.0809 | 0.0473 | GEN-2018-116 | -52.6795 | 147.59 | 192.9
18021901 | TC | Central | 26 | SP | contingency266.sav | 539681-539661 | 5.0809 | 16.8403 | GEN-2019-051 | 16740.3193 | 40 | 63
18021901 | TC | Central | 26 | SP | contingency268.sav | 539689-539661 | 5.7846 | 64.4331 | GEN-2018-116 | 64333.1123 | 2.41 | 3.1
18021901 | TC | Central | 26 | SP | contingency268.sav | 539689-539661 | 5.7846 | 17.8039 | GEN-2018-116 | 17703.9323 | 147.59 | 192.9
18021901 | TC | Central | 26 | SP | contingency268.sav | 539689-539661 | 5.7846 | 7.4603 | GEN-2019-051 | 7360.3363 | 40 | 63
18021901 | TC | Central | 26 | SP | contingency270.sav | 539695-763850 | 5.2515 | 4.1962 | GEN-2019-053 | 4096.1832 | 50 | 77
18021901 | TC | Central | 26 | SP | contingency270.sav | 539695-763850 | 5.2515 | 45.0385 | GEN-2019-055 | 44938.4813 | 2.45 | 3.1
18021901 | TC | Central | 26 | SP | contingency270.sav | 539695-763850 | 5.2515 | 5.5757 | GEN-2019-055 | 5475.7298 | 147.55 | 189.6
18021901 | TC | Central | 26 | SP | contingency383.sav | 532796-532782(1):532796-532782(2) | 1.8789 | 56.1841 | GEN-2018-116 | 56084.1398 | 2.41 | 3.1
18021901 | TC | Central | 26 | SP | contingency383.sav | 532796-532782(1):532796-532782(2) | 1.8789 | 12.7558 | GEN-2018-116 | 12655.8378 | 147.59 | 192.9
18021901 | TC | Central | 26 | SP | contingency383.sav | 532796-532782(1):532796-532782(2) | 1.8789 | 6.3751 | GEN-2019-051 | 6275.0568 | 40 | 63
18021901 | TC | Central | 26 | SP | contingency383.sav | 532796-532782(1):532796-532782(2) | 4.9797 | 36.3566 | GEN-2019-054 | 36256.6156 | 2.78 | 3.1
18021901 | TC | Central | 26 | SP | contingency383.sav | 532796-532782(1):532796-532782(2) | 4.9797 | 4.4051 | GEN-2019-054 | 4305.0876 | 147.22 | 192.9
18021901 | TC | Central | 26 | WP | base | N/A | 28.2706 | 0.0748 | GEN-2018-128 | -25.219 | 200.22 | 230.8
18021901 | TC | Central | 26 | WP | contingency68.sav | 539666-539689 | 5.816 | 62.634 | GEN-2018-116 | 62534.015 | 2.41 | 3.1
18021901 | TC | Central | 26 | WP | contingency68.sav | 539666-539689 | 5.816 | 15.9544 | GEN-2018-116 | 15854.4247 | 147.59 | 192.9
18021901 | TC | Central | 26 | WP | contingency68.sav | 539666-539689 | 5.816 | 7.0979 | GEN-2019-051 | 6997.9331 | 40 | 63
18021901 | TC | Central | 26 | WP | contingency72.sav | 539678-539681 | 5.1062 | 173.3548 | GEN-2018-116 | 173254.7807 | 2.41 | 3.1
18021901 | TC | Central | 26 | WP | contingency72.sav | 539678-539681 | 5.1062 | 0.0474 | GEN-2018-116 | -52.6119 | 147.59 | 192.9
18021901 | TC | Central | 26 | WP | contingency72.sav | 539678-539681 | 5.1062 | 15.0781 | GEN-2019-051 | 14978.1083 | 40 | 63
18021901 | TC | Central | 26 | WP | contingency117.sav | 300101-547478 | 5.2719 | 324.2164 | GEN-2019-016 | 324116.4053 | 200 | 220.2
18021901 | TC | Central | 26 | WP | contingency265.sav | 539679-763862 | 4.21 | 48.8026 | GEN-2019-054 | 48702.6472 | 2.78 | 3.1
18021901 | TC | Central | 26 | WP | contingency265.sav | 539679-763862 | 4.21 | 6.5974 | GEN-2019-054 | 6497.3963 | 147.22 | 192.9
18021901 | TC | Central | 26 | WP | contingency266.sav | 539681-539661 | 5.0669 | 143.7655 | GEN-2018-116 | 143665.5254 | 2.41 | 3.1
18021901 | TC | Central | 26 | WP | contingency266.sav | 539681-539661 | 5.0669 | 0.0474 | GEN-2018-116 | -52.5843 | 147.59 | 192.9
18021901 | TC | Central | 26 | WP | contingency266.sav | 539681-539661 | 5.0669 | 13.9963 | GEN-2019-051 | 13896.261 | 40 | 63
18021901 | TC | Central | 26 | WP | contingency268.sav | 539689-539661 | 5.7929 | 60.5642 | GEN-2018-116 | 60464.1941 | 2.41 | 3.1
18021901 | TC | Central | 26 | WP | contingency268.sav | 539689-539661 | 5.7929 | 14.2069 | GEN-2018-116 | 14106.8864 | 147.59 | 192.9
18021901 | TC | Central | 26 | WP | contingency268.sav | 539689-539661 | 5.7929 | 6.9452 | GEN-2019-051 | 6845.2162 | 40 | 63
18021901 | TC | Central | 26 | WP | contingency270.sav | 539695-763850 | 5.2345 | 4.6155 | GEN-2019-053 | 4515.5181 | 50 | 77
18021901 | TC | Central | 26 | WP | contingency270.sav | 539695-763850 | 5.2345 | 44.7075 | GEN-2019-055 | 44607.4982 | 2.45 | 3.1
18021901 | TC | Central | 26 | WP | contingency270.sav | 539695-763850 | 5.2345 | 5.7038 | GEN-2019-055 | 5603.8287 | 147.55 | 189.6
18021901 | TC | Central | 26 | WP | contingency383.sav | 532796-532782(1):532796-532782(2) | 3.0923 | 51.2379 | GEN-2018-116 | 51137.8592 | 2.41 | 3.1
18021901 | TC | Central | 26 | WP | contingency383.sav | 532796-532782(1):532796-532782(2) | 3.0923 | 8.677 | GEN-2018-116 | 8577.0376 | 147.59 | 192.9
18021901 | TC | Central | 26 | WP | contingency383.sav | 532796-532782(1):532796-532782(2) | 3.0923 | 5.3672 | GEN-2019-051 | 5267.2483 | 40 | 63
18021901 | TC | Central | 26 | WP | contingency383.sav | 532796-532782(1):532796-532782(2) | 1.9648 | 19.8297 | GEN-2019-044 | 19729.6763 | 100 | 113.4
18021901 | TC | Central | 26 | WP | contingency383.sav | 532796-532782(1):532796-532782(2) | 2.9674 | 3.5653 | GEN-2019-053 | 3465.2845 | 50 | 77
18021901 | TC | Central | 26 | WP | contingency383.sav | 532796-532782(1):532796-532782(2) | 2.9674 | 35.6198 | GEN-2019-055 | 35519.784 | 2.45 | 3.1
18021901 | TC | Central | 26 | WP | contingency383.sav | 532796-532782(1):532796-532782(2) | 2.9674 | 4.2579 | GEN-2019-055 | 4157.9345 | 147.55 | 189.6
18021901 | TC | Central | 26 | WP | contingency383.sav | 532796-532782(1):532796-532782(2) | 5.5513 | 36.0365 | GEN-2019-054 | 35936.4757 | 2.78 | 3.1
18021901 | TC | Central | 26 | WP | contingency383.sav | 532796-532782(1):532796-532782(2) | 5.5513 | 3.911 | GEN-2019-054 | 3810.9591 | 147.22 | 192.9
18021901 | TC | Southeast | 23 | SP | contingency37.sav | 510370-510379-510380 | 4.9753 | 42.2073 | GEN-2018-079 | 42107.2585 | 148 | 168
18021901 | TC | Southeast | 23 | SP | contingency234.sav | 510379-763113 | 4.9642 | 39.3062 | GEN-2018-079 | 39206.1849 | 148 | 168
18021901 | TC | Southeast | 23 | SP | contingency488.sav | 560022-525832(1):560022-525832(2) | 1.9942 | 0 | GEN-2018-064 | 0 | 0 | 0
18021901 | TC | Southeast | 23 | SP | contingency488.sav | 560022-525832(1):560022-525832(2) | 5.4087 | 0 | GEN-2018-071 | 0 | 0 | 0
18021901 | TC | Southeast | 23 | SP | contingency488.sav | 560022-525832(1):560022-525832(2) | 5.4087 | 0 | GEN-2018-072 | 0 | 0 | 0
18021901 | TC | Southeast | 23 | SP | contingency488.sav | 560022-525832(1):560022-525832(2) | 1.781 | 0 | GEN-2018-079 | 0 | 0 | 0
18021901 | TC | Southeast | 23 | SP | contingency488.sav | 560022-525832(1):560022-525832(2) | 12.4005 | 0 | GEN-2018-082 | 0 | 0 | 0
18021901 | TC | Southeast | 23 | SP | contingency488.sav | 560022-525832(1):560022-525832(2) | 12.4005 | 0 | GEN-2018-082 | 0 | 0 | 0
18021901 | TC | Southeast | 23 | SP | contingency488.sav | 560022-525832(1):560022-525832(2) | 13.3306 | 0 | GEN-2018-087 | 0 | 0 | 0
18021901 | TC | Southeast | 23 | SP | contingency488.sav | 560022-525832(1):560022-525832(2) | 13.3306 | 0 | GEN-2018-088 | 0 | 0 | 0
18021901 | TC | Southeast | 23 | SP | contingency488.sav | 560022-525832(1):560022-525832(2) | 5.9204 | 0 | GEN-2018-106 | 0 | 0 | 0
18021901 | TC | Southeast | 23 | SP | contingency488.sav | 560022-525832(1):560022-525832(2) | 8.4496 | 0 | GEN-2018-115 | 0 | 0 | 0
18021901 | TC | Southeast | 23 | SP | contingency488.sav | 560022-525832(1):560022-525832(2) | 8.4496 | 0 | GEN-2018-115 | 0 | 0 | 0
18021901 | TC | Southeast | 23 | SP | contingency488.sav | 560022-525832(1):560022-525832(2) | 38.1241 | 0 | GEN-2019-002 | 0 | 0 | 0
18021901 | TC | Southeast | 23 | SP | contingency488.sav | 560022-525832(1):560022-525832(2) | 5.1652 | 0 | GEN-2019-012 | 0 | 0 | 0
18021901 | TC | Southeast | 23 | SP | contingency488.sav | 560022-525832(1):560022-525832(2) | 10.157 | 0 | GEN-2019-013 | 0 | 0 | 0
18021901 | TC | Southeast | 23 | SP | contingency488.sav | 560022-525832(1):560022-525832(2) | 3.5671 | 0 | GEN-2019-045 | 0 | 0 | 0
18021901 | TC | Southeast | 26 | L | contingency57.sav | 511456-763215 | 7.7755 | 0 | GEN-2018-064 | 0 | 0 | 0
18021901 | TC | Southeast | 26 | L | contingency57.sav | 511456-763215 | 18.9382 | 0 | GEN-2018-071 | 0 | 0 | 0
18021901 | TC | Southeast | 26 | L | contingency57.sav | 511456-763215 | 18.9382 | 0 | GEN-2018-072 | 0 | 0 | 0
18021901 | TC | Southeast | 26 | L | contingency57.sav | 511456-763215 | 13.1262 | 0 | GEN-2018-079 | 0 | 0 | 0
18021901 | TC | Southeast | 26 | L | contingency57.sav | 511456-763215 | 35.622 | 0 | GEN-2018-082 | 0 | 0 | 0
18021901 | TC | Southeast | 26 | L | contingency57.sav | 511456-763215 | 35.622 | 0 | GEN-2018-082 | 0 | 0 | 0
18021901 | TC | Southeast | 26 | L | contingency57.sav | 511456-763215 | 30.9185 | 0 | GEN-2018-087 | 0 | 0 | 0
18021901 | TC | Southeast | 26 | L | contingency57.sav | 511456-763215 | 30.9185 | 0 | GEN-2018-088 | 0 | 0 | 0
18021901 | TC | Southeast | 26 | L | contingency57.sav | 511456-763215 | 43.7833 | 0 | GEN-2018-106 | 0 | 0 | 0
18021901 | TC | Southeast | 26 | L | contingency57.sav | 511456-763215 | 18.626 | 0 | GEN-2018-115 | 0 | 0 | 0
18021901 | TC | Southeast | 26 | L | contingency57.sav | 511456-763215 | 18.626 | 0 | GEN-2018-115 | 0 | 0 | 0
18021901 | TC | Southeast | 26 | L | contingency57.sav | 511456-763215 | 111.6816 | 0 | GEN-2019-002 | 0 | 0 | 0
18021901 | TC | Southeast | 26 | L | contingency57.sav | 511456-763215 | 38.6331 | 0 | GEN-2019-012 | 0 | 0 | 0
18021901 | TC | Southeast | 26 | L | contingency57.sav | 511456-763215 | 15.7658 | 0 | GEN-2019-013 | 0 | 0 | 0
18021901 | TC | Southeast | 26 | L | contingency57.sav | 511456-763215 | 22.3001 | 0 | GEN-2019-045 | 0 | 0 | 0
18021901 | TC | Southeast | 26 | L | contingency124.sav | 515458-560022 | 8.2857 | 0 | GEN-2018-064 | 0 | 0 | 0
18021901 | TC | Southeast | 26 | L | contingency124.sav | 515458-560022 | 20.8929 | 0 | GEN-2018-071 | 0 | 0 | 0
18021901 | TC | Southeast | 26 | L | contingency124.sav | 515458-560022 | 20.8929 | 0 | GEN-2018-072 | 0 | 0 | 0
18021901 | TC | Southeast | 26 | L | contingency124.sav | 515458-560022 | 14.2814 | 0 | GEN-2018-079 | 0 | 0 | 0
18021901 | TC | Southeast | 26 | L | contingency124.sav | 515458-560022 | 40.6697 | 0 | GEN-2018-082 | 0 | 0 | 0
18021901 | TC | Southeast | 26 | L | contingency124.sav | 515458-560022 | 40.6697 | 0 | GEN-2018-082 | 0 | 0 | 0
18021901 | TC | Southeast | 26 | L | contingency124.sav | 515458-560022 | 33.5145 | 0 | GEN-2018-087 | 0 | 0 | 0
18021901 | TC | Southeast | 26 | L | contingency124.sav | 515458-560022 | 33.5145 | 0 | GEN-2018-088 | 0 | 0 | 0
18021901 | TC | Southeast | 26 | L | contingency124.sav | 515458-560022 | 46.253 | 0 | GEN-2018-106 | 0 | 0 | 0
18021901 | TC | Southeast | 26 | L | contingency124.sav | 515458-560022 | 24.5782 | 0 | GEN-2018-115 | 0 | 0 | 0
18021901 | TC | Southeast | 26 | L | contingency124.sav | 515458-560022 | 24.5782 | 0 | GEN-2018-115 | 0 | 0 | 0
18021901 | TC | Southeast | 26 | L | contingency124.sav | 515458-560022 | 118.7895 | 0 | GEN-2019-002 | 0 | 0 | 0
18021901 | TC | Southeast | 26 | L | contingency124.sav | 515458-560022 | 53.9589 | 0 | GEN-2019-012 | 0 | 0 | 0
18021901 | TC | Southeast | 26 | L | contingency124.sav | 515458-560022 | 48.9412 | 0 | GEN-2019-013 | 0 | 0 | 0
18021901 | TC | Southeast | 26 | L | contingency124.sav | 515458-560022 | 28.883 | 0 | GEN-2019-045 | 0 | 0 | 0
18021901 | TC | Southeast | 26 | L | contingency255.sav | 511456-511468 | 6.7222 | 0 | GEN-2018-064 | 0 | 0 | 0
18021901 | TC | Southeast | 26 | L | contingency255.sav | 511456-511468 | 14.0109 | 0 | GEN-2018-071 | 0 | 0 | 0
18021901 | TC | Southeast | 26 | L | contingency255.sav | 511456-511468 | 14.0109 | 0 | GEN-2018-072 | 0 | 0 | 0
18021901 | TC | Southeast | 26 | L | contingency255.sav | 511456-511468 | 10.3204 | 0 | GEN-2018-079 | 0 | 0 | 0
18021901 | TC | Southeast | 26 | L | contingency255.sav | 511456-511468 | 25.6313 | 0 | GEN-2018-082 | 0 | 0 | 0
18021901 | TC | Southeast | 26 | L | contingency255.sav | 511456-511468 | 25.6313 | 0 | GEN-2018-082 | 0 | 0 | 0
18021901 | TC | Southeast | 26 | L | contingency255.sav | 511456-511468 | 22.9298 | 0 | GEN-2018-087 | 0 | 0 | 0
18021901 | TC | Southeast | 26 | L | contingency255.sav | 511456-511468 | 22.9298 | 0 | GEN-2018-088 | 0 | 0 | 0
18021901 | TC | Southeast | 26 | L | contingency255.sav | 511456-511468 | 39.4144 | 0 | GEN-2018-106 | 0 | 0 | 0
18021901 | TC | Southeast | 26 | L | contingency255.sav | 511456-511468 | 15.3216 | 0 | GEN-2018-115 | 0 | 0 | 0
18021901 | TC | Southeast | 26 | L | contingency255.sav | 511456-511468 | 15.3216 | 0 | GEN-2018-115 | 0 | 0 | 0
18021901 | TC | Southeast | 26 | L | contingency255.sav | 511456-511468 | 96.1134 | 0 | GEN-2019-002 | 0 | 0 | 0
18021901 | TC | Southeast | 26 | L | contingency255.sav | 511456-511468 | 34.7418 | 0 | GEN-2019-012 | 0 | 0 | 0
18021901 | TC | Southeast | 26 | L | contingency255.sav | 511456-511468 | 26.1989 | 0 | GEN-2019-013 | 0 | 0 | 0
18021901 | TC | Southeast | 26 | L | contingency255.sav | 511456-511468 | 18.3594 | 0 | GEN-2019-045 | 0 | 0 | 0
18021901 | TC | Southeast | 26 | L | contingency371.sav | 515458-755000 | 7.7242 | 0 | GEN-2018-064 | 0 | 0 | 0
18021901 | TC | Southeast | 26 | L | contingency371.sav | 515458-755000 | 19.1395 | 0 | GEN-2018-071 | 0 | 0 | 0
18021901 | TC | Southeast | 26 | L | contingency371.sav | 515458-755000 | 19.1395 | 0 | GEN-2018-072 | 0 | 0 | 0
18021901 | TC | Southeast | 26 | L | contingency371.sav | 515458-755000 | 13.1624 | 0 | GEN-2018-079 | 0 | 0 | 0
18021901 | TC | Southeast | 26 | L | contingency371.sav | 515458-755000 | 37.2896 | 0 | GEN-2018-082 | 0 | 0 | 0
18021901 | TC | Southeast | 26 | L | contingency371.sav | 515458-755000 | 37.2896 | 0 | GEN-2018-082 | 0 | 0 | 0
18021901 | TC | Southeast | 26 | L | contingency371.sav | 515458-755000 | 30.599 | 0 | GEN-2018-087 | 0 | 0 | 0
18021901 | TC | Southeast | 26 | L | contingency371.sav | 515458-755000 | 30.599 | 0 | GEN-2018-088 | 0 | 0 | 0
18021901 | TC | Southeast | 26 | L | contingency371.sav | 515458-755000 | 42.4845 | 0 | GEN-2018-106 | 0 | 0 | 0
18021901 | TC | Southeast | 26 | L | contingency371.sav | 515458-755000 | 24.9007 | 0 | GEN-2018-115 | 0 | 0 | 0
18021901 | TC | Southeast | 26 | L | contingency371.sav | 515458-755000 | 24.9007 | 0 | GEN-2018-115 | 0 | 0 | 0
18021901 | TC | Southeast | 26 | L | contingency371.sav | 515458-755000 | 111.4795 | 0 | GEN-2019-002 | 0 | 0 | 0
18021901 | TC | Southeast | 26 | L | contingency371.sav | 515458-755000 | 49.745 | 0 | GEN-2019-012 | 0 | 0 | 0
18021901 | TC | Southeast | 26 | L | contingency371.sav | 515458-755000 | 46.9076 | 0 | GEN-2019-013 | 0 | 0 | 0
18021901 | TC | Southeast | 26 | L | contingency371.sav | 515458-755000 | 26.0551 | 0 | GEN-2019-045 | 0 | 0 | 0
18021901 | TC | Southeast | 26 | L | contingency428.sav | 560022-762216 | 6.6224 | 0 | GEN-2018-064 | 0 | 0 | 0
18021901 | TC | Southeast | 26 | L | contingency428.sav | 560022-762216 | 13.6583 | 0 | GEN-2018-071 | 0 | 0 | 0
18021901 | TC | Southeast | 26 | L | contingency428.sav | 560022-762216 | 13.6583 | 0 | GEN-2018-072 | 0 | 0 | 0
18021901 | TC | Southeast | 26 | L | contingency428.sav | 560022-762216 | 10.0876 | 0 | GEN-2018-079 | 0 | 0 | 0
18021901 | TC | Southeast | 26 | L | contingency428.sav | 560022-762216 | 24.694 | 0 | GEN-2018-082 | 0 | 0 | 0
18021901 | TC | Southeast | 26 | L | contingency428.sav | 560022-762216 | 24.694 | 0 | GEN-2018-082 | 0 | 0 | 0
18021901 | TC | Southeast | 26 | L | contingency428.sav | 560022-762216 | 22.2455 | 0 | GEN-2018-087 | 0 | 0 | 0
18021901 | TC | Southeast | 26 | L | contingency428.sav | 560022-762216 | 22.2455 | 0 | GEN-2018-088 | 0 | 0 | 0
18021901 | TC | Southeast | 26 | L | contingency428.sav | 560022-762216 | 38.863 | 0 | GEN-2018-106 | 0 | 0 | 0
18021901 | TC | Southeast | 26 | L | contingency428.sav | 560022-762216 | 14.4559 | 0 | GEN-2018-115 | 0 | 0 | 0
18021901 | TC | Southeast | 26 | L | contingency428.sav | 560022-762216 | 14.4559 | 0 | GEN-2018-115 | 0 | 0 | 0
18021901 | TC | Southeast | 26 | L | contingency428.sav | 560022-762216 | 94.5945 | 0 | GEN-2019-002 | 0 | 0 | 0
18021901 | TC | Southeast | 26 | L | contingency428.sav | 560022-762216 | 33.8459 | 0 | GEN-2019-012 | 0 | 0 | 0
18021901 | TC | Southeast | 26 | L | contingency428.sav | 560022-762216 | 25.7308 | 0 | GEN-2019-013 | 0 | 0 | 0
18021901 | TC | Southeast | 26 | L | contingency428.sav | 560022-762216 | 17.9461 | 0 | GEN-2019-045 | 0 | 0 | 0
18021901 | TC | Southeast | 26 | L | contingency463.sav | 763215-762467 | 8.1075 | 0 | GEN-2018-064 | 0 | 0 | 0
18021901 | TC | Southeast | 26 | L | contingency463.sav | 763215-762467 | 21.2462 | 0 | GEN-2018-071 | 0 | 0 | 0
18021901 | TC | Southeast | 26 | L | contingency463.sav | 763215-762467 | 21.2462 | 0 | GEN-2018-072 | 0 | 0 | 0
18021901 | TC | Southeast | 26 | L | contingency463.sav | 763215-762467 | 14.1763 | 0 | GEN-2018-079 | 0 | 0 | 0
18021901 | TC | Southeast | 26 | L | contingency463.sav | 763215-762467 | 40.1114 | 0 | GEN-2018-082 | 0 | 0 | 0
18021901 | TC | Southeast | 26 | L | contingency463.sav | 763215-762467 | 40.1114 | 0 | GEN-2018-082 | 0 | 0 | 0
18021901 | TC | Southeast | 26 | L | contingency463.sav | 763215-762467 | 32.5413 | 0 | GEN-2018-087 | 0 | 0 | 0
18021901 | TC | Southeast | 26 | L | contingency463.sav | 763215-762467 | 32.5413 | 0 | GEN-2018-088 | 0 | 0 | 0
18021901 | TC | Southeast | 26 | L | contingency463.sav | 763215-762467 | 44.2676 | 0 | GEN-2018-106 | 0 | 0 | 0
18021901 | TC | Southeast | 26 | L | contingency463.sav | 763215-762467 | 24.3327 | 0 | GEN-2018-115 | 0 | 0 | 0
18021901 | TC | Southeast | 26 | L | contingency463.sav | 763215-762467 | 24.3327 | 0 | GEN-2018-115 | 0 | 0 | 0
18021901 | TC | Southeast | 26 | L | contingency463.sav | 763215-762467 | 117.1135 | 0 | GEN-2019-002 | 0 | 0 | 0
18021901 | TC | Southeast | 26 | L | contingency463.sav | 763215-762467 | 60.765 | 0 | GEN-2019-012 | 0 | 0 | 0
18021901 | TC | Southeast | 26 | L | contingency463.sav | 763215-762467 | 59.2556 | 0 | GEN-2019-013 | 0 | 0 | 0
18021901 | TC | Southeast | 26 | L | contingency463.sav | 763215-762467 | 30.7936 | 0 | GEN-2019-045 | 0 | 0 | 0
18021901 | TC | Southeast | 26 | L | contingency491.sav | 560022-525832(1):560022-525832(2) | 6.8923 | 0 | GEN-2018-064 | 0 | 0 | 0
18021901 | TC | Southeast | 26 | L | contingency491.sav | 560022-525832(1):560022-525832(2) | 14.2019 | 0 | GEN-2018-071 | 0 | 0 | 0
18021901 | TC | Southeast | 26 | L | contingency491.sav | 560022-525832(1):560022-525832(2) | 14.2019 | 0 | GEN-2018-072 | 0 | 0 | 0
18021901 | TC | Southeast | 26 | L | contingency491.sav | 560022-525832(1):560022-525832(2) | 10.642 | 0 | GEN-2018-079 | 0 | 0 | 0
18021901 | TC | Southeast | 26 | L | contingency491.sav | 560022-525832(1):560022-525832(2) | 26.4049 | 0 | GEN-2018-082 | 0 | 0 | 0
18021901 | TC | Southeast | 26 | L | contingency491.sav | 560022-525832(1):560022-525832(2) | 26.4049 | 0 | GEN-2018-082 | 0 | 0 | 0
18021901 | TC | Southeast | 26 | L | contingency491.sav | 560022-525832(1):560022-525832(2) | 24.2705 | 0 | GEN-2018-087 | 0 | 0 | 0
18021901 | TC | Southeast | 26 | L | contingency491.sav | 560022-525832(1):560022-525832(2) | 24.2705 | 0 | GEN-2018-088 | 0 | 0 | 0
18021901 | TC | Southeast | 26 | L | contingency491.sav | 560022-525832(1):560022-525832(2) | 40.5448 | 0 | GEN-2018-106 | 0 | 0 | 0
18021901 | TC | Southeast | 26 | L | contingency491.sav | 560022-525832(1):560022-525832(2) | 15.1753 | 0 | GEN-2018-115 | 0 | 0 | 0
18021901 | TC | Southeast | 26 | L | contingency491.sav | 560022-525832(1):560022-525832(2) | 15.1753 | 0 | GEN-2018-115 | 0 | 0 | 0
18021901 | TC | Southeast | 26 | L | contingency491.sav | 560022-525832(1):560022-525832(2) | 98.1187 | 0 | GEN-2019-002 | 0 | 0 | 0
18021901 | TC | Southeast | 26 | L | contingency491.sav | 560022-525832(1):560022-525832(2) | 33.2277 | 0 | GEN-2019-012 | 0 | 0 | 0
18021901 | TC | Southeast | 26 | L | contingency491.sav | 560022-525832(1):560022-525832(2) | 25.4386 | 0 | GEN-2019-013 | 0 | 0 | 0
18021901 | TC | Southeast | 26 | L | contingency491.sav | 560022-525832(1):560022-525832(2) | 18.2849 | 0 | GEN-2019-045 | 0 | 0 | 0
18021901 | TC | Southeast | 26 | SP | contingency491.sav | 560022-525832(1):560022-525832(2) | 2.3579 | 0 | GEN-2018-064 | 0 | 0 | 0
18021901 | TC | Southeast | 26 | SP | contingency491.sav | 560022-525832(1):560022-525832(2) | 4.3028 | 0 | GEN-2018-071 | 0 | 0 | 0
18021901 | TC | Southeast | 26 | SP | contingency491.sav | 560022-525832(1):560022-525832(2) | 4.3028 | 0 | GEN-2018-072 | 0 | 0 | 0
18021901 | TC | Southeast | 26 | SP | contingency491.sav | 560022-525832(1):560022-525832(2) | 3.687 | 0 | GEN-2018-079 | 0 | 0 | 0
18021901 | TC | Southeast | 26 | SP | contingency491.sav | 560022-525832(1):560022-525832(2) | 4.9225 | 0 | GEN-2018-082 | 0 | 0 | 0
18021901 | TC | Southeast | 26 | SP | contingency491.sav | 560022-525832(1):560022-525832(2) | 4.9225 | 0 | GEN-2018-082 | 0 | 0 | 0
18021901 | TC | Southeast | 26 | SP | contingency491.sav | 560022-525832(1):560022-525832(2) | 10.7215 | 0 | GEN-2018-087 | 0 | 0 | 0
18021901 | TC | Southeast | 26 | SP | contingency491.sav | 560022-525832(1):560022-525832(2) | 10.7215 | 0 | GEN-2018-088 | 0 | 0 | 0
18021901 | TC | Southeast | 26 | SP | contingency491.sav | 560022-525832(1):560022-525832(2) | 24.4201 | 0 | GEN-2018-106 | 0 | 0 | 0
18021901 | TC | Southeast | 26 | SP | contingency491.sav | 560022-525832(1):560022-525832(2) | 4.0653 | 0 | GEN-2018-115 | 0 | 0 | 0
18021901 | TC | Southeast | 26 | SP | contingency491.sav | 560022-525832(1):560022-525832(2) | 4.0653 | 0 | GEN-2018-115 | 0 | 0 | 0
18021901 | TC | Southeast | 26 | SP | contingency491.sav | 560022-525832(1):560022-525832(2) | 38.048 | 0 | GEN-2019-002 | 0 | 0 | 0
18021901 | TC | Southeast | 26 | SP | contingency491.sav | 560022-525832(1):560022-525832(2) | 7.2287 | 0 | GEN-2019-012 | 0 | 0 | 0
18021901 | TC | Southeast | 26 | SP | contingency491.sav | 560022-525832(1):560022-525832(2) | 12.1501 | 0 | GEN-2019-013 | 0 | 0 | 0
18021901 | TC | Southeast | 26 | SP | contingency491.sav | 560022-525832(1):560022-525832(2) | 2.5936 | 0 | GEN-2019-045 | 0 | 0 | 0
18021901 | TC | Southeast | 26 | WP | contingency491.sav | 560022-525832(1):560022-525832(2) | 2.4258 | 0 | GEN-2018-064 | 0 | 0 | 0
18021901 | TC | Southeast | 26 | WP | contingency491.sav | 560022-525832(1):560022-525832(2) | 5.6854 | 0 | GEN-2018-071 | 0 | 0 | 0
18021901 | TC | Southeast | 26 | WP | contingency491.sav | 560022-525832(1):560022-525832(2) | 5.6854 | 0 | GEN-2018-072 | 0 | 0 | 0
18021901 | TC | Southeast | 26 | WP | contingency491.sav | 560022-525832(1):560022-525832(2) | 2.127 | 0 | GEN-2018-079 | 0 | 0 | 0
18021901 | TC | Southeast | 26 | WP | contingency491.sav | 560022-525832(1):560022-525832(2) | 12.1037 | 0 | GEN-2018-082 | 0 | 0 | 0
18021901 | TC | Southeast | 26 | WP | contingency491.sav | 560022-525832(1):560022-525832(2) | 12.1037 | 0 | GEN-2018-082 | 0 | 0 | 0
18021901 | TC | Southeast | 26 | WP | contingency491.sav | 560022-525832(1):560022-525832(2) | 5.8022 | 0 | GEN-2018-087 | 0 | 0 | 0
18021901 | TC | Southeast | 26 | WP | contingency491.sav | 560022-525832(1):560022-525832(2) | 5.8022 | 0 | GEN-2018-088 | 0 | 0 | 0
18021901 | TC | Southeast | 26 | WP | contingency491.sav | 560022-525832(1):560022-525832(2) | 7.5665 | 0 | GEN-2018-106 | 0 | 0 | 0
18021901 | TC | Southeast | 26 | WP | contingency491.sav | 560022-525832(1):560022-525832(2) | 8.8044 | 0 | GEN-2018-115 | 0 | 0 | 0
18021901 | TC | Southeast | 26 | WP | contingency491.sav | 560022-525832(1):560022-525832(2) | 8.8044 | 0 | GEN-2018-115 | 0 | 0 | 0
18021901 | TC | Southeast | 26 | WP | contingency491.sav | 560022-525832(1):560022-525832(2) | 25.6659 | 0 | GEN-2019-002 | 0 | 0 | 0
18021901 | TC | Southeast | 26 | WP | contingency491.sav | 560022-525832(1):560022-525832(2) | 15.5298 | 0 | GEN-2019-012 | 0 | 0 | 0
18021901 | TC | Southeast | 26 | WP | contingency491.sav | 560022-525832(1):560022-525832(2) | 10.9506 | 0 | GEN-2019-013 | 0 | 0 | 0
18021901 | TC | Southeast | 26 | WP | contingency491.sav | 560022-525832(1):560022-525832(2) | 8.6624 | 0 | GEN-2019-045 | 0 | 0 | 0
18021901 | TC | Southwest | 23 | SP | base | N/A | 5.9149 | 12.5977 | GEN-2018-092 | 12497.7133 | 200 | 222.6
18021901 | TC | Southwest | 23 | SP | base | N/A | 5.9149 | 12.5977 | GEN-2018-092 | 12497.7133 | 200 | 222.6
18021901 | TC | Southwest | 23 | SP | contingency1.sav | 511456-511468 | 21.366 | 0.1426 | GEN-2018-089 | 42.6349 | 196 | 221
18021901 | TC | Southwest | 23 | SP | contingency85.sav | 511468-587744 | 22.5618 | 0.1407 | GEN-2018-089 | 40.7103 | 196 | 221
18021901 | TC | Southwest | 23 | SP | contingency287.sav | 523869-523866(1):523869-523866(2) | 4.7535 | 49.1725 | GEN-2018-073 | 49072.5018 | 250 | 154
18021901 | TC | Southwest | 23 | SP | contingency287.sav | 523869-523866(1):523869-523866(2) | 4.7535 | 49.6972 | GEN-2018-073 | 49597.1983 | 125 | 162.8
18021901 | TC | Southwest | 26 | SP | contingency1.sav | 511456-511468 | 22.3666 | 0.1405 | GEN-2018-089 | 40.5092 | 196 | 221
18021901 | TC | Southwest | 26 | SP | contingency1.sav | 511456-511468 | 4.2729 | 13.5466 | GEN-2018-092 | 13446.6119 | 200 | 222.6
18021901 | TC | Southwest | 26 | SP | contingency1.sav | 511456-511468 | 4.2729 | 13.5466 | GEN-2018-092 | 13446.6119 | 200 | 222.6
18021901 | TC | Southwest | 26 | SP | contingency6.sav | 523957-523961-523959 | 5.991 | 12.5992 | GEN-2018-092 | 12499.2232 | 200 | 222.6
18021901 | TC | Southwest | 26 | SP | contingency6.sav | 523957-523961-523959 | 5.991 | 12.5992 | GEN-2018-092 | 12499.2232 | 200 | 222.6
18021901 | TC | Southwest | 26 | SP | contingency55.sav | 525824-525832-525830 | 5.9519 | 12.6116 | GEN-2018-092 | 12511.6411 | 200 | 222.6
18021901 | TC | Southwest | 26 | SP | contingency55.sav | 525824-525832-525830 | 5.9519 | 12.6116 | GEN-2018-092 | 12511.6411 | 200 | 222.6
18021901 | TC | Southwest | 26 | SP | contingency56.sav | 525825-525832-525830 | 5.9724 | 12.614 | GEN-2018-092 | 12514.0367 | 200 | 222.6
18021901 | TC | Southwest | 26 | SP | contingency56.sav | 525825-525832-525830 | 5.9724 | 12.614 | GEN-2018-092 | 12514.0367 | 200 | 222.6
18021901 | TC | Southwest | 26 | SP | contingency82.sav | 762216-762467 | 3.2411 | 13.9599 | GEN-2018-092 | 13859.8648 | 200 | 222.6
18021901 | TC | Southwest | 26 | SP | contingency82.sav | 762216-762467 | 3.2411 | 13.9599 | GEN-2018-092 | 13859.8648 | 200 | 222.6
18021901 | TC | Southwest | 26 | SP | contingency84.sav | 511456-763215 | 20.0852 | 0.1439 | GEN-2018-089 | 43.8964 | 196 | 221
18021901 | TC | Southwest | 26 | SP | contingency84.sav | 511456-763215 | 4.5951 | 18.2351 | GEN-2018-092 | 18135.0575 | 200 | 222.6
18021901 | TC | Southwest | 26 | SP | contingency84.sav | 511456-763215 | 4.5951 | 18.2351 | GEN-2018-092 | 18135.0575 | 200 | 222.6
18021901 | TC | Southwest | 26 | SP | contingency85.sav | 511468-587744 | 5.4861 | 12.8124 | GEN-2018-092 | 12712.384 | 200 | 222.6
18021901 | TC | Southwest | 26 | SP | contingency85.sav | 511468-587744 | 5.4861 | 12.8124 | GEN-2018-092 | 12712.384 | 200 | 222.6
18021901 | TC | Southwest | 26 | SP | contingency86.sav | 511468-760938 | 5.7723 | 12.7186 | GEN-2018-092 | 12618.5646 | 200 | 222.6
18021901 | TC | Southwest | 26 | SP | contingency86.sav | 511468-760938 | 5.7723 | 12.7186 | GEN-2018-092 | 12618.5646 | 200 | 222.6
18021901 | TC | Southwest | 26 | SP | contingency89.sav | 511468-511467-511411 | 5.9824 | 12.594 | GEN-2018-092 | 12494.0314 | 200 | 222.6
18021901 | TC | Southwest | 26 | SP | contingency89.sav | 511468-511467-511411 | 5.9824 | 12.594 | GEN-2018-092 | 12494.0314 | 200 | 222.6
18021901 | TC | Southwest | 26 | SP | contingency103.sav | 515458-560022 | 5.7117 | 12.466 | GEN-2018-092 | 12365.9939 | 200 | 222.6
18021901 | TC | Southwest | 26 | SP | contingency103.sav | 515458-560022 | 5.7117 | 12.466 | GEN-2018-092 | 12365.9939 | 200 | 222.6
18021901 | TC | Southwest | 26 | SP | contingency104.sav | 515458-755000 | 5.7109 | 12.4672 | GEN-2018-092 | 12367.1988 | 200 | 222.6
18021901 | TC | Southwest | 26 | SP | contingency104.sav | 515458-755000 | 5.7109 | 12.4672 | GEN-2018-092 | 12367.1988 | 200 | 222.6
18021901 | TC | Southwest | 26 | SP | contingency111.sav | 523961-523097 | 5.981 | 12.5893 | GEN-2018-092 | 12489.3262 | 200 | 222.6
18021901 | TC | Southwest | 26 | SP | contingency111.sav | 523961-523097 | 5.981 | 12.5893 | GEN-2018-092 | 12489.3262 | 200 | 222.6
18021901 | TC | Southwest | 26 | SP | contingency209.sav | 525832-526936 | 5.9356 | 12.6177 | GEN-2018-092 | 12517.7483 | 200 | 222.6
18021901 | TC | Southwest | 26 | SP | contingency209.sav | 525832-526936 | 5.9356 | 12.6177 | GEN-2018-092 | 12517.7483 | 200 | 222.6
18021901 | TC | Southwest | 26 | SP | contingency276.sav | 762216-560022 | 2.8869 | 13.4 | GEN-2018-092 | 13299.9735 | 200 | 222.6
18021901 | TC | Southwest | 26 | SP | contingency276.sav | 762216-560022 | 2.8869 | 13.4 | GEN-2018-092 | 13299.9735 | 200 | 222.6
18021901 | TC | Southwest | 26 | SP | contingency283.sav | 762467-763215 | 3.4976 | 14.03 | GEN-2018-092 | 13929.97 | 200 | 222.6
18021901 | TC | Southwest | 26 | SP | contingency283.sav | 762467-763215 | 3.4976 | 14.03 | GEN-2018-092 | 13929.97 | 200 | 222.6
18021901 | TC | Southwest | 26 | SP | contingency286.sav | 515375-560071(1):515375-560071(2) | 5.8847 | 12.5221 | GEN-2018-092 | 12422.1362 | 200 | 222.6
18021901 | TC | Southwest | 26 | SP | contingency286.sav | 515375-560071(1):515375-560071(2) | 5.8847 | 12.5221 | GEN-2018-092 | 12422.1362 | 200 | 222.6
18021901 | TC | Southwest | 26 | SP | contingency288.sav | 525832-560022(1):525832-560022(2) | 5.2091 | 49.3564 | GEN-2018-073 | 49256.4223 | 250 | 154
18021901 | TC | Southwest | 26 | SP | contingency288.sav | 525832-560022(1):525832-560022(2) | 5.2091 | 49.835 | GEN-2018-073 | 49735.0268 | 125 | 162.8
18021901 | TC | Southwest | 26 | SP | contingency288.sav | 525832-560022(1):525832-560022(2) | 4.097 | 12.9511 | GEN-2018-092 | 12851.1118 | 200 | 222.6
18021901 | TC | Southwest | 26 | SP | contingency288.sav | 525832-560022(1):525832-560022(2) | 4.097 | 12.9511 | GEN-2018-092 | 12851.1118 | 200 | 222.6
18021901 | TC | Southwest | 26 | WP | base | N/A | 5.8571 | 12.6381 | GEN-2018-092 | 12538.1447 | 200 | 222.6
18021901 | TC | Southwest | 26 | WP | base | N/A | 5.8571 | 12.6381 | GEN-2018-092 | 12538.1447 | 200 | 222.6
18021901 | TC | Southwest | 26 | WP | contingency288.sav | 525832-560022(1):525832-560022(2) | 5.182 | 49.3212 | GEN-2018-073 | 49221.1668 | 250 | 154
18021901 | TC | Southwest | 26 | WP | contingency288.sav | 525832-560022(1):525832-560022(2) | 5.182 | 49.7924 | GEN-2018-073 | 49692.3897 | 125 | 162.8
18021901 | TC | Central | 26 | SP | contingency383.sav | 532796-532782(1):532796-532782(2) | 3.8717 | 0 | GEN-2019-014 | 0 | 0 | 0
18021901 | TC | Southeast | 23 | SP | contingency222.sav | 509080-763010 | 5.1945 | 0.1496 | GEN-2019-065 | 49.5597 | 180 | 335.8
18021901 | TC | Southeast | 23 | SP | contingency488.sav | 560022-525832(1):560022-525832(2) | 2.9129 | 0 | GEN-2019-065 | 0 | 0 | 0
18021901 | TC | Southeast | 26 | L | contingency222.sav | 509080-763010 | 4.8454 | 0 | GEN-2019-065 | 0 | 0 | 0
18021901 | TC | Southeast | 26 | SP | contingency222.sav | 509080-763010 | 5.389 | 0.1475 | GEN-2019-065 | 47.5432 | 180 | 335.8
18021901 | TC | Southeast | 26 | SP | contingency491.sav | 560022-525832(1):560022-525832(2) | 4.877 | 0 | GEN-2019-065 | 0 | 0 | 0
18021901 | TC | Southeast | 26 | WP | contingency222.sav | 509080-763010 | 5.168 | 0.1486 | GEN-2019-065 | 48.6313 | 180 | 335.8
18021901 | TC | Southeast | 26 | WP | contingency491.sav | 560022-525832(1):560022-525832(2) | 2.0252 | 0 | GEN-2019-065 | 0 | 0 | 0
18021901 | TC | Southwest | 26 | WP | contingency165.sav | 301348-300024 | 9.3536 | 0 | GEN-2019-003 | 0 | 0 | 0
18021901 | TC | Central | 26 | WP | contingency383.sav | 532796-532782(1):532796-532782(2) | 11.7266 | 0 | GEN-2019-058 | 0 | 0 | 0
18021901 | TC | North | 26 | L | contingency149.sav | 655940-655941 | 41.9725 | 0 | GEN-2019-037 | 0 | 0 | 0
18021901 | TC | Nebraska | 23 | SP | contingency129.sav | 640226-763982 | 4.8299 | 17.5539 | GEN-2019-073 | 17453.869 | 100 | 113.4
18021901 | TC | Nebraska | 23 | SP | contingency162.sav | 640342-763982 | 5.971 | 16.9869 | GEN-2019-073 | 16886.8766 | 100 | 113.4
18021901 | TC | Nebraska | 26 | SP | contingency130.sav | 640226-763982 | 4.843 | 17.53 | GEN-2019-073 | 17429.9695 | 100 | 113.4
18021901 | TC | Nebraska | 26 | SP | contingency163.sav | 640342-763982 | 5.9864 | 16.9881 | GEN-2019-073 | 16888.0834 | 100 | 113.4
18021901 | TC | Nebraska | 26 | WP | contingency129.sav | 640226-640520 | 5.3813 | 0 | GEN-2019-073 | 0 | 0 | 0
18021901 | TC | Nebraska | 26 | WP | contingency130.sav | 640226-763982 | 4.6611 | 17.6302 | GEN-2019-073 | 17530.2153 | 100 | 113.4
18021901 | TC | Nebraska | 26 | WP | contingency143.sav | 640252-763666 | 8.8571 | 0 | GEN-2019-073 | 0 | 0 | 0
18021901 | TC | Nebraska | 26 | WP | contingency163.sav | 640342-763982 | 5.8896 | 16.9324 | GEN-2019-073 | 16832.3812 | 100 | 113.4
18021901 | TC | Central | 23 | SP | contingency265.sav | 539679-763862 | 4.1704 | 5.3482 | GEN-2019-068 | 5248.2409 | 50 | 84
18021901 | TC | Central | 26 | SP | contingency265.sav | 539679-763862 | 4.2092 | 5.3116 | GEN-2019-068 | 5211.6378 | 50 | 84
18021901 | TC | Central | 26 | SP | contingency383.sav | 532796-532782(1):532796-532782(2) | 4.9797 | 3.7506 | GEN-2019-068 | 3650.5694 | 50 | 84
18021901 | TC | Central | 26 | WP | contingency265.sav | 539679-763862 | 4.21 | 5.0272 | GEN-2019-068 | 4927.203 | 50 | 84
18021901 | TC | Central | 26 | WP | contingency383.sav | 532796-532782(1):532796-532782(2) | 5.5513 | 3.5877 | GEN-2019-068 | 3487.7396 | 50 | 84

## WSCR
Study | Case Type | Region | Season Year | Season | Contingency Type | Contingency Definition | WSCR Group | WSCR Value | Bus 1 | Bus 2 | Bus 3 | Bus 4 | Bus 5 | Bus 6 | Bus 7 | Bus 8
18021901 | TC | 1 | 23 | SP | base | N/A | 1-23S-1 | 2.1959 | Bus 1: GEN-2018-067; Bus 2: GEN-2018-069,2019-023
18021901 | TC | 1 | 26 | SP | contingency203.sav | 762544-659423 | 1-26S-6 | 4.063 | Bus 1: GEN-2018-069,2019-023; Bus 2: GEN-2018-067; Bus 3: GEN-2016-130,2019-037
18021901 | TC | 1 | 26 | SP | base | N/A | 1-26S-1 | 2.2061 | Bus 1: GEN-2018-067; Bus 2: GEN-2016-130,2019-037
18021901 | TC | 1 | 26 | WP | base | N/A | 1-26W-1 | 2.222 | Bus 1: GEN-2018-067; Bus 2: GEN-2018-069,2019-023
18021901 | TC | 1 | 26 | L | base | N/A | 1-26L-1 | 1.9005 | Bus 1: GEN-2018-069,2019-023; Bus 2: GEN-2018-067; Bus 3: GEN-2016-130,2019-037
18021901 | TC | 1 | 26 | L | contingency182.sav | 659420-659421 | 1-26L-6 | 3.54 | Bus 1: GEN-2018-069,2019-023; Bus 2: GEN-2018-067; Bus 3: GEN-2016-130,2019-037
18021901 | TC | 1 | 26 | L | contingency184.sav | 659424-659105 | 1-26L-6 | 3.4621 | Bus 1: GEN-2018-069,2019-023; Bus 2: GEN-2018-067; Bus 3: GEN-2016-130,2019-037
18021901 | TC | 1 | 26 | L | contingency195.sav | 760357-659428 | 1-26L-6 | 3.4408 | Bus 1: GEN-2018-069,2019-023; Bus 2: GEN-2018-067; Bus 3: GEN-2016-130,2019-037
18021901 | TC | 1 | 26 | L | contingency56.sav | 659424-760357 | 1-26L-6 | 3.4623 | Bus 1: GEN-2018-069,2019-023; Bus 2: GEN-2018-067; Bus 3: GEN-2016-130,2019-037
18021901 | TC | 2 | 23 | SP | contingency165.sav | 640374-763410 | 2-23SP-1 | 3.5217 | Bus 1: GEN-2019-033,2019-029; Bus 2: GEN-2018-125
18021901 | TC | 3 | 23 | SP | contingency14.sav | 530582-539679 | 3-23S-1 | 4.2427 | Bus 1: GEN-2019-054, 2019-068; Bus 2: GEN-2018-116,2019-051
18021901 | TC | 3 | 23 | SP | contingency155.sav | 530582-530584 | 3-23S-1 | 4.5905 | Bus 1: GEN-2019-054, 2019-068; Bus 2: GEN-2018-116,2019-051
18021901 | TC | 3 | 23 | SP | contingency197.sav | 532871-763862 | 3-23S-1 | 3.9951 | Bus 1: GEN-2019-054, 2019-068; Bus 2: GEN-2018-116,2019-051
18021901 | TC | 3 | 23 | SP | contingency264.sav | 539679-763850 | 3-23S-1 | 4.5336 | Bus 1: GEN-2019-054, 2019-068; Bus 2: GEN-2018-116,2019-051
18021901 | TC | 3 | 23 | SP | contingency270.sav | 539695-763850 | 3-23S-1 | 2.5765 | Bus 1: GEN-2019-053,2019-055; Bus 2: GEN-2019-054, 2019-068; Bus 3: GEN-2018-116,2019-051
18021901 | TC | 3 | 26 | SP | contingency14.sav | 530582-539679 | 3-26S-1 | 4.2728 | Bus 1: GEN-2019-054,2019-068; Bus 2: GEN-2018-116,2019-051
18021901 | TC | 3 | 26 | SP | contingency155.sav | 530582-530584 | 3-26S-1 | 4.6272 | Bus 1: GEN-2019-054,2019-068; Bus 2: GEN-2018-116,2019-051
18021901 | TC | 3 | 26 | SP | contingency197.sav | 532871-763862 | 3-26S-1 | 4.0133 | Bus 1: GEN-2019-054,2019-068; Bus 2: GEN-2018-116,2019-051
18021901 | TC | 3 | 26 | SP | contingency264.sav | 539679-763850 | 3-26S-1 | 4.5695 | Bus 1: GEN-2019-054,2019-068; Bus 2: GEN-2018-116,2019-051
18021901 | TC | 3 | 26 | SP | contingency270.sav | 539695-763850 | 3-26S-1 | 2.5931 | Bus 1: GEN-2019-053,2019-055; Bus 2: GEN-2019-054,2019-068; Bus 3: GEN-2018-116,2019-051
18021901 | TC | 3 | 26 | WP | contingency14.sav | 530582-539679 | 3-26W-1 | 4.2439 | Bus 1: GEN-2019-054,2019-068; Bus 2: GEN-2018-116,2019-051
18021901 | TC | 3 | 26 | WP | contingency155.sav | 530582-530584 | 3-26W-1 | 4.5967 | Bus 1: GEN-2018-116,2019-051; Bus 2: GEN-2019-054,2019-068
18021901 | TC | 3 | 26 | WP | contingency197.sav | 532871-763862 | 3-26W-1 | 4.0025 | Bus 1: GEN-2019-054,2019-068; Bus 2: GEN-2018-116,2019-051
18021901 | TC | 3 | 26 | WP | contingency264.sav | 539679-763850 | 3-26W-1 | 4.5508 | Bus 1: GEN-2019-054,2019-068; Bus 2: GEN-2018-116,2019-051
18021901 | TC | 3 | 26 | WP | contingency270.sav | 539695-763850 | 3-26W-1 | 3.1161 | Bus 1: GEN-2019-053,2019-055; Bus 2: GEN-2018-116,2019-051
18021901 | TC | 3 | 26 | WP | contingency270.sav | 539695-763850 | 3-26W-4 | 2.5789 | Bus 1: GEN-2018-116,2019-051; Bus 2: GEN-2019-054,2019-068; Bus 3: GEN-2019-053,2019-055
18021901 | TC | 5 | 26 | SP | base | N/A | 5-26SP-1 | 4.1416 | GEN-2019-003,2019-021 | GEN-2018-081,2019-074 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2019-011 | GEN-2018-073
18021901 | TC | 5 | 26 | SP | base | N/A | 5-26SP-10 | 3.5627 | GEN-2019-003,2019-021 | GEN-2018-089 | GEN-2018-081,2019-074 | GEN-2019-011 | GEN-2018-073 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124
18021901 | TC | 5 | 26 | SP | base | N/A | 5-26SP-16 | 4.4438 | GEN-2019-003,2019-021 | GEN-2018-089 | GEN-2018-081,2019-074 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2019-056
18021901 | TC | 5 | 26 | SP | base | N/A | 5-26SP-4 | 4.0811 | GEN-2019-003,2019-021 | GEN-2018-081,2019-074 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2019-011 | GEN-2018-089
18021901 | TC | 5 | 26 | SP | contingency10.sav | 523978-524365 | 5-26SP-16 | 3.7436 | GEN-2019-003,2019-021 | GEN-2018-089 | GEN-2018-081,2019-074 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2019-011 | GEN-2019-056
18021901 | TC | 5 | 26 | SP | contingency103.sav | 515458-560022 | 5-26SP-1 | 2.5888 | GEN-2019-003,2019-021 | GEN-2018-089 | GEN-2018-081,2019-074 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2019-011 | GEN-2018-092 | GEN-2018-073
18021901 | TC | 5 | 26 | SP | contingency103.sav | 515458-560022 | 5-26SP-18 | 3.2542 | GEN-2019-003,2019-021 | GEN-2018-089 | GEN-2018-081,2019-074 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2019-011 | GEN-2018-073 | GEN-2019-056
18021901 | TC | 5 | 26 | SP | contingency103.sav | 515458-560022 | 5-26SP-5 | 4.7589 | Bus 1: GEN-2019-011; Bus 2: GEN-2018-073; Bus 3: GEN-2018-092
18021901 | TC | 5 | 26 | SP | contingency104.sav | 515458-755000 | 5-26SP-1 | 2.5879 | GEN-2019-003,2019-021 | GEN-2018-089 | GEN-2018-081,2019-074 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2019-011 | GEN-2018-092 | GEN-2018-073
18021901 | TC | 5 | 26 | SP | contingency104.sav | 515458-755000 | 5-26SP-18 | 3.253 | GEN-2019-003,2019-021 | GEN-2018-089 | GEN-2018-081,2019-074 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2019-011 | GEN-2018-073 | GEN-2019-056
18021901 | TC | 5 | 26 | SP | contingency104.sav | 515458-755000 | 5-26SP-5 | 4.7542 | Bus 1: GEN-2019-011; Bus 2: GEN-2018-073; Bus 3: GEN-2018-092
18021901 | TC | 5 | 26 | SP | contingency105.sav | 523323-523309 | 5-26SP-1 | 3.5603 | GEN-2019-003,2019-021 | GEN-2018-089 | GEN-2018-081,2019-074 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2019-011 | GEN-2018-073
18021901 | TC | 5 | 26 | SP | contingency107.sav | 523869-523221 | 5-26SP-1 | 5.996 | Bus 1: GEN-2019-003,2019-021; Bus 2: GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124; Bus 3: GEN-2018-081,2019-074
18021901 | TC | 5 | 26 | SP | contingency107.sav | 523869-523221 | 5-26SP-11 | 4.8546 | Bus 1: GEN-2019-003,2019-021; Bus 2: GEN-2018-081,2019-074; Bus 3: GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124; Bus 4: GEN-2019-011
18021901 | TC | 5 | 26 | SP | contingency11.sav | 524162-524224 | 5-26SP-1 | 5.9943 | Bus 1: GEN-2019-003,2019-021; Bus 2: GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124; Bus 3: GEN-2018-081,2019-074
18021901 | TC | 5 | 26 | SP | contingency11.sav | 524162-524224 | 5-26SP-11 | 4.8533 | Bus 1: GEN-2018-081,2019-074; Bus 2: GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124; Bus 3: GEN-2019-011; Bus 4: GEN-2019-003,2019-021
18021901 | TC | 5 | 26 | SP | contingency110.sav | 523959-525461 | 5-26SP-1 | 3.4917 | GEN-2019-003,2019-021 | GEN-2018-089 | GEN-2018-081,2019-074 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2019-011 | GEN-2018-073
18021901 | TC | 5 | 26 | SP | contingency111.sav | 523961-523097 | 5-26SP-1 | 3.5525 | GEN-2019-003,2019-021 | GEN-2018-089 | GEN-2018-081,2019-074 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2019-011 | GEN-2018-073
18021901 | TC | 5 | 26 | SP | contingency111.sav | 523961-523097 | 5-26SP-10 | 3.3052 | GEN-2019-056 | GEN-2019-003,2019-021 | GEN-2018-089 | GEN-2018-081,2019-074 | GEN-2019-011 | GEN-2018-073 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124
18021901 | TC | 5 | 26 | SP | contingency113.sav | 523978-523972 | 5-26SP-16 | 3.7418 | GEN-2019-003,2019-021 | GEN-2018-089 | GEN-2018-081,2019-074 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2019-011 | GEN-2019-056
18021901 | TC | 5 | 26 | SP | contingency115.sav | 523979-523267 | 5-26SP-1 | 5.9955 | Bus 1: GEN-2019-003,2019-021; Bus 2: GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124; Bus 3: GEN-2018-081,2019-074
18021901 | TC | 5 | 26 | SP | contingency115.sav | 523979-523267 | 5-26SP-10 | 4.8541 | Bus 1: GEN-2018-081,2019-074; Bus 2: GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124; Bus 3: GEN-2019-011; Bus 4: GEN-2019-003,2019-021
18021901 | TC | 5 | 26 | SP | contingency116.sav | 523979-523973 | 5-26SP-16 | 3.7419 | GEN-2019-003,2019-021 | GEN-2018-089 | GEN-2018-081,2019-074 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2019-011 | GEN-2019-056
18021901 | TC | 5 | 26 | SP | contingency117.sav | 524010-523977 | 5-26SP-1 | 3.5584 | GEN-2019-003,2019-021 | GEN-2018-089 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2019-011 | GEN-2018-073 | GEN-2018-081,2019-074
18021901 | TC | 5 | 26 | SP | contingency119.sav | 524162-524058 | 5-26SP-1 | 3.5617 | GEN-2019-003,2019-021 | GEN-2018-089 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2019-011 | GEN-2018-073 | GEN-2018-081,2019-074
18021901 | TC | 5 | 26 | SP | contingency119.sav | 524162-524058 | 5-26SP-12 | 4.8538 | Bus 1: GEN-2019-003,2019-021; Bus 2: GEN-2018-081,2019-074; Bus 3: GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124; Bus 4: GEN-2019-011
18021901 | TC | 5 | 26 | SP | contingency12.sav | 524267-524623 | 5-26SP-1 | 3.4872 | GEN-2019-003,2019-021 | GEN-2018-089 | GEN-2018-081,2019-074 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2019-011 | GEN-2018-073
18021901 | TC | 5 | 26 | SP | contingency12.sav | 524267-524623 | 5-26SP-16 | 5.413 | Bus 1: GEN-2018-089; Bus 2: GEN-2018-081,2019-074; Bus 3: GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124; Bus 4: GEN-2019-056
18021901 | TC | 5 | 26 | SP | contingency125.sav | 524224-524364 | 5-26SP-1 | 5.9942 | Bus 1: GEN-2019-003,2019-021; Bus 2: GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124; Bus 3: GEN-2018-081,2019-074
18021901 | TC | 5 | 26 | SP | contingency125.sav | 524224-524364 | 5-26SP-10 | 4.8532 | Bus 1: GEN-2018-081,2019-074; Bus 2: GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124; Bus 3: GEN-2019-011; Bus 4: GEN-2019-003,2019-021
18021901 | TC | 5 | 26 | SP | contingency127.sav | 524267-524266 | 5-26SP-1 | 3.5592 | GEN-2019-003,2019-021 | GEN-2018-089 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2019-011 | GEN-2018-073 | GEN-2018-081,2019-074
18021901 | TC | 5 | 26 | SP | contingency127.sav | 524267-524266 | 5-26SP-12 | 4.8496 | Bus 1: GEN-2019-003,2019-021; Bus 2: GEN-2018-081,2019-074; Bus 3: GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124; Bus 4: GEN-2019-011
18021901 | TC | 5 | 26 | SP | contingency129.sav | 524322-524364 | 5-26SP-1 | 3.5627 | GEN-2019-003,2019-021 | GEN-2018-089 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2019-011 | GEN-2018-073 | GEN-2018-081,2019-074
18021901 | TC | 5 | 26 | SP | contingency129.sav | 524322-524364 | 5-26SP-12 | 4.8552 | Bus 1: GEN-2019-003,2019-021; Bus 2: GEN-2018-081,2019-074; Bus 3: GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124; Bus 4: GEN-2019-011
18021901 | TC | 5 | 26 | SP | contingency135.sav | 524387-524388 | 5-26SP-1 | 5.9963 | Bus 1: GEN-2019-003,2019-021; Bus 2: GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124; Bus 3: GEN-2018-081,2019-074
18021901 | TC | 5 | 26 | SP | contingency135.sav | 524387-524388 | 5-26SP-11 | 4.8548 | Bus 1: GEN-2019-003,2019-021; Bus 2: GEN-2018-081,2019-074; Bus 3: GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124; Bus 4: GEN-2019-011
18021901 | TC | 5 | 26 | SP | contingency136.sav | 524415-524044 | 5-26SP-1 | 3.5586 | GEN-2019-003,2019-021 | GEN-2018-089 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2019-011 | GEN-2018-073 | GEN-2018-081,2019-074
18021901 | TC | 5 | 26 | SP | contingency137.sav | 524415-524414- 524410 | 5-26SP-1 | 3.5629 | GEN-2019-003,2019-021 | GEN-2018-089 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2019-011 | GEN-2018-073 | GEN-2018-081,2019-074
18021901 | TC | 5 | 26 | SP | contingency138.sav | 524522-524364 | 5-26SP-1 | 5.9693 | Bus 1: GEN-2019-003,2019-021; Bus 2: GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124; Bus 3: GEN-2018-081,2019-074
18021901 | TC | 5 | 26 | SP | contingency138.sav | 524520-524516 | 5-26SP-10 | 4.8349 | Bus 1: GEN-2018-081,2019-074; Bus 2: GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124; Bus 3: GEN-2019-011; Bus 4: GEN-2019-003,2019-021
18021901 | TC | 5 | 26 | SP | contingency139.sav | 524522-524364 | 5-26SP-1 | 5.9727 | Bus 1: GEN-2019-003,2019-021; Bus 2: GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124; Bus 3: GEN-2018-081,2019-074
18021901 | TC | 5 | 26 | SP | contingency139.sav | 524522-524364 | 5-26SP-10 | 4.8375 | Bus 1: GEN-2018-081,2019-074; Bus 2: GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124; Bus 3: GEN-2019-011; Bus 4: GEN-2019-003,2019-021
18021901 | TC | 5 | 26 | SP | contingency140.sav | 524530-524364 | 5-26SP-1 | 5.9882 | Bus 1: GEN-2019-003,2019-021; Bus 2: GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124; Bus 3: GEN-2018-081,2019-074
18021901 | TC | 5 | 26 | SP | contingency140.sav | 524530-524364 | 5-26SP-10 | 4.8487 | Bus 1: GEN-2018-081,2019-074; Bus 2: GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124; Bus 3: GEN-2019-011; Bus 4: GEN-2019-003,2019-021
18021901 | TC | 5 | 26 | SP | contingency144.sav | 524746-524734 | 5-26SP-1 | 3.5593 | GEN-2019-003,2019-021 | GEN-2018-089 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2019-011 | GEN-2018-073 | GEN-2018-081,2019-074
18021901 | TC | 5 | 26 | SP | contingency144.sav | 524746-524734 | 5-26SP-10 | 5.9964 | Bus 1: GEN-2019-003,2019-021; Bus 2: GEN-2018-081,2019-074; Bus 3: GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124
18021901 | TC | 5 | 26 | SP | contingency144.sav | 524746-524734 | 5-26SP-12 | 4.8548 | Bus 1: GEN-2019-003,2019-021; Bus 2: GEN-2018-081,2019-074; Bus 3: GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124; Bus 4: GEN-2019-011
18021901 | TC | 5 | 26 | SP | contingency146.sav | 524746-525050 | 5-26SP-1 | 5.9841 | Bus 1: GEN-2019-003,2019-021; Bus 2: GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124; Bus 3: GEN-2018-081,2019-074
18021901 | TC | 5 | 26 | SP | contingency146.sav | 524746-525050 | 5-26SP-10 | 4.8458 | Bus 1: GEN-2018-081,2019-074; Bus 2: GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124; Bus 3: GEN-2019-011; Bus 4: GEN-2019-003,2019-021
18021901 | TC | 5 | 26 | SP | contingency149.sav | 524768-524502 | 5-26SP-1 | 5.9839 | Bus 1: GEN-2019-003,2019-021; Bus 2: GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124; Bus 3: GEN-2018-081,2019-074
18021901 | TC | 5 | 26 | SP | contingency149.sav | 524768-524502 | 5-26SP-10 | 4.8456 | Bus 1: GEN-2018-081,2019-074; Bus 2: GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124; Bus 3: GEN-2019-011; Bus 4: GEN-2019-003,2019-021
18021901 | TC | 5 | 26 | SP | contingency154.sav | 524822-524669 | 5-26SP-1 | 5.9617 | Bus 1: GEN-2019-003,2019-021; Bus 2: GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124; Bus 3: GEN-2018-081,2019-074
18021901 | TC | 5 | 26 | SP | contingency154.sav | 524822-524669 | 5-26SP-10 | 4.8295 | Bus 1: GEN-2018-081,2019-074; Bus 2: GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124; Bus 3: GEN-2019-011; Bus 4: GEN-2019-003,2019-021
18021901 | TC | 5 | 26 | SP | contingency16.sav | 524331-524338 | 5-26SP-1 | 5.9965 | Bus 1: GEN-2019-003,2019-021; Bus 2: GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124; Bus 3: GEN-2018-081,2019-074
18021901 | TC | 5 | 26 | SP | contingency16.sav | 524331-524338 | 5-26SP-10 | 4.8549 | Bus 1: GEN-2018-081,2019-074; Bus 2: GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124; Bus 3: GEN-2019-011; Bus 4: GEN-2019-003,2019-021
18021901 | TC | 5 | 26 | SP | contingency166.sav | 524907-524909-524908 | 5-26SP-1 | 3.5577 | GEN-2019-003,2019-021 | GEN-2018-089 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2019-011 | GEN-2018-073 | GEN-2018-081,2019-074
18021901 | TC | 5 | 26 | SP | contingency166.sav | 524907-524909-524908 | 5-26SP-12 | 4.8469 | Bus 1: GEN-2019-003,2019-021; Bus 2: GEN-2018-081,2019-074; Bus 3: GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124; Bus 4: GEN-2019-011
18021901 | TC | 5 | 26 | SP | contingency17.sav | 524365-524415 | 5-26SP-1 | 5.9959 | Bus 1: GEN-2019-003,2019-021; Bus 2: GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124; Bus 3: GEN-2018-081,2019-074
18021901 | TC | 5 | 26 | SP | contingency17.sav | 524365-524415 | 5-26SP-11 | 4.8544 | Bus 1: GEN-2018-081,2019-074; Bus 2: GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124; Bus 3: GEN-2019-011; Bus 4: GEN-2019-003,2019-021
18021901 | TC | 5 | 26 | SP | contingency17.sav | 524365-524415 | 5-26SP-2 | 3.5613 | GEN-2019-003,2019-021 | GEN-2018-081,2019-074 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2019-011 | GEN-2018-073 | GEN-2018-089
18021901 | TC | 5 | 26 | SP | contingency171.sav | 525019-525018 | 5-26SP-1 | 5.9935 | Bus 1: GEN-2019-003,2019-021; Bus 2: GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124; Bus 3: GEN-2018-081,2019-074
18021901 | TC | 5 | 26 | SP | contingency171.sav | 525019-525018 | 5-26SP-10 | 4.8527 | Bus 1: GEN-2018-081,2019-074; Bus 2: GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124; Bus 3: GEN-2019-011; Bus 4: GEN-2019-003,2019-021
18021901 | TC | 5 | 26 | SP | contingency173.sav | 525056-525050 | 5-26SP-1 | 5.9832 | Bus 1: GEN-2019-003,2019-021; Bus 2: GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124; Bus 3: GEN-2018-081,2019-074
18021901 | TC | 5 | 26 | SP | contingency173.sav | 525056-525050 | 5-26SP-10 | 4.8451 | Bus 1: GEN-2018-081,2019-074; Bus 2: GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124; Bus 3: GEN-2019-011; Bus 4: GEN-2019-003,2019-021
18021901 | TC | 5 | 26 | SP | contingency175.sav | 525154-525179 | 5-26SP-1 | 3.5546 | GEN-2019-003,2019-021 | GEN-2018-089 | GEN-2018-081,2019-074 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2019-011 | GEN-2018-073
18021901 | TC | 5 | 26 | SP | contingency178.sav | 525192-525179 | 5-26SP-1 | 3.5542 | GEN-2019-003,2019-021 | GEN-2018-089 | GEN-2018-081,2019-074 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2019-011 | GEN-2018-073
18021901 | TC | 5 | 26 | SP | contingency18.sav | 524415-525213 | 5-26SP-1 | 3.5263 | GEN-2019-003,2019-021 | GEN-2018-089 | GEN-2018-081,2019-074 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2019-011 | GEN-2018-073
18021901 | TC | 5 | 26 | SP | contingency19.sav | 524520-524522 | 5-26SP-1 | 5.9704 | Bus 1: GEN-2019-003,2019-021; Bus 2: GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124; Bus 3: GEN-2018-081,2019-074
18021901 | TC | 5 | 26 | SP | contingency19.sav | 524520-524522 | 5-26SP-10 | 4.8358 | Bus 1: GEN-2018-081,2019-074; Bus 2: GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124; Bus 3: GEN-2019-011; Bus 4: GEN-2019-003,2019-021
18021901 | TC | 5 | 26 | SP | contingency194.sav | 525561-525531 | 5-26SP-1 | 3.0835 | GEN-2019-003,2019-021 | GEN-2018-089 | GEN-2018-081,2019-074 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2019-011 | GEN-2018-073
18021901 | TC | 5 | 26 | SP | contingency194.sav | 525561-525531 | 5-26SP-16 | 3.2054 | GEN-2019-003,2019-021 | GEN-2018-089 | GEN-2018-081,2019-074 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2019-011 | GEN-2019-056
18021901 | TC | 5 | 26 | SP | contingency194.sav | 525561-525531 | 5-26SP-4 | 2.881 | GEN-2019-056 | GEN-2019-003,2019-021 | GEN-2018-081,2019-074 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2019-011 | GEN-2018-073 | GEN-2018-089
18021901 | TC | 5 | 26 | SP | contingency195.sav | 525562-525531 | 5-26SP-1 | 3.0858 | GEN-2019-003,2019-021 | GEN-2018-089 | GEN-2018-081,2019-074 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2019-011 | GEN-2018-073
18021901 | TC | 5 | 26 | SP | contingency195.sav | 525562-525531 | 5-26SP-4 | 2.8831 | GEN-2019-056 | GEN-2019-003,2019-021 | GEN-2018-081,2019-074 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2019-011 | GEN-2018-073 | GEN-2018-089
18021901 | TC | 5 | 26 | SP | contingency2.sav | 511456-511565 | 5-26SP-1 | 3.5652 | GEN-2019-003,2019-021 | GEN-2018-089 | GEN-2018-081,2019-074 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2019-011 | GEN-2018-073
18021901 | TC | 5 | 26 | SP | contingency20.sav | 524522-524523 | 5-26SP-1 | 5.9959 | Bus 1: GEN-2019-003,2019-021; Bus 2: GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124; Bus 3: GEN-2018-081,2019-074
18021901 | TC | 5 | 26 | SP | contingency20.sav | 524522-524523 | 5-26SP-10 | 4.8545 | Bus 1: GEN-2018-081,2019-074; Bus 2: GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124; Bus 3: GEN-2019-011; Bus 4: GEN-2019-003,2019-021
18021901 | TC | 5 | 26 | SP | contingency202.sav | 525828-525780 | 5-26SP-1 | 3.5623 | GEN-2019-003,2019-021 | GEN-2018-089 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2019-011 | GEN-2018-073 | GEN-2018-081,2019-074
18021901 | TC | 5 | 26 | SP | contingency202.sav | 525828-525780 | 5-26SP-12 | 4.8567 | Bus 1: GEN-2019-003,2019-021; Bus 2: GEN-2018-081,2019-074; Bus 3: GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124; Bus 4: GEN-2019-011
18021901 | TC | 5 | 26 | SP | contingency208.sav | 525830-525531 | 5-26SP-10 | 3.8514 | GEN-2019-003,2019-021 | GEN-2018-089 | GEN-2018-081,2019-074 | GEN-2019-011 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124
18021901 | TC | 5 | 26 | SP | contingency208.sav | 525830-525531 | 5-26SP-13 | 3.364 | GEN-2018-089 | GEN-2018-081,2019-074 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2019-011 | GEN-2018-073 | GEN-2019-003,2019-021
18021901 | TC | 5 | 26 | SP | contingency209.sav | 525832-526936 | 5-26SP-16 | 3.6802 | GEN-2019-003,2019-021 | GEN-2018-089 | GEN-2018-081,2019-074 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2019-011 | GEN-2019-056
18021901 | TC | 5 | 26 | SP | contingency21.sav | 524530-525154 | 5-26SP-1 | 5.9884 | Bus 1: GEN-2019-003,2019-021; Bus 2: GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124; Bus 3: GEN-2018-081,2019-074
18021901 | TC | 5 | 26 | SP | contingency21.sav | 524530-525154 | 5-26SP-10 | 4.8488 | Bus 1: GEN-2018-081,2019-074; Bus 2: GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124; Bus 3: GEN-2019-011; Bus 4: GEN-2019-003,2019-021
18021901 | TC | 5 | 26 | SP | contingency210.sav | 525832-560022 | 5-26SP-1 | 3.5552 | GEN-2019-003,2019-021 | GEN-2018-089 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2019-011 | GEN-2018-073 | GEN-2018-081,2019-074
18021901 | TC | 5 | 26 | SP | contingency210.sav | 525832-560022 | 5-26SP-12 | 4.855 | Bus 1: GEN-2019-003,2019-021; Bus 2: GEN-2018-081,2019-074; Bus 3: GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124; Bus 4: GEN-2019-011
18021901 | TC | 5 | 26 | SP | contingency215.sav | 525850-525844 | 5-26SP-1 | 3.5015 | GEN-2019-003,2019-021 | GEN-2018-089 | GEN-2018-081,2019-074 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2019-011 | GEN-2018-073
18021901 | TC | 5 | 26 | SP | contingency216.sav | 525850-525845 | 5-26SP-1 | 3.5049 | GEN-2019-003,2019-021 | GEN-2018-089 | GEN-2018-081,2019-074 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2019-011 | GEN-2018-073
18021901 | TC | 5 | 26 | SP | contingency225.sav | 526337-526331 | 5-26SP-1 | 3.5423 | GEN-2019-003,2019-021 | GEN-2018-089 | GEN-2018-081,2019-074 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2019-011 | GEN-2018-073
18021901 | TC | 5 | 26 | SP | contingency226.sav | 526337-526332 | 5-26SP-1 | 3.543 | GEN-2019-003,2019-021 | GEN-2018-089 | GEN-2018-081,2019-074 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2019-011 | GEN-2018-073
18021901 | TC | 5 | 26 | SP | contingency227.sav | 526337-526333 | 5-26SP-1 | 3.5466 | GEN-2019-003,2019-021 | GEN-2018-089 | GEN-2018-081,2019-074 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2019-011 | GEN-2018-073
18021901 | TC | 5 | 26 | SP | contingency228.sav | 526337-526334 | 5-26SP-1 | 3.5463 | GEN-2019-003,2019-021 | GEN-2018-089 | GEN-2018-081,2019-074 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2019-011 | GEN-2018-073
18021901 | TC | 5 | 26 | SP | contingency234.sav | 526525-526269 | 5-26SP-1 | 3.5406 | GEN-2019-003,2019-021 | GEN-2018-089 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2019-011 | GEN-2018-073 | GEN-2018-081,2019-074
18021901 | TC | 5 | 26 | SP | contingency248.sav | 527656-527610 | 5-26SP-11 | 4.8635 | Bus 1: GEN-2019-003,2019-021; Bus 2: GEN-2018-081,2019-074; Bus 3: GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124; Bus 4: GEN-2019-011
18021901 | TC | 5 | 26 | SP | contingency25.sav | 524767-524770-524768 | 5-26SP-1 | 3.5616 | GEN-2019-003,2019-021 | GEN-2018-089 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2019-011 | GEN-2018-073 | GEN-2018-081,2019-074
18021901 | TC | 5 | 26 | SP | contingency253.sav | 527894-527903 | 5-26SP-1 | 3.531 | GEN-2019-003,2019-021 | GEN-2018-089 | GEN-2018-081,2019-074 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2019-011 | GEN-2018-073
18021901 | TC | 5 | 26 | SP | contingency27.sav | 524822-524908 | 5-26SP-1 | 3.5585 | GEN-2019-003,2019-021 | GEN-2018-089 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2019-011 | GEN-2018-073 | GEN-2018-081,2019-074
18021901 | TC | 5 | 26 | SP | contingency272.sav | 762174-525481 | 5-26SP-1 | 5.8489 | Bus 1: GEN-2019-003,2019-021; Bus 2: GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124; Bus 3: GEN-2018-081,2019-074
18021901 | TC | 5 | 26 | SP | contingency272.sav | 762174-525481 | 5-26SP-11 | 4.7475 | Bus 1: GEN-2018-081,2019-074; Bus 2: GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124; Bus 3: GEN-2019-011; Bus 4: GEN-2019-003,2019-021
18021901 | TC | 5 | 26 | SP | contingency273.sav | 762174-525481 | 5-26SP-1 | 5.8319 | Bus 1: GEN-2019-003,2019-021; Bus 2: GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124; Bus 3: GEN-2018-081,2019-074
18021901 | TC | 5 | 26 | SP | contingency273.sav | 762174-525481 | 5-26SP-10 | 4.735 | Bus 1: GEN-2018-081,2019-074; Bus 2: GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124; Bus 3: GEN-2019-011; Bus 4: GEN-2019-003,2019-021
18021901 | TC | 5 | 26 | SP | contingency274.sav | 762174-525531 | 5-26SP-1 | 5.7815 | Bus 1: GEN-2019-003,2019-021; Bus 2: GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124; Bus 3: GEN-2018-081,2019-074
18021901 | TC | 5 | 26 | SP | contingency274.sav | 762174-525531 | 5-26SP-10 | 4.6983 | Bus 1: GEN-2018-081,2019-074; Bus 2: GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124; Bus 3: GEN-2019-011; Bus 4: GEN-2019-003,2019-021
18021901 | TC | 5 | 26 | SP | contingency275.sav | 762174-525531 | 5-26SP-1 | 5.7691 | Bus 1: GEN-2019-003,2019-021; Bus 2: GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124; Bus 3: GEN-2018-081,2019-074
18021901 | TC | 5 | 26 | SP | contingency275.sav | 762174-525531 | 5-26SP-10 | 4.6893 | Bus 1: GEN-2018-081,2019-074; Bus 2: GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124; Bus 3: GEN-2019-011; Bus 4: GEN-2019-003,2019-021
18021901 | TC | 5 | 26 | SP | contingency276.sav | 762216-560022 | 5-26SP-1 | 3.2707 | GEN-2019-056 | GEN-2019-003,2019-021 | GEN-2018-089 | GEN-2018-081,2019-074 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2019-011 | GEN-2018-073
18021901 | TC | 5 | 26 | SP | contingency28.sav | 524872-524875-524874 | 5-26SP-1 | 3.5632 | GEN-2019-003,2019-021 | GEN-2018-089 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2019-011 | GEN-2018-073 | GEN-2018-081,2019-074
18021901 | TC | 5 | 26 | SP | contingency283.sav | 762467-763215 | 5-26SP-1 | 3.4852 | GEN-2019-003,2019-021 | GEN-2018-089 | GEN-2018-081,2019-074 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2019-011 | GEN-2018-073
18021901 | TC | 5 | 26 | SP | contingency283.sav | 762467-763215 | 5-26SP-13 | 3.2451 | GEN-2019-056 | GEN-2018-089 | GEN-2018-081,2019-074 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2019-011 | GEN-2018-073 | GEN-2019-003,2019-021
18021901 | TC | 5 | 26 | SP | contingency284.sav | 515375-515407(1):515375-515407(2) | 5-26SP-1 | 3.5597 | GEN-2019-003,2019-021 | GEN-2018-089 | GEN-2018-081,2019-074 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2019-011 | GEN-2018-073
18021901 | TC | 5 | 26 | SP | contingency284.sav | 515375-515407(1):515375-515407(2) | 5-26SP-16 | 3.7583 | GEN-2019-003,2019-021 | GEN-2018-089 | GEN-2018-081,2019-074 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2019-011 | GEN-2019-056
18021901 | TC | 5 | 26 | SP | contingency284.sav | 515375-515407(1):515375-515407(2) | 5-26SP-4 | 3.313 | GEN-2019-056 | GEN-2019-003,2019-021 | GEN-2018-081,2019-074 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2019-011 | GEN-2018-073 | GEN-2018-089
18021901 | TC | 5 | 26 | SP | contingency285.sav | 515375-515852(1):515375-515852(2) | 5-26SP-1 | 3.56 | GEN-2019-003,2019-021 | GEN-2018-089 | GEN-2018-081,2019-074 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2019-011 | GEN-2018-073
18021901 | TC | 5 | 26 | SP | contingency285.sav | 515375-515852(1):515375-515852(2) | 5-26SP-16 | 3.7588 | GEN-2019-003,2019-021 | GEN-2018-089 | GEN-2018-081,2019-074 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2019-011 | GEN-2019-056
18021901 | TC | 5 | 26 | SP | contingency286.sav | 515375-560071(1):515375-560071:(2) | 5-26SP-1 | 3.3044 | GEN-2019-056 | GEN-2019-003,2019-021 | GEN-2018-089 | GEN-2018-081,2019-074 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2019-011 | GEN-2018-073
18021901 | TC | 5 | 26 | SP | contingency288.sav | 525832-560022(1):525832-560022(2) | 5-26SP-1 | 2.3221 | Bus 1: GEN-2018-092; Bus 2: GEN-2018-073
18021901 | TC | 5 | 26 | SP | contingency288.sav | 525832-560022(1):525832-560022(2) | 5-26SP-10 | 3.719 | GEN-2019-056 | GEN-2019-003,2019-021 | GEN-2018-089 | GEN-2018-081,2019-074 | GEN-2019-011 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124
18021901 | TC | 5 | 26 | SP | contingency290.sav | 762174-525481(1):762174-525481(2) | 5-26SP-14 | 2.8301 | GEN-2019-003,2019-021 | GEN-2018-089 | GEN-2018-081,2019-074 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2018-073 | GEN-2019-011
18021901 | TC | 5 | 26 | SP | contingency290.sav | 762174-525481(1):762174-525481(2) | 5-26SP-4 | 2.6501 | GEN-2019-056 | GEN-2019-003,2019-021 | GEN-2018-081,2019-074 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2019-011 | GEN-2018-073 | GEN-2018-089
18021901 | TC | 5 | 26 | SP | contingency291.sav | 762174-525531(1):762174-525531(2) | 5-26SP-14 | 2.8304 | GEN-2019-003,2019-021 | GEN-2018-089 | GEN-2018-081,2019-074 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2018-073 | GEN-2019-011
18021901 | TC | 5 | 26 | SP | contingency291.sav | 762174-525531(1):762174-525531(2) | 5-26SP-4 | 2.6503 | GEN-2019-056 | GEN-2019-003,2019-021 | GEN-2018-081,2019-074 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2019-011 | GEN-2018-073 | GEN-2018-089
18021901 | TC | 5 | 26 | SP | contingency3.sav | 511456-588760 | 5-26SP-1 | 3.5634 | GEN-2019-003,2019-021 | GEN-2018-089 | GEN-2018-081,2019-074 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2019-011 | GEN-2018-073
18021901 | TC | 5 | 26 | SP | contingency34.sav | 525056-525480 | 5-26SP-1 | 5.9806 | Bus 1: GEN-2019-003,2019-021; Bus 2: GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124; Bus 3: GEN-2018-081,2019-074
18021901 | TC | 5 | 26 | SP | contingency34.sav | 525056-525480 | 5-26SP-10 | 4.8433 | Bus 1: GEN-2018-081,2019-074; Bus 2: GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124; Bus 3: GEN-2019-011; Bus 4: GEN-2019-003,2019-021
18021901 | TC | 5 | 26 | SP | contingency37.sav | 525192-525454 | 5-26SP-1 | 3.561 | GEN-2019-003,2019-021 | GEN-2018-089 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2019-011 | GEN-2018-073 | GEN-2018-081,2019-074
18021901 | TC | 5 | 26 | SP | contingency4.sav | 523323-523959 | 5-26SP-1 | 3.5597 | GEN-2019-003,2019-021 | GEN-2018-089 | GEN-2018-081,2019-074 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2019-011 | GEN-2018-073
18021901 | TC | 5 | 26 | SP | contingency43.sav | 525454-525828 | 5-26SP-1 | 5.9858 | Bus 1: GEN-2019-003,2019-021; Bus 2: GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124; Bus 3: GEN-2018-081,2019-074
18021901 | TC | 5 | 26 | SP | contingency43.sav | 525454-525828 | 5-26SP-11 | 4.847 | Bus 1: GEN-2019-003,2019-021; Bus 2: GEN-2018-081,2019-074; Bus 3: GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124; Bus 4: GEN-2019-011
18021901 | TC | 5 | 26 | SP | contingency47.sav | 525480-525636 | 5-26SP-1 | 3.56 | GEN-2019-003,2019-021 | GEN-2018-089 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2019-011 | GEN-2018-073 | GEN-2018-081,2019-074
18021901 | TC | 5 | 26 | SP | contingency47.sav | 525480-525636 | 5-26SP-12 | 4.8519 | Bus 1: GEN-2019-003,2019-021; Bus 2: GEN-2018-081,2019-074; Bus 3: GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124; Bus 4: GEN-2019-011
18021901 | TC | 5 | 26 | SP | contingency48.sav | 525549-527656 | 5-26SP-10 | 3.7774 | GEN-2019-003,2019-021 | GEN-2018-089 | GEN-2018-081,2019-074 | GEN-2019-011 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124
18021901 | TC | 5 | 26 | SP | contingency48.sav | 525549-527656 | 5-26SP-14 | 3.3305 | GEN-2019-003,2019-021 | GEN-2018-089 | GEN-2018-081,2019-074 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2018-073 | GEN-2019-011
18021901 | TC | 5 | 26 | SP | contingency52.sav | 525819-525830-525828 | 5-26SP-1 | 5.9974 | Bus 1: GEN-2019-003,2019-021; Bus 2: GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124; Bus 3: GEN-2018-081,2019-074
18021901 | TC | 5 | 26 | SP | contingency52.sav | 525819-525830-525828 | 5-26SP-10 | 4.8555 | Bus 1: GEN-2018-081,2019-074; Bus 2: GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124; Bus 3: GEN-2019-011; Bus 4: GEN-2019-003,2019-021
18021901 | TC | 5 | 26 | SP | contingency53.sav | 525820-525830 | 5-26SP-1 | 5.9963 | Bus 1: GEN-2019-003,2019-021; Bus 2: GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124; Bus 3: GEN-2018-081,2019-074
18021901 | TC | 5 | 26 | SP | contingency53.sav | 525820-525830 | 5-26SP-10 | 4.8545 | Bus 1: GEN-2018-081,2019-074; Bus 2: GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124; Bus 3: GEN-2019-011; Bus 4: GEN-2019-003,2019-021
18021901 | TC | 5 | 26 | SP | contingency54.sav | 525821-525830-525828 | 5-26SP-1 | 5.9975 | Bus 1: GEN-2019-003,2019-021; Bus 2: GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124; Bus 3: GEN-2018-081,2019-074
18021901 | TC | 5 | 26 | SP | contingency54.sav | 525821-525830-525828 | 5-26SP-10 | 4.8555 | Bus 1: GEN-2018-081,2019-074; Bus 2: GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124; Bus 3: GEN-2019-011; Bus 4: GEN-2019-003,2019-021
18021901 | TC | 5 | 26 | SP | contingency59.sav | 525830-526161 | 5-26SP-1 | 5.9973 | Bus 1: GEN-2019-003,2019-021; Bus 2: GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124; Bus 3: GEN-2018-081,2019-074
18021901 | TC | 5 | 26 | SP | contingency59.sav | 525830-526161 | 5-26SP-10 | 4.8553 | Bus 1: GEN-2018-081,2019-074; Bus 2: GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124; Bus 3: GEN-2019-011; Bus 4: GEN-2019-003,2019-021
18021901 | TC | 5 | 26 | SP | contingency6.sav | 523957-523961-523959 | 5-26SP-1 | 3.5535 | GEN-2019-003,2019-021 | GEN-2018-089 | GEN-2018-081,2019-074 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2019-011 | GEN-2018-073
18021901 | TC | 5 | 26 | SP | contingency6.sav | 523957-523961-523959 | 5-26SP-10 | 3.3062 | GEN-2019-056 | GEN-2019-003,2019-021 | GEN-2018-089 | GEN-2018-081,2019-074 | GEN-2019-011 | GEN-2018-073 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124
18021901 | TC | 5 | 26 | SP | contingency61.sav | 525832-525850 | 5-26SP-1 | 3.439 | GEN-2019-003,2019-021 | GEN-2018-089 | GEN-2018-081,2019-074 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2019-011 | GEN-2018-073
18021901 | TC | 5 | 26 | SP | contingency63.sav | 526432-526435-526434 | 5-26SP-16 | 5.5566 | Bus 1: GEN-2018-089; Bus 2: GEN-2018-081,2019-074; Bus 3: GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124; Bus 4: GEN-2019-056
18021901 | TC | 5 | 26 | SP | contingency65.sav | 526435-526525 | 5-26SP-1 | 5.9247 | Bus 1: GEN-2019-003,2019-021; Bus 2: GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124; Bus 3: GEN-2018-081,2019-074
18021901 | TC | 5 | 26 | SP | contingency65.sav | 526435-526525 | 5-26SP-10 | 4.799 | Bus 1: GEN-2018-081,2019-074; Bus 2: GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124; Bus 3: GEN-2019-011; Bus 4: GEN-2019-003,2019-021
18021901 | TC | 5 | 26 | SP | contingency7.sav | 523959-523979 | 5-26SP-1 | 3.5574 | GEN-2019-003,2019-021 | GEN-2018-089 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2019-011 | GEN-2018-073 | GEN-2018-081,2019-074
18021901 | TC | 5 | 26 | SP | contingency72.sav | 527028-527894 | 5-26SP-1 | 3.561 | GEN-2019-003,2019-021 | GEN-2018-089 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2019-011 | GEN-2018-073 | GEN-2018-081,2019-074
18021901 | TC | 5 | 26 | SP | contingency8.sav | 523959-524010 | 5-26SP-1 | 3.5577 | GEN-2019-003,2019-021 | GEN-2018-089 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2019-011 | GEN-2018-073 | GEN-2018-081,2019-074
18021901 | TC | 5 | 26 | SP | contingency81.sav | 762216-762217 | 5-26SP-1 | 3.5663 | GEN-2019-003,2019-021 | GEN-2018-089 | GEN-2018-081,2019-074 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2019-011 | GEN-2018-073
18021901 | TC | 5 | 26 | SP | contingency82.sav | 762216-762467 | 5-26SP-1 | 3.5044 | GEN-2019-003,2019-021 | GEN-2018-089 | GEN-2018-081,2019-074 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2019-011 | GEN-2018-073
18021901 | TC | 5 | 26 | SP | contingency82.sav | 762216-762467 | 5-26SP-10 | 3.2628 | GEN-2019-056 | GEN-2019-003,2019-021 | GEN-2018-089 | GEN-2018-081,2019-074 | GEN-2019-011 | GEN-2018-073 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124
18021901 | TC | 5 | 26 | SP | contingency83.sav | 762460-762467 | 5-26SP-1 | 3.5642 | GEN-2019-003,2019-021 | GEN-2018-089 | GEN-2018-081,2019-074 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2019-011 | GEN-2018-073
18021901 | TC | 5 | 26 | SP | contingency85.sav | 511468-587744 | 5-26SP-1 | 3.558 | GEN-2019-003,2019-021 | GEN-2018-089 | GEN-2018-081,2019-074 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2019-011 | GEN-2018-073
18021901 | TC | 5 | 26 | SP | contingency86.sav | 511468-760938 | 5-26SP-1 | 3.5573 | GEN-2019-003,2019-021 | GEN-2018-089 | GEN-2018-081,2019-074 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2019-011 | GEN-2018-073
18021901 | TC | 5 | 26 | SP | contingency86.sav | 511468-760938 | 5-26SP-16 | 3.7588 | GEN-2019-003,2019-021 | GEN-2018-089 | GEN-2018-081,2019-074 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2019-011 | GEN-2019-056
18021901 | TC | 5 | 26 | SP | contingency9.sav | 523959-524267 | 5-26SP-1 | 3.5152 | GEN-2019-003,2019-021 | GEN-2018-089 | GEN-2018-081,2019-074 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2019-011 | GEN-2018-073
18021901 | TC | 5 | 26 | SP | contingency99.sav | 515375-755000 | 5-26SP-1 | 3.5545 | GEN-2019-003,2019-021 | GEN-2018-089 | GEN-2018-081,2019-074 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2019-011 | GEN-2018-073
18021901 | TC | 5 | 26 | WP | base | N/A | 5-26W-1 | 3.3071 | GEN-2019-003,2019-021 | GEN-2018-074,GEN-2017-222 | GEN-2018-081,2019-074 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2019-011 | GEN-2018-073
18021901 | TC | 5 | 26 | WP | base | N/A | 5-26W-4 | 3.8809 | GEN-2019-003,2019-021 | GEN-2018-081,2019-074 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2019-011 | GEN-2018-074,GEN-2017-222
18021901 | TC | 5 | 26 | WP | contingency100.sav | 515375-763527 | 5-26W-17 | 3.8809 | GEN-2019-003,2019-021 | GEN-2018-074,GEN-2017-222 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2019-011 | GEN-2018-081,2019-074
18021901 | TC | 5 | 26 | WP | contingency101.sav | 515375-515376-515795 | 5-26W-17 | 3.8807 | GEN-2019-003,2019-021 | GEN-2018-074,GEN-2017-222 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2019-011 | GEN-2018-081,2019-074
18021901 | TC | 5 | 26 | WP | contingency102.sav | 515375-515376-515799 | 5-26W-17 | 3.8807 | GEN-2019-003,2019-021 | GEN-2018-074,GEN-2017-222 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2019-011 | GEN-2018-081,2019-074
18021901 | TC | 5 | 26 | WP | contingency103.sav | 515458-560022 | 5-26W-1 | 2.4016 | GEN-2019-003,2019-021 | GEN-2018-074,GEN-2017-222 | GEN-2018-081,2019-074 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2019-011 | GEN-2018-092 | GEN-2018-073
18021901 | TC | 5 | 26 | WP | contingency103.sav | 515458-560022 | 5-26W-10 | 3.2333 | GEN-2019-003,2019-021 | GEN-2018-074,GEN-2017-222 | GEN-2018-081,2019-074 | GEN-2019-011 | GEN-2018-073 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124
18021901 | TC | 5 | 26 | WP | contingency103.sav | 515458-560022 | 5-26W-16 | 3.0163 | GEN-2019-056 | GEN-2019-003,2019-021 | GEN-2018-074,GEN-2017-222 | GEN-2018-081,2019-074 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2018-073 | GEN-2019-011
18021901 | TC | 5 | 26 | WP | contingency103.sav | 515458-560022 | 5-26W-5 | 4.859 | Bus 1: GEN-2018-073; Bus 2: GEN-2018-092
18021901 | TC | 5 | 26 | WP | contingency104.sav | 515458-755000 | 5-26W-1 | 2.4001 | GEN-2019-003,2019-021 | GEN-2018-074,GEN-2017-222 | GEN-2018-081,2019-074 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2019-011 | GEN-2018-092 | GEN-2018-073
18021901 | TC | 5 | 26 | WP | contingency104.sav | 515458-755000 | 5-26W-10 | 3.2313 | GEN-2019-003,2019-021 | GEN-2018-074,GEN-2017-222 | GEN-2018-081,2019-074 | GEN-2019-011 | GEN-2018-073 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124
18021901 | TC | 5 | 26 | WP | contingency104.sav | 515458-755000 | 5-26W-16 | 3.0145 | GEN-2019-056 | GEN-2019-003,2019-021 | GEN-2018-074,GEN-2017-222 | GEN-2018-081,2019-074 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2018-073 | GEN-2019-011
18021901 | TC | 5 | 26 | WP | contingency104.sav | 515458-755000 | 5-26W-5 | 4.8485 | Bus 1: GEN-2018-073; Bus 2: GEN-2018-092
18021901 | TC | 5 | 26 | WP | contingency106.sav | 523323-523322-523321 | 5-26W-17 | 3.8807 | GEN-2019-003,2019-021 | GEN-2018-074,GEN-2017-222 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2019-011 | GEN-2018-081,2019-074
18021901 | TC | 5 | 26 | WP | contingency108.sav | 523869-523866 | 5-26W-17 | 3.8809 | GEN-2019-003,2019-021 | GEN-2018-074,GEN-2017-222 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2019-011 | GEN-2018-081,2019-074
18021901 | TC | 5 | 26 | WP | contingency108.sav | 523869-523866 | 5-26W-17 | 3.8809 | GEN-2019-003,2019-021 | GEN-2018-074,GEN-2017-222 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2019-011 | GEN-2018-081,2019-074
18021901 | TC | 5 | 26 | WP | contingency111.sav | 523961-523097 | 5-26W-10 | 3.071 | GEN-2019-056 | GEN-2019-003,2019-021 | GEN-2018-074,GEN-2017-222 | GEN-2018-081,2019-074 | GEN-2019-011 | GEN-2018-073 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124
18021901 | TC | 5 | 26 | WP | contingency111.sav | 523961-523097 | 5-26W-16 | 3.5669 | GEN-2019-003,2019-021 | GEN-2018-074,GEN-2017-222 | GEN-2018-081,2019-074 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2019-011 | GEN-2019-056
18021901 | TC | 5 | 26 | WP | contingency115.sav | 523979-523267 | 5-26W-1 | 3.3062 | GEN-2019-003,2019-021 | GEN-2018-074,GEN-2017-222 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2019-011 | GEN-2018-073 | GEN-2018-081,2019-074
18021901 | TC | 5 | 26 | WP | contingency118.sav | 524010-524007-524008 | 5-26W-17 | 3.8809 | GEN-2019-003,2019-021 | GEN-2018-074,GEN-2017-222 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2019-011 | GEN-2018-081,2019-074
18021901 | TC | 5 | 26 | WP | contingency120.sav | 524162-524136 | 5-26W-17 | 3.8808 | GEN-2019-003,2019-021 | GEN-2018-074,GEN-2017-222 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2019-011 | GEN-2018-081,2019-074
18021901 | TC | 5 | 26 | WP | contingency121.sav | 524162-524185 | 5-26W-17 | 3.8806 | GEN-2019-003,2019-021 | GEN-2018-074,GEN-2017-222 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2019-011 | GEN-2018-081,2019-074
18021901 | TC | 5 | 26 | WP | contingency122.sav | 524162-524161-524158 | 5-26W-17 | 3.8809 | GEN-2019-003,2019-021 | GEN-2018-074,GEN-2017-222 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2019-011 | GEN-2018-081,2019-074
18021901 | TC | 5 | 26 | WP | contingency123.sav | 524162-524161-524159 | 5-26W-17 | 3.8809 | GEN-2019-003,2019-021 | GEN-2018-074,GEN-2017-222 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2019-011 | GEN-2018-081,2019-074
18021901 | TC | 5 | 26 | WP | contingency124.sav | 524162-524163-524160 | 5-26W-17 | 3.8807 | GEN-2019-003,2019-021 | GEN-2018-074,GEN-2017-222 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2019-011 | GEN-2018-081,2019-074
18021901 | TC | 5 | 26 | WP | contingency127.sav | 524267-524266-524263 | 5-26W-17 | 3.8763 | GEN-2019-003,2019-021 | GEN-2018-074,GEN-2017-222 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2019-011 | GEN-2018-081,2019-074
18021901 | TC | 5 | 26 | WP | contingency128.sav | 524321-524209 | 5-26W-17 | 3.8809 | GEN-2019-003,2019-021 | GEN-2018-074,GEN-2017-222 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2019-011 | GEN-2018-081,2019-074
18021901 | TC | 5 | 26 | WP | contingency13.sav | 524320-524322-524321 | 5-26W-17 | 3.8809 | GEN-2019-003,2019-021 | GEN-2018-074,GEN-2017-222 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2019-011 | GEN-2018-081,2019-074
18021901 | TC | 5 | 26 | WP | contingency131.sav | 524338-524364 | 5-26W-1 | 3.3068 | GEN-2019-003,2019-021 | GEN-2018-074,GEN-2017-222 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2019-011 | GEN-2018-073 | GEN-2018-081,2019-074
18021901 | TC | 5 | 26 | WP | contingency131.sav | 524338-524364 | 5-26W-12 | 4.6078 | Bus 1: GEN-2019-003,2019-021; Bus 2: GEN-2018-081,2019-074; Bus 3: GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124; Bus 4: GEN-2019-011
18021901 | TC | 5 | 26 | WP | contingency132.sav | 524360-524365-524364 | 5-26W-17 | 3.8806 | GEN-2019-003,2019-021 | GEN-2018-074,GEN-2017-222 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2019-011 | GEN-2018-081,2019-074
18021901 | TC | 5 | 26 | WP | contingency134.sav | 524387-524377 | 5-26W-17 | 3.8807 | GEN-2019-003,2019-021 | GEN-2018-074,GEN-2017-222 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2019-011 | GEN-2018-081,2019-074
18021901 | TC | 5 | 26 | WP | contingency135.sav | 524387-524388 | 5-26W-17 | 3.8806 | GEN-2019-003,2019-021 | GEN-2018-074,GEN-2017-222 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2019-011 | GEN-2018-081,2019-074
18021901 | TC | 5 | 26 | WP | contingency14.sav | 524322-524325 | 5-26W-17 | 3.8809 | GEN-2019-003,2019-021 | GEN-2018-074,GEN-2017-222 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2019-011 | GEN-2018-081,2019-074
18021901 | TC | 5 | 26 | WP | contingency141.sav | 524623-524622-524620 | 5-26W-1 | 3.8328 | GEN-2019-003,2019-021 | GEN-2018-081,2019-074 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2019-011 | GEN-2018-073
18021901 | TC | 5 | 26 | WP | contingency141.sav | 524623-524622-524620 | 5-26W-10 | 3.3071 | GEN-2019-003,2019-021 | GEN-2018-074,GEN-2017-222 | GEN-2018-081,2019-074 | GEN-2019-011 | GEN-2018-073 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124
18021901 | TC | 5 | 26 | WP | contingency141.sav | 524623-524622-524620 | 5-26W-17 | 3.8809 | GEN-2019-003,2019-021 | GEN-2018-074,GEN-2017-222 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2019-011 | GEN-2018-081,2019-074
18021901 | TC | 5 | 26 | WP | contingency142.sav | 524623-524619-524621 | 5-26W-1 | 3.8328 | GEN-2019-003,2019-021 | GEN-2018-081,2019-074 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2019-011 | GEN-2018-073
18021901 | TC | 5 | 26 | WP | contingency142.sav | 524623-524619-524621 | 5-26W-10 | 3.3071 | GEN-2019-003,2019-021 | GEN-2018-074,GEN-2017-222 | GEN-2018-081,2019-074 | GEN-2019-011 | GEN-2018-073 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124
18021901 | TC | 5 | 26 | WP | contingency142.sav | 524623-524619-524621 | 5-26W-17 | 3.8809 | GEN-2019-003,2019-021 | GEN-2018-074,GEN-2017-222 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2019-011 | GEN-2018-081,2019-074
18021901 | TC | 5 | 26 | WP | contingency143.sav | 524746-524694 | 5-26W-1 | 5.7142 | Bus 1: GEN-2019-003,2019-021; Bus 2: GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124; Bus 3: GEN-2018-081,2019-074
18021901 | TC | 5 | 26 | WP | contingency143.sav | 524746-524694 | 5-26W-11 | 4.6061 | Bus 1: GEN-2019-003,2019-021; Bus 2: GEN-2018-081,2019-074; Bus 3: GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124; Bus 4: GEN-2019-011
18021901 | TC | 5 | 26 | WP | contingency145.sav | 524746-524757 | 5-26W-1 | 3.8329 | GEN-2019-003,2019-021 | GEN-2018-081,2019-074 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2019-011 | GEN-2018-073
18021901 | TC | 5 | 26 | WP | contingency145.sav | 524746-524757 | 5-26W-10 | 3.881 | GEN-2019-003,2019-021 | GEN-2018-074,GEN-2017-222 | GEN-2018-081,2019-074 | GEN-2019-011 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124
18021901 | TC | 5 | 26 | WP | contingency145.sav | 524746-524757 | 5-26W-13 | 3.3073 | GEN-2018-074,GEN-2017-222 | GEN-2018-081,2019-074 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2019-011 | GEN-2018-073 | GEN-2019-003,2019-021
18021901 | TC | 5 | 26 | WP | contingency147.sav | 524746-524745-524743 | 5-26W-17 | 3.8808 | GEN-2019-003,2019-021 | GEN-2018-074,GEN-2017-222 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2019-011 | GEN-2018-081,2019-074
18021901 | TC | 5 | 26 | WP | contingency148.sav | 524746-524745-524744 | 5-26W-17 | 3.8808 | GEN-2019-003,2019-021 | GEN-2018-074,GEN-2017-222 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2019-011 | GEN-2018-081,2019-074
18021901 | TC | 5 | 26 | WP | contingency149.sav | 524768-524502 | 5-26W-1 | 3.8261 | GEN-2019-003,2019-021 | GEN-2018-081,2019-074 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2019-011 | GEN-2018-073
18021901 | TC | 5 | 26 | WP | contingency149.sav | 524768-524502 | 5-26W-10 | 3.3017 | GEN-2019-003,2019-021 | GEN-2018-074,GEN-2017-222 | GEN-2018-081,2019-074 | GEN-2019-011 | GEN-2018-073 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124
18021901 | TC | 5 | 26 | WP | contingency149.sav | 524768-524502 | 5-26W-17 | 3.8739 | GEN-2019-003,2019-021 | GEN-2018-074,GEN-2017-222 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2019-011 | GEN-2018-081,2019-074
18021901 | TC | 5 | 26 | WP | contingency15.sav | 524322-524387 | 5-26W-17 | 3.8807 | GEN-2019-003,2019-021 | GEN-2018-074,GEN-2017-222 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2019-011 | GEN-2018-081,2019-074
18021901 | TC | 5 | 26 | WP | contingency150.sav | 524768-524773 | 5-26W-17 | 3.8806 | GEN-2019-003,2019-021 | GEN-2018-074,GEN-2017-222 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2019-011 | GEN-2018-081,2019-074
18021901 | TC | 5 | 26 | WP | contingency151.sav | 524768-524776 | 5-26W-17 | 3.8818 | GEN-2019-003,2019-021 | GEN-2018-074,GEN-2017-222 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2019-011 | GEN-2018-081,2019-074
18021901 | TC | 5 | 26 | WP | contingency152.sav | 524768-524831 | 5-26W-17 | 3.8805 | GEN-2019-003,2019-021 | GEN-2018-074,GEN-2017-222 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2019-011 | GEN-2018-081,2019-074
18021901 | TC | 5 | 26 | WP | contingency153.sav | 524770-524909 | 5-26W-17 | 3.8806 | GEN-2019-003,2019-021 | GEN-2018-074,GEN-2017-222 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2019-011 | GEN-2018-081,2019-074
18021901 | TC | 5 | 26 | WP | contingency154.sav | 524822-524669 | 5-26W-1 | 3.8136 | GEN-2019-003,2019-021 | GEN-2018-081,2019-074 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2019-011 | GEN-2018-073
18021901 | TC | 5 | 26 | WP | contingency154.sav | 524822-524669 | 5-26W-10 | 3.2913 | GEN-2019-003,2019-021 | GEN-2018-074,GEN-2017-222 | GEN-2018-081,2019-074 | GEN-2019-011 | GEN-2018-073 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124
18021901 | TC | 5 | 26 | WP | contingency155.sav | 524822-524764 | 5-26W-17 | 3.8802 | GEN-2019-003,2019-021 | GEN-2018-074,GEN-2017-222 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2019-011 | GEN-2018-081,2019-074
18021901 | TC | 5 | 26 | WP | contingency156.sav | 524822-524773 | 5-26W-17 | 3.8807 | GEN-2019-003,2019-021 | GEN-2018-074,GEN-2017-222 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2019-011 | GEN-2018-081,2019-074
18021901 | TC | 5 | 26 | WP | contingency157.sav | 524822-524838 | 5-26W-17 | 3.8806 | GEN-2019-003,2019-021 | GEN-2018-074,GEN-2017-222 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2019-011 | GEN-2018-081,2019-074
18021901 | TC | 5 | 26 | WP | contingency158.sav | 524822-525028 | 5-26W-1 | 3.8236 | GEN-2019-003,2019-021 | GEN-2018-081,2019-074 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2019-011 | GEN-2018-073
18021901 | TC | 5 | 26 | WP | contingency158.sav | 524822-525028 | 5-26W-10 | 3.2994 | GEN-2019-003,2019-021 | GEN-2018-074,GEN-2017-222 | GEN-2018-081,2019-074 | GEN-2019-011 | GEN-2018-073 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124
18021901 | TC | 5 | 26 | WP | contingency158.sav | 524822-525028 | 5-26W-17 | 3.8709 | GEN-2019-003,2019-021 | GEN-2018-074,GEN-2017-222 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2019-011 | GEN-2018-081,2019-074
18021901 | TC | 5 | 26 | WP | contingency159.sav | 524822-524821-524819 | 5-26W-17 | 3.8809 | GEN-2019-003,2019-021 | GEN-2018-074,GEN-2017-222 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2019-011 | GEN-2018-081,2019-074
18021901 | TC | 5 | 26 | WP | contingency160.sav | 524822-524821-524820 | 5-26W-17 | 3.8809 | GEN-2019-003,2019-021 | GEN-2018-074,GEN-2017-222 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2019-011 | GEN-2018-081,2019-074
18021901 | TC | 5 | 26 | WP | contingency162.sav | 524874-524863 | 5-26W-17 | 3.8798 | GEN-2019-003,2019-021 | GEN-2018-074,GEN-2017-222 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2019-011 | GEN-2018-081,2019-074
18021901 | TC | 5 | 26 | WP | contingency163.sav | 524875-524909 | 5-26W-1 | 3.8239 | GEN-2019-003,2019-021 | GEN-2018-081,2019-074 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2019-011 | GEN-2018-073
18021901 | TC | 5 | 26 | WP | contingency163.sav | 524875-524909 | 5-26W-10 | 3.2999 | GEN-2019-003,2019-021 | GEN-2018-074,GEN-2017-222 | GEN-2018-081,2019-074 | GEN-2019-011 | GEN-2018-073 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124
18021901 | TC | 5 | 26 | WP | contingency163.sav | 524875-524909 | 5-26W-17 | 3.8714 | GEN-2019-003,2019-021 | GEN-2018-074,GEN-2017-222 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2019-011 | GEN-2018-081,2019-074
18021901 | TC | 5 | 26 | WP | contingency164.sav | 524885-524889 | 5-26W-1 | 3.8336 | GEN-2019-003,2019-021 | GEN-2018-081,2019-074 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2019-011 | GEN-2018-073
18021901 | TC | 5 | 26 | WP | contingency164.sav | 524885-524889 | 5-26W-10 | 3.3079 | GEN-2019-003,2019-021 | GEN-2018-074,GEN-2017-222 | GEN-2018-081,2019-074 | GEN-2019-011 | GEN-2018-073 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124
18021901 | TC | 5 | 26 | WP | contingency165.sav | 524885-527483 | 5-26W-13 | 3.8371 | GEN-2018-074,GEN-2017-222 | GEN-2018-081,2019-074 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2019-011 | GEN-2019-003,2019-021
18021901 | TC | 5 | 26 | WP | contingency167.sav | 524924-524935 | 5-26W-17 | 3.8809 | GEN-2019-003,2019-021 | GEN-2018-074,GEN-2017-222 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2019-011 | GEN-2018-081,2019-074
18021901 | TC | 5 | 26 | WP | contingency168.sav | 524924-524977 | 5-26W-17 | 3.881 | GEN-2019-003,2019-021 | GEN-2018-074,GEN-2017-222 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2019-011 | GEN-2018-081,2019-074
18021901 | TC | 5 | 26 | WP | contingency169.sav | 524924-524923-524921 | 5-26W-17 | 3.8808 | GEN-2019-003,2019-021 | GEN-2018-074,GEN-2017-222 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2019-011 | GEN-2018-081,2019-074
18021901 | TC | 5 | 26 | WP | contingency170.sav | 524924-524923-524922 | 5-26W-17 | 3.8807 | GEN-2019-003,2019-021 | GEN-2018-074,GEN-2017-222 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2019-011 | GEN-2018-081,2019-074
18021901 | TC | 5 | 26 | WP | contingency172.sav | 525019-525028 | 5-26W-1 | 3.8256 | GEN-2019-003,2019-021 | GEN-2018-081,2019-074 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2019-011 | GEN-2018-073
18021901 | TC | 5 | 26 | WP | contingency172.sav | 525019-525028 | 5-26W-10 | 3.301 | GEN-2019-003,2019-021 | GEN-2018-074,GEN-2017-222 | GEN-2018-081,2019-074 | GEN-2019-011 | GEN-2018-073 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124
18021901 | TC | 5 | 26 | WP | contingency172.sav | 525019-525028 | 5-26W-17 | 3.873 | GEN-2019-003,2019-021 | GEN-2018-074,GEN-2017-222 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2019-011 | GEN-2018-081,2019-074
18021901 | TC | 5 | 26 | WP | contingency174.sav | 525124-525414 | 5-26W-1 | 3.8322 | GEN-2019-003,2019-021 | GEN-2018-081,2019-074 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2019-011 | GEN-2018-073
18021901 | TC | 5 | 26 | WP | contingency174.sav | 525124-525414 | 5-26W-10 | 3.3022 | GEN-2019-003,2019-021 | GEN-2018-074,GEN-2017-222 | GEN-2018-081,2019-074 | GEN-2019-011 | GEN-2018-073 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124
18021901 | TC | 5 | 26 | WP | contingency174.sav | 525124-525414 | 5-26W-17 | 3.8745 | GEN-2019-003,2019-021 | GEN-2018-074,GEN-2017-222 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2019-011 | GEN-2018-081,2019-074
18021901 | TC | 5 | 26 | WP | contingency218.sav | 525154-525179 | 5-26W-1 | 3.2981 | GEN-2019-003,2019-021 | GEN-2018-074,GEN-2017-222 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2019-011 | GEN-2018-073 | GEN-2018-081,2019-074
18021901 | TC | 5 | 26 | WP | contingency175.sav | 525154-525179 | 5-26W-12 | 4.5986 | Bus 1: GEN-2019-003,2019-021; Bus 2: GEN-2018-081,2019-074; Bus 3: GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124; Bus 4: GEN-2019-011
18021901 | TC | 5 | 26 | WP | contingency218.sav | 525154-525153-525151 | 5-26W-17 | 3.8809 | GEN-2019-003,2019-021 | GEN-2018-074,GEN-2017-222 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2019-011 | GEN-2018-081,2019-074
18021901 | TC | 5 | 26 | WP | contingency177.sav | 525154-525153-525152 | 5-26W-17 | 3.8809 | GEN-2019-003,2019-021 | GEN-2018-074,GEN-2017-222 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2019-011 | GEN-2018-081,2019-074
18021901 | TC | 5 | 26 | WP | contingency178.sav | 525192-525179 | 5-26W-1 | 5.704 | Bus 1: GEN-2019-003,2019-021; Bus 2: GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124; Bus 3: GEN-2018-081,2019-074
18021901 | TC | 5 | 26 | WP | contingency178.sav | 525192-525179 | 5-26W-11 | 4.5982 | Bus 1: GEN-2019-003,2019-021; Bus 2: GEN-2018-081,2019-074; Bus 3: GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124; Bus 4: GEN-2019-011
18021901 | TC | 5 | 26 | WP | contingency179.sav | 525192-525226 | 5-26W-1 | 3.8328 | GEN-2019-003,2019-021 | GEN-2018-081,2019-074 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2019-011 | GEN-2018-073
18021901 | TC | 5 | 26 | WP | contingency179.sav | 525192-525226 | 5-26W-10 | 3.3064 | GEN-2019-003,2019-021 | GEN-2018-074,GEN-2017-222 | GEN-2018-081,2019-074 | GEN-2019-011 | GEN-2018-073 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124
18021901 | TC | 5 | 26 | WP | contingency179.sav | 525192-525226 | 5-26W-17 | 3.8801 | GEN-2019-003,2019-021 | GEN-2018-074,GEN-2017-222 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2019-011 | GEN-2018-081,2019-074
18021901 | TC | 5 | 26 | WP | contingency180.sav | 525192-525191-525190 | 5-26W-1 | 3.3073 | GEN-2019-003,2019-021 | GEN-2018-074,GEN-2017-222 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2019-011 | GEN-2018-073 | GEN-2018-081,2019-074
18021901 | TC | 5 | 26 | WP | contingency180.sav | 525192-525191-525190 | 5-26W-12 | 4.6086 | Bus 1: GEN-2019-003,2019-021; Bus 2: GEN-2018-081,2019-074; Bus 3: GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124; Bus 4: GEN-2019-011
18021901 | TC | 5 | 26 | WP | contingency181.sav | 525213-525461 | 5-26W-1 | 3.8039 | GEN-2019-003,2019-021 | GEN-2018-081,2019-074 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2019-011 | GEN-2018-073
18021901 | TC | 5 | 26 | WP | contingency181.sav | 525213-525461 | 5-26W-10 | 3.7976 | GEN-2019-003,2019-021 | GEN-2018-074,GEN-2017-222 | GEN-2018-081,2019-074 | GEN-2019-011 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124
18021901 | TC | 5 | 26 | WP | contingency181.sav | 525213-525461 | 5-26W-13 | 3.2391 | GEN-2018-074,GEN-2017-222 | GEN-2018-081,2019-074 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2019-011 | GEN-2018-073 | GEN-2019-003,2019-021
18021901 | TC | 5 | 26 | WP | contingency182.sav | 525446-525393 | 5-26W-17 | 3.8809 | GEN-2019-003,2019-021 | GEN-2018-074,GEN-2017-222 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2019-011 | GEN-2018-081,2019-074
18021901 | TC | 5 | 26 | WP | contingency183.sav | 525446-525440 | 5-26W-1 | 3.8229 | GEN-2019-003,2019-021 | GEN-2018-081,2019-074 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2019-011 | GEN-2018-073
18021901 | TC | 5 | 26 | WP | contingency183.sav | 525446-525440 | 5-26W-10 | 3.2974 | GEN-2019-003,2019-021 | GEN-2018-074,GEN-2017-222 | GEN-2018-081,2019-074 | GEN-2019-011 | GEN-2018-073 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124
18021901 | TC | 5 | 26 | WP | contingency183.sav | 525446-525440 | 5-26W-17 | 3.8686 | GEN-2019-003,2019-021 | GEN-2018-074,GEN-2017-222 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2019-011 | GEN-2018-081,2019-074
18021901 | TC | 5 | 26 | WP | contingency184.sav | 525454-525326 | 5-26W-17 | 3.8793 | GEN-2019-003,2019-021 | GEN-2018-074,GEN-2017-222 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2019-011 | GEN-2018-081,2019-074
18021901 | TC | 5 | 26 | WP | contingency185.sav | 525454-525414 | 5-26W-1 | 3.8281 | GEN-2019-003,2019-021 | GEN-2018-081,2019-074 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2019-011 | GEN-2018-073
18021901 | TC | 5 | 26 | WP | contingency185.sav | 525454-525414 | 5-26W-10 | 3.3028 | GEN-2019-003,2019-021 | GEN-2018-074,GEN-2017-222 | GEN-2018-081,2019-074 | GEN-2019-011 | GEN-2018-073 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124
18021901 | TC | 5 | 26 | WP | contingency185.sav | 525454-525414 | 5-26W-17 | 3.8759 | GEN-2019-003,2019-021 | GEN-2018-074,GEN-2017-222 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2019-011 | GEN-2018-081,2019-074
18021901 | TC | 5 | 26 | WP | contingency186.sav | 525454-525453-525451 | 5-26W-17 | 3.8809 | GEN-2019-003,2019-021 | GEN-2018-074,GEN-2017-222 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2019-011 | GEN-2018-081,2019-074
18021901 | TC | 5 | 26 | WP | contingency187.sav | 525454-525453-525452 | 5-26W-17 | 3.8809 | GEN-2019-003,2019-021 | GEN-2018-074,GEN-2017-222 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2019-011 | GEN-2018-081,2019-074
18021901 | TC | 5 | 26 | WP | contingency188.sav | 525458-525461-525460 | 5-26W-17 | 3.875 | GEN-2019-003,2019-021 | GEN-2018-074,GEN-2017-222 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2019-011 | GEN-2018-081,2019-074
18021901 | TC | 5 | 26 | WP | contingency189.sav | 525459-525461-525460 | 5-26W-17 | 3.8755 | GEN-2019-003,2019-021 | GEN-2018-074,GEN-2017-222 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2019-011 | GEN-2018-081,2019-074
18021901 | TC | 5 | 26 | WP | contingency190.sav | 525479-525481-525480 | 5-26W-1 | 3.8037 | GEN-2019-003,2019-021 | GEN-2018-081,2019-074 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2019-011 | GEN-2018-073
18021901 | TC | 5 | 26 | WP | contingency190.sav | 525479-525481-525480 | 5-26W-10 | 3.2822 | GEN-2019-003,2019-021 | GEN-2018-074,GEN-2017-222 | GEN-2018-081,2019-074 | GEN-2019-011 | GEN-2018-073 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124
18021901 | TC | 5 | 26 | WP | contingency190.sav | 525479-525481-525480 | 5-26W-17 | 3.8487 | GEN-2019-003,2019-021 | GEN-2018-074,GEN-2017-222 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2019-011 | GEN-2018-081,2019-074
18021901 | TC | 5 | 26 | WP | contingency196.sav | 525585-525584 | 5-26W-17 | 3.8809 | GEN-2019-003,2019-021 | GEN-2018-074,GEN-2017-222 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2019-011 | GEN-2018-081,2019-074
18021901 | TC | 5 | 26 | WP | contingency197.sav | 525586-525531 | 5-26W-17 | 3.7734 | GEN-2019-003,2019-021 | GEN-2018-074,GEN-2017-222 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2019-011 | GEN-2018-081,2019-074
18021901 | TC | 5 | 26 | WP | contingency198.sav | 525636-526020 | 5-26W-1 | 3.8133 | GEN-2019-003,2019-021 | GEN-2018-081,2019-074 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2019-011 | GEN-2018-073
18021901 | TC | 5 | 26 | WP | contingency198.sav | 525636-526020 | 5-26W-10 | 3.291 | GEN-2019-003,2019-021 | GEN-2018-074,GEN-2017-222 | GEN-2018-081,2019-074 | GEN-2019-011 | GEN-2018-073 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124
18021901 | TC | 5 | 26 | WP | contingency199.sav | 525636-525635-525631 | 5-26W-17 | 3.8811 | GEN-2019-003,2019-021 | GEN-2018-074,GEN-2017-222 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2019-011 | GEN-2018-081,2019-074
18021901 | TC | 5 | 26 | WP | contingency200.sav | 525636-525635-525632 | 5-26W-17 | 3.8811 | GEN-2019-003,2019-021 | GEN-2018-074,GEN-2017-222 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2019-011 | GEN-2018-081,2019-074
18021901 | TC | 5 | 26 | WP | contingency201.sav | 525637-525531 | 5-26W-1 | 3.8118 | GEN-2019-003,2019-021 | GEN-2018-081,2019-074 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2019-011 | GEN-2018-073
18021901 | TC | 5 | 26 | WP | contingency201.sav | 525637-525531 | 5-26W-10 | 3.2899 | GEN-2019-003,2019-021 | GEN-2018-074,GEN-2017-222 | GEN-2018-081,2019-074 | GEN-2019-011 | GEN-2018-073 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124
18021901 | TC | 5 | 26 | WP | contingency202.sav | 525828-525780 | 5-26W-1 | 3.8319 | GEN-2019-003,2019-021 | GEN-2018-081,2019-074 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2019-011 | GEN-2018-073
18021901 | TC | 5 | 26 | WP | contingency202.sav | 525828-525780 | 5-26W-10 | 3.3062 | GEN-2019-003,2019-021 | GEN-2018-074,GEN-2017-222 | GEN-2018-081,2019-074 | GEN-2019-011 | GEN-2018-073 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124
18021901 | TC | 5 | 26 | WP | contingency202.sav | 525828-525780 | 5-26W-17 | 3.8807 | GEN-2019-003,2019-021 | GEN-2018-074,GEN-2017-222 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2019-011 | GEN-2018-081,2019-074
18021901 | TC | 5 | 26 | WP | contingency203.sav | 525828-526076 | 5-26W-17 | 3.8808 | GEN-2019-003,2019-021 | GEN-2018-074,GEN-2017-222 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2019-011 | GEN-2018-081,2019-074
18021901 | TC | 5 | 26 | WP | contingency204.sav | 525828-526298 | 5-26W-17 | 3.8795 | GEN-2019-003,2019-021 | GEN-2018-074,GEN-2017-222 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2019-011 | GEN-2018-081,2019-074
18021901 | TC | 5 | 26 | WP | contingency205.sav | 525828-525816-525814 | 5-26W-1 | 3.3064 | GEN-2019-003,2019-021 | GEN-2018-074,GEN-2017-222 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2019-011 | GEN-2018-073 | GEN-2018-081,2019-074
18021901 | TC | 5 | 26 | WP | contingency205.sav | 525828-525816-525814 | 5-26W-12 | 4.6075 | Bus 1: GEN-2019-003,2019-021; Bus 2: GEN-2018-081,2019-074; Bus 3: GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124; Bus 4: GEN-2019-011
18021901 | TC | 5 | 26 | WP | contingency206.sav | 525828-525826-525822 | 5-26W-17 | 3.8809 | GEN-2019-003,2019-021 | GEN-2018-074,GEN-2017-222 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2019-011 | GEN-2018-081,2019-074
18021901 | TC | 5 | 26 | WP | contingency207.sav | 525828-525826-525823 | 5-26W-17 | 3.8809 | GEN-2019-003,2019-021 | GEN-2018-074,GEN-2017-222 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2019-011 | GEN-2018-081,2019-074
18021901 | TC | 5 | 26 | WP | contingency208.sav | 525830-525531 | 5-26W-1 | 3.6333 | GEN-2019-003,2019-021 | GEN-2018-081,2019-074 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2019-011 | GEN-2018-073
18021901 | TC | 5 | 26 | WP | contingency208.sav | 525830-525531 | 5-26W-10 | 3.6982 | GEN-2019-003,2019-021 | GEN-2018-074,GEN-2017-222 | GEN-2018-081,2019-074 | GEN-2019-011 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124
18021901 | TC | 5 | 26 | WP | contingency208.sav | 525830-525531 | 5-26W-14 | 3.144 | GEN-2019-003,2019-021 | GEN-2018-074,GEN-2017-222 | GEN-2018-081,2019-074 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2018-073 | GEN-2019-011
18021901 | TC | 5 | 26 | WP | contingency209.sav | 525832-526936 | 5-26W-1 | 3.7003 | GEN-2019-003,2019-021 | GEN-2018-081,2019-074 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2019-011 | GEN-2018-073
18021901 | TC | 5 | 26 | WP | contingency209.sav | 525832-526936 | 5-26W-10 | 3.8089 | GEN-2019-003,2019-021 | GEN-2018-074,GEN-2017-222 | GEN-2018-081,2019-074 | GEN-2019-011 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124
18021901 | TC | 5 | 26 | WP | contingency209.sav | 525832-526936 | 5-26W-14 | 3.1989 | GEN-2019-003,2019-021 | GEN-2018-074,GEN-2017-222 | GEN-2018-081,2019-074 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2018-073 | GEN-2019-011
18021901 | TC | 5 | 26 | WP | contingency210.sav | 525832-560022 | 5-26W-1 | 3.8279 | GEN-2019-003,2019-021 | GEN-2018-081,2019-074 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2019-011 | GEN-2018-073
18021901 | TC | 5 | 26 | WP | contingency210.sav | 525832-560022 | 5-26W-10 | 3.3032 | GEN-2019-003,2019-021 | GEN-2018-074,GEN-2017-222 | GEN-2018-081,2019-074 | GEN-2019-011 | GEN-2018-073 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124
18021901 | TC | 5 | 26 | WP | contingency210.sav | 525832-560022 | 5-26W-17 | 3.8806 | GEN-2019-003,2019-021 | GEN-2018-074,GEN-2017-222 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2019-011 | GEN-2018-081,2019-074
18021901 | TC | 5 | 26 | WP | contingency215.sav | 525850-525844 | 5-26W-17 | 3.8809 | GEN-2019-003,2019-021 | GEN-2018-074,GEN-2017-222 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2019-011 | GEN-2018-081,2019-074
18021901 | TC | 5 | 26 | WP | contingency216.sav | 525850-525845 | 5-26W-17 | 3.8809 | GEN-2019-003,2019-021 | GEN-2018-074,GEN-2017-222 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2019-011 | GEN-2018-081,2019-074
18021901 | TC | 5 | 26 | WP | contingency217.sav | 525957-562268 | 5-26W-17 | 3.8809 | GEN-2019-003,2019-021 | GEN-2018-074,GEN-2017-222 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2019-011 | GEN-2018-081,2019-074
18021901 | TC | 5 | 26 | WP | contingency218.sav | 525957-525931-525930 | 5-26W-17 | 3.8815 | GEN-2019-003,2019-021 | GEN-2018-074,GEN-2017-222 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2019-011 | GEN-2018-081,2019-074
18021901 | TC | 5 | 26 | WP | contingency22.sav | 524530-587570 | 5-26W-1 | 3.8327 | GEN-2019-003,2019-021 | GEN-2018-081,2019-074 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2019-011 | GEN-2018-073
18021901 | TC | 5 | 26 | WP | contingency22.sav | 524530-587570 | 5-26W-10 | 3.3071 | GEN-2019-003,2019-021 | GEN-2018-074,GEN-2017-222 | GEN-2018-081,2019-074 | GEN-2019-011 | GEN-2018-073 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124
18021901 | TC | 5 | 26 | WP | contingency22.sav | 524530-587570 | 5-26W-17 | 3.8809 | GEN-2019-003,2019-021 | GEN-2018-074,GEN-2017-222 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2019-011 | GEN-2018-081,2019-074
18021901 | TC | 5 | 26 | WP | contingency221.sav | 526161-526160-526157 | 5-26W-17 | 3.8803 | GEN-2019-003,2019-021 | GEN-2018-074,GEN-2017-222 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2019-011 | GEN-2018-081,2019-074
18021901 | TC | 5 | 26 | WP | contingency222.sav | 526337-526269 | 5-26W-17 | 3.8796 | GEN-2019-003,2019-021 | GEN-2018-074,GEN-2017-222 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2019-011 | GEN-2018-081,2019-074
18021901 | TC | 5 | 26 | WP | contingency222.sav | 526337-526269 | 5-26W-17 | 3.8796 | GEN-2019-003,2019-021 | GEN-2018-074,GEN-2017-222 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2019-011 | GEN-2018-081,2019-074
18021901 | TC | 5 | 26 | WP | contingency227 | 526337-526333 | 5-26W-17 | 3.8808 | GEN-2019-003,2019-021 | GEN-2018-074,GEN-2017-222 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2019-011 | GEN-2018-081,2019-074
18021901 | TC | 5 | 26 | WP | contingency228.sav | 526337-526334 | 5-26W-17 | 3.8795 | GEN-2019-003,2019-021 | GEN-2018-074,GEN-2017-222 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2019-011 | GEN-2018-081,2019-074
18021901 | TC | 5 | 26 | WP | contingency229.sav | 526337-526677 | 5-26W-17 | 3.8814 | GEN-2019-003,2019-021 | GEN-2018-074,GEN-2017-222 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2019-011 | GEN-2018-081,2019-074
18021901 | TC | 5 | 26 | WP | contingency230.sav | 526434-526036 | 5-26W-1 | 3.8152 | GEN-2019-003,2019-021 | GEN-2018-081,2019-074 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2019-011 | GEN-2018-073
18021901 | TC | 5 | 26 | WP | contingency230.sav | 526434-526036 | 5-26W-10 | 3.2926 | GEN-2019-003,2019-021 | GEN-2018-074,GEN-2017-222 | GEN-2018-081,2019-074 | GEN-2019-011 | GEN-2018-073 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124
18021901 | TC | 5 | 26 | WP | contingency230.sav | 526434-526036 | 5-26W-17 | 3.8621 | GEN-2019-003,2019-021 | GEN-2018-074,GEN-2017-222 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2019-011 | GEN-2018-081,2019-074
18021901 | TC | 5 | 26 | WP | contingency231.sav | 526434-526424 | 5-26W-1 | 3.8243 | GEN-2019-003,2019-021 | GEN-2018-081,2019-074 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2019-011 | GEN-2018-073
18021901 | TC | 5 | 26 | WP | contingency231.sav | 526434-526424 | 5-26W-10 | 3.3 | GEN-2019-003,2019-021 | GEN-2018-074,GEN-2017-222 | GEN-2018-081,2019-074 | GEN-2019-011 | GEN-2018-073 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124
18021901 | TC | 5 | 26 | WP | contingency231.sav | 526434-526424 | 5-26W-17 | 3.8721 | GEN-2019-003,2019-021 | GEN-2018-074,GEN-2017-222 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2019-011 | GEN-2018-081,2019-074
18021901 | TC | 5 | 26 | WP | contingency232.sav | 526434-526445 | 5-26W-17 | 3.8735 | GEN-2019-003,2019-021 | GEN-2018-074,GEN-2017-222 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2019-011 | GEN-2018-081,2019-074
18021901 | TC | 5 | 26 | WP | contingency233.sav | 526435-525481 | 5-26W-1 | 3.7192 | GEN-2019-003,2019-021 | GEN-2018-081,2019-074 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2019-011 | GEN-2018-073
18021901 | TC | 5 | 26 | WP | contingency233.sav | 526435-525481 | 5-26W-10 | 3.7601 | GEN-2019-003,2019-021 | GEN-2018-074,GEN-2017-222 | GEN-2018-081,2019-074 | GEN-2019-011 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124
18021901 | TC | 5 | 26 | WP | contingency233.sav | 526435-525481 | 5-26W-14 | 3.2134 | GEN-2019-003,2019-021 | GEN-2018-074,GEN-2017-222 | GEN-2018-081,2019-074 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2018-073 | GEN-2019-011
18021901 | TC | 5 | 26 | WP | contingency234.sav | 526525-526269 | 5-26W-1 | 3.8157 | GEN-2019-003,2019-021 | GEN-2018-081,2019-074 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2019-011 | GEN-2018-073
18021901 | TC | 5 | 26 | WP | contingency234.sav | 526525-526269 | 5-26W-10 | 3.2932 | GEN-2019-003,2019-021 | GEN-2018-074,GEN-2017-222 | GEN-2018-081,2019-074 | GEN-2019-011 | GEN-2018-073 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124
18021901 | TC | 5 | 26 | WP | contingency235.sav | 526525-526524-526522 | 5-26W-1 | 3.8326 | GEN-2019-003,2019-021 | GEN-2018-081,2019-074 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2019-011 | GEN-2018-073
18021901 | TC | 5 | 26 | WP | contingency235.sav | 526525-526524-526522 | 5-26W-10 | 3.307 | GEN-2019-003,2019-021 | GEN-2018-074,GEN-2017-222 | GEN-2018-081,2019-074 | GEN-2019-011 | GEN-2018-073 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124
18021901 | TC | 5 | 26 | WP | contingency235.sav | 526525-526524-526522 | 5-26W-17 | 3.8808 | GEN-2019-003,2019-021 | GEN-2018-074,GEN-2017-222 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2019-011 | GEN-2018-081,2019-074
18021901 | TC | 5 | 26 | WP | contingency236.sav | 526934-526792 | 5-26W-17 | 3.8804 | GEN-2019-003,2019-021 | GEN-2018-074,GEN-2017-222 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2019-011 | GEN-2018-081,2019-074
18021901 | TC | 5 | 26 | WP | contingency237.sav | 526934-526928 | 5-26W-1 | 3.832 | GEN-2019-003,2019-021 | GEN-2018-081,2019-074 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2019-011 | GEN-2018-073
18021901 | TC | 5 | 26 | WP | contingency237.sav | 526934-526928 | 5-26W-10 | 3.3065 | GEN-2019-003,2019-021 | GEN-2018-074,GEN-2017-222 | GEN-2018-081,2019-074 | GEN-2019-011 | GEN-2018-073 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124
18021901 | TC | 5 | 26 | WP | contingency237.sav | 526934-526928 | 5-26W-17 | 3.88 | GEN-2019-003,2019-021 | GEN-2018-074,GEN-2017-222 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2019-011 | GEN-2018-081,2019-074
18021901 | TC | 5 | 26 | WP | contingency238.sav | 526934-527041 | 5-26W-17 | 3.8747 | GEN-2019-003,2019-021 | GEN-2018-074,GEN-2017-222 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2019-011 | GEN-2018-081,2019-074
18021901 | TC | 5 | 26 | WP | contingency239.sav | 526934-527194 | 5-26W-17 | 3.8796 | GEN-2019-003,2019-021 | GEN-2018-074,GEN-2017-222 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2019-011 | GEN-2018-081,2019-074
18021901 | TC | 5 | 26 | WP | contingency24.sav | 524746-525460 | 5-26W-17 | 3.8697 | GEN-2019-003,2019-021 | GEN-2018-074,GEN-2017-222 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2019-011 | GEN-2018-081,2019-074
18021901 | TC | 5 | 26 | WP | contingency240.sav | 526935-526936-526937 | 5-26W-17 | 3.7573 | GEN-2019-003,2019-021 | GEN-2018-074,GEN-2017-222 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2019-011 | GEN-2018-081,2019-074
18021901 | TC | 5 | 26 | WP | contingency241.sav | 527009-527010 | 5-26W-1 | 5.7165 | Bus 1: GEN-2019-003,2019-021; Bus 2: GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124; Bus 3: GEN-2018-081,2019-074
18021901 | TC | 5 | 26 | WP | contingency241.sav | 527009-527010 | 5-26W-10 | 4.6078 | Bus 1: GEN-2018-081,2019-074; Bus 2: GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124; Bus 3: GEN-2019-011; Bus 4: GEN-2019-003,2019-021
18021901 | TC | 5 | 26 | WP | contingency242.sav | 527009-527011 | 5-26W-17 | 3.8669 | GEN-2019-003,2019-021 | GEN-2018-074,GEN-2017-222 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2019-011 | GEN-2018-081,2019-074
18021901 | TC | 5 | 26 | WP | contingency243.sav | 527028-527027-527026 | 5-26W-1 | 3.8277 | GEN-2019-003,2019-021 | GEN-2018-081,2019-074 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2019-011 | GEN-2018-073
18021901 | TC | 5 | 26 | WP | contingency243.sav | 527028-527027-527026 | 5-26W-10 | 3.303 | GEN-2019-003,2019-021 | GEN-2018-074,GEN-2017-222 | GEN-2018-081,2019-074 | GEN-2019-011 | GEN-2018-073 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124
18021901 | TC | 5 | 26 | WP | contingency243.sav | 527028-527027-527026 | 5-26W-17 | 3.8758 | GEN-2019-003,2019-021 | GEN-2018-074,GEN-2017-222 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2019-011 | GEN-2018-081,2019-074
18021901 | TC | 5 | 26 | WP | contingency244.sav | 527149-526784 | 5-26W-17 | 3.8681 | GEN-2019-003,2019-021 | GEN-2018-074,GEN-2017-222 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2019-011 | GEN-2018-081,2019-074
18021901 | TC | 5 | 26 | WP | contingency246.sav | 527149-527276 | 5-26W-1 | 3.8295 | GEN-2019-003,2019-021 | GEN-2018-081,2019-074 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2019-011 | GEN-2018-073
18021901 | TC | 5 | 26 | WP | contingency246.sav | 527149-527276 | 5-26W-10 | 3.3045 | GEN-2019-003,2019-021 | GEN-2018-074,GEN-2017-222 | GEN-2018-081,2019-074 | GEN-2019-011 | GEN-2018-073 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124
18021901 | TC | 5 | 26 | WP | contingency246.sav | 527149-527276 | 5-26W-17 | 3.8776 | GEN-2019-003,2019-021 | GEN-2018-074,GEN-2017-222 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2019-011 | GEN-2018-081,2019-074
18021901 | TC | 5 | 26 | WP | contingency247.sav | 527149-527146-527143 | 5-26W-17 | 3.8764 | GEN-2019-003,2019-021 | GEN-2018-074,GEN-2017-222 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2019-011 | GEN-2018-081,2019-074
18021901 | TC | 5 | 26 | WP | contingency248.sav | 527656-527610 | 5-26W-1 | 3.8403 | GEN-2019-003,2019-021 | GEN-2018-081,2019-074 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2019-011 | GEN-2018-073
18021901 | TC | 5 | 26 | WP | contingency248.sav | 527656-527610 | 5-26W-10 | 3.3134 | GEN-2019-003,2019-021 | GEN-2018-074,GEN-2017-222 | GEN-2018-081,2019-074 | GEN-2019-011 | GEN-2018-073 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124
18021901 | TC | 5 | 26 | WP | contingency248.sav | 527656-527610 | 5-26W-17 | 3.8889 | GEN-2019-003,2019-021 | GEN-2018-074,GEN-2017-222 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2019-011 | GEN-2018-081,2019-074
18021901 | TC | 5 | 26 | WP | contingency25.sav | 524767-524770-524768 | 5-26W-17 | 3.8791 | GEN-2019-003,2019-021 | GEN-2018-074,GEN-2017-222 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2019-011 | GEN-2018-081,2019-074
18021901 | TC | 5 | 26 | WP | contingency251.sav | 527656-588000 | 5-26W-17 | 3.8809 | GEN-2019-003,2019-021 | GEN-2018-074,GEN-2017-222 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2019-011 | GEN-2018-081,2019-074
18021901 | TC | 5 | 26 | WP | contingency252.sav | 527894-527867 | 5-26W-17 | 3.8799 | GEN-2019-003,2019-021 | GEN-2018-074,GEN-2017-222 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2019-011 | GEN-2018-081,2019-074
18021901 | TC | 5 | 26 | WP | contingency255.sav | 527894-527891-527890 | 5-26W-17 | 3.8759 | GEN-2019-003,2019-021 | GEN-2018-074,GEN-2017-222 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2019-011 | GEN-2018-081,2019-074
18021901 | TC | 5 | 26 | WP | contingency256.sav | 527894-527891-527889 | 5-26W-17 | 3.8731 | GEN-2019-003,2019-021 | GEN-2018-074,GEN-2017-222 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2019-011 | GEN-2018-081,2019-074
18021901 | TC | 5 | 26 | WP | contingency257.sav | 527896-526936 | 5-26W-1 | 3.7129 | GEN-2019-003,2019-021 | GEN-2018-081,2019-074 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2019-011 | GEN-2018-073
18021901 | TC | 5 | 26 | WP | contingency257.sav | 527896-526936 | 5-26W-10 | 3.2097 | GEN-2019-003,2019-021 | GEN-2018-074,GEN-2017-222 | GEN-2018-081,2019-074 | GEN-2019-011 | GEN-2018-073 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124
18021901 | TC | 5 | 26 | WP | contingency257.sav | 527896-526936 | 5-26W-17 | 3.7687 | GEN-2019-003,2019-021 | GEN-2018-074,GEN-2017-222 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2019-011 | GEN-2018-081,2019-074
18021901 | TC | 5 | 26 | WP | contingency258.sav | 527965-527802 | 5-26W-17 | 3.8708 | GEN-2019-003,2019-021 | GEN-2018-074,GEN-2017-222 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2019-011 | GEN-2018-081,2019-074
18021901 | TC | 5 | 26 | WP | contingency26.sav | 524770-761467 | 5-26W-17 | 3.8813 | GEN-2019-003,2019-021 | GEN-2018-074,GEN-2017-222 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2019-011 | GEN-2018-081,2019-074
18021901 | TC | 5 | 26 | WP | contingency260.sav | 527965-527966-527964 | 5-26W-1 | 3.8281 | GEN-2019-003,2019-021 | GEN-2018-081,2019-074 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2019-011 | GEN-2018-073
18021901 | TC | 5 | 26 | WP | contingency260.sav | 527965-527966-527964 | 5-26W-10 | 3.3033 | GEN-2019-003,2019-021 | GEN-2018-074,GEN-2017-222 | GEN-2018-081,2019-074 | GEN-2019-011 | GEN-2018-073 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124
18021901 | TC | 5 | 26 | WP | contingency260.sav | 527965-527966-527964 | 5-26W-17 | 3.8762 | GEN-2019-003,2019-021 | GEN-2018-074,GEN-2017-222 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2019-011 | GEN-2018-081,2019-074
18021901 | TC | 5 | 26 | WP | contingency261.sav | 528027-528015 | 5-26W-17 | 3.8808 | GEN-2019-003,2019-021 | GEN-2018-074,GEN-2017-222 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2019-011 | GEN-2018-081,2019-074
18021901 | TC | 5 | 26 | WP | contingency263.sav | 587570-587571 | 5-26W-1 | 3.8327 | GEN-2019-003,2019-021 | GEN-2018-081,2019-074 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2019-011 | GEN-2018-073
18021901 | TC | 5 | 26 | WP | contingency263.sav | 587570-587571 | 5-26W-10 | 3.3071 | GEN-2019-003,2019-021 | GEN-2018-074,GEN-2017-222 | GEN-2018-081,2019-074 | GEN-2019-011 | GEN-2018-073 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124
18021901 | TC | 5 | 26 | WP | contingency263.sav | 587570-587571 | 5-26W-17 | 3.8809 | GEN-2019-003,2019-021 | GEN-2018-074,GEN-2017-222 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2019-011 | GEN-2018-081,2019-074
18021901 | TC | 5 | 26 | WP | contingency27.sav | 524822-524908 | 5-26W-17 | 3.8751 | GEN-2019-003,2019-021 | GEN-2018-074,GEN-2017-222 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2019-011 | GEN-2018-081,2019-074
18021901 | TC | 5 | 26 | WP | contingency272.sav | 762174-525481 | 5-26W-1 | 3.7591 | GEN-2019-003,2019-021 | GEN-2018-081,2019-074 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2019-011 | GEN-2018-073
18021901 | TC | 5 | 26 | WP | contingency272.sav | 762174-525481 | 5-26W-10 | 3.246 | GEN-2019-003,2019-021 | GEN-2018-074,GEN-2017-222 | GEN-2018-081,2019-074 | GEN-2019-011 | GEN-2018-073 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124
18021901 | TC | 5 | 26 | WP | contingency272.sav | 762174-525481 | 5-26W-17 | 3.8013 | GEN-2019-003,2019-021 | GEN-2018-074,GEN-2017-222 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2019-011 | GEN-2018-081,2019-074
18021901 | TC | 5 | 26 | WP | contingency272.sav | 762174-525481 | 5-26W-17 | 3.7924 | GEN-2019-003,2019-021 | GEN-2018-074,GEN-2017-222 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2019-011 | GEN-2018-081,2019-074
18021901 | TC | 5 | 26 | WP | contingency275.sav | 762174-525531 | 5-26W-17 | 3.7586 | GEN-2019-003,2019-021 | GEN-2018-074,GEN-2017-222 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2019-011 | GEN-2018-081,2019-074
18021901 | TC | 5 | 26 | WP | contingency276.sav | 762216-560022 | 5-26W-1 | 3.0272 | GEN-2019-056 | GEN-2019-003,2019-021 | GEN-2018-074,GEN-2017-222 | GEN-2018-081,2019-074 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2019-011 | GEN-2018-073
18021901 | TC | 5 | 26 | WP | contingency283.sav | 762467-763215 | 5-26W-10 | 3.0088 | GEN-2019-056 | GEN-2019-003,2019-021 | GEN-2018-074,GEN-2017-222 | GEN-2018-081,2019-074 | GEN-2019-011 | GEN-2018-073 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124
18021901 | TC | 5 | 26 | WP | contingency287.sav | 523869-523866(1):523869-523866(2) | 5-26W-1 | 3.0684 | GEN-2019-056 | GEN-2019-003,2019-021 | GEN-2018-074,GEN-2017-222 | GEN-2018-081,2019-074 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2019-011 | GEN-2018-073
18021901 | TC | 5 | 26 | WP | contingency287.sav | 523869-523866(1):523869-523866(2) | 5-26W-16 | 3.5672 | GEN-2019-003,2019-021 | GEN-2018-074,GEN-2017-222 | GEN-2018-081,2019-074 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2019-011 | GEN-2019-056
18021901 | TC | 5 | 26 | WP | contingency287.sav | 523869-523866(1):523869-523866(2) | 5-26W-17 | 3.8809 | GEN-2019-003,2019-021 | GEN-2018-074,GEN-2017-222 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2019-011 | GEN-2018-081,2019-074
18021901 | TC | 5 | 26 | WP | contingency288.sav | 525832-560022(1):525832-560022(2) | 5-26W-1 | 3.4995 | GEN-2019-056 | GEN-2019-003,2019-021 | GEN-2018-074,GEN-2017-222 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2019-011 | GEN-2018-081,2019-074
18021901 | TC | 5 | 26 | WP | contingency289.sav | 526337-526269(1):526337-526269(2) | 5-26W-1 | 3.8186 | GEN-2019-003,2019-021 | GEN-2018-081,2019-074 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2019-011 | GEN-2018-073
18021901 | TC | 5 | 26 | WP | contingency289.sav | 526337-526269(1):526337-526269(2) | 5-26W-10 | 3.2954 | GEN-2019-003,2019-021 | GEN-2018-074,GEN-2017-222 | GEN-2018-081,2019-074 | GEN-2019-011 | GEN-2018-073 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124
18021901 | TC | 5 | 26 | WP | contingency289.sav | 526337-526269(1):526337-526269(2) | 5-26W-17 | 3.8654 | GEN-2019-003,2019-021 | GEN-2018-074,GEN-2017-222 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2019-011 | GEN-2018-081,2019-074
18021901 | TC | 5 | 26 | WP | contingency29.sav | 524874-524924 | 5-26W-1 | 3.8332 | GEN-2019-003,2019-021 | GEN-2018-081,2019-074 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2019-011 | GEN-2018-073
18021901 | TC | 5 | 26 | WP | contingency29.sav | 524874-524924 | 5-26W-10 | 3.3075 | GEN-2019-003,2019-021 | GEN-2018-074,GEN-2017-222 | GEN-2018-081,2019-074 | GEN-2019-011 | GEN-2018-073 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124
18021901 | TC | 5 | 26 | WP | contingency29.sav | 524874-524924 | 5-26W-17 | 3.8814 | GEN-2019-003,2019-021 | GEN-2018-074,GEN-2017-222 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2019-011 | GEN-2018-081,2019-074
18021901 | TC | 5 | 26 | WP | contingency290.sav | 762174-525481(1):762174-525481(2) | 5-26W-1 | 3.0202 | GEN-2019-003,2019-021 | GEN-2018-081,2019-074 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2019-011 | GEN-2018-073
18021901 | TC | 5 | 26 | WP | contingency290.sav | 762174-525481(1):762174-525481(2) | 5-26W-13 | 2.6288 | GEN-2018-074,GEN-2017-222 | GEN-2018-081,2019-074 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2019-011 | GEN-2018-073 | GEN-2019-003,2019-021
18021901 | TC | 5 | 26 | WP | contingency290.sav | 762174-525481(1):762174-525481(2) | 5-26W-17 | 2.9972 | GEN-2019-003,2019-021 | GEN-2018-074,GEN-2017-222 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2019-011 | GEN-2018-081,2019-074
18021901 | TC | 5 | 26 | WP | contingency291.sav | 762174-525531(1):762174-525531(2) | 5-26W-1 | 3.0205 | GEN-2019-003,2019-021 | GEN-2018-081,2019-074 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2019-011 | GEN-2018-073
18021901 | TC | 5 | 26 | WP | contingency291.sav | 762174-525531(1):762174-525531(2) | 5-26W-13 | 2.629 | GEN-2018-074,GEN-2017-222 | GEN-2018-081,2019-074 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2019-011 | GEN-2018-073 | GEN-2019-003,2019-021
18021901 | TC | 5 | 26 | WP | contingency291.sav | 762174-525531(1):762174-525531(2) | 5-26W-17 | 2.9975 | GEN-2019-003,2019-021 | GEN-2018-074,GEN-2017-222 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2019-011 | GEN-2018-081,2019-074
18021901 | TC | 5 | 26 | WP | contingency30.sav | 524875-524885 | 5-26W-1 | 3.7969 | GEN-2019-003,2019-021 | GEN-2018-081,2019-074 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2019-011 | GEN-2018-073
18021901 | TC | 5 | 26 | WP | contingency30.sav | 524875-524885 | 5-26W-10 | 3.2777 | GEN-2019-003,2019-021 | GEN-2018-074,GEN-2017-222 | GEN-2018-081,2019-074 | GEN-2019-011 | GEN-2018-073 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124
18021901 | TC | 5 | 26 | WP | contingency30.sav | 524875-524885 | 5-26W-13 | 3.8424 | GEN-2018-074,GEN-2017-222 | GEN-2018-081,2019-074 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2019-011 | GEN-2019-003,2019-021
18021901 | TC | 5 | 26 | WP | contingency32.sav | 524908-524924 | 5-26W-17 | 3.8815 | GEN-2019-003,2019-021 | GEN-2018-074,GEN-2017-222 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2019-011 | GEN-2018-081,2019-074
18021901 | TC | 5 | 26 | WP | contingency33.sav | 525019-525480 | 5-26W-1 | 3.8266 | GEN-2019-003,2019-021 | GEN-2018-081,2019-074 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2019-011 | GEN-2018-073
18021901 | TC | 5 | 26 | WP | contingency33.sav | 525019-525480 | 5-26W-10 | 3.3018 | GEN-2019-003,2019-021 | GEN-2018-074,GEN-2017-222 | GEN-2018-081,2019-074 | GEN-2019-011 | GEN-2018-073 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124
18021901 | TC | 5 | 26 | WP | contingency34.sav | 525056-525480 | 5-26W-1 | 3.8252 | GEN-2019-003,2019-021 | GEN-2018-081,2019-074 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2019-011 | GEN-2018-073
18021901 | TC | 5 | 26 | WP | contingency34.sav | 525056-525480 | 5-26W-10 | 3.2995 | GEN-2019-003,2019-021 | GEN-2018-074,GEN-2017-222 | GEN-2018-081,2019-074 | GEN-2019-011 | GEN-2018-073 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124
18021901 | TC | 5 | 26 | WP | contingency34.sav | 525056-525480 | 5-26W-17 | 3.871 | GEN-2019-003,2019-021 | GEN-2018-074,GEN-2017-222 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2019-011 | GEN-2018-081,2019-074
18021901 | TC | 5 | 26 | WP | contingency35.sav | 525124-525460 | 5-26W-1 | 3.8323 | GEN-2019-003,2019-021 | GEN-2018-081,2019-074 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2019-011 | GEN-2018-073
18021901 | TC | 5 | 26 | WP | contingency35.sav | 525124-525460 | 5-26W-10 | 3.3023 | GEN-2019-003,2019-021 | GEN-2018-074,GEN-2017-222 | GEN-2018-081,2019-074 | GEN-2019-011 | GEN-2018-073 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124
18021901 | TC | 5 | 26 | WP | contingency36.sav | 525192-525212 | 5-26W-1 | 3.8322 | GEN-2019-003,2019-021 | GEN-2018-081,2019-074 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2019-011 | GEN-2018-073
18021901 | TC | 5 | 26 | WP | contingency36.sav | 525192-525212 | 5-26W-10 | 3.3063 | GEN-2019-003,2019-021 | GEN-2018-074,GEN-2017-222 | GEN-2018-081,2019-074 | GEN-2019-011 | GEN-2018-073 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124
18021901 | TC | 5 | 26 | WP | contingency36.sav | 525192-525212 | 5-26W-17 | 3.88 | GEN-2019-003,2019-021 | GEN-2018-074,GEN-2017-222 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2019-011 | GEN-2018-081,2019-074
18021901 | TC | 5 | 26 | WP | contingency37.sav | 525192-525454 | 5-26W-1 | 3.8316 | GEN-2019-003,2019-021 | GEN-2018-081,2019-074 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2019-011 | GEN-2018-073
18021901 | TC | 5 | 26 | WP | contingency37.sav | 525192-525454 | 5-26W-10 | 3.305 | GEN-2019-003,2019-021 | GEN-2018-074,GEN-2017-222 | GEN-2018-081,2019-074 | GEN-2019-011 | GEN-2018-073 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124
18021901 | TC | 5 | 26 | WP | contingency38.sav | 525192-525460 | 5-26W-17 | 3.8725 | GEN-2019-003,2019-021 | GEN-2018-074,GEN-2017-222 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2019-011 | GEN-2018-081,2019-074
18021901 | TC | 5 | 26 | WP | contingency40.sav | 525213-525830 | 5-26W-1 | 3.8042 | GEN-2019-003,2019-021 | GEN-2018-081,2019-074 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2019-011 | GEN-2018-073
18021901 | TC | 5 | 26 | WP | contingency40.sav | 525213-525830 | 5-26W-10 | 3.2625 | GEN-2019-003,2019-021 | GEN-2018-074,GEN-2017-222 | GEN-2018-081,2019-074 | GEN-2019-011 | GEN-2018-073 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124
18021901 | TC | 5 | 26 | WP | contingency41.sav | 525446-525480 | 5-26W-1 | 3.8229 | GEN-2019-003,2019-021 | GEN-2018-081,2019-074 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2019-011 | GEN-2018-073
18021901 | TC | 5 | 26 | WP | contingency41.sav | 525446-525480 | 5-26W-10 | 3.2974 | GEN-2019-003,2019-021 | GEN-2018-074,GEN-2017-222 | GEN-2018-081,2019-074 | GEN-2019-011 | GEN-2018-073 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124
18021901 | TC | 5 | 26 | WP | contingency41.sav | 525446-525480 | 5-26W-17 | 3.8686 | GEN-2019-003,2019-021 | GEN-2018-074,GEN-2017-222 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2019-011 | GEN-2018-081,2019-074
18021901 | TC | 5 | 26 | WP | contingency42.sav | 525454-525480 | 5-26W-1 | 3.8231 | GEN-2019-003,2019-021 | GEN-2018-081,2019-074 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2019-011 | GEN-2018-073
18021901 | TC | 5 | 26 | WP | contingency42.sav | 525454-525480 | 5-26W-10 | 3.299 | GEN-2019-003,2019-021 | GEN-2018-074,GEN-2017-222 | GEN-2018-081,2019-074 | GEN-2019-011 | GEN-2018-073 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124
18021901 | TC | 5 | 26 | WP | contingency42.sav | 525454-525480 | 5-26W-17 | 3.8711 | GEN-2019-003,2019-021 | GEN-2018-074,GEN-2017-222 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2019-011 | GEN-2018-081,2019-074
18021901 | TC | 5 | 26 | WP | contingency43.sav | 525454-525828 | 5-26W-1 | 3.8251 | GEN-2019-003,2019-021 | GEN-2018-081,2019-074 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2019-011 | GEN-2018-073
18021901 | TC | 5 | 26 | WP | contingency43.sav | 525454-525828 | 5-26W-10 | 3.2992 | GEN-2019-003,2019-021 | GEN-2018-074,GEN-2017-222 | GEN-2018-081,2019-074 | GEN-2019-011 | GEN-2018-073 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124
18021901 | TC | 5 | 26 | WP | contingency43.sav | 525454-525828 | 5-26W-17 | 3.8739 | GEN-2019-003,2019-021 | GEN-2018-074,GEN-2017-222 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2019-011 | GEN-2018-081,2019-074
18021901 | TC | 5 | 26 | WP | contingency44.sav | 525480-525491 | 5-26W-17 | 3.8809 | GEN-2019-003,2019-021 | GEN-2018-074,GEN-2017-222 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2019-011 | GEN-2018-081,2019-074
18021901 | TC | 5 | 26 | WP | contingency45.sav | 525480-525492 | 5-26W-17 | 3.8809 | GEN-2019-003,2019-021 | GEN-2018-074,GEN-2017-222 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2019-011 | GEN-2018-081,2019-074
18021901 | TC | 5 | 26 | WP | contingency46.sav | 525480-525493 | 5-26W-17 | 3.8809 | GEN-2019-003,2019-021 | GEN-2018-074,GEN-2017-222 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2019-011 | GEN-2018-081,2019-074
18021901 | TC | 5 | 26 | WP | contingency48.sav | 525549-527656 | 5-26W-10 | 3.6166 | GEN-2019-003,2019-021 | GEN-2018-074,GEN-2017-222 | GEN-2018-081,2019-074 | GEN-2019-011 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124
18021901 | TC | 5 | 26 | WP | contingency49.sav | 525585-525586 | 5-26W-17 | 3.8809 | GEN-2019-003,2019-021 | GEN-2018-074,GEN-2017-222 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2019-011 | GEN-2018-081,2019-074
18021901 | TC | 5 | 26 | WP | contingency5.sav | 523869-523959 | 5-26W-1 | 3.3063 | GEN-2019-003,2019-021 | GEN-2018-074,GEN-2017-222 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2019-011 | GEN-2018-073 | GEN-2018-081,2019-074
18021901 | TC | 5 | 26 | WP | contingency50.sav | 525586-526935 | 5-26W-1 | 3.7318 | GEN-2019-003,2019-021 | GEN-2018-081,2019-074 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2019-011 | GEN-2018-073
18021901 | TC | 5 | 26 | WP | contingency50.sav | 525586-526935 | 5-26W-10 | 3.7729 | GEN-2019-003,2019-021 | GEN-2018-074,GEN-2017-222 | GEN-2018-081,2019-074 | GEN-2019-011 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124
18021901 | TC | 5 | 26 | WP | contingency50.sav | 525586-526935 | 5-26W-13 | 3.2244 | GEN-2018-074,GEN-2017-222 | GEN-2018-081,2019-074 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2019-011 | GEN-2018-073 | GEN-2019-003,2019-021
18021901 | TC | 5 | 26 | WP | contingency51.sav | 525633-525637-525636 | 5-26W-1 | 3.8094 | GEN-2019-003,2019-021 | GEN-2018-081,2019-074 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2019-011 | GEN-2018-073
18021901 | TC | 5 | 26 | WP | contingency51.sav | 525633-525637-525636 | 5-26W-10 | 3.2879 | GEN-2019-003,2019-021 | GEN-2018-074,GEN-2017-222 | GEN-2018-081,2019-074 | GEN-2019-011 | GEN-2018-073 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124
18021901 | TC | 5 | 26 | WP | contingency53.sav | 525820-525830 | 5-26W-1 | 5.7161 | Bus 1: GEN-2019-003,2019-021; Bus 2: GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124; Bus 3: GEN-2018-081,2019-074
18021901 | TC | 5 | 26 | WP | contingency53.sav | 525820-525830 | 5-26W-12 | 4.6071 | Bus 1: GEN-2019-003,2019-021; Bus 2: GEN-2018-081,2019-074; Bus 3: GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124; Bus 4: GEN-2019-011
18021901 | TC | 5 | 26 | WP | contingency55.sav | 525824-525832-525830 | 5-26W-1 | 5.7082 | Bus 1: GEN-2019-003,2019-021; Bus 2: GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124; Bus 3: GEN-2018-081,2019-074
18021901 | TC | 5 | 26 | WP | contingency55.sav | 525824-525832-525830 | 5-26W-12 | 4.5972 | Bus 1: GEN-2019-003,2019-021; Bus 2: GEN-2018-081,2019-074; Bus 3: GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124; Bus 4: GEN-2019-011
18021901 | TC | 5 | 26 | WP | contingency56.sav | 525825-525832-525830 | 5-26W-1 | 3.8734 | GEN-2019-003,2019-021 | GEN-2018-074,GEN-2017-222 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2019-011 | GEN-2018-081,2019-074
18021901 | TC | 5 | 26 | WP | contingency56.sav | 525825-525832-525830 | 5-26W-12 | 4.5995 | Bus 1: GEN-2019-003,2019-021; Bus 2: GEN-2018-081,2019-074; Bus 3: GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124; Bus 4: GEN-2019-011
18021901 | TC | 5 | 26 | WP | contingency58.sav | 525830-525957 | 5-26W-17 | 3.8832 | GEN-2019-003,2019-021 | GEN-2018-074,GEN-2017-222 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2019-011 | GEN-2018-081,2019-074
18021901 | TC | 5 | 26 | WP | contingency59.sav | 525830-526161 | 5-26W-1 | 3.8198 | GEN-2019-003,2019-021 | GEN-2018-081,2019-074 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2019-011 | GEN-2018-073
18021901 | TC | 5 | 26 | WP | contingency59.sav | 525830-526161 | 5-26W-10 | 3.2963 | GEN-2019-003,2019-021 | GEN-2018-074,GEN-2017-222 | GEN-2018-081,2019-074 | GEN-2019-011 | GEN-2018-073 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124
18021901 | TC | 5 | 26 | WP | contingency59.sav | 525830-526161 | 5-26W-17 | 3.8803 | GEN-2019-003,2019-021 | GEN-2018-074,GEN-2017-222 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2019-011 | GEN-2018-081,2019-074
18021901 | TC | 5 | 26 | WP | contingency6.sav | 523957-523961-523959 | 5-26W-13 | 3.0722 | GEN-2019-056 | GEN-2018-074,GEN-2017-222 | GEN-2018-081,2019-074 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2019-011 | GEN-2018-073 | GEN-2019-003,2019-021
18021901 | TC | 5 | 26 | WP | contingency6.sav | 523957-523961-523959 | 5-26W-16 | 3.5682 | GEN-2019-003,2019-021 | GEN-2018-074,GEN-2017-222 | GEN-2018-081,2019-074 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2019-011 | GEN-2019-056
18021901 | TC | 5 | 26 | WP | contingency60.sav | 525830-526337 | 5-26W-1 | 3.8029 | GEN-2019-003,2019-021 | GEN-2018-081,2019-074 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2019-011 | GEN-2018-073
18021901 | TC | 5 | 26 | WP | contingency60.sav | 525830-526337 | 5-26W-10 | 3.282 | GEN-2019-003,2019-021 | GEN-2018-074,GEN-2017-222 | GEN-2018-081,2019-074 | GEN-2019-011 | GEN-2018-073 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124
18021901 | TC | 5 | 26 | WP | contingency60.sav | 525830-526337 | 5-26W-17 | 3.8688 | GEN-2019-003,2019-021 | GEN-2018-074,GEN-2017-222 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2019-011 | GEN-2018-081,2019-074
18021901 | TC | 5 | 26 | WP | contingency61.sav | 525832-525850 | 5-26W-17 | 3.8809 | GEN-2019-003,2019-021 | GEN-2018-074,GEN-2017-222 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2019-011 | GEN-2018-081,2019-074
18021901 | TC | 5 | 26 | WP | contingency62.sav | 526161-526525 | 5-26W-17 | 3.8808 | GEN-2019-003,2019-021 | GEN-2018-074,GEN-2017-222 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2019-011 | GEN-2018-081,2019-074
18021901 | TC | 5 | 26 | WP | contingency63.sav | 526432-526435-526434 | 5-26W-1 | 3.8308 | GEN-2019-003,2019-021 | GEN-2018-081,2019-074 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2019-011 | GEN-2018-073
18021901 | TC | 5 | 26 | WP | contingency63.sav | 526432-526435-526434 | 5-26W-10 | 3.3055 | GEN-2019-003,2019-021 | GEN-2018-074,GEN-2017-222 | GEN-2018-081,2019-074 | GEN-2019-011 | GEN-2018-073 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124
18021901 | TC | 5 | 26 | WP | contingency63.sav | 526432-526435-526434 | 5-26W-17 | 3.8792 | GEN-2019-003,2019-021 | GEN-2018-074,GEN-2017-222 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2019-011 | GEN-2018-081,2019-074
18021901 | TC | 5 | 26 | WP | contingency64.sav | 526435-526460 | 5-26W-1 | 3.8047 | GEN-2019-003,2019-021 | GEN-2018-081,2019-074 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2019-011 | GEN-2018-073
18021901 | TC | 5 | 26 | WP | contingency64.sav | 526435-526460 | 5-26W-10 | 3.2837 | GEN-2019-003,2019-021 | GEN-2018-074,GEN-2017-222 | GEN-2018-081,2019-074 | GEN-2019-011 | GEN-2018-073 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124
18021901 | TC | 5 | 26 | WP | contingency64.sav | 526435-526460 | 5-26W-17 | 3.8515 | GEN-2019-003,2019-021 | GEN-2018-074,GEN-2017-222 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2019-011 | GEN-2018-081,2019-074
18021901 | TC | 5 | 26 | WP | contingency65.sav | 526435-526525 | 5-26W-1 | 3.7973 | GEN-2019-003,2019-021 | GEN-2018-081,2019-074 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2019-011 | GEN-2018-073
18021901 | TC | 5 | 26 | WP | contingency65.sav | 526435-526525 | 5-26W-10 | 3.2783 | GEN-2019-003,2019-021 | GEN-2018-074,GEN-2017-222 | GEN-2018-081,2019-074 | GEN-2019-011 | GEN-2018-073 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124
18021901 | TC | 5 | 26 | WP | contingency65.sav | 526435-526525 | 5-26W-17 | 3.8507 | GEN-2019-003,2019-021 | GEN-2018-074,GEN-2017-222 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2019-011 | GEN-2018-081,2019-074
18021901 | TC | 5 | 26 | WP | contingency66.sav | 526460-526935 | 5-26W-17 | 3.859 | GEN-2019-003,2019-021 | GEN-2018-074,GEN-2017-222 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2019-011 | GEN-2018-081,2019-074
18021901 | TC | 5 | 26 | WP | contingency67.sav | 526931-526935-526934 | 5-26W-1 | 3.8302 | GEN-2019-003,2019-021 | GEN-2018-081,2019-074 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2019-011 | GEN-2018-073
18021901 | TC | 5 | 26 | WP | contingency67.sav | 526931-526935-526934 | 5-26W-10 | 3.3051 | GEN-2019-003,2019-021 | GEN-2018-074,GEN-2017-222 | GEN-2018-081,2019-074 | GEN-2019-011 | GEN-2018-073 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124
18021901 | TC | 5 | 26 | WP | contingency67.sav | 526931-526935-526934 | 5-26W-17 | 3.8783 | GEN-2019-003,2019-021 | GEN-2018-074,GEN-2017-222 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2019-011 | GEN-2018-081,2019-074
18021901 | TC | 5 | 26 | WP | contingency68.sav | 526932-526935-526934 | 5-26W-1 | 3.8303 | GEN-2019-003,2019-021 | GEN-2018-081,2019-074 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2019-011 | GEN-2018-073
18021901 | TC | 5 | 26 | WP | contingency68.sav | 526932-526935-526934 | 5-26W-10 | 3.3051 | GEN-2019-003,2019-021 | GEN-2018-074,GEN-2017-222 | GEN-2018-081,2019-074 | GEN-2019-011 | GEN-2018-073 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124
18021901 | TC | 5 | 26 | WP | contingency68.sav | 526932-526935-526934 | 5-26W-17 | 3.8783 | GEN-2019-003,2019-021 | GEN-2018-074,GEN-2017-222 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2019-011 | GEN-2018-081,2019-074
18021901 | TC | 5 | 26 | WP | contingency69.sav | 526935-527009 | 5-26W-17 | 3.8667 | GEN-2019-003,2019-021 | GEN-2018-074,GEN-2017-222 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2019-011 | GEN-2018-081,2019-074
18021901 | TC | 5 | 26 | WP | contingency70.sav | 526935-527028 | 5-26W-1 | 3.8247 | GEN-2019-003,2019-021 | GEN-2018-081,2019-074 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2019-011 | GEN-2018-073
18021901 | TC | 5 | 26 | WP | contingency70.sav | 526935-527028 | 5-26W-10 | 3.3005 | GEN-2019-003,2019-021 | GEN-2018-074,GEN-2017-222 | GEN-2018-081,2019-074 | GEN-2019-011 | GEN-2018-073 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124
18021901 | TC | 5 | 26 | WP | contingency70.sav | 526935-527028 | 5-26W-17 | 3.8733 | GEN-2019-003,2019-021 | GEN-2018-074,GEN-2017-222 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2019-011 | GEN-2018-081,2019-074
18021901 | TC | 5 | 26 | WP | contingency71.sav | 526935-527149 | 5-26W-17 | 3.8682 | GEN-2019-003,2019-021 | GEN-2018-074,GEN-2017-222 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2019-011 | GEN-2018-081,2019-074
18021901 | TC | 5 | 26 | WP | contingency72.sav | 527028-527894 | 5-26W-1 | 3.8311 | GEN-2019-003,2019-021 | GEN-2018-081,2019-074 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2019-011 | GEN-2018-073
18021901 | TC | 5 | 26 | WP | contingency72.sav | 527028-527894 | 5-26W-10 | 3.3058 | GEN-2019-003,2019-021 | GEN-2018-074,GEN-2017-222 | GEN-2018-081,2019-074 | GEN-2019-011 | GEN-2018-073 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124
18021901 | TC | 5 | 26 | WP | contingency72.sav | 527028-527894 | 5-26W-17 | 3.8796 | GEN-2019-003,2019-021 | GEN-2018-074,GEN-2017-222 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2019-011 | GEN-2018-081,2019-074
18021901 | TC | 5 | 26 | WP | contingency74.sav | 527656-527896 | 5-26W-17 | 3.8496 | GEN-2019-003,2019-021 | GEN-2018-074,GEN-2017-222 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2019-011 | GEN-2018-081,2019-074
18021901 | TC | 5 | 26 | WP | contingency74.sav | 527656-527896 | 5-26W-17 | 3.8496 | GEN-2019-003,2019-021 | GEN-2018-074,GEN-2017-222 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2019-011 | GEN-2018-081,2019-074
18021901 | TC | 5 | 26 | WP | contingency76.sav | 527896-527965 | 5-26W-17 | 3.8811 | GEN-2019-003,2019-021 | GEN-2018-074,GEN-2017-222 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2019-011 | GEN-2018-081,2019-074
18021901 | TC | 5 | 26 | WP | contingency78.sav | 527896-528027 | 5-26W-17 | 3.8814 | GEN-2019-003,2019-021 | GEN-2018-074,GEN-2017-222 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2019-011 | GEN-2018-081,2019-074
18021901 | TC | 5 | 26 | WP | contingency78.sav | 527896-528027 | 5-26W-17 | 3.8814 | GEN-2019-003,2019-021 | GEN-2018-074,GEN-2017-222 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2019-011 | GEN-2018-081,2019-074
18021901 | TC | 5 | 26 | WP | contingency79.sav | 527965-528027 | 5-26W-17 | 3.8815 | GEN-2019-003,2019-021 | GEN-2018-074,GEN-2017-222 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2019-011 | GEN-2018-081,2019-074
18021901 | TC | 5 | 26 | WP | contingency82.sav | 762216-762467 | 5-26W-14 | 3.0217 | GEN-2019-056 | GEN-2019-003,2019-021 | GEN-2018-074,GEN-2017-222 | GEN-2018-081,2019-074 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2018-073 | GEN-2019-011
18021901 | TC | 5 | 26 | WP | contingency82.sav | 762216-762467 | 5-26W-16 | 3.5465 | GEN-2019-003,2019-021 | GEN-2018-074,GEN-2017-222 | GEN-2018-081,2019-074 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2019-011 | GEN-2019-056
18021901 | TC | 5 | 26 | WP | contingency84.sav | 511456-763215 | 5-26W-1 | 2.29 | GEN-2019-003,2019-021 | GEN-2018-074,GEN-2017-222 | GEN-2018-081,2019-074 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2019-011 | GEN-2018-092 | GEN-2018-073
18021901 | TC | 5 | 26 | WP | contingency84.sav | 511456-763215 | 5-26W-10 | 2.1686 | GEN-2019-056 | GEN-2019-003,2019-021 | GEN-2018-074,GEN-2017-222 | GEN-2018-081,2019-074 | GEN-2019-011 | GEN-2018-073 | GEN-2018-092
18021901 | TC | 5 | 26 | WP | contingency87.sav | 511468-763318 | 5-26W-1 | 3.8808 | GEN-2019-003,2019-021 | GEN-2018-074,GEN-2017-222 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2019-011 | GEN-2018-081,2019-074
18021901 | TC | 5 | 26 | WP | contingency87.sav | 511468-763318 | 5-26W-10 | 3.3071 | GEN-2019-003,2019-021 | GEN-2018-074,GEN-2017-222 | GEN-2018-081,2019-074 | GEN-2019-011 | GEN-2018-073 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124
18021901 | TC | 5 | 26 | WP | contingency87.sav | 511468-763318 | 5-26W-12 | 4.6082 | Bus 1: GEN-2019-003,2019-021; Bus 2: GEN-2018-081,2019-074; Bus 3: GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124; Bus 4: GEN-2019-011
18021901 | TC | 5 | 26 | WP | contingency91.sav | 515375-515407 | 5-26W-17 | 3.88 | GEN-2019-003,2019-021 | GEN-2018-074,GEN-2017-222 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2019-011 | GEN-2018-081,2019-074
18021901 | TC | 5 | 26 | WP | contingency91.sav | 515375-515407 | 5-26W-17 | 3.88 | GEN-2019-003,2019-021 | GEN-2018-074,GEN-2017-222 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2019-011 | GEN-2018-081,2019-074
18021901 | TC | 5 | 26 | WP | contingency94.sav | 515375-515852 | 5-26W-1 | 5.7162 | Bus 1: GEN-2019-003,2019-021; Bus 2: GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124; Bus 3: GEN-2018-081,2019-074
18021901 | TC | 5 | 26 | WP | contingency94.sav | 515375-515852 | 5-26W-10 | 4.6075 | Bus 1: GEN-2019-003,2019-021; Bus 2: GEN-2018-081,2019-074; Bus 3: GEN-2019-011; Bus 4: GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124
18021901 | TC | 5 | 26 | WP | contingency94.sav | 515375-515852 | 5-26W-1 | 5.7162 | Bus 1: GEN-2019-003,2019-021; Bus 2: GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124; Bus 3: GEN-2018-081,2019-074
18021901 | TC | 5 | 26 | WP | contingency94.sav | 515375-515852 | 5-26W-10 | 4.6075 | Bus 1: GEN-2019-003,2019-021; Bus 2: GEN-2018-081,2019-074; Bus 3: GEN-2019-011; Bus 4: GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124
18021901 | TC | 5 | 26 | L | base | N/A | 5-26L-1 | 2.9407 | GEN-2019-003,2019-021 | GEN-2018-074,GEN-2017-222 | GEN-2018-081,2019-074 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2019-011 | GEN-2018-073
18021901 | TC | 5 | 26 | L | base | N/A | 5-26L-10 | 2.7353 | GEN-2019-056 | GEN-2019-003,2019-021 | GEN-2018-074,GEN-2017-222 | GEN-2018-081,2019-074 | GEN-2019-011 | GEN-2018-073 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124
18021901 | TC | 5 | 26 | L | contingency1.sav | 511456-511468 | 5-26L-1 | 1.9365 | GEN-2019-056 | GEN-2019-003,2019-021 | GEN-2018-074,GEN-2017-222 | GEN-2018-081,2019-074 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2019-011 | GEN-2018-092
18021901 | TC | 5 | 26 | L | contingency10.sav | 523978-524365 | 5-26L-16 | 5.3741 | Bus 1: GEN-2019-003,2019-021; Bus 2: GEN-2018-074,GEN-2017-222; Bus 3: GEN-2018-081,2019-074; Bus 4: GEN-2019-056
18021901 | TC | 5 | 26 | L | contingency103.sav | 515458-560022 | 5-26L-1 | 2.0252 | GEN-2019-056 | GEN-2019-003,2019-021 | GEN-2018-074,GEN-2017-222 | GEN-2018-081,2019-074 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2019-011 | GEN-2018-092
18021901 | TC | 5 | 26 | L | contingency103.sav | 515458-560022 | 5-26L-5 | 3.6539 | Bus 1: GEN-2019-011; Bus 2: GEN-2018-073; Bus 3: GEN-2018-092
18021901 | TC | 5 | 26 | L | contingency104.sav | 515458-755000 | 5-26L-1 | 2.0232 | GEN-2019-056 | GEN-2019-003,2019-021 | GEN-2018-074,GEN-2017-222 | GEN-2018-081,2019-074 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2019-011 | GEN-2018-092
18021901 | TC | 5 | 26 | L | contingency104.sav | 515458-755000 | 5-26L-5 | 3.6475 | Bus 1: GEN-2019-011; Bus 2: GEN-2018-073; Bus 3: GEN-2018-092
18021901 | TC | 5 | 26 | L | contingency105.sav | 523323-523309 | 5-26L-16 | 3.7924 | GEN-2019-003,2019-021 | GEN-2018-074,GEN-2017-222 | GEN-2018-081,2019-074 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2019-056
18021901 | TC | 5 | 26 | L | contingency11.sav | 523323-523309 | 5-26L-16 | 5.4467 | Bus 1: GEN-2019-003,2019-021; Bus 2: GEN-2018-074,GEN-2017-222; Bus 3: GEN-2019-056
18021901 | TC | 5 | 26 | L | contingency111.sav | 523961-523097 | 5-26L-1 | 2.7137 | GEN-2019-056 | GEN-2019-003,2019-021 | GEN-2018-074,GEN-2017-222 | GEN-2018-081,2019-074 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2019-011 | GEN-2018-073
18021901 | TC | 5 | 26 | L | contingency111.sav | 523961-523097 | 5-26L-16 | 3.1795 | GEN-2019-003,2019-021 | GEN-2018-074,GEN-2017-222 | GEN-2018-081,2019-074 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2019-011 | GEN-2019-056
18021901 | TC | 5 | 26 | L | contingency112.sav | 523961-524296 | 5-26L-16 | 5.4373 | Bus 1: GEN-2019-003,2019-021; Bus 2: GEN-2018-074,GEN-2017-222; Bus 3: GEN-2018-081,2019-074; Bus 4: GEN-2019-056
18021901 | TC | 5 | 26 | L | contingency119.sav | 524162-524058 | 5-26L-16 | 5.5432 | Bus 1: GEN-2019-003,2019-021; Bus 2: GEN-2018-074,GEN-2017-222; Bus 3: GEN-2019-056
18021901 | TC | 5 | 26 | L | contingency12.sav | 524267-524623 | 5-26L-13 | 2.6842 | GEN-2019-056 | GEN-2018-074,GEN-2017-222 | GEN-2018-081,2019-074 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2019-011 | GEN-2018-073 | GEN-2019-003,2019-021
18021901 | TC | 5 | 26 | L | contingency125.sav | 524224-524364 | 5-26L-16 | 5.4465 | Bus 1: GEN-2019-003,2019-021; Bus 2: GEN-2018-074,GEN-2017-222; Bus 3: GEN-2019-056
18021901 | TC | 5 | 26 | L | contingency126.sav | 524267-524290 | 5-26L-16 | 5.5881 | Bus 1: GEN-2019-003,2019-021; Bus 2: GEN-2018-074,GEN-2017-222; Bus 3: GEN-2019-056
18021901 | TC | 5 | 26 | L | contingency129.sav | 524322-524364 | 5-26L-16 | 5.467 | Bus 1: GEN-2019-003,2019-021; Bus 2: GEN-2018-074,GEN-2017-222; Bus 3: GEN-2019-056
18021901 | TC | 5 | 26 | L | contingency131.sav | 524338-524364 | 5-26L-16 | 5.5766 | Bus 1: GEN-2019-003,2019-021; Bus 2: GEN-2018-074,GEN-2017-222; Bus 3: GEN-2019-056
18021901 | TC | 5 | 26 | L | contingency136.sav | 524415-524044 | 5-26L-16 | 5.5452 | Bus 1: GEN-2019-003,2019-021; Bus 2: GEN-2018-074,GEN-2017-222; Bus 3: GEN-2019-056
18021901 | TC | 5 | 26 | L | contingency137.sav | 524415-524414-24410 | 5-26L-16 | 5.5583 | Bus 1: GEN-2019-003,2019-021; Bus 2: GEN-2018-074,GEN-2017-222; Bus 3: GEN-2019-056
18021901 | TC | 5 | 26 | L | contingency138.sav | 524520-524516 | 5-26L-13 | 2.7237 | GEN-2019-056 | GEN-2018-074,GEN-2017-222 | GEN-2018-081,2019-074 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2019-011 | GEN-2018-073 | GEN-2019-003,2019-021
18021901 | TC | 5 | 26 | L | contingency139.sav | 524522-524364 | 5-26L-13 | 2.724 | GEN-2019-056 | GEN-2018-074,GEN-2017-222 | GEN-2018-081,2019-074 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2019-011 | GEN-2018-073 | GEN-2019-003,2019-021
18021901 | TC | 5 | 26 | L | contingency143.sav | 524746-524694 | 5-26L-16 | 5.5761 | Bus 1: GEN-2019-003,2019-021; Bus 2: GEN-2018-074,GEN-2017-222; Bus 3: GEN-2019-056
18021901 | TC | 5 | 26 | L | contingency145.sav | 524746-524757 | 5-26L-16 | 5.5769 | Bus 1: GEN-2019-003,2019-021; Bus 2: GEN-2018-074,GEN-2017-222; Bus 3: GEN-2019-056
18021901 | TC | 5 | 26 | L | contingency149.sav | 524768-524502 | 5-26L-16 | 5.5967 | Bus 1: GEN-2019-003,2019-021; Bus 2: GEN-2018-074,GEN-2017-222; Bus 3: GEN-2019-056
18021901 | TC | 5 | 26 | L | contingency18.sav | 524415-525213 | 5-26L-13 | 2.7007 | GEN-2019-056 | GEN-2018-074,GEN-2017-222 | GEN-2018-081,2019-074 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2019-011 | GEN-2018-073 | GEN-2019-003,2019-021
18021901 | TC | 5 | 26 | L | contingency181.sav | 525213-525461 | 5-26L-4 | 3.1568 | GEN-2019-056 | GEN-2019-003,2019-021 | GEN-2018-081,2019-074 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2019-011 | GEN-2018-074,GEN-2017-222
18021901 | TC | 5 | 26 | L | contingency19.sav | 524520-524522 | 5-26L-13 | 2.7237 | GEN-2019-056 | GEN-2018-074,GEN-2017-222 | GEN-2018-081,2019-074 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2019-011 | GEN-2018-073 | GEN-2019-003,2019-021
18021901 | TC | 5 | 26 | L | contingency191.sav | 525494-525481 | 5-26L-16 | 4.9244 | Bus 1: GEN-2019-003,2019-021; Bus 2: GEN-2018-074,GEN-2017-222; Bus 3: GEN-2018-081,2019-074; Bus 4: GEN-2019-056
18021901 | TC | 5 | 26 | L | contingency205.sav | 525828-525816-525814 | 5-26L-16 | 5.577 | Bus 1: GEN-2019-003,2019-021; Bus 2: GEN-2018-074,GEN-2017-222; Bus 3: GEN-2019-056
18021901 | TC | 5 | 26 | L | contingency208.sav | 525830-525531 | 5-26L-16 | 5.3906 | Bus 1: GEN-2019-003,2019-021; Bus 2: GEN-2018-074,GEN-2017-222; Bus 3: GEN-2018-081,2019-074; Bus 4: GEN-2019-056
18021901 | TC | 5 | 26 | L | contingency209.sav | 525832-526936 | 5-26L-16 | 3.1605 | GEN-2019-003,2019-021 | GEN-2018-074,GEN-2017-222 | GEN-2018-081,2019-074 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2019-011 | GEN-2019-056
18021901 | TC | 5 | 26 | L | contingency218.sav | 525957-525931-525930 | 5-26L-16 | 5.5759 | Bus 1: GEN-2019-003,2019-021; Bus 2: GEN-2018-074,GEN-2017-222; Bus 3: GEN-2019-056
18021901 | TC | 5 | 26 | L | contingency219.sav | 525957-525981-525980 | 5-26L-16 | 5.575 | Bus 1: GEN-2019-003,2019-021; Bus 2: GEN-2018-074,GEN-2017-222; Bus 3: GEN-2019-056
18021901 | TC | 5 | 26 | L | contingency220.sav | 525957-525990-525989 | 5-26L-16 | 5.5738 | Bus 1: GEN-2019-003,2019-021; Bus 2: GEN-2018-074,GEN-2017-222; Bus 3: GEN-2019-056
18021901 | TC | 5 | 26 | L | contingency23.sav | 524623-760498 | 5-26L-13 | 2.6945 | GEN-2019-056 | GEN-2018-074,GEN-2017-222 | GEN-2018-081,2019-074 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2019-011 | GEN-2018-073 | GEN-2019-003,2019-021
18021901 | TC | 5 | 26 | L | contingency245.sav | 527149-527163 | 5-26L-16 | 5.5563 | Bus 1: GEN-2019-003,2019-021; Bus 2: GEN-2018-074,GEN-2017-222; Bus 3: GEN-2019-056
18021901 | TC | 5 | 26 | L | contingency249.sav | 527656-527655 | 5-26L-16 | 5.5456 | Bus 1: GEN-2019-003,2019-021; Bus 2: GEN-2018-074,GEN-2017-222; Bus 3: GEN-2019-056
18021901 | TC | 5 | 26 | L | contingency253.sav | 527894-527903 | 5-26L-16 | 5.5346 | Bus 1: GEN-2019-003,2019-021; Bus 2: GEN-2018-074,GEN-2017-222; Bus 3: GEN-2019-056
18021901 | TC | 5 | 26 | L | contingency257.sav | 527896-526936 | 5-26L-16 | 5.5673 | Bus 1: GEN-2019-003,2019-021; Bus 2: GEN-2018-074,GEN-2017-222; Bus 3: GEN-2019-056
18021901 | TC | 5 | 26 | L | contingency264.sav | 588760-588761 | 5-26L-16 | 5.5762 | Bus 1: GEN-2019-003,2019-021; Bus 2: GEN-2018-074,GEN-2017-222; Bus 3: GEN-2019-056
18021901 | TC | 5 | 26 | L | contingency265.sav | 588760-588765 | 5-26L-16 | 5.5762 | Bus 1: GEN-2019-003,2019-021; Bus 2: GEN-2018-074,GEN-2017-222; Bus 3: GEN-2019-056
18021901 | TC | 5 | 26 | L | contingency266.sav | 760494-760495 | 5-26L-16 | 5.429 | Bus 1: GEN-2019-003,2019-021; Bus 2: GEN-2018-074,GEN-2017-222; Bus 3: GEN-2018-081,2019-074; Bus 4: GEN-2019-056
18021901 | TC | 5 | 26 | L | contingency267.sav | 760498-525481 | 5-26L-13 | 2.6948 | GEN-2019-056 | GEN-2018-074,GEN-2017-222 | GEN-2018-081,2019-074 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2019-011 | GEN-2018-073 | GEN-2019-003,2019-021
18021901 | TC | 5 | 26 | L | contingency268.sav | 762133-762132 | 5-26L-16 | 5.5726 | Bus 1: GEN-2019-003,2019-021; Bus 2: GEN-2018-074,GEN-2017-222; Bus 3: GEN-2019-056
18021901 | TC | 5 | 26 | L | contingency269.sav | 762133-762134 | 5-26L-16 | 5.5726 | Bus 1: GEN-2019-003,2019-021; Bus 2: GEN-2018-074,GEN-2017-222; Bus 3: GEN-2019-056
18021901 | TC | 5 | 26 | L | contingency270.sav | 762136-762132 | 5-26L-16 | 5.5726 | Bus 1: GEN-2019-003,2019-021; Bus 2: GEN-2018-074,GEN-2017-222; Bus 3: GEN-2019-056
18021901 | TC | 5 | 26 | L | contingency271.sav | 762136-762137 | 5-26L-16 | 5.5726 | Bus 1: GEN-2019-003,2019-021; Bus 2: GEN-2018-074,GEN-2017-222; Bus 3: GEN-2019-056
18021901 | TC | 5 | 26 | L | contingency276.sav | 762216-560022 | 5-26L-1 | 2.6597 | GEN-2019-056 | GEN-2019-003,2019-021 | GEN-2018-074,GEN-2017-222 | GEN-2018-081,2019-074 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2019-011 | GEN-2018-073
18021901 | TC | 5 | 26 | L | contingency283.sav | 762467-763215 | 5-26L-1 | 2.6469 | GEN-2019-056 | GEN-2019-003,2019-021 | GEN-2018-074,GEN-2017-222 | GEN-2018-081,2019-074 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2019-011 | GEN-2018-073
18021901 | TC | 5 | 26 | L | contingency284.sav | 515375-515407(1):515375-515407(2) | 5-26L-16 | 5.4077 | Bus 1: GEN-2019-003,2019-021; Bus 2: GEN-2018-074,GEN-2017-222; Bus 3: GEN-2018-081,2019-074; Bus 4: GEN-2019-056
18021901 | TC | 5 | 26 | L | contingency285.sav | 515375-515852(1):515375-515852(2) | 5-26L-16 | 3.7903 | GEN-2019-003,2019-021 | GEN-2018-074,GEN-2017-222 | GEN-2018-081,2019-074 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2019-056
18021901 | TC | 5 | 26 | L | contingency286.sav | 515375-560071(1):515375-560071(2) | 5-26L-1 | 4.7799 | Bus 1: GEN-2018-092; Bus 2: GEN-2018-073
18021901 | TC | 5 | 26 | L | contingency286.sav | 515375-560071(1):515375-560071(2) | 5-26L-10 | 3.3272 | Bus 1: GEN-2019-003,2019-021; Bus 2: GEN-2018-081,2019-074; Bus 3: GEN-2018-092; Bus 4: GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124
18021901 | TC | 5 | 26 | L | contingency286.sav | 515375-560071(1):515375-560071(2) | 5-26L-13 | 2.8521 | GEN-2018-081,2019-074 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2019-011 | GEN-2018-092 | GEN-2019-003,2019-021
18021901 | TC | 5 | 26 | L | contingency286.sav | 515375-560071(1):515375-560071(2) | 5-26L-16 | 4.8568 | Bus 1: GEN-2018-092; Bus 2: GEN-2019-056
18021901 | TC | 5 | 26 | L | contingency286.sav | 515375-560071(1):515375-560071(2) | 5-26L-4 | 4.4596 | Bus 1: GEN-2018-092; Bus 2: GEN-2018-074,GEN-2017-222
18021901 | TC | 5 | 26 | L | contingency288.sav | 525832-560022(1):525832-560022(2) | 5-26L-1 | 2.4308 | Bus 1: GEN-2018-092; Bus 2: GEN-2018-073
18021901 | TC | 5 | 26 | L | contingency288.sav | 525832-560022(1):525832-560022(2) | 5-26L-10 | 3.0562 | GEN-2019-056 | GEN-2019-003,2019-021 | GEN-2018-074,GEN-2017-222 | GEN-2018-081,2019-074 | GEN-2019-011 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124
18021901 | TC | 5 | 26 | L | contingency290.sav | 762174-525481(1):762174-525481(2) | 5-26L-13 | 2.2512 | GEN-2019-056 | GEN-2018-074,GEN-2017-222 | GEN-2018-081,2019-074 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2019-011 | GEN-2018-073 | GEN-2019-003,2019-021
18021901 | TC | 5 | 26 | L | contingency290.sav | 762174-525481(1):762174-525481(2) | 5-26L-16 | 5.6681 | Bus 1: GEN-2018-074,GEN-2017-222; Bus 2: GEN-2018-081,2019-074; Bus 3: GEN-2019-056
18021901 | TC | 5 | 26 | L | contingency290.sav | 762174-525481(1):762174-525481(2) | 5-26L-4 | 2.5847 | GEN-2019-056 | GEN-2019-003,2019-021 | GEN-2018-081,2019-074 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2019-011 | GEN-2018-074,GEN-2017-222
18021901 | TC | 5 | 26 | L | contingency291.sav | 762174-525531(1):762174-525531(2) | 5-26L-13 | 2.2519 | GEN-2019-056 | GEN-2018-074,GEN-2017-222 | GEN-2018-081,2019-074 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2019-011 | GEN-2018-073 | GEN-2019-003,2019-021
18021901 | TC | 5 | 26 | L | contingency291.sav | 762174-525531(1):762174-525531(2) | 5-26L-16 | 5.6681 | Bus 1: GEN-2018-074,GEN-2017-222; Bus 2: GEN-2018-081,2019-074; Bus 3: GEN-2019-056
18021901 | TC | 5 | 26 | L | contingency291.sav | 762174-525531(1):762174-525531(2) | 5-26L-4 | 2.5855 | GEN-2019-056 | GEN-2019-003,2019-021 | GEN-2018-081,2019-074 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2019-011 | GEN-2018-074,GEN-2017-222
18021901 | TC | 5 | 26 | L | contingency3.sav | 511456-588760 | 5-26L-16 | 5.5751 | Bus 1: GEN-2019-003,2019-021; Bus 2: GEN-2018-074,GEN-2017-222; Bus 3: GEN-2019-056
18021901 | TC | 5 | 26 | L | contingency4.sav | 523323-523959 | 5-26L-16 | 5.4156 | Bus 1: GEN-2019-003,2019-021; Bus 2: GEN-2018-074,GEN-2017-222; Bus 3: GEN-2018-081,2019-074; Bus 4: GEN-2019-056
18021901 | TC | 5 | 26 | L | contingency40.sav | 525213-525830 | 5-26L-4 | 3.1828 | GEN-2019-056 | GEN-2019-003,2019-021 | GEN-2018-081,2019-074 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2019-011 | GEN-2018-074,GEN-2017-222
18021901 | TC | 5 | 26 | L | contingency48.sav | 525549-527656 | 5-26L-13 | 2.6013 | GEN-2019-056 | GEN-2018-074,GEN-2017-222 | GEN-2018-081,2019-074 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2019-011 | GEN-2018-073 | GEN-2019-003,2019-021
18021901 | TC | 5 | 26 | L | contingency55.sav | 525824-525832-525830 | 5-26L-16 | 5.5539 | Bus 1: GEN-2019-003,2019-021; Bus 2: GEN-2018-074,GEN-2017-222; Bus 3: GEN-2019-056
18021901 | TC | 5 | 26 | L | contingency56.sav | 525825-525832-525830 | 5-26L-16 | 5.5611 | Bus 1: GEN-2019-003,2019-021; Bus 2: GEN-2018-074,GEN-2017-222; Bus 3: GEN-2019-056
18021901 | TC | 5 | 26 | L | contingency58.sav | 525830-525957 | 5-26L-16 | 5.427 | Bus 1: GEN-2019-003,2019-021; Bus 2: GEN-2018-074,GEN-2017-222; Bus 3: GEN-2018-081,2019-074; Bus 4: GEN-2019-056
18021901 | TC | 5 | 26 | L | contingency6.sav | 523957-523961-523959 | 5-26L-1 | 2.7161 | GEN-2019-056 | GEN-2019-003,2019-021 | GEN-2018-074,GEN-2017-222 | GEN-2018-081,2019-074 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2019-011 | GEN-2018-073
18021901 | TC | 5 | 26 | L | contingency6.sav | 523957-523961-523959 | 5-26L-16 | 3.1825 | GEN-2019-003,2019-021 | GEN-2018-074,GEN-2017-222 | GEN-2018-081,2019-074 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2019-011 | GEN-2019-056
18021901 | TC | 5 | 26 | L | contingency65.sav | 526435-526525 | 5-26L-16 | 5.5651 | Bus 1: GEN-2019-003,2019-021; Bus 2: GEN-2018-074,GEN-2017-222; Bus 3: GEN-2019-056
18021901 | TC | 5 | 26 | L | contingency80.sav | 760494-760498 | 5-26L-16 | 5.4296 | Bus 1: GEN-2019-003,2019-021; Bus 2: GEN-2018-074,GEN-2017-222; Bus 3: GEN-2018-081,2019-074; Bus 4: GEN-2019-056
18021901 | TC | 5 | 26 | L | contingency81.sav | 762216-762217 | 5-26L-16 | 5.5684 | Bus 1: GEN-2019-003,2019-021; Bus 2: GEN-2018-074,GEN-2017-222; Bus 3: GEN-2019-056
18021901 | TC | 5 | 26 | L | contingency82.sav | 762216-762467 | 5-26L-1 | 2.6556 | GEN-2019-056 | GEN-2019-003,2019-021 | GEN-2018-074,GEN-2017-222 | GEN-2018-081,2019-074 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2019-011 | GEN-2018-073
18021901 | TC | 5 | 26 | L | contingency84.sav | 511456-763215 | 5-26L-1 | 1.9378 | GEN-2019-056 | GEN-2019-003,2019-021 | GEN-2018-074,GEN-2017-222 | GEN-2018-081,2019-074 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2019-011 | GEN-2018-092
18021901 | TC | 5 | 26 | L | contingency86.sav | 511468-760938 | 5-26L-16 | 5.4205 | Bus 1: GEN-2019-003,2019-021; Bus 2: GEN-2018-074,GEN-2017-222; Bus 3: GEN-2018-081,2019-074; Bus 4: GEN-2019-056
18021901 | TC | 5 | 26 | L | contingency9.sav | 523959-524267 | 5-26L-16 | 5.558 | Bus 1: GEN-2019-003,2019-021; Bus 2: GEN-2018-074,GEN-2017-222; Bus 3: GEN-2019-056
18021901 | TC | 5 | 26 | L | contingency90.sav | 515375-515407 | 5-26L-16 | 5.5722 | Bus 1: GEN-2019-003,2019-021; Bus 2: GEN-2018-074,GEN-2017-222; Bus 3: GEN-2019-056
18021901 | TC | 5 | 26 | L | contingency91.sav | 515375-515407 | 5-26L-16 | 5.5721 | Bus 1: GEN-2019-003,2019-021; Bus 2: GEN-2018-074,GEN-2017-222; Bus 3: GEN-2019-056
18021901 | TC | 5 | 26 | L | contingency93.sav | 515375-515852 | 5-26L-16 | 5.5738 | Bus 1: GEN-2019-003,2019-021; Bus 2: GEN-2018-074,GEN-2017-222; Bus 3: GEN-2019-056
18021901 | TC | 5 | 26 | L | contingency94.sav | 515375-515852 | 5-26L-16 | 5.5738 | Bus 1: GEN-2019-003,2019-021; Bus 2: GEN-2018-074,GEN-2017-222; Bus 3: GEN-2019-056
18021901 | TC | 5 | 26 | L | contingency96.sav | 515375-560071 | 5-26L-16 | 5.5599 | Bus 1: GEN-2019-003,2019-021; Bus 2: GEN-2018-074,GEN-2017-222; Bus 3: GEN-2019-056
18021901 | TC | 5 | 26 | L | contingency97.sav | 515375-560071 | 5-26L-16 | 5.5599 | Bus 1: GEN-2019-003,2019-021; Bus 2: GEN-2018-074,GEN-2017-222; Bus 3: GEN-2019-056
18021901 | TC | 5 | 26 | L | contingency98.sav | 515375-562024 | 5-26L-16 | 5.5775 | Bus 1: GEN-2019-003,2019-021; Bus 2: GEN-2018-074,GEN-2017-222; Bus 3: GEN-2019-056
18021901 | TC | 5 | 26 | L | contingency99.sav | 515375-755000 | 5-26L-16 | 3.7896 | GEN-2019-003,2019-021 | GEN-2018-074,GEN-2017-222 | GEN-2018-081,2019-074 | GEN-2017-158,2018-097,2018-099,2018-111,2018-112,2018-124 | GEN-2019-056
18021901 | TC | 3 | 26 | L | contingency14.sav | 530582-539679 | 3-26L-1 | 3.5117 | Bus 1: GEN-2019-054,GEN-2019-068; Bus 2: GEN-2018-116,GEN-2019-051
18021901 | TC | 3 | 26 | L | contingency155.sav | 530582-530584 | 3-26L-1 | 3.835 | Bus 1: GEN-2019-054,GEN-2019-068; Bus 2: GEN-2018-116,GEN-2019-051
18021901 | TC | 3 | 26 | L | contingency197.sav | 532871-763862 | 3-26L-1 | 3.4148 | Bus 1: GEN-2019-054,GEN-2019-068; Bus 2: GEN-2018-116,GEN-2019-051
18021901 | TC | 3 | 26 | L | contingency264.sav | 539679-763850 | 3-26L-1 | 3.8053 | Bus 1: GEN-2019-054,GEN-2019-068; Bus 2: GEN-2018-116,GEN-2019-051
18021901 | TC | 3 | 26 | L | contingency270.sav | 539695-763850 | 3-26L-1 | 2.213 | Bus 1: GEN-2019-053,GEN-2019-055; Bus 2: GEN-2019-054,GEN-2019-068; Bus 3: GEN-2018-116,GEN-2019-051