## Executive Summary
Executive Summary: DISIS-2018-002 and DISIS-2019-001 Phase 2 of Power Flow, Stability, and Short-Circuit
Pursuant to the Southwest Power Pool (SPP) Open Access Transmission Tariff (OATT), SPP has conducted this Definitive Interconnection System Impact Study (DISIS) for generation interconnection requests received during the DISIS Queue Cluster Window which closed on 11/16/22. The primary objective of this DISIS is to identify the system constraints, transient instabilities, and over-dutied equipment associated with connecting the generation to the area transmission system. The Impact Study and other subsequent Interconnection Studies are designed to identify required Transmission Owner Interconnection Facilities, Network Upgrades and other Direct Assignment Facilities needed to inject power into the grid at each specific point of interconnection. The study analysis for the generation interconnection requests included in this DISIS are displayed in this workbook. This workbook provides a convenient method to sort and analyze required study data. The DISIS Manual Version 2.0 posted on http://opsportal.spp.org/Studies/Gen contains details about the DISIS process, methodology, definitions, and useful links. Please review the DISIS Manual or contact gistudies@spp.org for more information about the study process. DISIS-2018-002 Phase 2 includes study requests in the following cluster groups: ( 01 - North, 02 - Nebraska, 03 - Central, 04 - Southeast, 05 - Southwest ) NOTE: per SPP Tariff Attachment V; section 8.4.2 DISIS Phase Two will consist of a power flow analysis, a stability analysis, and a short-circuit analysis.
DISIS Manual Version 2.0
https://opsportal.spp.org/documents/studies/DISIS%20Manual.pdf
This DISIS analyzes the impact of interconnecting new generation for total of:
10,463.54 MW
The minimum cost of interconnecting all requests included in this DISIS is estimated at:
Total Network Upgrade $1,875,887,008.07 Steady State Network Upgrade $1,421,466,955.46 Stability Network Upgrade $35,236,210.00 Interconnection Costs: $419,183,842.61
Models Used in Steady State Study
2021 ITP Series
Winter: 2026
Summer: 2023, 2026
Light: 2026
Models Used in Stability Study
2020 MDWG
Winter: 2025, Summer: 2025
By: SPP Generator Interconnection Department
Published: 9/22/2023
Costs for Solar/Battery Requests were allocated using the 26SP (summer peak) model.
Costs for Wind Requests were allocated using the 26L (light load) model.
Assigned Upgrade Costs include the new cumulative impact criteria from BP7250.

## Revision History
Revision History
Date | Author | Change Description
4515200% | SPP | Phase 2 Draft Posting
4516100% | SPP | Phase 2 Final Posting
4518300% | SPP | Phase 2 Final RePosting
4519100% | SPP | Phase 2 Final RePosting

## Revision Details
Revision Date | Update Type | Tab Order | Results Data Tab | Update Details
4515400% |  | 7 | Upgrade Summary | Changed the study type for "Build G19-029-TAP to Keystone Second Line_345 kV" and "Build Keystone to Gentleman Second Line_345 kV" from "Steady State" to "Steady State/ Stability".
4515500% |  | 6 | Assigned Upgrade Costs | Fixed the group naming inconsistency.
4515500% |  | 7 | Upgrade Summary | Fixed an extrapolation error for the Assigned Upgrade Number.
4515500% |  | 7 | Upgrade Summary | Fixed misquotation of "SVC" to "STATCOM" at Sweet Water 345 kV Substation
4515500% |  | 5 | Constraints Summary | Added Stability Results to the tab
4515500% |  | 1 | Executive Summary | Updated total interconnection costs
4515500% |  | 7 | Upgrade Summary | Updated all interconnection costs from phase 1 to phase 2
4515500% |  | 6 | Assigned Upgrade Costs | Updated all interconnection costs from phase 1 to phase 2
4515900% |  | 5 | Constraints Summary | Updated 01ALL and 02ALL constraints to reflect all upgrades
4515900% |  | 12 | SCRCCT | Correcting error with a wrong generator request associated with the correct POI.
4516000% |  | 7 | Upgrade Summary | Updated all interconnection costs for SPS
4516000% |  | 6 | Assigned Upgrade Costs | Updated all interconnection costs for SPS
4516000% |  | 5/6/7 | Constraints Summary/ Assigned Upgrade Cost/ Upgrade Summary | Updated Upgrade Name/Details/Cost for Wolfforth to Terry County 115 kV
4516000% |  | 6/7 | Assigned Upgrade Cost/ Upgrade Summary | Updated Upgrade Details/Cost for Crawfish - Seminole 765 kV
4516000% |  | 10 | Stability Analysis Results | Updated stability analysis results, violations summary, and mitigations
4516100% |  | 1/6 | Executive Summary/Assigned Upgrade Cost | Corrected interconnection cost for requests sharing gentie w/PQ request
4516100% |  | 1 | Executive Summary | Corrected MW of generation analyzed to match Requests tab
4518300% |  | 5/6/7 | Constraints Summary/ Assigned Upgrade Cost/ Upgrade Summary | Updated Upgrade Name/Details/Cost for multiple network upgrades
4518300% |  | 8 | All Thermal | Updated thermal results for Group 4 and Group 5
4518300% |  | 10 | Stability Analysis Results | Updated stability analysis results, violations summary, and mitigations for Group 5
4518300% |  | 5 | Constraints Summary | Updated one typo for Group 1
4518300% |  | 6 | Assigned Upgrade Costs | Updated small cost allocation for groups 1 and 2 to handle rounding errors from formulas
4518300% |  | 1 | Executive Summary | Updated total interconnection costs
4518300% |  | 12 | SCRCCT | Identified and fixed issues with CCT threshold evaluation
4518300% |  | 13 | WSCR | Added group which was inadvertently left off
4518700% |  | 5/6/7/8 | Constraints Summary/ Assigned Upgrade Cost/ Upgrade Summary/All Thermal | Removed Upgrade/Lawton Eastside 345/230 kV Third Transformer Build
4518800% |  | 4/5/6 | Requests/ Constraints Summary/ Assigned Upgrade Cost | Added costs for GEN-2019-004 and updated assigned costs for Group 5 requests
4518800% |  | 12 | SCRCCT | Corrected processing error resulting in three additional requests failing CCT

## Requests
Gen Number | Group | Queue Order | Queue | Fuel Type | MW Amount | LOIS Amount | Limiting Element | Reactive Compensation Requirements (MVAR) | Service | Area | POI | Status
GEN-2018-067 | 01 - North | 21 | DIS-18-2 | Wind | 255 | 0 | Non-Convergence | -10.73 | ER | BEPC | 115kV Strandahl sub | DISIS STAGE
GEN-2018-069 | 01 - North | 21 | DIS-18-2 | Wind | 125 | 0 | Voltage | -1.12 | ER/NR | WAPA | WAPA-UGP Mingusville 230kV | DISIS STAGE
GEN-2018-070 | 01 - North | 21 | DIS-18-2 | Wind | 18.31 | 0 | Voltage | 0 | ER/NR | WAPA | Utica Junction 230 kV substation | DISIS STAGE
GEN-2018-065 | 02 - Nebraska | 21 | DIS-18-2 | Wind | 19.8 | 0 | Non-Convergence | -0.41 | ER/NR | NPPD | Antelope 345 kV Substation | DISIS STAGE
GEN-2018-068 | 02 - Nebraska | 21 | DIS-18-2 | Wind | 302.4 | 0 | Non-Convergence | -5.82 | ER/NR | NPPD | Antelope 345 kV Substation | DISIS STAGE
GEN-2018-083 | 02 - Nebraska | 21 | DIS-18-2 | Wind | 250 | 0 | Non-Convergence | -13.6 | ER | NPPD | Shell Creek-Hoskins 345kv Line Break | DISIS STAGE
GEN-2018-090 | 02 - Nebraska | 21 | DIS-18-2 | Battery | 125 | 0 | Non-Convergence | -6.4 | ER | OPPD | Raun-Fort Calhoun 345kV Line | DISIS STAGE
GEN-2018-125 | 02 - Nebraska | 21 | DIS-18-2 | Wind | 231 | 0 | Non-Convergence | -2.05 | ER/NR | NPPD | New switching station on Gentleman to Sweetwater 345kV line | DISIS STAGE
GEN-2018-131 | 02 - Nebraska | 21 | DIS-18-2 | Solar | 221.4 | 0 | Non-Convergence | -1.9 | ER/NR | NPPD | Antelope 345kV Substation | DISIS STAGE
GEN-2018-132 | 02 - Nebraska | 21 | DIS-18-2 | Solar | 201.6 | 0 | Non-Convergence | -3.18 | ER/NR | NPPD | Antelope 345kV Substation | DISIS STAGE
GEN-2019-009 | 02 - Nebraska | 22 | DIS-19-1 | Solar | 100 | 100 | None | -1.13 | ER | OPPD | S1263 Brock 161kV substation | DISIS STAGE
GEN-2019-001 | 03 - Central | 22 | DIS-19-1 | Wind | 25 | 0 | 532791 BENTON 7 345 532796 WICHITA7 345 1 | -0.088 | ER | WERE | Thistle-Wichita Dbl Ckt (Buffalo Flats) 345kV | DISIS STAGE
GEN-2019-014 | 03 - Central | 22 | DIS-19-1 | Solar/Battery | 125 | 0 | Voltage: P42:345:SPS:CARPENTER:OR335:SLG:EHV: | -0.442 | ER/NR | SUNC | Holcomb 115kV substation | DISIS STAGE
GEN-2019-016 | 03 - Central | 22 | DIS-19-1 | Solar | 200 | 200 | None | -5.716 | ER | EMDE | Dadeville 161kV Substation | DISIS STAGE
GEN-2019-018 | 03 - Central | 22 | DIS-19-1 | Thermal | 15.56 | 15.56 | None | N/A | ER/NR | MIDW | Saxman 115kV substation | DISIS STAGE
GEN-2019-030 | 03 - Central | 22 | DIS-19-1 | Wind | 252 | 0 | Voltage: P42:345:SPS:CARPENTER:OR335:SLG:EHV: | -12.56 | ER/NR | SUNC | Spearville to Clark County 345 kV line | DISIS STAGE
GEN-2019-035 | 03 - Central | 22 | DIS-19-1 | Solar | 80 | 80 | None | -0.7 | ER/NR | EMDE | Reeds Spring-Aurora 161kV Line | DISIS STAGE
GEN-2019-044 | 03 - Central | 22 | DIS-19-1 | Solar | 100 | 0 | Voltage: P42:345:SPS:CARPENTER:OR335:SLG:EHV: | -5.155 | ER | SUNC | North Fort Dodge 115kV Substation | DISIS STAGE
GEN-2019-048 | 03 - Central | 22 | DIS-19-1 | Battery/Storage | 50 | 50 | None | -1.951 | ER | KCPL | Duncan 69kV substation | DISIS STAGE
GEN-2019-051 | 03 - Central | 22 | DIS-19-1 | Battery/Storage | 40 | 0 | Voltage: P42:345:SPS:CARPENTER:OR335:SLG:EHV: | 0 | ER/NR | SUNC | Frey St 115kV bus | DISIS STAGE
GEN-2019-053 | 03 - Central | 22 | DIS-19-1 | Battery/Storage | 50 | 0 | Voltage: P42:345:SPS:CARPENTER:OR335:SLG:EHV: | 0 | ER/NR | SUNC | Great Bend-Spearville 230kV line | DISIS STAGE
GEN-2019-054 | 03 - Central | 22 | DIS-19-1 | Solar | 150 | 0 | Voltage: P42:345:SPS:CARPENTER:OR335:SLG:EHV: | -3.682 | ER/NR | SUNC | Great Bend- Circle 230kV line | DISIS STAGE
GEN-2019-055 | 03 - Central | 22 | DIS-19-1 | Solar | 150 | 0 | Voltage: P42:345:SPS:CARPENTER:OR335:SLG:EHV: | -2.85 | ER/NR | SUNC | Great Bend-Spearville 230kV line | DISIS STAGE
GEN-2019-058 | 03 - Central | 22 | DIS-19-1 | Solar | 150 | 0 | Voltage: P42:345:SPS:CARPENTER:OR335:SLG:EHV: | -1.89 | ER/NR | SUNC | Clark County 345kV substation | DISIS STAGE
GEN-2019-062 | 03 - Central | 22 | DIS-19-1 | Battery/Storage | 90 | 0 | Voltage: P23:345:SUNC:HLC_BRK188:::EHV: | -4.2 | ER | WERE | Pony Meadows - El Paso 138kV Line Break | DISIS STAGE
GEN-2019-063 | 03 - Central | 22 | DIS-19-1 | Battery/Storage | 50 | 0 | Voltage: P42:345:SPS:CARPENTER:OR335:SLG:EHV: | 0 | ER/NR | SUNC | Clark County 345kV substation | DISIS STAGE
GEN-2019-068 | 03 - Central | 22 | DIS-19-1 | Battery/Storage | 50 | 0 | Voltage: P42:345:SPS:CARPENTER:OR335:SLG:EHV: | 0 | ER/NR | SUNC | Great Bend - Circle 230kV line | DISIS STAGE
GEN-2019-002 | 04 - Southeast | 22 | DIS-19-1 | Battery/Storage | 100 | 100 | None | -0.13 | ER | GRDA | Maid 161kV substation | DISIS STAGE
GEN-2019-012 | 04 - Southeast | 22 | DIS-19-1 | Battery/Storage | 200 | 200 | None | -0.19 | ER/NR | OGE | Woodward 345kV substation | DISIS STAGE
GEN-2019-013 | 04 - Southeast | 22 | DIS-19-1 | Battery/Storage | 50 | 50 | None | -4.38 | ER/NR | AEPW | Dempsey 230kV sub/Sweetwater 230kV | DISIS STAGE
GEN-2019-045 | 04 - Southeast | 22 | DIS-19-1 | Solar | 155 | 155 | None | -9.93 | ER | OGE | DeGrasse 138kV Substation | DISIS STAGE
GEN-2019-052 | 04 - Southeast | 22 | DIS-19-1 | Solar | 135 | 135 | None | -3.81 | ER/NR | OKGE | Cimarron 345kV | DISIS STAGE
GEN-2019-065 | 04 - Southeast | 22 | DIS-19-1 | Battery/Storage | 180 | 180 | None | -1.07 | ER | AEPW | Overton-Northwest Henderson 138kV | DISIS STAGE
GEN-2019-066 | 04 - Southeast | 22 | DIS-19-1 | Battery/Storage | 50 | 50 | None | 0.4 | ER/NR | AEPW | Sweetwater 230kV substation | DISIS STAGE
GEN-2019-067 | 04 - Southeast | 22 | DIS-19-1 | Battery/Storage | 30 | 30 | None | 0.26 | ER/NR | OKGE | Cimarron 345kV | DISIS STAGE
GEN-2019-003 | 05 - Southwest | 22 | DIS-19-1 | Solar | 150 | 0 | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT | -3.19 | ER/NR | SPS | Roosevelt 230kV Substation | DISIS STAGE
GEN-2019-004 | 05 - Southwest | 22 | DIS-19-1 | Thermal | 56 | 0 | Stability: Group5_Fault_0203_P1 | N/A | ER | SPS | Hobbs 230kV / 115kV Switchyard | DISIS STAGE
GEN-2019-011 | 05 - Southwest | 22 | DIS-19-1 | Battery/Storage | 230 | 0 | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT | -0.22 | ER/NR | SPS | Yoakum 345kV Substation | DISIS STAGE
GEN-2019-021 | 05 - Southwest | 22 | DIS-19-1 | Solar | 50 | 0 | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT | -0.88 | ER/NR | SPS | Roosevelt 230kV Substation | DISIS STAGE
GEN-2019-056 | 05 - Southwest | 22 | DIS-19-1 | Battery/Storage | 100 | 0 | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT | -4.81 | ER | SPS | Randall 115kV substation | DISIS STAGE
GEN-2019-074 | 05 - Southwest | 22 | DIS-19-1 | Battery/Storage | 100 | 0 | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT | -5.69 | ER | SPS | Plant X 230kV Substation | DISIS STAGE
GEN-2018-074 | 01 - North | 21 | DIS-18-2 | Wind | 78 | 0 | Voltage | -4.25 | ER | WAPA | Denison 230kV Substation | DISIS STAGE
GEN-2019-019 | 01 - North | 22 | DIS-19-1 | Thermal | 15.15 | 0 | Voltage | -0.08 | ER/NR | BEPC | Siouxland 69kV | DISIS STAGE
GEN-2019-023 | 01 - North | 22 | DIS-19-1 | Wind/Battery | 110 | 0 | Voltage | -4.63 | ER/NR | WAPA | WAPA-UGP Mingusville 230kV | DISIS STAGE
GEN-2019-037 | 01 - North | 22 | DIS-19-1 | Solar | 150 | 0 | Voltage | -4.5 | ER/NR | BEPC | Leland Olds 345kV substation | DISIS STAGE
GEN-2019-029 | 02 - Nebraska | 22 | DIS-19-1 | Wind | 404 | 0 | Non-Convergence | -15.4 | ER/NR | NPPD | Sidney Keystone 345 kV line | DISIS STAGE
GEN-2019-033 | 02 - Nebraska | 22 | DIS-19-1 | Solar | 182 | 0 | Non-Convergence | -6.15 | ER/NR | NPPD | Sidney Keystone 345 kV line | DISIS STAGE
GEN-2019-039 | 02 - Nebraska | 22 | DIS-19-1 | Solar | 174.5 | 0 | Non-Convergence | -0.95 | ER/NR | NPPD | Columbus Southeast-Rising City 115kV | DISIS STAGE
GEN-2019-041 | 02 - Nebraska | 22 | DIS-19-1 | Solar | 78 | 0 | Non-Convergence | -0.4 | ER/NR | NPPD | 115kV Monolith Substation | DISIS STAGE
GEN-2019-069 | 02 - Nebraska | 22 | DIS-19-1 | Solar | 100 | 0 | Non-Convergence | -4.8 | ER | NPPD | Shell Creek-Hoskins 345kV Line | DISIS STAGE
GEN-2019-070 | 02 - Nebraska | 22 | DIS-19-1 | Solar | 50 | 0 | Non-Convergence | -1.95 | ER | NPPD | Shell Creek-Hoskins 345kv Line | DISIS STAGE
GEN-2019-073 | 02 - Nebraska | 22 | DIS-19-1 | Solar | 100 | 0 | Non-Convergence | -4.8 | ER | NPPD | Shell Creek-Hoskins 345kv Line | DISIS STAGE
GEN-2018-063 | 03 - Central | 21 | DIS-18-2 | Solar | 57 | 57 | None | -0.063 | ER | EMDE | Sedalia Marshfield Springfield Nichols Street 69kV circuit | DISIS STAGE
GEN-2018-093 | 03 - Central | 21 | DIS-18-2 | Battery/Storage | 60 | 0 | Voltage: P23:345:SUNC:HLC_BRK188:::EHV: | -5.54 | ER | WERE | Gordan Evans 137kV Substation | DISIS STAGE
GEN-2018-108 | 03 - Central | 21 | DIS-18-2 | Battery/Storage | 95 | 0 | Voltage: P23:345:SUNC:HLC_BRK188:::EHV: | -33.2 | ER | SUNC | Thistle 345kV substation | DISIS STAGE
GEN-2018-116 | 03 - Central | 21 | DIS-18-2 | Solar | 150 | 0 | Voltage: P42:345:SPS:CARPENTER:OR335:SLG:EHV: | -4.045 | ER/NR | SUNC | Frey Street 115kV bus | DISIS STAGE
GEN-2018-121 | 03 - Central | 21 | DIS-18-2 | Battery/Storage | 50 | 50 | None | -3.34 | ER | KCPL | KC South-N. Raymore 161kV Line | DISIS STAGE
GEN-2018-128 | 03 - Central | 21 | DIS-18-2 | Wind | 200.22 | 0 | Voltage: P23:345:SUNC:HLC_BRK188:::EHV: | -7.55 | ER/NR | WERE | Renfrow-Viola 345 kV | DISIS STAGE
GEN-2018-064 | 04 - Southeast | 21 | DIS-18-2 | Solar | 80 | 80 | None | -0.61 | ER/NR | GRDA | Tonnece Substation 69kV | DISIS STAGE
GEN-2018-071 | 04 - Southeast | 21 | DIS-18-2 | Battery/Storage | 151 | 151 | None | -23.19 | ER/NR | OGE | Interconnecting into OG&E's Ranch Road 345kV substation by tapping a 0.1 gen tie line into the existing Frontier II gen-tie line | DISIS STAGE
GEN-2018-072 | 04 - Southeast | 21 | DIS-18-2 | Battery/Storage | 151 | 151 | None | -1.29 | ER/NR | OGE | Interconnecting into OG&E's Ranch Road 345kV substation by tapping a 0.1 gen tie line into the existing Frontier II gen-tie line | DISIS STAGE
GEN-2018-079 | 04 - Southeast | 21 | DIS-18-2 | Solar | 148 | 148 | None | -8.52 | ER | AEPW | Farmland-Delaware 138kV line | DISIS STAGE
GEN-2018-082 | 04 - Southeast | 21 | DIS-18-2 | Wind | 215 | 0 | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT | -15.6 | ER | AEPW | Pittsburg 345kV Substation | DISIS STAGE
GEN-2018-087 | 04 - Southeast | 21 | DIS-18-2 | Battery/Storage | 75 | 75 | None | -4.03 | ER | AEPW | Lydia 345kV substation | DISIS STAGE
GEN-2018-088 | 04 - Southeast | 21 | DIS-18-2 | Solar | 130 | 130 | None | -6.75 | ER | AEPW | Lydia 345kV substation | DISIS STAGE
GEN-2018-106 | 04 - Southeast | 21 | DIS-18-2 | Solar | 165 | 165 | None | -7.715 | ER | AEPW | Longwood 345kV substation | DISIS STAGE
GEN-2018-115 | 04 - Southeast | 21 | DIS-18-2 | Hybrid | 250 | 250 | None | -4.89 | ER/NR | AEPW | Lawton East Side 345kV/138kv Substation | DISIS STAGE
GEN-2018-117 | 04 - Southeast | 21 | DIS-18-2 | Solar | 150 | 150 | None | -2.03 | ER/NR | AEPW | Sweetwater 230kV | DISIS STAGE
GEN-2018-073 | 05 - Southwest | 21 | DIS-18-2 | Solar | 250 | 0 | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT | -6.16 | ER | SPS | 345kV Crawfish Substation | DISIS STAGE
GEN-2018-081 | 05 - Southwest | 21 | DIS-18-2 | Solar | 175 | 0 | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT | -8.88 | ER | SPS | Plant X 230kV Substation | DISIS STAGE
GEN-2018-089 | 05 - Southwest | 21 | DIS-18-2 | Wind | 196 | 0 | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT | -8.79 | ER | SPS | Newhart 230kV Substation | DISIS STAGE
GEN-2018-092 | 05 - Southwest | 21 | DIS-18-2 | Solar | 400 | 0 | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT | -14.9 | ER | SPS | Oklaunion-Tuco 345kV Line Break | DISIS STAGE
GEN-2018-097 | 05 - Southwest | 21 | DIS-18-2 | Solar | 100 | 0 | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT | -5.32 | ER | SPS | Tolk 230kV Substation | DISIS STAGE
GEN-2018-099 | 05 - Southwest | 21 | DIS-18-2 | Wind | 300 | 0 | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT | -5.1 | ER | SPS | Tolk 230kV Substation | DISIS STAGE
GEN-2018-111 | 05 - Southwest | 21 | DIS-18-2 | Battery/Storage | 75 | 0 | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT | -3.77 | ER | SPS | Tolk 230kV substation | DISIS STAGE
GEN-2018-112 | 05 - Southwest | 21 | DIS-18-2 | Solar | 185 | 0 | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT | -12.35 | ER | SPS | Tolk 230kV substation | DISIS STAGE
GEN-2018-124 | 05 - Southwest | 21 | DIS-18-2 | Solar | 200 | 0 | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT | -2.26 | ER | SPS | Tolk 230kV substation | DISIS STAGE
ASGI-2017-013 | 01 - North | 20 | DIS-18-1 | Wind | 40 |  |  |  | ER | WAPA | Wolsey 69kV Substation | DISIS STAGE
GEN-2018-008 | 01 - North | 20 | DIS-18-1 | Wind | 252 |  |  |  | ER/NR | WAPA | Groton-Leland Olds 345kV Line | DISIS STAGE
GEN-2018-010 | 01 - North | 20 | DIS-18-1 | Battery | 74.1 |  |  |  | ER/NR | WAPA | Neset 230kV Substation | DISIS STAGE
GEN-2018-039 | 01 - North | 20 | DIS-18-1 | Solar | 72 |  |  |  | ER/NR | WAPA | Edgeley 115kV substation | DISIS STAGE
GEN-2018-012 | 02 - Nebraska | 20 | DIS-18-1 | Wind | 74.1 |  |  |  | ER/NR | NPPD | Antelope 345kV Substation | DISIS STAGE
GEN-2018-025 | 02 - Nebraska | 20 | DIS-18-1 | Battery | 200 |  |  |  | ER | OPPD | Fort Calhoun 345kV Substation | DISIS STAGE
GEN-2018-033 | 02 - Nebraska | 20 | DIS-18-1 | Battery | 200 |  |  |  | ER | OPPD | Cass County 345kV Substation | DISIS STAGE
GEN-2018-037 | 02 - Nebraska | 20 | DIS-18-1 | Battery | 100 |  |  |  | ER | OPPD | Looping in OPPD (S1211) (S1220) (S1211) (S1299) 161kV | DISIS STAGE
GEN-2018-043 | 02 - Nebraska | 20 | DIS-18-1 | Solar | 500 |  |  |  | ER | OPPD | Ft. Calhoun - Raun 345 kV Line Break | DISIS STAGE
GEN-2018-056 | 02 - Nebraska | 20 | DIS-18-1 | Solar | 102.6 |  |  |  | ER/NR | WAPA | Fort Thompson-Grand Island (Grand Prairie) 345kV | DISIS STAGE
GEN-2018-060 | 02 - Nebraska | 20 | DIS-18-1 | Wind | 50 |  |  |  | ER/NR | NPPD | Axtell-Post Rock 345 kV | DISIS STAGE
ASGI-2018-003 | 03 - Central | 20 | DIS-18-1 | Solar | 20 |  |  |  | ER | KCPL | AP City 69kV Substation | DISIS STAGE
ASGI-2018-006 | 03 - Central | 20 | DIS-18-1 | Solar | 20 |  |  |  | ER | KCPL | Metz 69kV Substation | DISIS STAGE
ASGI-2018-007 | 03 - Central | 20 | DIS-18-1 | Solar | 20 |  |  |  | ER | KCPL | Salisbury 161kV Substation | DISIS STAGE
ASGI-2018-010 | 03 - Central | 20 | DIS-18-1 | Solar | 35 |  |  |  | ER | KCPL | Pleasant Valley 161kV Substation | DISIS STAGE
ASGI-2018-011 | 03 - Central | 20 | DIS-18-1 | Solar | 35 |  |  |  | ER | KCPL | South Ottawa 161kV Substation | DISIS STAGE
GEN-2018-009 | 03 - Central | 20 | DIS-18-1 | Wind | 150 |  |  |  | ER | SUNC | Cimarron 115kV Substation | DISIS STAGE
GEN-2018-013 | 03 - Central | 20 | DIS-18-1 | Wind | 74.1 |  |  |  | ER | WERE | Abilene Energy Center-Northview 115kV Line | DISIS STAGE
GEN-2018-022 | 03 - Central | 20 | DIS-18-1 | Solar | 300 |  |  |  | ER/NR | KCPL | Mullen Creek 345kV Substation | DISIS STAGE
GEN-2018-030 | 03 - Central | 20 | DIS-18-1 | Battery | 200 |  |  |  | ER | SPS | Lamar-Finney 345kV Substation | DISIS STAGE
GEN-2018-031 | 03 - Central | 20 | DIS-18-1 | Battery | 50 |  |  |  | ER | KCPL | Blue Valley 161kV Substation | DISIS STAGE
GEN-2018-032 | 03 - Central | 20 | DIS-18-1 | Wind | 310 |  |  |  | ER | WERE | Neosho 345kV Substation | DISIS STAGE
GEN-2018-049 | 03 - Central | 20 | DIS-18-1 | Solar | 120 |  |  |  | ER | SUNC | Thistle 345kV Substation | DISIS STAGE
GEN-2018-054 | 03 - Central | 20 | DIS-18-1 | Solar | 120 |  |  |  | ER | KCPL | KC South - N. Raymore 161kV Line | DISIS STAGE
GEN-2018-057 | 03 - Central | 20 | DIS-18-1 | Solar | 203.4 |  |  |  | ER/NR | WERE | Gordon Evans 138kV | DISIS STAGE
GEN-2018-062 | 03 - Central | 20 | DIS-18-1 | Solar | 75.6 |  |  |  | ER/NR | KACY | Nearman 161kV substation | DISIS STAGE
GEN-2018-003 | 04 - Southeast | 20 | DIS-18-1 | Solar | 150 |  |  |  | ER/NR | AEPW | North Boston-Bann 138kV Line | DISIS STAGE
GEN-2018-011 | 04 - Southeast | 20 | DIS-18-1 | Battery | 74.1 |  |  |  | ER/NR | WFEC | Dover 138 kV Switching Station | DISIS STAGE
GEN-2018-021 | 04 - Southeast | 20 | DIS-18-1 | Solar | 74.1 |  |  |  | ER/NR | AEPW | Chisholm-Gracemont 345kV Line | DISIS STAGE
GEN-2018-024 | 04 - Southeast | 20 | DIS-18-1 | Battery | 100 |  |  |  | ER | OKGE | Canadian River-Muskogee and Muskogee-Seminole 345kV | DISIS STAGE
GEN-2018-026 | 04 - Southeast | 20 | DIS-18-1 | Battery | 100 |  |  |  | ER | OKGE | Mustang 138kV Substation | DISIS STAGE
GEN-2018-027 | 04 - Southeast | 20 | DIS-18-1 | Battery | 100 |  |  |  | ER | OKGE | Tulsa Power Station 38kV Substation | DISIS STAGE
GEN-2018-028 | 04 - Southeast | 20 | DIS-18-1 | Battery | 200 |  |  |  | ER | OKGE | Tulsa North 138kV Substation | DISIS STAGE
GEN-2018-029 | 04 - Southeast | 20 | DIS-18-1 | Battery | 100 |  |  |  | ER | OKGE | Horseshoe Lake 138kV Substation | DISIS STAGE
GEN-2018-048 | 04 - Southeast | 20 | DIS-18-1 | Solar | 300 |  |  |  | ER | OKGE | Pecan Creek 345kV Substation | DISIS STAGE
GEN-2018-050 | 04 - Southeast | 20 | DIS-18-1 | Solar | 200 |  |  |  | ER | AEPW | Longwood 345kV Substation | DISIS STAGE
GEN-2018-055 | 04 - Southeast | 20 | DIS-18-1 | Solar | 252 |  |  |  | ER/NR | AEPW | Terry Road 345kV station (shared with Rush Springs Windfarm on a common gentie) | DISIS STAGE
GEN-2018-004 | 05 - Southwest | 20 | DIS-18-1 | Solar | 74.99 |  |  |  | ER | SPS | T14 Circuit 115kV line | DISIS STAGE
GEN-2018-015 | 05 - Southwest | 20 | DIS-18-1 | Solar | 252 |  |  |  | ER/NR | SPS | Tuco-Oklaunion 345kV Line | DISIS STAGE
GEN-2018-052 | 05 - Southwest | 20 | DIS-18-1 | Battery | 70 |  |  |  | ER | SPS | Roadrunner 115kV Substation | DISIS STAGE
J1040 | 01 - North | 19.5 | DIS-18-1-PQ | Wind | 250 |  |  |  | ER/NR | MDU | Wishek Junction 230 kV Substation | IA PENDING
J1045 | 01 - North | 19.5 | DIS-18-1-PQ | Battery | 20 |  |  |  | ER/NR | XEL | Fenton - Chanarambie 115kV Line Tap | IA PENDING
J1072 | 01 - North | 19.5 | DIS-18-1-PQ | Solar | 150 |  |  |  | ER/NR | XEL | Adams 345 kV Substation | IA PENDING
J1092 | 01 - North | 19.5 | DIS-18-1-PQ | Solar | 100 |  |  |  | ER/NR | XEL | Three Lakes 115 kV Substation | IA PENDING
J1124 | 01 - North | 19.5 | DIS-18-1-PQ | Solar | 100 |  |  |  | ER/NR | XEL | Byron 345kV Substation | IA PENDING
J1164 | 01 - North | 19.5 | DIS-18-1-PQ | Solar | 80 |  |  |  | ER | ALTW | Magnolia 161 kV Substation | IA PENDING
J1169 | 01 - North | 19.5 | DIS-18-1-PQ | Solar | 50 |  |  |  | ER | XEL | Grant 115 kV Substation | IA PENDING
J1181 | 01 - North | 19.5 | DIS-18-1-PQ | Wind | 200 |  |  |  | ER | ALTW | Hazleton - Mitchell county 345 kV line | IA PENDING
J1221 | 01 - North | 19.5 | DIS-18-1-PQ | Solar | 150 |  |  |  | ER/NR | GRE | Wing River- Riverton 230kV line | IA PENDING
J1298 | 01 - North | 19.5 | DIS-18-1-PQ | Solar | 150 |  |  |  | ER/NR | ALTW | Hayward - Murphy Creek 161kV Line | IA PENDING
J1312 | 01 - North | 19.5 | DIS-18-1-PQ | Solar | 50 |  |  |  | ER/NR | XEL | Grant 115 kV Substation | IA PENDING
J1314 | 01 - North | 19.5 | DIS-18-1-PQ | Solar | 100 |  |  |  | ER/NR | DPC | Apple River 161 kV Substation | IA PENDING
J1325 | 01 - North | 19.5 | DIS-18-1-PQ | Solar | 80 |  |  |  | ER/NR | ALTW | Magnolia 161 kV substation | IA PENDING
J1426 | 01 - North | 19.5 | DIS-18-1-PQ | Solar | 100 |  |  |  | ER/NR | XEL | Benton County 115kV Substation | IA PENDING
J1445 | 01 - North | 19.5 | DIS-18-1-PQ | Solar | 100 |  |  |  | ER/NR | XEL | Mayhew Lake 115kV Substation | IA PENDING
J1474 | 01 - North | 19.5 | DIS-18-1-PQ | Solar | 180 |  |  |  | ER/NR | XEL | Pine Lake - Eagle Point 115kV Line | IA PENDING
J1485 | 01 - North | 19.5 | DIS-18-1-PQ | Wind | 250 |  |  |  | ER | OTP | Astoria 345 kV Substation (J493/J510) | IA PENDING
J967 | 01 - North | 19.5 | DIS-18-1-PQ | Wind | 150 |  |  |  | ER | XEL | Adams 345kV Substation | IA PENDING
MPC03600 | 01 - North | 19.5 | DIS-18-1-PQ | Solar | 200 |  |  |  | ER | OTP | Frontier-Wahpeton 230 kV Line | IA PENDING
MPC03700 | 01 - North | 19.5 | DIS-18-1-PQ | Solar | 150 |  |  |  | ER | OTP | Frontier-Wahpeton 230 kV Line | IA PENDING
MPC03800 | 01 - North | 19.5 | DIS-18-1-PQ | Wind | 250 |  |  |  | ER/NR | OTP | Center-Prairie 345 kV Line
MPC03900 | 01 - North | 19.5 | DIS-18-1-PQ | Wind | 151.2 |  |  |  | ER/NR | OTP | Center-Prairie 345 kV Line
MPC04000 | 01 - North | 19.5 | DIS-18-1-PQ | Wind | 300 |  |  |  | ER/NR | OTP | Square Butte 230 kV Substation
J1050 | 02 - Nebraska | 19.5 | DIS-18-1-PQ | Wind | 225 |  |  |  | ER/NR | ALTW | Doud Tap 161 kV Substation | IA PENDING
J1132 | 02 - Nebraska | 19.5 | DIS-18-1-PQ | Solar | 50 |  |  |  | ER | ALTW | Creston East 69 kV Substation | IA PENDING
J1174 | 02 - Nebraska | 19.5 | DIS-18-1-PQ | Solar | 165 |  |  |  | ER/NR | ALTW | Ledyard - Colby 345 kV Line Tap | IA PENDING
J1175 | 02 - Nebraska | 19.5 | DIS-18-1-PQ | Wind | 165 |  |  |  | ER | ALTW | Ledyard - Colby 345kV Line Tap | IA PENDING
J1270 | 02 - Nebraska | 19.5 | DIS-18-1-PQ | Wind | 200 |  |  |  | ER | MEC | Kossuth - O'Brien 345 kV Line Tap | IA PENDING
J1313 | 02 - Nebraska | 19.5 | DIS-18-1-PQ | Solar | 100 |  |  |  | ER/NR | ALTW | 161kV bus at Karma substation | IA PENDING
J1359 | 02 - Nebraska | 19.5 | DIS-18-1-PQ | Gas | 95 |  |  |  | ER/NR | ALTW | Oakridge 69 kV Substation | IA PENDING
J1365 | 02 - Nebraska | 19.5 | DIS-18-1-PQ | Wind | 169.4 |  |  |  | ER | ALTW | Traer 161-kV Substation | IA PENDING
J1444 | 02 - Nebraska | 19.5 | DIS-18-1-PQ | Solar | 200 |  |  |  | ER/NR | ALTW | Duane Arnold 345kV Substation | IA PENDING
J982 | 02 - Nebraska | 19.5 | DIS-18-1-PQ | Wind | 300 |  |  |  | ER | MEC | Obrien County - Kossuth 345 kV Line Tap | IA PENDING
GIA-96 | 03 - Central | 19.5 | DIS-18-1-PQ | Wind | 101.32 |  |  |  | ER | AECI | Stroud 138kV | IA PENDING
J1025 | 03 - Central | 19.5 | DIS-18-1-PQ | Wind | 290 |  |  |  | ER/NR | AMMO | Zachary - Maywood 345 kV Line Tap | IA PENDING
J1026 | 03 - Central | 19.5 | DIS-18-1-PQ | Wind | 380 |  |  |  | ER/NR | AMMO | Maywood - Spencer Creek 345 kV Line Tap | IA PENDING
J1145 | 03 - Central | 19.5 | DIS-18-1-PQ | Solar | 250 |  |  |  | ER/NR | AMMO | Overton - (McCrede) - Montgomery 345 kV Line Tap | IA PENDING
J1182 | 03 - Central | 19.5 | DIS-18-1-PQ | Solar | 250 |  |  |  | ER/NR | AMMO | Zachary Substation 345 kV Bus | IA PENDING
J1191 | 03 - Central | 19.5 | DIS-18-1-PQ | Solar | 64 |  |  |  | ER/NR | CWLD | Bolstad 69 kV Substation | IA PENDING
J1202 | 03 - Central | 19.5 | DIS-18-1-PQ | Solar/Battery | 85 |  |  |  | ER/NR | AMIL | Baldwin Plant 345kV Switchyard - Baldwin Unit 2 | IA PENDING
J1208 | 03 - Central | 19.5 | DIS-18-1-PQ | Solar | 80 |  |  |  | ER/NR | AMIL | Muddy - Crab Orchard 138kV Line | IA PENDING
J1209 | 03 - Central | 19.5 | DIS-18-1-PQ | Solar | 80 |  |  |  | ER/NR | AMIL | Muddy - Crab Orchard 138kV Line | IA PENDING
J1213 | 03 - Central | 19.5 | DIS-18-1-PQ | Hydro | 60 |  |  |  | ER/NR | AMMO | Taum Sauk 138kV Switchyard, Bus 1 & 2 | IA PENDING
J1216 | 03 - Central | 19.5 | DIS-18-1-PQ | Solar | 185 |  |  |  | ER/NR | AMIL | Ashley 138 kV Substation | IA PENDING
J1241 | 03 - Central | 19.5 | DIS-18-1-PQ | Solar | 165 |  |  |  | ER/NR | AMIL | West Mt Vernon - Xenia 345kV Line | IA PENDING
J1268 | 03 - Central | 19.5 | DIS-18-1-PQ | Solar | 150 |  |  |  | ER/NR | AMMO | Pike - Troy 161kV Line | IA PENDING
J1303 | 03 - Central | 19.5 | DIS-18-1-PQ | Solar | 95 |  |  |  | ER/NR | SIPC | Campbell Hill - Jackson 161kV Line | IA PENDING
J1306 | 03 - Central | 19.5 | DIS-18-1-PQ | Solar | 200 |  |  |  | ER/NR | AMIL | Commodore-Jordan 345kV Line | IA PENDING
J1311 | 03 - Central | 19.5 | DIS-18-1-PQ | Solar | 150 |  |  |  | ER/NR | AMIL | Fayetteville Bee Hollow Road 138 kV Substation | IA PENDING
J1352 | 03 - Central | 19.5 | DIS-18-1-PQ | Solar | 100 |  |  |  | ER/NR | AMMO | Spencer Creek - Montgomery 345kV Line | IA PENDING
J1488 | 03 - Central | 19.5 | DIS-18-1-PQ | Wind | 500 |  |  |  | ER/NR | AMMO | McCredie - Montgomery 345 kV Line Tap | IA PENDING
J1490 | 03 - Central | 19.5 | DIS-18-1-PQ | Wind | 1000 |  |  |  | ER/NR | AMMO | McCredie - Montgomery 345 kV Line Tap | IA PENDING
J956 | 03 - Central | 19.5 | DIS-18-1-PQ | Solar | 200 |  |  |  | ER/NR | AMMO | Spencer Creek 345kV Substation | IA PENDING
J976 | 03 - Central | 19.5 | DIS-18-1-PQ | Solar | 300 |  |  |  | ER/NR | AMMO | Montgomery - Enon 345kV Line Tap | IA PENDING
J987 | 03 - Central | 19.5 | DIS-18-1-PQ | Solar | 100 |  |  |  | ER/NR | AMMO | Montgomery 161kV Substation | IA PENDING
J994 | 03 - Central | 19.5 | DIS-18-1-PQ | Solar | 100 |  |  |  | ER/NR | AMMO | Guthrie 161 kV Substation | IA PENDING
J1007 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Solar | 180 |  |  |  | ER/NR | EES-EAI | Marion - Marked Tree 161 kV | IA PENDING
J1030 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Solar | 150 |  |  |  | ER | EES | Poco - Menard 138 kV | IA PENDING
J1034 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Solar | 225 |  |  |  | ER/NR | AMMO | Stoddard - Morley 161kV Line Tap | IA PENDING
J1060 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Solar | 450 |  |  |  | ER/NR | EES-EAI | West Memphis - Keo 500 kV | IA PENDING
J1087 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Solar | 200 |  |  |  | ER/NR | AMMO | Miner - Kelso 161 kV Line Tap | IA PENDING
J1107 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Solar | 200 |  |  |  | ER/NR | AMMO | Kelso - Lutesville 345 kV Line Tap | IA PENDING
J1125 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Solar | 135 |  |  |  | ER/NR | EES-EAI | Wynne South - Wynne East AECC 161 kV | IA PENDING
J1155 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Solar | 150 |  |  |  | ER/NR | EES-EAI | Driver 230 kV | IA PENDING
J1205 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Solar | 125 |  |  |  | ER | CLEC | Centennial - West Bay 138 kV | IA PENDING
J1215 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Solar | 155 |  |  |  | ER/NR | EES-EAI | Stuttgart Ricuskey - Woodward 230 kV | IA PENDING
J1231 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Solar | 125 |  |  |  | ER/NR | BREC | Barkley - Caldwell 161kV Line | IA PENDING
J1239 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Solar | 100 |  |  |  | ER | EES | Rilla 115 kV | IA PENDING
J1258 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Battery | 50 |  |  |  | ER/NR | EES-EAI | KEO EHV 500 kV Substation | IA PENDING
J1281 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Solar | 75 |  |  |  | ER/NR | EES-EAI | Crossett - Monticello East 115 kV | IA PENDING
J1299 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Solar | 149 |  |  |  | ER/NR | AMMO | Miner - Kelso 161kV Line | IA PENDING
J1373 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Solar | 95 |  |  |  | ER/NR | EES-EAI | Griffithville - Searcy Price 115 kV Line Tap | IA PENDING
J1402 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Battery | 0 |  |  |  | ER/NR | EES-EAI | Cash - Newport AB161kV Line | IA PENDING
J1415 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Solar | 250 |  |  |  | ER/NR | EES-EAI | KEO EHV 500 kV Substation | IA PENDING
J1424 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Solar | 200 |  |  |  | ER | CLEC | Cooper - Penton Road 230 kV | IA PENDING
J1434 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Solar | 100 |  |  |  | ER/NR | EES-EAI | J907 230kV Sub, Brinkley East - Aubrey 230 kV Line | IA PENDING
J1436 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Solar | 50 |  |  |  | ER | EES | Oak Ridge 115 kV | IA PENDING
J1437 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Wind | 180 |  |  |  | ER/NR | EES-EAI | AECC Dry Creek 161 kV | IA PENDING
J1442 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Solar | 105 |  |  |  | ER | EES | Rich (SHECO) - Livingston 138 kV | IA PENDING
GEN-2017-175 | 01 - North | 19 | DIS-17-2 | Wind | 300 |  |  |  | ER | WAPA | Vfodnes-Utica Jct. 230kV | DISIS STAGE
GEN-2017-214 | 01 - North | 19 | DIS-17-2 | Wind | 100 |  |  |  | ER/NR | WAPA | Logan 230kV Substation | DISIS STAGE
GEN-2017-215 | 01 - North | 19 | DIS-17-2 | Wind | 100 |  |  |  | ER/NR | WAPA | Logan 230kV Substation | DISIS STAGE
GEN-2017-216 | 01 - North | 19 | DIS-17-2 | Wind | 100 |  |  |  | ER/NR | WAPA | Logan 230kV Substation | DISIS STAGE
GEN-2017-222 | 01 - North | 19 | DIS-17-2 | Wind | 180 |  |  |  | ER | WAPA | Denison 230kV Substation | DISIS STAGE
GEN-2017-105 | 02 - Nebraska | 19 | DIS-17-2 | Wind | 75 |  |  |  | ER/NR | OPPD | Tekamah - Raun 161 kV Line | DISIS STAGE
GEN-2017-144 | 02 - Nebraska | 19 | DIS-17-2 | Wind | 200 |  |  |  | ER | WAPA | Holt County 345kV | DISIS STAGE
GEN-2017-181 | 02 - Nebraska | 19 | DIS-17-2 | Wind | 300 |  |  |  | ER/NR | NPPD | Tobias 345kV Substation | DISIS STAGE
GEN-2017-182 | 02 - Nebraska | 19 | DIS-17-2 | Wind | 128 |  |  |  | ER/NR | NPPD | Tobias 345kV Substation | DISIS STAGE
GEN-2017-198 | 02 - Nebraska | 19 | DIS-17-2 | Battery | 11.64 |  |  |  | ER | OPPD | Jones St. No 1201 69kV substation | DISIS STAGE
GEN-2017-201 | 02 - Nebraska | 19 | DIS-17-2 | Wind | 250 |  |  |  | ER/NR | NPPD | Hoskins 345kV Substation | DISIS STAGE
GEN-2017-210 | 02 - Nebraska | 19 | DIS-17-2 | Solar/Battery | 310 |  |  |  | ER | NPPD | McCool 345kV Substation | DISIS STAGE
GEN-2017-234 | 02 - Nebraska | 19 | DIS-17-2 | Wind | 115 |  |  |  | ER | NPPD | Spalding to North Loup 115kV | DISIS STAGE
GEN-2017-108 | 03 - Central | 19 | DIS-17-2 | Solar | 400 |  |  |  | ER/NR | KCPL | Stillwell - Clinton 161kV Line | DISIS STAGE
GEN-2017-111 | 03 - Central | 19 | DIS-17-2 | Solar | 152 |  |  |  | ER | KCPL | Clinton â€“ Stilwell 161 kV Line Tap | DISIS STAGE
GEN-2017-115 | 03 - Central | 19 | DIS-17-2 | Wind | 244 |  |  |  | ER | KCPL | Holt County 345 kV | DISIS STAGE
GEN-2017-119 | 03 - Central | 19 | DIS-17-2 | Wind | 180 |  |  |  | ER | SUNC | Elm Creek 345kV substation | DISIS STAGE
GEN-2017-120 | 03 - Central | 19 | DIS-17-2 | Wind | 260 |  |  |  | ER | WERE | Abilene Energy Center-Northview 115kV | DISIS STAGE
GEN-2017-121 | 03 - Central | 19 | DIS-17-2 | Wind | 200 |  |  |  | ER/NR | WERE | Sumner 138kV | DISIS STAGE
GEN-2017-125 | 03 - Central | 19 | DIS-17-2 | Wind | 252 |  |  |  | ER/NR | WERE | Swissvale 345kV | DISIS STAGE
GEN-2017-128 | 03 - Central | 19 | DIS-17-2 | Wind | 202 |  |  |  | ER/NR | WERE | Swissvale 345kV | DISIS STAGE
GEN-2017-131 | 03 - Central | 19 | DIS-17-2 | Battery | 29.6 |  |  |  | ER/NR | WERE | Altoona- NE Parson 138kV | DISIS STAGE
GEN-2017-148 | 03 - Central | 19 | DIS-17-2 | Wind | 202 |  |  |  | ER/NR | EMDE | Joplin 161kV sub | DISIS STAGE
GEN-2017-179 | 03 - Central | 19 | DIS-17-2 | Wind | 222 |  |  |  | ER/NR | WERE | Gordon Evans 138kV Substation | DISIS STAGE
GEN-2017-183 | 03 - Central | 19 | DIS-17-2 | Wind | 400 |  |  |  | ER/NR | KCPL | Nashua-St. Joe 345kV | DISIS STAGE
GEN-2017-184 | 03 - Central | 19 | DIS-17-2 | Solar | 400 |  |  |  | ER/NR | KCPL | Nashua-St. Joe 345kV | DISIS STAGE
GEN-2017-188 | 03 - Central | 19 | DIS-17-2 | Solar | 130 |  |  |  | ER | EMDE | Asbury 161 kV | DISIS STAGE
GEN-2017-191 | 03 - Central | 19 | DIS-17-2 | Solar | 201.6 |  |  |  | ER/NR | WERE | Swissvale 345kV | DISIS STAGE
GEN-2017-192 | 03 - Central | 19 | DIS-17-2 | Battery | 52 |  |  |  | ER/NR | WERE | Swissvale 345kV | DISIS STAGE
GEN-2017-195 | 03 - Central | 19 | DIS-17-2 | Solar | 500.4 |  |  |  | ER/NR | KCPL | West Gardner 345kV | DISIS STAGE
GEN-2017-196 | 03 - Central | 19 | DIS-17-2 | Battery | 128 |  |  |  | ER/NR | KCPL | West Gardner 345kV | DISIS STAGE
GEN-2017-202 | 03 - Central | 19 | DIS-17-2 | Solar | 200 |  |  |  | ER/NR | SWPA | New Madrid - Sikeston 161kV | DISIS STAGE
GEN-2017-209 | 03 - Central | 19 | DIS-17-2 | Solar/Battery | 300 |  |  |  | ER | KCPL | LaCygne - Neosho 345kV | DISIS STAGE
GEN-2017-220 | 03 - Central | 19 | DIS-17-2 | Solar | 201.6 |  |  |  | ER/NR | WERE | Buffalo Flats 345kV Substation | DISIS STAGE
GEN-2017-221 | 03 - Central | 19 | DIS-17-2 | Battery | 152 |  |  |  | ER/NR | WERE | Buffalo Flats 345kV Substation | DISIS STAGE
GEN-2017-226 | 03 - Central | 19 | DIS-17-2 | Solar | 201.6 |  |  |  | ER/NR | WERE | Gordon Evans 138kV Substation | DISIS STAGE
GEN-2017-227 | 03 - Central | 19 | DIS-17-2 | Battery | 201.6 |  |  |  | ER/NR | WERE | Gordon Evans 138kV Substation | DISIS STAGE
GEN-2017-229 | 03 - Central | 19 | DIS-17-2 | Battery | 76 |  |  |  | ER/NR | KCPL | Stilwell 345kV Substation | DISIS STAGE
GEN-2017-117 | 04 - Southeast | 19 | DIS-17-2 | Battery | 19.8 |  |  |  | ER/NR | WFEC | El Reno SW 138kV | DISIS STAGE
GEN-2017-132 | 04 - Southeast | 19 | DIS-17-2 | Wind | 400 |  |  |  | ER/NR | OKGE | Arcadia 345kV | DISIS STAGE
GEN-2017-133 | 04 - Southeast | 19 | DIS-17-2 | Wind | 200 |  |  |  | ER/NR | OKGE | Arcadia 345kV | DISIS STAGE
GEN-2017-134 | 04 - Southeast | 19 | DIS-17-2 | Wind | 250 |  |  |  | ER/NR | OKGE | Arcadia 345kV | DISIS STAGE
GEN-2017-137 | 04 - Southeast | 19 | DIS-17-2 | Wind | 295 |  |  |  | ER/NR | OKGE | Arcadia 345kV | DISIS STAGE
GEN-2017-140 | 04 - Southeast | 19 | DIS-17-2 | Solar | 160 |  |  |  | ER/NR | AEPW | Clarksville 345kV Switching Station | DISIS STAGE
GEN-2017-141 | 04 - Southeast | 19 | DIS-17-2 | Solar | 241.7 |  |  |  | ER/NR | AEPW | Clarksville 345kV Switching Station | DISIS STAGE
GEN-2017-149 | 04 - Southeast | 19 | DIS-17-2 | Wind | 258 |  |  |  | ER/NR | OKGE | Johnson County 345kV Substation | DISIS STAGE
GEN-2017-150 | 04 - Southeast | 19 | DIS-17-2 | Solar | 250 |  |  |  | ER/NR | OKGE | Minco 345kV | DISIS STAGE
GEN-2017-152 | 04 - Southeast | 19 | DIS-17-2 | Wind | 252 |  |  |  | ER/NR | OKGE | McClain 138kV | DISIS STAGE
GEN-2017-154 | 04 - Southeast | 19 | DIS-17-2 | Wind | 255 |  |  |  | ER/NR | OKGE | Johnson County 345kV Substation | DISIS STAGE
GEN-2017-155 | 04 - Southeast | 19 | DIS-17-2 | Wind | 300 |  |  |  | ER/NR | OKGE | Muskogee 345kV Substation | DISIS STAGE
GEN-2017-164 | 04 - Southeast | 19 | DIS-17-2 | Solar | 250 |  |  |  | ER/NR | OKGE | Woodring 345kV Substation | DISIS STAGE
GEN-2017-166 | 04 - Southeast | 19 | DIS-17-2 | Solar | 250 |  |  |  | ER/NR | OKGE | Sunnyside 345kV | DISIS STAGE
GEN-2017-167 | 04 - Southeast | 19 | DIS-17-2 | Battery | 52 |  |  |  | ER/NR | OKGE | Sunnyside 345kV | DISIS STAGE
GEN-2017-168 | 04 - Southeast | 19 | DIS-17-2 | Solar | 250 |  |  |  | ER/NR | OKGE | McClain 138kV | DISIS STAGE
GEN-2017-169 | 04 - Southeast | 19 | DIS-17-2 | Battery | 52 |  |  |  | ER/NR | OKGE | McClain 138kV | DISIS STAGE
GEN-2017-171 | 04 - Southeast | 19 | DIS-17-2 | Solar | 150 |  |  |  | ER/NR | AEPW | Lawton Eastside - Terry Road 345kV | DISIS STAGE
GEN-2017-172 | 04 - Southeast | 19 | DIS-17-2 | Solar | 50 |  |  |  | ER/NR | AEPW | Lawton Eastside - Terry Road 345kV | DISIS STAGE
GEN-2017-173 | 04 - Southeast | 19 | DIS-17-2 | Solar | 50 |  |  |  | ER/NR | AEPW | Lawton Eastside - Terry Road 345kV | DISIS STAGE
GEN-2017-178 | 04 - Southeast | 19 | DIS-17-2 | Battery | 52 |  |  |  | ER/NR | OKGE | Woodring 345kV Substation | DISIS STAGE
GEN-2017-203 | 04 - Southeast | 19 | DIS-17-2 | Solar/Battery | 210 |  |  |  | ER | OKGE | Renfrow 345kV Substation | DISIS STAGE
GEN-2017-230 | 04 - Southeast | 19 | DIS-17-2 | Solar | 72.5 |  |  |  | ER/NR | OKGE | Tryon 138kV Substation | DISIS STAGE
GEN-2017-231 | 04 - Southeast | 19 | DIS-17-2 | Solar | 72.5 |  |  |  | ER/NR | OKGE | Branch 161kV Substation | DISIS STAGE
GEN-2017-232 | 04 - Southeast | 19 | DIS-17-2 | Solar | 52.2 |  |  |  | ER/NR | OKGE | Brown 138kV Substation | DISIS STAGE
GEN-2017-233 | 04 - Southeast | 19 | DIS-17-2 | Wind | 215 |  |  |  | ER/NR | OKGE | Minco 345kV | DISIS STAGE
GEN-2017-240 | 04 - Southeast | 19 | DIS-17-2 | Solar | 202 |  |  |  | ER/NR | OKGE | Bristow 138kV Substation | DISIS STAGE
GEN-2017-146 | 05 - Southwest | 19 | DIS-17-2 | Wind | 151.8 |  |  |  | ER | SPS | Deaf Smith-Plant X 230kV | DISIS STAGE
GEN-2017-151 | 05 - Southwest | 19 | DIS-17-2 | Wind | 300 |  |  |  | ER | SPS | TUCO-Oklaunion 345kV | DISIS STAGE
GEN-2017-158 | 05 - Southwest | 19 | DIS-17-2 | Wind | 265 |  |  |  | ER | SPS | Tolk 230kV Substation | DISIS STAGE
GEN-2017-187 | 05 - Southwest | 19 | DIS-17-2 | Solar | 150 |  |  |  | ER | SPS | Flatland 115 kV Substation | DISIS STAGE
GEN-2017-239 | 05 - Southwest | 19 | DIS-17-2 | Solar | 300 |  |  |  | ER | SPS | Mahoney 230kV Substation | DISIS STAGE
J545 | 01 - North | 18.5 | DIS-17-2-PQ | Wind | 110 |  |  |  | ER | XEL | Buffalo 115kV Substation
J722 | 01 - North | 18.5 | DIS-17-2-PQ | Wind | 200 |  |  |  | ER | OTP | Big Stone South 230kV Substation
J801 | 01 - North | 18.5 | DIS-17-2-PQ | Solar | 74 |  |  |  | ER | DPC | Crystal Cave-Rock Elm 161kV line tap | DISIS STAGE
J803 | 01 - North | 18.5 | DIS-17-2-PQ | Solar | 32.5 |  |  |  | ER | XEL | Tracy 69 kV line | DISIS STAGE
J874 | 01 - North | 18.5 | DIS-17-2-PQ | Solar | 150 |  |  |  | ER/NR | XEL | Fenton - Chanarambie 115kV Line | DISIS STAGE
J897 | 01 - North | 18.5 | DIS-17-2-PQ | Wind | 190 |  |  |  | ER | GRE | Prairie - Ramsey 230 kV line
J898 | 01 - North | 18.5 | DIS-17-2-PQ | Wind | 100 |  |  |  | ER | DPC | Rice - Beaver Creek 161kV line tap
J926 | 01 - North | 18.5 | DIS-17-2-PQ | Wind | 101.28 |  |  |  | ER | XEL | Pine Lake - Apple River 161 kV Line
IR24 | 02 - Nebraska | 18.5 | DIS-17-2-PQ | Wind | 56 |  |  |  | ER/NR | ALTW | New 69kV substation near Prescott REC
IR32 | 02 - Nebraska | 18.5 | DIS-17-2-PQ | Wind | 56 |  |  |  | ER/NR | ALTW | Murray Junction 69 kV substation
J836 | 02 - Nebraska | 18.5 | DIS-17-2-PQ | Wind | 200 |  |  |  | ER | ALTW | Ledyard 345kV Substation
J877 | 02 - Nebraska | 18.5 | DIS-17-2-PQ | Solar | 250 |  |  |  | ER/NR | MEC | Obrien - Kossuth 345kV Line (J529 & J590 New Substation) | DISIS STAGE
GIA-83 | 03 - Central | 18.5 | DIS-17-2-PQ | Wind | 1031 |  |  |  | ER/NR | AECI | McCredie 345 kV
GIA-85 | 03 - Central | 18.5 | DIS-17-2-PQ | Solar/Battery | 447.3 |  |  |  | ER/NR | AECI | Morgan 345 kV | DISIS STAGE
GIA-86 | 03 - Central | 18.5 | DIS-17-2-PQ | Solar | 103.68 |  |  |  | ER/NR | AECI | Thomas Hill 69 kV
GIA-90 | 03 - Central | 18.5 | DIS-17-2-PQ | Solar | 108 |  |  |  | ER/NR | AECI | Montgomery City 161 kV
GIA-91 | 03 - Central | 18.5 | DIS-17-2-PQ | Solar | 104.4 |  |  |  | ER/NR | AECI | Sedalia 69 kV
GIA-93 | 03 - Central | 18.5 | DIS-17-2-PQ | Solar | 100 |  |  |  | ER/NR | AECI | Palmyra 161 kV
GIA-95 | 03 - Central | 18.5 | DIS-17-2-PQ | Wind | 252 |  |  |  | ER/NR | AECI | Jasper-Morgan 345 kV
GEN-2017-010 | 01 - North | 18 | DIS-17-1 | Wind | 200.1 |  |  |  | ER | WAPA | Rhame 230 kV Sub | FACILITY STUDY STAGE
GEN-2017-014 | 01 - North | 18 | DIS-17-1 | Wind | 300 |  |  |  | ER | WAPA | Philip Tap 230 kV | FACILITY STUDY STAGE
GEN-2017-048 | 01 - North | 18 | DIS-17-1 | Wind | 300 |  |  |  | ER | WAPA | Neset 230 kV Substation | FACILITY STUDY STAGE
GEN-2017-094 | 01 - North | 18 | DIS-17-1 | Wind | 200 |  |  |  | ER | WAPA | Fort Thompson-Huron 230 kV | FACILITY STUDY STAGE
GEN-2017-097 | 01 - North | 18 | DIS-17-1 | Solar | 128 |  |  |  | ER | WAPA | Underwood 115 kV Sub | FACILITY STUDY STAGE
GEN-2017-004 | 03 - Central | 18 | DIS-17-1 | Wind | 201.6 |  |  |  | ER | SUNC | Elm Creek - Summit 345 kV | FACILITY STUDY STAGE
GEN-2017-005 | 03 - Central | 18 | DIS-17-1 | Wind | 190 |  |  |  | ER | WERE | Marmaton - Litchfield 161 kV | FACILITY STUDY STAGE
GEN-2017-018 | 03 - Central | 18 | DIS-17-1 | Solar | 189 |  |  |  | ER/NR | SUNC | Thistle 345 kV sub | FACILITY STUDY STAGE
GEN-2017-022 | 03 - Central | 18 | DIS-17-1 | Solar | 65 |  |  |  | ER/NR | WERE | Altoona- NE Parson 138kV | FACILITY STUDY STAGE
GEN-2017-068 | 03 - Central | 18 | DIS-17-1 | Solar | 103.5 |  |  |  | ER/NR | WERE | Gordon Evans 138kV Substation | FACILITY STUDY STAGE
GEN-2017-086 | 03 - Central | 18 | DIS-17-1 | Wind | 150 |  |  |  | ER | WERE | Viola 345kV | FACILITY STUDY STAGE
GEN-2016-037 | 04 - Southeast | 18 | DIS-17-1 | Wind | 300 |  |  |  | ER | AEPW | Chisholm-Gracemont 345kV | FACILITY STUDY STAGE
GEN-2017-011 | 04 - Southeast | 18 | DIS-17-1 | Solar | 151.8 |  |  |  | ER | OKGE | Badger-Woodward EHV Dbl Ckt 345kV | FACILITY STUDY STAGE
GEN-2017-023 | 04 - Southeast | 18 | DIS-17-1 | Solar | 85 |  |  |  | ER/NR | WFEC | Hugo Power Plant 138 kV Sub | FACILITY STUDY STAGE
GEN-2017-027 | 04 - Southeast | 18 | DIS-17-1 | Wind | 140 |  |  |  | ER | OKGE | Pooleville-Ratliff (Carter County) 138kV | FACILITY STUDY STAGE
GEN-2017-036 | 04 - Southeast | 18 | DIS-17-1 | Solar | 100 |  |  |  | ER | WFEC | Snyder - Cache 138 kV | FACILITY STUDY STAGE
GEN-2017-040 | 04 - Southeast | 18 | DIS-17-1 | Solar | 200.1 |  |  |  | ER | OKGE | Canadian River-Muskogee and Muskogee-Seminole 345kV | FACILITY STUDY STAGE
GEN-2017-057 | 04 - Southeast | 18 | DIS-17-1 | Solar | 72.5 |  |  |  | ER | AEPW | Hosston 69kV | FACILITY STUDY STAGE
GEN-2017-061 | 04 - Southeast | 18 | DIS-17-1 | Solar | 101.5 |  |  |  | ER/NR | GRDA | GRDA1 to CLARMR 5 161kV line | FACILITY STUDY STAGE
GEN-2017-071 | 04 - Southeast | 18 | DIS-17-1 | Solar | 124.7 |  |  |  | ER | OKGE | Greenwood 138kV sub | FACILITY STUDY STAGE
GEN-2017-072 | 04 - Southeast | 18 | DIS-17-1 | Solar | 52.2 |  |  |  | ER | OKGE | Greenwood 138kV sub | FACILITY STUDY STAGE
GEN-2017-073 | 04 - Southeast | 18 | DIS-17-1 | Solar | 72.5 |  |  |  | ER | GRDA | Dry Gulch 161kV sub | FACILITY STUDY STAGE
GEN-2017-074 | 04 - Southeast | 18 | DIS-17-1 | Solar | 72.5 |  |  |  | ER | AEPW | Pryor Junction 138kV sub | FACILITY STUDY STAGE
GEN-2017-075 | 04 - Southeast | 18 | DIS-17-1 | Solar | 200 |  |  |  | ER | OKGE | Hugo-Sunnyside 345 kV | FACILITY STUDY STAGE
GEN-2017-076 | 04 - Southeast | 18 | DIS-17-1 | Solar | 52.2 |  |  |  | ER | AEPW | Chamber Springs 161kV sub | FACILITY STUDY STAGE
GEN-2017-077 | 04 - Southeast | 18 | DIS-17-1 | Solar | 124.7 |  |  |  | ER | AEPW | Explorer Claremore Tap EXCLART4 | FACILITY STUDY STAGE
GEN-2017-092 | 04 - Southeast | 18 | DIS-17-1 | Solar | 200 |  |  |  | ER | OKGE | Canadian River-Muskogee and Muskogee-Seminole 345kV | FACILITY STUDY STAGE
GEN-2017-033 | 05 - Southwest | 18 | DIS-17-1 | Wind | 200 |  |  |  | ER/NR | AEPW | Oklaunion 345 kV sub | FACILITY STUDY STAGE
GEN-2017-047 | 05 - Southwest | 18 | DIS-17-1 | Wind | 102 |  |  |  | ER/NR | SPS | Cole 115kV | FACILITY STUDY STAGE
GEN-2017-100 | 05 - Southwest | 18 | DIS-17-1 | Solar | 102.6 |  |  |  | ER/NR | SPS | Texas County 115kV | FACILITY STUDY STAGE
BEPCNDPW1 | 01 - North | 17.5 | DIS-17-1-PQ | Wind | 5 |  |  |  | ER | BEPC-SPP | NELSON 7
GEN-2016-036 | 01 - North | 17 | DIS-16-2 | Wind | 44.6 |  |  |  | ER | WAPA | Granite Falls 115kV substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-087 | 01 - North | 17 | DIS-16-2 | Wind | 98.9 |  |  |  | ER | WAPA | Bismark-Glenham 230 kV line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-094 | 01 - North | 17 | DIS-16-2 | Wind | 200 |  |  |  | ER | WAPA | Tap Ft Thompson - Oahe 230kV Line (Single Circuit) | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-130 | 01 - North | 17 | DIS-16-2 | Wind | 202 |  |  |  | ER | WAPA | Leland Olds 345 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-074 | 02 - Nebraska | 17 | DIS-16-2 | Wind | 200 |  |  |  | ER | NPPD | Sweetwater 345kV | IA PENDING
GEN-2016-147 | 02 - Nebraska | 17 | DIS-16-2 | Solar | 40 |  |  |  | ER | NPPD | Sidney 115 kV Sub | IA PENDING
GEN-2016-111 | 03 - Central | 17 | DIS-16-2 | Wind | 302 |  |  |  | ER | WERE | Reno - Summit 345kV | IA FULLY EXECUTED/ON SUSPENSION
GEN-2016-115 | 03 - Central | 17 | DIS-16-2 | Wind | 300 |  |  |  | ER | KCPL | Nebraska City-Mullen Creek (Holt County MO) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-149 | 03 - Central | 17 | DIS-16-2 | Wind | 302 |  |  |  | ER | WERE | Stranger Creek 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-150 | 03 - Central | 17 | DIS-16-2 | Wind | 302 |  |  |  | ER | WERE | Stranger Creek 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-153 | 03 - Central | 17 | DIS-16-2 | Wind | 134 |  |  |  | ER | WERE | Viola 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-157 | 03 - Central | 17 | DIS-16-2 | Wind | 252 |  |  |  | ER | KCPL | West Gardner 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-158 | 03 - Central | 17 | DIS-16-2 | Wind | 252 |  |  |  | ER | KCPL | West Gardner 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-160 | 03 - Central | 17 | DIS-16-2 | Battery | 20 |  |  |  | ER/NR | MIDW | Post Rock 230kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-176 | 03 - Central | 17 | DIS-16-2 | Wind | 302 |  |  |  | ER | WERE | Stranger Creek 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-091 | 04 - Southeast | 17 | DIS-16-2 | Wind | 303.6 |  |  |  | ER | AEPW | Gracemont-Lawton East Side 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-095 | 04 - Southeast | 17 | DIS-16-2 | Wind | 200 |  |  |  | ER/NR | AEPW | Gracemont-Lawton East Side 345kV | IA PENDING
GEN-2016-097 | 04 - Southeast | 17 | DIS-16-2 | Wind | 100 |  |  |  | ER/NR | AEPW | Tap Southwestern-Fletcher Tap 138kV | IA PENDING
GEN-2016-102 | 04 - Southeast | 17 | DIS-16-2 | Wind | 150.9 |  |  |  | ER/NR | OKGE | Blue River 138kV | IA FULLY EXECUTED/ON SUSPENSION
GEN-2016-118 | 04 - Southeast | 17 | DIS-16-2 | Wind | 288 |  |  |  | ER | WFEC | Dover Switchyard 138 kV Line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-119 | 04 - Southeast | 17 | DIS-16-2 | Wind | 600 |  |  |  | ER | OKGE | Spring Creek-Sooner 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-126 | 04 - Southeast | 17 | DIS-16-2 | Wind | 172.5 |  |  |  | ER/NR | OKGE | Arbuckle 138kV substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-128 | 04 - Southeast | 17 | DIS-16-2 | Wind | 176 |  |  |  | ER | OKGE | Woodring 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-131 | 04 - Southeast | 17 | DIS-16-2 | Wind | 2.5 |  |  |  | ER | OKGE | Minco 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-132 | 04 - Southeast | 17 | DIS-16-2 | Wind | 6.12 |  |  |  | ER | AEPW | Sweetwater 230kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-133 | 04 - Southeast | 17 | DIS-16-2 | Wind | 187.5 |  |  |  | ER | AEPW | Riverside 345kV Substation | IA PENDING
GEN-2016-134 | 04 - Southeast | 17 | DIS-16-2 | Wind | 187.5 |  |  |  | ER | AEPW | Riverside 345kV Substation | IA PENDING
GEN-2016-137 | 04 - Southeast | 17 | DIS-16-2 | Wind | 187.5 |  |  |  | ER | AEPW | Riverside 345kV Substation | IA PENDING
GEN-2016-138 | 04 - Southeast | 17 | DIS-16-2 | Wind | 187.5 |  |  |  | ER | AEPW | Riverside 345kV Substation | IA PENDING
GEN-2016-139 | 04 - Southeast | 17 | DIS-16-2 | Wind | 100 |  |  |  | ER | AEPW | Riverside 345kV Substation | IA PENDING
GEN-2016-141 | 04 - Southeast | 17 | DIS-16-2 | Wind | 350 |  |  |  | ER | AEPW | Riverside 345kV Substation | IA PENDING
GEN-2016-142 | 04 - Southeast | 17 | DIS-16-2 | Wind | 350 |  |  |  | ER | AEPW | Riverside 345kV Substation | IA PENDING
GEN-2016-145 | 04 - Southeast | 17 | DIS-16-2 | Wind | 175 |  |  |  | ER | AEPW | Riverside 345kV Substation | IA PENDING
GEN-2016-146 | 04 - Southeast | 17 | DIS-16-2 | Wind | 175 |  |  |  | ER | AEPW | Riverside 345kV Substation | IA PENDING
GEN-2016-167 | 04 - Southeast | 17 | DIS-16-2 | Solar | 73.5 |  |  |  | ER/NR | AEPW | Lieberman - North Benton 138 kV Line | IA FULLY EXECUTED/ON SCHEDULE
ASGI-2016-010 | 05 - Southwest | 17 | DIS-16-2 | Wind | 90 |  |  |  | ER | SPS | TEXAS_CNTY 3
GEN-2016-121 | 05 - Southwest | 17 | DIS-16-2 | Solar | 110 |  |  |  | ER | SPS | Roadrunner 115kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-177 | 05 - Southwest | 17 | DIS-16-2 | Gas Turbine | 17 |  |  |  | ER | SPS | XTO-Cornell 115 kV station | IA FULLY EXECUTED/ON SCHEDULE
ASGI-2017-006GIA-53 | 03 - Central | 16.5 | Dis-16-2-PQ | Wind | 238 |  |  |  | ER/NR | AECI | 5MARYVL
GEN-2015-089 | 01 - North | 16 | DIS-16-1 | Wind | 200 |  |  |  | ER | BEPC-SPP |  | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-004 | 01 - North | 16 | DIS-16-1 | Wind | 202 |  |  |  | ER/NR | WAPA | Basin Electric 230 kV | IA FULLY EXECUTED/ON SUSPENSION
GEN-2016-007 | 01 - North | 16 | DIS-16-1 | Wind | 100.05 |  |  |  | ER | WAPA | Valley City 115 kV | IA FULLY EXECUTED/ON SUSPENSION
GEN-2016-021 | 02 - Nebraska | 16 | DIS-16-1 | WIND | 300 |  |  |  | ER | NPPD | Hoskins 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-043 | 02 - Nebraska | 16 | DIS-16-1 | Wind | 230 |  |  |  | ER | NPPD | Hoskins 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-050 | 02 - Nebraska | 16 | DIS-16-1 | Wind | 250.7 |  |  |  | ER | NPPD | Axtell â€“ Post Rock 345 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-075 | 02 - Nebraska | 16 | DIS-16-1 | Wind | 50 |  |  |  | ER | WAPA | Fort Thompson-Grand Island (Grand Prairie) 345kV | IA PENDING
GEN-2016-009 | 03 - Central | 16 | DIS-16-1 | Steam Turbine | 29 |  |  |  | ER | OKGE | Osage 69 kV Sub | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-016 | 03 - Central | 16 | DIS-16-1 | Wind | 78.2 |  |  |  | ER | MIDW | North Kinsley 115 kV | IA FULLY EXECUTED/ON SUSPENSION
GEN-2016-046 | 03 - Central | 16 | DIS-16-1 | Wind | 299 |  |  |  | ER | SUNC | Clark County-Ironwood 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-073 | 03 - Central | 16 | DIS-16-1 | WIND | 220 |  |  |  | ER | WERE | Thistle-Wichita Dbl Ckt (Buffalo Flats) 345kV | IA FULLY EXECUTED/ON SUSPENSION
GEN-2015-036 | 04 - Southeast | 16 | DIS-16-1 | Wind | 303.6 |  |  |  | ER | OKGE | Johnston County 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-095 | 04 - Southeast | 16 | DIS-16-1 | Wind | 176 |  |  |  | ER | WFEC | Tap Mooreland - Knob Hill 138kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-003 | 04 - Southeast | 16 | DIS-16-1 | Wind | 248.4 |  |  |  | ER | OKGE | Badger-Woodward EHV Dbl Ckt 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-020 | 04 - Southeast | 16 | DIS-16-1 | WIND | 150 |  |  |  | ER | WFEC | Moreland 138kV Substation | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-022 | 04 - Southeast | 16 | DIS-16-1 | Wind | 151.8 |  |  |  | ER | OKGE |  | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-030 | 04 - Southeast | 16 | DIS-16-1 | Solar | 100 |  |  |  | ER/NR | OKGE | Brown 138kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-031 | 04 - Southeast | 16 | DIS-16-1 | Wind | 1.5 |  |  |  | ER | OKGE | Rose Hill (Open Sky)-Sooner (Ranch Road) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-032 | 04 - Southeast | 16 | DIS-16-1 | Wind | 200 |  |  |  | ER/NR | OKGE | Crescent Substation 138 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-045 | 04 - Southeast | 16 | DIS-16-1 | Wind | 499.1 |  |  |  | ER | OKGE | Mathewson 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-051 | 04 - Southeast | 16 | DIS-16-1 | Wind | 9.8 |  |  |  | ER | AEPW | Clinton Junction-Weatherford Southeast 138kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-057 | 04 - Southeast | 16 | DIS-16-1 | Wind | 499.1 |  |  |  | ER | OKGE | Mathewson 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-061 | 04 - Southeast | 16 | DIS-16-1 | Wind | 250.7 |  |  |  | ER | OKGE | Sooner-Woodring 345 kV line | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-063 | 04 - Southeast | 16 | DIS-16-1 | Wind | 200 |  |  |  | ER/NR | OKGE | Hugo-Sunnyside 345 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-071 | 04 - Southeast | 16 | DIS-16-1 | Wind | 200.1 |  |  |  | ER | OKGE | Middleton Tap 138kV Substation | IA FULLY EXECUTED/ON SUSPENSION
ASGI-2016-004 | 05 - Southwest | 16 | DIS-16-1 | Wind | 10 |  |  |  | ER | SPS | Palo Duro 115kV
GEN-2015-082 | 05 - Southwest | 16 | DIS-16-1 | Wind | 200 |  |  |  | ER | OKGE | Beaver County - Woodward EHV Dbl Ckt (Badger) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-070 | 05 - Southwest | 16 | DIS-16-1 | Wind | 5.3 |  |  |  | ER | SPS | Martin 115 kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2015-088 | 02 - Nebraska | 15 | DIS-15-2 | Wind | 300 |  |  |  | ER/NR | NPPD | Tobias 345kV Substation | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-069 | 03 - Central | 15 | DIS-15-2 | Wind | 300 |  |  |  | ER | WERE | Union Ridge 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-090 | 03 - Central | 15 | DIS-15-2 | Wind | 219.99 |  |  |  | ER | WERE | Thistle-Wichita Dbl Ckt (Buffalo Flats) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-034 | 04 - Southeast | 15 | DIS-15-2 | Wind | 200 |  |  |  | ER | OKGE |  | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-045 | 04 - Southeast | 15 | DIS-15-2 | Battery | 20 |  |  |  | ER | AEPW | Lawton East Side-Sunnyside (Terry Road) 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2015-047 | 04 - Southeast | 15 | DIS-15-2 | Wind | 300 |  |  |  | ER | OKGE | Sooner 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-048 | 04 - Southeast | 15 | DIS-15-2 | Wind | 200 |  |  |  | ER | OKGE | Cleo Corner 138kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2015-052 | 04 - Southeast | 15 | DIS-15-2 | Wind | 300 |  |  |  | ER | WERE | Open Sky-Rose Hill 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2015-057 | 04 - Southeast | 15 | DIS-15-2 | Wind | 100.65 |  |  |  | ER | OKGE | Minco 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-062 | 04 - Southeast | 15 | DIS-15-2 | Wind | 4.5 |  |  |  | ER | OKGE | Breckinridge 138kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2015-063 | 04 - Southeast | 15 | DIS-15-2 | Wind | 300 |  |  |  | ER | OKGE | Woodring-Matthewson 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-066 | 04 - Southeast | 15 | DIS-15-2 | Wind | 248.4 |  |  |  | ER | OKGE | Sooner - Cleveland 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2015-092 | 04 - Southeast | 15 | DIS-15-2 | Wind | 250 |  |  |  | ER | AEPW | Lawton East Side-Sunnyside (Terry Road) 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2015-093 | 04 - Southeast | 15 | DIS-15-2 | Wind | 250 |  |  |  | ER | OKGE | Gracemont 345kV | IA FULLY EXECUTED/ON SCHEDULE
ASGI-2016-005NWE205 | 01 - North | 14.5 | DIS-15-2-PQ | Wind | 0.2 |  |  |  | ER | WAPA | Tap White Lake - Stickeny 69kV
ASGI-2016-007NWE208 | 01 - North | 14.5 | DIS-15-2-PQ | Wind | 0.2 |  |  |  | ER | WAPA | Kimball 69kV
GEN-2005-008IS | 01 - North | 14.5 | DIS-15-2-PQ | Wind | 0.5 |  |  |  | ER/NR | BEPC-SPP | Hilken 230kV [Ecklund 230kV]
GEN-2006-002IS | 01 - North | 14.5 | DIS-15-2-PQ | Wind | 2 |  |  |  | ER/NR | WAPA | Wessington Springs 230kV
GEN-2006-006IS | 01 - North | 14.5 | DIS-15-2-PQ | Wind | 10 |  |  |  | ER/NR | XEL | Marshall 115kV
GEN-2006-015IS | 01 - North | 14.5 | DIS-15-2-PQ | Wind | 0.5 |  |  |  | ER/NR | BEPC-SPP | Hilken 230kV [Ecklund 230kV]
GEN-2007-020IS | 01 - North | 14.5 | DIS-15-2-PQ | Wind | 16 |  |  |  | ER/NR | BEPC-SPP | Nelson 115kV
GEN-2008-008IS | 01 - North | 14.5 | DIS-15-2-PQ | Wind | 5 |  |  |  | ER/NR | WAPA | Nelson 115kV
GEN-2009-018IS | 01 - North | 14.5 | DIS-15-2-PQ | Wind | 0.5 |  |  |  | ER | BEPC-SPP | Groton 115kV
GEN-2009-020AIS | 01 - North | 14.5 | DIS-15-2-PQ | Wind | 0.4 |  |  |  | ER/NR | WAPA | Tripp Junction 115kV
GEN-2009-026IS | 01 - North | 14.5 | DIS-15-2-PQ | Wind | 3.5 |  |  |  | ER/NR | BEPC-SPP | Dickenson-Heskett 230kV
GEN-2010-003IS | 01 - North | 14.5 | DIS-15-2-PQ | Wind | 34 |  |  |  | ER/NR | BEPC-SPP | Wessington Springs 230kV
GEN-2014-001IS | 01 - North | 14.5 | DIS-15-2-PQ | Wind | 103.24 |  |  |  | ER | WAPA |  | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-006IS | 01 - North | 14.5 | DIS-15-2-PQ | Gas | 11.72 |  |  |  | ER/NR | BEPC-SPP | Williston 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
MPC02100 | 01 - North | 14.5 | DIS-15-2-PQ | Wind | 0.75 |  |  |  | ER | OTP | Center - Mandan 230 kV
GEN-2015-023 | 02 - Nebraska | 14 | DIS-15-1 | Wind | 300.72 |  |  |  | ER/NR | NPPD | Grand Prairie-Grand Island (Holt County NE) 345kV | IA FULLY EXECUTED/ON SCHEDULE
ASGI-2015-001 | 03 - Central | 14 | DIS-15-1 | Thermal | 6.13 |  |  |  | ER | SUNC | Ninnescah 115kV
GEN-2015-005 | 03 - Central | 14 | DIS-15-1 | Wind | 200.1 |  |  |  | ER | KCPL | Mullen Creek-Sibley (Ketchum) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-024 | 03 - Central | 14 | DIS-15-1 | Wind | 219.99 |  |  |  | ER | WERE | Thistle-Wichita Dbl Ckt (Buffalo Flats) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-025 | 03 - Central | 14 | DIS-15-1 | Wind | 219.98 |  |  |  | ER | WERE | Tap Thistle â€“ Wichita 345kV Dbl CKT | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2015-004 | 04 - Southeast | 14 | DIS-15-1 | Thermal | 54 |  |  |  | ER | GRDA
GEN-2015-001 | 04 - Southeast | 14 | DIS-15-1 | Wind | 200 |  |  |  | ER | OKGE |  | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-013 | 04 - Southeast | 14 | DIS-15-1 | Solar | 120 |  |  |  | ER/NR | WFEC | Snyder 138kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2014-032 | 02 - Nebraska | 13 | DIS-14-2 | Wind | 10.22 |  |  |  | ER/NR | NPPD | Meadow Grove 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-025 | 03 - Central | 13 | DIS-14-2 | Wind | 2.42 |  |  |  | ER | MIDW | Tap Nekoma - Bazine (Walnut Creek) 69kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-056 | 04 - Southeast | 13 | DIS-14-2 | Wind | 249.35 |  |  |  | ER | OKGE | Minco 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-064 | 04 - Southeast | 13 | DIS-14-2 | Wind | 248.4 |  |  |  | ER | OKGE | Otter 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-035 | 05 - Southwest | 13 | DIS-14-2 | Solar | 30 |  |  |  | ER | SPS | Chaves County 115kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2014-040 | 05 - Southwest | 13 | DIS-14-2 | Wind | 320 |  |  |  | ER | SPS | Castro 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-004 | 02 - Nebraska | 12 | DIS-14-1 | Wind | 3.96 |  |  |  | ER | NPPD | Steele City 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-013 | 02 - Nebraska | 12 | DIS-14-1 | Wind | 73.5 |  |  |  | ER/NR | LES | Meadow Grove 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-001 | 03 - Central | 12 | DIS-14-1 | Wind | 200.6 |  |  |  | ER | WERE | Tap Wichita - Emporia Energy Center 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2014-002 | 04 - Southeast | 12 | DIS-14-1 | Wind | 10.53 |  |  |  | ER | OKGE | Tatonga 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-005 | 04 - Southeast | 12 | DIS-14-1 | Wind | 5.67 |  |  |  | ER | OKGE | Minco 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2013-019 | 02 - Nebraska | 11 | DIS-13-2 | Wind | 73.6 |  |  |  | ER/NR | NPPD | Monolith 115kV | IA FULLY EXECUTED/ON SCHEDULE
ASGI-2013-005 | 05 - Southwest | 11 | DIS-13-2 | Wind | 1.65 |  |  |  | ER | SPS | FE Clovis 115kV
GEN-2013-002 | 02 - Nebraska | 10 | DIS-13-1 | Wind | 50.6 |  |  |  | ER/NR | NPPD | Monolith 115kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2013-008 | 02 - Nebraska | 10 | DIS-13-1 | Wind | 1.2 |  |  |  | ER | NPPD | Steele City 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2013-002 | 05 - Southwest | 10 | DIS-13-1 | Wind | 18.4 |  |  |  | ER | SPS | FE Tucumcari 115kV
ASGI-2013-003 | 05 - Southwest | 10 | DIS-13-1 | Wind | 18.4 |  |  |  | ER | SPS | FE Clovis 115kV
GEN-2012-024 | 03 - Central | 9 | DIS-12-2 | Wind | 180 |  |  |  | ER | SUNC | Clark County 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2012-032 | 04 - Southeast | 9 | DIS-12-2 | Wind | 299 |  |  |  | ER | OKGE |  | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2012-033 | 04 - Southeast | 9 | DIS-12-2 | Wind | 98.82 |  |  |  | ER | OKGE | Breckinridge 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2012-041 | 04 - Southeast | 9 | DIS-12-2 | CT | 121.5 |  |  |  | ER | OMPA |  | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2012-002 | 05 - Southwest | 9 | DIS-12-2 | Wind | 18.15 |  |  |  | ER | SPS | FE-Clovis Interchange 115kV
GEN-2003-021N | 02 - Nebraska | 8 | PQ | Wind | 75 |  |  |  | ER | NPPD | Ainsworth Wind Tap 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
NPPDBuffaloCountySolar | 02 - Nebraska | 8 | PQ | Solar | 10 |  |  |  | ER | NPPD | Kearney Northeast
NPPDBurtCountyWind | 02 - Nebraska | 8 | PQ | Wind | 20 |  |  |  | ER | NPPD | Tekamah & Oakland 115kV
ASGI-2012-006 | 03 - Central | 8 | DIS-12-1 | Steam | 22.5 |  |  |  | ER | SUNC | Tap Hugoton - Rolla 69kV
GEN-2001-039M | 03 - Central | 8 | PQ | Wind | 100 |  |  |  | ER | SUNC | Central Plains Tap 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2002-004 | 03 - Central | 8 | PQ | Wind | 153 |  |  |  | ER | WERE | Latham 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2003-006A | 03 - Central | 8 | PQ | Wind | 201 |  |  |  | ER | SUNC | Elm Creek 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2005-012 | 03 - Central | 8 | PQ | Wind | 248.4 |  |  |  | ER | SUNC |  | IA FULLY EXECUTED/COMMERCIAL OPERATION
GrayCountyWindMontezuma | 03 - Central | 8 | PQ | Wind | 110 |  |  |  | ER | SUNC
ASGI-2010-006GIA-27 | 04 - Southeast | 8 | PQ | Wind | 150 |  |  |  | ER | AECI | Remington 138kV
GEN-2006-002 | 04 - Southeast | 8 | PQ | Wind | 100.8 |  |  |  | ER | AEPW | Sweetwater 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-035 | 04 - Southeast | 8 | PQ | Wind | 132 |  |  |  | ER | AEPW |  | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-043 | 04 - Southeast | 8 | PQ | Wind | 99 |  |  |  | ER | AEPW |  | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2012-004 | 04 - Southeast | 8 | DIS-12-1 | Wind | 40.8 |  |  |  | ER/NR | OKGE | Pooleville-Ratliff (Carter County) 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-026 | 05 - Southwest | 8 | PQ | Gas | 603.98 |  |  |  | ER | SPS |  | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-044 | 05 - Southwest | 8 | PQ | Wind | 370 |  |  |  | ER | SPS | Hitchland 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-037 | 04 - Southeast | 7 | DIS-11-2 | Wind | 6.6 |  |  |  | ER | WFEC | Blue Canyon 5 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-054 | 04 - Southeast | 7 | DIS-11-2 | Wind | 300 |  |  |  | ER | OKGE | Cimarron 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-008 | 03 - Central | 6 | DIS-11-1 | Wind | 600 |  |  |  | ER | SUNC |  | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-010 | 04 - Southeast | 6 | DIS-11-1 | Wind | 100.8 |  |  |  | ER | OKGE | Minco 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-019 | 04 - Southeast | 6 | DIS-11-1 | Wind | 175 |  |  |  | ER/NR | OKGE | Woodward EHV 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2011-020 | 04 - Southeast | 6 | DIS-11-1 | Wind | 165.6 |  |  |  | ER/NR | OKGE | Woodward EHV 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2011-022 | 05 - Southwest | 6 | DIS-11-1 | Wind | 299 |  |  |  | ER | SPS | Hitchland 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2010-040 | 04 - Southeast | 5 | DIS-10-2 | Wind | 300 |  |  |  | ER | OKGE | Cimarron 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-001 | 05 - Southwest | 5 | DIS-10-2 | Wind | 300 |  |  |  | ER | OKGE | Hitchland-Woodward EHV Dbl Ckt (Beaver County) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-005 | 03 - Central | 4 | DIS-10-1 | Wind | 299.2 |  |  |  | ER | WERE | Viola 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2008-022 | 05 - Southwest | 4 | DIS-10-1 | Wind | 299.65 |  |  |  | ER | SPS | Eddy County-Tolk (Crossroads) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-047 | 05 - Southwest | 4 | DIS-10-1 | Wind | 263.13 |  |  |  | ER | OKGE | Hitchland-Woodward EHV Dbl Ckt (Beaver County) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-014 | 05 - Southwest | 4 | DIS-10-1 | Wind | 358.8 |  |  |  | ER | SPS | Hitchland 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2008-086N02 | 02 - Nebraska | 3 | DIS-09-1 | Wind | 201 |  |  |  | ER | NPPD | Meadow Grove 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-124 | 03 - Central | 3 | DIS-09-1 | Wind | 200.1 |  |  |  | ER | SUNC | Clark County-Spearville Ckt 1 (Ironwood) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-051 | 05 - Southwest | 3 | DIS-09-1 | Wind | 161 |  |  |  | ER | SPS | Potter County 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2007-025 | 03 - Central | 2 | ICS1 | Wind | 299.2 |  |  |  | ER | WERE | Viola 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2007-043 | 04 - Southeast | 2 | ICS1 | Wind | 200 |  |  |  | ER | OKGE | Minco 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2007-044 | 04 - Southeast | 2 | ICS1 | Wind | 299.2 |  |  |  | ER | OKGE | Tatonga 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION

## Constraints Summary
Group | Service Type | Constraint Type | Constraints | Seasons | Most Severe Contingency | MVA Rate A | MVA Rate B | BC Loading % | TC Loading % | TC Voltage | VMIN | VMAX | Upgrade Name
00NR | NRIS | Thermal | 514901 CIMARON7 345 997944 CIMARON1 _1 138 1 | 23SP | P13:138-345:OKGE:BKRBKR_3W021:::: |  | 478 | 89.54 | 106.39 |  |  |  | Multi - Minco - Pleasant Valley - Draper 345 kV (NTC 210616, NTC 210656, NTC 210670)
00NR | NRIS | Thermal | 526524 WOLFFORTH 3 115 526736 TERRY_CNTY 3 115 1 | 26SP | P42:345:SPS:YOAKUM:J18####:SLG1:EHV: |  | 164 | 97.56 | 101.03 |  |  |  | Wolfforth to Terry County 115 kV Line Model Correction
00NR | NRIS | Thermal | 539666 GBENDTP3 115 539692 SEWARD 3 115 1 | 23SP, 26SP | 532871 CIRCLE 6 230 763862 G19-054-TAP 230 1 |  | 101 | 33.27 | 107.54 |  |  |  | Great Bend Tap to Seward 115 kV Terminal Equipment Upgrade
00NR | NRIS | Thermal | 539692 SEWARD 3 115 539696 ST-JOHN3 115 1 | 23SP | 532871 CIRCLE 6 230 763862 G19-054-TAP 230 1 |  | 101 | 17.62 | 101.17 |  |  |  | Seward to St. John 115 kV Terminal Equipment Upgrade
00NR | NRIS | Thermal | 602006 SHEYNNE4 230 652435 FARGO 4 230 1 | 23SP | P12:345:MPC:JAMESTOWN-BISON:JAMESTN3:BISON 3 |  | 342 | 88.01 | 100.24 |  |  |  | Fargo 230 kV Terminal Upgrade (NTC ID 210715)
00NR | NRIS | Thermal | 640072 BATTLCR7 115 640115 CO.LINE7 115 1 | 26WP | P42:345:NPPD:BKR-MOR-3306::::: |  | 193 | 16.26 | 106.81 |  |  |  | Battle Creek to County Line 115 kV Line Rebuild
00NR | NRIS | Thermal | 640072 BATTLCR7 115 640296 NORFK.N7 115 1 | 26WP | P42:345:NPPD:BKR-MOR-3306::::: |  | 193 | 11.92 | 104.08 |  |  |  | Battle Creek to Norfork North 115 kV Line Rebuild
00NR | NRIS | Thermal | 640115 CO.LINE7 115 640521 ANTELOPE 7 115 1 | 26WP | P42:345:NPPD:BKR-MOR-3306::::: |  | 193 | 16.58 | 108.71 |  |  |  | County Line to Antelope 115 kV Line Rebuild
00NR | NRIS | Thermal | 652442 GARRISN7 115 659543 PICKCITY-RR7 115 1 | 23SP, 26SP | P12:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1 |  | 121 | 90.08 | 104.19 |  |  |  | Beulah to Garrison 115 kV Line Rebuild
00NR | NRIS | Thermal | 659300 STANTN.T-BE7 115 659543 PICKCITY-RR7 115 1 | 23SP, 26SP | P12:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1 |  | 121 | 90.87 | 104.47 |  |  |  | Beulah to Garrison 115 kV Line Rebuild
00NR | NRIS | Thermal | 659300 STANTN.T-BE7 115 661011 BEULAH27 115 1 | 26WP | P12:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1 |  | 132 | 93.18 | 100.18 |  |  |  | Beulah to Garrison 115 kV Line Rebuild
01ALL | ERIS | Thermal | 652424 BELFELD3 345 996760 BEF KU2A _1 230 1 | 26L | P23:345:UMZW:# 3576 #:: BE IN ND. BREAKER FAULT (1282):HV: |  | 312 | <90% | 111.68 | - | - | - | Replace Belfield 345-230-14 kV First Transformer
01ALL | ERIS | Thermal | 652511 GAVINS 7 115 660006 YANKTON JCT7 115 1 | 26L | P42:345:UMZW:# 1932 #:: SC2 IN IA. SC2 345 KV BREAKER FAILURE:EHV: |  | 121 | 111.91 | 105.99 | - | - | - | Rebuild Gavins to Yankton JCT_115 kV
01ALL | ERIS | Thermal | 652567 DENISON4 230 652583 DENISON8 69.0 2 | 23SP | P13:161-69:WAPA:DENISON5-DENISON8:KV2A |  | 150 | <90% | 100.24 | - | - | - | Add a third 230-69 kV transformer at Denison
01ALL | ERIS | Thermal | 652583 DENISON8 69.0 659912 J6BOYER_-NI8 69.0 1 | 23SP, 26L, 26SP, 26WP | P21:161:UMZW:# 1879 #: EXI IN IA. OPENING OF A LINE SECTION WO A FAULT (EXI-AT TAP) |  | 117 | 109.48 | 127.17 | - | - | - | Build a second 69 kV line from Denison to Boyer
01ALL | ERIS | Thermal | 652583 DENISON8 69.0 659912 J6BOYER_-NI8 69.0 1 | 23SP, 26L, 26SP, 26WP | P21:161:UMZW:# 1879 #: EXI IN IA. OPENING OF A LINE SECTION WO A FAULT (EXI-AT TAP) |  | 117 | 109.48 | 127.17 | - | - | - | Upgrade the terminal at Denison 69 kV
01ALL | ERIS | Thermal | 652626 UTICAJC7 115 660026 NAPA JCT 7 115 1 | 23SP, 26SP, 26WP | P42:345:UMZW:# 1932 #:: SC2 IN IA. SC2 345 KV BREAKER FAILURE:EHV: |  | 141 | 115.86 | 117.2 | - | - | - | Rebuild the existing Utica Jct to Napa Jct 115 kV line
01ALL | ERIS | Thermal | 652626 UTICAJC7 115 660026 NAPA JCT 7 115 1 | 23SP, 26SP, 26WP | P42:345:UMZW:# 1932 #:: SC2 IN IA. SC2 345 KV BREAKER FAILURE:EHV: |  | 141 | 115.86 | 117.2 | - | - | - | Upgrade the terminal at Utica Junction
01ALL | ERIS | Thermal | 655940 MONT -MW7 115 655941 STRNDAHL-MW7 115 1 | 23SP, 26L, 26SP, 26WP | 655931 BLKTLTAP-MW7 115 655941 STRNDAHL-MW7 115 1 |  | 115 | <90% | 173.52 | - | - | - | Rebuild Mont to STRNDAHL Line_115kV
01ALL | ERIS | Thermal | 659854 K335AMAI-NI8 69.0 659897 K338WTCT-NI8 69.0 1 | 23SP, 26SP | System Intact | 34.8 |  | <90% | 105.94 | - | - | - | Rebuild the existing K335AMAI-NI8 to Boyer 69 kV line
01ALL | ERIS | Thermal | 659854 K335AMAI-NI8 69.0 659912 J6BOYER_-NI8 69.0 1 | 23SP, 26SP | System Intact | 40 |  | <90% | 102.3 | - | - | - | Rebuild the existing K335AMAI-NI8 to K338WTCT-NI8 69 kV line
01ALL | ERIS | Thermal | 660006 YANKTON JCT7 115 660026 NAPA JCT 7 115 1 | 26L | P42:345:UMZW:# 1932 #:: SC2 IN IA. SC2 345 KV BREAKER FAILURE:EHV: |  | 120 | 104.79 | 100.08 | - | - | - | Rebuild the existing Yankton Jct to Napa Jct 115 kV line
01ALL | ERIS | Voltage | CHESTER-ER8 | 23SP | P23:345:UMZW:# 2423 #:: GI IN NE. GI 1596 BKR FAULT:EHV: |  |  |  |  | 0.8815 | 0.9 | 1.05 | Add a 30 MVAR Switched Shunt Capacitor at Hanlon 69 kV
01ALL | ERIS | Voltage | COLTON-ER8 | 23SP | P23:345:UMZW:# 2423 #:: GI IN NE. GI 1596 BKR FAULT:EHV: |  |  |  |  | 0.8978 | 0.9 | 1.05 | Add a 30 MVAR Switched Shunt Capacitor at Hanlon 69 kV
01ALL | ERIS | Voltage | DOLTON-ER8 | 23SP | P23:345:UMZW:# 2423 #:: GI IN NE. GI 1596 BKR FAULT:EHV: |  |  |  |  | 0.8605 | 0.9 | 1.05 | Add a 30 MVAR Switched Shunt Capacitor at Hanlon 69 kV
01ALL | ERIS | Voltage | FEDORA-ER8 | 23SP | P23:345:UMZW:# 2423 #:: GI IN NE. GI 1596 BKR FAULT:EHV: |  |  |  |  | 0.8868 | 0.9 | 1.05 | Add a 30 MVAR Switched Shunt Capacitor at Hanlon 69 kV
01ALL | ERIS | Voltage | HOWARDCI-ER8 | 23SP | P23:345:UMZW:# 2423 #:: GI IN NE. GI 1596 BKR FAULT:EHV: |  |  |  |  | 0.8773 | 0.9 | 1.05 | Add a 30 MVAR Switched Shunt Capacitor at Hanlon 69 kV
01ALL | ERIS | Voltage | HOWARD-ER8 | 23SP | P23:345:UMZW:# 2423 #:: GI IN NE. GI 1596 BKR FAULT:EHV: |  |  |  |  | 0.8767 | 0.9 | 1.05 | Add a 30 MVAR Switched Shunt Capacitor at Hanlon 69 kV
01ALL | ERIS | Voltage | HUMBOLT-ER8 | 23SP | P23:345:UMZW:# 2423 #:: GI IN NE. GI 1596 BKR FAULT:EHV: |  |  |  |  | 0.8981 | 0.9 | 1.05 | Add a 30 MVAR Switched Shunt Capacitor at Hanlon 69 kV
01ALL | ERIS | Voltage | INDMARIN-ER8 | 23SP | P23:345:UMZW:# 2423 #:: GI IN NE. GI 1596 BKR FAULT:EHV: |  |  |  |  | 0.8484 | 0.9 | 1.05 | Add a 30 MVAR Switched Shunt Capacitor at Hanlon 69 kV
01ALL | ERIS | Voltage | LOOMIS-ER8 | 23SP | P23:345:UMZW:# 2423 #:: GI IN NE. GI 1596 BKR FAULT:EHV: |  |  |  |  | 0.8916 | 0.9 | 1.05 | Add a 30 MVAR Switched Shunt Capacitor at Hanlon 69 kV
01ALL | ERIS | Voltage | LYONS-ER8 | 23SP | P23:345:UMZW:# 2423 #:: GI IN NE. GI 1596 BKR FAULT:EHV: |  |  |  |  | 0.8974 | 0.9 | 1.05 | Add a 30 MVAR Switched Shunt Capacitor at Hanlon 69 kV
01ALL | ERIS | Voltage | MARION-ER8 | 23SP | P23:345:UMZW:# 2423 #:: GI IN NE. GI 1596 BKR FAULT:EHV: |  |  |  |  | 0.8527 | 0.9 | 1.05 | Add a 30 MVAR Switched Shunt Capacitor at Hanlon 69 kV
01ALL | ERIS | Voltage | MONTROSE-ER8 | 23SP | P23:345:UMZW:# 2423 #:: GI IN NE. GI 1596 BKR FAULT:EHV: |  |  |  |  | 0.8964 | 0.9 | 1.05 | Add a 30 MVAR Switched Shunt Capacitor at Hanlon 69 kV
01ALL | ERIS | Voltage | MOS-CHST-ER8 | 23SP | P23:345:UMZW:# 2423 #:: GI IN NE. GI 1596 BKR FAULT:EHV: |  |  |  |  | 0.8815 | 0.9 | 1.05 | Add a 30 MVAR Switched Shunt Capacitor at Hanlon 69 kV
01ALL | ERIS | Voltage | MOS-CLTN-ER8 | 23SP | P23:345:UMZW:# 2423 #:: GI IN NE. GI 1596 BKR FAULT:EHV: |  |  |  |  | 0.8978 | 0.9 | 1.05 | Add a 30 MVAR Switched Shunt Capacitor at Hanlon 69 kV
01ALL | ERIS | Voltage | MOS-HMPA-ER8 | 23SP | P23:345:UMZW:# 2423 #:: GI IN NE. GI 1596 BKR FAULT:EHV: |  |  |  |  | 0.8863 | 0.9 | 1.05 | Add a 30 MVAR Switched Shunt Capacitor at Hanlon 69 kV
01ALL | ERIS | Voltage | MOS-INDM-ER8 | 23SP | P23:345:UMZW:# 2423 #:: GI IN NE. GI 1596 BKR FAULT:EHV: |  |  |  |  | 0.853 | 0.9 | 1.05 | Add a 30 MVAR Switched Shunt Capacitor at Hanlon 69 kV
01ALL | ERIS | Voltage | MOS-LMIS-ER8 | 23SP | P23:345:UMZW:# 2423 #:: GI IN NE. GI 1596 BKR FAULT:EHV: |  |  |  |  | 0.8968 | 0.9 | 1.05 | Add a 30 MVAR Switched Shunt Capacitor at Hanlon 69 kV
01ALL | ERIS | Voltage | MOS-MDCY-ER8 | 23SP | P23:345:UMZW:# 2423 #:: GI IN NE. GI 1596 BKR FAULT:EHV: |  |  |  |  | 0.8829 | 0.9 | 1.05 | Add a 30 MVAR Switched Shunt Capacitor at Hanlon 69 kV
01ALL | ERIS | Voltage | MOS-NMAR-ER8 | 23SP | P23:345:UMZW:# 2423 #:: GI IN NE. GI 1596 BKR FAULT:EHV: |  |  |  |  | 0.8848 | 0.9 | 1.05 | Add a 30 MVAR Switched Shunt Capacitor at Hanlon 69 kV
01ALL | ERIS | Voltage | MOS-PARK-ER8 | 23SP | P23:345:UMZW:# 2423 #:: GI IN NE. GI 1596 BKR FAULT:EHV: |  |  |  |  | 0.8855 | 0.9 | 1.05 | Add a 30 MVAR Switched Shunt Capacitor at Hanlon 69 kV
01ALL | ERIS | Voltage | MOS-SALM-ER8 | 23SP | P23:345:UMZW:# 2423 #:: GI IN NE. GI 1596 BKR FAULT:EHV: |  |  |  |  | 0.8989 | 0.9 | 1.05 | Add a 30 MVAR Switched Shunt Capacitor at Hanlon 69 kV
01ALL | ERIS | Voltage | MOS-SPNC-ER8 | 23SP | P23:345:UMZW:# 2423 #:: GI IN NE. GI 1596 BKR FAULT:EHV: |  |  |  |  | 0.8925 | 0.9 | 1.05 | Add a 30 MVAR Switched Shunt Capacitor at Hanlon 69 kV
01ALL | ERIS | Voltage | ORLAND-ER8 | 23SP | P23:345:UMZW:# 2423 #:: GI IN NE. GI 1596 BKR FAULT:EHV: |  |  |  |  | 0.8855 | 0.9 | 1.05 | Add a 30 MVAR Switched Shunt Capacitor at Hanlon 69 kV
01ALL | ERIS | Voltage | PARKERCI-ER8 | 23SP | P23:345:UMZW:# 2423 #:: GI IN NE. GI 1596 BKR FAULT:EHV: |  |  |  |  | 0.8846 | 0.9 | 1.05 | Add a 30 MVAR Switched Shunt Capacitor at Hanlon 69 kV
01ALL | ERIS | Voltage | PARKER-ER8 | 23SP | P23:345:UMZW:# 2423 #:: GI IN NE. GI 1596 BKR FAULT:EHV: |  |  |  |  | 0.8855 | 0.9 | 1.05 | Add a 30 MVAR Switched Shunt Capacitor at Hanlon 69 kV
01ALL | ERIS | Voltage | SALEM-ER8 | 23SP | P23:345:UMZW:# 2423 #:: GI IN NE. GI 1596 BKR FAULT:EHV: |  |  |  |  | 0.8985 | 0.9 | 1.05 | Add a 30 MVAR Switched Shunt Capacitor at Hanlon 69 kV
01ALL | ERIS | Voltage | SPENCER-ER8 | 23SP | P23:345:UMZW:# 2423 #:: GI IN NE. GI 1596 BKR FAULT:EHV: |  |  |  |  | 0.8928 | 0.9 | 1.05 | Add a 30 MVAR Switched Shunt Capacitor at Hanlon 69 kV
01ALL | ERIS | Voltage | SW130-ER8 | 23SP | P23:345:UMZW:# 2423 #:: GI IN NE. GI 1596 BKR FAULT:EHV: |  |  |  |  | 0.897 | 0.9 | 1.05 | Add a 30 MVAR Switched Shunt Capacitor at Hanlon 69 kV
01ALL | ERIS | Voltage | SW144-ER8 | 23SP | P23:345:UMZW:# 2423 #:: GI IN NE. GI 1596 BKR FAULT:EHV: |  |  |  |  | 0.8656 | 0.9 | 1.05 | Add a 30 MVAR Switched Shunt Capacitor at Hanlon 69 kV
01ALL | ERIS | Voltage | SW145-ER8 | 23SP | P23:345:UMZW:# 2423 #:: GI IN NE. GI 1596 BKR FAULT:EHV: |  |  |  |  | 0.8884 | 0.9 | 1.05 | Add a 30 MVAR Switched Shunt Capacitor at Hanlon 69 kV
01ALL | ERIS | Voltage | SW156-ER8 | 23SP | P23:345:UMZW:# 2423 #:: GI IN NE. GI 1596 BKR FAULT:EHV: |  |  |  |  | 0.8624 | 0.9 | 1.05 | Add a 30 MVAR Switched Shunt Capacitor at Hanlon 69 kV
01ALL | ERIS | Voltage | SW162-ER8 | 23SP | P23:345:UMZW:# 2423 #:: GI IN NE. GI 1596 BKR FAULT:EHV: |  |  |  |  | 0.8864 | 0.9 | 1.05 | Add a 30 MVAR Switched Shunt Capacitor at Hanlon 69 kV
01ALL | ERIS | Voltage | SW170-ER8 | 23SP | P23:345:UMZW:# 2423 #:: GI IN NE. GI 1596 BKR FAULT:EHV: |  |  |  |  | 0.8991 | 0.9 | 1.05 | Add a 30 MVAR Switched Shunt Capacitor at Hanlon 69 kV
01ALL | ERIS | Voltage | SW-FEDOR-ER8 | 23SP | P23:345:UMZW:# 2423 #:: GI IN NE. GI 1596 BKR FAULT:EHV: |  |  |  |  | 0.8876 | 0.9 | 1.05 | Add a 30 MVAR Switched Shunt Capacitor at Hanlon 69 kV
01ALL | ERIS | Voltage | SW-HOWAR-ER8 | 23SP | P23:345:UMZW:# 2423 #:: GI IN NE. GI 1596 BKR FAULT:EHV: |  |  |  |  | 0.8768 | 0.9 | 1.05 | Add a 30 MVAR Switched Shunt Capacitor at Hanlon 69 kV
01ALL | ERIS | Voltage | SW-SPENC-ER8 | 23SP | P23:345:UMZW:# 2423 #:: GI IN NE. GI 1596 BKR FAULT:EHV: |  |  |  |  | 0.893 | 0.9 | 1.05 | Add a 30 MVAR Switched Shunt Capacitor at Hanlon 69 kV
01ALL | ERIS | Voltage | XLSW4X1-ER8 | 23SP | P23:345:UMZW:# 2423 #:: GI IN NE. GI 1596 BKR FAULT:EHV: |  |  |  |  | 0.8988 | 0.9 | 1.05 | Add a 30 MVAR Switched Shunt Capacitor at Hanlon 69 kV
01ALL | ERIS | Non-Converge | Non-Converge | 23SP, 26SP, 26L | P12:115:UMZB:# 2578 #:: MNU IN ND. MONT - STRANDAHL:HV: | - | - | - | - | - | - | - | Build Strandahl to Black Tail 115 kV line
01ALL | ERIS | Non-Converge | Non-Converge | 23SP, 26SP, 26L | P21:115:UMZB:# 2582 #:: MNU IN ND. OPENING OF LINE SECTION WITHOUT FAULT MNU-STR:HV: | - | - | - | - | - | - | - | Build Strandahl to Black Tail 115 kV line
01ALL | ERIS | Non-Converge | Non-Converge | 23SP, 26SP, 26L | P21:115:UMZB:# 2613 #: STR IN ND. OPENING OF LINE SECTION WITHOUT FAULT STR-MNU | - | - | - | - | - | - | - | Build Strandahl to Black Tail 115 kV line
01ALL | ERIS | Non-Converge | Non-Converge | 23SP, 26SP, 26L | P21:115:UMZB:# 2613 #:: STR IN ND. OPENING OF LINE SECTION WITHOUT FAULT STR-MNU:HV: | - | - | - | - | - | - | - | Build Strandahl to Black Tail 115 kV line
01NR | NRIS | Thermal | 602006 SHEYNNE4 230 652435 FARGO 4 230 1 | 26L | P21:345:OTP:AUTO-SINGLE:BUFFALO3:JAMESTN3:1 |  | 342 | 108.32 | 115.19 | - | - | - | Rebuild the existing Sheynne to Fargo 230 kV line
02ALL | ERIS | Thermal | 640124 COL.SE 7 115 763718 G19-039-TAP 115 1 | 23SP, 26SP, 26WP | 640328 RISNGCY7 115 763718 G19-039-TAP 115 1 |  | 140 | <90% | 122.29 | - | - | - | Rebuild Rising to G19-039-TAP 115 kV
02ALL | ERIS | Thermal | 640184 GENTLMN4 230 640302 OGALALA4 230 1 | 23SP, 26SP, 26WP | 640183 GENTLMN3 345 640252 KEYSTON3 345 1 |  | 320 | <90% | 160.85 | - | - | - | Build Keystone to Gentleman Second Line_345 kV
02ALL | ERIS | Thermal | 640184 GENTLMN4 230 640302 OGALALA4 230 1 | 23SP, 26SP, 26WP | 640183 GENTLMN3 345 640252 KEYSTON3 345 1 |  | 320 | <90% | 160.85 | - | - | - | Build Gentleman Satellite substation
02ALL | ERIS | Thermal | 640226 HOSKINS3 345 996995 HOSKINS T2 _ 230 1 | 23SP, 26SP, 26WP | P13:115-345:NPPD:HOSKINS3:T4:::: |  | 336 | <90% | 117.95 | - | - | - | Build a Second 345-230 kV Transformer at Hoskins_345kV
02ALL | ERIS | Thermal | 640287 N.PLATT7 115 640365 STOCKVL7 115 1 | 23SP | 640183 GENTLMN3 345 640325 REDWILO3 345 1 |  | 137 | <90% | 112.07 | - | - | - | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV (R-Plan)(UID 50442 50444 50445 50446)
02ALL | ERIS | Thermal | 640325 REDWILO3 345 996944 RD.WILLOW T1 115 1 | 26WP | 640183 GENTLMN3 345 640325 REDWILO3 345 1 |  | 333 | <90% | 102.37 | - | - | - | Build a Second 345-115kV Transformer at Red Willow
02ALL | ERIS | Thermal | 640328 RISNGCY7 115 763718 G19-039-TAP 115 1 | 23SP, 26SP | 640124 COL.SE 7 115 763718 G19-039-TAP 115 1 |  | 140 | <90% | 125.85 | - | - | - | Rebuild Columbus SE to G19-039-TAP 115 kV
02ALL | ERIS | Thermal | 640520 ANTELOPE 3 345 996884 ANTELOPE T1 115 1 | 23SP, 26L, 26SP, 26WP | P42:345:NPPD:BKR-MOR-3306::::: |  | 417 | <90% | 199.01 | - | - | - | Build Antelope to Holt 345 kV
02ALL | ERIS | Thermal | 640521 ANTELOPE 7 115 996884 ANTELOPE T1 115 1 | 23SP, 26SP | P42:345:NPPD:BKR-MOR-3306::::: |  | 417 | <90% | 121.63 | - | - | - | Build Second 345-115kV transformer at Antelope
02ALL | ERIS | Thermal | 645451 S3451 3 345 762779 G18-043-TAP 345 1 | 23SP, 26SP, 26WP | P42:345:NPPD:BKR-CPR-3310::::: |  | 956 | <90% | 120.45 | - | - | - | Rebuild S3451 to G18-043-TAP Line_345kV
02ALL | ERIS | Non-Converge | Non-Converge | 23SP. 26SP. 26WP | 640226 HOSKINS3 345 640520 ANTELOPE 3 345 1 | - | - | - | - | - | - | - | Add FERC827 Switched Shunt for GEN-2018-065_34.5kV
02ALL | ERIS | Non-Converge | Non-Converge | 23SP. 26SP. 26WP | 640226 HOSKINS3 345 640520 ANTELOPE 3 345 1 | - | - | - | - | - | - | - | Add FERC827 Switched Shunt for GEN-2018-068_34.5kV
02ALL | ERIS | Non-Converge | Non-Converge | 23SP. 26SP. 26WP | 640226 HOSKINS3 345 640520 ANTELOPE 3 345 1 | - | - | - | - | - | - | - | Add FERC827 Switched Shunt for GEN-2018-131_34.5kV
02ALL | ERIS | Non-Converge | Non-Converge | 23SP. 26SP. 26WP | 640226 HOSKINS3 345 640520 ANTELOPE 3 345 1 | - | - | - | - | - | - | - | Add FERC827 Switched Shunt for GEN-2018-132_34.5kV
02ALL | ERIS | Non-Converge | Non-Converge | 23SP. 26SP. 26WP | 640252 KEYSTON3 345 763666 G19-029 TAP 345 1 | - | - | - | - | - | - | - | Build G19-029-TAP to Keystone Second Line_345 kV
02ALL | ERIS | Stability | Non-dampening Oscillations in Response of Generators | 25S, 25W | GROUP2_P1_FAULT_37 | [7 empty] | Build a 80 Mvar STATCOM at Sweet Water 345 kV Substation
02ALL | ERIS | Stability | Non-dampening Oscillations in Response of Generators | 25S, 25W | GROUP2_P1_FAULT_37 | [7 empty] | Build a 150 Mvar Switched Shunt Capacitor at Red Willow 345 kV Substation
02ALL | ERIS | Stability | Non-dampening Oscillations in Response of Generators | 25S, 25W | GROUP2_P1_FAULT_72 | [7 empty] | Build Keystone to Gentleman Second Line_345 kV
02ALL | ERIS | Stability | Non-dampening Oscillations in Response of Generators | 25S, 25W | GROUP2_P1_FAULT_72 | [7 empty] | Build G19-029-TAP to Keystone Second Line_345 kV
03ALL | ERIS | Voltage | 531359 BEELER 3 115 | 26SP | 531362 MANNGT 3 115 531433 SCOTCTY3 115 1 |  |  |  |  | 0.8948 | 0.9 | 1.05 | Jagger 115 kV Reactive Support
03ALL | ERIS | Voltage | 531360 JAGGER 3 115 | 23SP, 26SP | 531362 MANNGT 3 115 531433 SCOTCTY3 115 1 |  |  |  |  | 0.8731 | 0.9 | 1.05 | Jagger 115 kV Reactive Support
03ALL | ERIS | Voltage | 531361 DIGHTON3 115 | 23SP, 26SP | 531362 MANNGT 3 115 531433 SCOTCTY3 115 1 |  |  |  |  | 0.8725 | 0.9 | 1.05 | Jagger 115 kV Reactive Support
03ALL | ERIS | Voltage | 531362 MANNGT 3 115 | 23SP, 26SP | 531362 MANNGT 3 115 531433 SCOTCTY3 115 1 |  |  |  |  | 0.8711 | 0.9 | 1.05 | Jagger 115 kV Reactive Support
03ALL | ERIS | Voltage | 531363 MANNING3 115 | 23SP, 26SP | 531362 MANNGT 3 115 531433 SCOTCTY3 115 1 |  |  |  |  | 0.87 | 0.9 | 1.05 | Jagger 115 kV Reactive Support
03ALL | ERIS | Voltage | 531495 LIBERTYT 115 | 23SP, 26SP | 531362 MANNGT 3 115 531433 SCOTCTY3 115 1 |  |  |  |  | 0.8829 | 0.9 | 1.05 | Jagger 115 kV Reactive Support
03ALL | ERIS | Voltage | 531496 LIBERTY3 115 | 23SP, 26SP | 531362 MANNGT 3 115 531433 SCOTCTY3 115 1 |  |  |  |  | 0.8774 | 0.9 | 1.05 | Jagger 115 kV Reactive Support
03ALL | ERIS | Thermal | 532791 BENTON 7 345 532796 WICHITA7 345 1 | 23SP, 26L, 26SP, 26WP | P11:345:WERE:WOLFU1-GEN:::EHV: |  | 956 | 98.67 | 117.49 |  |  |  | Benton to Wichita 345 kV Terminal Equipment Upgrades
03ALL | ERIS | Thermal | 532987 BUTLER 4 138 532990 MIDIAN 4 138 1 | 26WP | System Intact | 143 |  | 90.34 | 100.74 |  |  |  | Butler to Midian 138 kV Terminal Equipment Upgrades
03ALL | ERIS | Thermal | 539642 ELLSWTP3 115 539678 GRTBEND3 115 1 | 23SP, 26SP | 532871 CIRCLE 6 230 763862 G19-054-TAP 230 1 |  | 89.8 | 41.78 | 114.49 |  |  |  | Ellsworth Tap to Great Bend 115 kV Equipment Upgrades
03ALL | ERIS | Thermal | 539659 CUDAHY 3 115 539783 CRKCK 3 115 1 | 23SP, 26SP | System Intact | 119.5 |  | 91.54 | 107.19 |  |  |  | Cudahy to Crooked Creek 115 kV Terminal Equipment Upgrades
03ALL | ERIS | Thermal | 539661 24-FREY3 115 539681 N-GBEND3 115 1 | 23SP, 26SP, 26WP | 539661 24-FREY3 115 539689 2ND-KS 3 115 1 |  | 148.2 | 6.64 | 119.18 |  |  |  | Great Bend Frey Street to Great Bend Northwest 115 kV Rebuild
03ALL | ERIS | Thermal | 539661 24-FREY3 115 539689 2ND-KS 3 115 1 | 23SP, 26SP, 26WP | 539661 24-FREY3 115 539681 N-GBEND3 115 1 |  | 148.2 | 6.63 | 119.16 |  |  |  | Great Bend Frey Street to 2ND-KS 115 kV Rebuild
03ALL | ERIS | Thermal | 539666 GBENDTP3 115 539689 2ND-KS 3 115 1 | 23SP, 26SP, 26WP | 539661 24-FREY3 115 539681 N-GBEND3 115 1 |  | 118.5 | 18.48 | 139.47 |  |  |  | Great Bend Tap to 2ND-KS 115 kV Rebuild
03ALL | ERIS | Thermal | 539678 GRTBEND3 115 539681 N-GBEND3 115 1 | 23SP, 26SP | 539661 24-FREY3 115 539689 2ND-KS 3 115 1 |  | 153.4 | 14.3 | 106.68 |  |  |  | Great Bend to Great Bend Northwest 115 kV Rebuild
03ALL | ERIS | Voltage | 539801 THISTLE7 345 | 26WP | P42:345:SPS:CARPENTER:OR335:SLG:EHV: |  |  |  |  | 0.9454 | 0.95 | 1.05 | Switch Out Thistle Line Reactor Circuit 1
03ALL | ERIS | Voltage | 539801 THISTLE7 345 | 26WP | P42:345:SPS:CARPENTER:OR335:SLG:EHV: |  |  |  |  | 0.9454 | 0.95 | 1.05 | Switch Out Thistle Line Reactor Circuit 2
03ALL | ERIS | Voltage | 539801 THISTLE7 345 | 26WP | P42:345:SPS:CARPENTER:OR335:SLG:EHV: |  |  |  |  | 0.9454 | 0.95 | 1.05 | Switch Out Wichita Line Reactor Circuit 1
03ALL | ERIS | Voltage | 539801 THISTLE7 345 | 26WP | P42:345:SPS:CARPENTER:OR335:SLG:EHV: |  |  |  |  | 0.9454 | 0.95 | 1.05 | Switch Out Wichita Line Reactor Circuit 2
03ALL | ERIS | Voltage | 539801 THISTLE7 345 | 26WP | P42:345:SPS:CARPENTER:OR335:SLG:EHV: |  |  |  |  | 0.9454 | 0.95 | 1.05 | Switch Out Buffalo Line Reactor Circuit 1
03ALL | ERIS | Voltage | 539801 THISTLE7 345 | 26WP | P42:345:SPS:CARPENTER:OR335:SLG:EHV: |  |  |  |  | 0.9454 | 0.95 | 1.05 | Switch Out Buffalo Line Reactor Circuit 2
03ALL | ERIS | Stability | Instability | 25S, 25W | G3_FLT29-3PH | [7 empty] | Holcomb to Finney 345 kV Second Line Build
04ALL | ERIS | Thermal | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 | 23SP, 26SP, 26WP | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 94.3 | 164.56 |  |  |  | Sweetwater to Chisholm 230 kV Line Rebuild
04ALL | ERIS | Thermal | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | 23SP, 26SP, 26WP | P12:230:AEPW:SWEETWT6:CHISHOLM6 |  | 395 | 84.05 | 148.63 |  |  |  | Sweetwater to Demarcation 230 kV Line Rebuild
04ALL | ERIS | Thermal | 523771 GRAPEVINE 6 230 523777 WHEELER 6 230 1 | 23SP, 26SP, 26WP | P12:230:AEPW:SWEETWT6:CHISHOLM6 |  | 319 | 74.29 | 135.76 |  |  |  | Wheeler to Grapevine 230 kV Line Model Correction
04ALL | ERIS | Thermal | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 | 23SP, 26SP, 26WP | P12:230:AEPW:SWEETWT6:CHISHOLM6 |  | 353 | 93.49 | 164.32 |  |  |  | Wheeler to Demarcation 230 kV Line Rebuild
04ALL | ERIS | Non-Converge | Non-Converge | 26L | 511456 O.K.U.-7 345 763215 G18-092-TAP 345 1 | [7 empty] | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build
04ALL | ERIS | Non-Converge | Non-Converge | 26L | 560022 CRAWFISH_DR 345 762216 G17-151TAP 345 1 | [7 empty] | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build
04ALL | ERIS | Non-Converge | Non-Converge | 26L | P12:345:AEPW:O.K.U.-7:L.E.S.-7 | [7 empty] | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build
04ALL | ERIS | Non-Converge | Non-Converge | 26L | 762216 G17-151TAP 345 762467 G18-015-TAP 345 1 | [7 empty] | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build
04ALL | ERIS | Non-Converge | Non-Converge | 26L | 762467 G18-015-TAP 345 763215 G18-092-TAP 345 1 | [7 empty] | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build
04ALL | ERIS | Non-Converge | Non-Converge | 26L | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT | [7 empty] | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build
04ALL | ERIS | Non-Converge | Non-Converge | 26L | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT | [7 empty] | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build
04ALL | ERIS | Non-Converge | Non-Converge | 26L | P23:345:AEPW:OKLAUNION CB 3401A NBTB | [7 empty] | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build
04ALL | ERIS | Non-Converge | Non-Converge | 26L | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB | [7 empty] | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build
04ALL | ERIS | Non-Converge | Non-Converge | 26L | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB | [7 empty] | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build
04ALL | ERIS | Non-Converge | Non-Converge | 26L | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT | [7 empty] | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build
05ALL | ERIS | Thermal | 525531 TOLK 6 230 997716 TOLK 6 230 2 | 23SP, 26SP, 26WP | 525549 TOLK 7 345 3WXFMR ABBXNL844501 1 |  | 560 | 84 | 162.04 |  |  |  | Tolk 345/230 kV Third Transformer Build
05ALL | ERIS | Thermal | 525549 TOLK 7 345 997715 ABBXNL844501 230 1 | 23SP, 26SP, 26WP | 525531 TOLK 6 230 3WXFMR TOLK 6 2 |  | 552.5 | 98 | 164.23 |  |  |  | Tolk 345/230 kV Third Transformer Build
05ALL | ERIS | Thermal | 511490 ELKCITY6 230 998036 ELKCTY-6 _1 138 1 | 23SP | P12:345:OKGE-AEPW:BKRBKR371:::: |  | 330 | 46 | 113.27 |  |  |  | Multi - Border - Woodward 345 kV Tap (NTC 210627, NTC 210628)
05ALL | ERIS | Stability | Multiple Out of Step Generators and Damping Issues | 25S, 25W | Group5_Fault_0222_P1 | [7 empty] | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build
05ALL | ERIS | Stability | Multiple Out of Step Generators | 25S, 25W | Group5_Fault_0333_P4 | [7 empty] | Lawton Eastside 345 kV Substation Upgrade to Double-Bus-Double-Breaker Configuration
05ALL | ERIS | Stability | Multiple Damping Issues | 25S, 25W | Group5_Fault_0203_P1 | [7 empty] | Potter to Tolk 345 kV Double Circuit Line Build Potter to Chisholm 345 kV Double Circuit Line Build
05ALL | ERIS | Non-Converge | Non-Converge | 23SP, 26SP | 511456 O.K.U.-7 345 763215 G18-092-TAP 345 1 | [7 empty] | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build Potter to Tolk 345 kV Double Circuit Line Build Potter to Chisholm 345 kV Double Circuit Line Build
05ALL | ERIS | Non-Converge | Non-Converge | 23SP, 26SP, 26WP | P12:345:AEPW:O.K.U.-7:L.E.S.-7 | [7 empty] | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build Potter to Tolk 345 kV Double Circuit Line Build Potter to Chisholm 345 kV Double Circuit Line Build
05ALL | ERIS | Non-Converge | Non-Converge | 23SP, 26SP | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT | [7 empty] | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build Potter to Tolk 345 kV Double Circuit Line Build Potter to Chisholm 345 kV Double Circuit Line Build
05ALL | ERIS | Non-Converge | Non-Converge | 23SP, 26SP, 26WP | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT | [7 empty] | Lawton Eastside 345 kV Substation Upgrade to Double-Bus-Double-Breaker Configuration
05ALL | ERIS | Non-Converge | Non-Converge | 23SP, 26SP | P23:345:AEPW:OKLAUNION CB 3401A NBTB | [7 empty] | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build Potter to Tolk 345 kV Double Circuit Line Build Potter to Chisholm 345 kV Double Circuit Line Build
05ALL | ERIS | Non-Converge | Non-Converge | 23SP, 26SP, 26WP | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB | [7 empty] | Lawton Eastside 345 kV Substation Upgrade to Double-Bus-Double-Breaker Configuration
05ALL | ERIS | Non-Converge | Non-Converge | 23SP, 26SP, 26WP | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB | [7 empty] | Lawton Eastside 345 kV Substation Upgrade to Double-Bus-Double-Breaker Configuration
05ALL | ERIS | Non-Converge | Non-Converge | 23SP, 26SP, 26WP | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT | [7 empty] | Lawton Eastside 345 kV Substation Upgrade to Double-Bus-Double-Breaker Configuration

## Assigned Upgrade Costs
Gen Number | Group | Upgrade ID | Service Type | Upgrade Name | Upgrade Type | Upgrade Details | Allocated Cost | % Allocated | Total Upgrade Cost | PTDF %
GEN-2018-067 | 01 NORTH | TBD | ERIS | Add a 30 MVAR Switched Shunt Capacitor at Hanlon 69 kV | Current Study | Build a 30Mvar Switched shunt capacitor at Hanlon | 326949.2582 | 32.04% | 1020300 | 0.02429
GEN-2018-067 | 01 NORTH | TBD | ERIS | Build Strandahl to Black Tail 115 kV line | Current Study | Build approximately 15 mile of new 115kV line from Strandahl to Black Tail | 13481505 | 100% | 13481505 | 0.38524
GEN-2018-067 | 01 NORTH | TBD | ERIS | Rebuild Mont to STRNDAHL Line_115kV | Current Study | Rebuild approximately 11.97 miles of 115kV line from Mont to STRNDAHL | 8508754.8 | 100% | 8508754.8 | 0.5193
GEN-2018-069 | 01 NORTH | TBD | ERIS | Add a 30 MVAR Switched Shunt Capacitor at Hanlon 69 kV | Current Study | Build a 30Mvar Switched shunt capacitor at Hanlon | 164162.1571 | 16.09% | 1020300 | 0.02488
GEN-2018-069 | 01 NORTH | TBD | ERIS | Replace Belfield 345-230-14 kV First Transformer | Current Study | Replace the first 345/230kV transformer at BELFELD | 7827925.6501 | 52.76% | 14835575 | 0.20942
GEN-2018-070 | 01 NORTH | TBD | ERIS | Add a 30 MVAR Switched Shunt Capacitor at Hanlon 69 kV | Current Study | Build a 30Mvar Switched shunt capacitor at Hanlon | 29275.2275 | 2.869% | 1020300 | 0.03029
GEN-2018-070 | 01 NORTH | TBD | ERIS | Rebuild Gavins to Yankton JCT_115 kV | Current Study | Rebuild approximately 4.03 miles of 115kV line from Gavins to Yankton Junction. | 2864685.2 | 100% | 2864685.2 | 0.09956
GEN-2018-070 | 01 NORTH | TBD | ERIS | Rebuild the existing Utica Jct to Napa Jct 115 kV line | Current Study | Rebuild approximately 13.16 miles of 115kV line from Utica to NAPA | 9354654.4 | 100% | 9354654.4 | 0.11327
GEN-2018-070 | 01 NORTH | TBD | ERIS | Rebuild the existing Yankton Jct to Napa Jct 115 kV line | Current Study | Rebuild approximately 2.7 miles of 115kV line from Yankton JCT to NAPA JCT | 1919268 | 100% | 1919268 | 0.11327
GEN-2018-070 | 01 NORTH | TBD | ERIS | Upgrade the terminal at Utica Junction | Current Study | Replace terminal equipment at Utica Junction to facilitate the Rebuild UTICAJC7 to NAPA JCT _115kV | 400000 | 100% | 400000 | 0.11327
GEN-2018-074 | 01 NORTH | TBD | ERIS | Add a 30 MVAR Switched Shunt Capacitor at Hanlon 69 kV | Current Study | Build a 30Mvar Switched shunt capacitor at Hanlon | 89550.1928 | 8.777% | 1020300 | 0.02175
GEN-2018-074 | 01 NORTH | TBD | ERIS | Add a third 230-69 kV transformer at Denison | Current Study | Build a third 230/69kV transformer at Denison | 8000000 | 100% | 8000000 | 0.0919
GEN-2018-074 | 01 NORTH | TBD | ERIS | Build a second 69 kV line from Denison to Boyer | Current Study | Build approximately 2.88 miles of second 230kV line from Denison to Boyer | 2000000 | 100% | 2000000 | 0.11075
GEN-2018-074 | 01 NORTH | TBD | ERIS | Rebuild the existing K335AMAI-NI8 to Boyer 69 kV line | Current Study | Rebuild approximately 0.69 miles of 69kV line from Boyer to K335AMAI | 627174.81 | 100% | 627174.81 | 0.0565
GEN-2018-074 | 01 NORTH | TBD | ERIS | Rebuild the existing K335AMAI-NI8 to K338WTCT-NI8 69 kV line | Current Study | Rebuild approximately 0.33 miles of 69 kV line from K335AMAI to K338WTCT | 299953.17 | 100% | 299953.17 | 0.0565
GEN-2018-074 | 01 NORTH | TBD | ERIS | Upgrade the terminal at Denison 69 kV | Current Study | Replace terminal equipment at Denison 69kV to facilitate the Build Denison to Boyer Second Line_69kV | 1000000 | 100% | 1000000 | 0.11075
GEN-2019-023 | 01 NORTH | TBD | ERIS | Add a 30 MVAR Switched Shunt Capacitor at Hanlon 69 kV | Current Study | Build a 30Mvar Switched shunt capacitor at Hanlon | 174017.165 | 17.06% | 1020300 | 0.02997
GEN-2019-023 | 01 NORTH | TBD | ERIS | Replace Belfield 345-230-14 kV First Transformer | Current Study | Replace the first 345/230kV transformer at BELFELD | 7007649.3499 | 47.24% | 14835575 | 0.21304
GEN-2019-037 | 01 NORTH | TBD | ERIS | Add a 30 MVAR Switched Shunt Capacitor at Hanlon 69 kV | Current Study | Build a 30Mvar Switched shunt capacitor at Hanlon | 236345.9995 | 23.16% | 1020300 | 0.02985
GEN-2018-065 | 02 NEBRASKA | TBD | ERIS | Add FERC827 Switched Shunt for GEN-2018-065_34.5kV | Current Study | Add a switched shunt capacitor at GEN-2018-065 substation low side to meet FERC 827 requirement (1 Mvar) | 24891 | 100% | 24891 | 1
GEN-2018-065 | 02 NEBRASKA | TBD | ERIS | Build a Second 345-230 kV Transformer at Hoskins_345kV | Current Study | Build a second 345/230kV transformer at Hoskins | 100254.3102 | 1.207% | 8302968 | 0.02431
GEN-2018-065 | 02 NEBRASKA | TBD | ERIS | Build Antelope to Holt 345 kV | Current Study | Build approximately 25 miles of 345kV line from Antelope to Holt | 764555.6072 | 2.672% | 28611100 | 0.43824
GEN-2018-065 | 02 NEBRASKA | TBD | ERIS | Build Second 345-115kV transformer at Antelope | Current Study | Build a second 345/115kV transformer at Antelope | 226300.1172 | 2.726% | 8302968 | 0.06073
GEN-2018-065 | 02 NEBRASKA | TBD | ERIS | Rebuild S3451 to G18-043-TAP Line_345kV | Current Study | Rebuild approximately 12.83 miles of 345kV line from S3451 to G18-043-TAP | 109450.6215 | 0.7454% | 14683216.52 | 0.07258
GEN-2018-068 | 02 NEBRASKA | TBD | ERIS | Add FERC827 Switched Shunt for GEN-2018-068_34.5kV | Current Study | Add a switched shunt capacitor at GEN-2018-068 substation low side to meet FERC 827 requirement (56 Mvar) | 1393896 | 100% | 1393896 | 1
GEN-2018-068 | 02 NEBRASKA | TBD | ERIS | Build a Second 345-230 kV Transformer at Hoskins_345kV | Current Study | Build a second 345/230kV transformer at Hoskins | 1531156.7372 | 18.44% | 8302968 | 0.02431
GEN-2018-068 | 02 NEBRASKA | TBD | ERIS | Build Antelope to Holt 345 kV | Current Study | Build approximately 25 miles of 345kV line from Antelope to Holt | 11676849.2729 | 40.81% | 28611100 | 0.43824
GEN-2018-068 | 02 NEBRASKA | TBD | ERIS | Build Second 345-115kV transformer at Antelope | Current Study | Build a second 345/115kV transformer at Antelope | 3456219.9714 | 41.63% | 8302968 | 0.06073
GEN-2018-068 | 02 NEBRASKA | TBD | ERIS | Rebuild S3451 to G18-043-TAP Line_345kV | Current Study | Rebuild approximately 12.83 miles of 345kV line from S3451 to G18-043-TAP | 1671609.4922 | 11.38% | 14683216.52 | 0.07258
GEN-2018-083 | 02 NEBRASKA | TBD | ERIS | Build a Second 345-230 kV Transformer at Hoskins_345kV | Current Study | Build a second 345/230kV transformer at Hoskins | 2044293.3123 | 24.62% | 8302968 | 0.03926
GEN-2018-083 | 02 NEBRASKA | TBD | ERIS | Rebuild S3451 to G18-043-TAP Line_345kV | Current Study | Rebuild approximately 12.83 miles of 345kV line from S3451 to G18-043-TAP | 1459637.1272 | 9.941% | 14683216.52 | 0.07666
GEN-2018-090 | 02 NEBRASKA | TBD | ERIS | Rebuild S3451 to G18-043-TAP Line_345kV | Current Study | Rebuild approximately 12.83 miles of 345kV line from S3451 to G18-043-TAP | 6501630.4674 | 44.28% | 14683216.52 | 0.68293
GEN-2018-125 | 02 NEBRASKA | TBD | ERIS | Build a 150 Mvar Switched Shunt Capacitor at Red Willow 345 kV Substation | Current Study | Build a 150 Mvar Switched Shunt Capacitor at Red Willow 345 kV Substation | 1055658.6903 | 28.27% | 3733650 | 0.01316
GEN-2018-125 | 02 NEBRASKA | TBD | ERIS | Build a 80 Mvar STATCOM at Sweet Water 345 kV Substation | Current Study | Build a 80 Mvar STATCOM at Sweet Water 345 kV Substation | 6727076.5219 | 37.16% | 18102560 | 0.04268
GEN-2018-125 | 02 NEBRASKA | TBD | ERIS | Build a Second 345-115kV Transformer at Red Willow | Current Study | Build a second 345/115kV transformer at Red Willow | 1678308.8874 | 20.21% | 8302968 | 0.00992
GEN-2018-131 | 02 NEBRASKA | TBD | ERIS | Add FERC827 Switched Shunt for GEN-2018-131_34.5kV | Current Study | Add a switched shunt capacitor at GEN-2018-131 substation low side to meet FERC 827 requirement (28 Mvar) | 696948 | 100% | 696948 | 1
GEN-2018-131 | 02 NEBRASKA | TBD | ERIS | Build a Second 345-230 kV Transformer at Hoskins_345kV | Current Study | Build a second 345/230kV transformer at Hoskins | 1145465.7603 | 13.8% | 8302968 | 0.02484
GEN-2018-131 | 02 NEBRASKA | TBD | ERIS | Build Antelope to Holt 345 kV | Current Study | Build approximately 25 miles of 345kV line from Antelope to Holt | 8463287.233 | 29.58% | 28611100 | 0.43384
GEN-2018-131 | 02 NEBRASKA | TBD | ERIS | Build Second 345-115kV transformer at Antelope | Current Study | Build a second 345/115kV transformer at Antelope | 2418362.0983 | 29.13% | 8302968 | 0.05804
GEN-2018-131 | 02 NEBRASKA | TBD | ERIS | Rebuild S3451 to G18-043-TAP Line_345kV | Current Study | Rebuild approximately 12.83 miles of 345kV line from S3451 to G18-043-TAP | 1480162.07 | 10.08% | 14683216.52 | 0.08778
GEN-2018-132 | 02 NEBRASKA | TBD | ERIS | Add FERC827 Switched Shunt for GEN-2018-132_34.5kV | Current Study | Add a switched shunt capacitor at GEN-2018-132 substation low side to meet FERC 827 requirement (26 Mvar) | 647166 | 100% | 647166 | 1
GEN-2018-132 | 02 NEBRASKA | TBD | ERIS | Build a Second 345-230 kV Transformer at Hoskins_345kV | Current Study | Build a second 345/230kV transformer at Hoskins | 1043025.733 | 12.56% | 8302968 | 0.02484
GEN-2018-132 | 02 NEBRASKA | TBD | ERIS | Build Antelope to Holt 345 kV | Current Study | Build approximately 25 miles of 345kV line from Antelope to Holt | 7706407.8869 | 26.94% | 28611100 | 0.43384
GEN-2018-132 | 02 NEBRASKA | TBD | ERIS | Build Second 345-115kV transformer at Antelope | Current Study | Build a second 345/115kV transformer at Antelope | 2202085.8131 | 26.52% | 8302968 | 0.05804
GEN-2018-132 | 02 NEBRASKA | TBD | ERIS | Rebuild S3451 to G18-043-TAP Line_345kV | Current Study | Rebuild approximately 12.83 miles of 345kV line from S3451 to G18-043-TAP | 1347789.8523 | 9.179% | 14683216.52 | 0.08778
GEN-2019-029 | 02 NEBRASKA | TBD | ERIS | Build a 150 Mvar Switched Shunt Capacitor at Red Willow 345 kV Substation | Current Study | Build a 150 Mvar Switched Shunt Capacitor at Red Willow 345 kV Substation | 1846260.2203 | 49.45% | 3733650 | 0.01316
GEN-2019-029 | 02 NEBRASKA | TBD | ERIS | Build a 80 Mvar STATCOM at Sweet Water 345 kV Substation | Current Study | Build a 80 Mvar STATCOM at Sweet Water 345 kV Substation | 7842483.49 | 43.32% | 18102560 | 0.02845
GEN-2019-029 | 02 NEBRASKA | TBD | ERIS | Build a Second 345-115kV Transformer at Red Willow | Current Study | Build a second 345/115kV transformer at Red Willow | 4615876.7682 | 55.59% | 8302968 | 0.0156
GEN-2019-029 | 02 NEBRASKA | TBD | ERIS | Build G19-029-TAP to Keystone Second Line_345 kV | Current Study | Build approximately 72.39 miles of second 345 kV line from G19-029-TAP to Keystone | 57252690.183 | 69.11% | 82846301.16 | 0.37692
GEN-2019-029 | 02 NEBRASKA | TBD | ERIS | Build Keystone to Gentleman Second Line_345 kV | Current Study | Build approximately 29.84 miles 345kV second line from Keystone to Gentleman | 31314867.4066 | 69.11% | 45314399.8 | 0.38262
GEN-2019-029 | 02 NEBRASKA | TBD | ERIS | Build Gentleman Satellite substation | Current Study | Build Gentleman Satellite substation to facilitate the Build Keystone to Gentleman Second Line_345 kV | 96678979.9605 | 69.11% | 139900000 | 0.38262
GEN-2019-029 | 02 NEBRASKA | 50442, 50444, 50445, 50446 | ERIS | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV (R-Plan)(UID 50442 50444 50445 50446) | Contingent | Build approximately 76 miles of new 345kV line from Gentleman to Cherry County and 146 miles from Cherry County to Holt | 0 | 69.65% | 332910090 | 0.14309
GEN-2019-033 | 02 NEBRASKA | TBD | ERIS | Build a 150 Mvar Switched Shunt Capacitor at Red Willow 345 kV Substation | Current Study | Build a 150 Mvar Switched Shunt Capacitor at Red Willow 345 kV Substation | 831731.0894 | 22.28% | 3733650 | 0.01316
GEN-2019-033 | 02 NEBRASKA | TBD | ERIS | Build a 80 Mvar STATCOM at Sweet Water 345 kV Substation | Current Study | Build a 80 Mvar STATCOM at Sweet Water 345 kV Substation | 3532999.9881 | 19.52% | 18102560 | 0.02845
GEN-2019-033 | 02 NEBRASKA | TBD | ERIS | Build a Second 345-115kV Transformer at Red Willow | Current Study | Build a second 345/115kV transformer at Red Willow | 2008782.3444 | 24.19% | 8302968 | 0.01507
GEN-2019-033 | 02 NEBRASKA | TBD | ERIS | Build G19-029-TAP to Keystone Second Line_345 kV | Current Study | Build approximately 72.39 miles of second 345 kV line from G19-029-TAP to Keystone | 25593610.977 | 30.89% | 82846301.16 | 0.37402
GEN-2019-033 | 02 NEBRASKA | TBD | ERIS | Build Gentleman Satellite substation | Current Study | Build Gentleman Satellite substation to facilitate the Build Keystone to Gentleman Second Line_345 kV | 43221020.0395 | 30.89% | 139900000 | 0.3797
GEN-2019-033 | 02 NEBRASKA | TBD | ERIS | Build Keystone to Gentleman Second Line_345 kV | Current Study | Build approximately 29.84 miles 345kV second line from Keystone to Gentleman | 13999532.3934 | 30.89% | 45314399.8 | 0.3797
GEN-2019-033 | 02 NEBRASKA | 50442, 50444, 50445, 50446 | ERIS | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV (R-Plan)(UID 50442 50444 50445 50446) | Contingent | Build approximately 76 miles of new 345kV line from Gentleman to Cherry County and 146 miles from Cherry County to Holt | 0 | 30.35% | 332910090 | 0.13843
GEN-2019-039 | 02 NEBRASKA | TBD | ERIS | Build a Second 345-230 kV Transformer at Hoskins_345kV | Current Study | Build a second 345/230kV transformer at Hoskins | 366360.6892 | 4.412% | 8302968 | 0.01008
GEN-2019-039 | 02 NEBRASKA | TBD | ERIS | Rebuild Columbus SE to G19-039-TAP 115 kV | Current Study | Rebuild approximately 6.76 miles of 115kV line from Clumbus southeast to G16-039-TAP | 4805278.4 | 100% | 4805278.4 | 0.82207
GEN-2019-039 | 02 NEBRASKA | TBD | ERIS | Rebuild Rising to G19-039-TAP 115 kV | Current Study | Rebuild approximately 6.76 miles of 115kV line from Rising to G19-039-TAP | 4805278.4 | 100% | 4805278.4 | 0.17793
GEN-2019-039 | 02 NEBRASKA | TBD | ERIS | Rebuild S3451 to G18-043-TAP Line_345kV | Current Study | Rebuild approximately 12.83 miles of 345kV line from S3451 to G18-043-TAP | 363885.6698 | 2.478% | 14683216.52 | 0.02738
GEN-2019-069 | 02 NEBRASKA | TBD | ERIS | Build a Second 345-230 kV Transformer at Hoskins_345kV | Current Study | Build a second 345/230kV transformer at Hoskins | 828964.5831 | 9.984% | 8302968 | 0.0398
GEN-2019-069 | 02 NEBRASKA | TBD | ERIS | Rebuild S3451 to G18-043-TAP Line_345kV | Current Study | Rebuild approximately 12.83 miles of 345kV line from S3451 to G18-043-TAP | 699620.4879 | 4.765% | 14683216.52 | 0.09186
GEN-2019-070 | 02 NEBRASKA | TBD | ERIS | Build a Second 345-230 kV Transformer at Hoskins_345kV | Current Study | Build a second 345/230kV transformer at Hoskins | 414482.2915 | 4.992% | 8302968 | 0.0398
GEN-2019-070 | 02 NEBRASKA | TBD | ERIS | Rebuild S3451 to G18-043-TAP Line_345kV | Current Study | Rebuild approximately 12.83 miles of 345kV line from S3451 to G18-043-TAP | 349810.2439 | 2.382% | 14683216.52 | 0.09186
GEN-2019-073 | 02 NEBRASKA | TBD | ERIS | Build a Second 345-230 kV Transformer at Hoskins_345kV | Current Study | Build a second 345/230kV transformer at Hoskins | 828964.5831 | 9.984% | 8302968 | 0.0398
GEN-2019-073 | 02 NEBRASKA | TBD | ERIS | Rebuild S3451 to G18-043-TAP Line_345kV | Current Study | Rebuild approximately 12.83 miles of 345kV line from S3451 to G18-043-TAP | 699620.4879 | 4.765% | 14683216.52 | 0.09186
GEN-2018-093 | 03 CENTRAL | TBD | ERIS | Benton to Wichita 345 kV Terminal Equipment Upgrades | Current Study | Upgrade terminal equipment at Benton to Wichita 345 kV substations to increase minimum Rate A/Rate B to 915/1145 MVA | 19231.609 | 2.481% | 775000 | 0.07712
GEN-2018-093 | 03 CENTRAL | TBD | ERIS | Butler to Midian 138 kV Terminal Equipment Upgrades | Current Study | Upgrade terminal equipment at Butler to Midian 138 kV substations to increase minimum summer/emergency rating to 160 MVA | 1814161 | 100% | 1814161 | 0.04823
GEN-2018-093 | 03 CENTRAL | TBD | ERIS | Switch Out Buffalo Line Reactor Circuit 1 | Current Study | Switch out the Buffalo 50 MVAR line reactor on the Buffalo to Thistle 345 kV line Circuit 1. Line reactor is remote switchable. | 0 | 0.5801% | 0 | 0.0164
GEN-2018-093 | 03 CENTRAL | TBD | ERIS | Switch Out Buffalo Line Reactor Circuit 2 | Current Study | Switch out the Buffalo 50 MVAR line reactor on the Buffalo to Thistle 345 kV line Circuit 2. Line reactor is remote switchable. | 0 | 0.5801% | 0 | 0.0164
GEN-2018-093 | 03 CENTRAL | TBD | ERIS | Switch Out Thistle Line Reactor Circuit 1 | Current Study | Switch out the Thistle 40 MVAR line reactor on the Clark County to Thistle 345 kV line Circuit 1. Line reactor is remote switchable. | 0 | 0.5801% | 0 | 0.0164
GEN-2018-093 | 03 CENTRAL | TBD | ERIS | Switch Out Thistle Line Reactor Circuit 2 | Current Study | Switch out the Thistle 40 MVAR line reactor on the Clark County to Thistle 345 kV line Circuit 2. Line reactor is remote switchable. | 0 | 0.5801% | 0 | 0.0164
GEN-2018-093 | 03 CENTRAL | TBD | ERIS | Switch Out Wichita Line Reactor Circuit 1 | Current Study | Switch out the Wichita 25 MVAR line reactor on the Buffalo to Wichita 345 kV line Circuit 1. Line reactor is remote switchable. | 0 | 0.5801% | 0 | 0.0164
GEN-2018-093 | 03 CENTRAL | TBD | ERIS | Switch Out Wichita Line Reactor Circuit 2 | Current Study | Switch out the Wichita 25 MVAR line reactor on the Buffalo to Wichita 345 kV line Circuit 2. Line reactor is remote switchable. | 0 | 0.5801% | 0 | 0.0164
GEN-2018-108 | 03 CENTRAL | TBD | ERIS | Benton to Wichita 345 kV Terminal Equipment Upgrades | Current Study | Upgrade terminal equipment at Benton to Wichita 345 kV substations to increase minimum Rate A/Rate B to 915/1145 MVA | 61488.4065 | 7.934% | 775000 | 0.15573
GEN-2018-108 | 03 CENTRAL | TBD | ERIS | Switch Out Buffalo Line Reactor Circuit 1 | Current Study | Switch out the Buffalo 50 MVAR line reactor on the Buffalo to Thistle 345 kV line Circuit 1. Line reactor is remote switchable. | 0 | 1.258% | 0 | 0.02246
GEN-2018-108 | 03 CENTRAL | TBD | ERIS | Switch Out Buffalo Line Reactor Circuit 2 | Current Study | Switch out the Buffalo 50 MVAR line reactor on the Buffalo to Thistle 345 kV line Circuit 2. Line reactor is remote switchable. | 0 | 1.258% | 0 | 0.02246
GEN-2018-108 | 03 CENTRAL | TBD | ERIS | Switch Out Thistle Line Reactor Circuit 1 | Current Study | Switch out the Thistle 40 MVAR line reactor on the Clark County to Thistle 345 kV line Circuit 1. Line reactor is remote switchable. | 0 | 1.258% | 0 | 0.02246
GEN-2018-108 | 03 CENTRAL | TBD | ERIS | Switch Out Thistle Line Reactor Circuit 2 | Current Study | Switch out the Thistle 40 MVAR line reactor on the Clark County to Thistle 345 kV line Circuit 2. Line reactor is remote switchable. | 0 | 1.258% | 0 | 0.02246
GEN-2018-108 | 03 CENTRAL | TBD | ERIS | Switch Out Wichita Line Reactor Circuit 1 | Current Study | Switch out the Wichita 25 MVAR line reactor on the Buffalo to Wichita 345 kV line Circuit 1. Line reactor is remote switchable. | 0 | 1.258% | 0 | 0.02246
GEN-2018-108 | 03 CENTRAL | TBD | ERIS | Switch Out Wichita Line Reactor Circuit 2 | Current Study | Switch out the Wichita 25 MVAR line reactor on the Buffalo to Wichita 345 kV line Circuit 2. Line reactor is remote switchable. | 0 | 1.258% | 0 | 0.02246
GEN-2018-116 | 03 CENTRAL | TBD | ERIS | Benton to Wichita 345 kV Terminal Equipment Upgrades | Current Study | Upgrade terminal equipment at Benton to Wichita 345 kV substations to increase minimum Rate A/Rate B to 915/1145 MVA | 74637.1963 | 9.631% | 775000 | 0.11972
GEN-2018-116 | 03 CENTRAL | TBD | ERIS | Ellsworth Tap to Great Bend 115 kV Equipment Upgrades | Current Study | Upgrade equipment at Ellsworth Tap to Great Bend 115 kV substations to increase minimum summer/emergency rating to 105 MVA | 412276.9093 | 54.97% | 750000 | 0.09197
GEN-2018-116 | 03 CENTRAL | TBD | ERIS | Great Bend Frey Street to 2ND-KS 115 kV Rebuild | Current Study | Rebuild the Great Bend Frey Street to 2ND-KS 115 kV 1.82 mile line | 1206585.3928 | 78.95% | 1528341.4976 | 0.29699
GEN-2018-116 | 03 CENTRAL | TBD | ERIS | Great Bend Frey Street to Great Bend Northwest 115 kV Rebuild | Current Study | Rebuild the Great Bend Frey Street to Great Bend Northwest 115 kV 5.1 mile line | 3381090.9359 | 78.95% | 4282715.1854 | 0.33135
GEN-2018-116 | 03 CENTRAL | TBD | ERIS | Great Bend Tap to 2ND-KS 115 kV Rebuild | Current Study | Rebuild the Great Bend Tap to 2ND-KS 115 kV 3.79 mile line | 2512614.6367 | 78.95% | 3182645.2064 | 0.29699
GEN-2018-116 | 03 CENTRAL | TBD | ERIS | Great Bend to Great Bend Northwest 115 kV Rebuild | Current Study | Rebuild the Great Bend to Great Bend Northwest 115 kV 3.58 mile line | 2373393.2452 | 78.95% | 3006298.1106 | 0.33103
GEN-2018-116 | 03 CENTRAL | TBD | ERIS | Holcomb to Finney 345 kV Second Line Build | Current Study | Build a second 345 kV line from Holcomb to Finney 345 kV | 671297.5416 | 5.01% | 13400000 | 0.01341
GEN-2018-116 | 03 CENTRAL | TBD | ERIS | Switch Out Buffalo Line Reactor Circuit 1 | Current Study | Switch out the Buffalo 50 MVAR line reactor on the Buffalo to Thistle 345 kV line Circuit 1. Line reactor is remote switchable. | 0 | 8.541% | 0 | 0.09659
GEN-2018-116 | 03 CENTRAL | TBD | ERIS | Switch Out Buffalo Line Reactor Circuit 2 | Current Study | Switch out the Buffalo 50 MVAR line reactor on the Buffalo to Thistle 345 kV line Circuit 2. Line reactor is remote switchable. | 0 | 8.541% | 0 | 0.09659
GEN-2018-116 | 03 CENTRAL | TBD | ERIS | Switch Out Thistle Line Reactor Circuit 1 | Current Study | Switch out the Thistle 40 MVAR line reactor on the Clark County to Thistle 345 kV line Circuit 1. Line reactor is remote switchable. | 0 | 8.541% | 0 | 0.09659
GEN-2018-116 | 03 CENTRAL | TBD | ERIS | Switch Out Thistle Line Reactor Circuit 2 | Current Study | Switch out the Thistle 40 MVAR line reactor on the Clark County to Thistle 345 kV line Circuit 2. Line reactor is remote switchable. | 0 | 8.541% | 0 | 0.09659
GEN-2018-116 | 03 CENTRAL | TBD | ERIS | Switch Out Wichita Line Reactor Circuit 1 | Current Study | Switch out the Wichita 25 MVAR line reactor on the Buffalo to Wichita 345 kV line Circuit 1. Line reactor is remote switchable. | 0 | 8.541% | 0 | 0.09659
GEN-2018-116 | 03 CENTRAL | TBD | ERIS | Switch Out Wichita Line Reactor Circuit 2 | Current Study | Switch out the Wichita 25 MVAR line reactor on the Buffalo to Wichita 345 kV line Circuit 2. Line reactor is remote switchable. | 0 | 8.541% | 0 | 0.09659
GEN-2018-128 | 03 CENTRAL | TBD | ERIS | Benton to Wichita 345 kV Terminal Equipment Upgrades | Current Study | Upgrade terminal equipment at Benton to Wichita 345 kV substations to increase minimum Rate A/Rate B to 915/1145 MVA | 69285.3178 | 8.94% | 775000 | 0.08326
GEN-2018-128 | 03 CENTRAL | TBD | ERIS | Switch Out Buffalo Line Reactor Circuit 1 | Current Study | Switch out the Buffalo 50 MVAR line reactor on the Buffalo to Thistle 345 kV line Circuit 1. Line reactor is remote switchable. | 0 | 0.2915% | 0 | 0.00247
GEN-2018-128 | 03 CENTRAL | TBD | ERIS | Switch Out Buffalo Line Reactor Circuit 2 | Current Study | Switch out the Buffalo 50 MVAR line reactor on the Buffalo to Thistle 345 kV line Circuit 2. Line reactor is remote switchable. | 0 | 0.2915% | 0 | 0.00247
GEN-2018-128 | 03 CENTRAL | TBD | ERIS | Switch Out Thistle Line Reactor Circuit 1 | Current Study | Switch out the Thistle 40 MVAR line reactor on the Clark County to Thistle 345 kV line Circuit 1. Line reactor is remote switchable. | 0 | 0.2915% | 0 | 0.00247
GEN-2018-128 | 03 CENTRAL | TBD | ERIS | Switch Out Thistle Line Reactor Circuit 2 | Current Study | Switch out the Thistle 40 MVAR line reactor on the Clark County to Thistle 345 kV line Circuit 2. Line reactor is remote switchable. | 0 | 0.2915% | 0 | 0.00247
GEN-2018-128 | 03 CENTRAL | TBD | ERIS | Switch Out Wichita Line Reactor Circuit 1 | Current Study | Switch out the Wichita 25 MVAR line reactor on the Buffalo to Wichita 345 kV line Circuit 1. Line reactor is remote switchable. | 0 | 0.2915% | 0 | 0.00247
GEN-2018-128 | 03 CENTRAL | TBD | ERIS | Switch Out Wichita Line Reactor Circuit 2 | Current Study | Switch out the Wichita 25 MVAR line reactor on the Buffalo to Wichita 345 kV line Circuit 2. Line reactor is remote switchable. | 0 | 0.2915% | 0 | 0.00247
GEN-2019-001 | 03 CENTRAL | TBD | ERIS | Benton to Wichita 345 kV Terminal Equipment Upgrades | Current Study | Upgrade terminal equipment at Benton to Wichita 345 kV substations to increase minimum Rate A/Rate B to 915/1145 MVA | 23230.0896 | 2.997% | 775000 | 0.22357
GEN-2019-001 | 03 CENTRAL | TBD | ERIS | Switch Out Buffalo Line Reactor Circuit 1 | Current Study | Switch out the Buffalo 50 MVAR line reactor on the Buffalo to Thistle 345 kV line Circuit 1. Line reactor is remote switchable. | 0 | 0.2663% | 0 | 0.01807
GEN-2019-001 | 03 CENTRAL | TBD | ERIS | Switch Out Buffalo Line Reactor Circuit 2 | Current Study | Switch out the Buffalo 50 MVAR line reactor on the Buffalo to Thistle 345 kV line Circuit 2. Line reactor is remote switchable. | 0 | 0.2663% | 0 | 0.01807
GEN-2019-001 | 03 CENTRAL | TBD | ERIS | Switch Out Thistle Line Reactor Circuit 1 | Current Study | Switch out the Thistle 40 MVAR line reactor on the Clark County to Thistle 345 kV line Circuit 1. Line reactor is remote switchable. | 0 | 0.2663% | 0 | 0.01807
GEN-2019-001 | 03 CENTRAL | TBD | ERIS | Switch Out Thistle Line Reactor Circuit 2 | Current Study | Switch out the Thistle 40 MVAR line reactor on the Clark County to Thistle 345 kV line Circuit 2. Line reactor is remote switchable. | 0 | 0.2663% | 0 | 0.01807
GEN-2019-001 | 03 CENTRAL | TBD | ERIS | Switch Out Wichita Line Reactor Circuit 1 | Current Study | Switch out the Wichita 25 MVAR line reactor on the Buffalo to Wichita 345 kV line Circuit 1. Line reactor is remote switchable. | 0 | 0.2663% | 0 | 0.01807
GEN-2019-001 | 03 CENTRAL | TBD | ERIS | Switch Out Wichita Line Reactor Circuit 2 | Current Study | Switch out the Wichita 25 MVAR line reactor on the Buffalo to Wichita 345 kV line Circuit 2. Line reactor is remote switchable. | 0 | 0.2663% | 0 | 0.01807
GEN-2019-014 | 03 CENTRAL | TBD | ERIS | Benton to Wichita 345 kV Terminal Equipment Upgrades | Current Study | Upgrade terminal equipment at Benton to Wichita 345 kV substations to increase minimum Rate A/Rate B to 915/1145 MVA | 48139.2876 | 6.212% | 775000 | 0.09266
GEN-2019-014 | 03 CENTRAL | TBD | ERIS | Holcomb to Finney 345 kV Second Line Build | Current Study | Build a second 345 kV line from Holcomb to Finney 345 kV | 4406902.3297 | 32.89% | 13400000 | 0.10564
GEN-2019-014 | 03 CENTRAL | TBD | ERIS | Jagger 115 kV Reactive Support | Current Study | Install +12 MVAR capacitor bank(s) at Jagger 115 kV | 2400000 | 100% | 2400000 | 0.03363
GEN-2019-014 | 03 CENTRAL | TBD | ERIS | Switch Out Buffalo Line Reactor Circuit 1 | Current Study | Switch out the Buffalo 50 MVAR line reactor on the Buffalo to Thistle 345 kV line Circuit 1. Line reactor is remote switchable. | 0 | 21.43% | 0 | 0.29081
GEN-2019-014 | 03 CENTRAL | TBD | ERIS | Switch Out Buffalo Line Reactor Circuit 2 | Current Study | Switch out the Buffalo 50 MVAR line reactor on the Buffalo to Thistle 345 kV line Circuit 2. Line reactor is remote switchable. | 0 | 21.43% | 0 | 0.29081
GEN-2019-014 | 03 CENTRAL | TBD | ERIS | Switch Out Thistle Line Reactor Circuit 1 | Current Study | Switch out the Thistle 40 MVAR line reactor on the Clark County to Thistle 345 kV line Circuit 1. Line reactor is remote switchable. | 0 | 21.43% | 0 | 0.29081
GEN-2019-014 | 03 CENTRAL | TBD | ERIS | Switch Out Thistle Line Reactor Circuit 2 | Current Study | Switch out the Thistle 40 MVAR line reactor on the Clark County to Thistle 345 kV line Circuit 2. Line reactor is remote switchable. | 0 | 21.43% | 0 | 0.29081
GEN-2019-014 | 03 CENTRAL | TBD | ERIS | Switch Out Wichita Line Reactor Circuit 1 | Current Study | Switch out the Wichita 25 MVAR line reactor on the Buffalo to Wichita 345 kV line Circuit 1. Line reactor is remote switchable. | 0 | 21.43% | 0 | 0.29081
GEN-2019-014 | 03 CENTRAL | TBD | ERIS | Switch Out Wichita Line Reactor Circuit 2 | Current Study | Switch out the Wichita 25 MVAR line reactor on the Buffalo to Wichita 345 kV line Circuit 2. Line reactor is remote switchable. | 0 | 21.43% | 0 | 0.29081
GEN-2019-030 | 03 CENTRAL | TBD | ERIS | Benton to Wichita 345 kV Terminal Equipment Upgrades | Current Study | Upgrade terminal equipment at Benton to Wichita 345 kV substations to increase minimum Rate A/Rate B to 915/1145 MVA | 102694.0989 | 13.25% | 775000 | 0.09805
GEN-2019-030 | 03 CENTRAL | TBD | ERIS | Holcomb to Finney 345 kV Second Line Build | Current Study | Build a second 345 kV line from Holcomb to Finney 345 kV | 695506.303 | 5.19% | 13400000 | 0.00827
GEN-2019-030 | 03 CENTRAL | TBD | ERIS | Switch Out Buffalo Line Reactor Circuit 1 | Current Study | Switch out the Buffalo 50 MVAR line reactor on the Buffalo to Thistle 345 kV line Circuit 1. Line reactor is remote switchable. | 0 | 19.3% | 0 | 0.12992
GEN-2019-030 | 03 CENTRAL | TBD | ERIS | Switch Out Buffalo Line Reactor Circuit 2 | Current Study | Switch out the Buffalo 50 MVAR line reactor on the Buffalo to Thistle 345 kV line Circuit 2. Line reactor is remote switchable. | 0 | 19.3% | 0 | 0.12992
GEN-2019-030 | 03 CENTRAL | TBD | ERIS | Switch Out Thistle Line Reactor Circuit 1 | Current Study | Switch out the Thistle 40 MVAR line reactor on the Clark County to Thistle 345 kV line Circuit 1. Line reactor is remote switchable. | 0 | 19.3% | 0 | 0.12992
GEN-2019-030 | 03 CENTRAL | TBD | ERIS | Switch Out Thistle Line Reactor Circuit 2 | Current Study | Switch out the Thistle 40 MVAR line reactor on the Clark County to Thistle 345 kV line Circuit 2. Line reactor is remote switchable. | 0 | 19.3% | 0 | 0.12992
GEN-2019-030 | 03 CENTRAL | TBD | ERIS | Switch Out Wichita Line Reactor Circuit 1 | Current Study | Switch out the Wichita 25 MVAR line reactor on the Buffalo to Wichita 345 kV line Circuit 1. Line reactor is remote switchable. | 0 | 19.3% | 0 | 0.12992
GEN-2019-030 | 03 CENTRAL | TBD | ERIS | Switch Out Wichita Line Reactor Circuit 2 | Current Study | Switch out the Wichita 25 MVAR line reactor on the Buffalo to Wichita 345 kV line Circuit 2. Line reactor is remote switchable. | 0 | 19.3% | 0 | 0.12992
GEN-2019-044 | 03 CENTRAL | TBD | ERIS | Benton to Wichita 345 kV Terminal Equipment Upgrades | Current Study | Upgrade terminal equipment at Benton to Wichita 345 kV substations to increase minimum Rate A/Rate B to 915/1145 MVA | 48681.6728 | 6.282% | 775000 | 0.11713
GEN-2019-044 | 03 CENTRAL | TBD | ERIS | Cudahy to Crooked Creek 115 kV Terminal Equipment Upgrades | Current Study | Upgrade terminal equipment at Cudahy 115 kV substation to increase minimum summer/emergency rating to 135 MVA | 250000 | 100% | 250000 | 0.12037
GEN-2019-044 | 03 CENTRAL | TBD | ERIS | Holcomb to Finney 345 kV Second Line Build | Current Study | Build a second 345 kV line from Holcomb to Finney 345 kV | 808627.3643 | 6.035% | 13400000 | 0.02423
GEN-2019-044 | 03 CENTRAL | TBD | ERIS | Switch Out Buffalo Line Reactor Circuit 1 | Current Study | Switch out the Buffalo 50 MVAR line reactor on the Buffalo to Thistle 345 kV line Circuit 1. Line reactor is remote switchable. | 0 | 9.142% | 0 | 0.15509
GEN-2019-044 | 03 CENTRAL | TBD | ERIS | Switch Out Buffalo Line Reactor Circuit 2 | Current Study | Switch out the Buffalo 50 MVAR line reactor on the Buffalo to Thistle 345 kV line Circuit 2. Line reactor is remote switchable. | 0 | 9.142% | 0 | 0.15509
GEN-2019-044 | 03 CENTRAL | TBD | ERIS | Switch Out Thistle Line Reactor Circuit 1 | Current Study | Switch out the Thistle 40 MVAR line reactor on the Clark County to Thistle 345 kV line Circuit 1. Line reactor is remote switchable. | 0 | 9.142% | 0 | 0.15509
GEN-2019-044 | 03 CENTRAL | TBD | ERIS | Switch Out Thistle Line Reactor Circuit 2 | Current Study | Switch out the Thistle 40 MVAR line reactor on the Clark County to Thistle 345 kV line Circuit 2. Line reactor is remote switchable. | 0 | 9.142% | 0 | 0.15509
GEN-2019-044 | 03 CENTRAL | TBD | ERIS | Switch Out Wichita Line Reactor Circuit 1 | Current Study | Switch out the Wichita 25 MVAR line reactor on the Buffalo to Wichita 345 kV line Circuit 1. Line reactor is remote switchable. | 0 | 9.142% | 0 | 0.15509
GEN-2019-044 | 03 CENTRAL | TBD | ERIS | Switch Out Wichita Line Reactor Circuit 2 | Current Study | Switch out the Wichita 25 MVAR line reactor on the Buffalo to Wichita 345 kV line Circuit 2. Line reactor is remote switchable. | 0 | 9.142% | 0 | 0.15509
GEN-2019-051 | 03 CENTRAL | TBD | ERIS | Benton to Wichita 345 kV Terminal Equipment Upgrades | Current Study | Upgrade terminal equipment at Benton to Wichita 345 kV substations to increase minimum Rate A/Rate B to 915/1145 MVA | 19903.2523 | 2.568% | 775000 | 0.11972
GEN-2019-051 | 03 CENTRAL | TBD | ERIS | Ellsworth Tap to Great Bend 115 kV Equipment Upgrades | Current Study | Upgrade equipment at Ellsworth Tap to Great Bend 115 kV substations to increase minimum summer/emergency rating to 105 MVA | 109940.5092 | 14.66% | 750000 | 0.09197
GEN-2019-051 | 03 CENTRAL | TBD | ERIS | Great Bend Frey Street to 2ND-KS 115 kV Rebuild | Current Study | Rebuild the Great Bend Frey Street to 2ND-KS 115 kV 1.82 mile line | 321756.1047 | 21.05% | 1528341.4976 | 0.29699
GEN-2019-051 | 03 CENTRAL | TBD | ERIS | Great Bend Frey Street to Great Bend Northwest 115 kV Rebuild | Current Study | Rebuild the Great Bend Frey Street to Great Bend Northwest 115 kV 5.1 mile line | 901624.2496 | 21.05% | 4282715.1854 | 0.33135
GEN-2019-051 | 03 CENTRAL | TBD | ERIS | Great Bend Tap to 2ND-KS 115 kV Rebuild | Current Study | Rebuild the Great Bend Tap to 2ND-KS 115 kV 3.79 mile line | 670030.5698 | 21.05% | 3182645.2064 | 0.29699
GEN-2019-051 | 03 CENTRAL | TBD | ERIS | Great Bend to Great Bend Northwest 115 kV Rebuild | Current Study | Rebuild the Great Bend to Great Bend Northwest 115 kV 3.58 mile line | 632904.8654 | 21.05% | 3006298.1106 | 0.33103
GEN-2019-051 | 03 CENTRAL | TBD | ERIS | Holcomb to Finney 345 kV Second Line Build | Current Study | Build a second 345 kV line from Holcomb to Finney 345 kV | 767311.612 | 5.726% | 13400000 | 0.05748
GEN-2019-051 | 03 CENTRAL | TBD | ERIS | Switch Out Buffalo Line Reactor Circuit 1 | Current Study | Switch out the Buffalo 50 MVAR line reactor on the Buffalo to Thistle 345 kV line Circuit 1. Line reactor is remote switchable. | 0 | 2.278% | 0 | 0.09659
GEN-2019-051 | 03 CENTRAL | TBD | ERIS | Switch Out Buffalo Line Reactor Circuit 2 | Current Study | Switch out the Buffalo 50 MVAR line reactor on the Buffalo to Thistle 345 kV line Circuit 2. Line reactor is remote switchable. | 0 | 2.278% | 0 | 0.09659
GEN-2019-051 | 03 CENTRAL | TBD | ERIS | Switch Out Thistle Line Reactor Circuit 1 | Current Study | Switch out the Thistle 40 MVAR line reactor on the Clark County to Thistle 345 kV line Circuit 1. Line reactor is remote switchable. | 0 | 2.278% | 0 | 0.09659
GEN-2019-051 | 03 CENTRAL | TBD | ERIS | Switch Out Thistle Line Reactor Circuit 2 | Current Study | Switch out the Thistle 40 MVAR line reactor on the Clark County to Thistle 345 kV line Circuit 2. Line reactor is remote switchable. | 0 | 2.278% | 0 | 0.09659
GEN-2019-051 | 03 CENTRAL | TBD | ERIS | Switch Out Wichita Line Reactor Circuit 1 | Current Study | Switch out the Wichita 25 MVAR line reactor on the Buffalo to Wichita 345 kV line Circuit 1. Line reactor is remote switchable. | 0 | 2.278% | 0 | 0.09659
GEN-2019-051 | 03 CENTRAL | TBD | ERIS | Switch Out Wichita Line Reactor Circuit 2 | Current Study | Switch out the Wichita 25 MVAR line reactor on the Buffalo to Wichita 345 kV line Circuit 2. Line reactor is remote switchable. | 0 | 2.278% | 0 | 0.09659
GEN-2019-053 | 03 CENTRAL | TBD | ERIS | Benton to Wichita 345 kV Terminal Equipment Upgrades | Current Study | Upgrade terminal equipment at Benton to Wichita 345 kV substations to increase minimum Rate A/Rate B to 915/1145 MVA | 24586.0527 | 3.172% | 775000 | 0.11831
GEN-2019-053 | 03 CENTRAL | TBD | ERIS | Holcomb to Finney 345 kV Second Line Build | Current Study | Build a second 345 kV line from Holcomb to Finney 345 kV | 959139.515 | 7.158% | 13400000 | 0.05748
GEN-2019-053 | 03 CENTRAL | TBD | ERIS | Switch Out Buffalo Line Reactor Circuit 1 | Current Study | Switch out the Buffalo 50 MVAR line reactor on the Buffalo to Thistle 345 kV line Circuit 1. Line reactor is remote switchable. | 0 | 3.461% | 0 | 0.11743
GEN-2019-053 | 03 CENTRAL | TBD | ERIS | Switch Out Buffalo Line Reactor Circuit 2 | Current Study | Switch out the Buffalo 50 MVAR line reactor on the Buffalo to Thistle 345 kV line Circuit 2. Line reactor is remote switchable. | 0 | 3.461% | 0 | 0.11743
GEN-2019-053 | 03 CENTRAL | TBD | ERIS | Switch Out Thistle Line Reactor Circuit 1 | Current Study | Switch out the Thistle 40 MVAR line reactor on the Clark County to Thistle 345 kV line Circuit 1. Line reactor is remote switchable. | 0 | 3.461% | 0 | 0.11743
GEN-2019-053 | 03 CENTRAL | TBD | ERIS | Switch Out Thistle Line Reactor Circuit 2 | Current Study | Switch out the Thistle 40 MVAR line reactor on the Clark County to Thistle 345 kV line Circuit 2. Line reactor is remote switchable. | 0 | 3.461% | 0 | 0.11743
GEN-2019-053 | 03 CENTRAL | TBD | ERIS | Switch Out Wichita Line Reactor Circuit 1 | Current Study | Switch out the Wichita 25 MVAR line reactor on the Buffalo to Wichita 345 kV line Circuit 1. Line reactor is remote switchable. | 0 | 3.461% | 0 | 0.11743
GEN-2019-053 | 03 CENTRAL | TBD | ERIS | Switch Out Wichita Line Reactor Circuit 2 | Current Study | Switch out the Wichita 25 MVAR line reactor on the Buffalo to Wichita 345 kV line Circuit 2. Line reactor is remote switchable. | 0 | 3.461% | 0 | 0.11743
GEN-2019-054 | 03 CENTRAL | TBD | ERIS | Benton to Wichita 345 kV Terminal Equipment Upgrades | Current Study | Upgrade terminal equipment at Benton to Wichita 345 kV substations to increase minimum Rate A/Rate B to 915/1145 MVA | 76395.2726 | 9.857% | 775000 | 0.12254
GEN-2019-054 | 03 CENTRAL | TBD | ERIS | Ellsworth Tap to Great Bend 115 kV Equipment Upgrades | Current Study | Upgrade equipment at Ellsworth Tap to Great Bend 115 kV substations to increase minimum summer/emergency rating to 105 MVA | 170836.9361 | 22.78% | 750000 | 0.03811
GEN-2019-054 | 03 CENTRAL | TBD | ERIS | Holcomb to Finney 345 kV Second Line Build | Current Study | Build a second 345 kV line from Holcomb to Finney 345 kV | 205243.8419 | 1.532% | 13400000 | 0.0041
GEN-2019-054 | 03 CENTRAL | TBD | ERIS | Switch Out Buffalo Line Reactor Circuit 1 | Current Study | Switch out the Buffalo 50 MVAR line reactor on the Buffalo to Thistle 345 kV line Circuit 1. Line reactor is remote switchable. | 0 | 7.923% | 0 | 0.0896
GEN-2019-054 | 03 CENTRAL | TBD | ERIS | Switch Out Buffalo Line Reactor Circuit 2 | Current Study | Switch out the Buffalo 50 MVAR line reactor on the Buffalo to Thistle 345 kV line Circuit 2. Line reactor is remote switchable. | 0 | 7.923% | 0 | 0.0896
GEN-2019-054 | 03 CENTRAL | TBD | ERIS | Switch Out Thistle Line Reactor Circuit 1 | Current Study | Switch out the Thistle 40 MVAR line reactor on the Clark County to Thistle 345 kV line Circuit 1. Line reactor is remote switchable. | 0 | 7.923% | 0 | 0.0896
GEN-2019-054 | 03 CENTRAL | TBD | ERIS | Switch Out Thistle Line Reactor Circuit 2 | Current Study | Switch out the Thistle 40 MVAR line reactor on the Clark County to Thistle 345 kV line Circuit 2. Line reactor is remote switchable. | 0 | 7.923% | 0 | 0.0896
GEN-2019-054 | 03 CENTRAL | TBD | ERIS | Switch Out Wichita Line Reactor Circuit 1 | Current Study | Switch out the Wichita 25 MVAR line reactor on the Buffalo to Wichita 345 kV line Circuit 1. Line reactor is remote switchable. | 0 | 7.923% | 0 | 0.0896
GEN-2019-054 | 03 CENTRAL | TBD | ERIS | Switch Out Wichita Line Reactor Circuit 2 | Current Study | Switch out the Wichita 25 MVAR line reactor on the Buffalo to Wichita 345 kV line Circuit 2. Line reactor is remote switchable. | 0 | 7.923% | 0 | 0.0896
GEN-2019-055 | 03 CENTRAL | TBD | ERIS | Benton to Wichita 345 kV Terminal Equipment Upgrades | Current Study | Upgrade terminal equipment at Benton to Wichita 345 kV substations to increase minimum Rate A/Rate B to 915/1145 MVA | 73758.1581 | 9.517% | 775000 | 0.11831
GEN-2019-055 | 03 CENTRAL | TBD | ERIS | Holcomb to Finney 345 kV Second Line Build | Current Study | Build a second 345 kV line from Holcomb to Finney 345 kV | 699330.8468 | 5.219% | 13400000 | 0.01397
GEN-2019-055 | 03 CENTRAL | TBD | ERIS | Switch Out Buffalo Line Reactor Circuit 1 | Current Study | Switch out the Buffalo 50 MVAR line reactor on the Buffalo to Thistle 345 kV line Circuit 1. Line reactor is remote switchable. | 0 | 10.38% | 0 | 0.11743
GEN-2019-055 | 03 CENTRAL | TBD | ERIS | Switch Out Buffalo Line Reactor Circuit 2 | Current Study | Switch out the Buffalo 50 MVAR line reactor on the Buffalo to Thistle 345 kV line Circuit 2. Line reactor is remote switchable. | 0 | 10.38% | 0 | 0.11743
GEN-2019-055 | 03 CENTRAL | TBD | ERIS | Switch Out Thistle Line Reactor Circuit 1 | Current Study | Switch out the Thistle 40 MVAR line reactor on the Clark County to Thistle 345 kV line Circuit 1. Line reactor is remote switchable. | 0 | 10.38% | 0 | 0.11743
GEN-2019-055 | 03 CENTRAL | TBD | ERIS | Switch Out Thistle Line Reactor Circuit 2 | Current Study | Switch out the Thistle 40 MVAR line reactor on the Clark County to Thistle 345 kV line Circuit 2. Line reactor is remote switchable. | 0 | 10.38% | 0 | 0.11743
GEN-2019-055 | 03 CENTRAL | TBD | ERIS | Switch Out Wichita Line Reactor Circuit 1 | Current Study | Switch out the Wichita 25 MVAR line reactor on the Buffalo to Wichita 345 kV line Circuit 1. Line reactor is remote switchable. | 0 | 10.38% | 0 | 0.11743
GEN-2019-055 | 03 CENTRAL | TBD | ERIS | Switch Out Wichita Line Reactor Circuit 2 | Current Study | Switch out the Wichita 25 MVAR line reactor on the Buffalo to Wichita 345 kV line Circuit 2. Line reactor is remote switchable. | 0 | 10.38% | 0 | 0.11743
GEN-2019-058 | 03 CENTRAL | TBD | ERIS | Benton to Wichita 345 kV Terminal Equipment Upgrades | Current Study | Upgrade terminal equipment at Benton to Wichita 345 kV substations to increase minimum Rate A/Rate B to 915/1145 MVA | 80628.3712 | 10.4% | 775000 | 0.12933
GEN-2019-058 | 03 CENTRAL | TBD | ERIS | Holcomb to Finney 345 kV Second Line Build | Current Study | Build a second 345 kV line from Holcomb to Finney 345 kV | 2511984.3874 | 18.75% | 13400000 | 0.05018
GEN-2019-058 | 03 CENTRAL | TBD | ERIS | Switch Out Buffalo Line Reactor Circuit 1 | Current Study | Switch out the Buffalo 50 MVAR line reactor on the Buffalo to Thistle 345 kV line Circuit 1. Line reactor is remote switchable. | 0 | 8.902% | 0 | 0.10067
GEN-2019-058 | 03 CENTRAL | TBD | ERIS | Switch Out Buffalo Line Reactor Circuit 2 | Current Study | Switch out the Buffalo 50 MVAR line reactor on the Buffalo to Thistle 345 kV line Circuit 2. Line reactor is remote switchable. | 0 | 8.902% | 0 | 0.10067
GEN-2019-058 | 03 CENTRAL | TBD | ERIS | Switch Out Thistle Line Reactor Circuit 1 | Current Study | Switch out the Thistle 40 MVAR line reactor on the Clark County to Thistle 345 kV line Circuit 1. Line reactor is remote switchable. | 0 | 8.902% | 0 | 0.10067
GEN-2019-058 | 03 CENTRAL | TBD | ERIS | Switch Out Thistle Line Reactor Circuit 2 | Current Study | Switch out the Thistle 40 MVAR line reactor on the Clark County to Thistle 345 kV line Circuit 2. Line reactor is remote switchable. | 0 | 8.902% | 0 | 0.10067
GEN-2019-058 | 03 CENTRAL | TBD | ERIS | Switch Out Wichita Line Reactor Circuit 1 | Current Study | Switch out the Wichita 25 MVAR line reactor on the Buffalo to Wichita 345 kV line Circuit 1. Line reactor is remote switchable. | 0 | 8.902% | 0 | 0.10067
GEN-2019-058 | 03 CENTRAL | TBD | ERIS | Switch Out Wichita Line Reactor Circuit 2 | Current Study | Switch out the Wichita 25 MVAR line reactor on the Buffalo to Wichita 345 kV line Circuit 2. Line reactor is remote switchable. | 0 | 8.902% | 0 | 0.10067
GEN-2019-062 | 03 CENTRAL | TBD | ERIS | Switch Out Buffalo Line Reactor Circuit 1 | Current Study | Switch out the Buffalo 50 MVAR line reactor on the Buffalo to Thistle 345 kV line Circuit 1. Line reactor is remote switchable. | 0 | 0.6388% | 0 | 0.01204
GEN-2019-062 | 03 CENTRAL | TBD | ERIS | Switch Out Buffalo Line Reactor Circuit 2 | Current Study | Switch out the Buffalo 50 MVAR line reactor on the Buffalo to Thistle 345 kV line Circuit 2. Line reactor is remote switchable. | 0 | 0.6388% | 0 | 0.01204
GEN-2019-062 | 03 CENTRAL | TBD | ERIS | Switch Out Thistle Line Reactor Circuit 1 | Current Study | Switch out the Thistle 40 MVAR line reactor on the Clark County to Thistle 345 kV line Circuit 1. Line reactor is remote switchable. | 0 | 0.6388% | 0 | 0.01204
GEN-2019-062 | 03 CENTRAL | TBD | ERIS | Switch Out Thistle Line Reactor Circuit 2 | Current Study | Switch out the Thistle 40 MVAR line reactor on the Clark County to Thistle 345 kV line Circuit 2. Line reactor is remote switchable. | 0 | 0.6388% | 0 | 0.01204
GEN-2019-062 | 03 CENTRAL | TBD | ERIS | Switch Out Wichita Line Reactor Circuit 1 | Current Study | Switch out the Wichita 25 MVAR line reactor on the Buffalo to Wichita 345 kV line Circuit 1. Line reactor is remote switchable. | 0 | 0.6388% | 0 | 0.01204
GEN-2019-062 | 03 CENTRAL | TBD | ERIS | Switch Out Wichita Line Reactor Circuit 2 | Current Study | Switch out the Wichita 25 MVAR line reactor on the Buffalo to Wichita 345 kV line Circuit 2. Line reactor is remote switchable. | 0 | 0.6388% | 0 | 0.01204
GEN-2019-063 | 03 CENTRAL | TBD | ERIS | Benton to Wichita 345 kV Terminal Equipment Upgrades | Current Study | Upgrade terminal equipment at Benton to Wichita 345 kV substations to increase minimum Rate A/Rate B to 915/1145 MVA | 26876.1237 | 3.468% | 775000 | 0.12933
GEN-2019-063 | 03 CENTRAL | TBD | ERIS | Holcomb to Finney 345 kV Second Line Build | Current Study | Build a second 345 kV line from Holcomb to Finney 345 kV | 837328.1291 | 6.249% | 13400000 | 0.05018
GEN-2019-063 | 03 CENTRAL | TBD | ERIS | Switch Out Buffalo Line Reactor Circuit 1 | Current Study | Switch out the Buffalo 50 MVAR line reactor on the Buffalo to Thistle 345 kV line Circuit 1. Line reactor is remote switchable. | 0 | 2.967% | 0 | 0.10067
GEN-2019-063 | 03 CENTRAL | TBD | ERIS | Switch Out Buffalo Line Reactor Circuit 2 | Current Study | Switch out the Buffalo 50 MVAR line reactor on the Buffalo to Thistle 345 kV line Circuit 2. Line reactor is remote switchable. | 0 | 2.967% | 0 | 0.10067
GEN-2019-063 | 03 CENTRAL | TBD | ERIS | Switch Out Thistle Line Reactor Circuit 1 | Current Study | Switch out the Thistle 40 MVAR line reactor on the Clark County to Thistle 345 kV line Circuit 1. Line reactor is remote switchable. | 0 | 2.967% | 0 | 0.10067
GEN-2019-063 | 03 CENTRAL | TBD | ERIS | Switch Out Thistle Line Reactor Circuit 2 | Current Study | Switch out the Thistle 40 MVAR line reactor on the Clark County to Thistle 345 kV line Circuit 2. Line reactor is remote switchable. | 0 | 2.967% | 0 | 0.10067
GEN-2019-063 | 03 CENTRAL | TBD | ERIS | Switch Out Wichita Line Reactor Circuit 1 | Current Study | Switch out the Wichita 25 MVAR line reactor on the Buffalo to Wichita 345 kV line Circuit 1. Line reactor is remote switchable. | 0 | 2.967% | 0 | 0.10067
GEN-2019-063 | 03 CENTRAL | TBD | ERIS | Switch Out Wichita Line Reactor Circuit 2 | Current Study | Switch out the Wichita 25 MVAR line reactor on the Buffalo to Wichita 345 kV line Circuit 2. Line reactor is remote switchable. | 0 | 2.967% | 0 | 0.10067
GEN-2019-068 | 03 CENTRAL | TBD | ERIS | Benton to Wichita 345 kV Terminal Equipment Upgrades | Current Study | Upgrade terminal equipment at Benton to Wichita 345 kV substations to increase minimum Rate A/Rate B to 915/1145 MVA | 25465.0909 | 3.286% | 775000 | 0.12254
GEN-2019-068 | 03 CENTRAL | TBD | ERIS | Ellsworth Tap to Great Bend 115 kV Equipment Upgrades | Current Study | Upgrade equipment at Ellsworth Tap to Great Bend 115 kV substations to increase minimum summer/emergency rating to 105 MVA | 56945.6454 | 7.593% | 750000 | 0.03811
GEN-2019-068 | 03 CENTRAL | TBD | ERIS | Holcomb to Finney 345 kV Second Line Build | Current Study | Build a second 345 kV line from Holcomb to Finney 345 kV | 837328.1291 | 6.249% | 13400000 | 0.05018
GEN-2019-068 | 03 CENTRAL | TBD | ERIS | Switch Out Buffalo Line Reactor Circuit 1 | Current Study | Switch out the Buffalo 50 MVAR line reactor on the Buffalo to Thistle 345 kV line Circuit 1. Line reactor is remote switchable. | 0 | 2.641% | 0 | 0.0896
GEN-2019-068 | 03 CENTRAL | TBD | ERIS | Switch Out Buffalo Line Reactor Circuit 2 | Current Study | Switch out the Buffalo 50 MVAR line reactor on the Buffalo to Thistle 345 kV line Circuit 2. Line reactor is remote switchable. | 0 | 2.641% | 0 | 0.0896
GEN-2019-068 | 03 CENTRAL | TBD | ERIS | Switch Out Thistle Line Reactor Circuit 1 | Current Study | Switch out the Thistle 40 MVAR line reactor on the Clark County to Thistle 345 kV line Circuit 1. Line reactor is remote switchable. | 0 | 2.641% | 0 | 0.0896
GEN-2019-068 | 03 CENTRAL | TBD | ERIS | Switch Out Thistle Line Reactor Circuit 2 | Current Study | Switch out the Thistle 40 MVAR line reactor on the Clark County to Thistle 345 kV line Circuit 2. Line reactor is remote switchable. | 0 | 2.641% | 0 | 0.0896
GEN-2019-068 | 03 CENTRAL | TBD | ERIS | Switch Out Wichita Line Reactor Circuit 1 | Current Study | Switch out the Wichita 25 MVAR line reactor on the Buffalo to Wichita 345 kV line Circuit 1. Line reactor is remote switchable. | 0 | 2.641% | 0 | 0.0896
GEN-2019-068 | 03 CENTRAL | TBD | ERIS | Switch Out Wichita Line Reactor Circuit 2 | Current Study | Switch out the Wichita 25 MVAR line reactor on the Buffalo to Wichita 345 kV line Circuit 2. Line reactor is remote switchable. | 0 | 2.641% | 0 | 0.0896
GEN-2018-117 | 04 SOUTHEAST | TBD | ERIS | Sweetwater to Chisholm 230 kV Line Rebuild | Current Study | Rebuild the Sweetwater to Chisholm 230 kV 11.15 mile Line to a minimum rating of 581 MVA | 17394000 | 60% | 28990000 | 0.79582
GEN-2018-117 | 04 SOUTHEAST | TBD | ERIS | Sweetwater to Demarcation 230 kV Line Rebuild | Current Study | Rebuild the Sweetwater to Demarcation 230 kV 5 mile Line to a minimum rating of 588 MVA | 7800000 | 60% | 13000000 | 0.20418
GEN-2018-117 | 04 SOUTHEAST | TBD | ERIS | Wheeler to Demarcation 230 kV Line Rebuild | Current Study | Rebuild the Wheeler to Demarcation 230 kV 13.92 mile Line to a minimum rating of 583 MVA | 8352000 | 60% | 13920000 | 0.20418
GEN-2018-117 | 04 SOUTHEAST | TBD | ERIS | Wheeler to Grapevine 230 kV Line Model Correction | Current Study | Wheeler to Grapevine 230 kV line rating updated to summer/emergency and winter/emergency ratings of 500/550 MVA and 510/611 MVA | 0 | 60% | 0 | 0.16994
GEN-2019-013 | 04 SOUTHEAST | TBD | ERIS | Sweetwater to Chisholm 230 kV Line Rebuild | Current Study | Rebuild the Sweetwater to Chisholm 230 kV 11.15 mile Line to a minimum rating of 581 MVA | 5798000 | 20% | 28990000 | 0.79582
GEN-2019-013 | 04 SOUTHEAST | TBD | ERIS | Sweetwater to Demarcation 230 kV Line Rebuild | Current Study | Rebuild the Sweetwater to Demarcation 230 kV 5 mile Line to a minimum rating of 588 MVA | 2600000 | 20% | 13000000 | 0.20418
GEN-2019-013 | 04 SOUTHEAST | TBD | ERIS | Wheeler to Demarcation 230 kV Line Rebuild | Current Study | Rebuild the Wheeler to Demarcation 230 kV 13.92 mile Line to a minimum rating of 583 MVA | 2784000 | 20% | 13920000 | 0.20418
GEN-2019-013 | 04 SOUTHEAST | TBD | ERIS | Wheeler to Grapevine 230 kV Line Model Correction | Current Study | Wheeler to Grapevine 230 kV line rating updated to summer/emergency and winter/emergency ratings of 500/550 MVA and 510/611 MVA | 0 | 20% | 0 | 0.16994
GEN-2019-066 | 04 SOUTHEAST | TBD | ERIS | Sweetwater to Chisholm 230 kV Line Rebuild | Current Study | Rebuild the Sweetwater to Chisholm 230 kV 11.15 mile Line to a minimum rating of 581 MVA | 5798000 | 20% | 28990000 | 0.79582
GEN-2019-066 | 04 SOUTHEAST | TBD | ERIS | Sweetwater to Demarcation 230 kV Line Rebuild | Current Study | Rebuild the Sweetwater to Demarcation 230 kV 5 mile Line to a minimum rating of 588 MVA | 2600000 | 20% | 13000000 | 0.20418
GEN-2019-066 | 04 SOUTHEAST | TBD | ERIS | Wheeler to Demarcation 230 kV Line Rebuild | Current Study | Rebuild the Wheeler to Demarcation 230 kV 13.92 mile Line to a minimum rating of 583 MVA | 2784000 | 20% | 13920000 | 0.20418
GEN-2019-066 | 04 SOUTHEAST | TBD | ERIS | Wheeler to Grapevine 230 kV Line Model Correction | Current Study | Wheeler to Grapevine 230 kV line rating updated to summer/emergency and winter/emergency ratings of 500/550 MVA and 510/611 MVA | 0 | 20% | 0 | 0.16994
GEN-2018-073 | 04 SOUTHEAST / 05 SOUTHWEST | TBD | ERIS | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Current Study | Build a 345 kV 247.2 mile double circuit line from Crawfish to Lawton Eastside connecting via G18-015-Tap for line 1 and G18-092-Tap for line 2 | 53342600.8553 | 12.91% | 413142888 | 0.15855
GEN-2018-081 | 04 SOUTHEAST / 05 SOUTHWEST | TBD | ERIS | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Current Study | Build a 345 kV 247.2 mile double circuit line from Crawfish to Lawton Eastside connecting via G18-015-Tap for line 1 and G18-092-Tap for line 2 | 24280892.4865 | 5.877% | 413142888 | 0.1031
GEN-2018-082 | 04 SOUTHEAST / 05 SOUTHWEST | TBD | ERIS | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Current Study | Build a 345 kV 247.2 mile double circuit line from Crawfish to Lawton Eastside connecting via G18-015-Tap for line 1 and G18-092-Tap for line 2 | 5404845.2489 | 1.308% | 413142888 | 0.01868
GEN-2018-089 | 04 SOUTHEAST / 05 SOUTHWEST | TBD | ERIS | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Current Study | Build a 345 kV 247.2 mile double circuit line from Crawfish to Lawton Eastside connecting via G18-015-Tap for line 1 and G18-092-Tap for line 2 | 25073895.6017 | 6.069% | 413142888 | 0.09506
GEN-2018-092 | 04 SOUTHEAST / 05 SOUTHWEST | TBD | ERIS | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Current Study | Build a 345 kV 247.2 mile double circuit line from Crawfish to Lawton Eastside connecting via G18-015-Tap for line 1 and G18-092-Tap for line 2 | 89186271.6842 | 21.59% | 413142888 | 0.16568
GEN-2018-097 | 04 SOUTHEAST / 05 SOUTHWEST | TBD | ERIS | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Current Study | Build a 345 kV 247.2 mile double circuit line from Crawfish to Lawton Eastside connecting via G18-015-Tap for line 1 and G18-092-Tap for line 2 | 13827694.0722 | 3.347% | 413142888 | 0.10275
GEN-2018-099 | 04 SOUTHEAST / 05 SOUTHWEST | TBD | ERIS | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Current Study | Build a 345 kV 247.2 mile double circuit line from Crawfish to Lawton Eastside connecting via G18-015-Tap for line 1 and G18-092-Tap for line 2 | 39189905.5063 | 9.486% | 413142888 | 0.09707
GEN-2018-111 | 04 SOUTHEAST / 05 SOUTHWEST | TBD | ERIS | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Current Study | Build a 345 kV 247.2 mile double circuit line from Crawfish to Lawton Eastside connecting via G18-015-Tap for line 1 and G18-092-Tap for line 2 | 10370770.5542 | 2.51% | 413142888 | 0.10275
GEN-2018-112 | 04 SOUTHEAST / 05 SOUTHWEST | TBD | ERIS | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Current Study | Build a 345 kV 247.2 mile double circuit line from Crawfish to Lawton Eastside connecting via G18-015-Tap for line 1 and G18-092-Tap for line 2 | 25581234.0336 | 6.192% | 413142888 | 0.10275
GEN-2018-124 | 04 SOUTHEAST / 05 SOUTHWEST | TBD | ERIS | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Current Study | Build a 345 kV 247.2 mile double circuit line from Crawfish to Lawton Eastside connecting via G18-015-Tap for line 1 and G18-092-Tap for line 2 | 27655388.1445 | 6.694% | 413142888 | 0.10275
GEN-2019-003 | 04 SOUTHEAST / 05 SOUTHWEST | TBD | ERIS | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Current Study | Build a 345 kV 247.2 mile double circuit line from Crawfish to Lawton Eastside connecting via G18-015-Tap for line 1 and G18-092-Tap for line 2 | 20858622.3136 | 5.049% | 413142888 | 0.10333
GEN-2019-004 | 04 SOUTHEAST / 05 SOUTHWEST | TBD | ERIS | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Current Study | Build a 345 kV 247.2 mile double circuit line from Crawfish to Lawton Eastside connecting via G18-015-Tap for line 1 and G18-092-Tap for line 2 | 8748092.337 | 2.117% | 413142888 | 0.11608
GEN-2019-011 | 04 SOUTHEAST / 05 SOUTHWEST | TBD | ERIS | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Current Study | Build a 345 kV 247.2 mile double circuit line from Crawfish to Lawton Eastside connecting via G18-015-Tap for line 1 and G18-092-Tap for line 2 | 38693723.4329 | 9.366% | 413142888 | 0.12501
GEN-2019-021 | 04 SOUTHEAST / 05 SOUTHWEST | TBD | ERIS | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Current Study | Build a 345 kV 247.2 mile double circuit line from Crawfish to Lawton Eastside connecting via G18-015-Tap for line 1 and G18-092-Tap for line 2 | 6952874.1045 | 1.683% | 413142888 | 0.10333
GEN-2019-056 | 04 SOUTHEAST / 05 SOUTHWEST | TBD | ERIS | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Current Study | Build a 345 kV 247.2 mile double circuit line from Crawfish to Lawton Eastside connecting via G18-015-Tap for line 1 and G18-092-Tap for line 2 | 10101281.9179 | 2.445% | 413142888 | 0.07506
GEN-2019-074 | 04 SOUTHEAST / 05 SOUTHWEST | TBD | ERIS | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Current Study | Build a 345 kV 247.2 mile double circuit line from Crawfish to Lawton Eastside connecting via G18-015-Tap for line 1 and G18-092-Tap for line 2 | 13874795.7065 | 3.358% | 413142888 | 0.1031
GEN-2018-073 | 05 SOUTHWEST | TBD | ERIS | Lawton Eastside 345 kV Substation Upgrade to Double-Bus-Double-Breaker Configuration | Current Study | Upgrade the Lawton Eastside 345 kV substation to a double-bus-double-breaker configuration | 4457930.8121 | 12.1% | 36855504 | 0.14938
GEN-2018-073 | 05 SOUTHWEST | 81717 | ERIS | Multi - Border - Woodward 345 kV Tap (NTC 210627, NTC 210628) | Contingent | Install any necessary terminal equipment to support a new 345 kV line from Border to Woodward 345 kV substation with a summer emergency rating of 1792 MVA. Build 0.84-miles of new 345 kV line from a new tap on the Woodward to Border 345 kV line to Chisholm with a summer emergency rating of 1792 MVA. | 0 | 2.011% | 29784319 | 0.0117
GEN-2018-073 | 05 SOUTHWEST | TBD | ERIS | Potter to Chisholm 345 kV Double Circuit Line Build | Current Study | Build approximately 170 miles of new double circuit 345 kV lines from Potter County to Chisholm | 12300040.2954 | 4.906% | 250693500 | 0.03872
GEN-2018-073 | 05 SOUTHWEST | TBD | ERIS | Potter to Tolk 345 kV Double Circuit Line Build | Current Study | Build approximately 115 miles of new double circuit 345 kV lines from Potter County to Tolk | 10555774.0675 | 6.12% | 172477128 | 0.08254
GEN-2018-073 | 05 SOUTHWEST | TBD | ERIS | Tolk 345/230 kV Third Transformer Build | Current Study | Build a third 345/230 kV transformer at Tolk | 1104835.996 | 4.249% | 26000000 | 0.03498
GEN-2018-081 | 05 SOUTHWEST | TBD | ERIS | Lawton Eastside 345 kV Substation Upgrade to Double-Bus-Double-Breaker Configuration | Current Study | Upgrade the Lawton Eastside 345 kV substation to a double-bus-double-breaker configuration | 2029047.8902 | 5.505% | 36855504 | 0.09713
GEN-2018-081 | 05 SOUTHWEST | 81717 | ERIS | Multi - Border - Woodward 345 kV Tap (NTC 210627, NTC 210628) | Contingent | Install any necessary terminal equipment to support a new 345 kV line from Border to Woodward 345 kV substation with a summer emergency rating of 1792 MVA. Build 0.84-miles of new 345 kV line from a new tap on the Woodward to Border 345 kV line to Chisholm with a summer emergency rating of 1792 MVA. | 0 | 9.317% | 29784319 | 0.07745
GEN-2018-081 | 05 SOUTHWEST | TBD | ERIS | Potter to Chisholm 345 kV Double Circuit Line Build | Current Study | Build approximately 170 miles of new double circuit 345 kV lines from Potter County to Chisholm | 21809699.5485 | 8.7% | 250693500 | 0.09808
GEN-2018-081 | 05 SOUTHWEST | TBD | ERIS | Potter to Tolk 345 kV Double Circuit Line Build | Current Study | Build approximately 115 miles of new double circuit 345 kV lines from Potter County to Tolk | 14458494.6541 | 8.383% | 172477128 | 0.16151
GEN-2018-081 | 05 SOUTHWEST | TBD | ERIS | Tolk 345/230 kV Third Transformer Build | Current Study | Build a third 345/230 kV transformer at Tolk | 2715691.9317 | 10.44% | 26000000 | 0.12283
GEN-2018-089 | 05 SOUTHWEST | TBD | ERIS | Lawton Eastside 345 kV Substation Upgrade to Double-Bus-Double-Breaker Configuration | Current Study | Upgrade the Lawton Eastside 345 kV substation to a double-bus-double-breaker configuration | 2095185.7016 | 5.685% | 36855504 | 0.08955
GEN-2018-089 | 05 SOUTHWEST | 81717 | ERIS | Multi - Border - Woodward 345 kV Tap (NTC 210627, NTC 210628) | Contingent | Install any necessary terminal equipment to support a new 345 kV line from Border to Woodward 345 kV substation with a summer emergency rating of 1792 MVA. Build 0.84-miles of new 345 kV line from a new tap on the Woodward to Border 345 kV line to Chisholm with a summer emergency rating of 1792 MVA. | 0 | 10.83% | 29784319 | 0.08036
GEN-2018-089 | 05 SOUTHWEST | TBD | ERIS | Potter to Chisholm 345 kV Double Circuit Line Build | Current Study | Build approximately 170 miles of new double circuit 345 kV lines from Potter County to Chisholm | 22003603.0763 | 8.777% | 250693500 | 0.08835
GEN-2018-089 | 05 SOUTHWEST | TBD | ERIS | Potter to Tolk 345 kV Double Circuit Line Build | Current Study | Build approximately 115 miles of new double circuit 345 kV lines from Potter County to Tolk | 8832187.7863 | 5.121% | 172477128 | 0.08809
GEN-2018-089 | 05 SOUTHWEST | TBD | ERIS | Tolk 345/230 kV Third Transformer Build | Current Study | Build a third 345/230 kV transformer at Tolk | 1667752.7786 | 6.414% | 26000000 | 0.06735
GEN-2018-092 | 05 SOUTHWEST | TBD | ERIS | Lawton Eastside 345 kV Substation Upgrade to Double-Bus-Double-Breaker Configuration | Current Study | Upgrade the Lawton Eastside 345 kV substation to a double-bus-double-breaker configuration | 10234917.3337 | 27.77% | 36855504 | 0.21435
GEN-2018-092 | 05 SOUTHWEST | TBD | ERIS | Potter to Chisholm 345 kV Double Circuit Line Build | Current Study | Build approximately 170 miles of new double circuit 345 kV lines from Potter County to Chisholm | 7075064.5005 | 2.822% | 250693500 | 0.01392
GEN-2018-092 | 05 SOUTHWEST | TBD | ERIS | Potter to Tolk 345 kV Double Circuit Line Build | Current Study | Build approximately 115 miles of new double circuit 345 kV lines from Potter County to Tolk | 9856489.2044 | 5.715% | 172477128 | 0.04817
GEN-2018-097 | 05 SOUTHWEST | TBD | ERIS | Lawton Eastside 345 kV Substation Upgrade to Double-Bus-Double-Breaker Configuration | Current Study | Upgrade the Lawton Eastside 345 kV substation to a double-bus-double-breaker configuration | 1155516.6759 | 3.135% | 36855504 | 0.0968
GEN-2018-097 | 05 SOUTHWEST | 81717 | ERIS | Multi - Border - Woodward 345 kV Tap (NTC 210627, NTC 210628) | Contingent | Install any necessary terminal equipment to support a new 345 kV line from Border to Woodward 345 kV substation with a summer emergency rating of 1792 MVA. Build 0.84-miles of new 345 kV line from a new tap on the Woodward to Border 345 kV line to Chisholm with a summer emergency rating of 1792 MVA. | 0 | 5.437% | 29784319 | 0.0791
GEN-2018-097 | 05 SOUTHWEST | TBD | ERIS | Potter to Chisholm 345 kV Double Circuit Line Build | Current Study | Build approximately 170 miles of new double circuit 345 kV lines from Potter County to Chisholm | 12836261.0603 | 5.12% | 250693500 | 0.10102
GEN-2018-097 | 05 SOUTHWEST | TBD | ERIS | Potter to Tolk 345 kV Double Circuit Line Build | Current Study | Build approximately 115 miles of new double circuit 345 kV lines from Potter County to Tolk | 9440089.8785 | 5.473% | 172477128 | 0.18454
GEN-2018-097 | 05 SOUTHWEST | TBD | ERIS | Tolk 345/230 kV Third Transformer Build | Current Study | Build a third 345/230 kV transformer at Tolk | 1832296.9068 | 7.047% | 26000000 | 0.14503
GEN-2018-099 | 05 SOUTHWEST | TBD | ERIS | Lawton Eastside 345 kV Substation Upgrade to Double-Bus-Double-Breaker Configuration | Current Study | Upgrade the Lawton Eastside 345 kV substation to a double-bus-double-breaker configuration | 3274958.678 | 8.886% | 36855504 | 0.09145
GEN-2018-099 | 05 SOUTHWEST | 81717 | ERIS | Multi - Border - Woodward 345 kV Tap (NTC 210627, NTC 210628) | Contingent | Install any necessary terminal equipment to support a new 345 kV line from Border to Woodward 345 kV substation with a summer emergency rating of 1792 MVA. Build 0.84-miles of new 345 kV line from a new tap on the Woodward to Border 345 kV line to Chisholm with a summer emergency rating of 1792 MVA. | 0 | 16.91% | 29784319 | 0.08199
GEN-2018-099 | 05 SOUTHWEST | TBD | ERIS | Potter to Chisholm 345 kV Double Circuit Line Build | Current Study | Build approximately 170 miles of new double circuit 345 kV lines from Potter County to Chisholm | 37300380.4619 | 14.88% | 250693500 | 0.09785
GEN-2018-099 | 05 SOUTHWEST | TBD | ERIS | Potter to Tolk 345 kV Double Circuit Line Build | Current Study | Build approximately 115 miles of new double circuit 345 kV lines from Potter County to Tolk | 28591901.1367 | 16.58% | 172477128 | 0.18631
GEN-2018-099 | 05 SOUTHWEST | TBD | ERIS | Tolk 345/230 kV Third Transformer Build | Current Study | Build a third 345/230 kV transformer at Tolk | 5618176.3185 | 21.61% | 26000000 | 0.14823
GEN-2018-111 | 05 SOUTHWEST | TBD | ERIS | Lawton Eastside 345 kV Substation Upgrade to Double-Bus-Double-Breaker Configuration | Current Study | Upgrade the Lawton Eastside 345 kV substation to a double-bus-double-breaker configuration | 866637.5069 | 2.351% | 36855504 | 0.0968
GEN-2018-111 | 05 SOUTHWEST | 81717 | ERIS | Multi - Border - Woodward 345 kV Tap (NTC 210627, NTC 210628) | Contingent | Install any necessary terminal equipment to support a new 345 kV line from Border to Woodward 345 kV substation with a summer emergency rating of 1792 MVA. Build 0.84-miles of new 345 kV line from a new tap on the Woodward to Border 345 kV line to Chisholm with a summer emergency rating of 1792 MVA. | 0 | 4.078% | 29784319 | 0.0791
GEN-2018-111 | 05 SOUTHWEST | TBD | ERIS | Potter to Chisholm 345 kV Double Circuit Line Build | Current Study | Build approximately 170 miles of new double circuit 345 kV lines from Potter County to Chisholm | 9627195.7952 | 3.84% | 250693500 | 0.10102
GEN-2018-111 | 05 SOUTHWEST | TBD | ERIS | Potter to Tolk 345 kV Double Circuit Line Build | Current Study | Build approximately 115 miles of new double circuit 345 kV lines from Potter County to Tolk | 7080067.4089 | 4.105% | 172477128 | 0.18454
GEN-2018-111 | 05 SOUTHWEST | TBD | ERIS | Tolk 345/230 kV Third Transformer Build | Current Study | Build a third 345/230 kV transformer at Tolk | 1374222.6801 | 5.285% | 26000000 | 0.14503
GEN-2018-112 | 05 SOUTHWEST | TBD | ERIS | Lawton Eastside 345 kV Substation Upgrade to Double-Bus-Double-Breaker Configuration | Current Study | Upgrade the Lawton Eastside 345 kV substation to a double-bus-double-breaker configuration | 2137705.8504 | 5.8% | 36855504 | 0.0968
GEN-2018-112 | 05 SOUTHWEST | 81717 | ERIS | Multi - Border - Woodward 345 kV Tap (NTC 210627, NTC 210628) | Contingent | Install any necessary terminal equipment to support a new 345 kV line from Border to Woodward 345 kV substation with a summer emergency rating of 1792 MVA. Build 0.84-miles of new 345 kV line from a new tap on the Woodward to Border 345 kV line to Chisholm with a summer emergency rating of 1792 MVA. | 0 | 10.06% | 29784319 | 0.0791
GEN-2018-112 | 05 SOUTHWEST | TBD | ERIS | Potter to Chisholm 345 kV Double Circuit Line Build | Current Study | Build approximately 170 miles of new double circuit 345 kV lines from Potter County to Chisholm | 23747082.9616 | 9.473% | 250693500 | 0.10102
GEN-2018-112 | 05 SOUTHWEST | TBD | ERIS | Potter to Tolk 345 kV Double Circuit Line Build | Current Study | Build approximately 115 miles of new double circuit 345 kV lines from Potter County to Tolk | 17464166.2752 | 10.13% | 172477128 | 0.18454
GEN-2018-112 | 05 SOUTHWEST | TBD | ERIS | Tolk 345/230 kV Third Transformer Build | Current Study | Build a third 345/230 kV transformer at Tolk | 3389749.2775 | 13.04% | 26000000 | 0.14503
GEN-2018-124 | 05 SOUTHWEST | TBD | ERIS | Lawton Eastside 345 kV Substation Upgrade to Double-Bus-Double-Breaker Configuration | Current Study | Upgrade the Lawton Eastside 345 kV substation to a double-bus-double-breaker configuration | 2311033.3518 | 6.271% | 36855504 | 0.0968
GEN-2018-124 | 05 SOUTHWEST | 81717 | ERIS | Multi - Border - Woodward 345 kV Tap (NTC 210627, NTC 210628) | Contingent | Install any necessary terminal equipment to support a new 345 kV line from Border to Woodward 345 kV substation with a summer emergency rating of 1792 MVA. Build 0.84-miles of new 345 kV line from a new tap on the Woodward to Border 345 kV line to Chisholm with a summer emergency rating of 1792 MVA. | 0 | 10.87% | 29784319 | 0.0791
GEN-2018-124 | 05 SOUTHWEST | TBD | ERIS | Potter to Chisholm 345 kV Double Circuit Line Build | Current Study | Build approximately 170 miles of new double circuit 345 kV lines from Potter County to Chisholm | 25672522.1206 | 10.24% | 250693500 | 0.10102
GEN-2018-124 | 05 SOUTHWEST | TBD | ERIS | Potter to Tolk 345 kV Double Circuit Line Build | Current Study | Build approximately 115 miles of new double circuit 345 kV lines from Potter County to Tolk | 18880179.7569 | 10.95% | 172477128 | 0.18454
GEN-2018-124 | 05 SOUTHWEST | TBD | ERIS | Tolk 345/230 kV Third Transformer Build | Current Study | Build a third 345/230 kV transformer at Tolk | 3664593.8135 | 14.09% | 26000000 | 0.14503
GEN-2019-003 | 05 SOUTHWEST | TBD | ERIS | Lawton Eastside 345 kV Substation Upgrade to Double-Bus-Double-Breaker Configuration | Current Study | Upgrade the Lawton Eastside 345 kV substation to a double-bus-double-breaker configuration | 1743123.1673 | 4.73% | 36855504 | 0.09735
GEN-2019-003 | 05 SOUTHWEST | 81717 | ERIS | Multi - Border - Woodward 345 kV Tap (NTC 210627, NTC 210628) | Contingent | Install any necessary terminal equipment to support a new 345 kV line from Border to Woodward 345 kV substation with a summer emergency rating of 1792 MVA. Build 0.84-miles of new 345 kV line from a new tap on the Woodward to Border 345 kV line to Chisholm with a summer emergency rating of 1792 MVA. | 0 | 7.968% | 29784319 | 0.07728
GEN-2019-003 | 05 SOUTHWEST | TBD | ERIS | Potter to Chisholm 345 kV Double Circuit Line Build | Current Study | Build approximately 170 miles of new double circuit 345 kV lines from Potter County to Chisholm | 18734054.142 | 7.473% | 250693500 | 0.09829
GEN-2019-003 | 05 SOUTHWEST | TBD | ERIS | Potter to Tolk 345 kV Double Circuit Line Build | Current Study | Build approximately 115 miles of new double circuit 345 kV lines from Potter County to Tolk | 12705294.9123 | 7.366% | 172477128 | 0.16558
GEN-2019-003 | 05 SOUTHWEST | TBD | ERIS | Tolk 345/230 kV Third Transformer Build | Current Study | Build a third 345/230 kV transformer at Tolk | 1989462.8277 | 7.652% | 26000000 | 0.10498
GEN-2019-004 | 05 SOUTHWEST | TBD | ERIS | Lawton Eastside 345 kV Substation Upgrade to Double-Bus-Double-Breaker Configuration | Current Study | Upgrade the Lawton Eastside 345 kV substation to a double-bus-double-breaker configuration | 731050.5171 | 1.984% | 36855504 | 0.10936
GEN-2019-004 | 05 SOUTHWEST | TBD | ERIS | Potter to Chisholm 345 kV Double Circuit Line Build | Current Study | Build approximately 170 miles of new double circuit 345 kV lines from Potter County to Chisholm | 6076829.8253 | 2.424% | 250693500 | 0.0854
GEN-2019-004 | 05 SOUTHWEST | TBD | ERIS | Potter to Tolk 345 kV Double Circuit Line Build | Current Study | Build approximately 115 miles of new double circuit 345 kV lines from Potter County to Tolk | 4678282.2353 | 2.712% | 172477128 | 0.16331
GEN-2019-011 | 05 SOUTHWEST | TBD | ERIS | Lawton Eastside 345 kV Substation Upgrade to Double-Bus-Double-Breaker Configuration | Current Study | Upgrade the Lawton Eastside 345 kV substation to a double-bus-double-breaker configuration | 3233703.8677 | 8.774% | 36855504 | 0.11778
GEN-2019-011 | 05 SOUTHWEST | 81717 | ERIS | Multi - Border - Woodward 345 kV Tap (NTC 210627, NTC 210628) | Contingent | Install any necessary terminal equipment to support a new 345 kV line from Border to Woodward 345 kV substation with a summer emergency rating of 1792 MVA. Build 0.84-miles of new 345 kV line from a new tap on the Woodward to Border 345 kV line to Chisholm with a summer emergency rating of 1792 MVA. | 0 | 6.797% | 29784319 | 0.04299
GEN-2019-011 | 05 SOUTHWEST | TBD | ERIS | Potter to Chisholm 345 kV Double Circuit Line Build | Current Study | Build approximately 170 miles of new double circuit 345 kV lines from Potter County to Chisholm | 22336898.5897 | 8.91% | 250693500 | 0.07643
GEN-2019-011 | 05 SOUTHWEST | TBD | ERIS | Potter to Tolk 345 kV Double Circuit Line Build | Current Study | Build approximately 115 miles of new double circuit 345 kV lines from Potter County to Tolk | 17224813.3948 | 9.987% | 172477128 | 0.1464
GEN-2019-011 | 05 SOUTHWEST | TBD | ERIS | Tolk 345/230 kV Third Transformer Build | Current Study | Build a third 345/230 kV transformer at Tolk | 265009.032 | 1.019% | 26000000 | 0.00912
GEN-2019-021 | 05 SOUTHWEST | TBD | ERIS | Lawton Eastside 345 kV Substation Upgrade to Double-Bus-Double-Breaker Configuration | Current Study | Upgrade the Lawton Eastside 345 kV substation to a double-bus-double-breaker configuration | 581041.0558 | 1.577% | 36855504 | 0.09735
GEN-2019-021 | 05 SOUTHWEST | 81717 | ERIS | Multi - Border - Woodward 345 kV Tap (NTC 210627, NTC 210628) | Contingent | Install any necessary terminal equipment to support a new 345 kV line from Border to Woodward 345 kV substation with a summer emergency rating of 1792 MVA. Build 0.84-miles of new 345 kV line from a new tap on the Woodward to Border 345 kV line to Chisholm with a summer emergency rating of 1792 MVA. | 0 | 2.656% | 29784319 | 0.07728
GEN-2019-021 | 05 SOUTHWEST | TBD | ERIS | Potter to Chisholm 345 kV Double Circuit Line Build | Current Study | Build approximately 170 miles of new double circuit 345 kV lines from Potter County to Chisholm | 6244684.714 | 2.491% | 250693500 | 0.09829
GEN-2019-021 | 05 SOUTHWEST | TBD | ERIS | Potter to Tolk 345 kV Double Circuit Line Build | Current Study | Build approximately 115 miles of new double circuit 345 kV lines from Potter County to Tolk | 4235098.3041 | 2.455% | 172477128 | 0.16558
GEN-2019-021 | 05 SOUTHWEST | TBD | ERIS | Tolk 345/230 kV Third Transformer Build | Current Study | Build a third 345/230 kV transformer at Tolk | 663154.2759 | 2.551% | 26000000 | 0.10498
GEN-2019-056 | 05 SOUTHWEST | TBD | ERIS | Lawton Eastside 345 kV Substation Upgrade to Double-Bus-Double-Breaker Configuration | Current Study | Upgrade the Lawton Eastside 345 kV substation to a double-bus-double-breaker configuration | 844195.6541 | 2.291% | 36855504 | 0.07072
GEN-2019-056 | 05 SOUTHWEST | 81717 | ERIS | Multi - Border - Woodward 345 kV Tap (NTC 210627, NTC 210628) | Contingent | Install any necessary terminal equipment to support a new 345 kV line from Border to Woodward 345 kV substation with a summer emergency rating of 1792 MVA. Build 0.84-miles of new 345 kV line from a new tap on the Woodward to Border 345 kV line to Chisholm with a summer emergency rating of 1792 MVA. | 0 | 7.742% | 29784319 | 0.11263
GEN-2019-056 | 05 SOUTHWEST | TBD | ERIS | Potter to Chisholm 345 kV Double Circuit Line Build | Current Study | Build approximately 170 miles of new double circuit 345 kV lines from Potter County to Chisholm | 12466497.4523 | 4.973% | 250693500 | 0.09811
GEN-2019-056 | 05 SOUTHWEST | TBD | ERIS | Potter to Tolk 345 kV Double Circuit Line Build | Current Study | Build approximately 115 miles of new double circuit 345 kV lines from Potter County to Tolk | 212292.0396 | 0.1231% | 172477128 | 0.00415
GEN-2019-056 | 05 SOUTHWEST | TBD | ERIS | Tolk 345/230 kV Third Transformer Build | Current Study | Build a third 345/230 kV transformer at Tolk | 163230.2009 | 0.6278% | 26000000 | 0.01292
GEN-2019-074 | 05 SOUTHWEST | TBD | ERIS | Lawton Eastside 345 kV Substation Upgrade to Double-Bus-Double-Breaker Configuration | Current Study | Upgrade the Lawton Eastside 345 kV substation to a double-bus-double-breaker configuration | 1159455.9373 | 3.146% | 36855504 | 0.09713
GEN-2019-074 | 05 SOUTHWEST | 81717 | ERIS | Multi - Border - Woodward 345 kV Tap (NTC 210627, NTC 210628) | Contingent | Install any necessary terminal equipment to support a new 345 kV line from Border to Woodward 345 kV substation with a summer emergency rating of 1792 MVA. Build 0.84-miles of new 345 kV line from a new tap on the Woodward to Border 345 kV line to Chisholm with a summer emergency rating of 1792 MVA. | 0 | 5.324% | 29784319 | 0.07745
GEN-2019-074 | 05 SOUTHWEST | TBD | ERIS | Potter to Chisholm 345 kV Double Circuit Line Build | Current Study | Build approximately 170 miles of new double circuit 345 kV lines from Potter County to Chisholm | 12462685.4563 | 4.971% | 250693500 | 0.09808
GEN-2019-074 | 05 SOUTHWEST | TBD | ERIS | Potter to Tolk 345 kV Double Circuit Line Build | Current Study | Build approximately 115 miles of new double circuit 345 kV lines from Potter County to Tolk | 8261996.9452 | 4.79% | 172477128 | 0.16151
GEN-2019-074 | 05 SOUTHWEST | TBD | ERIS | Tolk 345/230 kV Third Transformer Build | Current Study | Build a third 345/230 kV transformer at Tolk | 1551823.961 | 5.969% | 26000000 | 0.12283
GEN-2018-069 | 01 NORTH | TBD | NRIS | Beulah to Garrison 115 kV Line Rebuild | Current Study | Rebuild the Stanton Basin to Beulah 115 kV 13.41 mile Line, the Stanton Basin to Pick City 115 kV 7.43 mile Line, and the Pick City to Garrison 115 kV 5 mile Line each to a minimum rating of 150 MVA | 5759607.0678 | 52.36% | 11000000 | 0.01356
GEN-2018-069 | 01 NORTH | 92394 | NRIS | Fargo 230 kV Terminal Upgrade (NTC ID 210715) | Contingent | Upgrade terminal conductor at Fargo 230 kV substation to support the line to Sheyenne to increase minimum ratings to 458/505 MVA | 0 | 53.19% | 3119998 | 0.03399
GEN-2018-069 | 01 NORTH | TBD | NRIS | Rebuild the existing Sheynne to Fargo 230 kV line | Contingent | Rebuild approximately 4.2 miles of 230kV line from Sheynne to Fargo | 0 | 53.19% | 3119998 | 0.03214
GEN-2019-023 | 01 NORTH | TBD | NRIS | Beulah to Garrison 115 kV Line Rebuild | Current Study | Rebuild the Stanton Basin to Beulah 115 kV 13.41 mile Line, the Stanton Basin to Pick City 115 kV 7.43 mile Line, and the Pick City to Garrison 115 kV 5 mile Line each to a minimum rating of 150 MVA | 5240392.9322 | 47.64% | 11000000 | 0.01402
GEN-2019-023 | 01 NORTH | 92394 | NRIS | Fargo 230 kV Terminal Upgrade (NTC ID 210715) | Contingent | Upgrade terminal conductor at Fargo 230 kV substation to support the line to Sheyenne to increase minimum ratings to 458/505 MVA | 0 | 46.81% | 3119998 | 0.03399
GEN-2019-023 | 01 NORTH | TBD | NRIS | Rebuild the existing Sheynne to Fargo 230 kV line | Contingent | Rebuild approximately 4.2 miles of 230kV line from Sheynne to Fargo | 0 | 46.81% | 3119998 | 0.03214
GEN-2018-065 | 02 NEBRASKA | TBD | NRIS | Battle Creek to County Line 115 kV Line Rebuild | Current Study | Rebuild the Battle Creek to County Line 115 kV 10.96 mile Line to a minimum rating of 227 MVA | 230344.1109 | 2.957% | 7790806.4 | 0.03669
GEN-2018-065 | 02 NEBRASKA | TBD | NRIS | Battle Creek to Norfork North 115 kV Line Rebuild | Current Study | Rebuild the Battle Creek to Norfork North 115 kV 10.56 mile Line to a minimum rating of 222 MVA | 221937.3915 | 2.957% | 7506470.4 | 0.03669
GEN-2018-065 | 02 NEBRASKA | TBD | NRIS | County Line to Antelope 115 kV Line Rebuild | Current Study | Rebuild the County Line to Antelope 115 kV 12.2 mile Line to a minimum rating of 231 MVA | 256404.941 | 2.957% | 8672248 | 0.03669
GEN-2018-068 | 02 NEBRASKA | TBD | NRIS | Battle Creek to County Line 115 kV Line Rebuild | Current Study | Rebuild the Battle Creek to County Line 115 kV 10.96 mile Line to a minimum rating of 227 MVA | 3517982.7848 | 45.16% | 7790806.4 | 0.03669
GEN-2018-068 | 02 NEBRASKA | TBD | NRIS | Battle Creek to Norfork North 115 kV Line Rebuild | Current Study | Rebuild the Battle Creek to Norfork North 115 kV 10.56 mile Line to a minimum rating of 222 MVA | 3389589.2525 | 45.16% | 7506470.4 | 0.03669
GEN-2018-068 | 02 NEBRASKA | TBD | NRIS | County Line to Antelope 115 kV Line Rebuild | Current Study | Rebuild the County Line to Antelope 115 kV 12.2 mile Line to a minimum rating of 231 MVA | 3916002.7349 | 45.16% | 8672248 | 0.03669
GEN-2018-131 | 02 NEBRASKA | TBD | NRIS | Battle Creek to County Line 115 kV Line Rebuild | Current Study | Rebuild the Battle Creek to County Line 115 kV 10.96 mile Line to a minimum rating of 227 MVA | 2115850.9746 | 27.16% | 7790806.4 | 0.03014
GEN-2018-131 | 02 NEBRASKA | TBD | NRIS | Battle Creek to Norfork North 115 kV Line Rebuild | Current Study | Rebuild the Battle Creek to Norfork North 115 kV 10.56 mile Line to a minimum rating of 222 MVA | 2038630.1361 | 27.16% | 7506470.4 | 0.03014
GEN-2018-131 | 02 NEBRASKA | TBD | NRIS | County Line to Antelope 115 kV Line Rebuild | Current Study | Rebuild the County Line to Antelope 115 kV 12.2 mile Line to a minimum rating of 231 MVA | 2355235.5739 | 27.16% | 8672248 | 0.03014
GEN-2018-132 | 02 NEBRASKA | TBD | NRIS | Battle Creek to County Line 115 kV Line Rebuild | Current Study | Rebuild the Battle Creek to County Line 115 kV 10.96 mile Line to a minimum rating of 227 MVA | 1926628.5297 | 24.73% | 7790806.4 | 0.03014
GEN-2018-132 | 02 NEBRASKA | TBD | NRIS | Battle Creek to Norfork North 115 kV Line Rebuild | Current Study | Rebuild the Battle Creek to Norfork North 115 kV 10.56 mile Line to a minimum rating of 222 MVA | 1856313.6199 | 24.73% | 7506470.4 | 0.03014
GEN-2018-132 | 02 NEBRASKA | TBD | NRIS | County Line to Antelope 115 kV Line Rebuild | Current Study | Rebuild the County Line to Antelope 115 kV 12.2 mile Line to a minimum rating of 231 MVA | 2144604.7502 | 24.73% | 8672248 | 0.03014
GEN-2018-116 | 03 CENTRAL | TBD | NRIS | Great Bend Tap to Seward 115 kV Terminal Equipment Upgrade | Current Study | Upgrade terminal equipment at Great Bend Tap to Seward 115 kV substation to increase minimum rating to 109 MVA | 131311.032 | 54.71% | 240000 | 0.15901
GEN-2018-116 | 03 CENTRAL | TBD | NRIS | Seward to St. John 115 kV Terminal Equipment Upgrade | Current Study | Upgrade terminal equipment at Seward to St.John 115 kV substation to increase minimum rating to 109 MVA | 121488.1404 | 50.62% | 240000 | 0.14956
GEN-2019-051 | 03 CENTRAL | TBD | NRIS | Great Bend Tap to Seward 115 kV Terminal Equipment Upgrade | Current Study | Upgrade terminal equipment at Great Bend Tap to Seward 115 kV substation to increase minimum rating to 109 MVA | 35016.2752 | 14.59% | 240000 | 0.15901
GEN-2019-051 | 03 CENTRAL | TBD | NRIS | Seward to St. John 115 kV Terminal Equipment Upgrade | Current Study | Upgrade terminal equipment at Seward to St.John 115 kV substation to increase minimum rating to 109 MVA | 32396.8374 | 13.5% | 240000 | 0.14956
GEN-2019-053 | 03 CENTRAL | TBD | NRIS | Great Bend Tap to Seward 115 kV Terminal Equipment Upgrade | Current Study | Upgrade terminal equipment at Great Bend Tap to Seward 115 kV substation to increase minimum rating to 109 MVA | 6958.7718 | 2.899% | 240000 | 0.02528
GEN-2019-053 | 03 CENTRAL | TBD | NRIS | Seward to St. John 115 kV Terminal Equipment Upgrade | Current Study | Upgrade terminal equipment at Seward to St.John 115 kV substation to increase minimum rating to 109 MVA | 8193.4366 | 3.414% | 240000 | 0.03026
GEN-2019-054 | 03 CENTRAL | TBD | NRIS | Great Bend Tap to Seward 115 kV Terminal Equipment Upgrade | Current Study | Upgrade terminal equipment at Great Bend Tap to Seward 115 kV substation to increase minimum rating to 109 MVA | 34378.2043 | 14.32% | 240000 | 0.04163
GEN-2019-054 | 03 CENTRAL | TBD | NRIS | Seward to St. John 115 kV Terminal Equipment Upgrade | Current Study | Upgrade terminal equipment at Seward to St.John 115 kV substation to increase minimum rating to 109 MVA | 40005.9569 | 16.67% | 240000 | 0.04925
GEN-2019-055 | 03 CENTRAL | TBD | NRIS | Great Bend Tap to Seward 115 kV Terminal Equipment Upgrade | Current Study | Upgrade terminal equipment at Great Bend Tap to Seward 115 kV substation to increase minimum rating to 109 MVA | 20876.3153 | 8.698% | 240000 | 0.02528
GEN-2019-055 | 03 CENTRAL | TBD | NRIS | Seward to St. John 115 kV Terminal Equipment Upgrade | Current Study | Upgrade terminal equipment at Seward to St.John 115 kV substation to increase minimum rating to 109 MVA | 24580.3098 | 10.24% | 240000 | 0.03026
GEN-2019-068 | 03 CENTRAL | TBD | NRIS | Great Bend Tap to Seward 115 kV Terminal Equipment Upgrade | Current Study | Upgrade terminal equipment at Great Bend Tap to Seward 115 kV substation to increase minimum rating to 109 MVA | 11459.4014 | 4.775% | 240000 | 0.04163
GEN-2019-068 | 03 CENTRAL | TBD | NRIS | Seward to St. John 115 kV Terminal Equipment Upgrade | Current Study | Upgrade terminal equipment at Seward to St.John 115 kV substation to increase minimum rating to 109 MVA | 13335.319 | 5.556% | 240000 | 0.04925
GEN-2018-071 | 04 SOUTHEAST | 81741 | NRIS | Multi - Minco - Pleasant Valley - Draper 345 kV (NTC 210616, NTC 210656, NTC 210670) | Contingent | Expand the existing Pleasant Valley 138 kV substation to 345 kV with new terminals to accommodate new line from Minco to Pleasant Valley to Draper and terminals to accommodate cut in of existing Cimarron to Draper 345 kV line. Tie into existing Cimarron to Draper 345 kV line. Build 34.8 miles of 345 kV line from Minco to Pleasant Valley 345 kV to achieve a 1792 MVA summer emergency rating. Build a second 13.2-mile 345 kV line from Draper 345 kV substation to Pleasant Valley 345 kV substation with a summer emergency rating of 1792 MVA | 0 | 12.79% | 106585363 | 0.03424
GEN-2018-072 | 04 SOUTHEAST | 81741 | NRIS | Multi - Minco - Pleasant Valley - Draper 345 kV (NTC 210616, NTC 210656, NTC 210670) | Contingent | Expand the existing Pleasant Valley 138 kV substation to 345 kV with new terminals to accommodate new line from Minco to Pleasant Valley to Draper and terminals to accommodate cut in of existing Cimarron to Draper 345 kV line. Tie into existing Cimarron to Draper 345 kV line. Build 34.8 miles of 345 kV line from Minco to Pleasant Valley 345 kV to achieve a 1792 MVA summer emergency rating. Build a second 13.2-mile 345 kV line from Draper 345 kV substation to Pleasant Valley 345 kV substation with a summer emergency rating of 1792 MVA | 0 | 12.79% | 106585363 | 0.03424
GEN-2019-012 | 04 SOUTHEAST | 81741 | NRIS | Multi - Minco - Pleasant Valley - Draper 345 kV (NTC 210616, NTC 210656, NTC 210670) | Contingent | Expand the existing Pleasant Valley 138 kV substation to 345 kV with new terminals to accommodate new line from Minco to Pleasant Valley to Draper and terminals to accommodate cut in of existing Cimarron to Draper 345 kV line. Tie into existing Cimarron to Draper 345 kV line. Build 34.8 miles of 345 kV line from Minco to Pleasant Valley 345 kV to achieve a 1792 MVA summer emergency rating. Build a second 13.2-mile 345 kV line from Draper 345 kV substation to Pleasant Valley 345 kV substation with a summer emergency rating of 1792 MVA | 0 | 33.04% | 106585363 | 0.06681
GEN-2019-052 | 04 SOUTHEAST | 81741 | NRIS | Multi - Minco - Pleasant Valley - Draper 345 kV (NTC 210616, NTC 210656, NTC 210670) | Contingent | Expand the existing Pleasant Valley 138 kV substation to 345 kV with new terminals to accommodate new line from Minco to Pleasant Valley to Draper and terminals to accommodate cut in of existing Cimarron to Draper 345 kV line. Tie into existing Cimarron to Draper 345 kV line. Build 34.8 miles of 345 kV line from Minco to Pleasant Valley 345 kV to achieve a 1792 MVA summer emergency rating. Build a second 13.2-mile 345 kV line from Draper 345 kV substation to Pleasant Valley 345 kV substation with a summer emergency rating of 1792 MVA | 0 | 33.86% | 106585363 | 0.10142
GEN-2019-067 | 04 SOUTHEAST | 81741 | NRIS | Multi - Minco - Pleasant Valley - Draper 345 kV (NTC 210616, NTC 210656, NTC 210670) | Contingent | Expand the existing Pleasant Valley 138 kV substation to 345 kV with new terminals to accommodate new line from Minco to Pleasant Valley to Draper and terminals to accommodate cut in of existing Cimarron to Draper 345 kV line. Tie into existing Cimarron to Draper 345 kV line. Build 34.8 miles of 345 kV line from Minco to Pleasant Valley 345 kV to achieve a 1792 MVA summer emergency rating. Build a second 13.2-mile 345 kV line from Draper 345 kV substation to Pleasant Valley 345 kV substation with a summer emergency rating of 1792 MVA | 0 | 7.524% | 106585363 | 0.10142
GEN-2019-011 | 05 SOUTHWEST | TBD | NRIS | Wolfforth to Terry County 115 kV Line Model Correction | Current Study | Wolfforth to Terry County 115 kV line rating updated to summer normal/emergency ratings of 230.9 MVA | 0 | 100% | 0 | 0.03007
GEN-2018-067 | 01 NORTH | 156804 |  | Strandahl 115kV GEN-2018-067 Interconnection (Non-shared NU) (MWEC) | Interconnection | Facilitate the interconnection of GEN-2018-067 | 1728103 | 100% | 1728103 | -
GEN-2018-067 | 01 NORTH | 156803 |  | Strandahl 115kV GEN-2018-067 Interconnection (TOIF) (MWEC) | Interconnection | Facilitate the interconnection of GEN-2018-067 | 0 | 100% | 0 | -
GEN-2018-069 | 01 NORTH | 156826 |  | WAPA-UGP Mingusville 230kV GEN-2018-069 Interconnection (TOIF) (WAPA) | Interconnection | Facilitate the interconnection of GEN-2018-069 | 207000.5 | 100% | 207000.5 | -
GEN-2018-069 | 01 NORTH | 156828 |  | WAPA-UGP Mingusville 230kV Interconnection Expansion (DISIS-2018-002 - DISIS-2019-001) | Interconnection | Facilitate the interconnection of GEN-2018-069 | 1285106.383 | 53.19% | 2416000 | -
GEN-2018-070 | 01 NORTH | 156824 |  | Utica Junction 230 kV GEN-2018-070 Interconnection (TOIF) (WAPA) | Interconnection | Facilitate the interconnection of GEN-2018-070 | 100000 | 100% | 100000 | -
GEN-2018-070 | 01 NORTH | 156825 |  | Utica Junction 230 kV GEN-2018-070 Interconnection (Non-shared NU) (WAPA) | Interconnection | Facilitate the interconnection of GEN-2018-070 | 0 | 100% | 0 | -
GEN-2018-074 | 01 NORTH | 156696 |  | Denison 230kV GEN-2018-074 Interconnection (Non-shared NU) (WAPA) | Interconnection | Facilitate the interconnection of GEN-2018-074 | 0 | 100% | 0 | -
GEN-2018-074 | 01 NORTH | 156695 |  | Denison 230kV GEN-2018-074 Interconnection (TOIF) (WAPA) | Interconnection | Facilitate the interconnection of GEN-2018-074 | 100000 | 100% | 100000 | -
GEN-2019-019 | 01 NORTH | 143690 |  | Siouxland 69kV GEN-2019-019 Interconnection (Non-shared NU) (NIPCO) | Interconnection | Facilitate the interconnection of GEN-2019-019 | 2747959 | 100% | 2747959 | -
GEN-2019-019 | 01 NORTH | 143689 |  | Siouxland 69kV GEN-2019-019 Interconnection (TOIF) (NIPCO) | Interconnection | Facilitate the interconnection of GEN-2019-019 | 2747959 | 100% | 2747959 | -
GEN-2019-023 | 01 NORTH | 156827 |  | WAPA-UGP Mingusville 230kV GEN-2019-023 Interconnection (TOIF) (WAPA) | Interconnection | Facilitate the interconnection of GEN-2019-023 | 207000.5 | 100% | 207000.5 | -
GEN-2019-023 | 01 NORTH | 156828 |  | WAPA-UGP Mingusville 230kV Interconnection Expansion (DISIS-2018-002 - DISIS-2019-001) | Interconnection | Facilitate the interconnection of GEN-2019-023 | 1130893.617 | 46.81% | 2416000 | -
GEN-2019-037 | 01 NORTH | 156675 |  | Leland Olds 345kV GEN-2019-037 Interconnection (Non-shared NU) (BEPC) | Interconnection | Facilitate the interconnection of GEN-2019-037 | 3373813 | 100% | 3373813 | -
GEN-2019-037 | 01 NORTH | 156674 |  | Leland Olds 345kV GEN-2019-037 Interconnection (TOIF) (BEPC) | Interconnection | Facilitate the interconnection of GEN-2019-037 | 1050470 | 100% | 1050470 | -
GEN-2018-065 | 02 NEBRASKA | 156666 |  | Antelope 345kV GEN-2018-065 Interconnection (TOIF) (NPPD) | Interconnection | Facilitate the interconnection of GEN-2018-065 | 500000 | 100% | 500000 | -
GEN-2018-065 | 02 NEBRASKA | 156668 |  | Antelope 345kV Interconnection Expansion (DISIS-2018-002 - DISIS-2019-001) | Interconnection | Facilitate the interconnection of GEN-2018-065 | 141340.7821 | 6.145% | 2300000 | -
GEN-2018-068 | 02 NEBRASKA | 156667 |  | Antelope 345kV GEN-2018-068 Interconnection (TOIF) (NPPD) | Interconnection | Facilitate the interconnection of GEN-2018-068 | 500000 | 100% | 500000 | -
GEN-2018-068 | 02 NEBRASKA | 156668 |  | Antelope 345kV Interconnection Expansion (DISIS-2018-002 - DISIS-2019-001) | Interconnection | Facilitate the interconnection of GEN-2018-068 | 2158659.2179 | 93.85% | 2300000 | -
GEN-2018-083 | 02 NEBRASKA | 156792 |  | Shell Creek-Hoskins 345kv GEN-2018-083 Interconnection (TOIF) (NPPD) | Interconnection | Facilitate the interconnection of GEN-2018-083 | 250000 | 100% | 250000 | -
GEN-2018-083 | 02 NEBRASKA | 156793 |  | Shell Creek-Hoskins 345kv Interconnection Expansion (DISIS-2018-002 - DISIS-2019-001) | Interconnection | Facilitate the interconnection of GEN-2018-083 | 13050000 | 50% | 26100000 | -
GEN-2018-090 | 02 NEBRASKA | 156772 |  | Raun - Fort Calhoun 345kV GEN-2018-090 Interconnection (Non-shared NU) (OPPD) | Interconnection | Facilitate the interconnection of GEN-2018-090 | 0 | 100% | 0 | -
GEN-2018-090 | 02 NEBRASKA | 156771 |  | Raun - Fort Calhoun 345kV GEN-2018-090 Interconnection (TOIF) (OPPD) | Interconnection | Facilitate the interconnection of GEN-2018-090 | 0 | 100% | 0 | -
GEN-2018-125 | 02 NEBRASKA | 156709 |  | Gentleman to Sweetwater 345kV GEN-2018-125 Interconnection (Non-shared NU) (NPPD) | Interconnection | Facilitate the interconnection of GEN-2018-125 | 23100000 | 100% | 23100000 | -
GEN-2018-125 | 02 NEBRASKA | 156708 |  | Gentleman to Sweetwater 345kV GEN-2018-125 Interconnection (TOIF) (NPPD) | Interconnection | Facilitate the interconnection of GEN-2018-125 | 1000000 | 100% | 1000000 | -
GEN-2018-131 | 02 NEBRASKA | 156669 |  | Antelope 345kV GEN-2018-131 Interconnection (TOIF) (NPPD) | Interconnection | Facilitate the interconnection of GEN-2018-131 | 500000 | 100% | 500000 | -
GEN-2018-131 | 02 NEBRASKA | 156671 |  | Antelope 345kV Interconnection Expansion (2) (DISIS-2018-002 - DISIS-2019-001) | Interconnection | Facilitate the interconnection of GEN-2018-131 | 9735319.1489 | 52.34% | 18600000 | -
GEN-2018-132 | 02 NEBRASKA | 156670 |  | Antelope 345kV GEN-2018-132 Interconnection (TOIF) (NPPD) | Interconnection | Facilitate the interconnection of GEN-2018-132 | 500000 | 100% | 500000 | -
GEN-2018-132 | 02 NEBRASKA | 156671 |  | Antelope 345kV Interconnection Expansion (2) (DISIS-2018-002 - DISIS-2019-001) | Interconnection | Facilitate the interconnection of GEN-2018-132 | 8864680.8511 | 47.66% | 18600000 | -
GEN-2019-009 | 02 NEBRASKA | 156781 |  | S1263 Brock 161kV GEN-2019-009 Interconnection (Non-shared NU) (OPPD) | Interconnection | Facilitate the interconnection of GEN-2019-009 | 1176131 | 100% | 1176131 | -
GEN-2019-009 | 02 NEBRASKA | 156780 |  | S1263 Brock 161kV GEN-2019-009 Interconnection (TOIF) (OPPD) | Interconnection | Facilitate the interconnection of GEN-2019-009 | 100000 | 100% | 100000 | -
GEN-2019-029 | 02 NEBRASKA | 156798 |  | Sidney Keystone 345 kV GEN-2019-029 Interconnection (TOIF) (NPPD) | Interconnection | Facilitate the interconnection of GEN-2019-029 | 500000 | 100% | 500000 | -
GEN-2019-029 | 02 NEBRASKA | 156800 |  | Sidney Keystone 345 kV Interconnection Expansion (DISIS-2018-002 - DISIS-2019-001) | Interconnection | Facilitate the interconnection of GEN-2019-029 | 17511262.7986 | 68.94% | 25400000 | -
GEN-2019-033 | 02 NEBRASKA | 156799 |  | Sidney Keystone 345 kV GEN-2019-033 Interconnection (TOIF) (NPPD) | Interconnection | Facilitate the interconnection of GEN-2019-033 | 500000 | 100% | 500000 | -
GEN-2019-033 | 02 NEBRASKA | 156800 |  | Sidney Keystone 345 kV Interconnection Expansion (DISIS-2018-002 - DISIS-2019-001) | Interconnection | Facilitate the interconnection of GEN-2019-033 | 7888737.2014 | 31.06% | 25400000 | -
GEN-2019-039 | 02 NEBRASKA | 156685 |  | Columbus Southeast - Rising City 115kV GEN-2019-039 Interconnection (Non-shared NU) (NPPD) | Interconnection | Facilitate the interconnection of GEN-2019-039 | 6800000 | 100% | 6800000 | -
GEN-2019-039 | 02 NEBRASKA | 156684 |  | Columbus Southeast - Rising City 115kV GEN-2019-039 Interconnection (TOIF) (NPPD) | Interconnection | Facilitate the interconnection of GEN-2019-039 | 700000 | 100% | 700000 | -
GEN-2019-041 | 02 NEBRASKA | 156747 |  | Monolith 115kV GEN-2019-041 Interconnection (Non-shared NU) (NPPD) | Interconnection | Facilitate the interconnection of GEN-2019-041 | 1400000 | 100% | 1400000 | -
GEN-2019-041 | 02 NEBRASKA | 156746 |  | Monolith 115kV GEN-2019-041 Interconnection (TOIF) (NPPD) | Interconnection | Facilitate the interconnection of GEN-2019-041 | 700000 | 100% | 700000 | -
GEN-2019-069 | 02 NEBRASKA | 156789 |  | Shell Creek-Hoskins 345kv GEN-2019-069 Interconnection (TOIF) (NPPD) | Interconnection | Facilitate the interconnection of GEN-2019-069 | 250000 | 100% | 250000 | -
GEN-2019-069 | 02 NEBRASKA | 156793 |  | Shell Creek-Hoskins 345kv Interconnection Expansion (DISIS-2018-002 - DISIS-2019-001) | Interconnection | Facilitate the interconnection of GEN-2019-069 | 5220000 | 20% | 26100000 | -
GEN-2019-070 | 02 NEBRASKA | 156790 |  | Shell Creek-Hoskins 345kv GEN-2019-070 Interconnection (TOIF) (NPPD) | Interconnection | Facilitate the interconnection of GEN-2019-070 | 250000 | 100% | 250000 | -
GEN-2019-070 | 02 NEBRASKA | 156793 |  | Shell Creek-Hoskins 345kv Interconnection Expansion (DISIS-2018-002 - DISIS-2019-001) | Interconnection | Facilitate the interconnection of GEN-2019-070 | 2610000 | 10% | 26100000 | -
GEN-2019-073 | 02 NEBRASKA | 156791 |  | Shell Creek-Hoskins 345kv GEN-2019-073 Interconnection (TOIF) (NPPD) | Interconnection | Facilitate the interconnection of GEN-2019-073 | 250000 | 100% | 250000 | -
GEN-2019-073 | 02 NEBRASKA | 156793 |  | Shell Creek-Hoskins 345kv Interconnection Expansion (DISIS-2018-002 - DISIS-2019-001) | Interconnection | Facilitate the interconnection of GEN-2019-073 | 5220000 | 20% | 26100000 | -
GEN-2018-063 | 03 CENTRAL | 156788 |  | Sedalia Marshfield Springfield Nichols Street 69kV GEN-2018-063 Interconnection (Non-shared NU) (EDE) | Interconnection | Facilitate the interconnection of GEN-2018-063 | 693356 | 100% | 693356 | -
GEN-2018-063 | 03 CENTRAL | 156787 |  | Sedalia Marshfield Springfield Nichols Street 69kV GEN-2018-063 Interconnection (TOIF) (EDE) | Interconnection | Facilitate the interconnection of GEN-2018-063 | 8294029 | 100% | 8294029 | -
GEN-2018-093 | 03 CENTRAL | 156713 |  | Gordan Evans 137kV GEN-2018-093 Interconnection (Non-shared NU) (WERE) | Interconnection | Facilitate the interconnection of GEN-2018-093 | 20000 | 100% | 20000 | -
GEN-2018-093 | 03 CENTRAL | 156712 |  | Gordan Evans 137kV GEN-2018-093 Interconnection (TOIF) (WERE) | Interconnection | Facilitate the interconnection of GEN-2018-093 | 0 | 100% | 0 | -
GEN-2018-108 | 03 CENTRAL | 156813 |  | Thistle 345kV GEN-2018-108 Interconnection (Non-shared NU) (ITCGP) | Interconnection | Sharing a GEN Tie line with GEN-2018-049 | 0 | 100% | 0 | -
GEN-2018-108 | 03 CENTRAL | 156812 |  | Thistle 345kV GEN-2018-108 Interconnection (TOIF) (ITCGP) | Interconnection | Sharing a GEN Tie line with GEN-2018-049 | 0 | 100% | 0 | -
GEN-2018-116 | 03 CENTRAL | 156706 |  | Frey Street 115kV GEN-2018-116 Interconnection (TOIF) (SUNC) | Interconnection | Facilitate the interconnection of GEN-2018-116 | 904012.5 | 100% | 904012.5 | -
GEN-2018-116 | 03 CENTRAL | 156707 |  | Frey Street 115kV Interconnection Expansion (DISIS-2018-002 - DISIS-2019-001) | Interconnection | Facilitate the interconnection of GEN-2018-116 | 18060387.6316 | 78.95% | 22876491 | -
GEN-2018-121 | 03 CENTRAL | 156732 |  | KC South - N. Raymore 161kV GEN-2018-121 Interconnection (Non-shared NU) (GMO) | Interconnection | Facilitate the interconnection of GEN-2018-121 | 112911 | 100% | 112911 | -
GEN-2018-121 | 03 CENTRAL | 156731 |  | KC South - N. Raymore 161kV GEN-2018-121 Interconnection (TOIF) (GMO) | Interconnection | Facilitate the interconnection of GEN-2018-121 | 0 | 100% | 0 | -
GEN-2018-128 | 03 CENTRAL | 156776 |  | Renfrow-Viola 345 kV GEN-2018-128 Interconnection (Non-shared NU) (WERE) | Interconnection | Facilitate the interconnection of GEN-2018-128 | 21420837 | 100% | 21420837 | -
GEN-2018-128 | 03 CENTRAL | 156775 |  | Renfrow-Viola 345 kV GEN-2018-128 Interconnection (TOIF) (WERE) | Interconnection | Facilitate the interconnection of GEN-2018-128 | 0 | 100% | 0 | -
GEN-2019-001 | 03 CENTRAL | 156815 |  | Buffalo Flats 345kV GEN-2019-001 Interconnection (Non-shared NU) (WERE) | Interconnection | Facilitate the interconnection of GEN-2019-001 | 20000 | 100% | 20000 | -
GEN-2019-001 | 03 CENTRAL | 156814 |  | Buffalo Flats 345kV GEN-2019-001 Interconnection (TOIF) (WERE) | Interconnection | Facilitate the interconnection of GEN-2019-001 | 0 | 100% | 0 | -
GEN-2019-014 | 03 CENTRAL | 156730 |  | Holcomb 115kV GEN-2019-014 Interconnection (Non-shared NU) (SUNC) | Interconnection | Facilitate the interconnection of GEN-2019-014 | 3116328 | 100% | 3116328 | -
GEN-2019-014 | 03 CENTRAL | 156729 |  | Holcomb 115kV GEN-2019-014 Interconnection (TOIF) (SUNC) | Interconnection | Facilitate the interconnection of GEN-2019-014 | 2584368 | 100% | 2584368 | -
GEN-2019-016 | 03 CENTRAL | 156689 |  | Dadeville 161kV GEN-2019-016 Interconnection (Non-shared NU) (EDE) | Interconnection | Facilitate the interconnection of GEN-2019-016 | 2300858 | 100% | 2300858 | -
GEN-2019-016 | 03 CENTRAL | 156688 |  | Dadeville 161kV GEN-2019-016 Interconnection (TOIF) (EDE) | Interconnection | Facilitate the interconnection of GEN-2019-016 | 14050289 | 100% | 14050289 | -
GEN-2019-018 | 03 CENTRAL | 156786 |  | Saxman 115kV Substation GEN-2019-018 Interconnection (Non-shared NU) (MIDW) | Interconnection | Facilitate the interconnection of GEN-2019-018 | 0 | 100% | 0 | -
GEN-2019-018 | 03 CENTRAL | 156785 |  | Saxman 115kV Substation GEN-2019-018 Interconnection (TOIF) (MIDW) | Interconnection | Facilitate the interconnection of GEN-2019-018 | 0 | 100% | 0 | -
GEN-2019-030 | 03 CENTRAL | 156802 |  | Spearville to Clark County 345 kV GEN-2019-030 Interconnection (Non-shared NU) (ITCGP) | Interconnection | Facilitate the interconnection of GEN-2019-030 | 14337682 | 100% | 14337682 | -
GEN-2019-030 | 03 CENTRAL | 156801 |  | Spearville to Clark County 345 kV GEN-2019-030 Interconnection (TOIF) (ITCGP) | Interconnection | Facilitate the interconnection of GEN-2019-030 | 1207987 | 100% | 1207987 | -
GEN-2019-035 | 03 CENTRAL | 156774 |  | Reeds Spring-Aurora 161kV GEN-2019-035 Interconnection (Non-shared NU) (EDE) | Interconnection | Facilitate the interconnection of GEN-2019-035 | 593644 | 100% | 593644 | -
GEN-2019-035 | 03 CENTRAL | 156773 |  | Reeds Spring-Aurora 161kV GEN-2019-035 Interconnection (TOIF) (EDE) | Interconnection | Facilitate the interconnection of GEN-2019-035 | 8325155 | 100% | 8325155 | -
GEN-2019-044 | 03 CENTRAL | 156751 |  | North Fort Dodge 115kV GEN-2019-044 Interconnection (Non-shared NU) (SUNC) | Interconnection | Facilitate the interconnection of GEN-2019-044 | 6361713 | 100% | 6361713 | -
GEN-2019-044 | 03 CENTRAL | 156750 |  | North Fort Dodge 115kV GEN-2019-044 Interconnection (TOIF) (SUNC) | Interconnection | Facilitate the interconnection of GEN-2019-044 | 297327 | 100% | 297327 | -
GEN-2019-048 | 03 CENTRAL | 156698 |  | Duncan 69kV GEN-2019-048 Interconnection (Non-shared NU) (KCPL) | Interconnection | Facilitate the interconnection of GEN-2019-048 | 350000 | 100% | 350000 | -
GEN-2019-048 | 03 CENTRAL | 156697 |  | Duncan 69kV GEN-2019-048 Interconnection (TOIF) (KCPL) | Interconnection | Facilitate the interconnection of GEN-2019-048 | 500000 | 100% | 500000 | -
GEN-2019-051 | 03 CENTRAL | 156705 |  | Frey Street 115kV GEN-2019-051 Interconnection (TOIF) (SUNC) | Interconnection | Facilitate the interconnection of GEN-2019-051 | 904012.5 | 100% | 904012.5 | -
GEN-2019-051 | 03 CENTRAL | 156707 |  | Frey Street 115kV Interconnection Expansion (DISIS-2018-002 - DISIS-2019-001) | Interconnection | Facilitate the interconnection of GEN-2019-051 | 4816103.3684 | 21.05% | 22876491 | -
GEN-2019-053 | 03 CENTRAL | 156719 |  | Great Bend - Spearville 230kV GEN-2019-053 Interconnection (TOIF) (SUNC) | Interconnection | Facilitate the interconnection of GEN-2019-053 | 397714.5 | 100% | 397714.5 | -
GEN-2019-053 | 03 CENTRAL | 156721 |  | Great Bend - Spearville 230kV Interconnection Expansion (DISIS-2018-002 - DISIS-2019-001) | Interconnection | Facilitate the interconnection of GEN-2019-053 | 3209322.75 | 25% | 12837291 | -
GEN-2019-054 | 03 CENTRAL | 156717 |  | Great Bend - Circle 230kV GEN-2019-054 Interconnection (TOIF) (SUNC) | Interconnection | Facilitate the interconnection of GEN-2019-054 | 401498.5 | 100% | 401498.5 | -
GEN-2019-054 | 03 CENTRAL | 156718 |  | Great Bend - Circle 230kV Interconnection Expansion (DISIS-2018-002 - DISIS-2019-001) | Interconnection | Facilitate the interconnection of GEN-2019-054 | 9936342.75 | 75% | 13248457 | -
GEN-2019-055 | 03 CENTRAL | 156720 |  | Great Bend - Spearville 230kV GEN-2019-055 Interconnection (TOIF) (SUNC) | Interconnection | Facilitate the interconnection of GEN-2019-055 | 397714.5 | 100% | 397714.5 | -
GEN-2019-055 | 03 CENTRAL | 156721 |  | Great Bend - Spearville 230kV Interconnection Expansion (DISIS-2018-002 - DISIS-2019-001) | Interconnection | Facilitate the interconnection of GEN-2019-055 | 9627968.25 | 75% | 12837291 | -
GEN-2019-058 | 03 CENTRAL | 156681 |  | Clark County 345kV GEN-2019-058 Interconnection (TOIF) (ITCGP) | Interconnection | Facilitate the interconnection of GEN-2019-058 | 603993.5 | 100% | 603993.5 | -
GEN-2019-058 | 03 CENTRAL | 156683 |  | Clark County 345kV Interconnection Expansion (DISIS-2018-002 - DISIS-2019-001) | Interconnection | Facilitate the interconnection of GEN-2019-058 | 1398384.75 | 75% | 1864513 | -
GEN-2019-062 | 03 CENTRAL | 156765 |  | El Paso – Pony Meadows 161kV GEN-2019-062 Interconnection (Non-shared NU) (WERE) | Interconnection | Facilitate the interconnection of GEN-2019-062 | 9471666 | 100% | 9471666 | -
GEN-2019-062 | 03 CENTRAL | 156764 |  | El Paso – Pony Meadows 161kV GEN-2019-062 Interconnection (TOIF) (WERE) | Interconnection | Facilitate the interconnection of GEN-2019-062 | 1000000 | 100% | 1000000 | -
GEN-2019-063 | 03 CENTRAL | 156682 |  | Clark County 345kV GEN-2019-063 Interconnection (TOIF) (ITCGP) | Interconnection | Facilitate the interconnection of GEN-2019-063 | 603993.5 | 100% | 603993.5 | -
GEN-2019-063 | 03 CENTRAL | 156683 |  | Clark County 345kV Interconnection Expansion (DISIS-2018-002 - DISIS-2019-001) | Interconnection | Facilitate the interconnection of GEN-2019-063 | 466128.25 | 25% | 1864513 | -
GEN-2019-068 | 03 CENTRAL | 156716 |  | Great Bend - Circle 230kV GEN-2019-068 Interconnection (TOIF) (SUNC) | Interconnection | Facilitate the interconnection of GEN-2019-068 | 401498.5 | 100% | 401498.5 | -
GEN-2019-068 | 03 CENTRAL | 156718 |  | Great Bend - Circle 230kV Interconnection Expansion (DISIS-2018-002 - DISIS-2019-001) | Interconnection | Facilitate the interconnection of GEN-2019-068 | 3312114.25 | 25% | 13248457 | -
GEN-2018-064 | 04 SOUTHEAST | 156823 |  | Tonnece 69kV GEN-2018-064 Interconnection (Non-shared NU) (GRDA) | Interconnection | Facilitate the interconnection of GEN-2018-064 | 446000 | 100% | 446000 | -
GEN-2018-064 | 04 SOUTHEAST | 156822 |  | Tonnece 69kV GEN-2018-064 Interconnection (TOIF) (GRDA) | Interconnection | Facilitate the interconnection of GEN-2018-064 | 0 | 100% | 0 | -
GEN-2018-071 | 04 SOUTHEAST | 156766 |  | Ranch Road 345 kV GEN-2018-071 Interconnection (TOIF) (OGE) | Interconnection | Facilitate the interconnection of GEN-2018-071 | 15000 | 100% | 15000 | -
GEN-2018-071 | 04 SOUTHEAST | 156768 |  | Ranch Road 345 kV Interconnection Expansion (DISIS-2018-002 - DISIS-2019-001) | Interconnection | Facilitate the interconnection of GEN-2018-071 | 15000 | 50% | 30000 | -
GEN-2018-072 | 04 SOUTHEAST | 156767 |  | Ranch Road 345 kV GEN-2018-072 Interconnection (TOIF) (OGE) | Interconnection | Facilitate the interconnection of GEN-2018-072 | 15000 | 100% | 15000 | -
GEN-2018-072 | 04 SOUTHEAST | 156768 |  | Ranch Road 345 kV Interconnection Expansion (DISIS-2018-002 - DISIS-2019-001) | Interconnection | Facilitate the interconnection of GEN-2018-072 | 15000 | 50% | 30000 | -
GEN-2018-079 | 04 SOUTHEAST | 156700 |  | Farmland - Delaware 138kV GEN-2018-079 Interconnection (Non-shared NU) (AEP) | Interconnection | Facilitate the interconnection of GEN-2018-079 | 11400000 | 100% | 11400000 | -
GEN-2018-079 | 04 SOUTHEAST | 156699 |  | Farmland - Delaware 138kV GEN-2018-079 Interconnection (TOIF) (AEP) | Interconnection | Facilitate the interconnection of GEN-2018-079 | 1860836 | 100% | 1860836 | -
GEN-2018-082 | 04 SOUTHEAST | 156760 |  | Pittsburg 345kV GEN-2018-082 Interconnection (Non-shared NU) (AEP) | Interconnection | Facilitate the interconnection of GEN-2018-082 | 14458738 | 100% | 14458738 | -
GEN-2018-082 | 04 SOUTHEAST | 156759 |  | Pittsburg 345kV GEN-2018-082 Interconnection (TOIF) (AEP) | Interconnection | Facilitate the interconnection of GEN-2018-082 | 2977940 | 100% | 2977940 | -
GEN-2018-087 | 04 SOUTHEAST | 156741 |  | Lydia 345kV GEN-2018-087 Interconnection (TOIF) (AEP) | Interconnection | Facilitate the interconnection of GEN-2018-087 | 1305691 | 100% | 1305691 | -
GEN-2018-087 | 04 SOUTHEAST | 156743 |  | Lydia 345kV Interconnection Expansion (DISIS-2018-002 - DISIS-2019-001) | Interconnection | Facilitate the interconnection of GEN-2018-087 | 792955.9756 | 36.59% | 2167413 | -
GEN-2018-088 | 04 SOUTHEAST | 156742 |  | Lydia 345kV GEN-2018-088 Interconnection (TOIF) (AEP) | Interconnection | Facilitate the interconnection of GEN-2018-088 | 1305691 | 100% | 1305691 | -
GEN-2018-088 | 04 SOUTHEAST | 156743 |  | Lydia 345kV Interconnection Expansion (DISIS-2018-002 - DISIS-2019-001) | Interconnection | Facilitate the interconnection of GEN-2018-088 | 1374457.0244 | 63.41% | 2167413 | -
GEN-2018-106 | 04 SOUTHEAST | 156740 |  | Longwood 345kV GEN-2018-106 Interconnection (Non-shared NU) (AEP) | Interconnection | Facilitate the interconnection of GEN-2018-106 | 0 | 100% | 0 | -
GEN-2018-106 | 04 SOUTHEAST | 156739 |  | Longwood 345kV GEN-2018-106 Interconnection (TOIF) (AEP) | Interconnection | Facilitate the interconnection of GEN-2018-106 | 300000 | 100% | 300000 | -
GEN-2018-115 | 04 SOUTHEAST | 156738 |  | Lawton East Side 345kV/138kv GEN-2018-115 Interconnection (Non-shared NU) (AEP) | Interconnection | Facilitate the interconnection of GEN-2018-115 | 4975815 | 100% | 4975815 | -
GEN-2018-115 | 04 SOUTHEAST | 156737 |  | Lawton East Side 345kV/138kv GEN-2018-115 Interconnection (TOIF) (AEP) | Interconnection | Facilitate the interconnection of GEN-2018-115 | 2977940 | 100% | 2977940 | -
GEN-2019-002 | 04 SOUTHEAST | 156745 |  | Maid 161kV GEN-2019-002 Interconnection (Non-shared NU) (GRDA) | Interconnection | Facilitate the interconnection of GEN-2019-002 | 1250000 | 100% | 1250000 | -
GEN-2019-002 | 04 SOUTHEAST | 156744 |  | Maid 161kV GEN-2019-002 Interconnection (TOIF) (GRDA) | Interconnection | Facilitate the interconnection of GEN-2019-002 | 1250000 | 100% | 1250000 | -
GEN-2019-012 | 04 SOUTHEAST | 156830 |  | Woodward 345kV GEN-2019-012 Interconnection (Non-shared NU) (OGE) | Interconnection | Facilitate the interconnection of GEN-2019-012 | 1790448 | 100% | 1790448 | -
GEN-2019-012 | 04 SOUTHEAST | 156829 |  | Woodward 345kV GEN-2019-012 Interconnection (TOIF) (OGE) | Interconnection | Facilitate the interconnection of GEN-2019-012 | 1591654 | 100% | 1591654 | -
GEN-2019-013 | 04 SOUTHEAST | 156694 |  | Sweetwater 230kV and Dempsey 230kV GEN-2019-013 Interconnection (Non-shared NU) (AEP) | Interconnection | Facilitate the interconnection of GEN-2019-013 | 0 | 100% | 0 | -
GEN-2019-013 | 04 SOUTHEAST | 156693 |  | Sweetwater 230kV and Dempsey 230kV GEN-2019-013 Interconnection (TOIF) (AEP) | Interconnection | Facilitate the interconnection of GEN-2019-013 | 600000 | 100% | 600000 | -
GEN-2019-045 | 04 SOUTHEAST | 156690 |  | DeGrasse 138kV GEN-2019-045 Interconnection (TOIF) (OGE) | Interconnection | Facilitate the interconnection of GEN-2019-045 | 1875903 | 100% | 1875903 | -
GEN-2019-045 | 04 SOUTHEAST | 156692 |  | DeGrasse 138kV Interconnection Expansion (DISIS-2018-002 - DISIS-2019-001) | Interconnection | Facilitate the interconnection of GEN-2019-045 | 1637992 | 100% | 1637992 | -
GEN-2019-065 | 04 SOUTHEAST | 156758 |  | Overton-Northwest Henderson 138kV GEN-2019-065 Interconnection (Non-shared NU) (AEP) | Interconnection | Facilitate the interconnection of GEN-2019-065 | 14277112 | 100% | 14277112 | -
GEN-2019-065 | 04 SOUTHEAST | 156757 |  | Overton-Northwest Henderson 138kV GEN-2019-065 Interconnection (TOIF) (AEP) | Interconnection | Facilitate the interconnection of GEN-2019-065 | 1776551 | 100% | 1776551 | -
GEN-2018-073 | 05 SOUTHWEST | 156687 |  | Crawfish 345kV GEN-2018-073 Interconnection (Non-shared NU) (SPS) | Interconnection | Facilitate the interconnection of GEN-2018-073 | 23744495.24 | 100% | 23744495.24 | -
GEN-2018-073 | 05 SOUTHWEST | 156686 |  | Crawfish 345kV GEN-2018-073 Interconnection (TOIF) (SPS) | Interconnection | Facilitate the interconnection of GEN-2018-073 | 1826971.81 | 100% | 1826971.81 | -
GEN-2018-081 | 05 SOUTHWEST | 156761 |  | Plant X 230kV GEN-2018-081 Interconnection (TOIF) (SPS) | Interconnection | Facilitate the interconnection of GEN-2018-081 | 1037920.19 | 100% | 1037920.19 | -
GEN-2018-081 | 05 SOUTHWEST | 156763 |  | Plant X 230kV Interconnection Expansion (DISIS-2018-002 - DISIS-2019-001) | Interconnection | Facilitate the interconnection of GEN-2018-081 | 1924470.9145 | 63.64% | 3024168.58 | -
GEN-2018-089 | 05 SOUTHWEST | 156749 |  | Newhart 230kV GEN-2018-089 Interconnection (Non-shared NU) (SPS) | Interconnection | Facilitate the interconnection of GEN-2018-089 | 2052442.83 | 100% | 2052442.83 | -
GEN-2018-089 | 05 SOUTHWEST | 156748 |  | Newhart 230kV GEN-2018-089 Interconnection (TOIF) (SPS) | Interconnection | Facilitate the interconnection of GEN-2018-089 | 1227189.53 | 100% | 1227189.53 | -
GEN-2018-092 | 05 SOUTHWEST | 156755 |  | Oklaunion - Tuco 345kV GEN-2018-092 Interconnection (TOIF) (SPS) | Interconnection | Facilitate the interconnection of GEN-2018-092 | 2240672.15 | 100% | 2240672.15 | -
GEN-2018-092 | 05 SOUTHWEST | 156756 |  | Oklaunion - Tuco 345kV Interconnection Expansion (DISIS-2018-002 - DISIS-2019-001) | Interconnection | Facilitate the interconnection of GEN-2018-092 | 19604028.62 | 100% | 19604028.62 | -
GEN-2018-097 | 05 SOUTHWEST | 156816 |  | Tolk 230kV GEN-2018-097 Interconnection (TOIF) (SPS) | Interconnection | Facilitate the interconnection of GEN-2018-097 | 224225.4675 | 100% | 224225.4675 | -
GEN-2018-097 | 05 SOUTHWEST | 156821 |  | Tolk 230kV Interconnection Expansion (DISIS-2018-002 - DISIS-2019-001) | Interconnection | Facilitate the interconnection of GEN-2018-097 | 590596.4286 | 17.86% | 3307340 | -
GEN-2018-099 | 05 SOUTHWEST | 156817 |  | Tolk 230kV GEN-2018-099 Interconnection (TOIF) (SPS) | Interconnection | Sharing a GEN Tie line with GEN-2017-158 | 0 | 100% | 0 | -
GEN-2018-099 | 05 SOUTHWEST | 156821 |  | Tolk 230kV Interconnection Expansion (DISIS-2018-002 - DISIS-2019-001) | Interconnection | Sharing a GEN Tie line with GEN-2017-158 | 0 | 100% | 0 | -
GEN-2018-111 | 05 SOUTHWEST | 156818 |  | Tolk 230kV GEN-2018-111 Interconnection (TOIF) (SPS) | Interconnection | Facilitate the interconnection of GEN-2018-111 | 224225.4675 | 100% | 224225.4675 | -
GEN-2018-111 | 05 SOUTHWEST | 156821 |  | Tolk 230kV Interconnection Expansion (DISIS-2018-002 - DISIS-2019-001) | Interconnection | Facilitate the interconnection of GEN-2018-111 | 442947.3214 | 13.39% | 3307340 | -
GEN-2018-112 | 05 SOUTHWEST | 156819 |  | Tolk 230kV GEN-2018-112 Interconnection (TOIF) (SPS) | Interconnection | Facilitate the interconnection of GEN-2018-112 | 224225.4675 | 100% | 224225.4675 | -
GEN-2018-112 | 05 SOUTHWEST | 156821 |  | Tolk 230kV Interconnection Expansion (DISIS-2018-002 - DISIS-2019-001) | Interconnection | Facilitate the interconnection of GEN-2018-112 | 1092603.3929 | 33.04% | 3307340 | -
GEN-2018-124 | 05 SOUTHWEST | 156820 |  | Tolk 230kV GEN-2018-124 Interconnection (TOIF) (SPS) | Interconnection | Facilitate the interconnection of GEN-2018-124 | 224225.4675 | 100% | 224225.4675 | -
GEN-2018-124 | 05 SOUTHWEST | 156821 |  | Tolk 230kV Interconnection Expansion (DISIS-2018-002 - DISIS-2019-001) | Interconnection | Facilitate the interconnection of GEN-2018-124 | 1181192.8571 | 35.71% | 3307340 | -
GEN-2019-003 | 05 SOUTHWEST | 156777 |  | Roosevelt 230kV GEN-2019-003 Interconnection (TOIF) (SPS) | Interconnection | Facilitate the interconnection of GEN-2019-003 | 446204.385 | 100% | 446204.385 | -
GEN-2019-003 | 05 SOUTHWEST | 156779 |  | Roosevelt 230kV Interconnection Expansion (DISIS-2018-002 - DISIS-2019-001) | Interconnection | Facilitate the interconnection of GEN-2019-003 | 2481744.675 | 75% | 3308992.9 | -
GEN-2019-004 | 05 SOUTHWEST | 156726 |  | Hobbs 230kV GEN-2019-004 Interconnection (TOIF) (SPS) | Interconnection | Facilitate the interconnection of GEN-2019-004 | 0 | 100% | 0 | -
GEN-2019-004 | 05 SOUTHWEST | 156728 |  | Hobbs 230kV Interconnection Expansion (DISIS-2018-002 - DISIS-2019-001) | Interconnection | Facilitate the interconnection of GEN-2019-004 | 0 | 100% | 0 | -
GEN-2019-011 | 05 SOUTHWEST | 156832 |  | Yoakum 345kV GEN-2019-011 Interconnection (Non-shared NU) (SPS) | Interconnection | Facilitate the interconnection of GEN-2019-011 | 4162790.99 | 100% | 4162790.99 | -
GEN-2019-011 | 05 SOUTHWEST | 156831 |  | Yoakum 345kV GEN-2019-011 Interconnection (TOIF) (SPS) | Interconnection | Facilitate the interconnection of GEN-2019-011 | 1009778.79 | 100% | 1009778.79 | -
GEN-2019-021 | 05 SOUTHWEST | 156778 |  | Roosevelt 230kV GEN-2019-021 Interconnection (TOIF) (SPS) | Interconnection | Facilitate the interconnection of GEN-2019-021 | 446204.385 | 100% | 446204.385 | -
GEN-2019-021 | 05 SOUTHWEST | 156779 |  | Roosevelt 230kV Interconnection Expansion (DISIS-2018-002 - DISIS-2019-001) | Interconnection | Facilitate the interconnection of GEN-2019-021 | 827248.225 | 25% | 3308992.9 | -
GEN-2019-056 | 05 SOUTHWEST | 156770 |  | Randall 115kV GEN-2019-056 Interconnection (Non-shared NU) (SPS) | Interconnection | Facilitate the interconnection of GEN-2019-056 | 1996462.76 | 100% | 1996462.76 | -
GEN-2019-056 | 05 SOUTHWEST | 156769 |  | Randall 115kV GEN-2019-056 Interconnection (TOIF) (SPS) | Interconnection | Facilitate the interconnection of GEN-2019-056 | 973857.39 | 100% | 973857.39 | -
GEN-2019-074 | 05 SOUTHWEST | 156762 |  | Plant X 230kV GEN-2019-074 Interconnection (TOIF) (SPS) | Interconnection | Facilitate the interconnection of GEN-2019-074 | 1037920.19 | 100% | 1037920.19 | -
GEN-2019-074 | 05 SOUTHWEST | 156763 |  | Plant X 230kV Interconnection Expansion (DISIS-2018-002 - DISIS-2019-001) | Interconnection | Facilitate the interconnection of GEN-2019-074 | 1099697.6655 | 36.36% | 3024168.58 | -
1875887008.07

## Upgrade Summary
Upgrade Type | Study Type | Group | Assigned Study Number | Service Type | Upgrade Name | Upgrade ID | Upgrade Details | Transmission Owner(s) | Estimated Lead Time | Total Upgrade Cost
Current Study | Steady State | 01 NORTH | DISIS-2018-002 & DISIS-2019-001 | ERIS | Build Strandahl to Black Tail 115 kV line | TBD | Build approximately 15 mile of new 115kV line from Strandahl to Black Tail | BEPC-SPP | 36 | 13481505
Current Study | Steady State | 01 NORTH | DISIS-2018-002 & DISIS-2019-001 | ERIS | Add a third 230-69 kV transformer at Denison | TBD | Build a third 230/69kV transformer at Denison | WAPA | 36 | 8000000
Current Study | Steady State | 01 NORTH | DISIS-2018-002 & DISIS-2019-001 | ERIS | Build a second 69 kV line from Denison to Boyer | TBD | Build approximately 2.88 miles of second 230kV line from Denison to Boyer | BEPC-SPP | 36 | 2000000
Current Study | Steady State | 01 NORTH | DISIS-2018-002 & DISIS-2019-001 | ERIS | Rebuild the existing K335AMAI-NI8 to Boyer 69 kV line | TBD | Rebuild approximately 0.69 miles of 69kV line from Boyer to K335AMAI | BEPC-SPP | 36 | 627174.81
Current Study | Steady State | 01 NORTH | DISIS-2018-002 & DISIS-2019-001 | ERIS | Rebuild Gavins to Yankton JCT_115 kV | TBD | Rebuild approximately 4.03 miles of 115kV line from Gavins to Yankton Junction. | WAPA | 36 | 2864685.2
Current Study | Steady State | 01 NORTH | DISIS-2018-002 & DISIS-2019-001 | ERIS | Rebuild the existing K335AMAI-NI8 to K338WTCT-NI8 69 kV line | TBD | Rebuild approximately 0.33 miles of 69 kV line from K335AMAI to K338WTCT | BEPC-SPP | 36 | 299953.17
Current Study | Steady State | 01 NORTH | DISIS-2018-002 & DISIS-2019-001 | ERIS | Rebuild Mont to STRNDAHL Line_115kV | TBD | Rebuild approximately 11.97 miles of 115kV line from Mont to STRNDAHL | BEPC-SPP | 36 | 8508754.8
Current Study | Steady State | 01 NORTH | DISIS-2018-002 & DISIS-2019-001 | ERIS | Rebuild the existing Utica Jct to Napa Jct 115 kV line | TBD | Rebuild approximately 13.16 miles of 115kV line from Utica to NAPA | North Western | 36 | 9354654.4
Current Study | Steady State | 01 NORTH | DISIS-2018-002 & DISIS-2019-001 | ERIS | Upgrade the terminal at Utica Junction | TBD | Replace terminal equipment at Utica Junction to facilitate the Rebuild UTICAJC7 to NAPA JCT _115kV | WAPA | 36 | 400000
Current Study | Steady State | 01 NORTH | DISIS-2018-002 & DISIS-2019-001 | ERIS | Rebuild the existing Yankton Jct to Napa Jct 115 kV line | TBD | Rebuild approximately 2.7 miles of 115kV line from Yankton JCT to NAPA JCT | WAPA/NorthWestern | 36 | 1919268
Current Study | Steady State | 01 NORTH | DISIS-2018-002 & DISIS-2019-001 | ERIS | Replace Belfield 345-230-14 kV First Transformer | TBD | Replace the first 345/230kV transformer at BELFELD | WAPA | 36 | 14835575
Current Study | Steady State | 01 NORTH | DISIS-2018-002 & DISIS-2019-001 | ERIS | Add a 30 MVAR Switched Shunt Capacitor at Hanlon 69 kV | TBD | Build a 30Mvar Switched shunt capacitor at Hanlon | WAPA | 36 | 1020300
Current Study | Steady State | 01 NORTH | DISIS-2018-002 & DISIS-2019-001 | ERIS | Upgrade the terminal at Denison 69 kV | TBD | Replace terminal equipment at Denison 69kV to facilitate the Build Denison to Boyer Second Line_69kV | WAPA | 36 | 1000000
Current Study | Stability | 02 NEBRASKA | DISIS-2018-002 & DISIS-2019-001 | ERIS | Build a 150 Mvar Switched Shunt Capacitor at Red Willow 345 kV Substation | TBD | Build a 150 Mvar Switched Shunt Capacitor at Red Willow 345 kV Substation | NPPD | 36 | 3733650
Current Study | Stability | 02 NEBRASKA | DISIS-2018-002 & DISIS-2019-001 | ERIS | Build a 80 Mvar STATCOM at Sweet Water 345 kV Substation | TBD | Build a 80 Mvar STATCOM at Sweet Water 345 kV Substation | NPPD | 36 | 18102560
Contingent | Steady State | 02 NEBRASKA | 2012 ITP10 | ERIS | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV (R-Plan)(UID 50442 50444 50445 50446) | 50442, 50444, 50445, 50446 | Build approximately 76 miles of new 345kV line from Gentleman to Cherry County and 146 miles from Cherry County to Holt | NPPD | 36 | 332910090
Current Study | Steady State | 02 NEBRASKA | DISIS-2018-002 & DISIS-2019-001 | ERIS | Add FERC827 Switched Shunt for GEN-2018-065_34.5kV | TBD | Add a switched shunt capacitor at GEN-2018-065 substation low side to meet FERC 827 requirement (1 Mvar) |  | 36 | 24891
Current Study | Steady State | 02 NEBRASKA | DISIS-2018-002 & DISIS-2019-001 | ERIS | Add FERC827 Switched Shunt for GEN-2018-068_34.5kV | TBD | Add a switched shunt capacitor at GEN-2018-068 substation low side to meet FERC 827 requirement (56 Mvar) |  | 36 | 1393896
Current Study | Steady State | 02 NEBRASKA | DISIS-2018-002 & DISIS-2019-001 | ERIS | Add FERC827 Switched Shunt for GEN-2018-131_34.5kV | TBD | Add a switched shunt capacitor at GEN-2018-131 substation low side to meet FERC 827 requirement (28 Mvar) |  | 36 | 696948
Current Study | Steady State | 02 NEBRASKA | DISIS-2018-002 & DISIS-2019-001 | ERIS | Add FERC827 Switched Shunt for GEN-2018-132_34.5kV | TBD | Add a switched shunt capacitor at GEN-2018-132 substation low side to meet FERC 827 requirement (26 Mvar) |  | 36 | 647166
Current Study | Steady State | 02 NEBRASKA | DISIS-2018-002 & DISIS-2019-001 | ERIS | Build a Second 345-115kV Transformer at Red Willow | TBD | Build a second 345/115kV transformer at Red Willow | NPPD | 36 | 8302968
Current Study | Steady State | 02 NEBRASKA | DISIS-2018-002 & DISIS-2019-001 | ERIS | Build a Second 345-230 kV Transformer at Hoskins_345kV | TBD | Build a second 345/230kV transformer at Hoskins | NPPD | 36 | 8302968
Current Study | Steady State | 02 NEBRASKA | DISIS-2018-002 & DISIS-2019-001 | ERIS | Build Antelope to Holt 345 kV | TBD | Build approximately 25 miles of 345kV line from Antelope to Holt | NPPD | 36 | 28611100
Current Study | Steady State | 02 NEBRASKA | DISIS-2018-002 & DISIS-2019-001 | ERIS | Build Second 345-115kV transformer at Antelope | TBD | Build a second 345/115kV transformer at Antelope | NPPD | 36 | 8302968
Current Study | Steady State | 02 NEBRASKA | DISIS-2018-002 & DISIS-2019-001 | ERIS | Rebuild Columbus SE to G19-039-TAP 115 kV | TBD | Rebuild approximately 6.76 miles of 115kV line from Clumbus southeast to G16-039-TAP | NPPD | 36 | 4805278.4
Current Study | Steady State | 02 NEBRASKA | DISIS-2018-002 & DISIS-2019-001 | ERIS | Rebuild Rising to G19-039-TAP 115 kV | TBD | Rebuild approximately 6.76 miles of 115kV line from Rising to G19-039-TAP | NPPD | 36 | 4805278.4
Current Study | Steady State | 02 NEBRASKA | DISIS-2018-002 & DISIS-2019-001 | ERIS | Rebuild S3451 to G18-043-TAP Line_345kV | TBD | Rebuild approximately 12.83 miles of 345kV line from S3451 to G18-043-TAP | OPPD / MEC | 36 | 14683216.52
Current Study | Steady State | 02 NEBRASKA | DISIS-2018-002 & DISIS-2019-001 | ERIS | Build Gentleman Satellite substation | TBD | Build Gentleman Satellite substation to facilitate the Build Keystone to Gentleman Second Line_345 kV | NPPD | 36 | 139900000
Current Study | Steady State / Stability | 02 NEBRASKA | DISIS-2018-002 & DISIS-2019-001 | ERIS | Build G19-029-TAP to Keystone Second Line_345 kV | TBD | Build approximately 72.39 miles of second 345 kV line from G19-029-TAP to Keystone | NPPD | 36 | 82846301.16
Current Study | Steady State / Stability | 02 NEBRASKA | DISIS-2018-002 & DISIS-2019-001 | ERIS | Build Keystone to Gentleman Second Line_345 kV | TBD | Build approximately 29.84 miles 345kV second line from Keystone to Gentleman | NPPD | 36 | 45314399.8
Current Study | Stability | 03 CENTRAL | DISIS-2018-002 & DISIS-2019-001 | ERIS | Holcomb to Finney 345 kV Second Line Build | TBD | Build a second 345 kV line from Holcomb to Finney 345 kV | SUNC/SPS | 36 | 13400000
Current Study | Steady State | 03 CENTRAL | DISIS-2018-002 & DISIS-2019-001 | ERIS | Great Bend Tap to 2ND-KS 115 kV Rebuild | TBD | Rebuild the Great Bend Tap to 2ND-KS 115 kV 3.79 mile line | SUNC | 36 | 3182645.2064
Current Study | Steady State | 03 CENTRAL | DISIS-2018-002 & DISIS-2019-001 | ERIS | Great Bend Frey Street to Great Bend Northwest 115 kV Rebuild | TBD | Rebuild the Great Bend Frey Street to Great Bend Northwest 115 kV 5.1 mile line | SUNC | 36 | 4282715.1854
Current Study | Steady State | 03 CENTRAL | DISIS-2018-002 & DISIS-2019-001 | ERIS | Great Bend Frey Street to 2ND-KS 115 kV Rebuild | TBD | Rebuild the Great Bend Frey Street to 2ND-KS 115 kV 1.82 mile line | SUNC | 36 | 1528341.4976
Current Study | Steady State | 03 CENTRAL | DISIS-2018-002 & DISIS-2019-001 | ERIS | Ellsworth Tap to Great Bend 115 kV Equipment Upgrades | TBD | Upgrade equipment at Ellsworth Tap to Great Bend 115 kV substations to increase minimum summer/emergency rating to 105 MVA | SUNC | 36 | 750000
Current Study | Steady State | 03 CENTRAL | DISIS-2018-002 & DISIS-2019-001 | ERIS | Great Bend to Great Bend Northwest 115 kV Rebuild | TBD | Rebuild the Great Bend to Great Bend Northwest 115 kV 3.58 mile line | SUNC | 36 | 3006298.1106
Current Study | Steady State | 03 CENTRAL | DISIS-2018-002 & DISIS-2019-001 | ERIS | Benton to Wichita 345 kV Terminal Equipment Upgrades | TBD | Upgrade terminal equipment at Benton to Wichita 345 kV substations to increase minimum Rate A/Rate B to 915/1145 MVA | Evergy | 36 | 775000
Current Study | Steady State | 03 CENTRAL | DISIS-2018-002 & DISIS-2019-001 | ERIS | Cudahy to Crooked Creek 115 kV Terminal Equipment Upgrades | TBD | Upgrade terminal equipment at Cudahy 115 kV substation to increase minimum summer/emergency rating to 135 MVA | SUNC | 36 | 250000
Current Study | Steady State | 03 CENTRAL | DISIS-2018-002 & DISIS-2019-001 | ERIS | Butler to Midian 138 kV Terminal Equipment Upgrades | TBD | Upgrade terminal equipment at Butler to Midian 138 kV substations to increase minimum summer/emergency rating to 160 MVA | Evergy | 36 | 1814161
Current Study | Steady State | 03 CENTRAL | DISIS-2018-002 & DISIS-2019-001 | ERIS | Jagger 115 kV Reactive Support | TBD | Install +12 MVAR capacitor bank(s) at Jagger 115 kV | SUNC | 36 | 2400000
Current Study | Steady State | 03 CENTRAL | DISIS-2018-002 & DISIS-2019-001 | ERIS | Switch Out Thistle Line Reactor Circuit 1 | TBD | Switch out the Thistle 40 MVAR line reactor on the Clark County to Thistle 345 kV line Circuit 1. Line reactor is remote switchable. | ITC | 36 | 0
Current Study | Steady State | 03 CENTRAL | DISIS-2018-002 & DISIS-2019-001 | ERIS | Switch Out Thistle Line Reactor Circuit 2 | TBD | Switch out the Thistle 40 MVAR line reactor on the Clark County to Thistle 345 kV line Circuit 2. Line reactor is remote switchable. | ITC | 36 | 0
Current Study | Steady State | 03 CENTRAL | DISIS-2018-002 & DISIS-2019-001 | ERIS | Switch Out Wichita Line Reactor Circuit 1 | TBD | Switch out the Wichita 25 MVAR line reactor on the Buffalo to Wichita 345 kV line Circuit 1. Line reactor is remote switchable. | Evergy | 36 | 0
Current Study | Steady State | 03 CENTRAL | DISIS-2018-002 & DISIS-2019-001 | ERIS | Switch Out Wichita Line Reactor Circuit 2 | TBD | Switch out the Wichita 25 MVAR line reactor on the Buffalo to Wichita 345 kV line Circuit 2. Line reactor is remote switchable. | Evergy | 36 | 0
Current Study | Steady State | 03 CENTRAL | DISIS-2018-002 & DISIS-2019-001 | ERIS | Switch Out Buffalo Line Reactor Circuit 1 | TBD | Switch out the Buffalo 50 MVAR line reactor on the Buffalo to Thistle 345 kV line Circuit 1. Line reactor is remote switchable. | Evergy/ITC | 36 | 0
Current Study | Steady State | 03 CENTRAL | DISIS-2018-002 & DISIS-2019-001 | ERIS | Switch Out Buffalo Line Reactor Circuit 2 | TBD | Switch out the Buffalo 50 MVAR line reactor on the Buffalo to Thistle 345 kV line Circuit 2. Line reactor is remote switchable. | Evergy/ITC | 36 | 0
Current Study | Steady State | 04 SOUTHEAST | DISIS-2018-002 & DISIS-2019-001 | ERIS | Sweetwater to Chisholm 230 kV Line Rebuild | TBD | Rebuild the Sweetwater to Chisholm 230 kV 11.15 mile Line to a minimum rating of 581 MVA | AEPW | 36 | 28990000
Current Study | Steady State | 04 SOUTHEAST | DISIS-2018-002 & DISIS-2019-001 | ERIS | Sweetwater to Demarcation 230 kV Line Rebuild | TBD | Rebuild the Sweetwater to Demarcation 230 kV 5 mile Line to a minimum rating of 588 MVA | AEPW/SPS | 36 | 13000000
Current Study | Steady State | 04 SOUTHEAST | DISIS-2018-002 & DISIS-2019-001 | ERIS | Wheeler to Demarcation 230 kV Line Rebuild | TBD | Rebuild the Wheeler to Demarcation 230 kV 13.92 mile Line to a minimum rating of 583 MVA | AEPW/SPS | 36 | 13920000
Current Study | Steady State | 04 SOUTHEAST | DISIS-2018-002 & DISIS-2019-001 | ERIS | Wheeler to Grapevine 230 kV Line Model Correction | TBD | Wheeler to Grapevine 230 kV line rating updated to summer/emergency and winter/emergency ratings of 500/550 MVA and 510/611 MVA | SPS | 36 | 0
Current Study | Steady State / Stability | 04 SOUTHEAST / 05 SOUTHWEST | DISIS-2018-002 & DISIS-2019-001 | ERIS | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | TBD | Build a 345 kV 247.2 mile double circuit line from Crawfish to Lawton Eastside connecting via G18-015-Tap for line 1 and G18-092-Tap for line 2 | SPS | 36 | 413142888
Current Study | Steady State | 05 SOUTHWEST | DISIS-2018-002 & DISIS-2019-001 | ERIS | Tolk 345/230 kV Third Transformer Build | TBD | Build a third 345/230 kV transformer at Tolk | SPS | 36 | 26000000
Current Study | Steady State / Stability | 05 SOUTHWEST | DISIS-2018-002 & DISIS-2019-001 | ERIS | Potter to Chisholm 345 kV Double Circuit Line Build | TBD | Build approximately 170 miles of new double circuit 345 kV lines from Potter County to Chisholm | AEPW/SPS | 36 | 250693500
Current Study | Steady State / Stability | 05 SOUTHWEST | DISIS-2018-002 & DISIS-2019-001 | ERIS | Potter to Tolk 345 kV Double Circuit Line Build | TBD | Build approximately 115 miles of new double circuit 345 kV lines from Potter County to Tolk | SPS | 36 | 172477128
Contingent | Steady State | 05 SOUTHWEST | DISIS-2018-002 & DISIS-2019-001 | ERIS | Multi - Border - Woodward 345 kV Tap (NTC 210627, NTC 210628) | 81717 | Install any necessary terminal equipment to support a new 345 kV line from Border to Woodward 345 kV substation with a summer emergency rating of 1792 MVA. Build 0.84-miles of new 345 kV line from a new tap on the Woodward to Border 345 kV line to Chisholm with a summer emergency rating of 1792 MVA. | OKGE | 36 | 29784319
Current Study | Steady State / Stability | 05 SOUTHWEST | DISIS-2018-002 & DISIS-2019-001 | ERIS | Lawton Eastside 345 kV Substation Upgrade to Double-Bus-Double-Breaker Configuration | TBD | Upgrade the Lawton Eastside 345 kV substation to a double-bus-double-breaker configuration | AEPW | 36 | 36855504
Contingent | Steady State | 01 NORTH | DISIS-2018-002 & DISIS-2019-001 | NRIS | Rebuild the existing Sheynne to Fargo 230 kV line | TBD | Rebuild approximately 4.2 miles of 230kV line from Sheynne to Fargo | WAPA | 36 | 3119998
Contingent | Steady State | 01 NORTH | DISIS-2018-002 & DISIS-2019-001 | NRIS | Fargo 230 kV Terminal Upgrade (NTC ID 210715) | 92394 | Upgrade terminal conductor at Fargo 230 kV substation to support the line to Sheyenne to increase minimum ratings to 458/505 MVA | XEL/WAPA | 36 | 3119998
Current Study | Steady State | 01 NORTH | DISIS-2018-002 & DISIS-2019-001 | NRIS | Beulah to Garrison 115 kV Line Rebuild | TBD | Rebuild the Stanton Basin to Beulah 115 kV 13.41 mile Line, the Stanton Basin to Pick City 115 kV 7.43 mile Line, and the Pick City to Garrison 115 kV 5 mile Line each to a minimum rating of 150 MVA | WAPA | 36 | 11000000
Current Study | Steady State | 02 NEBRASKA | DISIS-2018-002 & DISIS-2019-001 | NRIS | Battle Creek to County Line 115 kV Line Rebuild | TBD | Rebuild the Battle Creek to County Line 115 kV 10.96 mile Line to a minimum rating of 227 MVA | NPPD | 36 | 7790806.4
Current Study | Steady State | 02 NEBRASKA | DISIS-2018-002 & DISIS-2019-001 | NRIS | Battle Creek to Norfork North 115 kV Line Rebuild | TBD | Rebuild the Battle Creek to Norfork North 115 kV 10.56 mile Line to a minimum rating of 222 MVA | NPPD | 36 | 7506470.4
Current Study | Steady State | 02 NEBRASKA | DISIS-2018-002 & DISIS-2019-001 | NRIS | County Line to Antelope 115 kV Line Rebuild | TBD | Rebuild the County Line to Antelope 115 kV 12.2 mile Line to a minimum rating of 231 MVA | NPPD | 36 | 8672248
Current Study | Steady State | 03 CENTRAL | DISIS-2018-002 & DISIS-2019-001 | NRIS | Great Bend Tap to Seward 115 kV Terminal Equipment Upgrade | TBD | Upgrade terminal equipment at Great Bend Tap to Seward 115 kV substation to increase minimum rating to 109 MVA | SUNC | 36 | 240000
Current Study | Steady State | 03 CENTRAL | DISIS-2018-002 & DISIS-2019-001 | NRIS | Seward to St. John 115 kV Terminal Equipment Upgrade | TBD | Upgrade terminal equipment at Seward to St.John 115 kV substation to increase minimum rating to 109 MVA | SUNC | 36 | 240000
Contingent | Steady State | 04 SOUTHEAST | DISIS-2018-002 & DISIS-2019-001 | NRIS | Multi - Minco - Pleasant Valley - Draper 345 kV (NTC 210616, NTC 210656, NTC 210670) | 81741 | Expand the existing Pleasant Valley 138 kV substation to 345 kV with new terminals to accommodate new line from Minco to Pleasant Valley to Draper and terminals to accommodate cut in of existing Cimarron to Draper 345 kV line. Tie into existing Cimarron to Draper 345 kV line. Build 34.8 miles of 345 kV line from Minco to Pleasant Valley 345 kV to achieve a 1792 MVA summer emergency rating. Build a second 13.2-mile 345 kV line from Draper 345 kV substation to Pleasant Valley 345 kV substation with a summer emergency rating of 1792 MVA | OKGE | 36 | 106585363
Current Study | Steady State | 05 SOUTHWEST | DISIS-2018-002 & DISIS-2019-001 | NRIS | Wolfforth to Terry County 115 kV Line Model Correction | TBD | Wolfforth to Terry County 115 kV line rating updated to summer normal/emergency ratings of 230.9 MVA | SPS | 36 | 0
Interconnection |  | 01 NORTH | DISIS-2018-002 & DISIS-2019-001 |  | Denison 230kV GEN-2018-074 Interconnection (Non-shared NU) (WAPA) | 156696 | Facilitate the interconnection of GEN-2018-074 | WAPA | 12 | 0
Interconnection |  | 01 NORTH | DISIS-2018-002 & DISIS-2019-001 |  | Denison 230kV GEN-2018-074 Interconnection (TOIF) (WAPA) | 156695 | Facilitate the interconnection of GEN-2018-074 | WAPA | 12 | 100000
Interconnection |  | 01 NORTH | DISIS-2018-002 & DISIS-2019-001 |  | Leland Olds 345kV GEN-2019-037 Interconnection (Non-shared NU) (BEPC) | 156675 | Facilitate the interconnection of GEN-2019-037 | BEPC | 24 | 3373813
Interconnection |  | 01 NORTH | DISIS-2018-002 & DISIS-2019-001 |  | Leland Olds 345kV GEN-2019-037 Interconnection (TOIF) (BEPC) | 156674 | Facilitate the interconnection of GEN-2019-037 | BEPC | 24 | 1050470
Interconnection |  | 01 NORTH | DISIS-2018-002 & DISIS-2019-001 |  | Siouxland 69kV GEN-2019-019 Interconnection (Non-shared NU) (NIPCO) | 143690 | Facilitate the interconnection of GEN-2019-019 | NIPCO | 12 | 2747959
Interconnection |  | 01 NORTH | DISIS-2018-002 & DISIS-2019-001 |  | Siouxland 69kV GEN-2019-019 Interconnection (TOIF) (NIPCO) | 143689 | Facilitate the interconnection of GEN-2019-019 | NIPCO | 12 | 2747959
Interconnection |  | 01 NORTH | DISIS-2018-002 & DISIS-2019-001 |  | Strandahl 115kV GEN-2018-067 Interconnection (Non-shared NU) (MWEC) | 156804 | Facilitate the interconnection of GEN-2018-067 | MWEC | 24 | 1728103
Interconnection |  | 01 NORTH | DISIS-2018-002 & DISIS-2019-001 |  | Strandahl 115kV GEN-2018-067 Interconnection (TOIF) (MWEC) | 156803 | Facilitate the interconnection of GEN-2018-067 | MWEC | 0 | 0
Interconnection |  | 01 NORTH | DISIS-2018-002 & DISIS-2019-001 |  | Utica Junction 230 kV GEN-2018-070 Interconnection (TOIF) (WAPA) | 156824 | Facilitate the interconnection of GEN-2018-070 | WAPA | 12 | 100000
Interconnection |  | 01 NORTH | DISIS-2018-002 & DISIS-2019-001 |  | WAPA-UGP Mingusville 230kV GEN-2018-069 Interconnection (TOIF) (WAPA) | 156826 | Facilitate the interconnection of GEN-2018-069 | WAPA | 30 | 207000.5
Interconnection |  | 01 NORTH | DISIS-2018-002 & DISIS-2019-001 |  | WAPA-UGP Mingusville 230kV GEN-2019-023 Interconnection (TOIF) (WAPA) | 156827 | Facilitate the interconnection of GEN-2019-023 | WAPA | 12 | 207000.5
Interconnection |  | 01 NORTH | DISIS-2018-002 & DISIS-2019-001 |  | WAPA-UGP Mingusville 230kV Interconnection Expansion (DISIS-2018-002 - DISIS-2019-001) | 156828 | Facilitate the interconnection of GEN-2018-069, GEN-2019-023 | WAPA | 30 | 2416000
Interconnection |  | 01 NORTH | DISIS-2018-002 & DISIS-2019-001 |  | Utica Junction 230 kV GEN-2018-070 Interconnection (Non-shared NU) (WAPA) | 156825 | Facilitate the interconnection of GEN-2018-070 | WAPA | 12 | 0
Interconnection |  | 02 NEBRASKA | DISIS-2018-002 & DISIS-2019-001 |  | Antelope 345kV GEN-2018-131 Interconnection (TOIF) (NPPD) | 156669 | Facilitate the interconnection of GEN-2018-131 | NPPD | 36 | 500000
Interconnection |  | 02 NEBRASKA | DISIS-2018-002 & DISIS-2019-001 |  | Antelope 345kV GEN-2018-065 Interconnection (TOIF) (NPPD) | 156666 | Facilitate the interconnection of GEN-2018-065 | NPPD | 36 | 500000
Interconnection |  | 02 NEBRASKA | DISIS-2018-002 & DISIS-2019-001 |  | Antelope 345kV GEN-2018-068 Interconnection (TOIF) (NPPD) | 156667 | Facilitate the interconnection of GEN-2018-068 | NPPD | 36 | 500000
Interconnection |  | 02 NEBRASKA | DISIS-2018-002 & DISIS-2019-001 |  | Antelope 345kV GEN-2018-132 Interconnection (TOIF) (NPPD) | 156670 | Facilitate the interconnection of GEN-2018-132 | NPPD | 36 | 500000
Interconnection |  | 02 NEBRASKA | DISIS-2018-002 & DISIS-2019-001 |  | Antelope 345kV Interconnection Expansion (2) (DISIS-2018-002 - DISIS-2019-001) | 156671 | Facilitate the interconnection of GEN-2018-131, GEN-2018-132 | NPPD | 36 | 18600000
Interconnection |  | 02 NEBRASKA | DISIS-2018-002 & DISIS-2019-001 |  | Antelope 345kV Interconnection Expansion (DISIS-2018-002 - DISIS-2019-001) | 156668 | Facilitate the interconnection of GEN-2018-065, GEN-2018-068 | NPPD | 36 | 2300000
Interconnection |  | 02 NEBRASKA | DISIS-2018-002 & DISIS-2019-001 |  | Columbus Southeast - Rising City 115kV GEN-2019-039 Interconnection (Non-shared NU) (NPPD) | 156685 | Facilitate the interconnection of GEN-2019-039 | NPPD | 36 | 6800000
Interconnection |  | 02 NEBRASKA | DISIS-2018-002 & DISIS-2019-001 |  | Columbus Southeast - Rising City 115kV GEN-2019-039 Interconnection (TOIF) (NPPD) | 156684 | Facilitate the interconnection of GEN-2019-039 | NPPD | 36 | 700000
Interconnection |  | 02 NEBRASKA | DISIS-2018-002 & DISIS-2019-001 |  | Gentleman to Sweetwater 345kV GEN-2018-125 Interconnection (Non-shared NU) (NPPD) | 156709 | Facilitate the interconnection of GEN-2018-125 | NPPD | 36 | 23100000
Interconnection |  | 02 NEBRASKA | DISIS-2018-002 & DISIS-2019-001 |  | Gentleman to Sweetwater 345kV GEN-2018-125 Interconnection (TOIF) (NPPD) | 156708 | Facilitate the interconnection of GEN-2018-125 | NPPD | 36 | 1000000
Interconnection |  | 02 NEBRASKA | DISIS-2018-002 & DISIS-2019-001 |  | Monolith 115kV GEN-2019-041 Interconnection (Non-shared NU) (NPPD) | 156747 | Facilitate the interconnection of GEN-2019-041 | NPPD | 36 | 1400000
Interconnection |  | 02 NEBRASKA | DISIS-2018-002 & DISIS-2019-001 |  | Monolith 115kV GEN-2019-041 Interconnection (TOIF) (NPPD) | 156746 | Facilitate the interconnection of GEN-2019-041 | NPPD | 36 | 700000
Interconnection |  | 02 NEBRASKA | DISIS-2018-002 & DISIS-2019-001 |  | Raun - Fort Calhoun 345kV GEN-2018-090 Interconnection (Non-shared NU) (OPPD) | 156772 | Facilitate the interconnection of GEN-2018-090 | OPPD | 30 | 0
Interconnection |  | 02 NEBRASKA | DISIS-2018-002 & DISIS-2019-001 |  | Raun - Fort Calhoun 345kV GEN-2018-090 Interconnection (TOIF) (OPPD) | 156771 | Facilitate the interconnection of GEN-2018-090 | OPPD | 30 | 0
Interconnection |  | 02 NEBRASKA | DISIS-2018-002 & DISIS-2019-001 |  | S1263 Brock 161kV GEN-2019-009 Interconnection (Non-shared NU) (OPPD) | 156781 | Facilitate the interconnection of GEN-2019-009 | OPPD | 24 | 1176131
Interconnection |  | 02 NEBRASKA | DISIS-2018-002 & DISIS-2019-001 |  | S1263 Brock 161kV GEN-2019-009 Interconnection (TOIF) (OPPD) | 156780 | Facilitate the interconnection of GEN-2019-009 | OPPD | 24 | 100000
Interconnection |  | 02 NEBRASKA | DISIS-2018-002 & DISIS-2019-001 |  | Shell Creek-Hoskins 345kv GEN-2018-083 Interconnection (TOIF) (NPPD) | 156792 | Facilitate the interconnection of GEN-2018-083 | NPPD | 36 | 250000
Interconnection |  | 02 NEBRASKA | DISIS-2018-002 & DISIS-2019-001 |  | Shell Creek-Hoskins 345kv GEN-2019-069 Interconnection (TOIF) (NPPD) | 156789 | Facilitate the interconnection of GEN-2019-069 | NPPD | 36 | 250000
Interconnection |  | 02 NEBRASKA | DISIS-2018-002 & DISIS-2019-001 |  | Shell Creek-Hoskins 345kv GEN-2019-070 Interconnection (TOIF) (NPPD) | 156790 | Facilitate the interconnection of GEN-2019-070 | NPPD | 36 | 250000
Interconnection |  | 02 NEBRASKA | DISIS-2018-002 & DISIS-2019-001 |  | Shell Creek-Hoskins 345kv GEN-2019-073 Interconnection (TOIF) (NPPD) | 156791 | Facilitate the interconnection of GEN-2019-073 | NPPD | 36 | 250000
Interconnection |  | 02 NEBRASKA | DISIS-2018-002 & DISIS-2019-001 |  | Shell Creek-Hoskins 345kv Interconnection Expansion (DISIS-2018-002 - DISIS-2019-001) | 156793 | Facilitate the interconnection of GEN-2018-083, GEN-2019-069, GEN-2019-070, GEN-2019-073 | NPPD | 36 | 26100000
Interconnection |  | 02 NEBRASKA | DISIS-2018-002 & DISIS-2019-001 |  | Sidney Keystone 345 kV GEN-2019-029 Interconnection (TOIF) (NPPD) | 156798 | Facilitate the interconnection of GEN-2019-029 | NPPD | 36 | 500000
Interconnection |  | 02 NEBRASKA | DISIS-2018-002 & DISIS-2019-001 |  | Sidney Keystone 345 kV GEN-2019-033 Interconnection (TOIF) (NPPD) | 156799 | Facilitate the interconnection of GEN-2019-033 | NPPD | 36 | 500000
Interconnection |  | 02 NEBRASKA | DISIS-2018-002 & DISIS-2019-001 |  | Sidney Keystone 345 kV Interconnection Expansion (DISIS-2018-002 - DISIS-2019-001) | 156800 | Facilitate the interconnection of GEN-2019-029, GEN-2019-033 | NPPD | 36 | 25400000
Interconnection |  | 03 CENTRAL | DISIS-2018-002 & DISIS-2019-001 |  | Buffalo Flats 345kV GEN-2019-001 Interconnection (Non-shared NU) (WERE) | 156815 | Facilitate the interconnection of GEN-2019-001 | WERE | 12 | 20000
Interconnection |  | 03 CENTRAL | DISIS-2018-002 & DISIS-2019-001 |  | Buffalo Flats 345kV GEN-2019-001 Interconnection (TOIF) (WERE) | 156814 | Facilitate the interconnection of GEN-2019-001 | WERE | 12 | 0
Interconnection |  | 03 CENTRAL | DISIS-2018-002 & DISIS-2019-001 |  | Clark County 345kV GEN-2019-058 Interconnection (TOIF) (ITCGP) | 156681 | Facilitate the interconnection of GEN-2019-058 | ITCGP | 24 | 603993.5
Interconnection |  | 03 CENTRAL | DISIS-2018-002 & DISIS-2019-001 |  | Clark County 345kV GEN-2019-063 Interconnection (TOIF) (ITCGP) | 156682 | Facilitate the interconnection of GEN-2019-063 | ITCGP | 24 | 603993.5
Interconnection |  | 03 CENTRAL | DISIS-2018-002 & DISIS-2019-001 |  | Clark County 345kV Interconnection Expansion (DISIS-2018-002 - DISIS-2019-001) | 156683 | Facilitate the interconnection of GEN-2019-058, GEN-2019-063 | ITCGP | 0 | 1864513
Interconnection |  | 03 CENTRAL | DISIS-2018-002 & DISIS-2019-001 |  | Dadeville 161kV GEN-2019-016 Interconnection (Non-shared NU) (EDE) | 156689 | Facilitate the interconnection of GEN-2019-016 | EDE | 36 | 2300858
Interconnection |  | 03 CENTRAL | DISIS-2018-002 & DISIS-2019-001 |  | Dadeville 161kV GEN-2019-016 Interconnection (TOIF) (EDE) | 156688 | Facilitate the interconnection of GEN-2019-016 | EDE | 36 | 14050289
Interconnection |  | 03 CENTRAL | DISIS-2018-002 & DISIS-2019-001 |  | Duncan 69kV GEN-2019-048 Interconnection (Non-shared NU) (KCPL) | 156698 | Facilitate the interconnection of GEN-2019-048 | KCPL | 36 | 350000
Interconnection |  | 03 CENTRAL | DISIS-2018-002 & DISIS-2019-001 |  | Duncan 69kV GEN-2019-048 Interconnection (TOIF) (KCPL) | 156697 | Facilitate the interconnection of GEN-2019-048 | KCPL | 36 | 500000
Interconnection |  | 03 CENTRAL | DISIS-2018-002 & DISIS-2019-001 |  | El Paso – Pony Meadows 161kV GEN-2019-062 Interconnection (Non-shared NU) (WERE) | 156765 | Facilitate the interconnection of GEN-2019-062 | WERE | 36 | 9471666
Interconnection |  | 03 CENTRAL | DISIS-2018-002 & DISIS-2019-001 |  | El Paso – Pony Meadows 161kV GEN-2019-062 Interconnection (TOIF) (WERE) | 156764 | Facilitate the interconnection of GEN-2019-062 | WERE | 36 | 1000000
Interconnection |  | 03 CENTRAL | DISIS-2018-002 & DISIS-2019-001 |  | Frey Street 115kV GEN-2018-116 Interconnection (TOIF) (SUNC) | 156706 | Facilitate the interconnection of GEN-2018-116 | SUNC | 36 | 904012.5
Interconnection |  | 03 CENTRAL | DISIS-2018-002 & DISIS-2019-001 |  | Frey Street 115kV GEN-2019-051 Interconnection (TOIF) (SUNC) | 156705 | Facilitate the interconnection of GEN-2019-051 | SUNC | 36 | 904012.5
Interconnection |  | 03 CENTRAL | DISIS-2018-002 & DISIS-2019-001 |  | Frey Street 115kV Interconnection Expansion (DISIS-2018-002 - DISIS-2019-001) | 156707 | Facilitate the interconnection of GEN-2018-116, GEN-2019-051 | SUNC | 36 | 22876491
Interconnection |  | 03 CENTRAL | DISIS-2018-002 & DISIS-2019-001 |  | Gordan Evans 137kV GEN-2018-093 Interconnection (Non-shared NU) (WERE) | 156713 | Facilitate the interconnection of GEN-2018-093 | WERE | 0 | 20000
Interconnection |  | 03 CENTRAL | DISIS-2018-002 & DISIS-2019-001 |  | Gordan Evans 137kV GEN-2018-093 Interconnection (TOIF) (WERE) | 156712 | Facilitate the interconnection of GEN-2018-093 | WERE | 0 | 0
Interconnection |  | 03 CENTRAL | DISIS-2018-002 & DISIS-2019-001 |  | Great Bend - Circle 230kV GEN-2019-054 Interconnection (TOIF) (SUNC) | 156717 | Facilitate the interconnection of GEN-2019-054 | SUNC | 40 | 401498.5
Interconnection |  | 03 CENTRAL | DISIS-2018-002 & DISIS-2019-001 |  | Great Bend - Circle 230kV GEN-2019-068 Interconnection (TOIF) (SUNC) | 156716 | Facilitate the interconnection of GEN-2019-068 | SUNC | 40 | 401498.5
Interconnection |  | 03 CENTRAL | DISIS-2018-002 & DISIS-2019-001 |  | Great Bend - Circle 230kV Interconnection Expansion (DISIS-2018-002 - DISIS-2019-001) | 156718 | Facilitate the interconnection of GEN-2019-054, GEN-2019-068 | SUNC | 40 | 13248457
Interconnection |  | 03 CENTRAL | DISIS-2018-002 & DISIS-2019-001 |  | Great Bend - Spearville 230kV GEN-2019-053 Interconnection (TOIF) (SUNC) | 156719 | Facilitate the interconnection of GEN-2019-053 | SUNC | 40 | 397714.5
Interconnection |  | 03 CENTRAL | DISIS-2018-002 & DISIS-2019-001 |  | Great Bend - Spearville 230kV GEN-2019-055 Interconnection (TOIF) (SUNC) | 156720 | Facilitate the interconnection of GEN-2019-055 | SUNC | 40 | 397714.5
Interconnection |  | 03 CENTRAL | DISIS-2018-002 & DISIS-2019-001 |  | Great Bend - Spearville 230kV Interconnection Expansion (DISIS-2018-002 - DISIS-2019-001) | 156721 | Facilitate the interconnection of GEN-2019-053, GEN-2019-055 | SUNC | 40 | 12837291
Interconnection |  | 03 CENTRAL | DISIS-2018-002 & DISIS-2019-001 |  | Holcomb 115kV GEN-2019-014 Interconnection (Non-shared NU) (SUNC) | 156730 | Facilitate the interconnection of GEN-2019-014 | SUNC | 36 | 3116328
Interconnection |  | 03 CENTRAL | DISIS-2018-002 & DISIS-2019-001 |  | Holcomb 115kV GEN-2019-014 Interconnection (TOIF) (SUNC) | 156729 | Facilitate the interconnection of GEN-2019-014 | SUNC | 36 | 2584368
Interconnection |  | 03 CENTRAL | DISIS-2018-002 & DISIS-2019-001 |  | KC South - N. Raymore 161kV GEN-2018-121 Interconnection (Non-shared NU) (GMO) | 156732 | Facilitate the interconnection of GEN-2018-121 | GMO | 36 | 112911
Interconnection |  | 03 CENTRAL | DISIS-2018-002 & DISIS-2019-001 |  | KC South - N. Raymore 161kV GEN-2018-121 Interconnection (TOIF) (GMO) | 156731 | Facilitate the interconnection of GEN-2018-121 | GMO | 36 | 0
Interconnection |  | 03 CENTRAL | DISIS-2018-002 & DISIS-2019-001 |  | North Fort Dodge 115kV GEN-2019-044 Interconnection (TOIF) (SUNC) | 156750 | Facilitate the interconnection of GEN-2019-044 | SUNC | 45 | 297327
Interconnection |  | 03 CENTRAL | DISIS-2018-002 & DISIS-2019-001 |  | Reeds Spring-Aurora 161kV GEN-2019-035 Interconnection (Non-shared NU) (EDE) | 156774 | Facilitate the interconnection of GEN-2019-035 | EDE | 24 | 593644
Interconnection |  | 03 CENTRAL | DISIS-2018-002 & DISIS-2019-001 |  | Reeds Spring-Aurora 161kV GEN-2019-035 Interconnection (TOIF) (EDE) | 156773 | Facilitate the interconnection of GEN-2019-035 | EDE | 24 | 8325155
Interconnection |  | 03 CENTRAL | DISIS-2018-002 & DISIS-2019-001 |  | Renfrow-Viola 345 kV GEN-2018-128 Interconnection (Non-shared NU) (WERE) | 156776 | Facilitate the interconnection of GEN-2018-128 | WERE | 42 | 21420837
Interconnection |  | 03 CENTRAL | DISIS-2018-002 & DISIS-2019-001 |  | Saxman 115kV Substation GEN-2019-018 Interconnection (Non-shared NU) (MIDW) | 156786 | Facilitate the interconnection of GEN-2019-018 | MIDW | 0 | 0
Interconnection |  | 03 CENTRAL | DISIS-2018-002 & DISIS-2019-001 |  | Sedalia Marshfield Springfield Nichols Street 69kV GEN-2018-063 Interconnection (Non-shared NU) (EDE) | 156788 | Facilitate the interconnection of GEN-2018-063 | EDE | 36 | 693356
Interconnection |  | 03 CENTRAL | DISIS-2018-002 & DISIS-2019-001 |  | Sedalia Marshfield Springfield Nichols Street 69kV GEN-2018-063 Interconnection (TOIF) (EDE) | 156787 | Facilitate the interconnection of GEN-2018-063 | EDE | 36 | 8294029
Interconnection |  | 03 CENTRAL | DISIS-2018-002 & DISIS-2019-001 |  | Spearville to Clark County 345 kV GEN-2019-030 Interconnection (Non-shared NU) (ITCGP) | 156802 | Facilitate the interconnection of GEN-2019-030 | ITCGP | 24 | 14337682
Interconnection |  | 03 CENTRAL | DISIS-2018-002 & DISIS-2019-001 |  | Spearville to Clark County 345 kV GEN-2019-030 Interconnection (TOIF) (ITCGP) | 156801 | Facilitate the interconnection of GEN-2019-030 | ITCGP | 24 | 1207987
Interconnection |  | 03 CENTRAL | DISIS-2018-002 & DISIS-2019-001 |  | Thistle 345kV GEN-2018-108 Interconnection (Non-shared NU) (ITCGP) | 156813 | Sharing a GEN Tie line with GEN-2018-049 | ITCGP | 0 | 0
Interconnection |  | 03 CENTRAL | DISIS-2018-002 & DISIS-2019-001 |  | Thistle 345kV GEN-2018-108 Interconnection (TOIF) (ITCGP) | 156812 | Sharing a GEN Tie line with GEN-2018-049 | ITCGP | 0 | 0
Interconnection |  | 03 CENTRAL | DISIS-2018-002 & DISIS-2019-001 |  | North Fort Dodge 115kV GEN-2019-044 Interconnection (Non-shared NU) (SUNC) | 156751 | Facilitate the interconnection of GEN-2019-044 | SUNC | 45 | 6361713
Interconnection |  | 03 CENTRAL | DISIS-2018-002 & DISIS-2019-001 |  | Renfrow-Viola 345 kV GEN-2018-128 Interconnection (TOIF) (WERE) | 156775 | Facilitate the interconnection of GEN-2018-128 | WERE | 42 | 0
Interconnection |  | 03 CENTRAL | DISIS-2018-002 & DISIS-2019-001 |  | Saxman 115kV Substation GEN-2019-018 Interconnection (TOIF) (MIDW) | 156785 | Facilitate the interconnection of GEN-2019-018 | MIDW | 0 | 0
Interconnection |  | 04 SOUTHEAST | DISIS-2018-002 & DISIS-2019-001 |  | DeGrasse 138kV GEN-2019-045 Interconnection (TOIF) (OGE) | 156690 | Facilitate the interconnection of GEN-2019-045 | OGE | 18 | 1875903
Interconnection |  | 04 SOUTHEAST | DISIS-2018-002 & DISIS-2019-001 |  | DeGrasse 138kV Interconnection Expansion (DISIS-2018-002 - DISIS-2019-001) | 156692 | Facilitate the interconnection of GEN-2019-045 | OGE | 18 | 1637992
Interconnection |  | 04 SOUTHEAST | DISIS-2018-002 & DISIS-2019-001 |  | Farmland - Delaware 138kV GEN-2018-079 Interconnection (Non-shared NU) (AEP) | 156700 | Facilitate the interconnection of GEN-2018-079 | AEP | 30 | 11400000
Interconnection |  | 04 SOUTHEAST | DISIS-2018-002 & DISIS-2019-001 |  | Farmland - Delaware 138kV GEN-2018-079 Interconnection (TOIF) (AEP) | 156699 | Facilitate the interconnection of GEN-2018-079 | AEP | 30 | 1860836
Interconnection |  | 04 SOUTHEAST | DISIS-2018-002 & DISIS-2019-001 |  | Lawton East Side 345kV/138kv GEN-2018-115 Interconnection (Non-shared NU) (AEP) | 156738 | Facilitate the interconnection of GEN-2018-115 | AEP | 30 | 4975815
Interconnection |  | 04 SOUTHEAST | DISIS-2018-002 & DISIS-2019-001 |  | Lawton East Side 345kV/138kv GEN-2018-115 Interconnection (TOIF) (AEP) | 156737 | Facilitate the interconnection of GEN-2018-115 | AEP | 30 | 2977940
Interconnection |  | 04 SOUTHEAST | DISIS-2018-002 & DISIS-2019-001 |  | Longwood 345kV GEN-2018-106 Interconnection (Non-shared NU) (AEP) | 156740 | Facilitate the interconnection of GEN-2018-106 | AEP | 24 | 0
Interconnection |  | 04 SOUTHEAST | DISIS-2018-002 & DISIS-2019-001 |  | Longwood 345kV GEN-2018-106 Interconnection (TOIF) (AEP) | 156739 | Facilitate the interconnection of GEN-2018-106 | AEP | 24 | 300000
Interconnection |  | 04 SOUTHEAST | DISIS-2018-002 & DISIS-2019-001 |  | Lydia 345kV GEN-2018-087 Interconnection (TOIF) (AEP) | 156741 | Facilitate the interconnection of GEN-2018-087 | AEP | 24 | 1305691
Interconnection |  | 04 SOUTHEAST | DISIS-2018-002 & DISIS-2019-001 |  | Lydia 345kV GEN-2018-088 Interconnection (TOIF) (AEP) | 156742 | Facilitate the interconnection of GEN-2018-088 | AEP | 24 | 1305691
Interconnection |  | 04 SOUTHEAST | DISIS-2018-002 & DISIS-2019-001 |  | Lydia 345kV Interconnection Expansion (DISIS-2018-002 - DISIS-2019-001) | 156743 | Facilitate the interconnection of GEN-2018-087, GEN-2018-088 | AEP | 24 | 2167413
Interconnection |  | 04 SOUTHEAST | DISIS-2018-002 & DISIS-2019-001 |  | Maid 161kV GEN-2019-002 Interconnection (Non-shared NU) (GRDA) | 156745 | Facilitate the interconnection of GEN-2019-002 | GRDA | 18 | 1250000
Interconnection |  | 04 SOUTHEAST | DISIS-2018-002 & DISIS-2019-001 |  | Maid 161kV GEN-2019-002 Interconnection (TOIF) (GRDA) | 156744 | Facilitate the interconnection of GEN-2019-002 | GRDA | 18 | 1250000
Interconnection |  | 04 SOUTHEAST | DISIS-2018-002 & DISIS-2019-001 |  | Overton-Northwest Henderson 138kV GEN-2019-065 Interconnection (Non-shared NU) (AEP) | 156758 | Facilitate the interconnection of GEN-2019-065 | AEP | 30 | 14277112
Interconnection |  | 04 SOUTHEAST | DISIS-2018-002 & DISIS-2019-001 |  | Overton-Northwest Henderson 138kV GEN-2019-065 Interconnection (TOIF) (AEP) | 156757 | Facilitate the interconnection of GEN-2019-065 | AEP | 30 | 1776551
Interconnection |  | 04 SOUTHEAST | DISIS-2018-002 & DISIS-2019-001 |  | Pittsburg 345kV GEN-2018-082 Interconnection (Non-shared NU) (AEP) | 156760 | Facilitate the interconnection of GEN-2018-082 | AEP | 36 | 14458738
Interconnection |  | 04 SOUTHEAST | DISIS-2018-002 & DISIS-2019-001 |  | Pittsburg 345kV GEN-2018-082 Interconnection (TOIF) (AEP) | 156759 | Facilitate the interconnection of GEN-2018-082 | AEP | 36 | 2977940
Interconnection |  | 04 SOUTHEAST | DISIS-2018-002 & DISIS-2019-001 |  | Ranch Road 345 kV GEN-2018-071 Interconnection (TOIF) (OGE) | 156766 | Facilitate the interconnection of GEN-2018-071 | OGE | 9 | 15000
Interconnection |  | 04 SOUTHEAST | DISIS-2018-002 & DISIS-2019-001 |  | Ranch Road 345 kV GEN-2018-072 Interconnection (TOIF) (OGE) | 156767 | Facilitate the interconnection of GEN-2018-072 | OGE | 9 | 15000
Interconnection |  | 04 SOUTHEAST | DISIS-2018-002 & DISIS-2019-001 |  | Ranch Road 345 kV Interconnection Expansion (DISIS-2018-002 - DISIS-2019-001) | 156768 | Facilitate the interconnection of GEN-2018-071, GEN-2018-072 | OGE | 9 | 30000
Interconnection |  | 04 SOUTHEAST | DISIS-2018-002 & DISIS-2019-001 |  | Sweetwater 230kV and Dempsey 230kV GEN-2019-013 Interconnection (Non-shared NU) (AEP) | 156694 | Facilitate the interconnection of GEN-2019-013 | AEP | 24 | 0
Interconnection |  | 04 SOUTHEAST | DISIS-2018-002 & DISIS-2019-001 |  | Sweetwater 230kV and Dempsey 230kV GEN-2019-013 Interconnection (TOIF) (AEP) | 156693 | Facilitate the interconnection of GEN-2019-013 | AEP | 24 | 600000
Interconnection |  | 04 SOUTHEAST | DISIS-2018-002 & DISIS-2019-001 |  | Tonnece 69kV GEN-2018-064 Interconnection (Non-shared NU) (GRDA) | 156823 | Facilitate the interconnection of GEN-2018-064 | GRDA | 0 | 446000
Interconnection |  | 04 SOUTHEAST | DISIS-2018-002 & DISIS-2019-001 |  | Woodward 345kV GEN-2019-012 Interconnection (Non-shared NU) (OGE) | 156830 | Facilitate the interconnection of GEN-2019-012 | OGE | 18 | 1790448
Interconnection |  | 04 SOUTHEAST | DISIS-2018-002 & DISIS-2019-001 |  | Woodward 345kV GEN-2019-012 Interconnection (TOIF) (OGE) | 156829 | Facilitate the interconnection of GEN-2019-012 | OGE | 18 | 1591654
Interconnection |  | 04 SOUTHEAST | DISIS-2018-002 & DISIS-2019-001 |  | Tonnece 69kV GEN-2018-064 Interconnection (TOIF) (GRDA) | 156822 | Facilitate the interconnection of GEN-2018-064 | GRDA | 18 | 0
Interconnection |  | 05 SOUTHWEST | DISIS-2018-002 & DISIS-2019-001 |  | Crawfish 345kV GEN-2018-073 Interconnection (Non-shared NU) (SPS) | 156687 | Facilitate the interconnection of GEN-2018-073 | SPS | 36 | 23744495.24
Interconnection |  | 05 SOUTHWEST | DISIS-2018-002 & DISIS-2019-001 |  | Crawfish 345kV GEN-2018-073 Interconnection (TOIF) (SPS) | 156686 | Facilitate the interconnection of GEN-2018-073 | SPS | 36 | 1826971.81
Interconnection |  | 05 SOUTHWEST | DISIS-2018-002 & DISIS-2019-001 |  | Hobbs 230kV GEN-2019-004 Interconnection (TOIF) (SPS) | 156726 | Facilitate the interconnection of GEN-2019-004 | SPS | 0 | 0
Interconnection |  | 05 SOUTHWEST | DISIS-2018-002 & DISIS-2019-001 |  | Hobbs 230kV Interconnection Expansion (DISIS-2018-002 - DISIS-2019-001) | 156728 | Facilitate the interconnection of GEN-2019-004 | SPS | 0 | 0
Interconnection |  | 05 SOUTHWEST | DISIS-2018-002 & DISIS-2019-001 |  | Newhart 230kV GEN-2018-089 Interconnection (Non-shared NU) (SPS) | 156749 | Facilitate the interconnection of GEN-2018-089 | SPS | 36 | 2052442.83
Interconnection |  | 05 SOUTHWEST | DISIS-2018-002 & DISIS-2019-001 |  | Newhart 230kV GEN-2018-089 Interconnection (TOIF) (SPS) | 156748 | Facilitate the interconnection of GEN-2018-089 | SPS | 36 | 1227189.53
Interconnection |  | 05 SOUTHWEST | DISIS-2018-002 & DISIS-2019-001 |  | Oklaunion - Tuco 345kV GEN-2018-092 Interconnection (TOIF) (SPS) | 156755 | Facilitate the interconnection of GEN-2018-092 | SPS | 36 | 2240672.15
Interconnection |  | 05 SOUTHWEST | DISIS-2018-002 & DISIS-2019-001 |  | Oklaunion - Tuco 345kV Interconnection Expansion (DISIS-2018-002 - DISIS-2019-001) | 156756 | Facilitate the interconnection of GEN-2018-092 | SPS | 36 | 19604028.62
Interconnection |  | 05 SOUTHWEST | DISIS-2018-002 & DISIS-2019-001 |  | Plant X 230kV GEN-2018-081 Interconnection (TOIF) (SPS) | 156761 | Facilitate the interconnection of GEN-2018-081 | SPS | 36 | 1037920.19
Interconnection |  | 05 SOUTHWEST | DISIS-2018-002 & DISIS-2019-001 |  | Plant X 230kV GEN-2019-074 Interconnection (TOIF) (SPS) | 156762 | Facilitate the interconnection of GEN-2019-074 | SPS | 36 | 1037920.19
Interconnection |  | 05 SOUTHWEST | DISIS-2018-002 & DISIS-2019-001 |  | Plant X 230kV Interconnection Expansion (DISIS-2018-002 - DISIS-2019-001) | 156763 | Facilitate the interconnection of GEN-2018-081, GEN-2019-074 | SPS | 36 | 3024168.58
Interconnection |  | 05 SOUTHWEST | DISIS-2018-002 & DISIS-2019-001 |  | Randall 115kV GEN-2019-056 Interconnection (Non-shared NU) (SPS) | 156770 | Facilitate the interconnection of GEN-2019-056 | SPS | 36 | 1996462.76
Interconnection |  | 05 SOUTHWEST | DISIS-2018-002 & DISIS-2019-001 |  | Randall 115kV GEN-2019-056 Interconnection (TOIF) (SPS) | 156769 | Facilitate the interconnection of GEN-2019-056 | SPS | 36 | 973857.39
Interconnection |  | 05 SOUTHWEST | DISIS-2018-002 & DISIS-2019-001 |  | Roosevelt 230kV GEN-2019-003 Interconnection (TOIF) (SPS) | 156777 | Facilitate the interconnection of GEN-2019-003 | SPS | 36 | 446204.385
Interconnection |  | 05 SOUTHWEST | DISIS-2018-002 & DISIS-2019-001 |  | Roosevelt 230kV GEN-2019-021 Interconnection (TOIF) (SPS) | 156778 | Facilitate the interconnection of GEN-2019-021 | SPS | 36 | 446204.385
Interconnection |  | 05 SOUTHWEST | DISIS-2018-002 & DISIS-2019-001 |  | Roosevelt 230kV Interconnection Expansion (DISIS-2018-002 - DISIS-2019-001) | 156779 | Facilitate the interconnection of GEN-2019-003, GEN-2019-021 | SPS | 36 | 3308992.9
Interconnection |  | 05 SOUTHWEST | DISIS-2018-002 & DISIS-2019-001 |  | Tolk 230kV GEN-2018-097 Interconnection (TOIF) (SPS) | 156816 | Facilitate the interconnection of GEN-2018-097 | SPS | 36 | 224225.4675
Interconnection |  | 05 SOUTHWEST | DISIS-2018-002 & DISIS-2019-001 |  | Tolk 230kV GEN-2018-099 Interconnection (TOIF) (SPS) | 156817 | Sharing a GEN Tie line with GEN-2017-158 | SPS | 0 | 0
Interconnection |  | 05 SOUTHWEST | DISIS-2018-002 & DISIS-2019-001 |  | Tolk 230kV GEN-2018-111 Interconnection (TOIF) (SPS) | 156818 | Facilitate the interconnection of GEN-2018-111 | SPS | 36 | 224225.4675
Interconnection |  | 05 SOUTHWEST | DISIS-2018-002 & DISIS-2019-001 |  | Tolk 230kV GEN-2018-112 Interconnection (TOIF) (SPS) | 156819 | Facilitate the interconnection of GEN-2018-112 | SPS | 36 | 224225.4675
Interconnection |  | 05 SOUTHWEST | DISIS-2018-002 & DISIS-2019-001 |  | Tolk 230kV GEN-2018-124 Interconnection (TOIF) (SPS) | 156820 | Facilitate the interconnection of GEN-2018-124 | SPS | 36 | 224225.4675
Interconnection |  | 05 SOUTHWEST | DISIS-2018-002 & DISIS-2019-001 |  | Tolk 230kV Interconnection Expansion (DISIS-2018-002 - DISIS-2019-001) | 156821 | Facilitate the interconnection of GEN-2018-097, GEN-2018-111, GEN-2018-112, GEN-2018-124, GEN-2018-099 | SPS | 36 | 3307340
Interconnection |  | 05 SOUTHWEST | DISIS-2018-002 & DISIS-2019-001 |  | Yoakum 345kV GEN-2019-011 Interconnection (Non-shared NU) (SPS) | 156832 | Facilitate the interconnection of GEN-2019-011 | SPS | 36 | 4162790.99
Interconnection |  | 05 SOUTHWEST | DISIS-2018-002 & DISIS-2019-001 |  | Yoakum 345kV GEN-2019-011 Interconnection (TOIF) (SPS) | 156831 | Facilitate the interconnection of GEN-2019-011 | SPS | 36 | 1009778.79
2351406776.07

## All Thermal
SOLUTIONTYPE | GROUP | SCENARIO | SEASON | SOURCE | DIRECTION | MONTCOMMONNAME | RATEA | RATEB | TDF | TC%LOADING | CONTNAME
Non-Converge | 00ALL | 0 | 23SP | N/A | " | None |  |  |  |  | None
Non-Converge | 00ALL | 0 | 26SP | N/A | " | None |  |  |  |  | None
Non-Converge | 00ALL | 0 | 26WP | N/A | " | None |  |  |  |  | None
Thermal | 00ALL | 1 | 23SP | N/A | " | None |  |  |  |  | None
Thermal | 00ALL | 1 | 26SP | N/A | " | None |  |  |  |  | None
Thermal | 00ALL | 1 | 26WP | N/A | " | None |  |  |  |  | None
Non-Converge | 00NR | 0 | 23SP | N/A | " | None |  |  |  |  | None
Non-Converge | 00NR | 0 | 26SP | N/A | " | None |  |  |  |  | None
Non-Converge | 00NR | 0 | 26WP | N/A | " | None |  |  |  |  | None
Thermal | 00NR | 1 | 23SP | GEN-2018-069 | FROM->TO | 602006 SHEYNNE4 230 652435 FARGO 4 230 1 |  | 342 | 0.05923 | 100.24 | P12:345:MPC:JAMESTOWN-BISON:JAMESTN3:BISON 3
Thermal | 00NR | 1 | 23SP | GEN-2018-069 | FROM->TO | 602006 SHEYNNE4 230 652435 FARGO 4 230 1 |  | 342 | 0.05935 | 100.39 | P23:345:OTP:BUFFALO3:3655:V2016
Thermal | 00NR | 1 | 23SP | GEN-2018-069 | FROM->TO | 602006 SHEYNNE4 230 652435 FARGO 4 230 1 |  | 342 | 0.05937 | 100.52 | P12:345:OTP:AUTO-SINGLE:BUFFALO3:JAMESTN3:1
Thermal | 00NR | 1 | 23SP | GEN-2018-069 | FROM->TO | 602006 SHEYNNE4 230 652435 FARGO 4 230 1 |  | 342 | 0.05937 | 100.52 | P23:345:OTP:JAMESTN3:3145:V2020
Thermal | 00NR | 1 | 23SP | GEN-2018-069 | FROM->TO | 602006 SHEYNNE4 230 652435 FARGO 4 230 1 |  | 342 | 0.05937 | 100.52 | P23:345:OTP:JAMESTN3:3135:V2020
Thermal | 00NR | 1 | 23SP | GEN-2018-069 | FROM->TO | 602006 SHEYNNE4 230 652435 FARGO 4 230 1 |  | 342 | 0.05937 | 100.52 | P21:345:OTP:AUTO-SINGLE:BUFFALO3:JAMESTN3:1
Thermal | 00NR | 1 | 23SP | GEN-2018-071 | FROM->TO | 514898 CIMARON4 138 997944 CIMARON1 _1 138 1 |  | 478 | 0.03261 | 102.26 | P13:138-345:OKGE:BKRBKR_3W021::::
Thermal | 00NR | 1 | 23SP | GEN-2018-071 | FROM->TO | 514901 CIMARON7 345 997944 CIMARON1 _1 138 1 |  | 478 | 0.03261 | 106.39 | P13:138-345:OKGE:BKRBKR_3W021::::
Thermal | 00NR | 1 | 23SP | GEN-2018-072 | FROM->TO | 514898 CIMARON4 138 997944 CIMARON1 _1 138 1 |  | 478 | 0.03261 | 102.26 | P13:138-345:OKGE:BKRBKR_3W021::::
Thermal | 00NR | 1 | 23SP | GEN-2018-072 | FROM->TO | 514901 CIMARON7 345 997944 CIMARON1 _1 138 1 |  | 478 | 0.03261 | 106.39 | P13:138-345:OKGE:BKRBKR_3W021::::
Thermal | 00NR | 1 | 23SP | GEN-2018-116 | FROM->TO | 539666 GBENDTP3 115 539692 SEWARD 3 115 1 |  | 101 | 0.17071 | 107.54 | 532871 CIRCLE 6 230 763862 G19-054-TAP 230 1
Thermal | 00NR | 1 | 23SP | GEN-2018-116 | FROM->TO | 539692 SEWARD 3 115 539696 ST-JOHN3 115 1 |  | 101 | 0.16389 | 101.17 | 532871 CIRCLE 6 230 763862 G19-054-TAP 230 1
Thermal | 00NR | 1 | 23SP | GEN-2019-012 | FROM->TO | 514898 CIMARON4 138 997944 CIMARON1 _1 138 1 |  | 478 | 0.03691 | 102.26 | P13:138-345:OKGE:BKRBKR_3W021::::
Thermal | 00NR | 1 | 23SP | GEN-2019-012 | FROM->TO | 514901 CIMARON7 345 997944 CIMARON1 _1 138 1 |  | 478 | 0.03691 | 106.39 | P13:138-345:OKGE:BKRBKR_3W021::::
Thermal | 00NR | 1 | 23SP | GEN-2019-023 | FROM->TO | 602006 SHEYNNE4 230 652435 FARGO 4 230 1 |  | 342 | 0.05923 | 100.24 | P12:345:MPC:JAMESTOWN-BISON:JAMESTN3:BISON 3
Thermal | 00NR | 1 | 23SP | GEN-2019-023 | FROM->TO | 602006 SHEYNNE4 230 652435 FARGO 4 230 1 |  | 342 | 0.05935 | 100.39 | P23:345:OTP:BUFFALO3:3655:V2016
Thermal | 00NR | 1 | 23SP | GEN-2019-023 | FROM->TO | 602006 SHEYNNE4 230 652435 FARGO 4 230 1 |  | 342 | 0.05937 | 100.52 | P12:345:OTP:AUTO-SINGLE:BUFFALO3:JAMESTN3:1
Thermal | 00NR | 1 | 23SP | GEN-2019-023 | FROM->TO | 602006 SHEYNNE4 230 652435 FARGO 4 230 1 |  | 342 | 0.05937 | 100.52 | P23:345:OTP:JAMESTN3:3145:V2020
Thermal | 00NR | 1 | 23SP | GEN-2019-023 | FROM->TO | 602006 SHEYNNE4 230 652435 FARGO 4 230 1 |  | 342 | 0.05937 | 100.52 | P23:345:OTP:JAMESTN3:3135:V2020
Thermal | 00NR | 1 | 23SP | GEN-2019-023 | FROM->TO | 602006 SHEYNNE4 230 652435 FARGO 4 230 1 |  | 342 | 0.05937 | 100.52 | P21:345:OTP:AUTO-SINGLE:BUFFALO3:JAMESTN3:1
Thermal | 00NR | 1 | 23SP | GEN-2019-051 | FROM->TO | 539666 GBENDTP3 115 539692 SEWARD 3 115 1 |  | 101 | 0.17071 | 107.54 | 532871 CIRCLE 6 230 763862 G19-054-TAP 230 1
Thermal | 00NR | 1 | 23SP | GEN-2019-051 | FROM->TO | 539692 SEWARD 3 115 539696 ST-JOHN3 115 1 |  | 101 | 0.16389 | 101.17 | 532871 CIRCLE 6 230 763862 G19-054-TAP 230 1
Thermal | 00NR | 1 | 23SP | GEN-2019-052 | FROM->TO | 514898 CIMARON4 138 997944 CIMARON1 _1 138 1 |  | 478 | 0.10043 | 102.26 | P13:138-345:OKGE:BKRBKR_3W021::::
Thermal | 00NR | 1 | 23SP | GEN-2019-052 | FROM->TO | 514901 CIMARON7 345 997944 CIMARON1 _1 138 1 |  | 478 | 0.10043 | 106.39 | P13:138-345:OKGE:BKRBKR_3W021::::
Thermal | 00NR | 1 | 23SP | GEN-2019-053 | FROM->TO | 539666 GBENDTP3 115 539692 SEWARD 3 115 1 |  | 101 | 0.03316 | 107.54 | 532871 CIRCLE 6 230 763862 G19-054-TAP 230 1
Thermal | 00NR | 1 | 23SP | GEN-2019-053 | FROM->TO | 539692 SEWARD 3 115 539696 ST-JOHN3 115 1 |  | 101 | 0.03992 | 101.17 | 532871 CIRCLE 6 230 763862 G19-054-TAP 230 1
Thermal | 00NR | 1 | 23SP | GEN-2019-054 | FROM->TO | 539666 GBENDTP3 115 539692 SEWARD 3 115 1 |  | 101 | 0.06926 | 107.54 | 532871 CIRCLE 6 230 763862 G19-054-TAP 230 1
Thermal | 00NR | 1 | 23SP | GEN-2019-054 | FROM->TO | 539692 SEWARD 3 115 539696 ST-JOHN3 115 1 |  | 101 | 0.08304 | 101.17 | 532871 CIRCLE 6 230 763862 G19-054-TAP 230 1
Thermal | 00NR | 1 | 23SP | GEN-2019-055 | FROM->TO | 539666 GBENDTP3 115 539692 SEWARD 3 115 1 |  | 101 | 0.03316 | 107.54 | 532871 CIRCLE 6 230 763862 G19-054-TAP 230 1
Thermal | 00NR | 1 | 23SP | GEN-2019-055 | FROM->TO | 539692 SEWARD 3 115 539696 ST-JOHN3 115 1 |  | 101 | 0.03992 | 101.17 | 532871 CIRCLE 6 230 763862 G19-054-TAP 230 1
Thermal | 00NR | 1 | 23SP | GEN-2019-067 | FROM->TO | 514898 CIMARON4 138 997944 CIMARON1 _1 138 1 |  | 478 | 0.10043 | 102.26 | P13:138-345:OKGE:BKRBKR_3W021::::
Thermal | 00NR | 1 | 23SP | GEN-2019-067 | FROM->TO | 514901 CIMARON7 345 997944 CIMARON1 _1 138 1 |  | 478 | 0.10043 | 106.39 | P13:138-345:OKGE:BKRBKR_3W021::::
Thermal | 00NR | 1 | 23SP | GEN-2019-068 | FROM->TO | 539666 GBENDTP3 115 539692 SEWARD 3 115 1 |  | 101 | 0.06926 | 107.54 | 532871 CIRCLE 6 230 763862 G19-054-TAP 230 1
Thermal | 00NR | 1 | 23SP | GEN-2019-068 | FROM->TO | 539692 SEWARD 3 115 539696 ST-JOHN3 115 1 |  | 101 | 0.08304 | 101.17 | 532871 CIRCLE 6 230 763862 G19-054-TAP 230 1
Thermal | 00NR | 1 | 26SP | GEN-2018-116 | FROM->TO | 539666 GBENDTP3 115 539692 SEWARD 3 115 1 |  | 101 | 0.17156 | 103.49 | 532871 CIRCLE 6 230 763862 G19-054-TAP 230 1
Thermal | 00NR | 1 | 26SP | GEN-2019-011 | FROM->TO | 526524 WOLFFORTH 3 115 526736 TERRY_CNTY 3 115 1 |  | 164 | 0.03399 | 101.03 | P42:345:SPS:YOAKUM:J18####:SLG1:EHV:
Thermal | 00NR | 1 | 26SP | GEN-2019-011 | FROM->TO | 526524 WOLFFORTH 3 115 526736 TERRY_CNTY 3 115 1 |  | 164 | 0.03399 | 101.03 | P43:345:SPS:YOAKUM:TF#####:SLG:EHV:
Thermal | 00NR | 1 | 26SP | GEN-2019-011 | FROM->TO | 526524 WOLFFORTH 3 115 526736 TERRY_CNTY 3 115 1 |  | 164 | 0.03399 | 101.03 | P42:345:SPS:YOAKUM:J17####:SLG:EHV:
Thermal | 00NR | 1 | 26SP | GEN-2019-011 | FROM->TO | 526524 WOLFFORTH 3 115 526736 TERRY_CNTY 3 115 1 |  | 164 | 0.03399 | 101.03 | P42:345:SPS:YOAKUM:J18####:SLG2:EHV:
Thermal | 00NR | 1 | 26SP | GEN-2019-051 | FROM->TO | 539666 GBENDTP3 115 539692 SEWARD 3 115 1 |  | 101 | 0.17156 | 103.49 | 532871 CIRCLE 6 230 763862 G19-054-TAP 230 1
Thermal | 00NR | 1 | 26SP | GEN-2019-053 | FROM->TO | 539666 GBENDTP3 115 539692 SEWARD 3 115 1 |  | 101 | 0.034 | 103.49 | 532871 CIRCLE 6 230 763862 G19-054-TAP 230 1
Thermal | 00NR | 1 | 26SP | GEN-2019-054 | FROM->TO | 539666 GBENDTP3 115 539692 SEWARD 3 115 1 |  | 101 | 0.0701 | 103.49 | 532871 CIRCLE 6 230 763862 G19-054-TAP 230 1
Thermal | 00NR | 1 | 26SP | GEN-2019-055 | FROM->TO | 539666 GBENDTP3 115 539692 SEWARD 3 115 1 |  | 101 | 0.034 | 103.49 | 532871 CIRCLE 6 230 763862 G19-054-TAP 230 1
Thermal | 00NR | 1 | 26SP | GEN-2019-068 | FROM->TO | 539666 GBENDTP3 115 539692 SEWARD 3 115 1 |  | 101 | 0.0701 | 103.49 | 532871 CIRCLE 6 230 763862 G19-054-TAP 230 1
Thermal | 00NR | 1 | 26WP | GEN-2018-065 | FROM->TO | 640072 BATTLCR7 115 640115 CO.LINE7 115 1 |  | 193 | 0.08555 | 106.81 | P42:345:NPPD:BKR-MOR-3306:::::
Thermal | 00NR | 1 | 26WP | GEN-2018-065 | FROM->TO | 640072 BATTLCR7 115 640115 CO.LINE7 115 1 |  | 193 | 0.08893 | 107.19 | 640226 HOSKINS3 345 640520 ANTELOPE 3 345 1
Thermal | 00NR | 1 | 26WP | GEN-2018-065 | FROM->TO | 640072 BATTLCR7 115 640296 NORFK.N7 115 1 |  | 193 | 0.08555 | 104.08 | P42:345:NPPD:BKR-MOR-3306:::::
Thermal | 00NR | 1 | 26WP | GEN-2018-065 | FROM->TO | 640072 BATTLCR7 115 640296 NORFK.N7 115 1 |  | 193 | 0.08893 | 104.28 | 640226 HOSKINS3 345 640520 ANTELOPE 3 345 1
Thermal | 00NR | 1 | 26WP | GEN-2018-065 | FROM->TO | 640115 CO.LINE7 115 640521 ANTELOPE 7 115 1 |  | 193 | 0.08555 | 108.71 | P42:345:NPPD:BKR-MOR-3306:::::
Thermal | 00NR | 1 | 26WP | GEN-2018-065 | FROM->TO | 640115 CO.LINE7 115 640521 ANTELOPE 7 115 1 |  | 193 | 0.08893 | 109.2 | 640226 HOSKINS3 345 640520 ANTELOPE 3 345 1
Thermal | 00NR | 1 | 26WP | GEN-2018-068 | FROM->TO | 640072 BATTLCR7 115 640115 CO.LINE7 115 1 |  | 193 | 0.08555 | 106.81 | P42:345:NPPD:BKR-MOR-3306:::::
Thermal | 00NR | 1 | 26WP | GEN-2018-068 | FROM->TO | 640072 BATTLCR7 115 640115 CO.LINE7 115 1 |  | 193 | 0.08893 | 107.19 | 640226 HOSKINS3 345 640520 ANTELOPE 3 345 1
Thermal | 00NR | 1 | 26WP | GEN-2018-068 | FROM->TO | 640072 BATTLCR7 115 640296 NORFK.N7 115 1 |  | 193 | 0.08555 | 104.08 | P42:345:NPPD:BKR-MOR-3306:::::
Thermal | 00NR | 1 | 26WP | GEN-2018-068 | FROM->TO | 640072 BATTLCR7 115 640296 NORFK.N7 115 1 |  | 193 | 0.08893 | 104.28 | 640226 HOSKINS3 345 640520 ANTELOPE 3 345 1
Thermal | 00NR | 1 | 26WP | GEN-2018-068 | FROM->TO | 640115 CO.LINE7 115 640521 ANTELOPE 7 115 1 |  | 193 | 0.08555 | 108.71 | P42:345:NPPD:BKR-MOR-3306:::::
Thermal | 00NR | 1 | 26WP | GEN-2018-068 | FROM->TO | 640115 CO.LINE7 115 640521 ANTELOPE 7 115 1 |  | 193 | 0.08893 | 109.2 | 640226 HOSKINS3 345 640520 ANTELOPE 3 345 1
Thermal | 00NR | 1 | 26WP | GEN-2018-069 | FROM->TO | 659300 STANTN.T-BE7 115 661011 BEULAH27 115 1 |  | 132 | 0.03538 | 100.18 | P12:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1
Thermal | 00NR | 1 | 26WP | GEN-2018-069 | FROM->TO | 659300 STANTN.T-BE7 115 661011 BEULAH27 115 1 |  | 132 | 0.03538 | 100.18 | P21:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1
Thermal | 00NR | 1 | 26WP | GEN-2018-131 | FROM->TO | 640072 BATTLCR7 115 640115 CO.LINE7 115 1 |  | 193 | 0.08555 | 106.81 | P42:345:NPPD:BKR-MOR-3306:::::
Thermal | 00NR | 1 | 26WP | GEN-2018-131 | FROM->TO | 640072 BATTLCR7 115 640115 CO.LINE7 115 1 |  | 193 | 0.08893 | 107.19 | 640226 HOSKINS3 345 640520 ANTELOPE 3 345 1
Thermal | 00NR | 1 | 26WP | GEN-2018-131 | FROM->TO | 640072 BATTLCR7 115 640296 NORFK.N7 115 1 |  | 193 | 0.08555 | 104.08 | P42:345:NPPD:BKR-MOR-3306:::::
Thermal | 00NR | 1 | 26WP | GEN-2018-131 | FROM->TO | 640072 BATTLCR7 115 640296 NORFK.N7 115 1 |  | 193 | 0.08893 | 104.28 | 640226 HOSKINS3 345 640520 ANTELOPE 3 345 1
Thermal | 00NR | 1 | 26WP | GEN-2018-131 | FROM->TO | 640115 CO.LINE7 115 640521 ANTELOPE 7 115 1 |  | 193 | 0.08555 | 108.71 | P42:345:NPPD:BKR-MOR-3306:::::
Thermal | 00NR | 1 | 26WP | GEN-2018-131 | FROM->TO | 640115 CO.LINE7 115 640521 ANTELOPE 7 115 1 |  | 193 | 0.08893 | 109.2 | 640226 HOSKINS3 345 640520 ANTELOPE 3 345 1
Thermal | 00NR | 1 | 26WP | GEN-2018-132 | FROM->TO | 640072 BATTLCR7 115 640115 CO.LINE7 115 1 |  | 193 | 0.08555 | 106.81 | P42:345:NPPD:BKR-MOR-3306:::::
Thermal | 00NR | 1 | 26WP | GEN-2018-132 | FROM->TO | 640072 BATTLCR7 115 640115 CO.LINE7 115 1 |  | 193 | 0.08893 | 107.19 | 640226 HOSKINS3 345 640520 ANTELOPE 3 345 1
Thermal | 00NR | 1 | 26WP | GEN-2018-132 | FROM->TO | 640072 BATTLCR7 115 640296 NORFK.N7 115 1 |  | 193 | 0.08555 | 104.08 | P42:345:NPPD:BKR-MOR-3306:::::
Thermal | 00NR | 1 | 26WP | GEN-2018-132 | FROM->TO | 640072 BATTLCR7 115 640296 NORFK.N7 115 1 |  | 193 | 0.08893 | 104.28 | 640226 HOSKINS3 345 640520 ANTELOPE 3 345 1
Thermal | 00NR | 1 | 26WP | GEN-2018-132 | FROM->TO | 640115 CO.LINE7 115 640521 ANTELOPE 7 115 1 |  | 193 | 0.08555 | 108.71 | P42:345:NPPD:BKR-MOR-3306:::::
Thermal | 00NR | 1 | 26WP | GEN-2018-132 | FROM->TO | 640115 CO.LINE7 115 640521 ANTELOPE 7 115 1 |  | 193 | 0.08893 | 109.2 | 640226 HOSKINS3 345 640520 ANTELOPE 3 345 1
Thermal | 00NR | 1 | 26WP | GEN-2019-023 | FROM->TO | 659300 STANTN.T-BE7 115 661011 BEULAH27 115 1 |  | 132 | 0.03538 | 100.18 | P12:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1
Thermal | 00NR | 1 | 26WP | GEN-2019-023 | FROM->TO | 659300 STANTN.T-BE7 115 661011 BEULAH27 115 1 |  | 132 | 0.03538 | 100.18 | P21:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1
Thermal | 00NR | 1 | 23SP | GEN-2018-069 | FROM->TO | 652442 GARRISN7 115 659543 PICKCITY-RR7 115 1 |  | 121 | 0.03658 | 104.19 | P12:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1
Thermal | 00NR | 1 | 23SP | GEN-2018-069 | FROM->TO | 652442 GARRISN7 115 659543 PICKCITY-RR7 115 1 |  | 121 | 0.03658 | 104.19 | P21:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1
Thermal | 00NR | 1 | 23SP | GEN-2018-069 | FROM->TO | 659300 STANTN.T-BE7 115 659543 PICKCITY-RR7 115 1 |  | 121 | 0.03658 | 104.47 | P12:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1
Thermal | 00NR | 1 | 23SP | GEN-2018-069 | FROM->TO | 659300 STANTN.T-BE7 115 659543 PICKCITY-RR7 115 1 |  | 121 | 0.03658 | 104.47 | P21:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1
Thermal | 00NR | 1 | 23SP | GEN-2019-023 | FROM->TO | 652442 GARRISN7 115 659543 PICKCITY-RR7 115 1 |  | 121 | 0.03658 | 104.19 | P12:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1
Thermal | 00NR | 1 | 23SP | GEN-2019-023 | FROM->TO | 652442 GARRISN7 115 659543 PICKCITY-RR7 115 1 |  | 121 | 0.03658 | 104.19 | P21:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1
Thermal | 00NR | 1 | 23SP | GEN-2019-023 | FROM->TO | 659300 STANTN.T-BE7 115 659543 PICKCITY-RR7 115 1 |  | 121 | 0.03658 | 104.47 | P12:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1
Thermal | 00NR | 1 | 23SP | GEN-2019-023 | FROM->TO | 659300 STANTN.T-BE7 115 659543 PICKCITY-RR7 115 1 |  | 121 | 0.03658 | 104.47 | P21:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1
Thermal | 00NR | 1 | 26SP | GEN-2018-069 | FROM->TO | 652442 GARRISN7 115 659543 PICKCITY-RR7 115 1 |  | 121 | 0.03655 | 100.76 | P12:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1
Thermal | 00NR | 1 | 26SP | GEN-2018-069 | FROM->TO | 652442 GARRISN7 115 659543 PICKCITY-RR7 115 1 |  | 121 | 0.03655 | 100.76 | P21:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1
Thermal | 00NR | 1 | 26SP | GEN-2018-069 | FROM->TO | 659300 STANTN.T-BE7 115 659543 PICKCITY-RR7 115 1 |  | 121 | 0.03655 | 101.01 | P12:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1
Thermal | 00NR | 1 | 26SP | GEN-2018-069 | FROM->TO | 659300 STANTN.T-BE7 115 659543 PICKCITY-RR7 115 1 |  | 121 | 0.03655 | 101.01 | P21:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1
Thermal | 00NR | 1 | 26SP | GEN-2019-023 | FROM->TO | 652442 GARRISN7 115 659543 PICKCITY-RR7 115 1 |  | 121 | 0.03655 | 100.76 | P12:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1
Thermal | 00NR | 1 | 26SP | GEN-2019-023 | FROM->TO | 652442 GARRISN7 115 659543 PICKCITY-RR7 115 1 |  | 121 | 0.03655 | 100.76 | P21:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1
Thermal | 00NR | 1 | 26SP | GEN-2019-023 | FROM->TO | 659300 STANTN.T-BE7 115 659543 PICKCITY-RR7 115 1 |  | 121 | 0.03655 | 101.01 | P12:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1
Thermal | 00NR | 1 | 26SP | GEN-2019-023 | FROM->TO | 659300 STANTN.T-BE7 115 659543 PICKCITY-RR7 115 1 |  | 121 | 0.03655 | 101.01 | P21:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1
Non-Converge | 01ALL | 0 | 23SP | GEN-2018-067 | FROM->TO | Non-Converge |  |  | 0.82697 |  | P21:115:UMZB:# 2613 #: STR IN ND. OPENING OF LINE SECTION WITHOUT FAULT STR-MNU
Non-Converge | 01ALL | 0 | 23SP | GEN-2018-067 | FROM->TO | Non-Converge |  |  | 0.82697 |  | P12:115:UMZB:# 2578 #:: MNU IN ND. MONT - STRANDAHL:HV:
Non-Converge | 01ALL | 0 | 23SP | GEN-2018-067 | FROM->TO | Non-Converge |  |  | 0.82697 |  | P21:115:UMZB:# 2582 #:: MNU IN ND. OPENING OF LINE SECTION WITHOUT FAULT MNU-STR:HV:
Non-Converge | 01ALL | 0 | 23SP | GEN-2018-067 | FROM->TO | Non-Converge |  |  | 0.82697 |  | P21:115:UMZB:# 2613 #:: STR IN ND. OPENING OF LINE SECTION WITHOUT FAULT STR-MNU:HV:
Non-Converge | 01ALL | 0 | 26L | GEN-2018-067 | FROM->TO | Non-Converge |  |  | 0.82718 |  | P21:115:UMZB:# 2613 #: STR IN ND. OPENING OF LINE SECTION WITHOUT FAULT STR-MNU
Non-Converge | 01ALL | 0 | 26L | GEN-2018-067 | FROM->TO | Non-Converge |  |  | 0.82718 |  | P12:115:UMZB:# 2578 #:: MNU IN ND. MONT - STRANDAHL:HV:
Non-Converge | 01ALL | 0 | 26L | GEN-2018-067 | FROM->TO | Non-Converge |  |  | 0.82718 |  | P21:115:UMZB:# 2582 #:: MNU IN ND. OPENING OF LINE SECTION WITHOUT FAULT MNU-STR:HV:
Non-Converge | 01ALL | 0 | 26L | GEN-2018-067 | FROM->TO | Non-Converge |  |  | 0.82718 |  | P21:115:UMZB:# 2613 #:: STR IN ND. OPENING OF LINE SECTION WITHOUT FAULT STR-MNU:HV:
Non-Converge | 01ALL | 0 | 26SP | GEN-2018-067 | FROM->TO | Non-Converge |  |  | 0.82696 |  | P21:115:UMZB:# 2613 #: STR IN ND. OPENING OF LINE SECTION WITHOUT FAULT STR-MNU
Non-Converge | 01ALL | 0 | 26SP | GEN-2018-067 | FROM->TO | Non-Converge |  |  | 0.82696 |  | P12:115:UMZB:# 2578 #:: MNU IN ND. MONT - STRANDAHL:HV:
Non-Converge | 01ALL | 0 | 26SP | GEN-2018-067 | FROM->TO | Non-Converge |  |  | 0.82696 |  | P21:115:UMZB:# 2582 #:: MNU IN ND. OPENING OF LINE SECTION WITHOUT FAULT MNU-STR:HV:
Non-Converge | 01ALL | 0 | 26SP | GEN-2018-067 | FROM->TO | Non-Converge |  |  | 0.82696 |  | P21:115:UMZB:# 2613 #:: STR IN ND. OPENING OF LINE SECTION WITHOUT FAULT STR-MNU:HV:
Non-Converge | 01ALL | 0 | N/A | GEN-2018-069 | FROM->TO | None |  |  |  |  | None
Non-Converge | 01ALL | 0 | N/A | GEN-2018-070 | FROM->TO | None |  |  |  |  | None
Non-Converge | 01ALL | 0 | N/A | GEN-2018-074 | FROM->TO | None |  |  |  |  | None
Non-Converge | 01ALL | 0 | N/A | GEN-2019-019 | FROM->TO | None |  |  |  |  | None
Non-Converge | 01ALL | 0 | N/A | GEN-2019-023 | FROM->TO | None |  |  |  |  | None
Thermal | 01ALL | 1 | 26L | GEN-2018-069 | FROM->TO | 652424 BELFELD3 345 996760 BEF KU2A _1 230 1 |  | 312 | 0.57056 | 112.09 | P23:345:UMZW:# 3576 #:: BE IN ND. BREAKER FAULT (1282):HV:
Thermal | 01ALL | 1 | 26L | GEN-2019-023 | FROM->TO | 652424 BELFELD3 345 996760 BEF KU2A _1 230 1 |  | 312 | 0.57056 | 112.09 | P23:345:UMZW:# 3576 #:: BE IN ND. BREAKER FAULT (1282):HV:
Thermal | 01ALL | 1 | 26L | GEN-2018-069 | FROM->TO | 652425 BELFELD4 230 996760 BEF KU2A _1 230 1 |  | 312 | 0.57056 | 110.96 | P23:345:UMZW:# 3576 #:: BE IN ND. BREAKER FAULT (1282):HV:
Thermal | 01ALL | 1 | 26L | GEN-2018-070 | FROM->TO | 652511 GAVINS 7 115 660006 YANKTON JCT7 115 1 |  | 121 | 0.21464 | 105.99 | P42:345:UMZW:# 1932 #:: SC2 IN IA. SC2 345 KV BREAKER FAILURE:EHV:
Thermal | 01ALL | 1 | 23SP | GEN-2018-074 | FROM->TO | 652567 DENISON4 230 652583 DENISON8 69.0 1 |  | 150 | 0.22319 | 100.03 | P13:161-69:WAPA:DENISON5-DENISON8:KV3A
Thermal | 01ALL | 1 | 23SP | GEN-2018-074 | FROM->TO | 652567 DENISON4 230 652583 DENISON8 69.0 2 |  | 150 | 0.22369 | 100.24 | P13:161-69:WAPA:DENISON5-DENISON8:KV2A
Thermal | 01ALL | 1 | 23SP | GEN-2018-074 | FROM->TO | 652583 DENISON8 69.0 659912 J6BOYER_-NI8 69.0 1 |  | 117 | 0.23966 | 127.17 | P21:161:UMZW:# 1879 #: EXI IN IA. OPENING OF A LINE SECTION WO A FAULT (EXI-AT TAP)
Thermal | 01ALL | 1 | 23SP | GEN-2018-074 | FROM->TO | 652583 DENISON8 69.0 659912 J6BOYER_-NI8 69.0 1 |  | 117 | 0.23966 | 127.17 | P21:161:UMZW:# 1879 #:: EXI IN IA. OPENING OF A LINE SECTION W
Thermal | 01ALL | 1 | 23SP | GEN-2018-074 | FROM->TO | 652583 DENISON8 69.0 659912 J6BOYER_-NI8 69.0 1 |  | 117 | 0.23977 | 127.06 | P12:161:UMZ:# 5512 #: PROPER N-1 (LINE) FOR 631069-631070-1
Thermal | 01ALL | 1 | 23SP | GEN-2018-074 | FROM->TO | 652583 DENISON8 69.0 659912 J6BOYER_-NI8 69.0 1 |  | 117 | 0.23977 | 127.06 | P12:161:WAPA-CIPCO:EXIRA-CRESTON5:IA-SW
Thermal | 01ALL | 1 | 26WP | GEN-2018-074 | FROM->TO | 652583 DENISON8 69.0 659912 J6BOYER_-NI8 69.0 1 |  | 117 | 0.23921 | 120.46 | P12:161:WAPA:DENISON-EXIRA:1
Thermal | 01ALL | 1 | 26WP | GEN-2018-074 | FROM->TO | 652583 DENISON8 69.0 659912 J6BOYER_-NI8 69.0 1 |  | 117 | 0.23921 | 120.46 | P13:230-161:WAPA:DENISON4-DENISON5:KV1A
Thermal | 01ALL | 1 | 26WP | GEN-2018-074 | FROM->TO | 652583 DENISON8 69.0 659912 J6BOYER_-NI8 69.0 1 |  | 117 | 0.23921 | 120.37 | P21:161:UMZW:# 1879 #:: EXI IN IA. OPENING OF A LINE SECTION W
Thermal | 01ALL | 1 | 26WP | GEN-2018-074 | FROM->TO | 652583 DENISON8 69.0 659912 J6BOYER_-NI8 69.0 1 |  | 117 | 0.23921 | 120.37 | P21:161:UMZW:# 1879 #: EXI IN IA. OPENING OF A LINE SECTION WO A FAULT (EXI-AT TAP)
Thermal | 01ALL | 1 | 26WP | GEN-2018-074 | FROM->TO | 652583 DENISON8 69.0 659912 J6BOYER_-NI8 69.0 1 |  | 117 | 0.23932 | 120.29 | P12:161:UMZ:# 5512 #: PROPER N-1 (LINE) FOR 631069-631070-1
Thermal | 01ALL | 1 | 26WP | GEN-2018-074 | FROM->TO | 652583 DENISON8 69.0 659912 J6BOYER_-NI8 69.0 1 |  | 117 | 0.23932 | 120.29 | P12:161:WAPA-CIPCO:EXIRA-CRESTON5:IA-SW
Thermal | 01ALL | 1 | 26WP | GEN-2018-074 | FROM->TO | 652583 DENISON8 69.0 659912 J6BOYER_-NI8 69.0 1 |  | 117 | 0.24022 | 118.03 | P21:345:XEL-WAPA:SPLTRK-SIOUXCY:1(1)
Thermal | 01ALL | 1 | 26SP | GEN-2018-074 | FROM->TO | 652583 DENISON8 69.0 659912 J6BOYER_-NI8 69.0 1 |  | 117 | 0.23953 | 116.73 | P12:161:WAPA:DENISON-EXIRA:1
Thermal | 01ALL | 1 | 26SP | GEN-2018-074 | FROM->TO | 652583 DENISON8 69.0 659912 J6BOYER_-NI8 69.0 1 |  | 117 | 0.23953 | 116.73 | P13:230-161:WAPA:DENISON4-DENISON5:KV1A
Thermal | 01ALL | 1 | 26SP | GEN-2018-074 | FROM->TO | 652583 DENISON8 69.0 659912 J6BOYER_-NI8 69.0 1 |  | 117 | 0.23953 | 116.65 | P21:161:UMZW:# 1879 #: EXI IN IA. OPENING OF A LINE SECTION WO A FAULT (EXI-AT TAP)
Thermal | 01ALL | 1 | 26SP | GEN-2018-074 | FROM->TO | 652583 DENISON8 69.0 659912 J6BOYER_-NI8 69.0 1 |  | 117 | 0.23953 | 116.65 | P21:161:UMZW:# 1879 #:: EXI IN IA. OPENING OF A LINE SECTION W
Thermal | 01ALL | 1 | 26SP | GEN-2018-074 | FROM->TO | 652583 DENISON8 69.0 659912 J6BOYER_-NI8 69.0 1 |  | 117 | 0.23964 | 116.52 | P12:161:UMZ:# 5512 #: PROPER N-1 (LINE) FOR 631069-631070-1
Thermal | 01ALL | 1 | 26SP | GEN-2018-074 | FROM->TO | 652583 DENISON8 69.0 659912 J6BOYER_-NI8 69.0 1 |  | 117 | 0.23964 | 116.52 | P12:161:WAPA-CIPCO:EXIRA-CRESTON5:IA-SW
Thermal | 01ALL | 1 | 23SP | GEN-2018-074 | FROM->TO | 652583 DENISON8 69.0 659912 J6BOYER_-NI8 69.0 1 |  | 117 | 0.23966 | 116.44 | P12:161:WAPA:DENISON-EXIRA:1
Thermal | 01ALL | 1 | 23SP | GEN-2018-074 | FROM->TO | 652583 DENISON8 69.0 659912 J6BOYER_-NI8 69.0 1 |  | 117 | 0.23966 | 116.44 | P13:230-161:WAPA:DENISON4-DENISON5:KV1A
Thermal | 01ALL | 1 | 26SP | GEN-2018-074 | FROM->TO | 652583 DENISON8 69.0 659912 J6BOYER_-NI8 69.0 1 |  | 117 | 0.24053 | 113.44 | P21:345:XEL-WAPA:SPLTRK-SIOUXCY:1(1)
Thermal | 01ALL | 1 | 23SP | GEN-2018-074 | FROM->TO | 652583 DENISON8 69.0 659912 J6BOYER_-NI8 69.0 1 |  | 117 | 0.24064 | 113.13 | P21:345:XEL-WAPA:SPLTRK-SIOUXCY:1(1)
Thermal | 01ALL | 1 | 26L | GEN-2018-074 | FROM->TO | 652583 DENISON8 69.0 659912 J6BOYER_-NI8 69.0 1 |  | 117 | 0.23849 | 111.26 | P12:161:WAPA:DENISON-EXIRA:1
Thermal | 01ALL | 1 | 26L | GEN-2018-074 | FROM->TO | 652583 DENISON8 69.0 659912 J6BOYER_-NI8 69.0 1 |  | 117 | 0.23849 | 111.26 | P13:230-161:WAPA:DENISON4-DENISON5:KV1A
Thermal | 01ALL | 1 | 26L | GEN-2018-074 | FROM->TO | 652583 DENISON8 69.0 659912 J6BOYER_-NI8 69.0 1 |  | 117 | 0.2386 | 111.24 | P12:161:UMZ:# 5512 #: PROPER N-1 (LINE) FOR 631069-631070-1
Thermal | 01ALL | 1 | 26L | GEN-2018-074 | FROM->TO | 652583 DENISON8 69.0 659912 J6BOYER_-NI8 69.0 1 |  | 117 | 0.2386 | 111.24 | P12:161:WAPA-CIPCO:EXIRA-CRESTON5:IA-SW
Thermal | 01ALL | 1 | 26L | GEN-2018-074 | FROM->TO | 652583 DENISON8 69.0 659912 J6BOYER_-NI8 69.0 1 |  | 117 | 0.23849 | 111.16 | P21:161:UMZW:# 1879 #:: EXI IN IA. OPENING OF A LINE SECTION W
Thermal | 01ALL | 1 | 26L | GEN-2018-074 | FROM->TO | 652583 DENISON8 69.0 659912 J6BOYER_-NI8 69.0 1 |  | 117 | 0.23849 | 111.16 | P21:161:UMZW:# 1879 #: EXI IN IA. OPENING OF A LINE SECTION WO A FAULT (EXI-AT TAP)
Thermal | 01ALL | 1 | 26L | GEN-2018-074 | FROM->TO | 652583 DENISON8 69.0 659912 J6BOYER_-NI8 69.0 1 |  | 117 | 0.23953 | 107.94 | P21:345:XEL-WAPA:SPLTRK-SIOUXCY:1(1)
Thermal | 01ALL | 1 | 23SP | GEN-2018-074 | FROM->TO | 652583 DENISON8 69.0 659912 J6BOYER_-NI8 69.0 1 |  | 117 | 0.21016 | 101.27 | 652583 DENISON8 69.0 656267 MANNINGTAP 8 69.0 1
Thermal | 01ALL | 1 | 23SP | GEN-2018-074 | FROM->TO | 652583 DENISON8 69.0 659912 J6BOYER_-NI8 69.0 1 |  | 117 | 0.21016 | 101.27 | 656247 TEMPLTON8 69.0 656267 MANNINGTAP 8 69.0 1
Thermal | 01ALL | 1 | 23SP | GEN-2018-074 | FROM->TO | 652583 DENISON8 69.0 659912 J6BOYER_-NI8 69.0 1 |  | 117 | 0.21016 | 100.83 | 656247 TEMPLTON8 69.0 656249 TOYNE8 69.0 1
Thermal | 01ALL | 1 | 23SP | GEN-2018-070 | FROM->TO | 652626 UTICAJC7 115 660026 NAPA JCT 7 115 1 |  | 141 | 0.24359 | 117.2 | P42:345:UMZW:# 1932 #:: SC2 IN IA. SC2 345 KV BREAKER FAILURE:EHV:
Thermal | 01ALL | 1 | 26SP | GEN-2018-070 | FROM->TO | 652626 UTICAJC7 115 660026 NAPA JCT 7 115 1 |  | 141 | 0.24318 | 110.87 | P42:345:UMZW:# 1932 #:: SC2 IN IA. SC2 345 KV BREAKER FAILURE:EHV:
Thermal | 01ALL | 1 | 26WP | GEN-2018-070 | FROM->TO | 652626 UTICAJC7 115 660026 NAPA JCT 7 115 1 |  | 141 | 0.24342 | 102.59 | P42:345:UMZW:# 1932 #:: SC2 IN IA. SC2 345 KV BREAKER FAILURE:EHV:
Thermal | 01ALL | 1 | 23SP | GEN-2018-067 | FROM->TO | 655940 MONT -MW7 115 655941 STRNDAHL-MW7 115 1 |  | 115 | 0.82688 | 173.44 | P12:115:UMZB:# 7139 #:: ZAH IN ND. ZAHL - TYRONE:HV:
Thermal | 01ALL | 1 | 23SP | GEN-2018-067 | FROM->TO | 655940 MONT -MW7 115 655941 STRNDAHL-MW7 115 1 |  | 115 | 0.82688 | 173.29 | P12:115:UMZ:# 5692 #: PROPER N-1 (LINE) FOR 655931-655955-1
Thermal | 01ALL | 1 | 26SP | GEN-2018-067 | FROM->TO | 655940 MONT -MW7 115 655941 STRNDAHL-MW7 115 1 |  | 115 | 0.82688 | 172.54 | P12:115:UMZB:# 7139 #:: ZAH IN ND. ZAHL - TYRONE:HV:
Thermal | 01ALL | 1 | 26SP | GEN-2018-067 | FROM->TO | 655940 MONT -MW7 115 655941 STRNDAHL-MW7 115 1 |  | 115 | 0.82688 | 172.39 | P12:115:UMZ:# 5692 #: PROPER N-1 (LINE) FOR 655931-655955-1
Thermal | 01ALL | 1 | 26WP | GEN-2018-067 | FROM->TO | 655940 MONT -MW7 115 655941 STRNDAHL-MW7 115 1 |  | 163 | 0.82684 | 117.41 | P12:115:UMZB:# 7139 #:: ZAH IN ND. ZAHL - TYRONE:HV:
Thermal | 01ALL | 1 | 26WP | GEN-2018-067 | FROM->TO | 655940 MONT -MW7 115 655941 STRNDAHL-MW7 115 1 |  | 163 | 0.82684 | 117.31 | P12:115:UMZ:# 5692 #: PROPER N-1 (LINE) FOR 655931-655955-1
Thermal | 01ALL | 1 | 26L | GEN-2018-067 | FROM->TO | 655940 MONT -MW7 115 655941 STRNDAHL-MW7 115 1 |  | 115 | 0.8271 | 165.32 | P12:115:UMZB:# 7139 #:: ZAH IN ND. ZAHL - TYRONE:HV:
Thermal | 01ALL | 1 | 26L | GEN-2018-067 | FROM->TO | 655940 MONT -MW7 115 655941 STRNDAHL-MW7 115 1 |  | 115 | 0.8271 | 165.17 | P12:115:UMZ:# 5692 #: PROPER N-1 (LINE) FOR 655931-655955-1
Thermal | 01ALL | 1 | 26L | GEN-2018-067 | FROM->TO | 655940 MONT -MW7 115 655941 STRNDAHL-MW7 115 1 |  | 115 | 0.55694 | 118.67 | P21:115:UMZB:# 2628 #: BTE IN ND. OPENING OF LINE SECTION WITHOUT FAULT BTE-STR
Thermal | 01ALL | 1 | 26L | GEN-2018-067 | FROM->TO | 655940 MONT -MW7 115 655941 STRNDAHL-MW7 115 1 |  | 115 | 0.55694 | 118.67 | P12:115:UMZB:# 2612 #:: STR IN ND. STRANDAHL - BARR BUTTE:HV:
Thermal | 01ALL | 1 | 26L | GEN-2018-067 | FROM->TO | 655940 MONT -MW7 115 655941 STRNDAHL-MW7 115 1 |  | 115 | 0.55694 | 118.67 | P21:115:UMZB:# 2628 #:: BTE IN ND. OPENING OF LINE SECTION WITHOUT FAULT BTE-STR:HV:
Thermal | 01ALL | 1 | 26L | GEN-2018-067 | FROM->TO | 655940 MONT -MW7 115 655941 STRNDAHL-MW7 115 1 |  | 115 | 0.55694 | 118.67 | P21:115:UMZB:# 2614 #:: STR IN ND. OPENING OF LINE SECTION WITHOUT FAULT STR-BTE:HV:
Thermal | 01ALL | 1 | 23SP | GEN-2018-067 | FROM->TO | 655940 MONT -MW7 115 655941 STRNDAHL-MW7 115 1 |  | 115 | 0.55748 | 118.3 | P21:115:UMZB:# 2538 #:: SLN IN ND. OPENING OF LINE SECTION WITHOUT FAULT SLN-SBT:HV:
Thermal | 01ALL | 1 | 23SP | GEN-2018-067 | FROM->TO | 655940 MONT -MW7 115 655941 STRNDAHL-MW7 115 1 |  | 115 | 0.55748 | 118.3 | P12:115:UMZB:# 2535 #:: SLN IN ND. PIONEER - STATELINE:HV:
Thermal | 01ALL | 1 | 26L | GEN-2018-067 | FROM->TO | 655940 MONT -MW7 115 655941 STRNDAHL-MW7 115 1 |  | 115 | 0.55694 | 118.22 | P21:115:UMZB:# 2813 #:: GRN IN ND. OPENING OF LINE SECTION WITHOUT FAULT:HV:
Thermal | 01ALL | 1 | 26L | GEN-2018-067 | FROM->TO | 655940 MONT -MW7 115 655941 STRNDAHL-MW7 115 1 |  | 115 | 0.55694 | 118.22 | P21:115:UMZB:# 2813 #: GRN IN ND. OPENING OF LINE SECTION WITHOUT FAULT
Thermal | 01ALL | 1 | 26L | GEN-2018-067 | FROM->TO | 655940 MONT -MW7 115 655941 STRNDAHL-MW7 115 1 |  | 115 | 0.55694 | 118.22 | P21:115:UMZB:# 2627 #:: BTE IN ND. OPENING OF LINE SECTION WITHOUT FAULT BTE-GRN:HV:
Thermal | 01ALL | 1 | 26L | GEN-2018-067 | FROM->TO | 655940 MONT -MW7 115 655941 STRNDAHL-MW7 115 1 |  | 115 | 0.55694 | 118.22 | P12:115:UMZB:# 2625 #:: BTE IN ND. BARR BUTTE - GRENORA:HV:
Thermal | 01ALL | 1 | 26SP | GEN-2018-067 | FROM->TO | 655940 MONT -MW7 115 655941 STRNDAHL-MW7 115 1 |  | 115 | 0.55748 | 117.36 | P21:115:UMZB:# 2538 #:: SLN IN ND. OPENING OF LINE SECTION WITHOUT FAULT SLN-SBT:HV:
Thermal | 01ALL | 1 | 26SP | GEN-2018-067 | FROM->TO | 655940 MONT -MW7 115 655941 STRNDAHL-MW7 115 1 |  | 115 | 0.55748 | 117.36 | P12:115:UMZB:# 2535 #:: SLN IN ND. PIONEER - STATELINE:HV:
Thermal | 01ALL | 1 | 26L | GEN-2018-067 | FROM->TO | 655940 MONT -MW7 115 655941 STRNDAHL-MW7 115 1 |  | 115 | 0.63708 | 112.95 | P12:115:UMZB:# 7142 #:: TYO IN ND. TYRONE - EAST FORK:HV:
Thermal | 01ALL | 1 | 23SP | GEN-2018-067 | FROM->TO | 655940 MONT -MW7 115 655941 STRNDAHL-MW7 115 1 |  | 115 | 0.63735 | 110.52 | P12:115:UMZB:# 7142 #:: TYO IN ND. TYRONE - EAST FORK:HV:
Thermal | 01ALL | 1 | 26L | GEN-2018-067 | FROM->TO | 655940 MONT -MW7 115 655941 STRNDAHL-MW7 115 1 |  | 115 | 0.55694 | 109.21 | P21:115:UMZB:# 2815 #:: GRN IN ND. GRENORA TO SNAKE BUTTE TAP LINE:HV:
Thermal | 01ALL | 1 | 26L | GEN-2018-067 | FROM->TO | 655940 MONT -MW7 115 655941 STRNDAHL-MW7 115 1 |  | 115 | 0.55694 | 108.86 | P12:115:UMZ:# 5800 #: PROPER N-1 (LINE) FOR 659145-655778-1
Thermal | 01ALL | 1 | 26L | GEN-2018-067 | FROM->TO | 655940 MONT -MW7 115 655941 STRNDAHL-MW7 115 1 |  | 115 | 0.55694 | 108.86 | P12:115:UMZB:# 2810 #:: SBT IN ND. LOSS OF SNAKE BUTTE TAP:HV:
Thermal | 01ALL | 1 | 26L | GEN-2018-067 | FROM->TO | 655940 MONT -MW7 115 655941 STRNDAHL-MW7 115 1 |  | 115 | 0.55694 | 106.54 | P21:115:UMZB:# 2538 #:: SLN IN ND. OPENING OF LINE SECTION WITHOUT FAULT SLN-SBT:HV:
Thermal | 01ALL | 1 | 26L | GEN-2018-067 | FROM->TO | 655940 MONT -MW7 115 655941 STRNDAHL-MW7 115 1 |  | 115 | 0.55694 | 106.54 | P12:115:UMZB:# 2535 #:: SLN IN ND. PIONEER - STATELINE:HV:
Thermal | 01ALL | 1 | 26SP | GEN-2018-067 | FROM->TO | 655940 MONT -MW7 115 655941 STRNDAHL-MW7 115 1 |  | 115 | 0.63735 | 105.1 | P12:115:UMZB:# 7142 #:: TYO IN ND. TYRONE - EAST FORK:HV:
Thermal | 01ALL | 1 | 23SP | GEN-2018-067 | FROM->TO | 655940 MONT -MW7 115 655941 STRNDAHL-MW7 115 1 |  | 115 | 0.55748 | 101.51 | P21:115:UMZB:# 2628 #: BTE IN ND. OPENING OF LINE SECTION WITHOUT FAULT BTE-STR
Thermal | 01ALL | 1 | 23SP | GEN-2018-067 | FROM->TO | 655940 MONT -MW7 115 655941 STRNDAHL-MW7 115 1 |  | 115 | 0.55748 | 101.51 | P21:115:UMZB:# 2628 #:: BTE IN ND. OPENING OF LINE SECTION WITHOUT FAULT BTE-STR:HV:
Thermal | 01ALL | 1 | 23SP | GEN-2018-067 | FROM->TO | 655940 MONT -MW7 115 655941 STRNDAHL-MW7 115 1 |  | 115 | 0.55748 | 101.51 | P21:115:UMZB:# 2614 #:: STR IN ND. OPENING OF LINE SECTION WITHOUT FAULT STR-BTE:HV:
Thermal | 01ALL | 1 | 23SP | GEN-2018-067 | FROM->TO | 655940 MONT -MW7 115 655941 STRNDAHL-MW7 115 1 |  | 115 | 0.55748 | 101.51 | P12:115:UMZB:# 2612 #:: STR IN ND. STRANDAHL - BARR BUTTE:HV:
Thermal | 01ALL | 1 | 23SP | GEN-2018-067 | FROM->TO | 655940 MONT -MW7 115 655941 STRNDAHL-MW7 115 1 |  | 115 | 0.55748 | 101.14 | P21:115:UMZB:# 2813 #: GRN IN ND. OPENING OF LINE SECTION WITHOUT FAULT
Thermal | 01ALL | 1 | 23SP | GEN-2018-067 | FROM->TO | 655940 MONT -MW7 115 655941 STRNDAHL-MW7 115 1 |  | 115 | 0.55748 | 101.14 | P12:115:UMZB:# 2625 #:: BTE IN ND. BARR BUTTE - GRENORA:HV:
Thermal | 01ALL | 1 | 23SP | GEN-2018-067 | FROM->TO | 655940 MONT -MW7 115 655941 STRNDAHL-MW7 115 1 |  | 115 | 0.55748 | 101.14 | P21:115:UMZB:# 2813 #:: GRN IN ND. OPENING OF LINE SECTION WITHOUT FAULT:HV:
Thermal | 01ALL | 1 | 23SP | GEN-2018-067 | FROM->TO | 655940 MONT -MW7 115 655941 STRNDAHL-MW7 115 1 |  | 115 | 0.55748 | 101.14 | P21:115:UMZB:# 2627 #:: BTE IN ND. OPENING OF LINE SECTION WITHOUT FAULT BTE-GRN:HV:
Thermal | 01ALL | 1 | 26SP | GEN-2018-067 | FROM->TO | 655940 MONT -MW7 115 655941 STRNDAHL-MW7 115 1 |  | 115 | 0.55748 | 100.9 | P21:115:UMZB:# 2614 #:: STR IN ND. OPENING OF LINE SECTION WITHOUT FAULT STR-BTE:HV:
Thermal | 01ALL | 1 | 26SP | GEN-2018-067 | FROM->TO | 655940 MONT -MW7 115 655941 STRNDAHL-MW7 115 1 |  | 115 | 0.55748 | 100.9 | P21:115:UMZB:# 2628 #: BTE IN ND. OPENING OF LINE SECTION WITHOUT FAULT BTE-STR
Thermal | 01ALL | 1 | 26SP | GEN-2018-067 | FROM->TO | 655940 MONT -MW7 115 655941 STRNDAHL-MW7 115 1 |  | 115 | 0.55748 | 100.9 | P12:115:UMZB:# 2612 #:: STR IN ND. STRANDAHL - BARR BUTTE:HV:
Thermal | 01ALL | 1 | 26SP | GEN-2018-067 | FROM->TO | 655940 MONT -MW7 115 655941 STRNDAHL-MW7 115 1 |  | 115 | 0.55748 | 100.9 | P21:115:UMZB:# 2628 #:: BTE IN ND. OPENING OF LINE SECTION WITHOUT FAULT BTE-STR:HV:
Thermal | 01ALL | 1 | 26SP | GEN-2018-067 | FROM->TO | 655940 MONT -MW7 115 655941 STRNDAHL-MW7 115 1 |  | 115 | 0.55748 | 100.42 | P21:115:UMZB:# 2813 #:: GRN IN ND. OPENING OF LINE SECTION WITHOUT FAULT:HV:
Thermal | 01ALL | 1 | 26SP | GEN-2018-067 | FROM->TO | 655940 MONT -MW7 115 655941 STRNDAHL-MW7 115 1 |  | 115 | 0.55748 | 100.42 | P21:115:UMZB:# 2813 #: GRN IN ND. OPENING OF LINE SECTION WITHOUT FAULT
Thermal | 01ALL | 1 | 26SP | GEN-2018-067 | FROM->TO | 655940 MONT -MW7 115 655941 STRNDAHL-MW7 115 1 |  | 115 | 0.55748 | 100.42 | P21:115:UMZB:# 2627 #:: BTE IN ND. OPENING OF LINE SECTION WITHOUT FAULT BTE-GRN:HV:
Thermal | 01ALL | 1 | 26SP | GEN-2018-067 | FROM->TO | 655940 MONT -MW7 115 655941 STRNDAHL-MW7 115 1 |  | 115 | 0.55748 | 100.42 | P12:115:UMZB:# 2625 #:: BTE IN ND. BARR BUTTE - GRENORA:HV:
Thermal | 01ALL | 1 | 23SP | GEN-2018-067 | FROM->TO | 655940 MONT -MW7 115 655941 STRNDAHL-MW7 115 1 |  | 115 | 0.48261 | 100.02 | P21:115:UMZB:# 2583 #: MNU IN ND. OPENING OF LINE SECTION WITHOUT FAULTMNU-SLN
Thermal | 01ALL | 1 | 23SP | GEN-2018-067 | FROM->TO | 655940 MONT -MW7 115 655941 STRNDAHL-MW7 115 1 |  | 115 | 0.48261 | 100.02 | P12:115:UMZB:# 2536 #:: SLN IN ND. STATELINE - MONT:HV:
Thermal | 01ALL | 1 | 23SP | GEN-2018-067 | FROM->TO | 655940 MONT -MW7 115 655941 STRNDAHL-MW7 115 1 |  | 115 | 0.48261 | 100.02 | P21:115:UMZB:# 2583 #:: MNU IN ND. OPENING OF LINE SECTION WITHOUT FAULTMNU-SLN:HV:
Thermal | 01ALL | 1 | 23SP | GEN-2018-067 | FROM->TO | 655940 MONT -MW7 115 655941 STRNDAHL-MW7 115 1 |  | 115 | 0.48261 | 100.02 | P21:115:UMZB:# 2540 #:: SLN IN ND. OPENING OF LINE SECTION WITHOUT FAULT SLN-MNU:HV:
Thermal | 01ALL | 1 | 23SP | GEN-2018-074 | FROM->TO | 659854 K335AMAI-NI8 69.0 659897 K338WTCT-NI8 69.0 1 | 34.8 |  | 0.05689 | 100.58 | System Intact
Thermal | 01ALL | 1 | 23SP | GEN-2018-074 | FROM->TO | 659854 K335AMAI-NI8 69.0 659912 J6BOYER_-NI8 69.0 1 | 34.8 |  | 0.05013 | 105.93 | System Intact
Thermal | 01ALL | 1 | 26SP | GEN-2018-074 | FROM->TO | 659854 K335AMAI-NI8 69.0 659912 J6BOYER_-NI8 69.0 1 | 34.8 |  | 0.05007 | 105.35 | System Intact
Thermal | 01ALL | 1 | 26L | GEN-2018-070 | FROM->TO | 660006 YANKTON JCT7 115 660026 NAPA JCT 7 115 1 |  | 120 | 0.24743 | 100.08 | P42:345:UMZW:# 1932 #:: SC2 IN IA. SC2 345 KV BREAKER FAILURE:EHV:
Thermal | 01ALL | 1 | 26L | GEN-2019-023 | FROM->TO | 652424 BELFELD3 345 996760 BEF KU2A _1 230 1 |  | 312 | 0.5704 | 110.96 | P23:345:UMZW:# 3576 #:: BE IN ND. BREAKER FAULT (1282):HV:
Non-Converge | 01NR | 0 | N/A | GEN-2018-067 | FROM->TO | None |  |  |  |  | None
Non-Converge | 01NR | 0 | N/A | GEN-2018-069 | FROM->TO | None |  |  |  |  | None
Non-Converge | 01NR | 0 | N/A | GEN-2018-070 | FROM->TO | None |  |  |  |  | None
Non-Converge | 01NR | 0 | N/A | GEN-2018-074 | FROM->TO | None |  |  |  |  | None
Non-Converge | 01NR | 0 | N/A | GEN-2019-019 | FROM->TO | None |  |  |  |  | None
Non-Converge | 01NR | 0 | N/A | GEN-2019-023 | FROM->TO | None |  |  |  |  | None
Thermal | 01NR | 1 | 26L | GEN-2018-069 | FROM->TO | 602006 SHEYNNE4 230 652435 FARGO 4 230 1 |  | 342 | 0.05873 | 115.19 | P21:345:OTP:AUTO-SINGLE:BUFFALO3:JAMESTN3:1
Thermal | 01NR | 1 | 26L | GEN-2018-069 | FROM->TO | 602006 SHEYNNE4 230 652435 FARGO 4 230 1 |  | 342 | 0.05873 | 115.19 | P12:345:OTP:AUTO-SINGLE:BUFFALO3:JAMESTN3:1
Thermal | 01NR | 1 | 26L | GEN-2018-069 | FROM->TO | 602006 SHEYNNE4 230 652435 FARGO 4 230 1 |  | 342 | 0.05874 | 115.19 | P23:345:OTP:JAMESTN3:3145:V2020
Thermal | 01NR | 1 | 26L | GEN-2018-069 | FROM->TO | 602006 SHEYNNE4 230 652435 FARGO 4 230 1 |  | 342 | 0.05874 | 115.19 | P23:345:OTP:JAMESTN3:3135:V2020
Thermal | 01NR | 1 | 26L | GEN-2019-023 | FROM->TO | 602006 SHEYNNE4 230 652435 FARGO 4 230 1 |  | 342 | 0.05873 | 115.19 | P21:345:OTP:AUTO-SINGLE:BUFFALO3:JAMESTN3:1
Thermal | 01NR | 1 | 26L | GEN-2019-023 | FROM->TO | 602006 SHEYNNE4 230 652435 FARGO 4 230 1 |  | 342 | 0.05873 | 115.19 | P12:345:OTP:AUTO-SINGLE:BUFFALO3:JAMESTN3:1
Thermal | 01NR | 1 | 26L | GEN-2019-023 | FROM->TO | 602006 SHEYNNE4 230 652435 FARGO 4 230 1 |  | 342 | 0.05874 | 115.19 | P23:345:OTP:JAMESTN3:3145:V2020
Thermal | 01NR | 1 | 26L | GEN-2019-023 | FROM->TO | 602006 SHEYNNE4 230 652435 FARGO 4 230 1 |  | 342 | 0.05874 | 115.19 | P23:345:OTP:JAMESTN3:3135:V2020
Thermal | 01NR | 1 | 26L | GEN-2018-069 | FROM->TO | 602006 SHEYNNE4 230 652435 FARGO 4 230 1 |  | 342 | 0.05871 | 115.11 | P23:345:OTP:BUFFALO3:3655:V2016
Thermal | 01NR | 1 | 26L | GEN-2019-023 | FROM->TO | 602006 SHEYNNE4 230 652435 FARGO 4 230 1 |  | 342 | 0.05871 | 115.11 | P23:345:OTP:BUFFALO3:3655:V2016
Thermal | 01NR | 1 | 26L | GEN-2018-069 | FROM->TO | 602006 SHEYNNE4 230 652435 FARGO 4 230 1 |  | 342 | 0.0586 | 114.69 | P12:345:MPC:JAMESTOWN-BISON:JAMESTN3:BISON 3
Thermal | 01NR | 1 | 26L | GEN-2019-023 | FROM->TO | 602006 SHEYNNE4 230 652435 FARGO 4 230 1 |  | 342 | 0.0586 | 114.69 | P12:345:MPC:JAMESTOWN-BISON:JAMESTN3:BISON 3
Thermal | 01NR | 1 | 26L | GEN-2018-069 | FROM->TO | 602006 SHEYNNE4 230 652435 FARGO 4 230 1 |  | 342 | 0.05892 | 113.34 | P23:345:OTP:JAMESTN3:3125:R2020
Thermal | 01NR | 1 | 26L | GEN-2019-023 | FROM->TO | 602006 SHEYNNE4 230 652435 FARGO 4 230 1 |  | 342 | 0.05892 | 113.34 | P23:345:OTP:JAMESTN3:3125:R2020
Thermal | 01NR | 1 | 26L | GEN-2018-069 | FROM->TO | 602006 SHEYNNE4 230 652435 FARGO 4 230 1 |  | 342 | 0.05885 | 108 | P23:345:OTP:JAMESTN3:3125:V2020
Thermal | 01NR | 1 | 26L | GEN-2019-023 | FROM->TO | 602006 SHEYNNE4 230 652435 FARGO 4 230 1 |  | 342 | 0.05885 | 108 | P23:345:OTP:JAMESTN3:3125:V2020
Thermal | 01NR | 1 | 26L | GEN-2018-069 | FROM->TO | 602006 SHEYNNE4 230 652435 FARGO 4 230 1 |  | 342 | 0.05885 | 107.98 | P23:345:OTP:JAMESTN3:3115:V2020
Thermal | 01NR | 1 | 26L | GEN-2019-023 | FROM->TO | 602006 SHEYNNE4 230 652435 FARGO 4 230 1 |  | 342 | 0.05885 | 107.98 | P23:345:OTP:JAMESTN3:3115:V2020
Thermal | 01NR | 1 | 26L | GEN-2018-069 | FROM->TO | 602006 SHEYNNE4 230 652435 FARGO 4 230 1 |  | 342 | 0.05885 | 107.95 | P12:345:OTP:AUTO-SINGLE:JAMESTN3:CENTER3:1
Thermal | 01NR | 1 | 26L | GEN-2018-069 | FROM->TO | 602006 SHEYNNE4 230 652435 FARGO 4 230 1 |  | 342 | 0.05885 | 107.95 | P21:345:OTP:AUTO-SINGLE:JAMESTN3:CENTER3:1
Thermal | 01NR | 1 | 26L | GEN-2018-069 | FROM->TO | 602006 SHEYNNE4 230 652435 FARGO 4 230 1 |  | 342 | 0.05886 | 107.95 | P23:345:OTP:CENTER 3:3245
Thermal | 01NR | 1 | 26L | GEN-2018-069 | FROM->TO | 602006 SHEYNNE4 230 652435 FARGO 4 230 1 |  | 342 | 0.05886 | 107.95 | P23:345:OTP:CENTER 3:3235
Thermal | 01NR | 1 | 26L | GEN-2019-023 | FROM->TO | 602006 SHEYNNE4 230 652435 FARGO 4 230 1 |  | 342 | 0.05885 | 107.95 | P12:345:OTP:AUTO-SINGLE:JAMESTN3:CENTER3:1
Thermal | 01NR | 1 | 26L | GEN-2019-023 | FROM->TO | 602006 SHEYNNE4 230 652435 FARGO 4 230 1 |  | 342 | 0.05885 | 107.95 | P21:345:OTP:AUTO-SINGLE:JAMESTN3:CENTER3:1
Thermal | 01NR | 1 | 26L | GEN-2019-023 | FROM->TO | 602006 SHEYNNE4 230 652435 FARGO 4 230 1 |  | 342 | 0.05886 | 107.95 | P23:345:OTP:CENTER 3:3245
Thermal | 01NR | 1 | 26L | GEN-2019-023 | FROM->TO | 602006 SHEYNNE4 230 652435 FARGO 4 230 1 |  | 342 | 0.05886 | 107.95 | P23:345:OTP:CENTER 3:3235
Non-Converge | 02ALL | 0 | 23SP | GEN-2018-065 | FROM->TO | Non-Converge |  |  | 0.80589 |  | P42:345:NPPD:BKR-MOR-3306:::::
Non-Converge | 02ALL | 0 | 23SP | GEN-2018-065 | FROM->TO | Non-Converge |  |  | 0.80589 |  | 640226 HOSKINS3 345 640520 ANTELOPE 3 345 1
Non-Converge | 02ALL | 0 | 26SP | GEN-2018-065 | FROM->TO | Non-Converge |  |  | 0.80488 |  | P42:345:NPPD:BKR-MOR-3306:::::
Non-Converge | 02ALL | 0 | 26SP | GEN-2018-065 | FROM->TO | Non-Converge |  |  | 0.80488 |  | 640226 HOSKINS3 345 640520 ANTELOPE 3 345 1
Non-Converge | 02ALL | 0 | 26WP | GEN-2018-065 | FROM->TO | Non-Converge |  |  | 0.80283 |  | P42:345:NPPD:BKR-MOR-3306:::::
Non-Converge | 02ALL | 0 | 26WP | GEN-2018-065 | FROM->TO | Non-Converge |  |  | 0.80283 |  | 640226 HOSKINS3 345 640520 ANTELOPE 3 345 1
Non-Converge | 02ALL | 0 | 23SP | GEN-2018-068 | FROM->TO | Non-Converge |  |  | 0.80589 |  | P42:345:NPPD:BKR-MOR-3306:::::
Non-Converge | 02ALL | 0 | 23SP | GEN-2018-068 | FROM->TO | Non-Converge |  |  | 0.80589 |  | 640226 HOSKINS3 345 640520 ANTELOPE 3 345 1
Non-Converge | 02ALL | 0 | 26SP | GEN-2018-068 | FROM->TO | Non-Converge |  |  | 0.80488 |  | P42:345:NPPD:BKR-MOR-3306:::::
Non-Converge | 02ALL | 0 | 26SP | GEN-2018-068 | FROM->TO | Non-Converge |  |  | 0.80488 |  | 640226 HOSKINS3 345 640520 ANTELOPE 3 345 1
Non-Converge | 02ALL | 0 | 26WP | GEN-2018-068 | FROM->TO | Non-Converge |  |  | 0.80283 |  | P42:345:NPPD:BKR-MOR-3306:::::
Non-Converge | 02ALL | 0 | 26WP | GEN-2018-068 | FROM->TO | Non-Converge |  |  | 0.80283 |  | 640226 HOSKINS3 345 640520 ANTELOPE 3 345 1
Non-Converge | 02ALL | 0 | 26SP | GEN-2018-083 | FROM->TO | Non-Converge |  |  | 0.53288 |  | P42:345:NPPD:BKR-MOR-3306:::::
Non-Converge | 02ALL | 0 | 23SP | GEN-2018-090 | FROM->TO | Non-Converge |  |  | 0.04434 |  | P42:345:NPPD:BKR-MOR-3306:::::
Non-Converge | 02ALL | 0 | 26WP | GEN-2018-090 | FROM->TO | Non-Converge |  |  | 0.04203 |  | P42:345:NPPD:BKR-MOR-3306:::::
Non-Converge | 02ALL | 0 | 26SP | GEN-2018-125 | FROM->TO | Non-Converge |  |  | 0.04396 |  | P42:345:NPPD:BKR-MOR-3306:::::
Non-Converge | 02ALL | 0 | 23SP | GEN-2018-131 | FROM->TO | Non-Converge |  |  | 0.80589 |  | P42:345:NPPD:BKR-MOR-3306:::::
Non-Converge | 02ALL | 0 | 23SP | GEN-2018-131 | FROM->TO | Non-Converge |  |  | 0.80589 |  | 640226 HOSKINS3 345 640520 ANTELOPE 3 345 1
Non-Converge | 02ALL | 0 | 26SP | GEN-2018-131 | FROM->TO | Non-Converge |  |  | 0.80488 |  | P42:345:NPPD:BKR-MOR-3306:::::
Non-Converge | 02ALL | 0 | 26SP | GEN-2018-131 | FROM->TO | Non-Converge |  |  | 0.80488 |  | 640226 HOSKINS3 345 640520 ANTELOPE 3 345 1
Non-Converge | 02ALL | 0 | 26WP | GEN-2018-131 | FROM->TO | Non-Converge |  |  | 0.80283 |  | P42:345:NPPD:BKR-MOR-3306:::::
Non-Converge | 02ALL | 0 | 26WP | GEN-2018-131 | FROM->TO | Non-Converge |  |  | 0.80283 |  | 640226 HOSKINS3 345 640520 ANTELOPE 3 345 1
Non-Converge | 02ALL | 0 | 23SP | GEN-2018-132 | FROM->TO | Non-Converge |  |  | 0.80589 |  | P42:345:NPPD:BKR-MOR-3306:::::
Non-Converge | 02ALL | 0 | 23SP | GEN-2018-132 | FROM->TO | Non-Converge |  |  | 0.80589 |  | 640226 HOSKINS3 345 640520 ANTELOPE 3 345 1
Non-Converge | 02ALL | 0 | 26SP | GEN-2018-132 | FROM->TO | Non-Converge |  |  | 0.80488 |  | P42:345:NPPD:BKR-MOR-3306:::::
Non-Converge | 02ALL | 0 | 26SP | GEN-2018-132 | FROM->TO | Non-Converge |  |  | 0.80488 |  | 640226 HOSKINS3 345 640520 ANTELOPE 3 345 1
Non-Converge | 02ALL | 0 | 26WP | GEN-2018-132 | FROM->TO | Non-Converge |  |  | 0.80283 |  | P42:345:NPPD:BKR-MOR-3306:::::
Non-Converge | 02ALL | 0 | 26WP | GEN-2018-132 | FROM->TO | Non-Converge |  |  | 0.80283 |  | 640226 HOSKINS3 345 640520 ANTELOPE 3 345 1
Non-Converge | 02ALL | 0 | 23SP | GEN-2019-029 | FROM->TO | Non-Converge |  |  | 0.62122 |  | 640252 KEYSTON3 345 763666 G19-029 TAP 345 1
Non-Converge | 02ALL | 0 | 26SP | GEN-2019-029 | FROM->TO | Non-Converge |  |  | 0.03013 |  | P42:345:NPPD:BKR-MOR-3306:::::
Non-Converge | 02ALL | 0 | 26SP | GEN-2019-029 | FROM->TO | Non-Converge |  |  | 0.62844 |  | 640252 KEYSTON3 345 763666 G19-029 TAP 345 1
Non-Converge | 02ALL | 0 | 26WP | GEN-2019-029 | FROM->TO | Non-Converge |  |  | 0.62605 |  | 640252 KEYSTON3 345 763666 G19-029 TAP 345 1
Non-Converge | 02ALL | 0 | 23SP | GEN-2019-033 | FROM->TO | Non-Converge |  |  | 0.62122 |  | 640252 KEYSTON3 345 763666 G19-029 TAP 345 1
Non-Converge | 02ALL | 0 | 26SP | GEN-2019-033 | FROM->TO | Non-Converge |  |  | 0.03013 |  | P42:345:NPPD:BKR-MOR-3306:::::
Non-Converge | 02ALL | 0 | 26SP | GEN-2019-033 | FROM->TO | Non-Converge |  |  | 0.62844 |  | 640252 KEYSTON3 345 763666 G19-029 TAP 345 1
Non-Converge | 02ALL | 0 | 26WP | GEN-2019-033 | FROM->TO | Non-Converge |  |  | 0.62605 |  | 640252 KEYSTON3 345 763666 G19-029 TAP 345 1
Non-Converge | 02ALL | 0 | 26SP | GEN-2019-039 | FROM->TO | Non-Converge |  |  | 0.16912 |  | P42:345:NPPD:BKR-MOR-3306:::::
Non-Converge | 02ALL | 0 | 26SP | GEN-2019-041 | FROM->TO | Non-Converge |  |  | 0.06386 |  | P42:345:NPPD:BKR-MOR-3306:::::
Non-Converge | 02ALL | 0 | 26SP | GEN-2019-069 | FROM->TO | Non-Converge |  |  | 0.53288 |  | P42:345:NPPD:BKR-MOR-3306:::::
Non-Converge | 02ALL | 0 | 26SP | GEN-2019-070 | FROM->TO | Non-Converge |  |  | 0.53288 |  | P42:345:NPPD:BKR-MOR-3306:::::
Non-Converge | 02ALL | 0 | 26SP | GEN-2019-073 | FROM->TO | Non-Converge |  |  | 0.53288 |  | P42:345:NPPD:BKR-MOR-3306:::::
Non-Converge | 02ALL | 0 | N/A | GEN-2019-009 | FROM->TO | None |  |  |  |  | None
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2018-065 | FROM->TO | 640054 ALBION 7 115 640318 PETRSBG7 115 1 |  | 137 | 0.22947 | 136.13 | 640226 HOSKINS3 345 640520 ANTELOPE 3 345 1
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2018-068 | FROM->TO | 640054 ALBION 7 115 640318 PETRSBG7 115 1 |  | 137 | 0.22947 | 136.13 | 640226 HOSKINS3 345 640520 ANTELOPE 3 345 1
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2018-131 | FROM->TO | 640054 ALBION 7 115 640318 PETRSBG7 115 1 |  | 137 | 0.22947 | 136.13 | 640226 HOSKINS3 345 640520 ANTELOPE 3 345 1
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2018-132 | FROM->TO | 640054 ALBION 7 115 640318 PETRSBG7 115 1 |  | 137 | 0.22947 | 136.13 | 640226 HOSKINS3 345 640520 ANTELOPE 3 345 1
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2018-065 | FROM->TO | 640054 ALBION 7 115 640318 PETRSBG7 115 1 |  | 137 | 0.23498 | 133.76 | P42:345:NPPD:BKR-MOR-3306:::::
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2018-068 | FROM->TO | 640054 ALBION 7 115 640318 PETRSBG7 115 1 |  | 137 | 0.23498 | 133.76 | P42:345:NPPD:BKR-MOR-3306:::::
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2018-131 | FROM->TO | 640054 ALBION 7 115 640318 PETRSBG7 115 1 |  | 137 | 0.23498 | 133.76 | P42:345:NPPD:BKR-MOR-3306:::::
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2018-132 | FROM->TO | 640054 ALBION 7 115 640318 PETRSBG7 115 1 |  | 137 | 0.23498 | 133.76 | P42:345:NPPD:BKR-MOR-3306:::::
Thermal | 02ALL | 1 | 02ALL-23SP | GEN-2018-065 | FROM->TO | 640054 ALBION 7 115 640318 PETRSBG7 115 1 |  | 137 | 0.23224 | 117.44 | 640226 HOSKINS3 345 640520 ANTELOPE 3 345 1
Thermal | 02ALL | 1 | 02ALL-23SP | GEN-2018-068 | FROM->TO | 640054 ALBION 7 115 640318 PETRSBG7 115 1 |  | 137 | 0.23224 | 117.44 | 640226 HOSKINS3 345 640520 ANTELOPE 3 345 1
Thermal | 02ALL | 1 | 02ALL-23SP | GEN-2018-131 | FROM->TO | 640054 ALBION 7 115 640318 PETRSBG7 115 1 |  | 137 | 0.23224 | 117.44 | 640226 HOSKINS3 345 640520 ANTELOPE 3 345 1
Thermal | 02ALL | 1 | 02ALL-23SP | GEN-2018-132 | FROM->TO | 640054 ALBION 7 115 640318 PETRSBG7 115 1 |  | 137 | 0.23224 | 117.44 | 640226 HOSKINS3 345 640520 ANTELOPE 3 345 1
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2018-065 | FROM->TO | 640054 ALBION 7 115 640318 PETRSBG7 115 1 |  | 137 | 0.23087 | 116.86 | 640226 HOSKINS3 345 640520 ANTELOPE 3 345 1
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2018-068 | FROM->TO | 640054 ALBION 7 115 640318 PETRSBG7 115 1 |  | 137 | 0.23087 | 116.86 | 640226 HOSKINS3 345 640520 ANTELOPE 3 345 1
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2018-131 | FROM->TO | 640054 ALBION 7 115 640318 PETRSBG7 115 1 |  | 137 | 0.23087 | 116.86 | 640226 HOSKINS3 345 640520 ANTELOPE 3 345 1
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2018-132 | FROM->TO | 640054 ALBION 7 115 640318 PETRSBG7 115 1 |  | 137 | 0.23087 | 116.86 | 640226 HOSKINS3 345 640520 ANTELOPE 3 345 1
Thermal | 02ALL | 1 | 02ALL-23SP | GEN-2018-065 | FROM->TO | 640054 ALBION 7 115 640318 PETRSBG7 115 1 |  | 137 | 0.23793 | 113.1 | P42:345:NPPD:BKR-MOR-3306:::::
Thermal | 02ALL | 1 | 02ALL-23SP | GEN-2018-068 | FROM->TO | 640054 ALBION 7 115 640318 PETRSBG7 115 1 |  | 137 | 0.23793 | 113.1 | P42:345:NPPD:BKR-MOR-3306:::::
Thermal | 02ALL | 1 | 02ALL-23SP | GEN-2018-131 | FROM->TO | 640054 ALBION 7 115 640318 PETRSBG7 115 1 |  | 137 | 0.23793 | 113.1 | P42:345:NPPD:BKR-MOR-3306:::::
Thermal | 02ALL | 1 | 02ALL-23SP | GEN-2018-132 | FROM->TO | 640054 ALBION 7 115 640318 PETRSBG7 115 1 |  | 137 | 0.23793 | 113.1 | P42:345:NPPD:BKR-MOR-3306:::::
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2018-065 | FROM->TO | 640054 ALBION 7 115 640318 PETRSBG7 115 1 |  | 137 | 0.23644 | 112.26 | P42:345:NPPD:BKR-MOR-3306:::::
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2018-068 | FROM->TO | 640054 ALBION 7 115 640318 PETRSBG7 115 1 |  | 137 | 0.23644 | 112.26 | P42:345:NPPD:BKR-MOR-3306:::::
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2018-131 | FROM->TO | 640054 ALBION 7 115 640318 PETRSBG7 115 1 |  | 137 | 0.23644 | 112.26 | P42:345:NPPD:BKR-MOR-3306:::::
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2018-132 | FROM->TO | 640054 ALBION 7 115 640318 PETRSBG7 115 1 |  | 137 | 0.23644 | 112.26 | P42:345:NPPD:BKR-MOR-3306:::::
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2018-065 | FROM->TO | 640072 BATTLCR7 115 640115 CO.LINE7 115 1 |  | 193 | 0.38145 | 162.63 | P42:345:NPPD:BKR-MOR-3306:::::
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2018-068 | FROM->TO | 640072 BATTLCR7 115 640115 CO.LINE7 115 1 |  | 193 | 0.38145 | 162.63 | P42:345:NPPD:BKR-MOR-3306:::::
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2018-131 | FROM->TO | 640072 BATTLCR7 115 640115 CO.LINE7 115 1 |  | 193 | 0.38145 | 162.63 | P42:345:NPPD:BKR-MOR-3306:::::
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2018-132 | FROM->TO | 640072 BATTLCR7 115 640115 CO.LINE7 115 1 |  | 193 | 0.38145 | 162.63 | P42:345:NPPD:BKR-MOR-3306:::::
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2018-065 | FROM->TO | 640072 BATTLCR7 115 640115 CO.LINE7 115 1 |  | 193 | 0.38817 | 160.13 | 640226 HOSKINS3 345 640520 ANTELOPE 3 345 1
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2018-068 | FROM->TO | 640072 BATTLCR7 115 640115 CO.LINE7 115 1 |  | 193 | 0.38817 | 160.13 | 640226 HOSKINS3 345 640520 ANTELOPE 3 345 1
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2018-131 | FROM->TO | 640072 BATTLCR7 115 640115 CO.LINE7 115 1 |  | 193 | 0.38817 | 160.13 | 640226 HOSKINS3 345 640520 ANTELOPE 3 345 1
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2018-132 | FROM->TO | 640072 BATTLCR7 115 640115 CO.LINE7 115 1 |  | 193 | 0.38817 | 160.13 | 640226 HOSKINS3 345 640520 ANTELOPE 3 345 1
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2018-065 | FROM->TO | 640072 BATTLCR7 115 640115 CO.LINE7 115 1 |  | 193 | 0.38267 | 132.88 | P42:345:NPPD:BKR-MOR-3306:::::
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2018-068 | FROM->TO | 640072 BATTLCR7 115 640115 CO.LINE7 115 1 |  | 193 | 0.38267 | 132.88 | P42:345:NPPD:BKR-MOR-3306:::::
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2018-131 | FROM->TO | 640072 BATTLCR7 115 640115 CO.LINE7 115 1 |  | 193 | 0.38267 | 132.88 | P42:345:NPPD:BKR-MOR-3306:::::
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2018-132 | FROM->TO | 640072 BATTLCR7 115 640115 CO.LINE7 115 1 |  | 193 | 0.38267 | 132.88 | P42:345:NPPD:BKR-MOR-3306:::::
Thermal | 02ALL | 1 | 02ALL-23SP | GEN-2018-065 | FROM->TO | 640072 BATTLCR7 115 640115 CO.LINE7 115 1 |  | 193 | 0.3848 | 132.25 | P42:345:NPPD:BKR-MOR-3306:::::
Thermal | 02ALL | 1 | 02ALL-23SP | GEN-2018-068 | FROM->TO | 640072 BATTLCR7 115 640115 CO.LINE7 115 1 |  | 193 | 0.3848 | 132.25 | P42:345:NPPD:BKR-MOR-3306:::::
Thermal | 02ALL | 1 | 02ALL-23SP | GEN-2018-131 | FROM->TO | 640072 BATTLCR7 115 640115 CO.LINE7 115 1 |  | 193 | 0.3848 | 132.25 | P42:345:NPPD:BKR-MOR-3306:::::
Thermal | 02ALL | 1 | 02ALL-23SP | GEN-2018-132 | FROM->TO | 640072 BATTLCR7 115 640115 CO.LINE7 115 1 |  | 193 | 0.3848 | 132.25 | P42:345:NPPD:BKR-MOR-3306:::::
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2018-065 | FROM->TO | 640072 BATTLCR7 115 640115 CO.LINE7 115 1 |  | 193 | 0.38946 | 128.24 | 640226 HOSKINS3 345 640520 ANTELOPE 3 345 1
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2018-068 | FROM->TO | 640072 BATTLCR7 115 640115 CO.LINE7 115 1 |  | 193 | 0.38946 | 128.24 | 640226 HOSKINS3 345 640520 ANTELOPE 3 345 1
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2018-131 | FROM->TO | 640072 BATTLCR7 115 640115 CO.LINE7 115 1 |  | 193 | 0.38946 | 128.24 | 640226 HOSKINS3 345 640520 ANTELOPE 3 345 1
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2018-132 | FROM->TO | 640072 BATTLCR7 115 640115 CO.LINE7 115 1 |  | 193 | 0.38946 | 128.24 | 640226 HOSKINS3 345 640520 ANTELOPE 3 345 1
Thermal | 02ALL | 1 | 02ALL-23SP | GEN-2018-065 | FROM->TO | 640072 BATTLCR7 115 640115 CO.LINE7 115 1 |  | 193 | 0.39165 | 127.9 | 640226 HOSKINS3 345 640520 ANTELOPE 3 345 1
Thermal | 02ALL | 1 | 02ALL-23SP | GEN-2018-068 | FROM->TO | 640072 BATTLCR7 115 640115 CO.LINE7 115 1 |  | 193 | 0.39165 | 127.9 | 640226 HOSKINS3 345 640520 ANTELOPE 3 345 1
Thermal | 02ALL | 1 | 02ALL-23SP | GEN-2018-131 | FROM->TO | 640072 BATTLCR7 115 640115 CO.LINE7 115 1 |  | 193 | 0.39165 | 127.9 | 640226 HOSKINS3 345 640520 ANTELOPE 3 345 1
Thermal | 02ALL | 1 | 02ALL-23SP | GEN-2018-132 | FROM->TO | 640072 BATTLCR7 115 640115 CO.LINE7 115 1 |  | 193 | 0.39165 | 127.9 | 640226 HOSKINS3 345 640520 ANTELOPE 3 345 1
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2018-065 | FROM->TO | 640072 BATTLCR7 115 640296 NORFK.N7 115 1 |  | 193 | 0.38145 | 158.68 | P42:345:NPPD:BKR-MOR-3306:::::
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2018-068 | FROM->TO | 640072 BATTLCR7 115 640296 NORFK.N7 115 1 |  | 193 | 0.38145 | 158.68 | P42:345:NPPD:BKR-MOR-3306:::::
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2018-131 | FROM->TO | 640072 BATTLCR7 115 640296 NORFK.N7 115 1 |  | 193 | 0.38145 | 158.68 | P42:345:NPPD:BKR-MOR-3306:::::
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2018-132 | FROM->TO | 640072 BATTLCR7 115 640296 NORFK.N7 115 1 |  | 193 | 0.38145 | 158.68 | P42:345:NPPD:BKR-MOR-3306:::::
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2018-065 | FROM->TO | 640072 BATTLCR7 115 640296 NORFK.N7 115 1 |  | 193 | 0.38817 | 156.19 | 640226 HOSKINS3 345 640520 ANTELOPE 3 345 1
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2018-068 | FROM->TO | 640072 BATTLCR7 115 640296 NORFK.N7 115 1 |  | 193 | 0.38817 | 156.19 | 640226 HOSKINS3 345 640520 ANTELOPE 3 345 1
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2018-131 | FROM->TO | 640072 BATTLCR7 115 640296 NORFK.N7 115 1 |  | 193 | 0.38817 | 156.19 | 640226 HOSKINS3 345 640520 ANTELOPE 3 345 1
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2018-132 | FROM->TO | 640072 BATTLCR7 115 640296 NORFK.N7 115 1 |  | 193 | 0.38817 | 156.19 | 640226 HOSKINS3 345 640520 ANTELOPE 3 345 1
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2018-065 | FROM->TO | 640072 BATTLCR7 115 640296 NORFK.N7 115 1 |  | 193 | 0.38267 | 119.77 | P42:345:NPPD:BKR-MOR-3306:::::
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2018-068 | FROM->TO | 640072 BATTLCR7 115 640296 NORFK.N7 115 1 |  | 193 | 0.38267 | 119.77 | P42:345:NPPD:BKR-MOR-3306:::::
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2018-131 | FROM->TO | 640072 BATTLCR7 115 640296 NORFK.N7 115 1 |  | 193 | 0.38267 | 119.77 | P42:345:NPPD:BKR-MOR-3306:::::
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2018-132 | FROM->TO | 640072 BATTLCR7 115 640296 NORFK.N7 115 1 |  | 193 | 0.38267 | 119.77 | P42:345:NPPD:BKR-MOR-3306:::::
Thermal | 02ALL | 1 | 02ALL-23SP | GEN-2018-065 | FROM->TO | 640072 BATTLCR7 115 640296 NORFK.N7 115 1 |  | 193 | 0.3848 | 119.28 | P42:345:NPPD:BKR-MOR-3306:::::
Thermal | 02ALL | 1 | 02ALL-23SP | GEN-2018-068 | FROM->TO | 640072 BATTLCR7 115 640296 NORFK.N7 115 1 |  | 193 | 0.3848 | 119.28 | P42:345:NPPD:BKR-MOR-3306:::::
Thermal | 02ALL | 1 | 02ALL-23SP | GEN-2018-131 | FROM->TO | 640072 BATTLCR7 115 640296 NORFK.N7 115 1 |  | 193 | 0.3848 | 119.28 | P42:345:NPPD:BKR-MOR-3306:::::
Thermal | 02ALL | 1 | 02ALL-23SP | GEN-2018-132 | FROM->TO | 640072 BATTLCR7 115 640296 NORFK.N7 115 1 |  | 193 | 0.3848 | 119.28 | P42:345:NPPD:BKR-MOR-3306:::::
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2018-065 | FROM->TO | 640072 BATTLCR7 115 640296 NORFK.N7 115 1 |  | 193 | 0.38946 | 115.15 | 640226 HOSKINS3 345 640520 ANTELOPE 3 345 1
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2018-068 | FROM->TO | 640072 BATTLCR7 115 640296 NORFK.N7 115 1 |  | 193 | 0.38946 | 115.15 | 640226 HOSKINS3 345 640520 ANTELOPE 3 345 1
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2018-131 | FROM->TO | 640072 BATTLCR7 115 640296 NORFK.N7 115 1 |  | 193 | 0.38946 | 115.15 | 640226 HOSKINS3 345 640520 ANTELOPE 3 345 1
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2018-132 | FROM->TO | 640072 BATTLCR7 115 640296 NORFK.N7 115 1 |  | 193 | 0.38946 | 115.15 | 640226 HOSKINS3 345 640520 ANTELOPE 3 345 1
Thermal | 02ALL | 1 | 02ALL-23SP | GEN-2018-065 | FROM->TO | 640072 BATTLCR7 115 640296 NORFK.N7 115 1 |  | 193 | 0.39165 | 114.94 | 640226 HOSKINS3 345 640520 ANTELOPE 3 345 1
Thermal | 02ALL | 1 | 02ALL-23SP | GEN-2018-068 | FROM->TO | 640072 BATTLCR7 115 640296 NORFK.N7 115 1 |  | 193 | 0.39165 | 114.94 | 640226 HOSKINS3 345 640520 ANTELOPE 3 345 1
Thermal | 02ALL | 1 | 02ALL-23SP | GEN-2018-131 | FROM->TO | 640072 BATTLCR7 115 640296 NORFK.N7 115 1 |  | 193 | 0.39165 | 114.94 | 640226 HOSKINS3 345 640520 ANTELOPE 3 345 1
Thermal | 02ALL | 1 | 02ALL-23SP | GEN-2018-132 | FROM->TO | 640072 BATTLCR7 115 640296 NORFK.N7 115 1 |  | 193 | 0.39165 | 114.94 | 640226 HOSKINS3 345 640520 ANTELOPE 3 345 1
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2018-065 | FROM->TO | 640084 BLMFLD 7 115 652511 GAVINS 7 115 1 |  | 144 | 0.20056 | 120.49 | P42:345:NPPD:BKR-MOR-3306:::::
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2018-068 | FROM->TO | 640084 BLMFLD 7 115 652511 GAVINS 7 115 1 |  | 144 | 0.20056 | 120.49 | P42:345:NPPD:BKR-MOR-3306:::::
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2018-131 | FROM->TO | 640084 BLMFLD 7 115 652511 GAVINS 7 115 1 |  | 144 | 0.20056 | 120.49 | P42:345:NPPD:BKR-MOR-3306:::::
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2018-132 | FROM->TO | 640084 BLMFLD 7 115 652511 GAVINS 7 115 1 |  | 144 | 0.20056 | 120.49 | P42:345:NPPD:BKR-MOR-3306:::::
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2018-065 | FROM->TO | 640084 BLMFLD 7 115 652511 GAVINS 7 115 1 |  | 144 | 0.20068 | 120.24 | 640226 HOSKINS3 345 640520 ANTELOPE 3 345 1
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2018-068 | FROM->TO | 640084 BLMFLD 7 115 652511 GAVINS 7 115 1 |  | 144 | 0.20068 | 120.24 | 640226 HOSKINS3 345 640520 ANTELOPE 3 345 1
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2018-131 | FROM->TO | 640084 BLMFLD 7 115 652511 GAVINS 7 115 1 |  | 144 | 0.20068 | 120.24 | 640226 HOSKINS3 345 640520 ANTELOPE 3 345 1
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2018-132 | FROM->TO | 640084 BLMFLD 7 115 652511 GAVINS 7 115 1 |  | 144 | 0.20068 | 120.24 | 640226 HOSKINS3 345 640520 ANTELOPE 3 345 1
Thermal | 02ALL | 1 | 02ALL-26L | GEN-2018-065 | FROM->TO | 640084 BLMFLD 7 115 652511 GAVINS 7 115 1 |  | 144 | 0.19705 | 113.53 | 640226 HOSKINS3 345 640520 ANTELOPE 3 345 1
Thermal | 02ALL | 1 | 02ALL-26L | GEN-2018-068 | FROM->TO | 640084 BLMFLD 7 115 652511 GAVINS 7 115 1 |  | 144 | 0.19705 | 113.53 | 640226 HOSKINS3 345 640520 ANTELOPE 3 345 1
Thermal | 02ALL | 1 | 02ALL-26L | GEN-2018-065 | FROM->TO | 640084 BLMFLD 7 115 652511 GAVINS 7 115 1 |  | 144 | 0.19694 | 113.45 | P42:345:NPPD:BKR-MOR-3306:::::
Thermal | 02ALL | 1 | 02ALL-26L | GEN-2018-068 | FROM->TO | 640084 BLMFLD 7 115 652511 GAVINS 7 115 1 |  | 144 | 0.19694 | 113.45 | P42:345:NPPD:BKR-MOR-3306:::::
Thermal | 02ALL | 1 | 02ALL-23SP | GEN-2018-065 | FROM->TO | 640113 CLRWATR7 115 640293 NELIGH 7 115 1 |  | 120 | 0.1717 | 108.27 | 640226 HOSKINS3 345 640520 ANTELOPE 3 345 1
Thermal | 02ALL | 1 | 02ALL-23SP | GEN-2018-068 | FROM->TO | 640113 CLRWATR7 115 640293 NELIGH 7 115 1 |  | 120 | 0.1717 | 108.27 | 640226 HOSKINS3 345 640520 ANTELOPE 3 345 1
Thermal | 02ALL | 1 | 02ALL-23SP | GEN-2018-131 | FROM->TO | 640113 CLRWATR7 115 640293 NELIGH 7 115 1 |  | 120 | 0.1717 | 108.27 | 640226 HOSKINS3 345 640520 ANTELOPE 3 345 1
Thermal | 02ALL | 1 | 02ALL-23SP | GEN-2018-132 | FROM->TO | 640113 CLRWATR7 115 640293 NELIGH 7 115 1 |  | 120 | 0.1717 | 108.27 | 640226 HOSKINS3 345 640520 ANTELOPE 3 345 1
Thermal | 02ALL | 1 | 02ALL-23SP | GEN-2018-065 | FROM->TO | 640113 CLRWATR7 115 640293 NELIGH 7 115 1 |  | 120 | 0.17298 | 107.19 | P42:345:NPPD:BKR-MOR-3306:::::
Thermal | 02ALL | 1 | 02ALL-23SP | GEN-2018-068 | FROM->TO | 640113 CLRWATR7 115 640293 NELIGH 7 115 1 |  | 120 | 0.17298 | 107.19 | P42:345:NPPD:BKR-MOR-3306:::::
Thermal | 02ALL | 1 | 02ALL-23SP | GEN-2018-131 | FROM->TO | 640113 CLRWATR7 115 640293 NELIGH 7 115 1 |  | 120 | 0.17298 | 107.19 | P42:345:NPPD:BKR-MOR-3306:::::
Thermal | 02ALL | 1 | 02ALL-23SP | GEN-2018-132 | FROM->TO | 640113 CLRWATR7 115 640293 NELIGH 7 115 1 |  | 120 | 0.17298 | 107.19 | P42:345:NPPD:BKR-MOR-3306:::::
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2018-065 | FROM->TO | 640113 CLRWATR7 115 640293 NELIGH 7 115 1 |  | 120 | 0.17602 | 105.38 | 640226 HOSKINS3 345 640520 ANTELOPE 3 345 1
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2018-068 | FROM->TO | 640113 CLRWATR7 115 640293 NELIGH 7 115 1 |  | 120 | 0.17602 | 105.38 | 640226 HOSKINS3 345 640520 ANTELOPE 3 345 1
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2018-131 | FROM->TO | 640113 CLRWATR7 115 640293 NELIGH 7 115 1 |  | 120 | 0.17602 | 105.38 | 640226 HOSKINS3 345 640520 ANTELOPE 3 345 1
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2018-132 | FROM->TO | 640113 CLRWATR7 115 640293 NELIGH 7 115 1 |  | 120 | 0.17602 | 105.38 | 640226 HOSKINS3 345 640520 ANTELOPE 3 345 1
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2018-065 | FROM->TO | 640113 CLRWATR7 115 640293 NELIGH 7 115 1 |  | 120 | 0.17735 | 104.87 | P42:345:NPPD:BKR-MOR-3306:::::
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2018-068 | FROM->TO | 640113 CLRWATR7 115 640293 NELIGH 7 115 1 |  | 120 | 0.17735 | 104.87 | P42:345:NPPD:BKR-MOR-3306:::::
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2018-131 | FROM->TO | 640113 CLRWATR7 115 640293 NELIGH 7 115 1 |  | 120 | 0.17735 | 104.87 | P42:345:NPPD:BKR-MOR-3306:::::
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2018-132 | FROM->TO | 640113 CLRWATR7 115 640293 NELIGH 7 115 1 |  | 120 | 0.17735 | 104.87 | P42:345:NPPD:BKR-MOR-3306:::::
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2018-065 | FROM->TO | 640113 CLRWATR7 115 640293 NELIGH 7 115 1 |  | 120 | 0.17614 | 104.71 | 640226 HOSKINS3 345 640520 ANTELOPE 3 345 1
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2018-068 | FROM->TO | 640113 CLRWATR7 115 640293 NELIGH 7 115 1 |  | 120 | 0.17614 | 104.71 | 640226 HOSKINS3 345 640520 ANTELOPE 3 345 1
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2018-131 | FROM->TO | 640113 CLRWATR7 115 640293 NELIGH 7 115 1 |  | 120 | 0.17614 | 104.71 | 640226 HOSKINS3 345 640520 ANTELOPE 3 345 1
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2018-132 | FROM->TO | 640113 CLRWATR7 115 640293 NELIGH 7 115 1 |  | 120 | 0.17614 | 104.71 | 640226 HOSKINS3 345 640520 ANTELOPE 3 345 1
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2018-065 | FROM->TO | 640113 CLRWATR7 115 640293 NELIGH 7 115 1 |  | 120 | 0.17748 | 103.51 | P42:345:NPPD:BKR-MOR-3306:::::
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2018-068 | FROM->TO | 640113 CLRWATR7 115 640293 NELIGH 7 115 1 |  | 120 | 0.17748 | 103.51 | P42:345:NPPD:BKR-MOR-3306:::::
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2018-131 | FROM->TO | 640113 CLRWATR7 115 640293 NELIGH 7 115 1 |  | 120 | 0.17748 | 103.51 | P42:345:NPPD:BKR-MOR-3306:::::
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2018-132 | FROM->TO | 640113 CLRWATR7 115 640293 NELIGH 7 115 1 |  | 120 | 0.17748 | 103.51 | P42:345:NPPD:BKR-MOR-3306:::::
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2018-065 | FROM->TO | 640113 CLRWATR7 115 640305 ONEILL 7 115 1 |  | 120 | 0.17602 | 103.49 | 640226 HOSKINS3 345 640520 ANTELOPE 3 345 1
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2018-068 | FROM->TO | 640113 CLRWATR7 115 640305 ONEILL 7 115 1 |  | 120 | 0.17602 | 103.49 | 640226 HOSKINS3 345 640520 ANTELOPE 3 345 1
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2018-131 | FROM->TO | 640113 CLRWATR7 115 640305 ONEILL 7 115 1 |  | 120 | 0.17602 | 103.49 | 640226 HOSKINS3 345 640520 ANTELOPE 3 345 1
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2018-132 | FROM->TO | 640113 CLRWATR7 115 640305 ONEILL 7 115 1 |  | 120 | 0.17602 | 103.49 | 640226 HOSKINS3 345 640520 ANTELOPE 3 345 1
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2018-065 | FROM->TO | 640113 CLRWATR7 115 640305 ONEILL 7 115 1 |  | 120 | 0.17735 | 102.98 | P42:345:NPPD:BKR-MOR-3306:::::
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2018-068 | FROM->TO | 640113 CLRWATR7 115 640305 ONEILL 7 115 1 |  | 120 | 0.17735 | 102.98 | P42:345:NPPD:BKR-MOR-3306:::::
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2018-131 | FROM->TO | 640113 CLRWATR7 115 640305 ONEILL 7 115 1 |  | 120 | 0.17735 | 102.98 | P42:345:NPPD:BKR-MOR-3306:::::
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2018-132 | FROM->TO | 640113 CLRWATR7 115 640305 ONEILL 7 115 1 |  | 120 | 0.17735 | 102.98 | P42:345:NPPD:BKR-MOR-3306:::::
Thermal | 02ALL | 1 | 02ALL-23SP | GEN-2018-065 | FROM->TO | 640113 CLRWATR7 115 640305 ONEILL 7 115 1 |  | 120 | 0.1717 | 101.66 | 640226 HOSKINS3 345 640520 ANTELOPE 3 345 1
Thermal | 02ALL | 1 | 02ALL-23SP | GEN-2018-068 | FROM->TO | 640113 CLRWATR7 115 640305 ONEILL 7 115 1 |  | 120 | 0.1717 | 101.66 | 640226 HOSKINS3 345 640520 ANTELOPE 3 345 1
Thermal | 02ALL | 1 | 02ALL-23SP | GEN-2018-131 | FROM->TO | 640113 CLRWATR7 115 640305 ONEILL 7 115 1 |  | 120 | 0.1717 | 101.66 | 640226 HOSKINS3 345 640520 ANTELOPE 3 345 1
Thermal | 02ALL | 1 | 02ALL-23SP | GEN-2018-132 | FROM->TO | 640113 CLRWATR7 115 640305 ONEILL 7 115 1 |  | 120 | 0.1717 | 101.66 | 640226 HOSKINS3 345 640520 ANTELOPE 3 345 1
Thermal | 02ALL | 1 | 02ALL-23SP | GEN-2018-065 | FROM->TO | 640113 CLRWATR7 115 640305 ONEILL 7 115 1 |  | 120 | 0.17298 | 100.59 | P42:345:NPPD:BKR-MOR-3306:::::
Thermal | 02ALL | 1 | 02ALL-23SP | GEN-2018-068 | FROM->TO | 640113 CLRWATR7 115 640305 ONEILL 7 115 1 |  | 120 | 0.17298 | 100.59 | P42:345:NPPD:BKR-MOR-3306:::::
Thermal | 02ALL | 1 | 02ALL-23SP | GEN-2018-131 | FROM->TO | 640113 CLRWATR7 115 640305 ONEILL 7 115 1 |  | 120 | 0.17298 | 100.59 | P42:345:NPPD:BKR-MOR-3306:::::
Thermal | 02ALL | 1 | 02ALL-23SP | GEN-2018-132 | FROM->TO | 640113 CLRWATR7 115 640305 ONEILL 7 115 1 |  | 120 | 0.17298 | 100.59 | P42:345:NPPD:BKR-MOR-3306:::::
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2018-065 | FROM->TO | 640115 CO.LINE7 115 640521 ANTELOPE 7 115 1 |  | 193 | 0.38145 | 162.88 | P42:345:NPPD:BKR-MOR-3306:::::
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2018-068 | FROM->TO | 640115 CO.LINE7 115 640521 ANTELOPE 7 115 1 |  | 193 | 0.38145 | 162.88 | P42:345:NPPD:BKR-MOR-3306:::::
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2018-131 | FROM->TO | 640115 CO.LINE7 115 640521 ANTELOPE 7 115 1 |  | 193 | 0.38145 | 162.88 | P42:345:NPPD:BKR-MOR-3306:::::
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2018-132 | FROM->TO | 640115 CO.LINE7 115 640521 ANTELOPE 7 115 1 |  | 193 | 0.38145 | 162.88 | P42:345:NPPD:BKR-MOR-3306:::::
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2018-065 | FROM->TO | 640115 CO.LINE7 115 640521 ANTELOPE 7 115 1 |  | 193 | 0.38817 | 160.39 | 640226 HOSKINS3 345 640520 ANTELOPE 3 345 1
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2018-068 | FROM->TO | 640115 CO.LINE7 115 640521 ANTELOPE 7 115 1 |  | 193 | 0.38817 | 160.39 | 640226 HOSKINS3 345 640520 ANTELOPE 3 345 1
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2018-131 | FROM->TO | 640115 CO.LINE7 115 640521 ANTELOPE 7 115 1 |  | 193 | 0.38817 | 160.39 | 640226 HOSKINS3 345 640520 ANTELOPE 3 345 1
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2018-132 | FROM->TO | 640115 CO.LINE7 115 640521 ANTELOPE 7 115 1 |  | 193 | 0.38817 | 160.39 | 640226 HOSKINS3 345 640520 ANTELOPE 3 345 1
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2018-065 | FROM->TO | 640115 CO.LINE7 115 640521 ANTELOPE 7 115 1 |  | 193 | 0.38267 | 135.42 | P42:345:NPPD:BKR-MOR-3306:::::
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2018-068 | FROM->TO | 640115 CO.LINE7 115 640521 ANTELOPE 7 115 1 |  | 193 | 0.38267 | 135.42 | P42:345:NPPD:BKR-MOR-3306:::::
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2018-131 | FROM->TO | 640115 CO.LINE7 115 640521 ANTELOPE 7 115 1 |  | 193 | 0.38267 | 135.42 | P42:345:NPPD:BKR-MOR-3306:::::
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2018-132 | FROM->TO | 640115 CO.LINE7 115 640521 ANTELOPE 7 115 1 |  | 193 | 0.38267 | 135.42 | P42:345:NPPD:BKR-MOR-3306:::::
Thermal | 02ALL | 1 | 02ALL-23SP | GEN-2018-065 | FROM->TO | 640115 CO.LINE7 115 640521 ANTELOPE 7 115 1 |  | 193 | 0.3848 | 134.79 | P42:345:NPPD:BKR-MOR-3306:::::
Thermal | 02ALL | 1 | 02ALL-23SP | GEN-2018-068 | FROM->TO | 640115 CO.LINE7 115 640521 ANTELOPE 7 115 1 |  | 193 | 0.3848 | 134.79 | P42:345:NPPD:BKR-MOR-3306:::::
Thermal | 02ALL | 1 | 02ALL-23SP | GEN-2018-131 | FROM->TO | 640115 CO.LINE7 115 640521 ANTELOPE 7 115 1 |  | 193 | 0.3848 | 134.79 | P42:345:NPPD:BKR-MOR-3306:::::
Thermal | 02ALL | 1 | 02ALL-23SP | GEN-2018-132 | FROM->TO | 640115 CO.LINE7 115 640521 ANTELOPE 7 115 1 |  | 193 | 0.3848 | 134.79 | P42:345:NPPD:BKR-MOR-3306:::::
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2018-065 | FROM->TO | 640115 CO.LINE7 115 640521 ANTELOPE 7 115 1 |  | 193 | 0.38946 | 130.78 | 640226 HOSKINS3 345 640520 ANTELOPE 3 345 1
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2018-068 | FROM->TO | 640115 CO.LINE7 115 640521 ANTELOPE 7 115 1 |  | 193 | 0.38946 | 130.78 | 640226 HOSKINS3 345 640520 ANTELOPE 3 345 1
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2018-131 | FROM->TO | 640115 CO.LINE7 115 640521 ANTELOPE 7 115 1 |  | 193 | 0.38946 | 130.78 | 640226 HOSKINS3 345 640520 ANTELOPE 3 345 1
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2018-132 | FROM->TO | 640115 CO.LINE7 115 640521 ANTELOPE 7 115 1 |  | 193 | 0.38946 | 130.78 | 640226 HOSKINS3 345 640520 ANTELOPE 3 345 1
Thermal | 02ALL | 1 | 02ALL-23SP | GEN-2018-065 | FROM->TO | 640115 CO.LINE7 115 640521 ANTELOPE 7 115 1 |  | 193 | 0.39165 | 130.44 | 640226 HOSKINS3 345 640520 ANTELOPE 3 345 1
Thermal | 02ALL | 1 | 02ALL-23SP | GEN-2018-068 | FROM->TO | 640115 CO.LINE7 115 640521 ANTELOPE 7 115 1 |  | 193 | 0.39165 | 130.44 | 640226 HOSKINS3 345 640520 ANTELOPE 3 345 1
Thermal | 02ALL | 1 | 02ALL-23SP | GEN-2018-131 | FROM->TO | 640115 CO.LINE7 115 640521 ANTELOPE 7 115 1 |  | 193 | 0.39165 | 130.44 | 640226 HOSKINS3 345 640520 ANTELOPE 3 345 1
Thermal | 02ALL | 1 | 02ALL-23SP | GEN-2018-132 | FROM->TO | 640115 CO.LINE7 115 640521 ANTELOPE 7 115 1 |  | 193 | 0.39165 | 130.44 | 640226 HOSKINS3 345 640520 ANTELOPE 3 345 1
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2019-039 | FROM->TO | 640124 COL.SE 7 115 763718 G19-039-TAP 115 1 |  | 140 | 1 | 122.29 | 640328 RISNGCY7 115 763718 G19-039-TAP 115 1
Thermal | 02ALL | 1 | 02ALL-23SP | GEN-2019-039 | FROM->TO | 640124 COL.SE 7 115 763718 G19-039-TAP 115 1 |  | 140 | 1 | 122.26 | 640328 RISNGCY7 115 763718 G19-039-TAP 115 1
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2019-039 | FROM->TO | 640124 COL.SE 7 115 763718 G19-039-TAP 115 1 |  | 140 | 1 | 122.25 | 640328 RISNGCY7 115 763718 G19-039-TAP 115 1
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2018-065 | FROM->TO | 640149 CREITON7 115 640521 ANTELOPE 7 115 1 |  | 143 | 0.20323 | 126.8 | P42:345:NPPD:BKR-MOR-3306:::::
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2018-068 | FROM->TO | 640149 CREITON7 115 640521 ANTELOPE 7 115 1 |  | 143 | 0.20323 | 126.8 | P42:345:NPPD:BKR-MOR-3306:::::
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2018-131 | FROM->TO | 640149 CREITON7 115 640521 ANTELOPE 7 115 1 |  | 143 | 0.20323 | 126.8 | P42:345:NPPD:BKR-MOR-3306:::::
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2018-132 | FROM->TO | 640149 CREITON7 115 640521 ANTELOPE 7 115 1 |  | 143 | 0.20323 | 126.8 | P42:345:NPPD:BKR-MOR-3306:::::
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2018-065 | FROM->TO | 640149 CREITON7 115 640521 ANTELOPE 7 115 1 |  | 143 | 0.20335 | 126.52 | 640226 HOSKINS3 345 640520 ANTELOPE 3 345 1
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2018-068 | FROM->TO | 640149 CREITON7 115 640521 ANTELOPE 7 115 1 |  | 143 | 0.20335 | 126.52 | 640226 HOSKINS3 345 640520 ANTELOPE 3 345 1
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2018-131 | FROM->TO | 640149 CREITON7 115 640521 ANTELOPE 7 115 1 |  | 143 | 0.20335 | 126.52 | 640226 HOSKINS3 345 640520 ANTELOPE 3 345 1
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2018-132 | FROM->TO | 640149 CREITON7 115 640521 ANTELOPE 7 115 1 |  | 143 | 0.20335 | 126.52 | 640226 HOSKINS3 345 640520 ANTELOPE 3 345 1
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2018-065 | FROM->TO | 640149 CREITON7 115 640521 ANTELOPE 7 115 1 |  | 143 | 0.20262 | 120.13 | P42:345:NPPD:BKR-MOR-3306:::::
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2018-068 | FROM->TO | 640149 CREITON7 115 640521 ANTELOPE 7 115 1 |  | 143 | 0.20262 | 120.13 | P42:345:NPPD:BKR-MOR-3306:::::
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2018-131 | FROM->TO | 640149 CREITON7 115 640521 ANTELOPE 7 115 1 |  | 143 | 0.20262 | 120.13 | P42:345:NPPD:BKR-MOR-3306:::::
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2018-132 | FROM->TO | 640149 CREITON7 115 640521 ANTELOPE 7 115 1 |  | 143 | 0.20262 | 120.13 | P42:345:NPPD:BKR-MOR-3306:::::
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2018-065 | FROM->TO | 640149 CREITON7 115 640521 ANTELOPE 7 115 1 |  | 143 | 0.20274 | 119.87 | 640226 HOSKINS3 345 640520 ANTELOPE 3 345 1
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2018-068 | FROM->TO | 640149 CREITON7 115 640521 ANTELOPE 7 115 1 |  | 143 | 0.20274 | 119.87 | 640226 HOSKINS3 345 640520 ANTELOPE 3 345 1
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2018-131 | FROM->TO | 640149 CREITON7 115 640521 ANTELOPE 7 115 1 |  | 143 | 0.20274 | 119.87 | 640226 HOSKINS3 345 640520 ANTELOPE 3 345 1
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2018-132 | FROM->TO | 640149 CREITON7 115 640521 ANTELOPE 7 115 1 |  | 143 | 0.20274 | 119.87 | 640226 HOSKINS3 345 640520 ANTELOPE 3 345 1
Thermal | 02ALL | 1 | 02ALL-23SP | GEN-2018-065 | FROM->TO | 640149 CREITON7 115 640521 ANTELOPE 7 115 1 |  | 143 | 0.20349 | 118.88 | P42:345:NPPD:BKR-MOR-3306:::::
Thermal | 02ALL | 1 | 02ALL-23SP | GEN-2018-068 | FROM->TO | 640149 CREITON7 115 640521 ANTELOPE 7 115 1 |  | 143 | 0.20349 | 118.88 | P42:345:NPPD:BKR-MOR-3306:::::
Thermal | 02ALL | 1 | 02ALL-23SP | GEN-2018-131 | FROM->TO | 640149 CREITON7 115 640521 ANTELOPE 7 115 1 |  | 143 | 0.20349 | 118.88 | P42:345:NPPD:BKR-MOR-3306:::::
Thermal | 02ALL | 1 | 02ALL-23SP | GEN-2018-132 | FROM->TO | 640149 CREITON7 115 640521 ANTELOPE 7 115 1 |  | 143 | 0.20349 | 118.88 | P42:345:NPPD:BKR-MOR-3306:::::
Thermal | 02ALL | 1 | 02ALL-23SP | GEN-2018-065 | FROM->TO | 640149 CREITON7 115 640521 ANTELOPE 7 115 1 |  | 143 | 0.2036 | 118.63 | 640226 HOSKINS3 345 640520 ANTELOPE 3 345 1
Thermal | 02ALL | 1 | 02ALL-23SP | GEN-2018-068 | FROM->TO | 640149 CREITON7 115 640521 ANTELOPE 7 115 1 |  | 143 | 0.2036 | 118.63 | 640226 HOSKINS3 345 640520 ANTELOPE 3 345 1
Thermal | 02ALL | 1 | 02ALL-23SP | GEN-2018-131 | FROM->TO | 640149 CREITON7 115 640521 ANTELOPE 7 115 1 |  | 143 | 0.2036 | 118.63 | 640226 HOSKINS3 345 640520 ANTELOPE 3 345 1
Thermal | 02ALL | 1 | 02ALL-23SP | GEN-2018-132 | FROM->TO | 640149 CREITON7 115 640521 ANTELOPE 7 115 1 |  | 143 | 0.2036 | 118.63 | 640226 HOSKINS3 345 640520 ANTELOPE 3 345 1
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2019-029 | FROM->TO | 640183 GENTLMN3 345 997012 GGS T1 _1 230 1 |  | 336 | 0.23769 | 104.04 | 640183 GENTLMN3 345 640252 KEYSTON3 345 1
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2019-033 | FROM->TO | 640183 GENTLMN3 345 997012 GGS T1 _1 230 1 |  | 336 | 0.23769 | 104.04 | 640183 GENTLMN3 345 640252 KEYSTON3 345 1
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2019-029 | FROM->TO | 640184 GENTLMN4 230 640302 OGALALA4 230 1 |  | 320 | 0.5491 | 160.85 | 640183 GENTLMN3 345 640252 KEYSTON3 345 1
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2019-033 | FROM->TO | 640184 GENTLMN4 230 640302 OGALALA4 230 1 |  | 320 | 0.5491 | 160.85 | 640183 GENTLMN3 345 640252 KEYSTON3 345 1
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2019-029 | FROM->TO | 640184 GENTLMN4 230 640302 OGALALA4 230 1 |  | 320 | 0.55116 | 130.36 | 640183 GENTLMN3 345 640252 KEYSTON3 345 1
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2019-033 | FROM->TO | 640184 GENTLMN4 230 640302 OGALALA4 230 1 |  | 320 | 0.55116 | 130.36 | 640183 GENTLMN3 345 640252 KEYSTON3 345 1
Thermal | 02ALL | 1 | 02ALL-23SP | GEN-2019-029 | FROM->TO | 640184 GENTLMN4 230 640302 OGALALA4 230 1 |  | 320 | 0.54661 | 121.86 | 640183 GENTLMN3 345 640252 KEYSTON3 345 1
Thermal | 02ALL | 1 | 02ALL-23SP | GEN-2019-033 | FROM->TO | 640184 GENTLMN4 230 640302 OGALALA4 230 1 |  | 320 | 0.54661 | 121.86 | 640183 GENTLMN3 345 640252 KEYSTON3 345 1
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2019-029 | FROM->TO | 640184 GENTLMN4 230 997012 GGS T1 _1 230 1 |  | 336 | 0.23769 | 103.91 | 640183 GENTLMN3 345 640252 KEYSTON3 345 1
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2019-033 | FROM->TO | 640184 GENTLMN4 230 997012 GGS T1 _1 230 1 |  | 336 | 0.23769 | 103.91 | 640183 GENTLMN3 345 640252 KEYSTON3 345 1
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2018-065 | FROM->TO | 640226 HOSKINS3 345 996993 HOSKN T4 _1 115 1 |  | 336 | 0.07734 | 112.71 | P13:230-345:NPPD:NUCOR-1:::::
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2018-065 | FROM->TO | 640226 HOSKINS3 345 996993 HOSKN T4 _1 115 1 |  | 336 | 0.07734 | 112.71 | P13:230-345:NPPD:HOSKINS3:T2::::
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2018-068 | FROM->TO | 640226 HOSKINS3 345 996993 HOSKN T4 _1 115 1 |  | 336 | 0.07734 | 112.71 | P13:230-345:NPPD:NUCOR-1:::::
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2018-068 | FROM->TO | 640226 HOSKINS3 345 996993 HOSKN T4 _1 115 1 |  | 336 | 0.07734 | 112.71 | P13:230-345:NPPD:HOSKINS3:T2::::
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2018-083 | FROM->TO | 640226 HOSKINS3 345 996993 HOSKN T4 _1 115 1 |  | 336 | 0.10373 | 112.71 | P13:230-345:NPPD:NUCOR-1:::::
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2018-083 | FROM->TO | 640226 HOSKINS3 345 996993 HOSKN T4 _1 115 1 |  | 336 | 0.10373 | 112.71 | P13:230-345:NPPD:HOSKINS3:T2::::
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2018-131 | FROM->TO | 640226 HOSKINS3 345 996993 HOSKN T4 _1 115 1 |  | 336 | 0.07734 | 112.71 | P13:230-345:NPPD:NUCOR-1:::::
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2018-131 | FROM->TO | 640226 HOSKINS3 345 996993 HOSKN T4 _1 115 1 |  | 336 | 0.07734 | 112.71 | P13:230-345:NPPD:HOSKINS3:T2::::
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2018-132 | FROM->TO | 640226 HOSKINS3 345 996993 HOSKN T4 _1 115 1 |  | 336 | 0.07734 | 112.71 | P13:230-345:NPPD:NUCOR-1:::::
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2018-132 | FROM->TO | 640226 HOSKINS3 345 996993 HOSKN T4 _1 115 1 |  | 336 | 0.07734 | 112.71 | P13:230-345:NPPD:HOSKINS3:T2::::
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2019-069 | FROM->TO | 640226 HOSKINS3 345 996993 HOSKN T4 _1 115 1 |  | 336 | 0.10373 | 112.71 | P13:230-345:NPPD:NUCOR-1:::::
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2019-069 | FROM->TO | 640226 HOSKINS3 345 996993 HOSKN T4 _1 115 1 |  | 336 | 0.10373 | 112.71 | P13:230-345:NPPD:HOSKINS3:T2::::
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2019-070 | FROM->TO | 640226 HOSKINS3 345 996993 HOSKN T4 _1 115 1 |  | 336 | 0.10373 | 112.71 | P13:230-345:NPPD:NUCOR-1:::::
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2019-070 | FROM->TO | 640226 HOSKINS3 345 996993 HOSKN T4 _1 115 1 |  | 336 | 0.10373 | 112.71 | P13:230-345:NPPD:HOSKINS3:T2::::
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2019-073 | FROM->TO | 640226 HOSKINS3 345 996993 HOSKN T4 _1 115 1 |  | 336 | 0.10373 | 112.71 | P13:230-345:NPPD:NUCOR-1:::::
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2019-073 | FROM->TO | 640226 HOSKINS3 345 996993 HOSKN T4 _1 115 1 |  | 336 | 0.10373 | 112.71 | P13:230-345:NPPD:HOSKINS3:T2::::
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2018-065 | FROM->TO | 640226 HOSKINS3 345 996993 HOSKN T4 _1 115 1 |  | 336 | 0.09511 | 100.04 | 640342 SHELCRK3 345 763982 G19-069TAP 345 1
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2018-068 | FROM->TO | 640226 HOSKINS3 345 996993 HOSKN T4 _1 115 1 |  | 336 | 0.09511 | 100.04 | 640342 SHELCRK3 345 763982 G19-069TAP 345 1
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2018-083 | FROM->TO | 640226 HOSKINS3 345 996993 HOSKN T4 _1 115 1 |  | 336 | 0.13964 | 100.04 | 640342 SHELCRK3 345 763982 G19-069TAP 345 1
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2018-131 | FROM->TO | 640226 HOSKINS3 345 996993 HOSKN T4 _1 115 1 |  | 336 | 0.09511 | 100.04 | 640342 SHELCRK3 345 763982 G19-069TAP 345 1
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2018-132 | FROM->TO | 640226 HOSKINS3 345 996993 HOSKN T4 _1 115 1 |  | 336 | 0.09511 | 100.04 | 640342 SHELCRK3 345 763982 G19-069TAP 345 1
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2019-069 | FROM->TO | 640226 HOSKINS3 345 996993 HOSKN T4 _1 115 1 |  | 336 | 0.13964 | 100.04 | 640342 SHELCRK3 345 763982 G19-069TAP 345 1
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2019-070 | FROM->TO | 640226 HOSKINS3 345 996993 HOSKN T4 _1 115 1 |  | 336 | 0.13964 | 100.04 | 640342 SHELCRK3 345 763982 G19-069TAP 345 1
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2019-073 | FROM->TO | 640226 HOSKINS3 345 996993 HOSKN T4 _1 115 1 |  | 336 | 0.13964 | 100.04 | 640342 SHELCRK3 345 763982 G19-069TAP 345 1
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2018-065 | FROM->TO | 640226 HOSKINS3 345 996995 HOSKINS T2 _ 230 1 |  | 336 | 0.09602 | 117.95 | P13:115-345:NPPD:HOSKINS3:T4::::
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2018-065 | FROM->TO | 640226 HOSKINS3 345 996995 HOSKINS T2 _ 230 1 |  | 336 | 0.09602 | 117.95 | P13:115-345:NPPD:NUCOR-2:::::
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2018-068 | FROM->TO | 640226 HOSKINS3 345 996995 HOSKINS T2 _ 230 1 |  | 336 | 0.09602 | 117.95 | P13:115-345:NPPD:HOSKINS3:T4::::
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2018-068 | FROM->TO | 640226 HOSKINS3 345 996995 HOSKINS T2 _ 230 1 |  | 336 | 0.09602 | 117.95 | P13:115-345:NPPD:NUCOR-2:::::
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2018-083 | FROM->TO | 640226 HOSKINS3 345 996995 HOSKINS T2 _ 230 1 |  | 336 | 0.11439 | 117.95 | P13:115-345:NPPD:HOSKINS3:T4::::
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2018-083 | FROM->TO | 640226 HOSKINS3 345 996995 HOSKINS T2 _ 230 1 |  | 336 | 0.11439 | 117.95 | P13:115-345:NPPD:NUCOR-2:::::
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2018-131 | FROM->TO | 640226 HOSKINS3 345 996995 HOSKINS T2 _ 230 1 |  | 336 | 0.09602 | 117.95 | P13:115-345:NPPD:HOSKINS3:T4::::
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2018-131 | FROM->TO | 640226 HOSKINS3 345 996995 HOSKINS T2 _ 230 1 |  | 336 | 0.09602 | 117.95 | P13:115-345:NPPD:NUCOR-2:::::
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2018-132 | FROM->TO | 640226 HOSKINS3 345 996995 HOSKINS T2 _ 230 1 |  | 336 | 0.09602 | 117.95 | P13:115-345:NPPD:HOSKINS3:T4::::
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2018-132 | FROM->TO | 640226 HOSKINS3 345 996995 HOSKINS T2 _ 230 1 |  | 336 | 0.09602 | 117.95 | P13:115-345:NPPD:NUCOR-2:::::
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2019-069 | FROM->TO | 640226 HOSKINS3 345 996995 HOSKINS T2 _ 230 1 |  | 336 | 0.11439 | 117.95 | P13:115-345:NPPD:HOSKINS3:T4::::
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2019-069 | FROM->TO | 640226 HOSKINS3 345 996995 HOSKINS T2 _ 230 1 |  | 336 | 0.11439 | 117.95 | P13:115-345:NPPD:NUCOR-2:::::
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2019-070 | FROM->TO | 640226 HOSKINS3 345 996995 HOSKINS T2 _ 230 1 |  | 336 | 0.11439 | 117.95 | P13:115-345:NPPD:HOSKINS3:T4::::
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2019-070 | FROM->TO | 640226 HOSKINS3 345 996995 HOSKINS T2 _ 230 1 |  | 336 | 0.11439 | 117.95 | P13:115-345:NPPD:NUCOR-2:::::
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2019-073 | FROM->TO | 640226 HOSKINS3 345 996995 HOSKINS T2 _ 230 1 |  | 336 | 0.11439 | 117.95 | P13:115-345:NPPD:HOSKINS3:T4::::
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2019-073 | FROM->TO | 640226 HOSKINS3 345 996995 HOSKINS T2 _ 230 1 |  | 336 | 0.11439 | 117.95 | P13:115-345:NPPD:NUCOR-2:::::
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2018-065 | FROM->TO | 640226 HOSKINS3 345 996995 HOSKINS T2 _ 230 1 |  | 336 | 0.13121 | 110.74 | 640342 SHELCRK3 345 763982 G19-069TAP 345 1
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2018-068 | FROM->TO | 640226 HOSKINS3 345 996995 HOSKINS T2 _ 230 1 |  | 336 | 0.13121 | 110.74 | 640342 SHELCRK3 345 763982 G19-069TAP 345 1
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2018-083 | FROM->TO | 640226 HOSKINS3 345 996995 HOSKINS T2 _ 230 1 |  | 336 | 0.15949 | 110.74 | 640342 SHELCRK3 345 763982 G19-069TAP 345 1
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2018-131 | FROM->TO | 640226 HOSKINS3 345 996995 HOSKINS T2 _ 230 1 |  | 336 | 0.13121 | 110.74 | 640342 SHELCRK3 345 763982 G19-069TAP 345 1
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2018-132 | FROM->TO | 640226 HOSKINS3 345 996995 HOSKINS T2 _ 230 1 |  | 336 | 0.13121 | 110.74 | 640342 SHELCRK3 345 763982 G19-069TAP 345 1
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2019-069 | FROM->TO | 640226 HOSKINS3 345 996995 HOSKINS T2 _ 230 1 |  | 336 | 0.15949 | 110.74 | 640342 SHELCRK3 345 763982 G19-069TAP 345 1
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2019-070 | FROM->TO | 640226 HOSKINS3 345 996995 HOSKINS T2 _ 230 1 |  | 336 | 0.15949 | 110.74 | 640342 SHELCRK3 345 763982 G19-069TAP 345 1
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2019-073 | FROM->TO | 640226 HOSKINS3 345 996995 HOSKINS T2 _ 230 1 |  | 336 | 0.15949 | 110.74 | 640342 SHELCRK3 345 763982 G19-069TAP 345 1
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2018-065 | FROM->TO | 640226 HOSKINS3 345 996995 HOSKINS T2 _ 230 1 |  | 336 | 0.13115 | 110.64 | P42:345:NPPD:BKR-CPR-3310:::::
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2018-068 | FROM->TO | 640226 HOSKINS3 345 996995 HOSKINS T2 _ 230 1 |  | 336 | 0.13115 | 110.64 | P42:345:NPPD:BKR-CPR-3310:::::
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2018-083 | FROM->TO | 640226 HOSKINS3 345 996995 HOSKINS T2 _ 230 1 |  | 336 | 0.15943 | 110.64 | P42:345:NPPD:BKR-CPR-3310:::::
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2018-131 | FROM->TO | 640226 HOSKINS3 345 996995 HOSKINS T2 _ 230 1 |  | 336 | 0.13115 | 110.64 | P42:345:NPPD:BKR-CPR-3310:::::
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2018-132 | FROM->TO | 640226 HOSKINS3 345 996995 HOSKINS T2 _ 230 1 |  | 336 | 0.13115 | 110.64 | P42:345:NPPD:BKR-CPR-3310:::::
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2019-069 | FROM->TO | 640226 HOSKINS3 345 996995 HOSKINS T2 _ 230 1 |  | 336 | 0.15943 | 110.64 | P42:345:NPPD:BKR-CPR-3310:::::
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2019-070 | FROM->TO | 640226 HOSKINS3 345 996995 HOSKINS T2 _ 230 1 |  | 336 | 0.15943 | 110.64 | P42:345:NPPD:BKR-CPR-3310:::::
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2019-073 | FROM->TO | 640226 HOSKINS3 345 996995 HOSKINS T2 _ 230 1 |  | 336 | 0.15943 | 110.64 | P42:345:NPPD:BKR-CPR-3310:::::
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2018-065 | FROM->TO | 640226 HOSKINS3 345 996995 HOSKINS T2 _ 230 1 |  | 336 | 0.1534 | 105.32 | P21:345:MEC-NPPD:AUTO-SINGLE:RAUN3:HOSKINS3:1
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2018-065 | FROM->TO | 640226 HOSKINS3 345 996995 HOSKINS T2 _ 230 1 |  | 336 | 0.1534 | 105.32 | P12:345:MEC-NPPD:AUTO-SINGLE:RAUN3:HOSKINS3:1
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2018-068 | FROM->TO | 640226 HOSKINS3 345 996995 HOSKINS T2 _ 230 1 |  | 336 | 0.1534 | 105.32 | P21:345:MEC-NPPD:AUTO-SINGLE:RAUN3:HOSKINS3:1
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2018-068 | FROM->TO | 640226 HOSKINS3 345 996995 HOSKINS T2 _ 230 1 |  | 336 | 0.1534 | 105.32 | P12:345:MEC-NPPD:AUTO-SINGLE:RAUN3:HOSKINS3:1
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2018-083 | FROM->TO | 640226 HOSKINS3 345 996995 HOSKINS T2 _ 230 1 |  | 336 | 0.15559 | 105.32 | P21:345:MEC-NPPD:AUTO-SINGLE:RAUN3:HOSKINS3:1
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2018-083 | FROM->TO | 640226 HOSKINS3 345 996995 HOSKINS T2 _ 230 1 |  | 336 | 0.15559 | 105.32 | P12:345:MEC-NPPD:AUTO-SINGLE:RAUN3:HOSKINS3:1
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2018-131 | FROM->TO | 640226 HOSKINS3 345 996995 HOSKINS T2 _ 230 1 |  | 336 | 0.1534 | 105.32 | P21:345:MEC-NPPD:AUTO-SINGLE:RAUN3:HOSKINS3:1
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2018-131 | FROM->TO | 640226 HOSKINS3 345 996995 HOSKINS T2 _ 230 1 |  | 336 | 0.1534 | 105.32 | P12:345:MEC-NPPD:AUTO-SINGLE:RAUN3:HOSKINS3:1
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2018-132 | FROM->TO | 640226 HOSKINS3 345 996995 HOSKINS T2 _ 230 1 |  | 336 | 0.1534 | 105.32 | P21:345:MEC-NPPD:AUTO-SINGLE:RAUN3:HOSKINS3:1
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2018-132 | FROM->TO | 640226 HOSKINS3 345 996995 HOSKINS T2 _ 230 1 |  | 336 | 0.1534 | 105.32 | P12:345:MEC-NPPD:AUTO-SINGLE:RAUN3:HOSKINS3:1
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2019-039 | FROM->TO | 640226 HOSKINS3 345 996995 HOSKINS T2 _ 230 1 |  | 336 | 0.05639 | 105.32 | P21:345:MEC-NPPD:AUTO-SINGLE:RAUN3:HOSKINS3:1
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2019-039 | FROM->TO | 640226 HOSKINS3 345 996995 HOSKINS T2 _ 230 1 |  | 336 | 0.05639 | 105.32 | P12:345:MEC-NPPD:AUTO-SINGLE:RAUN3:HOSKINS3:1
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2019-069 | FROM->TO | 640226 HOSKINS3 345 996995 HOSKINS T2 _ 230 1 |  | 336 | 0.15559 | 105.32 | P21:345:MEC-NPPD:AUTO-SINGLE:RAUN3:HOSKINS3:1
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2019-069 | FROM->TO | 640226 HOSKINS3 345 996995 HOSKINS T2 _ 230 1 |  | 336 | 0.15559 | 105.32 | P12:345:MEC-NPPD:AUTO-SINGLE:RAUN3:HOSKINS3:1
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2019-070 | FROM->TO | 640226 HOSKINS3 345 996995 HOSKINS T2 _ 230 1 |  | 336 | 0.15559 | 105.32 | P21:345:MEC-NPPD:AUTO-SINGLE:RAUN3:HOSKINS3:1
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2019-070 | FROM->TO | 640226 HOSKINS3 345 996995 HOSKINS T2 _ 230 1 |  | 336 | 0.15559 | 105.32 | P12:345:MEC-NPPD:AUTO-SINGLE:RAUN3:HOSKINS3:1
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2019-073 | FROM->TO | 640226 HOSKINS3 345 996995 HOSKINS T2 _ 230 1 |  | 336 | 0.15559 | 105.32 | P21:345:MEC-NPPD:AUTO-SINGLE:RAUN3:HOSKINS3:1
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2019-073 | FROM->TO | 640226 HOSKINS3 345 996995 HOSKINS T2 _ 230 1 |  | 336 | 0.15559 | 105.32 | P12:345:MEC-NPPD:AUTO-SINGLE:RAUN3:HOSKINS3:1
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2018-065 | FROM->TO | 640226 HOSKINS3 345 996995 HOSKN T4 _1 115 1 |  | 336 | 0.07681 | 112.7 | P13:230-345:NPPD:NUCOR-1:::::
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2018-065 | FROM->TO | 640226 HOSKINS3 345 996995 HOSKN T4 _1 115 1 |  | 336 | 0.07681 | 112.7 | P13:230-345:NPPD:HOSKINS3:T2::::
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2018-068 | FROM->TO | 640226 HOSKINS3 345 996995 HOSKN T4 _1 115 1 |  | 336 | 0.07681 | 112.7 | P13:230-345:NPPD:NUCOR-1:::::
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2018-068 | FROM->TO | 640226 HOSKINS3 345 996995 HOSKN T4 _1 115 1 |  | 336 | 0.07681 | 112.7 | P13:230-345:NPPD:HOSKINS3:T2::::
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2018-083 | FROM->TO | 640226 HOSKINS3 345 996995 HOSKN T4 _1 115 1 |  | 336 | 0.1032 | 112.7 | P13:230-345:NPPD:NUCOR-1:::::
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2018-083 | FROM->TO | 640226 HOSKINS3 345 996995 HOSKN T4 _1 115 1 |  | 336 | 0.1032 | 112.7 | P13:230-345:NPPD:HOSKINS3:T2::::
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2018-131 | FROM->TO | 640226 HOSKINS3 345 996995 HOSKN T4 _1 115 1 |  | 336 | 0.07681 | 112.7 | P13:230-345:NPPD:NUCOR-1:::::
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2018-131 | FROM->TO | 640226 HOSKINS3 345 996995 HOSKN T4 _1 115 1 |  | 336 | 0.07681 | 112.7 | P13:230-345:NPPD:HOSKINS3:T2::::
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2018-132 | FROM->TO | 640226 HOSKINS3 345 996995 HOSKN T4 _1 115 1 |  | 336 | 0.07681 | 112.7 | P13:230-345:NPPD:NUCOR-1:::::
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2018-132 | FROM->TO | 640226 HOSKINS3 345 996995 HOSKN T4 _1 115 1 |  | 336 | 0.07681 | 112.7 | P13:230-345:NPPD:HOSKINS3:T2::::
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2019-069 | FROM->TO | 640226 HOSKINS3 345 996995 HOSKN T4 _1 115 1 |  | 336 | 0.1032 | 112.7 | P13:230-345:NPPD:NUCOR-1:::::
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2019-069 | FROM->TO | 640226 HOSKINS3 345 996995 HOSKN T4 _1 115 1 |  | 336 | 0.1032 | 112.7 | P13:230-345:NPPD:HOSKINS3:T2::::
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2019-070 | FROM->TO | 640226 HOSKINS3 345 996995 HOSKN T4 _1 115 1 |  | 336 | 0.1032 | 112.7 | P13:230-345:NPPD:NUCOR-1:::::
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2019-070 | FROM->TO | 640226 HOSKINS3 345 996995 HOSKN T4 _1 115 1 |  | 336 | 0.1032 | 112.7 | P13:230-345:NPPD:HOSKINS3:T2::::
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2019-073 | FROM->TO | 640226 HOSKINS3 345 996995 HOSKN T4 _1 115 1 |  | 336 | 0.1032 | 112.7 | P13:230-345:NPPD:NUCOR-1:::::
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2019-073 | FROM->TO | 640226 HOSKINS3 345 996995 HOSKN T4 _1 115 1 |  | 336 | 0.1032 | 112.7 | P13:230-345:NPPD:HOSKINS3:T2::::
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2018-065 | FROM->TO | 640226 HOSKINS3 345 996995 HOSKN T4 _1 115 1 |  | 336 | 0.0996 | 101.97 | P13:115-345:NPPD:ANTELOPE:T1::::
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2018-068 | FROM->TO | 640226 HOSKINS3 345 996995 HOSKN T4 _1 115 1 |  | 336 | 0.0996 | 101.97 | P13:115-345:NPPD:ANTELOPE:T1::::
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2018-083 | FROM->TO | 640226 HOSKINS3 345 996995 HOSKN T4 _1 115 1 |  | 336 | 0.07967 | 101.97 | P13:115-345:NPPD:ANTELOPE:T1::::
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2018-131 | FROM->TO | 640226 HOSKINS3 345 996995 HOSKN T4 _1 115 1 |  | 336 | 0.0996 | 101.97 | P13:115-345:NPPD:ANTELOPE:T1::::
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2018-132 | FROM->TO | 640226 HOSKINS3 345 996995 HOSKN T4 _1 115 1 |  | 336 | 0.0996 | 101.97 | P13:115-345:NPPD:ANTELOPE:T1::::
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2019-069 | FROM->TO | 640226 HOSKINS3 345 996995 HOSKN T4 _1 115 1 |  | 336 | 0.07967 | 101.97 | P13:115-345:NPPD:ANTELOPE:T1::::
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2019-070 | FROM->TO | 640226 HOSKINS3 345 996995 HOSKN T4 _1 115 1 |  | 336 | 0.07967 | 101.97 | P13:115-345:NPPD:ANTELOPE:T1::::
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2019-073 | FROM->TO | 640226 HOSKINS3 345 996995 HOSKN T4 _1 115 1 |  | 336 | 0.07967 | 101.97 | P13:115-345:NPPD:ANTELOPE:T1::::
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2018-065 | FROM->TO | 640226 HOSKINS3 345 996997 HOSKINS T2 _ 230 1 |  | 336 | 0.09556 | 116.72 | P13:115-345:NPPD:NUCOR-2:::::
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2018-065 | FROM->TO | 640226 HOSKINS3 345 996997 HOSKINS T2 _ 230 1 |  | 336 | 0.09556 | 116.72 | P13:115-345:NPPD:HOSKINS3:T4::::
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2018-068 | FROM->TO | 640226 HOSKINS3 345 996997 HOSKINS T2 _ 230 1 |  | 336 | 0.09556 | 116.72 | P13:115-345:NPPD:NUCOR-2:::::
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2018-068 | FROM->TO | 640226 HOSKINS3 345 996997 HOSKINS T2 _ 230 1 |  | 336 | 0.09556 | 116.72 | P13:115-345:NPPD:HOSKINS3:T4::::
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2018-083 | FROM->TO | 640226 HOSKINS3 345 996997 HOSKINS T2 _ 230 1 |  | 336 | 0.11394 | 116.72 | P13:115-345:NPPD:NUCOR-2:::::
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2018-083 | FROM->TO | 640226 HOSKINS3 345 996997 HOSKINS T2 _ 230 1 |  | 336 | 0.11394 | 116.72 | P13:115-345:NPPD:HOSKINS3:T4::::
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2018-131 | FROM->TO | 640226 HOSKINS3 345 996997 HOSKINS T2 _ 230 1 |  | 336 | 0.09556 | 116.72 | P13:115-345:NPPD:NUCOR-2:::::
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2018-131 | FROM->TO | 640226 HOSKINS3 345 996997 HOSKINS T2 _ 230 1 |  | 336 | 0.09556 | 116.72 | P13:115-345:NPPD:HOSKINS3:T4::::
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2018-132 | FROM->TO | 640226 HOSKINS3 345 996997 HOSKINS T2 _ 230 1 |  | 336 | 0.09556 | 116.72 | P13:115-345:NPPD:NUCOR-2:::::
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2018-132 | FROM->TO | 640226 HOSKINS3 345 996997 HOSKINS T2 _ 230 1 |  | 336 | 0.09556 | 116.72 | P13:115-345:NPPD:HOSKINS3:T4::::
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2019-069 | FROM->TO | 640226 HOSKINS3 345 996997 HOSKINS T2 _ 230 1 |  | 336 | 0.11394 | 116.72 | P13:115-345:NPPD:NUCOR-2:::::
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2019-069 | FROM->TO | 640226 HOSKINS3 345 996997 HOSKINS T2 _ 230 1 |  | 336 | 0.11394 | 116.72 | P13:115-345:NPPD:HOSKINS3:T4::::
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2019-070 | FROM->TO | 640226 HOSKINS3 345 996997 HOSKINS T2 _ 230 1 |  | 336 | 0.11394 | 116.72 | P13:115-345:NPPD:NUCOR-2:::::
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2019-070 | FROM->TO | 640226 HOSKINS3 345 996997 HOSKINS T2 _ 230 1 |  | 336 | 0.11394 | 116.72 | P13:115-345:NPPD:HOSKINS3:T4::::
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2019-073 | FROM->TO | 640226 HOSKINS3 345 996997 HOSKINS T2 _ 230 1 |  | 336 | 0.11394 | 116.72 | P13:115-345:NPPD:NUCOR-2:::::
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2019-073 | FROM->TO | 640226 HOSKINS3 345 996997 HOSKINS T2 _ 230 1 |  | 336 | 0.11394 | 116.72 | P13:115-345:NPPD:HOSKINS3:T4::::
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2018-065 | FROM->TO | 640226 HOSKINS3 345 996997 HOSKINS T2 _ 230 1 |  | 336 | 0.13125 | 104 | 640342 SHELCRK3 345 763982 G19-069TAP 345 1
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2018-068 | FROM->TO | 640226 HOSKINS3 345 996997 HOSKINS T2 _ 230 1 |  | 336 | 0.13125 | 104 | 640342 SHELCRK3 345 763982 G19-069TAP 345 1
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2018-083 | FROM->TO | 640226 HOSKINS3 345 996997 HOSKINS T2 _ 230 1 |  | 336 | 0.15953 | 104 | 640342 SHELCRK3 345 763982 G19-069TAP 345 1
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2018-131 | FROM->TO | 640226 HOSKINS3 345 996997 HOSKINS T2 _ 230 1 |  | 336 | 0.13125 | 104 | 640342 SHELCRK3 345 763982 G19-069TAP 345 1
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2018-132 | FROM->TO | 640226 HOSKINS3 345 996997 HOSKINS T2 _ 230 1 |  | 336 | 0.13125 | 104 | 640342 SHELCRK3 345 763982 G19-069TAP 345 1
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2019-069 | FROM->TO | 640226 HOSKINS3 345 996997 HOSKINS T2 _ 230 1 |  | 336 | 0.15953 | 104 | 640342 SHELCRK3 345 763982 G19-069TAP 345 1
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2019-070 | FROM->TO | 640226 HOSKINS3 345 996997 HOSKINS T2 _ 230 1 |  | 336 | 0.15953 | 104 | 640342 SHELCRK3 345 763982 G19-069TAP 345 1
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2019-073 | FROM->TO | 640226 HOSKINS3 345 996997 HOSKINS T2 _ 230 1 |  | 336 | 0.15953 | 104 | 640342 SHELCRK3 345 763982 G19-069TAP 345 1
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2018-065 | FROM->TO | 640226 HOSKINS3 345 996997 HOSKINS T2 _ 230 1 |  | 336 | 0.13118 | 103.92 | P42:345:NPPD:BKR-CPR-3310:::::
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2018-068 | FROM->TO | 640226 HOSKINS3 345 996997 HOSKINS T2 _ 230 1 |  | 336 | 0.13118 | 103.92 | P42:345:NPPD:BKR-CPR-3310:::::
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2018-083 | FROM->TO | 640226 HOSKINS3 345 996997 HOSKINS T2 _ 230 1 |  | 336 | 0.15947 | 103.92 | P42:345:NPPD:BKR-CPR-3310:::::
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2018-131 | FROM->TO | 640226 HOSKINS3 345 996997 HOSKINS T2 _ 230 1 |  | 336 | 0.13118 | 103.92 | P42:345:NPPD:BKR-CPR-3310:::::
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2018-132 | FROM->TO | 640226 HOSKINS3 345 996997 HOSKINS T2 _ 230 1 |  | 336 | 0.13118 | 103.92 | P42:345:NPPD:BKR-CPR-3310:::::
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2019-069 | FROM->TO | 640226 HOSKINS3 345 996997 HOSKINS T2 _ 230 1 |  | 336 | 0.15947 | 103.92 | P42:345:NPPD:BKR-CPR-3310:::::
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2019-070 | FROM->TO | 640226 HOSKINS3 345 996997 HOSKINS T2 _ 230 1 |  | 336 | 0.15947 | 103.92 | P42:345:NPPD:BKR-CPR-3310:::::
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2019-073 | FROM->TO | 640226 HOSKINS3 345 996997 HOSKINS T2 _ 230 1 |  | 336 | 0.15947 | 103.92 | P42:345:NPPD:BKR-CPR-3310:::::
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2018-065 | FROM->TO | 640226 HOSKINS3 345 996997 HOSKINS T2 _ 230 1 |  | 336 | 0.15344 | 100.05 | P21:345:MEC-NPPD:AUTO-SINGLE:RAUN3:HOSKINS3:1
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2018-065 | FROM->TO | 640226 HOSKINS3 345 996997 HOSKINS T2 _ 230 1 |  | 336 | 0.15344 | 100.05 | P12:345:MEC-NPPD:AUTO-SINGLE:RAUN3:HOSKINS3:1
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2018-068 | FROM->TO | 640226 HOSKINS3 345 996997 HOSKINS T2 _ 230 1 |  | 336 | 0.15344 | 100.05 | P21:345:MEC-NPPD:AUTO-SINGLE:RAUN3:HOSKINS3:1
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2018-068 | FROM->TO | 640226 HOSKINS3 345 996997 HOSKINS T2 _ 230 1 |  | 336 | 0.15344 | 100.05 | P12:345:MEC-NPPD:AUTO-SINGLE:RAUN3:HOSKINS3:1
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2018-083 | FROM->TO | 640226 HOSKINS3 345 996997 HOSKINS T2 _ 230 1 |  | 336 | 0.15562 | 100.05 | P21:345:MEC-NPPD:AUTO-SINGLE:RAUN3:HOSKINS3:1
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2018-083 | FROM->TO | 640226 HOSKINS3 345 996997 HOSKINS T2 _ 230 1 |  | 336 | 0.15562 | 100.05 | P12:345:MEC-NPPD:AUTO-SINGLE:RAUN3:HOSKINS3:1
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2018-131 | FROM->TO | 640226 HOSKINS3 345 996997 HOSKINS T2 _ 230 1 |  | 336 | 0.15344 | 100.05 | P21:345:MEC-NPPD:AUTO-SINGLE:RAUN3:HOSKINS3:1
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2018-131 | FROM->TO | 640226 HOSKINS3 345 996997 HOSKINS T2 _ 230 1 |  | 336 | 0.15344 | 100.05 | P12:345:MEC-NPPD:AUTO-SINGLE:RAUN3:HOSKINS3:1
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2018-132 | FROM->TO | 640226 HOSKINS3 345 996997 HOSKINS T2 _ 230 1 |  | 336 | 0.15344 | 100.05 | P21:345:MEC-NPPD:AUTO-SINGLE:RAUN3:HOSKINS3:1
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2018-132 | FROM->TO | 640226 HOSKINS3 345 996997 HOSKINS T2 _ 230 1 |  | 336 | 0.15344 | 100.05 | P12:345:MEC-NPPD:AUTO-SINGLE:RAUN3:HOSKINS3:1
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2019-039 | FROM->TO | 640226 HOSKINS3 345 996997 HOSKINS T2 _ 230 1 |  | 336 | 0.05643 | 100.05 | P21:345:MEC-NPPD:AUTO-SINGLE:RAUN3:HOSKINS3:1
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2019-039 | FROM->TO | 640226 HOSKINS3 345 996997 HOSKINS T2 _ 230 1 |  | 336 | 0.05643 | 100.05 | P12:345:MEC-NPPD:AUTO-SINGLE:RAUN3:HOSKINS3:1
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2019-069 | FROM->TO | 640226 HOSKINS3 345 996997 HOSKINS T2 _ 230 1 |  | 336 | 0.15562 | 100.05 | P21:345:MEC-NPPD:AUTO-SINGLE:RAUN3:HOSKINS3:1
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2019-069 | FROM->TO | 640226 HOSKINS3 345 996997 HOSKINS T2 _ 230 1 |  | 336 | 0.15562 | 100.05 | P12:345:MEC-NPPD:AUTO-SINGLE:RAUN3:HOSKINS3:1
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2019-070 | FROM->TO | 640226 HOSKINS3 345 996997 HOSKINS T2 _ 230 1 |  | 336 | 0.15562 | 100.05 | P21:345:MEC-NPPD:AUTO-SINGLE:RAUN3:HOSKINS3:1
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2019-070 | FROM->TO | 640226 HOSKINS3 345 996997 HOSKINS T2 _ 230 1 |  | 336 | 0.15562 | 100.05 | P12:345:MEC-NPPD:AUTO-SINGLE:RAUN3:HOSKINS3:1
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2019-073 | FROM->TO | 640226 HOSKINS3 345 996997 HOSKINS T2 _ 230 1 |  | 336 | 0.15562 | 100.05 | P21:345:MEC-NPPD:AUTO-SINGLE:RAUN3:HOSKINS3:1
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2019-073 | FROM->TO | 640226 HOSKINS3 345 996997 HOSKINS T2 _ 230 1 |  | 336 | 0.15562 | 100.05 | P12:345:MEC-NPPD:AUTO-SINGLE:RAUN3:HOSKINS3:1
Thermal | 02ALL | 1 | 02ALL-23SP | GEN-2018-065 | FROM->TO | 640226 HOSKINS3 345 996997 HOSKN T4 _1 115 1 |  | 336 | 0.07662 | 112.64 | P13:230-345:NPPD:HOSKINS3:T2::::
Thermal | 02ALL | 1 | 02ALL-23SP | GEN-2018-065 | FROM->TO | 640226 HOSKINS3 345 996997 HOSKN T4 _1 115 1 |  | 336 | 0.07662 | 112.64 | P13:230-345:NPPD:NUCOR-1:::::
Thermal | 02ALL | 1 | 02ALL-23SP | GEN-2018-068 | FROM->TO | 640226 HOSKINS3 345 996997 HOSKN T4 _1 115 1 |  | 336 | 0.07662 | 112.64 | P13:230-345:NPPD:HOSKINS3:T2::::
Thermal | 02ALL | 1 | 02ALL-23SP | GEN-2018-068 | FROM->TO | 640226 HOSKINS3 345 996997 HOSKN T4 _1 115 1 |  | 336 | 0.07662 | 112.64 | P13:230-345:NPPD:NUCOR-1:::::
Thermal | 02ALL | 1 | 02ALL-23SP | GEN-2018-083 | FROM->TO | 640226 HOSKINS3 345 996997 HOSKN T4 _1 115 1 |  | 336 | 0.10305 | 112.64 | P13:230-345:NPPD:HOSKINS3:T2::::
Thermal | 02ALL | 1 | 02ALL-23SP | GEN-2018-083 | FROM->TO | 640226 HOSKINS3 345 996997 HOSKN T4 _1 115 1 |  | 336 | 0.10305 | 112.64 | P13:230-345:NPPD:NUCOR-1:::::
Thermal | 02ALL | 1 | 02ALL-23SP | GEN-2018-131 | FROM->TO | 640226 HOSKINS3 345 996997 HOSKN T4 _1 115 1 |  | 336 | 0.07662 | 112.64 | P13:230-345:NPPD:HOSKINS3:T2::::
Thermal | 02ALL | 1 | 02ALL-23SP | GEN-2018-131 | FROM->TO | 640226 HOSKINS3 345 996997 HOSKN T4 _1 115 1 |  | 336 | 0.07662 | 112.64 | P13:230-345:NPPD:NUCOR-1:::::
Thermal | 02ALL | 1 | 02ALL-23SP | GEN-2018-132 | FROM->TO | 640226 HOSKINS3 345 996997 HOSKN T4 _1 115 1 |  | 336 | 0.07662 | 112.64 | P13:230-345:NPPD:HOSKINS3:T2::::
Thermal | 02ALL | 1 | 02ALL-23SP | GEN-2018-132 | FROM->TO | 640226 HOSKINS3 345 996997 HOSKN T4 _1 115 1 |  | 336 | 0.07662 | 112.64 | P13:230-345:NPPD:NUCOR-1:::::
Thermal | 02ALL | 1 | 02ALL-23SP | GEN-2019-069 | FROM->TO | 640226 HOSKINS3 345 996997 HOSKN T4 _1 115 1 |  | 336 | 0.10305 | 112.64 | P13:230-345:NPPD:HOSKINS3:T2::::
Thermal | 02ALL | 1 | 02ALL-23SP | GEN-2019-069 | FROM->TO | 640226 HOSKINS3 345 996997 HOSKN T4 _1 115 1 |  | 336 | 0.10305 | 112.64 | P13:230-345:NPPD:NUCOR-1:::::
Thermal | 02ALL | 1 | 02ALL-23SP | GEN-2019-070 | FROM->TO | 640226 HOSKINS3 345 996997 HOSKN T4 _1 115 1 |  | 336 | 0.10305 | 112.64 | P13:230-345:NPPD:HOSKINS3:T2::::
Thermal | 02ALL | 1 | 02ALL-23SP | GEN-2019-070 | FROM->TO | 640226 HOSKINS3 345 996997 HOSKN T4 _1 115 1 |  | 336 | 0.10305 | 112.64 | P13:230-345:NPPD:NUCOR-1:::::
Thermal | 02ALL | 1 | 02ALL-23SP | GEN-2019-073 | FROM->TO | 640226 HOSKINS3 345 996997 HOSKN T4 _1 115 1 |  | 336 | 0.10305 | 112.64 | P13:230-345:NPPD:HOSKINS3:T2::::
Thermal | 02ALL | 1 | 02ALL-23SP | GEN-2019-073 | FROM->TO | 640226 HOSKINS3 345 996997 HOSKN T4 _1 115 1 |  | 336 | 0.10305 | 112.64 | P13:230-345:NPPD:NUCOR-1:::::
Thermal | 02ALL | 1 | 02ALL-23SP | GEN-2018-065 | FROM->TO | 640226 HOSKINS3 345 996997 HOSKN T4 _1 115 1 |  | 336 | 0.09938 | 102.23 | P13:115-345:NPPD:ANTELOPE:T1::::
Thermal | 02ALL | 1 | 02ALL-23SP | GEN-2018-068 | FROM->TO | 640226 HOSKINS3 345 996997 HOSKN T4 _1 115 1 |  | 336 | 0.09938 | 102.23 | P13:115-345:NPPD:ANTELOPE:T1::::
Thermal | 02ALL | 1 | 02ALL-23SP | GEN-2018-083 | FROM->TO | 640226 HOSKINS3 345 996997 HOSKN T4 _1 115 1 |  | 336 | 0.07948 | 102.23 | P13:115-345:NPPD:ANTELOPE:T1::::
Thermal | 02ALL | 1 | 02ALL-23SP | GEN-2018-131 | FROM->TO | 640226 HOSKINS3 345 996997 HOSKN T4 _1 115 1 |  | 336 | 0.09938 | 102.23 | P13:115-345:NPPD:ANTELOPE:T1::::
Thermal | 02ALL | 1 | 02ALL-23SP | GEN-2018-132 | FROM->TO | 640226 HOSKINS3 345 996997 HOSKN T4 _1 115 1 |  | 336 | 0.09938 | 102.23 | P13:115-345:NPPD:ANTELOPE:T1::::
Thermal | 02ALL | 1 | 02ALL-23SP | GEN-2019-069 | FROM->TO | 640226 HOSKINS3 345 996997 HOSKN T4 _1 115 1 |  | 336 | 0.07948 | 102.23 | P13:115-345:NPPD:ANTELOPE:T1::::
Thermal | 02ALL | 1 | 02ALL-23SP | GEN-2019-070 | FROM->TO | 640226 HOSKINS3 345 996997 HOSKN T4 _1 115 1 |  | 336 | 0.07948 | 102.23 | P13:115-345:NPPD:ANTELOPE:T1::::
Thermal | 02ALL | 1 | 02ALL-23SP | GEN-2019-073 | FROM->TO | 640226 HOSKINS3 345 996997 HOSKN T4 _1 115 1 |  | 336 | 0.07948 | 102.23 | P13:115-345:NPPD:ANTELOPE:T1::::
Thermal | 02ALL | 1 | 02ALL-23SP | GEN-2018-065 | FROM->TO | 640226 HOSKINS3 345 996999 HOSKINS T2 _ 230 1 |  | 336 | 0.09536 | 115.97 | P13:115-345:NPPD:NUCOR-2:::::
Thermal | 02ALL | 1 | 02ALL-23SP | GEN-2018-065 | FROM->TO | 640226 HOSKINS3 345 996999 HOSKINS T2 _ 230 1 |  | 336 | 0.09536 | 115.97 | P13:115-345:NPPD:HOSKINS3:T4::::
Thermal | 02ALL | 1 | 02ALL-23SP | GEN-2018-068 | FROM->TO | 640226 HOSKINS3 345 996999 HOSKINS T2 _ 230 1 |  | 336 | 0.09536 | 115.97 | P13:115-345:NPPD:NUCOR-2:::::
Thermal | 02ALL | 1 | 02ALL-23SP | GEN-2018-068 | FROM->TO | 640226 HOSKINS3 345 996999 HOSKINS T2 _ 230 1 |  | 336 | 0.09536 | 115.97 | P13:115-345:NPPD:HOSKINS3:T4::::
Thermal | 02ALL | 1 | 02ALL-23SP | GEN-2018-083 | FROM->TO | 640226 HOSKINS3 345 996999 HOSKINS T2 _ 230 1 |  | 336 | 0.11376 | 115.97 | P13:115-345:NPPD:NUCOR-2:::::
Thermal | 02ALL | 1 | 02ALL-23SP | GEN-2018-083 | FROM->TO | 640226 HOSKINS3 345 996999 HOSKINS T2 _ 230 1 |  | 336 | 0.11376 | 115.97 | P13:115-345:NPPD:HOSKINS3:T4::::
Thermal | 02ALL | 1 | 02ALL-23SP | GEN-2018-131 | FROM->TO | 640226 HOSKINS3 345 996999 HOSKINS T2 _ 230 1 |  | 336 | 0.09536 | 115.97 | P13:115-345:NPPD:NUCOR-2:::::
Thermal | 02ALL | 1 | 02ALL-23SP | GEN-2018-131 | FROM->TO | 640226 HOSKINS3 345 996999 HOSKINS T2 _ 230 1 |  | 336 | 0.09536 | 115.97 | P13:115-345:NPPD:HOSKINS3:T4::::
Thermal | 02ALL | 1 | 02ALL-23SP | GEN-2018-132 | FROM->TO | 640226 HOSKINS3 345 996999 HOSKINS T2 _ 230 1 |  | 336 | 0.09536 | 115.97 | P13:115-345:NPPD:NUCOR-2:::::
Thermal | 02ALL | 1 | 02ALL-23SP | GEN-2018-132 | FROM->TO | 640226 HOSKINS3 345 996999 HOSKINS T2 _ 230 1 |  | 336 | 0.09536 | 115.97 | P13:115-345:NPPD:HOSKINS3:T4::::
Thermal | 02ALL | 1 | 02ALL-23SP | GEN-2019-069 | FROM->TO | 640226 HOSKINS3 345 996999 HOSKINS T2 _ 230 1 |  | 336 | 0.11376 | 115.97 | P13:115-345:NPPD:NUCOR-2:::::
Thermal | 02ALL | 1 | 02ALL-23SP | GEN-2019-069 | FROM->TO | 640226 HOSKINS3 345 996999 HOSKINS T2 _ 230 1 |  | 336 | 0.11376 | 115.97 | P13:115-345:NPPD:HOSKINS3:T4::::
Thermal | 02ALL | 1 | 02ALL-23SP | GEN-2019-070 | FROM->TO | 640226 HOSKINS3 345 996999 HOSKINS T2 _ 230 1 |  | 336 | 0.11376 | 115.97 | P13:115-345:NPPD:NUCOR-2:::::
Thermal | 02ALL | 1 | 02ALL-23SP | GEN-2019-070 | FROM->TO | 640226 HOSKINS3 345 996999 HOSKINS T2 _ 230 1 |  | 336 | 0.11376 | 115.97 | P13:115-345:NPPD:HOSKINS3:T4::::
Thermal | 02ALL | 1 | 02ALL-23SP | GEN-2019-073 | FROM->TO | 640226 HOSKINS3 345 996999 HOSKINS T2 _ 230 1 |  | 336 | 0.11376 | 115.97 | P13:115-345:NPPD:NUCOR-2:::::
Thermal | 02ALL | 1 | 02ALL-23SP | GEN-2019-073 | FROM->TO | 640226 HOSKINS3 345 996999 HOSKINS T2 _ 230 1 |  | 336 | 0.11376 | 115.97 | P13:115-345:NPPD:HOSKINS3:T4::::
Thermal | 02ALL | 1 | 02ALL-23SP | GEN-2018-065 | FROM->TO | 640226 HOSKINS3 345 996999 HOSKINS T2 _ 230 1 |  | 336 | 0.13133 | 103.47 | 640342 SHELCRK3 345 763982 G19-069TAP 345 1
Thermal | 02ALL | 1 | 02ALL-23SP | GEN-2018-068 | FROM->TO | 640226 HOSKINS3 345 996999 HOSKINS T2 _ 230 1 |  | 336 | 0.13133 | 103.47 | 640342 SHELCRK3 345 763982 G19-069TAP 345 1
Thermal | 02ALL | 1 | 02ALL-23SP | GEN-2018-083 | FROM->TO | 640226 HOSKINS3 345 996999 HOSKINS T2 _ 230 1 |  | 336 | 0.15956 | 103.47 | 640342 SHELCRK3 345 763982 G19-069TAP 345 1
Thermal | 02ALL | 1 | 02ALL-23SP | GEN-2018-131 | FROM->TO | 640226 HOSKINS3 345 996999 HOSKINS T2 _ 230 1 |  | 336 | 0.13133 | 103.47 | 640342 SHELCRK3 345 763982 G19-069TAP 345 1
Thermal | 02ALL | 1 | 02ALL-23SP | GEN-2018-132 | FROM->TO | 640226 HOSKINS3 345 996999 HOSKINS T2 _ 230 1 |  | 336 | 0.13133 | 103.47 | 640342 SHELCRK3 345 763982 G19-069TAP 345 1
Thermal | 02ALL | 1 | 02ALL-23SP | GEN-2019-069 | FROM->TO | 640226 HOSKINS3 345 996999 HOSKINS T2 _ 230 1 |  | 336 | 0.15956 | 103.47 | 640342 SHELCRK3 345 763982 G19-069TAP 345 1
Thermal | 02ALL | 1 | 02ALL-23SP | GEN-2019-070 | FROM->TO | 640226 HOSKINS3 345 996999 HOSKINS T2 _ 230 1 |  | 336 | 0.15956 | 103.47 | 640342 SHELCRK3 345 763982 G19-069TAP 345 1
Thermal | 02ALL | 1 | 02ALL-23SP | GEN-2019-073 | FROM->TO | 640226 HOSKINS3 345 996999 HOSKINS T2 _ 230 1 |  | 336 | 0.15956 | 103.47 | 640342 SHELCRK3 345 763982 G19-069TAP 345 1
Thermal | 02ALL | 1 | 02ALL-23SP | GEN-2018-065 | FROM->TO | 640226 HOSKINS3 345 996999 HOSKINS T2 _ 230 1 |  | 336 | 0.13126 | 103.4 | P42:345:NPPD:BKR-CPR-3310:::::
Thermal | 02ALL | 1 | 02ALL-23SP | GEN-2018-068 | FROM->TO | 640226 HOSKINS3 345 996999 HOSKINS T2 _ 230 1 |  | 336 | 0.13126 | 103.4 | P42:345:NPPD:BKR-CPR-3310:::::
Thermal | 02ALL | 1 | 02ALL-23SP | GEN-2018-083 | FROM->TO | 640226 HOSKINS3 345 996999 HOSKINS T2 _ 230 1 |  | 336 | 0.1595 | 103.4 | P42:345:NPPD:BKR-CPR-3310:::::
Thermal | 02ALL | 1 | 02ALL-23SP | GEN-2018-131 | FROM->TO | 640226 HOSKINS3 345 996999 HOSKINS T2 _ 230 1 |  | 336 | 0.13126 | 103.4 | P42:345:NPPD:BKR-CPR-3310:::::
Thermal | 02ALL | 1 | 02ALL-23SP | GEN-2018-132 | FROM->TO | 640226 HOSKINS3 345 996999 HOSKINS T2 _ 230 1 |  | 336 | 0.13126 | 103.4 | P42:345:NPPD:BKR-CPR-3310:::::
Thermal | 02ALL | 1 | 02ALL-23SP | GEN-2019-069 | FROM->TO | 640226 HOSKINS3 345 996999 HOSKINS T2 _ 230 1 |  | 336 | 0.1595 | 103.4 | P42:345:NPPD:BKR-CPR-3310:::::
Thermal | 02ALL | 1 | 02ALL-23SP | GEN-2019-070 | FROM->TO | 640226 HOSKINS3 345 996999 HOSKINS T2 _ 230 1 |  | 336 | 0.1595 | 103.4 | P42:345:NPPD:BKR-CPR-3310:::::
Thermal | 02ALL | 1 | 02ALL-23SP | GEN-2019-073 | FROM->TO | 640226 HOSKINS3 345 996999 HOSKINS T2 _ 230 1 |  | 336 | 0.1595 | 103.4 | P42:345:NPPD:BKR-CPR-3310:::::
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2018-065 | FROM->TO | 640227 HOSKINS4 230 996995 HOSKINS T2 _ 230 1 |  | 336 | 0.09602 | 116.92 | P13:115-345:NPPD:NUCOR-2:::::
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2018-065 | FROM->TO | 640227 HOSKINS4 230 996995 HOSKINS T2 _ 230 1 |  | 336 | 0.09602 | 116.92 | P13:115-345:NPPD:HOSKINS3:T4::::
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2018-068 | FROM->TO | 640227 HOSKINS4 230 996995 HOSKINS T2 _ 230 1 |  | 336 | 0.09602 | 116.92 | P13:115-345:NPPD:NUCOR-2:::::
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2018-068 | FROM->TO | 640227 HOSKINS4 230 996995 HOSKINS T2 _ 230 1 |  | 336 | 0.09602 | 116.92 | P13:115-345:NPPD:HOSKINS3:T4::::
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2018-083 | FROM->TO | 640227 HOSKINS4 230 996995 HOSKINS T2 _ 230 1 |  | 336 | 0.11439 | 116.92 | P13:115-345:NPPD:NUCOR-2:::::
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2018-083 | FROM->TO | 640227 HOSKINS4 230 996995 HOSKINS T2 _ 230 1 |  | 336 | 0.11439 | 116.92 | P13:115-345:NPPD:HOSKINS3:T4::::
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2018-131 | FROM->TO | 640227 HOSKINS4 230 996995 HOSKINS T2 _ 230 1 |  | 336 | 0.09602 | 116.92 | P13:115-345:NPPD:NUCOR-2:::::
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2018-131 | FROM->TO | 640227 HOSKINS4 230 996995 HOSKINS T2 _ 230 1 |  | 336 | 0.09602 | 116.92 | P13:115-345:NPPD:HOSKINS3:T4::::
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2018-132 | FROM->TO | 640227 HOSKINS4 230 996995 HOSKINS T2 _ 230 1 |  | 336 | 0.09602 | 116.92 | P13:115-345:NPPD:NUCOR-2:::::
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2018-132 | FROM->TO | 640227 HOSKINS4 230 996995 HOSKINS T2 _ 230 1 |  | 336 | 0.09602 | 116.92 | P13:115-345:NPPD:HOSKINS3:T4::::
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2019-069 | FROM->TO | 640227 HOSKINS4 230 996995 HOSKINS T2 _ 230 1 |  | 336 | 0.11439 | 116.92 | P13:115-345:NPPD:NUCOR-2:::::
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2019-069 | FROM->TO | 640227 HOSKINS4 230 996995 HOSKINS T2 _ 230 1 |  | 336 | 0.11439 | 116.92 | P13:115-345:NPPD:HOSKINS3:T4::::
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2019-070 | FROM->TO | 640227 HOSKINS4 230 996995 HOSKINS T2 _ 230 1 |  | 336 | 0.11439 | 116.92 | P13:115-345:NPPD:NUCOR-2:::::
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2019-070 | FROM->TO | 640227 HOSKINS4 230 996995 HOSKINS T2 _ 230 1 |  | 336 | 0.11439 | 116.92 | P13:115-345:NPPD:HOSKINS3:T4::::
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2019-073 | FROM->TO | 640227 HOSKINS4 230 996995 HOSKINS T2 _ 230 1 |  | 336 | 0.11439 | 116.92 | P13:115-345:NPPD:NUCOR-2:::::
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2019-073 | FROM->TO | 640227 HOSKINS4 230 996995 HOSKINS T2 _ 230 1 |  | 336 | 0.11439 | 116.92 | P13:115-345:NPPD:HOSKINS3:T4::::
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2018-065 | FROM->TO | 640227 HOSKINS4 230 996995 HOSKINS T2 _ 230 1 |  | 336 | 0.13121 | 110.51 | 640342 SHELCRK3 345 763982 G19-069TAP 345 1
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2018-068 | FROM->TO | 640227 HOSKINS4 230 996995 HOSKINS T2 _ 230 1 |  | 336 | 0.13121 | 110.51 | 640342 SHELCRK3 345 763982 G19-069TAP 345 1
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2018-083 | FROM->TO | 640227 HOSKINS4 230 996995 HOSKINS T2 _ 230 1 |  | 336 | 0.15949 | 110.51 | 640342 SHELCRK3 345 763982 G19-069TAP 345 1
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2018-131 | FROM->TO | 640227 HOSKINS4 230 996995 HOSKINS T2 _ 230 1 |  | 336 | 0.13121 | 110.51 | 640342 SHELCRK3 345 763982 G19-069TAP 345 1
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2018-132 | FROM->TO | 640227 HOSKINS4 230 996995 HOSKINS T2 _ 230 1 |  | 336 | 0.13121 | 110.51 | 640342 SHELCRK3 345 763982 G19-069TAP 345 1
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2019-069 | FROM->TO | 640227 HOSKINS4 230 996995 HOSKINS T2 _ 230 1 |  | 336 | 0.15949 | 110.51 | 640342 SHELCRK3 345 763982 G19-069TAP 345 1
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2019-070 | FROM->TO | 640227 HOSKINS4 230 996995 HOSKINS T2 _ 230 1 |  | 336 | 0.15949 | 110.51 | 640342 SHELCRK3 345 763982 G19-069TAP 345 1
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2019-073 | FROM->TO | 640227 HOSKINS4 230 996995 HOSKINS T2 _ 230 1 |  | 336 | 0.15949 | 110.51 | 640342 SHELCRK3 345 763982 G19-069TAP 345 1
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2018-065 | FROM->TO | 640227 HOSKINS4 230 996995 HOSKINS T2 _ 230 1 |  | 336 | 0.13115 | 110.41 | P42:345:NPPD:BKR-CPR-3310:::::
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2018-068 | FROM->TO | 640227 HOSKINS4 230 996995 HOSKINS T2 _ 230 1 |  | 336 | 0.13115 | 110.41 | P42:345:NPPD:BKR-CPR-3310:::::
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2018-083 | FROM->TO | 640227 HOSKINS4 230 996995 HOSKINS T2 _ 230 1 |  | 336 | 0.15943 | 110.41 | P42:345:NPPD:BKR-CPR-3310:::::
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2018-131 | FROM->TO | 640227 HOSKINS4 230 996995 HOSKINS T2 _ 230 1 |  | 336 | 0.13115 | 110.41 | P42:345:NPPD:BKR-CPR-3310:::::
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2018-132 | FROM->TO | 640227 HOSKINS4 230 996995 HOSKINS T2 _ 230 1 |  | 336 | 0.13115 | 110.41 | P42:345:NPPD:BKR-CPR-3310:::::
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2019-069 | FROM->TO | 640227 HOSKINS4 230 996995 HOSKINS T2 _ 230 1 |  | 336 | 0.15943 | 110.41 | P42:345:NPPD:BKR-CPR-3310:::::
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2019-070 | FROM->TO | 640227 HOSKINS4 230 996995 HOSKINS T2 _ 230 1 |  | 336 | 0.15943 | 110.41 | P42:345:NPPD:BKR-CPR-3310:::::
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2019-073 | FROM->TO | 640227 HOSKINS4 230 996995 HOSKINS T2 _ 230 1 |  | 336 | 0.15943 | 110.41 | P42:345:NPPD:BKR-CPR-3310:::::
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2018-065 | FROM->TO | 640227 HOSKINS4 230 996995 HOSKINS T2 _ 230 1 |  | 336 | 0.1534 | 105.26 | P21:345:MEC-NPPD:AUTO-SINGLE:RAUN3:HOSKINS3:1
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2018-065 | FROM->TO | 640227 HOSKINS4 230 996995 HOSKINS T2 _ 230 1 |  | 336 | 0.1534 | 105.26 | P12:345:MEC-NPPD:AUTO-SINGLE:RAUN3:HOSKINS3:1
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2018-068 | FROM->TO | 640227 HOSKINS4 230 996995 HOSKINS T2 _ 230 1 |  | 336 | 0.1534 | 105.26 | P21:345:MEC-NPPD:AUTO-SINGLE:RAUN3:HOSKINS3:1
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2018-068 | FROM->TO | 640227 HOSKINS4 230 996995 HOSKINS T2 _ 230 1 |  | 336 | 0.1534 | 105.26 | P12:345:MEC-NPPD:AUTO-SINGLE:RAUN3:HOSKINS3:1
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2018-083 | FROM->TO | 640227 HOSKINS4 230 996995 HOSKINS T2 _ 230 1 |  | 336 | 0.15559 | 105.26 | P21:345:MEC-NPPD:AUTO-SINGLE:RAUN3:HOSKINS3:1
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2018-083 | FROM->TO | 640227 HOSKINS4 230 996995 HOSKINS T2 _ 230 1 |  | 336 | 0.15559 | 105.26 | P12:345:MEC-NPPD:AUTO-SINGLE:RAUN3:HOSKINS3:1
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2018-131 | FROM->TO | 640227 HOSKINS4 230 996995 HOSKINS T2 _ 230 1 |  | 336 | 0.1534 | 105.26 | P21:345:MEC-NPPD:AUTO-SINGLE:RAUN3:HOSKINS3:1
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2018-131 | FROM->TO | 640227 HOSKINS4 230 996995 HOSKINS T2 _ 230 1 |  | 336 | 0.1534 | 105.26 | P12:345:MEC-NPPD:AUTO-SINGLE:RAUN3:HOSKINS3:1
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2018-132 | FROM->TO | 640227 HOSKINS4 230 996995 HOSKINS T2 _ 230 1 |  | 336 | 0.1534 | 105.26 | P21:345:MEC-NPPD:AUTO-SINGLE:RAUN3:HOSKINS3:1
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2018-132 | FROM->TO | 640227 HOSKINS4 230 996995 HOSKINS T2 _ 230 1 |  | 336 | 0.1534 | 105.26 | P12:345:MEC-NPPD:AUTO-SINGLE:RAUN3:HOSKINS3:1
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2019-039 | FROM->TO | 640227 HOSKINS4 230 996995 HOSKINS T2 _ 230 1 |  | 336 | 0.05639 | 105.26 | P21:345:MEC-NPPD:AUTO-SINGLE:RAUN3:HOSKINS3:1
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2019-039 | FROM->TO | 640227 HOSKINS4 230 996995 HOSKINS T2 _ 230 1 |  | 336 | 0.05639 | 105.26 | P12:345:MEC-NPPD:AUTO-SINGLE:RAUN3:HOSKINS3:1
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2019-069 | FROM->TO | 640227 HOSKINS4 230 996995 HOSKINS T2 _ 230 1 |  | 336 | 0.15559 | 105.26 | P21:345:MEC-NPPD:AUTO-SINGLE:RAUN3:HOSKINS3:1
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2019-069 | FROM->TO | 640227 HOSKINS4 230 996995 HOSKINS T2 _ 230 1 |  | 336 | 0.15559 | 105.26 | P12:345:MEC-NPPD:AUTO-SINGLE:RAUN3:HOSKINS3:1
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2019-070 | FROM->TO | 640227 HOSKINS4 230 996995 HOSKINS T2 _ 230 1 |  | 336 | 0.15559 | 105.26 | P21:345:MEC-NPPD:AUTO-SINGLE:RAUN3:HOSKINS3:1
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2019-070 | FROM->TO | 640227 HOSKINS4 230 996995 HOSKINS T2 _ 230 1 |  | 336 | 0.15559 | 105.26 | P12:345:MEC-NPPD:AUTO-SINGLE:RAUN3:HOSKINS3:1
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2019-073 | FROM->TO | 640227 HOSKINS4 230 996995 HOSKINS T2 _ 230 1 |  | 336 | 0.15559 | 105.26 | P21:345:MEC-NPPD:AUTO-SINGLE:RAUN3:HOSKINS3:1
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2019-073 | FROM->TO | 640227 HOSKINS4 230 996995 HOSKINS T2 _ 230 1 |  | 336 | 0.15559 | 105.26 | P12:345:MEC-NPPD:AUTO-SINGLE:RAUN3:HOSKINS3:1
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2018-065 | FROM->TO | 640227 HOSKINS4 230 996997 HOSKINS T2 _ 230 1 |  | 336 | 0.09556 | 115.93 | P13:115-345:NPPD:HOSKINS3:T4::::
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2018-065 | FROM->TO | 640227 HOSKINS4 230 996997 HOSKINS T2 _ 230 1 |  | 336 | 0.09556 | 115.93 | P13:115-345:NPPD:NUCOR-2:::::
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2018-068 | FROM->TO | 640227 HOSKINS4 230 996997 HOSKINS T2 _ 230 1 |  | 336 | 0.09556 | 115.93 | P13:115-345:NPPD:HOSKINS3:T4::::
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2018-068 | FROM->TO | 640227 HOSKINS4 230 996997 HOSKINS T2 _ 230 1 |  | 336 | 0.09556 | 115.93 | P13:115-345:NPPD:NUCOR-2:::::
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2018-083 | FROM->TO | 640227 HOSKINS4 230 996997 HOSKINS T2 _ 230 1 |  | 336 | 0.11394 | 115.93 | P13:115-345:NPPD:HOSKINS3:T4::::
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2018-083 | FROM->TO | 640227 HOSKINS4 230 996997 HOSKINS T2 _ 230 1 |  | 336 | 0.11394 | 115.93 | P13:115-345:NPPD:NUCOR-2:::::
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2018-131 | FROM->TO | 640227 HOSKINS4 230 996997 HOSKINS T2 _ 230 1 |  | 336 | 0.09556 | 115.93 | P13:115-345:NPPD:HOSKINS3:T4::::
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2018-131 | FROM->TO | 640227 HOSKINS4 230 996997 HOSKINS T2 _ 230 1 |  | 336 | 0.09556 | 115.93 | P13:115-345:NPPD:NUCOR-2:::::
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2018-132 | FROM->TO | 640227 HOSKINS4 230 996997 HOSKINS T2 _ 230 1 |  | 336 | 0.09556 | 115.93 | P13:115-345:NPPD:HOSKINS3:T4::::
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2018-132 | FROM->TO | 640227 HOSKINS4 230 996997 HOSKINS T2 _ 230 1 |  | 336 | 0.09556 | 115.93 | P13:115-345:NPPD:NUCOR-2:::::
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2019-069 | FROM->TO | 640227 HOSKINS4 230 996997 HOSKINS T2 _ 230 1 |  | 336 | 0.11394 | 115.93 | P13:115-345:NPPD:HOSKINS3:T4::::
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2019-069 | FROM->TO | 640227 HOSKINS4 230 996997 HOSKINS T2 _ 230 1 |  | 336 | 0.11394 | 115.93 | P13:115-345:NPPD:NUCOR-2:::::
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2019-070 | FROM->TO | 640227 HOSKINS4 230 996997 HOSKINS T2 _ 230 1 |  | 336 | 0.11394 | 115.93 | P13:115-345:NPPD:HOSKINS3:T4::::
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2019-070 | FROM->TO | 640227 HOSKINS4 230 996997 HOSKINS T2 _ 230 1 |  | 336 | 0.11394 | 115.93 | P13:115-345:NPPD:NUCOR-2:::::
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2019-073 | FROM->TO | 640227 HOSKINS4 230 996997 HOSKINS T2 _ 230 1 |  | 336 | 0.11394 | 115.93 | P13:115-345:NPPD:HOSKINS3:T4::::
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2019-073 | FROM->TO | 640227 HOSKINS4 230 996997 HOSKINS T2 _ 230 1 |  | 336 | 0.11394 | 115.93 | P13:115-345:NPPD:NUCOR-2:::::
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2018-065 | FROM->TO | 640227 HOSKINS4 230 996997 HOSKINS T2 _ 230 1 |  | 336 | 0.13125 | 103.85 | 640342 SHELCRK3 345 763982 G19-069TAP 345 1
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2018-068 | FROM->TO | 640227 HOSKINS4 230 996997 HOSKINS T2 _ 230 1 |  | 336 | 0.13125 | 103.85 | 640342 SHELCRK3 345 763982 G19-069TAP 345 1
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2018-083 | FROM->TO | 640227 HOSKINS4 230 996997 HOSKINS T2 _ 230 1 |  | 336 | 0.15953 | 103.85 | 640342 SHELCRK3 345 763982 G19-069TAP 345 1
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2018-131 | FROM->TO | 640227 HOSKINS4 230 996997 HOSKINS T2 _ 230 1 |  | 336 | 0.13125 | 103.85 | 640342 SHELCRK3 345 763982 G19-069TAP 345 1
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2018-132 | FROM->TO | 640227 HOSKINS4 230 996997 HOSKINS T2 _ 230 1 |  | 336 | 0.13125 | 103.85 | 640342 SHELCRK3 345 763982 G19-069TAP 345 1
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2019-069 | FROM->TO | 640227 HOSKINS4 230 996997 HOSKINS T2 _ 230 1 |  | 336 | 0.15953 | 103.85 | 640342 SHELCRK3 345 763982 G19-069TAP 345 1
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2019-070 | FROM->TO | 640227 HOSKINS4 230 996997 HOSKINS T2 _ 230 1 |  | 336 | 0.15953 | 103.85 | 640342 SHELCRK3 345 763982 G19-069TAP 345 1
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2019-073 | FROM->TO | 640227 HOSKINS4 230 996997 HOSKINS T2 _ 230 1 |  | 336 | 0.15953 | 103.85 | 640342 SHELCRK3 345 763982 G19-069TAP 345 1
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2018-065 | FROM->TO | 640227 HOSKINS4 230 996997 HOSKINS T2 _ 230 1 |  | 336 | 0.13118 | 103.77 | P42:345:NPPD:BKR-CPR-3310:::::
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2018-068 | FROM->TO | 640227 HOSKINS4 230 996997 HOSKINS T2 _ 230 1 |  | 336 | 0.13118 | 103.77 | P42:345:NPPD:BKR-CPR-3310:::::
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2018-083 | FROM->TO | 640227 HOSKINS4 230 996997 HOSKINS T2 _ 230 1 |  | 336 | 0.15947 | 103.77 | P42:345:NPPD:BKR-CPR-3310:::::
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2018-131 | FROM->TO | 640227 HOSKINS4 230 996997 HOSKINS T2 _ 230 1 |  | 336 | 0.13118 | 103.77 | P42:345:NPPD:BKR-CPR-3310:::::
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2018-132 | FROM->TO | 640227 HOSKINS4 230 996997 HOSKINS T2 _ 230 1 |  | 336 | 0.13118 | 103.77 | P42:345:NPPD:BKR-CPR-3310:::::
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2019-069 | FROM->TO | 640227 HOSKINS4 230 996997 HOSKINS T2 _ 230 1 |  | 336 | 0.15947 | 103.77 | P42:345:NPPD:BKR-CPR-3310:::::
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2019-070 | FROM->TO | 640227 HOSKINS4 230 996997 HOSKINS T2 _ 230 1 |  | 336 | 0.15947 | 103.77 | P42:345:NPPD:BKR-CPR-3310:::::
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2019-073 | FROM->TO | 640227 HOSKINS4 230 996997 HOSKINS T2 _ 230 1 |  | 336 | 0.15947 | 103.77 | P42:345:NPPD:BKR-CPR-3310:::::
Thermal | 02ALL | 1 | 02ALL-23SP | GEN-2018-065 | FROM->TO | 640227 HOSKINS4 230 996999 HOSKINS T2 _ 230 1 |  | 336 | 0.09536 | 115.05 | P13:115-345:NPPD:HOSKINS3:T4::::
Thermal | 02ALL | 1 | 02ALL-23SP | GEN-2018-065 | FROM->TO | 640227 HOSKINS4 230 996999 HOSKINS T2 _ 230 1 |  | 336 | 0.09536 | 115.05 | P13:115-345:NPPD:NUCOR-2:::::
Thermal | 02ALL | 1 | 02ALL-23SP | GEN-2018-068 | FROM->TO | 640227 HOSKINS4 230 996999 HOSKINS T2 _ 230 1 |  | 336 | 0.09536 | 115.05 | P13:115-345:NPPD:HOSKINS3:T4::::
Thermal | 02ALL | 1 | 02ALL-23SP | GEN-2018-068 | FROM->TO | 640227 HOSKINS4 230 996999 HOSKINS T2 _ 230 1 |  | 336 | 0.09536 | 115.05 | P13:115-345:NPPD:NUCOR-2:::::
Thermal | 02ALL | 1 | 02ALL-23SP | GEN-2018-083 | FROM->TO | 640227 HOSKINS4 230 996999 HOSKINS T2 _ 230 1 |  | 336 | 0.11376 | 115.05 | P13:115-345:NPPD:HOSKINS3:T4::::
Thermal | 02ALL | 1 | 02ALL-23SP | GEN-2018-083 | FROM->TO | 640227 HOSKINS4 230 996999 HOSKINS T2 _ 230 1 |  | 336 | 0.11376 | 115.05 | P13:115-345:NPPD:NUCOR-2:::::
Thermal | 02ALL | 1 | 02ALL-23SP | GEN-2018-131 | FROM->TO | 640227 HOSKINS4 230 996999 HOSKINS T2 _ 230 1 |  | 336 | 0.09536 | 115.05 | P13:115-345:NPPD:HOSKINS3:T4::::
Thermal | 02ALL | 1 | 02ALL-23SP | GEN-2018-131 | FROM->TO | 640227 HOSKINS4 230 996999 HOSKINS T2 _ 230 1 |  | 336 | 0.09536 | 115.05 | P13:115-345:NPPD:NUCOR-2:::::
Thermal | 02ALL | 1 | 02ALL-23SP | GEN-2018-132 | FROM->TO | 640227 HOSKINS4 230 996999 HOSKINS T2 _ 230 1 |  | 336 | 0.09536 | 115.05 | P13:115-345:NPPD:HOSKINS3:T4::::
Thermal | 02ALL | 1 | 02ALL-23SP | GEN-2018-132 | FROM->TO | 640227 HOSKINS4 230 996999 HOSKINS T2 _ 230 1 |  | 336 | 0.09536 | 115.05 | P13:115-345:NPPD:NUCOR-2:::::
Thermal | 02ALL | 1 | 02ALL-23SP | GEN-2019-069 | FROM->TO | 640227 HOSKINS4 230 996999 HOSKINS T2 _ 230 1 |  | 336 | 0.11376 | 115.05 | P13:115-345:NPPD:HOSKINS3:T4::::
Thermal | 02ALL | 1 | 02ALL-23SP | GEN-2019-069 | FROM->TO | 640227 HOSKINS4 230 996999 HOSKINS T2 _ 230 1 |  | 336 | 0.11376 | 115.05 | P13:115-345:NPPD:NUCOR-2:::::
Thermal | 02ALL | 1 | 02ALL-23SP | GEN-2019-070 | FROM->TO | 640227 HOSKINS4 230 996999 HOSKINS T2 _ 230 1 |  | 336 | 0.11376 | 115.05 | P13:115-345:NPPD:HOSKINS3:T4::::
Thermal | 02ALL | 1 | 02ALL-23SP | GEN-2019-070 | FROM->TO | 640227 HOSKINS4 230 996999 HOSKINS T2 _ 230 1 |  | 336 | 0.11376 | 115.05 | P13:115-345:NPPD:NUCOR-2:::::
Thermal | 02ALL | 1 | 02ALL-23SP | GEN-2019-073 | FROM->TO | 640227 HOSKINS4 230 996999 HOSKINS T2 _ 230 1 |  | 336 | 0.11376 | 115.05 | P13:115-345:NPPD:HOSKINS3:T4::::
Thermal | 02ALL | 1 | 02ALL-23SP | GEN-2019-073 | FROM->TO | 640227 HOSKINS4 230 996999 HOSKINS T2 _ 230 1 |  | 336 | 0.11376 | 115.05 | P13:115-345:NPPD:NUCOR-2:::::
Thermal | 02ALL | 1 | 02ALL-23SP | GEN-2018-065 | FROM->TO | 640227 HOSKINS4 230 996999 HOSKINS T2 _ 230 1 |  | 336 | 0.13133 | 103.24 | 640342 SHELCRK3 345 763982 G19-069TAP 345 1
Thermal | 02ALL | 1 | 02ALL-23SP | GEN-2018-068 | FROM->TO | 640227 HOSKINS4 230 996999 HOSKINS T2 _ 230 1 |  | 336 | 0.13133 | 103.24 | 640342 SHELCRK3 345 763982 G19-069TAP 345 1
Thermal | 02ALL | 1 | 02ALL-23SP | GEN-2018-083 | FROM->TO | 640227 HOSKINS4 230 996999 HOSKINS T2 _ 230 1 |  | 336 | 0.15956 | 103.24 | 640342 SHELCRK3 345 763982 G19-069TAP 345 1
Thermal | 02ALL | 1 | 02ALL-23SP | GEN-2018-131 | FROM->TO | 640227 HOSKINS4 230 996999 HOSKINS T2 _ 230 1 |  | 336 | 0.13133 | 103.24 | 640342 SHELCRK3 345 763982 G19-069TAP 345 1
Thermal | 02ALL | 1 | 02ALL-23SP | GEN-2018-132 | FROM->TO | 640227 HOSKINS4 230 996999 HOSKINS T2 _ 230 1 |  | 336 | 0.13133 | 103.24 | 640342 SHELCRK3 345 763982 G19-069TAP 345 1
Thermal | 02ALL | 1 | 02ALL-23SP | GEN-2019-069 | FROM->TO | 640227 HOSKINS4 230 996999 HOSKINS T2 _ 230 1 |  | 336 | 0.15956 | 103.24 | 640342 SHELCRK3 345 763982 G19-069TAP 345 1
Thermal | 02ALL | 1 | 02ALL-23SP | GEN-2019-070 | FROM->TO | 640227 HOSKINS4 230 996999 HOSKINS T2 _ 230 1 |  | 336 | 0.15956 | 103.24 | 640342 SHELCRK3 345 763982 G19-069TAP 345 1
Thermal | 02ALL | 1 | 02ALL-23SP | GEN-2019-073 | FROM->TO | 640227 HOSKINS4 230 996999 HOSKINS T2 _ 230 1 |  | 336 | 0.15956 | 103.24 | 640342 SHELCRK3 345 763982 G19-069TAP 345 1
Thermal | 02ALL | 1 | 02ALL-23SP | GEN-2018-065 | FROM->TO | 640227 HOSKINS4 230 996999 HOSKINS T2 _ 230 1 |  | 336 | 0.13126 | 103.17 | P42:345:NPPD:BKR-CPR-3310:::::
Thermal | 02ALL | 1 | 02ALL-23SP | GEN-2018-068 | FROM->TO | 640227 HOSKINS4 230 996999 HOSKINS T2 _ 230 1 |  | 336 | 0.13126 | 103.17 | P42:345:NPPD:BKR-CPR-3310:::::
Thermal | 02ALL | 1 | 02ALL-23SP | GEN-2018-083 | FROM->TO | 640227 HOSKINS4 230 996999 HOSKINS T2 _ 230 1 |  | 336 | 0.1595 | 103.17 | P42:345:NPPD:BKR-CPR-3310:::::
Thermal | 02ALL | 1 | 02ALL-23SP | GEN-2018-131 | FROM->TO | 640227 HOSKINS4 230 996999 HOSKINS T2 _ 230 1 |  | 336 | 0.13126 | 103.17 | P42:345:NPPD:BKR-CPR-3310:::::
Thermal | 02ALL | 1 | 02ALL-23SP | GEN-2018-132 | FROM->TO | 640227 HOSKINS4 230 996999 HOSKINS T2 _ 230 1 |  | 336 | 0.13126 | 103.17 | P42:345:NPPD:BKR-CPR-3310:::::
Thermal | 02ALL | 1 | 02ALL-23SP | GEN-2019-069 | FROM->TO | 640227 HOSKINS4 230 996999 HOSKINS T2 _ 230 1 |  | 336 | 0.1595 | 103.17 | P42:345:NPPD:BKR-CPR-3310:::::
Thermal | 02ALL | 1 | 02ALL-23SP | GEN-2019-070 | FROM->TO | 640227 HOSKINS4 230 996999 HOSKINS T2 _ 230 1 |  | 336 | 0.1595 | 103.17 | P42:345:NPPD:BKR-CPR-3310:::::
Thermal | 02ALL | 1 | 02ALL-23SP | GEN-2019-073 | FROM->TO | 640227 HOSKINS4 230 996999 HOSKINS T2 _ 230 1 |  | 336 | 0.1595 | 103.17 | P42:345:NPPD:BKR-CPR-3310:::::
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2018-065 | FROM->TO | 640228 HOSKINS7 115 996993 HOSKN T4 _1 115 1 |  | 336 | 0.07734 | 111.2 | P13:230-345:NPPD:HOSKINS3:T2::::
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2018-065 | FROM->TO | 640228 HOSKINS7 115 996993 HOSKN T4 _1 115 1 |  | 336 | 0.07734 | 111.2 | P13:230-345:NPPD:NUCOR-1:::::
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2018-068 | FROM->TO | 640228 HOSKINS7 115 996993 HOSKN T4 _1 115 1 |  | 336 | 0.07734 | 111.2 | P13:230-345:NPPD:HOSKINS3:T2::::
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2018-068 | FROM->TO | 640228 HOSKINS7 115 996993 HOSKN T4 _1 115 1 |  | 336 | 0.07734 | 111.2 | P13:230-345:NPPD:NUCOR-1:::::
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2018-083 | FROM->TO | 640228 HOSKINS7 115 996993 HOSKN T4 _1 115 1 |  | 336 | 0.10373 | 111.2 | P13:230-345:NPPD:HOSKINS3:T2::::
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2018-083 | FROM->TO | 640228 HOSKINS7 115 996993 HOSKN T4 _1 115 1 |  | 336 | 0.10373 | 111.2 | P13:230-345:NPPD:NUCOR-1:::::
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2018-131 | FROM->TO | 640228 HOSKINS7 115 996993 HOSKN T4 _1 115 1 |  | 336 | 0.07734 | 111.2 | P13:230-345:NPPD:HOSKINS3:T2::::
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2018-131 | FROM->TO | 640228 HOSKINS7 115 996993 HOSKN T4 _1 115 1 |  | 336 | 0.07734 | 111.2 | P13:230-345:NPPD:NUCOR-1:::::
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2018-132 | FROM->TO | 640228 HOSKINS7 115 996993 HOSKN T4 _1 115 1 |  | 336 | 0.07734 | 111.2 | P13:230-345:NPPD:HOSKINS3:T2::::
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2018-132 | FROM->TO | 640228 HOSKINS7 115 996993 HOSKN T4 _1 115 1 |  | 336 | 0.07734 | 111.2 | P13:230-345:NPPD:NUCOR-1:::::
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2019-069 | FROM->TO | 640228 HOSKINS7 115 996993 HOSKN T4 _1 115 1 |  | 336 | 0.10373 | 111.2 | P13:230-345:NPPD:HOSKINS3:T2::::
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2019-069 | FROM->TO | 640228 HOSKINS7 115 996993 HOSKN T4 _1 115 1 |  | 336 | 0.10373 | 111.2 | P13:230-345:NPPD:NUCOR-1:::::
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2019-070 | FROM->TO | 640228 HOSKINS7 115 996993 HOSKN T4 _1 115 1 |  | 336 | 0.10373 | 111.2 | P13:230-345:NPPD:HOSKINS3:T2::::
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2019-070 | FROM->TO | 640228 HOSKINS7 115 996993 HOSKN T4 _1 115 1 |  | 336 | 0.10373 | 111.2 | P13:230-345:NPPD:NUCOR-1:::::
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2019-073 | FROM->TO | 640228 HOSKINS7 115 996993 HOSKN T4 _1 115 1 |  | 336 | 0.10373 | 111.2 | P13:230-345:NPPD:HOSKINS3:T2::::
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2019-073 | FROM->TO | 640228 HOSKINS7 115 996993 HOSKN T4 _1 115 1 |  | 336 | 0.10373 | 111.2 | P13:230-345:NPPD:NUCOR-1:::::
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2018-065 | FROM->TO | 640228 HOSKINS7 115 996995 HOSKN T4 _1 115 1 |  | 336 | 0.07681 | 111.77 | P13:230-345:NPPD:HOSKINS3:T2::::
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2018-065 | FROM->TO | 640228 HOSKINS7 115 996995 HOSKN T4 _1 115 1 |  | 336 | 0.07681 | 111.77 | P13:230-345:NPPD:NUCOR-1:::::
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2018-068 | FROM->TO | 640228 HOSKINS7 115 996995 HOSKN T4 _1 115 1 |  | 336 | 0.07681 | 111.77 | P13:230-345:NPPD:HOSKINS3:T2::::
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2018-068 | FROM->TO | 640228 HOSKINS7 115 996995 HOSKN T4 _1 115 1 |  | 336 | 0.07681 | 111.77 | P13:230-345:NPPD:NUCOR-1:::::
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2018-083 | FROM->TO | 640228 HOSKINS7 115 996995 HOSKN T4 _1 115 1 |  | 336 | 0.1032 | 111.77 | P13:230-345:NPPD:HOSKINS3:T2::::
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2018-083 | FROM->TO | 640228 HOSKINS7 115 996995 HOSKN T4 _1 115 1 |  | 336 | 0.1032 | 111.77 | P13:230-345:NPPD:NUCOR-1:::::
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2018-131 | FROM->TO | 640228 HOSKINS7 115 996995 HOSKN T4 _1 115 1 |  | 336 | 0.07681 | 111.77 | P13:230-345:NPPD:HOSKINS3:T2::::
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2018-131 | FROM->TO | 640228 HOSKINS7 115 996995 HOSKN T4 _1 115 1 |  | 336 | 0.07681 | 111.77 | P13:230-345:NPPD:NUCOR-1:::::
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2018-132 | FROM->TO | 640228 HOSKINS7 115 996995 HOSKN T4 _1 115 1 |  | 336 | 0.07681 | 111.77 | P13:230-345:NPPD:HOSKINS3:T2::::
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2018-132 | FROM->TO | 640228 HOSKINS7 115 996995 HOSKN T4 _1 115 1 |  | 336 | 0.07681 | 111.77 | P13:230-345:NPPD:NUCOR-1:::::
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2019-069 | FROM->TO | 640228 HOSKINS7 115 996995 HOSKN T4 _1 115 1 |  | 336 | 0.1032 | 111.77 | P13:230-345:NPPD:HOSKINS3:T2::::
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2019-069 | FROM->TO | 640228 HOSKINS7 115 996995 HOSKN T4 _1 115 1 |  | 336 | 0.1032 | 111.77 | P13:230-345:NPPD:NUCOR-1:::::
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2019-070 | FROM->TO | 640228 HOSKINS7 115 996995 HOSKN T4 _1 115 1 |  | 336 | 0.1032 | 111.77 | P13:230-345:NPPD:HOSKINS3:T2::::
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2019-070 | FROM->TO | 640228 HOSKINS7 115 996995 HOSKN T4 _1 115 1 |  | 336 | 0.1032 | 111.77 | P13:230-345:NPPD:NUCOR-1:::::
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2019-073 | FROM->TO | 640228 HOSKINS7 115 996995 HOSKN T4 _1 115 1 |  | 336 | 0.1032 | 111.77 | P13:230-345:NPPD:HOSKINS3:T2::::
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2019-073 | FROM->TO | 640228 HOSKINS7 115 996995 HOSKN T4 _1 115 1 |  | 336 | 0.1032 | 111.77 | P13:230-345:NPPD:NUCOR-1:::::
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2018-065 | FROM->TO | 640228 HOSKINS7 115 996995 HOSKN T4 _1 115 1 |  | 336 | 0.0996 | 101.75 | P13:115-345:NPPD:ANTELOPE:T1::::
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2018-068 | FROM->TO | 640228 HOSKINS7 115 996995 HOSKN T4 _1 115 1 |  | 336 | 0.0996 | 101.75 | P13:115-345:NPPD:ANTELOPE:T1::::
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2018-083 | FROM->TO | 640228 HOSKINS7 115 996995 HOSKN T4 _1 115 1 |  | 336 | 0.07967 | 101.75 | P13:115-345:NPPD:ANTELOPE:T1::::
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2018-131 | FROM->TO | 640228 HOSKINS7 115 996995 HOSKN T4 _1 115 1 |  | 336 | 0.0996 | 101.75 | P13:115-345:NPPD:ANTELOPE:T1::::
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2018-132 | FROM->TO | 640228 HOSKINS7 115 996995 HOSKN T4 _1 115 1 |  | 336 | 0.0996 | 101.75 | P13:115-345:NPPD:ANTELOPE:T1::::
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2019-069 | FROM->TO | 640228 HOSKINS7 115 996995 HOSKN T4 _1 115 1 |  | 336 | 0.07967 | 101.75 | P13:115-345:NPPD:ANTELOPE:T1::::
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2019-070 | FROM->TO | 640228 HOSKINS7 115 996995 HOSKN T4 _1 115 1 |  | 336 | 0.07967 | 101.75 | P13:115-345:NPPD:ANTELOPE:T1::::
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2019-073 | FROM->TO | 640228 HOSKINS7 115 996995 HOSKN T4 _1 115 1 |  | 336 | 0.07967 | 101.75 | P13:115-345:NPPD:ANTELOPE:T1::::
Thermal | 02ALL | 1 | 02ALL-23SP | GEN-2018-065 | FROM->TO | 640228 HOSKINS7 115 996997 HOSKN T4 _1 115 1 |  | 336 | 0.07662 | 111.38 | P13:230-345:NPPD:NUCOR-1:::::
Thermal | 02ALL | 1 | 02ALL-23SP | GEN-2018-065 | FROM->TO | 640228 HOSKINS7 115 996997 HOSKN T4 _1 115 1 |  | 336 | 0.07662 | 111.38 | P13:230-345:NPPD:HOSKINS3:T2::::
Thermal | 02ALL | 1 | 02ALL-23SP | GEN-2018-068 | FROM->TO | 640228 HOSKINS7 115 996997 HOSKN T4 _1 115 1 |  | 336 | 0.07662 | 111.38 | P13:230-345:NPPD:NUCOR-1:::::
Thermal | 02ALL | 1 | 02ALL-23SP | GEN-2018-068 | FROM->TO | 640228 HOSKINS7 115 996997 HOSKN T4 _1 115 1 |  | 336 | 0.07662 | 111.38 | P13:230-345:NPPD:HOSKINS3:T2::::
Thermal | 02ALL | 1 | 02ALL-23SP | GEN-2018-083 | FROM->TO | 640228 HOSKINS7 115 996997 HOSKN T4 _1 115 1 |  | 336 | 0.10305 | 111.38 | P13:230-345:NPPD:NUCOR-1:::::
Thermal | 02ALL | 1 | 02ALL-23SP | GEN-2018-083 | FROM->TO | 640228 HOSKINS7 115 996997 HOSKN T4 _1 115 1 |  | 336 | 0.10305 | 111.38 | P13:230-345:NPPD:HOSKINS3:T2::::
Thermal | 02ALL | 1 | 02ALL-23SP | GEN-2018-131 | FROM->TO | 640228 HOSKINS7 115 996997 HOSKN T4 _1 115 1 |  | 336 | 0.07662 | 111.38 | P13:230-345:NPPD:NUCOR-1:::::
Thermal | 02ALL | 1 | 02ALL-23SP | GEN-2018-131 | FROM->TO | 640228 HOSKINS7 115 996997 HOSKN T4 _1 115 1 |  | 336 | 0.07662 | 111.38 | P13:230-345:NPPD:HOSKINS3:T2::::
Thermal | 02ALL | 1 | 02ALL-23SP | GEN-2018-132 | FROM->TO | 640228 HOSKINS7 115 996997 HOSKN T4 _1 115 1 |  | 336 | 0.07662 | 111.38 | P13:230-345:NPPD:NUCOR-1:::::
Thermal | 02ALL | 1 | 02ALL-23SP | GEN-2018-132 | FROM->TO | 640228 HOSKINS7 115 996997 HOSKN T4 _1 115 1 |  | 336 | 0.07662 | 111.38 | P13:230-345:NPPD:HOSKINS3:T2::::
Thermal | 02ALL | 1 | 02ALL-23SP | GEN-2019-069 | FROM->TO | 640228 HOSKINS7 115 996997 HOSKN T4 _1 115 1 |  | 336 | 0.10305 | 111.38 | P13:230-345:NPPD:NUCOR-1:::::
Thermal | 02ALL | 1 | 02ALL-23SP | GEN-2019-069 | FROM->TO | 640228 HOSKINS7 115 996997 HOSKN T4 _1 115 1 |  | 336 | 0.10305 | 111.38 | P13:230-345:NPPD:HOSKINS3:T2::::
Thermal | 02ALL | 1 | 02ALL-23SP | GEN-2019-070 | FROM->TO | 640228 HOSKINS7 115 996997 HOSKN T4 _1 115 1 |  | 336 | 0.10305 | 111.38 | P13:230-345:NPPD:NUCOR-1:::::
Thermal | 02ALL | 1 | 02ALL-23SP | GEN-2019-070 | FROM->TO | 640228 HOSKINS7 115 996997 HOSKN T4 _1 115 1 |  | 336 | 0.10305 | 111.38 | P13:230-345:NPPD:HOSKINS3:T2::::
Thermal | 02ALL | 1 | 02ALL-23SP | GEN-2019-073 | FROM->TO | 640228 HOSKINS7 115 996997 HOSKN T4 _1 115 1 |  | 336 | 0.10305 | 111.38 | P13:230-345:NPPD:NUCOR-1:::::
Thermal | 02ALL | 1 | 02ALL-23SP | GEN-2019-073 | FROM->TO | 640228 HOSKINS7 115 996997 HOSKN T4 _1 115 1 |  | 336 | 0.10305 | 111.38 | P13:230-345:NPPD:HOSKINS3:T2::::
Thermal | 02ALL | 1 | 02ALL-23SP | GEN-2018-065 | FROM->TO | 640228 HOSKINS7 115 996997 HOSKN T4 _1 115 1 |  | 336 | 0.09938 | 101.98 | P13:115-345:NPPD:ANTELOPE:T1::::
Thermal | 02ALL | 1 | 02ALL-23SP | GEN-2018-068 | FROM->TO | 640228 HOSKINS7 115 996997 HOSKN T4 _1 115 1 |  | 336 | 0.09938 | 101.98 | P13:115-345:NPPD:ANTELOPE:T1::::
Thermal | 02ALL | 1 | 02ALL-23SP | GEN-2018-083 | FROM->TO | 640228 HOSKINS7 115 996997 HOSKN T4 _1 115 1 |  | 336 | 0.07948 | 101.98 | P13:115-345:NPPD:ANTELOPE:T1::::
Thermal | 02ALL | 1 | 02ALL-23SP | GEN-2018-131 | FROM->TO | 640228 HOSKINS7 115 996997 HOSKN T4 _1 115 1 |  | 336 | 0.09938 | 101.98 | P13:115-345:NPPD:ANTELOPE:T1::::
Thermal | 02ALL | 1 | 02ALL-23SP | GEN-2018-132 | FROM->TO | 640228 HOSKINS7 115 996997 HOSKN T4 _1 115 1 |  | 336 | 0.09938 | 101.98 | P13:115-345:NPPD:ANTELOPE:T1::::
Thermal | 02ALL | 1 | 02ALL-23SP | GEN-2019-069 | FROM->TO | 640228 HOSKINS7 115 996997 HOSKN T4 _1 115 1 |  | 336 | 0.07948 | 101.98 | P13:115-345:NPPD:ANTELOPE:T1::::
Thermal | 02ALL | 1 | 02ALL-23SP | GEN-2019-070 | FROM->TO | 640228 HOSKINS7 115 996997 HOSKN T4 _1 115 1 |  | 336 | 0.07948 | 101.98 | P13:115-345:NPPD:ANTELOPE:T1::::
Thermal | 02ALL | 1 | 02ALL-23SP | GEN-2019-073 | FROM->TO | 640228 HOSKINS7 115 996997 HOSKN T4 _1 115 1 |  | 336 | 0.07948 | 101.98 | P13:115-345:NPPD:ANTELOPE:T1::::
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2019-029 | FROM->TO | 640252 KEYSTON3 345 996983 KEYSTONE T1 115 1 |  | 336 | 0.41755 | 145.29 | 640183 GENTLMN3 345 640252 KEYSTON3 345 1
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2019-033 | FROM->TO | 640252 KEYSTON3 345 996983 KEYSTONE T1 115 1 |  | 336 | 0.41755 | 145.29 | 640183 GENTLMN3 345 640252 KEYSTON3 345 1
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2019-029 | FROM->TO | 640252 KEYSTON3 345 996985 KEYSTONE T1 115 1 |  | 336 | 0.41897 | 147.2 | 640183 GENTLMN3 345 640252 KEYSTON3 345 1
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2019-033 | FROM->TO | 640252 KEYSTON3 345 996985 KEYSTONE T1 115 1 |  | 336 | 0.41897 | 147.2 | 640183 GENTLMN3 345 640252 KEYSTON3 345 1
Thermal | 02ALL | 1 | 02ALL-23SP | GEN-2019-029 | FROM->TO | 640252 KEYSTON3 345 996987 KEYSTONE T1 115 1 |  | 336 | 0.41677 | 152.45 | 640183 GENTLMN3 345 640252 KEYSTON3 345 1
Thermal | 02ALL | 1 | 02ALL-23SP | GEN-2019-033 | FROM->TO | 640252 KEYSTON3 345 996987 KEYSTONE T1 115 1 |  | 336 | 0.41677 | 152.45 | 640183 GENTLMN3 345 640252 KEYSTON3 345 1
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2019-029 | FROM->TO | 640253 KEYSTON7 115 640304 OGALALANPPD7 115 1 |  | 400 | 0.41897 | 129.07 | 640183 GENTLMN3 345 640252 KEYSTON3 345 1
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2019-033 | FROM->TO | 640253 KEYSTON7 115 640304 OGALALANPPD7 115 1 |  | 400 | 0.41897 | 129.07 | 640183 GENTLMN3 345 640252 KEYSTON3 345 1
Thermal | 02ALL | 1 | 02ALL-23SP | GEN-2019-029 | FROM->TO | 640253 KEYSTON7 115 640304 OGALALANPPD7 115 1 |  | 400 | 0.41677 | 121.3 | 640183 GENTLMN3 345 640252 KEYSTON3 345 1
Thermal | 02ALL | 1 | 02ALL-23SP | GEN-2019-033 | FROM->TO | 640253 KEYSTON7 115 640304 OGALALANPPD7 115 1 |  | 400 | 0.41677 | 121.3 | 640183 GENTLMN3 345 640252 KEYSTON3 345 1
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2019-029 | FROM->TO | 640253 KEYSTON7 115 640304 OGALALANPPD7 115 1 |  | 400 | 0.41755 | 114.64 | 640183 GENTLMN3 345 640252 KEYSTON3 345 1
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2019-033 | FROM->TO | 640253 KEYSTON7 115 640304 OGALALANPPD7 115 1 |  | 400 | 0.41755 | 114.64 | 640183 GENTLMN3 345 640252 KEYSTON3 345 1
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2019-029 | FROM->TO | 640253 KEYSTON7 115 996983 KEYSTONE T1 115 1 |  | 336 | 0.41755 | 141.62 | 640183 GENTLMN3 345 640252 KEYSTON3 345 1
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2019-033 | FROM->TO | 640253 KEYSTON7 115 996983 KEYSTONE T1 115 1 |  | 336 | 0.41755 | 141.62 | 640183 GENTLMN3 345 640252 KEYSTON3 345 1
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2019-029 | FROM->TO | 640253 KEYSTON7 115 996985 KEYSTONE T1 115 1 |  | 336 | 0.41897 | 144.44 | 640183 GENTLMN3 345 640252 KEYSTON3 345 1
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2019-033 | FROM->TO | 640253 KEYSTON7 115 996985 KEYSTONE T1 115 1 |  | 336 | 0.41897 | 144.44 | 640183 GENTLMN3 345 640252 KEYSTON3 345 1
Thermal | 02ALL | 1 | 02ALL-23SP | GEN-2019-029 | FROM->TO | 640253 KEYSTON7 115 996987 KEYSTONE T1 115 1 |  | 336 | 0.41677 | 149.73 | 640183 GENTLMN3 345 640252 KEYSTON3 345 1
Thermal | 02ALL | 1 | 02ALL-23SP | GEN-2019-033 | FROM->TO | 640253 KEYSTON7 115 996987 KEYSTONE T1 115 1 |  | 336 | 0.41677 | 149.73 | 640183 GENTLMN3 345 640252 KEYSTON3 345 1
Thermal | 02ALL | 1 | 02ALL-23SP | GEN-2019-029 | FROM->TO | 640287 N.PLATT7 115 640365 STOCKVL7 115 1 |  | 137 | 0.05049 | 112.07 | 640183 GENTLMN3 345 640325 REDWILO3 345 1
Thermal | 02ALL | 1 | 02ALL-23SP | GEN-2019-033 | FROM->TO | 640287 N.PLATT7 115 640365 STOCKVL7 115 1 |  | 137 | 0.05049 | 112.07 | 640183 GENTLMN3 345 640325 REDWILO3 345 1
Thermal | 02ALL | 1 | 02ALL-23SP | GEN-2018-065 | FROM->TO | 640293 NELIGH 7 115 640444 PETERSBRG.N7 115 1 |  | 137 | 0.23289 | 113.7 | 640226 HOSKINS3 345 640520 ANTELOPE 3 345 1
Thermal | 02ALL | 1 | 02ALL-23SP | GEN-2018-068 | FROM->TO | 640293 NELIGH 7 115 640444 PETERSBRG.N7 115 1 |  | 137 | 0.23289 | 113.7 | 640226 HOSKINS3 345 640520 ANTELOPE 3 345 1
Thermal | 02ALL | 1 | 02ALL-23SP | GEN-2018-131 | FROM->TO | 640293 NELIGH 7 115 640444 PETERSBRG.N7 115 1 |  | 137 | 0.23289 | 113.7 | 640226 HOSKINS3 345 640520 ANTELOPE 3 345 1
Thermal | 02ALL | 1 | 02ALL-23SP | GEN-2018-132 | FROM->TO | 640293 NELIGH 7 115 640444 PETERSBRG.N7 115 1 |  | 137 | 0.23289 | 113.7 | 640226 HOSKINS3 345 640520 ANTELOPE 3 345 1
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2018-065 | FROM->TO | 640293 NELIGH 7 115 640444 PETERSBRG.N7 115 1 |  | 137 | 0.23149 | 113.48 | 640226 HOSKINS3 345 640520 ANTELOPE 3 345 1
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2018-068 | FROM->TO | 640293 NELIGH 7 115 640444 PETERSBRG.N7 115 1 |  | 137 | 0.23149 | 113.48 | 640226 HOSKINS3 345 640520 ANTELOPE 3 345 1
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2018-131 | FROM->TO | 640293 NELIGH 7 115 640444 PETERSBRG.N7 115 1 |  | 137 | 0.23149 | 113.48 | 640226 HOSKINS3 345 640520 ANTELOPE 3 345 1
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2018-132 | FROM->TO | 640293 NELIGH 7 115 640444 PETERSBRG.N7 115 1 |  | 137 | 0.23149 | 113.48 | 640226 HOSKINS3 345 640520 ANTELOPE 3 345 1
Thermal | 02ALL | 1 | 02ALL-23SP | GEN-2018-065 | FROM->TO | 640293 NELIGH 7 115 640444 PETERSBRG.N7 115 1 |  | 137 | 0.23857 | 108.74 | P42:345:NPPD:BKR-MOR-3306:::::
Thermal | 02ALL | 1 | 02ALL-23SP | GEN-2018-068 | FROM->TO | 640293 NELIGH 7 115 640444 PETERSBRG.N7 115 1 |  | 137 | 0.23857 | 108.74 | P42:345:NPPD:BKR-MOR-3306:::::
Thermal | 02ALL | 1 | 02ALL-23SP | GEN-2018-131 | FROM->TO | 640293 NELIGH 7 115 640444 PETERSBRG.N7 115 1 |  | 137 | 0.23857 | 108.74 | P42:345:NPPD:BKR-MOR-3306:::::
Thermal | 02ALL | 1 | 02ALL-23SP | GEN-2018-132 | FROM->TO | 640293 NELIGH 7 115 640444 PETERSBRG.N7 115 1 |  | 137 | 0.23857 | 108.74 | P42:345:NPPD:BKR-MOR-3306:::::
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2018-065 | FROM->TO | 640293 NELIGH 7 115 640444 PETERSBRG.N7 115 1 |  | 137 | 0.23706 | 108.21 | P42:345:NPPD:BKR-MOR-3306:::::
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2018-068 | FROM->TO | 640293 NELIGH 7 115 640444 PETERSBRG.N7 115 1 |  | 137 | 0.23706 | 108.21 | P42:345:NPPD:BKR-MOR-3306:::::
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2018-131 | FROM->TO | 640293 NELIGH 7 115 640444 PETERSBRG.N7 115 1 |  | 137 | 0.23706 | 108.21 | P42:345:NPPD:BKR-MOR-3306:::::
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2018-132 | FROM->TO | 640293 NELIGH 7 115 640444 PETERSBRG.N7 115 1 |  | 137 | 0.23706 | 108.21 | P42:345:NPPD:BKR-MOR-3306:::::
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2018-065 | FROM->TO | 640318 PETRSBG7 115 640444 PETERSBRG.N7 115 Z1 |  | 137 | 0.22947 | 137.74 | 640226 HOSKINS3 345 640520 ANTELOPE 3 345 1
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2018-068 | FROM->TO | 640318 PETRSBG7 115 640444 PETERSBRG.N7 115 Z1 |  | 137 | 0.22947 | 137.74 | 640226 HOSKINS3 345 640520 ANTELOPE 3 345 1
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2018-131 | FROM->TO | 640318 PETRSBG7 115 640444 PETERSBRG.N7 115 Z1 |  | 137 | 0.22947 | 137.74 | 640226 HOSKINS3 345 640520 ANTELOPE 3 345 1
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2018-132 | FROM->TO | 640318 PETRSBG7 115 640444 PETERSBRG.N7 115 Z1 |  | 137 | 0.22947 | 137.74 | 640226 HOSKINS3 345 640520 ANTELOPE 3 345 1
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2018-065 | FROM->TO | 640318 PETRSBG7 115 640444 PETERSBRG.N7 115 Z1 |  | 137 | 0.23498 | 135.37 | P42:345:NPPD:BKR-MOR-3306:::::
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2018-068 | FROM->TO | 640318 PETRSBG7 115 640444 PETERSBRG.N7 115 Z1 |  | 137 | 0.23498 | 135.37 | P42:345:NPPD:BKR-MOR-3306:::::
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2018-131 | FROM->TO | 640318 PETRSBG7 115 640444 PETERSBRG.N7 115 Z1 |  | 137 | 0.23498 | 135.37 | P42:345:NPPD:BKR-MOR-3306:::::
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2018-132 | FROM->TO | 640318 PETRSBG7 115 640444 PETERSBRG.N7 115 Z1 |  | 137 | 0.23498 | 135.37 | P42:345:NPPD:BKR-MOR-3306:::::
Thermal | 02ALL | 1 | 02ALL-23SP | GEN-2018-065 | FROM->TO | 640318 PETRSBG7 115 640444 PETERSBRG.N7 115 Z1 |  | 137 | 0.23224 | 121.34 | 640226 HOSKINS3 345 640520 ANTELOPE 3 345 1
Thermal | 02ALL | 1 | 02ALL-23SP | GEN-2018-068 | FROM->TO | 640318 PETRSBG7 115 640444 PETERSBRG.N7 115 Z1 |  | 137 | 0.23224 | 121.34 | 640226 HOSKINS3 345 640520 ANTELOPE 3 345 1
Thermal | 02ALL | 1 | 02ALL-23SP | GEN-2018-131 | FROM->TO | 640318 PETRSBG7 115 640444 PETERSBRG.N7 115 Z1 |  | 137 | 0.23224 | 121.34 | 640226 HOSKINS3 345 640520 ANTELOPE 3 345 1
Thermal | 02ALL | 1 | 02ALL-23SP | GEN-2018-132 | FROM->TO | 640318 PETRSBG7 115 640444 PETERSBRG.N7 115 Z1 |  | 137 | 0.23224 | 121.34 | 640226 HOSKINS3 345 640520 ANTELOPE 3 345 1
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2018-065 | FROM->TO | 640318 PETRSBG7 115 640444 PETERSBRG.N7 115 Z1 |  | 137 | 0.23087 | 120.9 | 640226 HOSKINS3 345 640520 ANTELOPE 3 345 1
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2018-068 | FROM->TO | 640318 PETRSBG7 115 640444 PETERSBRG.N7 115 Z1 |  | 137 | 0.23087 | 120.9 | 640226 HOSKINS3 345 640520 ANTELOPE 3 345 1
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2018-131 | FROM->TO | 640318 PETRSBG7 115 640444 PETERSBRG.N7 115 Z1 |  | 137 | 0.23087 | 120.9 | 640226 HOSKINS3 345 640520 ANTELOPE 3 345 1
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2018-132 | FROM->TO | 640318 PETRSBG7 115 640444 PETERSBRG.N7 115 Z1 |  | 137 | 0.23087 | 120.9 | 640226 HOSKINS3 345 640520 ANTELOPE 3 345 1
Thermal | 02ALL | 1 | 02ALL-23SP | GEN-2018-065 | FROM->TO | 640318 PETRSBG7 115 640444 PETERSBRG.N7 115 Z1 |  | 137 | 0.23793 | 116.97 | P42:345:NPPD:BKR-MOR-3306:::::
Thermal | 02ALL | 1 | 02ALL-23SP | GEN-2018-068 | FROM->TO | 640318 PETRSBG7 115 640444 PETERSBRG.N7 115 Z1 |  | 137 | 0.23793 | 116.97 | P42:345:NPPD:BKR-MOR-3306:::::
Thermal | 02ALL | 1 | 02ALL-23SP | GEN-2018-131 | FROM->TO | 640318 PETRSBG7 115 640444 PETERSBRG.N7 115 Z1 |  | 137 | 0.23793 | 116.97 | P42:345:NPPD:BKR-MOR-3306:::::
Thermal | 02ALL | 1 | 02ALL-23SP | GEN-2018-132 | FROM->TO | 640318 PETRSBG7 115 640444 PETERSBRG.N7 115 Z1 |  | 137 | 0.23793 | 116.97 | P42:345:NPPD:BKR-MOR-3306:::::
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2018-065 | FROM->TO | 640318 PETRSBG7 115 640444 PETERSBRG.N7 115 Z1 |  | 137 | 0.23644 | 116.28 | P42:345:NPPD:BKR-MOR-3306:::::
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2018-068 | FROM->TO | 640318 PETRSBG7 115 640444 PETERSBRG.N7 115 Z1 |  | 137 | 0.23644 | 116.28 | P42:345:NPPD:BKR-MOR-3306:::::
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2018-131 | FROM->TO | 640318 PETRSBG7 115 640444 PETERSBRG.N7 115 Z1 |  | 137 | 0.23644 | 116.28 | P42:345:NPPD:BKR-MOR-3306:::::
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2018-132 | FROM->TO | 640318 PETRSBG7 115 640444 PETERSBRG.N7 115 Z1 |  | 137 | 0.23644 | 116.28 | P42:345:NPPD:BKR-MOR-3306:::::
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2018-125 | FROM->TO | 640325 REDWILO3 345 996944 RD.WILLOW T1 115 1 |  | 333 | 0.0924 | 102.37 | 640183 GENTLMN3 345 640325 REDWILO3 345 1
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2019-029 | FROM->TO | 640325 REDWILO3 345 996944 RD.WILLOW T1 115 1 |  | 333 | 0.11602 | 102.37 | 640183 GENTLMN3 345 640325 REDWILO3 345 1
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2019-033 | FROM->TO | 640325 REDWILO3 345 996944 RD.WILLOW T1 115 1 |  | 333 | 0.11602 | 102.37 | 640183 GENTLMN3 345 640325 REDWILO3 345 1
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2019-039 | FROM->TO | 640328 RISNGCY7 115 763718 G19-039-TAP 115 1 |  | 140 | 1 | 125.85 | 640124 COL.SE 7 115 763718 G19-039-TAP 115 1
Thermal | 02ALL | 1 | 02ALL-23SP | GEN-2019-039 | FROM->TO | 640328 RISNGCY7 115 763718 G19-039-TAP 115 1 |  | 140 | 1 | 125.76 | 640124 COL.SE 7 115 763718 G19-039-TAP 115 1
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2019-039 | FROM->TO | 640328 RISNGCY7 115 763718 G19-039-TAP 115 1 |  | 140 | 1 | 125.22 | 640124 COL.SE 7 115 763718 G19-039-TAP 115 1
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2018-065 | FROM->TO | 640342 SHELCRK3 345 996933 SHELLCREEKT1 230 1 |  | 336 | 0.2149 | 101.57 | 640125 COLMB.E3 345 640342 SHELCRK3 345 1
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2018-068 | FROM->TO | 640342 SHELCRK3 345 996933 SHELLCREEKT1 230 1 |  | 336 | 0.2149 | 101.57 | 640125 COLMB.E3 345 640342 SHELCRK3 345 1
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2018-083 | FROM->TO | 640342 SHELCRK3 345 996933 SHELLCREEKT1 230 1 |  | 336 | 0.30376 | 101.57 | 640125 COLMB.E3 345 640342 SHELCRK3 345 1
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2018-131 | FROM->TO | 640342 SHELCRK3 345 996933 SHELLCREEKT1 230 1 |  | 336 | 0.2149 | 101.57 | 640125 COLMB.E3 345 640342 SHELCRK3 345 1
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2018-132 | FROM->TO | 640342 SHELCRK3 345 996933 SHELLCREEKT1 230 1 |  | 336 | 0.2149 | 101.57 | 640125 COLMB.E3 345 640342 SHELCRK3 345 1
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2019-069 | FROM->TO | 640342 SHELCRK3 345 996933 SHELLCREEKT1 230 1 |  | 336 | 0.30376 | 101.57 | 640125 COLMB.E3 345 640342 SHELCRK3 345 1
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2019-070 | FROM->TO | 640342 SHELCRK3 345 996933 SHELLCREEKT1 230 1 |  | 336 | 0.30376 | 101.57 | 640125 COLMB.E3 345 640342 SHELCRK3 345 1
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2019-073 | FROM->TO | 640342 SHELCRK3 345 996933 SHELLCREEKT1 230 1 |  | 336 | 0.30376 | 101.57 | 640125 COLMB.E3 345 640342 SHELCRK3 345 1
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2018-065 | FROM->TO | 640343 SHELCRK4 230 996933 SHELLCREEKT1 230 1 |  | 336 | 0.2149 | 100.47 | 640125 COLMB.E3 345 640342 SHELCRK3 345 1
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2018-068 | FROM->TO | 640343 SHELCRK4 230 996933 SHELLCREEKT1 230 1 |  | 336 | 0.2149 | 100.47 | 640125 COLMB.E3 345 640342 SHELCRK3 345 1
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2018-083 | FROM->TO | 640343 SHELCRK4 230 996933 SHELLCREEKT1 230 1 |  | 336 | 0.30376 | 100.47 | 640125 COLMB.E3 345 640342 SHELCRK3 345 1
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2018-131 | FROM->TO | 640343 SHELCRK4 230 996933 SHELLCREEKT1 230 1 |  | 336 | 0.2149 | 100.47 | 640125 COLMB.E3 345 640342 SHELCRK3 345 1
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2018-132 | FROM->TO | 640343 SHELCRK4 230 996933 SHELLCREEKT1 230 1 |  | 336 | 0.2149 | 100.47 | 640125 COLMB.E3 345 640342 SHELCRK3 345 1
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2019-069 | FROM->TO | 640343 SHELCRK4 230 996933 SHELLCREEKT1 230 1 |  | 336 | 0.30376 | 100.47 | 640125 COLMB.E3 345 640342 SHELCRK3 345 1
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2019-070 | FROM->TO | 640343 SHELCRK4 230 996933 SHELLCREEKT1 230 1 |  | 336 | 0.30376 | 100.47 | 640125 COLMB.E3 345 640342 SHELCRK3 345 1
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2019-073 | FROM->TO | 640343 SHELCRK4 230 996933 SHELLCREEKT1 230 1 |  | 336 | 0.30376 | 100.47 | 640125 COLMB.E3 345 640342 SHELCRK3 345 1
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2019-029 | FROM->TO | 640370 SUTHLND7 115 659808 PAXTON__-TS7 115 1 |  | 108 | 0.11286 | 111.87 | 640183 GENTLMN3 345 640252 KEYSTON3 345 1
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2019-033 | FROM->TO | 640370 SUTHLND7 115 659808 PAXTON__-TS7 115 1 |  | 108 | 0.11286 | 111.87 | 640183 GENTLMN3 345 640252 KEYSTON3 345 1
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2018-065 | FROM->TO | 640520 ANTELOPE 3 345 996881 ANTELOPE T1 115 1 |  | 417 | 0.23751 | 118.08 | P42:345:NPPD:BKR-MOR-3306:::::
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2018-068 | FROM->TO | 640520 ANTELOPE 3 345 996881 ANTELOPE T1 115 1 |  | 417 | 0.23751 | 118.08 | P42:345:NPPD:BKR-MOR-3306:::::
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2018-131 | FROM->TO | 640520 ANTELOPE 3 345 996881 ANTELOPE T1 115 1 |  | 417 | 0.23751 | 118.08 | P42:345:NPPD:BKR-MOR-3306:::::
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2018-132 | FROM->TO | 640520 ANTELOPE 3 345 996881 ANTELOPE T1 115 1 |  | 417 | 0.23751 | 118.08 | P42:345:NPPD:BKR-MOR-3306:::::
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2018-065 | FROM->TO | 640520 ANTELOPE 3 345 996881 ANTELOPE T1 115 1 |  | 417 | 0.23748 | 114.79 | 640226 HOSKINS3 345 640520 ANTELOPE 3 345 1
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2018-068 | FROM->TO | 640520 ANTELOPE 3 345 996881 ANTELOPE T1 115 1 |  | 417 | 0.23748 | 114.79 | 640226 HOSKINS3 345 640520 ANTELOPE 3 345 1
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2018-131 | FROM->TO | 640520 ANTELOPE 3 345 996881 ANTELOPE T1 115 1 |  | 417 | 0.23748 | 114.79 | 640226 HOSKINS3 345 640520 ANTELOPE 3 345 1
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2018-132 | FROM->TO | 640520 ANTELOPE 3 345 996881 ANTELOPE T1 115 1 |  | 417 | 0.23748 | 114.79 | 640226 HOSKINS3 345 640520 ANTELOPE 3 345 1
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2018-065 | FROM->TO | 640520 ANTELOPE 3 345 996884 ANTELOPE T1 115 1 |  | 417 | 1 | 199.01 | P42:345:NPPD:BKR-MOR-3306:::::
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2018-068 | FROM->TO | 640520 ANTELOPE 3 345 996884 ANTELOPE T1 115 1 |  | 417 | 1 | 199.01 | P42:345:NPPD:BKR-MOR-3306:::::
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2018-131 | FROM->TO | 640520 ANTELOPE 3 345 996884 ANTELOPE T1 115 1 |  | 417 | 1 | 199.01 | P42:345:NPPD:BKR-MOR-3306:::::
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2018-132 | FROM->TO | 640520 ANTELOPE 3 345 996884 ANTELOPE T1 115 1 |  | 417 | 1 | 199.01 | P42:345:NPPD:BKR-MOR-3306:::::
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2018-065 | FROM->TO | 640520 ANTELOPE 3 345 996884 ANTELOPE T1 115 1 |  | 417 | 1 | 198.85 | 640226 HOSKINS3 345 640520 ANTELOPE 3 345 1
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2018-068 | FROM->TO | 640520 ANTELOPE 3 345 996884 ANTELOPE T1 115 1 |  | 417 | 1 | 198.85 | 640226 HOSKINS3 345 640520 ANTELOPE 3 345 1
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2018-131 | FROM->TO | 640520 ANTELOPE 3 345 996884 ANTELOPE T1 115 1 |  | 417 | 1 | 198.85 | 640226 HOSKINS3 345 640520 ANTELOPE 3 345 1
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2018-132 | FROM->TO | 640520 ANTELOPE 3 345 996884 ANTELOPE T1 115 1 |  | 417 | 1 | 198.85 | 640226 HOSKINS3 345 640520 ANTELOPE 3 345 1
Thermal | 02ALL | 1 | 02ALL-23SP | GEN-2018-065 | FROM->TO | 640520 ANTELOPE 3 345 996884 ANTELOPE T1 115 1 |  | 417 | 0.26979 | 120.02 | P42:345:NPPD:BKR-MOR-3306:::::
Thermal | 02ALL | 1 | 02ALL-23SP | GEN-2018-068 | FROM->TO | 640520 ANTELOPE 3 345 996884 ANTELOPE T1 115 1 |  | 417 | 0.26979 | 120.02 | P42:345:NPPD:BKR-MOR-3306:::::
Thermal | 02ALL | 1 | 02ALL-23SP | GEN-2018-131 | FROM->TO | 640520 ANTELOPE 3 345 996884 ANTELOPE T1 115 1 |  | 417 | 0.26979 | 120.02 | P42:345:NPPD:BKR-MOR-3306:::::
Thermal | 02ALL | 1 | 02ALL-23SP | GEN-2018-132 | FROM->TO | 640520 ANTELOPE 3 345 996884 ANTELOPE T1 115 1 |  | 417 | 0.26979 | 120.02 | P42:345:NPPD:BKR-MOR-3306:::::
Thermal | 02ALL | 1 | 02ALL-23SP | GEN-2018-065 | FROM->TO | 640520 ANTELOPE 3 345 996884 ANTELOPE T1 115 1 |  | 417 | 0.27016 | 117.02 | 640226 HOSKINS3 345 640520 ANTELOPE 3 345 1
Thermal | 02ALL | 1 | 02ALL-23SP | GEN-2018-068 | FROM->TO | 640520 ANTELOPE 3 345 996884 ANTELOPE T1 115 1 |  | 417 | 0.27016 | 117.02 | 640226 HOSKINS3 345 640520 ANTELOPE 3 345 1
Thermal | 02ALL | 1 | 02ALL-23SP | GEN-2018-131 | FROM->TO | 640520 ANTELOPE 3 345 996884 ANTELOPE T1 115 1 |  | 417 | 0.27016 | 117.02 | 640226 HOSKINS3 345 640520 ANTELOPE 3 345 1
Thermal | 02ALL | 1 | 02ALL-23SP | GEN-2018-132 | FROM->TO | 640520 ANTELOPE 3 345 996884 ANTELOPE T1 115 1 |  | 417 | 0.27016 | 117.02 | 640226 HOSKINS3 345 640520 ANTELOPE 3 345 1
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2018-065 | FROM->TO | 640520 ANTELOPE 3 345 996886 ANTELOPE T1 115 1 |  | 417 | 1 | 196.75 | P42:345:NPPD:BKR-MOR-3306:::::
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2018-068 | FROM->TO | 640520 ANTELOPE 3 345 996886 ANTELOPE T1 115 1 |  | 417 | 1 | 196.75 | P42:345:NPPD:BKR-MOR-3306:::::
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2018-131 | FROM->TO | 640520 ANTELOPE 3 345 996886 ANTELOPE T1 115 1 |  | 417 | 1 | 196.75 | P42:345:NPPD:BKR-MOR-3306:::::
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2018-132 | FROM->TO | 640520 ANTELOPE 3 345 996886 ANTELOPE T1 115 1 |  | 417 | 1 | 196.75 | P42:345:NPPD:BKR-MOR-3306:::::
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2018-065 | FROM->TO | 640520 ANTELOPE 3 345 996886 ANTELOPE T1 115 1 |  | 417 | 1 | 196.67 | 640226 HOSKINS3 345 640520 ANTELOPE 3 345 1
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2018-068 | FROM->TO | 640520 ANTELOPE 3 345 996886 ANTELOPE T1 115 1 |  | 417 | 1 | 196.67 | 640226 HOSKINS3 345 640520 ANTELOPE 3 345 1
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2018-131 | FROM->TO | 640520 ANTELOPE 3 345 996886 ANTELOPE T1 115 1 |  | 417 | 1 | 196.67 | 640226 HOSKINS3 345 640520 ANTELOPE 3 345 1
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2018-132 | FROM->TO | 640520 ANTELOPE 3 345 996886 ANTELOPE T1 115 1 |  | 417 | 1 | 196.67 | 640226 HOSKINS3 345 640520 ANTELOPE 3 345 1
Thermal | 02ALL | 1 | 02ALL-23SP | GEN-2018-065 | FROM->TO | 640520 ANTELOPE 3 345 996889 ANTELOPE T1 115 1 |  | 417 | 1 | 196.76 | P42:345:NPPD:BKR-MOR-3306:::::
Thermal | 02ALL | 1 | 02ALL-23SP | GEN-2018-068 | FROM->TO | 640520 ANTELOPE 3 345 996889 ANTELOPE T1 115 1 |  | 417 | 1 | 196.76 | P42:345:NPPD:BKR-MOR-3306:::::
Thermal | 02ALL | 1 | 02ALL-23SP | GEN-2018-131 | FROM->TO | 640520 ANTELOPE 3 345 996889 ANTELOPE T1 115 1 |  | 417 | 1 | 196.76 | P42:345:NPPD:BKR-MOR-3306:::::
Thermal | 02ALL | 1 | 02ALL-23SP | GEN-2018-132 | FROM->TO | 640520 ANTELOPE 3 345 996889 ANTELOPE T1 115 1 |  | 417 | 1 | 196.76 | P42:345:NPPD:BKR-MOR-3306:::::
Thermal | 02ALL | 1 | 02ALL-23SP | GEN-2018-065 | FROM->TO | 640520 ANTELOPE 3 345 996889 ANTELOPE T1 115 1 |  | 417 | 1 | 196.68 | 640226 HOSKINS3 345 640520 ANTELOPE 3 345 1
Thermal | 02ALL | 1 | 02ALL-23SP | GEN-2018-068 | FROM->TO | 640520 ANTELOPE 3 345 996889 ANTELOPE T1 115 1 |  | 417 | 1 | 196.68 | 640226 HOSKINS3 345 640520 ANTELOPE 3 345 1
Thermal | 02ALL | 1 | 02ALL-23SP | GEN-2018-131 | FROM->TO | 640520 ANTELOPE 3 345 996889 ANTELOPE T1 115 1 |  | 417 | 1 | 196.68 | 640226 HOSKINS3 345 640520 ANTELOPE 3 345 1
Thermal | 02ALL | 1 | 02ALL-23SP | GEN-2018-132 | FROM->TO | 640520 ANTELOPE 3 345 996889 ANTELOPE T1 115 1 |  | 417 | 1 | 196.68 | 640226 HOSKINS3 345 640520 ANTELOPE 3 345 1
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2018-065 | FROM->TO | 640521 ANTELOPE 7 115 996881 ANTELOPE T1 115 1 |  | 417 | 0.23751 | 119.62 | P42:345:NPPD:BKR-MOR-3306:::::
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2018-068 | FROM->TO | 640521 ANTELOPE 7 115 996881 ANTELOPE T1 115 1 |  | 417 | 0.23751 | 119.62 | P42:345:NPPD:BKR-MOR-3306:::::
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2018-131 | FROM->TO | 640521 ANTELOPE 7 115 996881 ANTELOPE T1 115 1 |  | 417 | 0.23751 | 119.62 | P42:345:NPPD:BKR-MOR-3306:::::
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2018-132 | FROM->TO | 640521 ANTELOPE 7 115 996881 ANTELOPE T1 115 1 |  | 417 | 0.23751 | 119.62 | P42:345:NPPD:BKR-MOR-3306:::::
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2018-065 | FROM->TO | 640521 ANTELOPE 7 115 996881 ANTELOPE T1 115 1 |  | 417 | 0.23748 | 116.55 | 640226 HOSKINS3 345 640520 ANTELOPE 3 345 1
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2018-068 | FROM->TO | 640521 ANTELOPE 7 115 996881 ANTELOPE T1 115 1 |  | 417 | 0.23748 | 116.55 | 640226 HOSKINS3 345 640520 ANTELOPE 3 345 1
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2018-131 | FROM->TO | 640521 ANTELOPE 7 115 996881 ANTELOPE T1 115 1 |  | 417 | 0.23748 | 116.55 | 640226 HOSKINS3 345 640520 ANTELOPE 3 345 1
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2018-132 | FROM->TO | 640521 ANTELOPE 7 115 996881 ANTELOPE T1 115 1 |  | 417 | 0.23748 | 116.55 | 640226 HOSKINS3 345 640520 ANTELOPE 3 345 1
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2018-065 | FROM->TO | 640521 ANTELOPE 7 115 996884 ANTELOPE T1 115 1 |  | 417 | 1 | 192.57 | 640226 HOSKINS3 345 640520 ANTELOPE 3 345 1
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2018-068 | FROM->TO | 640521 ANTELOPE 7 115 996884 ANTELOPE T1 115 1 |  | 417 | 1 | 192.57 | 640226 HOSKINS3 345 640520 ANTELOPE 3 345 1
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2018-131 | FROM->TO | 640521 ANTELOPE 7 115 996884 ANTELOPE T1 115 1 |  | 417 | 1 | 192.57 | 640226 HOSKINS3 345 640520 ANTELOPE 3 345 1
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2018-132 | FROM->TO | 640521 ANTELOPE 7 115 996884 ANTELOPE T1 115 1 |  | 417 | 1 | 192.57 | 640226 HOSKINS3 345 640520 ANTELOPE 3 345 1
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2018-065 | FROM->TO | 640521 ANTELOPE 7 115 996884 ANTELOPE T1 115 1 |  | 417 | 1 | 192.56 | P42:345:NPPD:BKR-MOR-3306:::::
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2018-068 | FROM->TO | 640521 ANTELOPE 7 115 996884 ANTELOPE T1 115 1 |  | 417 | 1 | 192.56 | P42:345:NPPD:BKR-MOR-3306:::::
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2018-131 | FROM->TO | 640521 ANTELOPE 7 115 996884 ANTELOPE T1 115 1 |  | 417 | 1 | 192.56 | P42:345:NPPD:BKR-MOR-3306:::::
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2018-132 | FROM->TO | 640521 ANTELOPE 7 115 996884 ANTELOPE T1 115 1 |  | 417 | 1 | 192.56 | P42:345:NPPD:BKR-MOR-3306:::::
Thermal | 02ALL | 1 | 02ALL-23SP | GEN-2018-065 | FROM->TO | 640521 ANTELOPE 7 115 996884 ANTELOPE T1 115 1 |  | 417 | 0.26979 | 121.63 | P42:345:NPPD:BKR-MOR-3306:::::
Thermal | 02ALL | 1 | 02ALL-23SP | GEN-2018-068 | FROM->TO | 640521 ANTELOPE 7 115 996884 ANTELOPE T1 115 1 |  | 417 | 0.26979 | 121.63 | P42:345:NPPD:BKR-MOR-3306:::::
Thermal | 02ALL | 1 | 02ALL-23SP | GEN-2018-131 | FROM->TO | 640521 ANTELOPE 7 115 996884 ANTELOPE T1 115 1 |  | 417 | 0.26979 | 121.63 | P42:345:NPPD:BKR-MOR-3306:::::
Thermal | 02ALL | 1 | 02ALL-23SP | GEN-2018-132 | FROM->TO | 640521 ANTELOPE 7 115 996884 ANTELOPE T1 115 1 |  | 417 | 0.26979 | 121.63 | P42:345:NPPD:BKR-MOR-3306:::::
Thermal | 02ALL | 1 | 02ALL-23SP | GEN-2018-065 | FROM->TO | 640521 ANTELOPE 7 115 996884 ANTELOPE T1 115 1 |  | 417 | 0.27016 | 118.85 | 640226 HOSKINS3 345 640520 ANTELOPE 3 345 1
Thermal | 02ALL | 1 | 02ALL-23SP | GEN-2018-068 | FROM->TO | 640521 ANTELOPE 7 115 996884 ANTELOPE T1 115 1 |  | 417 | 0.27016 | 118.85 | 640226 HOSKINS3 345 640520 ANTELOPE 3 345 1
Thermal | 02ALL | 1 | 02ALL-23SP | GEN-2018-131 | FROM->TO | 640521 ANTELOPE 7 115 996884 ANTELOPE T1 115 1 |  | 417 | 0.27016 | 118.85 | 640226 HOSKINS3 345 640520 ANTELOPE 3 345 1
Thermal | 02ALL | 1 | 02ALL-23SP | GEN-2018-132 | FROM->TO | 640521 ANTELOPE 7 115 996884 ANTELOPE T1 115 1 |  | 417 | 0.27016 | 118.85 | 640226 HOSKINS3 345 640520 ANTELOPE 3 345 1
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2018-065 | FROM->TO | 640521 ANTELOPE 7 115 996886 ANTELOPE T1 115 1 |  | 417 | 1 | 192.99 | 640226 HOSKINS3 345 640520 ANTELOPE 3 345 1
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2018-068 | FROM->TO | 640521 ANTELOPE 7 115 996886 ANTELOPE T1 115 1 |  | 417 | 1 | 192.99 | 640226 HOSKINS3 345 640520 ANTELOPE 3 345 1
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2018-131 | FROM->TO | 640521 ANTELOPE 7 115 996886 ANTELOPE T1 115 1 |  | 417 | 1 | 192.99 | 640226 HOSKINS3 345 640520 ANTELOPE 3 345 1
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2018-132 | FROM->TO | 640521 ANTELOPE 7 115 996886 ANTELOPE T1 115 1 |  | 417 | 1 | 192.99 | 640226 HOSKINS3 345 640520 ANTELOPE 3 345 1
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2018-065 | FROM->TO | 640521 ANTELOPE 7 115 996886 ANTELOPE T1 115 1 |  | 417 | 1 | 192.96 | P42:345:NPPD:BKR-MOR-3306:::::
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2018-068 | FROM->TO | 640521 ANTELOPE 7 115 996886 ANTELOPE T1 115 1 |  | 417 | 1 | 192.96 | P42:345:NPPD:BKR-MOR-3306:::::
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2018-131 | FROM->TO | 640521 ANTELOPE 7 115 996886 ANTELOPE T1 115 1 |  | 417 | 1 | 192.96 | P42:345:NPPD:BKR-MOR-3306:::::
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2018-132 | FROM->TO | 640521 ANTELOPE 7 115 996886 ANTELOPE T1 115 1 |  | 417 | 1 | 192.96 | P42:345:NPPD:BKR-MOR-3306:::::
Thermal | 02ALL | 1 | 02ALL-23SP | GEN-2018-065 | FROM->TO | 640521 ANTELOPE 7 115 996889 ANTELOPE T1 115 1 |  | 417 | 1 | 192.98 | 640226 HOSKINS3 345 640520 ANTELOPE 3 345 1
Thermal | 02ALL | 1 | 02ALL-23SP | GEN-2018-068 | FROM->TO | 640521 ANTELOPE 7 115 996889 ANTELOPE T1 115 1 |  | 417 | 1 | 192.98 | 640226 HOSKINS3 345 640520 ANTELOPE 3 345 1
Thermal | 02ALL | 1 | 02ALL-23SP | GEN-2018-131 | FROM->TO | 640521 ANTELOPE 7 115 996889 ANTELOPE T1 115 1 |  | 417 | 1 | 192.98 | 640226 HOSKINS3 345 640520 ANTELOPE 3 345 1
Thermal | 02ALL | 1 | 02ALL-23SP | GEN-2018-132 | FROM->TO | 640521 ANTELOPE 7 115 996889 ANTELOPE T1 115 1 |  | 417 | 1 | 192.98 | 640226 HOSKINS3 345 640520 ANTELOPE 3 345 1
Thermal | 02ALL | 1 | 02ALL-23SP | GEN-2018-065 | FROM->TO | 640521 ANTELOPE 7 115 996889 ANTELOPE T1 115 1 |  | 417 | 1 | 192.95 | P42:345:NPPD:BKR-MOR-3306:::::
Thermal | 02ALL | 1 | 02ALL-23SP | GEN-2018-068 | FROM->TO | 640521 ANTELOPE 7 115 996889 ANTELOPE T1 115 1 |  | 417 | 1 | 192.95 | P42:345:NPPD:BKR-MOR-3306:::::
Thermal | 02ALL | 1 | 02ALL-23SP | GEN-2018-131 | FROM->TO | 640521 ANTELOPE 7 115 996889 ANTELOPE T1 115 1 |  | 417 | 1 | 192.95 | P42:345:NPPD:BKR-MOR-3306:::::
Thermal | 02ALL | 1 | 02ALL-23SP | GEN-2018-132 | FROM->TO | 640521 ANTELOPE 7 115 996889 ANTELOPE T1 115 1 |  | 417 | 1 | 192.95 | P42:345:NPPD:BKR-MOR-3306:::::
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2018-065 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.21407 | 120.45 | P42:345:NPPD:BKR-CPR-3310:::::
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2018-068 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.21407 | 120.45 | P42:345:NPPD:BKR-CPR-3310:::::
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2018-083 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.22733 | 120.45 | P42:345:NPPD:BKR-CPR-3310:::::
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2018-090 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.69163 | 120.45 | P42:345:NPPD:BKR-CPR-3310:::::
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2018-131 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.21407 | 120.45 | P42:345:NPPD:BKR-CPR-3310:::::
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2018-132 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.21407 | 120.45 | P42:345:NPPD:BKR-CPR-3310:::::
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2019-069 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.22733 | 120.45 | P42:345:NPPD:BKR-CPR-3310:::::
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2019-070 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.22733 | 120.45 | P42:345:NPPD:BKR-CPR-3310:::::
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2019-073 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.22733 | 120.45 | P42:345:NPPD:BKR-CPR-3310:::::
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2018-065 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.21304 | 119.92 | 640342 SHELCRK3 345 763982 G19-069TAP 345 1
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2018-068 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.21304 | 119.92 | 640342 SHELCRK3 345 763982 G19-069TAP 345 1
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2018-083 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.22645 | 119.92 | 640342 SHELCRK3 345 763982 G19-069TAP 345 1
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2018-090 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.69209 | 119.92 | 640342 SHELCRK3 345 763982 G19-069TAP 345 1
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2018-131 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.21304 | 119.92 | 640342 SHELCRK3 345 763982 G19-069TAP 345 1
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2018-132 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.21304 | 119.92 | 640342 SHELCRK3 345 763982 G19-069TAP 345 1
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2019-069 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.22645 | 119.92 | 640342 SHELCRK3 345 763982 G19-069TAP 345 1
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2019-070 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.22645 | 119.92 | 640342 SHELCRK3 345 763982 G19-069TAP 345 1
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2019-073 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.22645 | 119.92 | 640342 SHELCRK3 345 763982 G19-069TAP 345 1
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2018-065 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.14141 | 119.5 | 635600 GRIMES 3 345 636003 BVR CRK 3 345 1
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2018-068 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.14141 | 119.5 | 635600 GRIMES 3 345 636003 BVR CRK 3 345 1
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2018-083 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.12013 | 119.5 | 635600 GRIMES 3 345 636003 BVR CRK 3 345 1
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2018-090 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.68627 | 119.5 | 635600 GRIMES 3 345 636003 BVR CRK 3 345 1
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2018-131 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.14141 | 119.5 | 635600 GRIMES 3 345 636003 BVR CRK 3 345 1
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2018-132 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.14141 | 119.5 | 635600 GRIMES 3 345 636003 BVR CRK 3 345 1
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2019-069 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.12013 | 119.5 | 635600 GRIMES 3 345 636003 BVR CRK 3 345 1
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2019-070 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.12013 | 119.5 | 635600 GRIMES 3 345 636003 BVR CRK 3 345 1
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2019-073 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.12013 | 119.5 | 635600 GRIMES 3 345 636003 BVR CRK 3 345 1
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2018-065 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.12794 | 116.6 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2018-068 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.12794 | 116.6 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2018-083 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.10828 | 116.6 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2018-090 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.68142 | 116.6 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2018-131 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.12794 | 116.6 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2018-132 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.12794 | 116.6 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2019-069 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.10828 | 116.6 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2019-070 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.10828 | 116.6 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2019-073 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.10828 | 116.6 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2018-065 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.14141 | 116.24 | 636003 BVR CRK 3 345 636010 LEHIGH 3 345 1
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2018-068 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.14141 | 116.24 | 636003 BVR CRK 3 345 636010 LEHIGH 3 345 1
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2018-083 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.12013 | 116.24 | 636003 BVR CRK 3 345 636010 LEHIGH 3 345 1
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2018-090 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.68627 | 116.24 | 636003 BVR CRK 3 345 636010 LEHIGH 3 345 1
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2018-131 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.14141 | 116.24 | 636003 BVR CRK 3 345 636010 LEHIGH 3 345 1
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2018-132 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.14141 | 116.24 | 636003 BVR CRK 3 345 636010 LEHIGH 3 345 1
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2019-069 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.12013 | 116.24 | 636003 BVR CRK 3 345 636010 LEHIGH 3 345 1
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2019-070 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.12013 | 116.24 | 636003 BVR CRK 3 345 636010 LEHIGH 3 345 1
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2019-073 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.12013 | 116.24 | 636003 BVR CRK 3 345 636010 LEHIGH 3 345 1
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2018-065 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.1448 | 116.2 | 635219 GARD AVE 3 345 636010 LEHIGH 3 345 1
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2018-068 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.1448 | 116.2 | 635219 GARD AVE 3 345 636010 LEHIGH 3 345 1
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2018-083 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.12406 | 116.2 | 635219 GARD AVE 3 345 636010 LEHIGH 3 345 1
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2018-090 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.6938 | 116.2 | 635219 GARD AVE 3 345 636010 LEHIGH 3 345 1
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2018-131 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.1448 | 116.2 | 635219 GARD AVE 3 345 636010 LEHIGH 3 345 1
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2018-132 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.1448 | 116.2 | 635219 GARD AVE 3 345 636010 LEHIGH 3 345 1
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2019-069 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.12406 | 116.2 | 635219 GARD AVE 3 345 636010 LEHIGH 3 345 1
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2019-070 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.12406 | 116.2 | 635219 GARD AVE 3 345 636010 LEHIGH 3 345 1
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2019-073 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.12406 | 116.2 | 635219 GARD AVE 3 345 636010 LEHIGH 3 345 1
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2018-065 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.18238 | 116 | P42:345:NPPD:BKR-CPR-3316:::::
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2018-068 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.18238 | 116 | P42:345:NPPD:BKR-CPR-3316:::::
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2018-083 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.17799 | 116 | P42:345:NPPD:BKR-CPR-3316:::::
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2018-090 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.6845 | 116 | P42:345:NPPD:BKR-CPR-3316:::::
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2018-131 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.18238 | 116 | P42:345:NPPD:BKR-CPR-3316:::::
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2018-132 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.18238 | 116 | P42:345:NPPD:BKR-CPR-3316:::::
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2019-039 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.06086 | 116 | P42:345:NPPD:BKR-CPR-3316:::::
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2019-069 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.17799 | 116 | P42:345:NPPD:BKR-CPR-3316:::::
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2019-070 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.17799 | 116 | P42:345:NPPD:BKR-CPR-3316:::::
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2019-073 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.17799 | 116 | P42:345:NPPD:BKR-CPR-3316:::::
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2018-065 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.12794 | 115.43 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2018-068 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.12794 | 115.43 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2018-083 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.10828 | 115.43 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2018-090 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.68142 | 115.43 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2018-131 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.12794 | 115.43 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2018-132 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.12794 | 115.43 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2019-069 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.10828 | 115.43 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2019-070 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.10828 | 115.43 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2019-073 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.10828 | 115.43 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2018-065 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.17511 | 115.02 | P42:345:LES:L3516::NW68&HOLDREGE.MOORE.CB3005
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2018-068 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.17511 | 115.02 | P42:345:LES:L3516::NW68&HOLDREGE.MOORE.CB3005
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2018-083 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.16724 | 115.02 | P42:345:LES:L3516::NW68&HOLDREGE.MOORE.CB3005
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2018-090 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.68233 | 115.02 | P42:345:LES:L3516::NW68&HOLDREGE.MOORE.CB3005
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2018-131 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.17511 | 115.02 | P42:345:LES:L3516::NW68&HOLDREGE.MOORE.CB3005
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2018-132 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.17511 | 115.02 | P42:345:LES:L3516::NW68&HOLDREGE.MOORE.CB3005
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2019-039 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.07605 | 115.02 | P42:345:LES:L3516::NW68&HOLDREGE.MOORE.CB3005
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2019-069 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.16724 | 115.02 | P42:345:LES:L3516::NW68&HOLDREGE.MOORE.CB3005
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2019-070 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.16724 | 115.02 | P42:345:LES:L3516::NW68&HOLDREGE.MOORE.CB3005
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2019-073 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.16724 | 115.02 | P42:345:LES:L3516::NW68&HOLDREGE.MOORE.CB3005
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2018-065 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.12794 | 114.79 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2018-068 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.12794 | 114.79 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2018-083 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.10828 | 114.79 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2018-090 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.68142 | 114.79 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2018-131 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.12794 | 114.79 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2018-132 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.12794 | 114.79 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2019-069 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.10828 | 114.79 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2019-070 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.10828 | 114.79 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2019-073 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.10828 | 114.79 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2018-065 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.17547 | 114.77 | P42:345:LES:L1485::NW68&HOLDREGE.WAGENER.CB3006
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2018-068 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.17547 | 114.77 | P42:345:LES:L1485::NW68&HOLDREGE.WAGENER.CB3006
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2018-083 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.16767 | 114.77 | P42:345:LES:L1485::NW68&HOLDREGE.WAGENER.CB3006
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2018-090 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.68207 | 114.77 | P42:345:LES:L1485::NW68&HOLDREGE.WAGENER.CB3006
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2018-131 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.17547 | 114.77 | P42:345:LES:L1485::NW68&HOLDREGE.WAGENER.CB3006
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2018-132 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.17547 | 114.77 | P42:345:LES:L1485::NW68&HOLDREGE.WAGENER.CB3006
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2019-039 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.07779 | 114.77 | P42:345:LES:L1485::NW68&HOLDREGE.WAGENER.CB3006
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2019-069 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.16767 | 114.77 | P42:345:LES:L1485::NW68&HOLDREGE.WAGENER.CB3006
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2019-070 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.16767 | 114.77 | P42:345:LES:L1485::NW68&HOLDREGE.WAGENER.CB3006
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2019-073 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.16767 | 114.77 | P42:345:LES:L1485::NW68&HOLDREGE.WAGENER.CB3006
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2018-065 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.17568 | 114.49 | P12:345:NPPD:L3521::NW68&HOLDREGE.COLUMBUSEAST.CKT1
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2018-068 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.17568 | 114.49 | P12:345:NPPD:L3521::NW68&HOLDREGE.COLUMBUSEAST.CKT1
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2018-083 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.16781 | 114.49 | P12:345:NPPD:L3521::NW68&HOLDREGE.COLUMBUSEAST.CKT1
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2018-090 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.68362 | 114.49 | P12:345:NPPD:L3521::NW68&HOLDREGE.COLUMBUSEAST.CKT1
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2018-131 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.17568 | 114.49 | P12:345:NPPD:L3521::NW68&HOLDREGE.COLUMBUSEAST.CKT1
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2018-132 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.17568 | 114.49 | P12:345:NPPD:L3521::NW68&HOLDREGE.COLUMBUSEAST.CKT1
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2019-039 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.07699 | 114.49 | P12:345:NPPD:L3521::NW68&HOLDREGE.COLUMBUSEAST.CKT1
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2019-069 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.16781 | 114.49 | P12:345:NPPD:L3521::NW68&HOLDREGE.COLUMBUSEAST.CKT1
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2019-070 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.16781 | 114.49 | P12:345:NPPD:L3521::NW68&HOLDREGE.COLUMBUSEAST.CKT1
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2019-073 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.16781 | 114.49 | P12:345:NPPD:L3521::NW68&HOLDREGE.COLUMBUSEAST.CKT1
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2018-065 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.12707 | 114.45 | P23:345:MEC:CBEC 905
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2018-068 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.12707 | 114.45 | P23:345:MEC:CBEC 905
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2018-083 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.1072 | 114.45 | P23:345:MEC:CBEC 905
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2018-090 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.67835 | 114.45 | P23:345:MEC:CBEC 905
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2018-131 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.12707 | 114.45 | P23:345:MEC:CBEC 905
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2018-132 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.12707 | 114.45 | P23:345:MEC:CBEC 905
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2019-069 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.1072 | 114.45 | P23:345:MEC:CBEC 905
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2019-070 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.1072 | 114.45 | P23:345:MEC:CBEC 905
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2019-073 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.1072 | 114.45 | P23:345:MEC:CBEC 905
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2018-065 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.12794 | 114.26 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2018-068 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.12794 | 114.26 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2018-083 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.10828 | 114.26 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2018-090 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.68142 | 114.26 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2018-131 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.12794 | 114.26 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2018-132 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.12794 | 114.26 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2019-069 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.10828 | 114.26 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2019-070 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.10828 | 114.26 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2019-073 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.10828 | 114.26 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2018-065 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.12789 | 114.19 | P23:345:MEC:CBEC 908
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2018-068 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.12789 | 114.19 | P23:345:MEC:CBEC 908
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2018-083 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.10823 | 114.19 | P23:345:MEC:CBEC 908
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2018-090 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.68129 | 114.19 | P23:345:MEC:CBEC 908
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2018-131 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.12789 | 114.19 | P23:345:MEC:CBEC 908
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2018-132 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.12789 | 114.19 | P23:345:MEC:CBEC 908
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2019-069 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.10823 | 114.19 | P23:345:MEC:CBEC 908
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2019-070 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.10823 | 114.19 | P23:345:MEC:CBEC 908
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2019-073 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.10823 | 114.19 | P23:345:MEC:CBEC 908
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2018-065 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.1448 | 113.88 | 635206 IDA CO 3 345 635219 GARD AVE 3 345 1
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2018-068 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.1448 | 113.88 | 635206 IDA CO 3 345 635219 GARD AVE 3 345 1
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2018-083 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.12406 | 113.88 | 635206 IDA CO 3 345 635219 GARD AVE 3 345 1
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2018-090 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.6938 | 113.88 | 635206 IDA CO 3 345 635219 GARD AVE 3 345 1
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2018-131 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.1448 | 113.88 | 635206 IDA CO 3 345 635219 GARD AVE 3 345 1
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2018-132 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.1448 | 113.88 | 635206 IDA CO 3 345 635219 GARD AVE 3 345 1
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2019-069 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.12406 | 113.88 | 635206 IDA CO 3 345 635219 GARD AVE 3 345 1
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2019-070 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.12406 | 113.88 | 635206 IDA CO 3 345 635219 GARD AVE 3 345 1
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2019-073 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.12406 | 113.88 | 635206 IDA CO 3 345 635219 GARD AVE 3 345 1
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2018-065 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.16662 | 113.03 | 640125 COLMB.E3 345 640342 SHELCRK3 345 1
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2018-068 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.16662 | 113.03 | 640125 COLMB.E3 345 640342 SHELCRK3 345 1
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2018-083 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.16026 | 113.03 | 640125 COLMB.E3 345 640342 SHELCRK3 345 1
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2018-090 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.68438 | 113.03 | 640125 COLMB.E3 345 640342 SHELCRK3 345 1
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2018-131 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.16662 | 113.03 | 640125 COLMB.E3 345 640342 SHELCRK3 345 1
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2018-132 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.16662 | 113.03 | 640125 COLMB.E3 345 640342 SHELCRK3 345 1
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2019-069 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.16026 | 113.03 | 640125 COLMB.E3 345 640342 SHELCRK3 345 1
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2019-070 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.16026 | 113.03 | 640125 COLMB.E3 345 640342 SHELCRK3 345 1
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2019-073 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.16026 | 113.03 | 640125 COLMB.E3 345 640342 SHELCRK3 345 1
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2018-065 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.12794 | 112.82 | P11:345:MEC-NPPD:COOPER 1
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2018-068 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.12794 | 112.82 | P11:345:MEC-NPPD:COOPER 1
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2018-083 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.10828 | 112.82 | P11:345:MEC-NPPD:COOPER 1
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2018-090 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.68142 | 112.82 | P11:345:MEC-NPPD:COOPER 1
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2018-131 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.12794 | 112.82 | P11:345:MEC-NPPD:COOPER 1
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2018-132 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.12794 | 112.82 | P11:345:MEC-NPPD:COOPER 1
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2019-069 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.10828 | 112.82 | P11:345:MEC-NPPD:COOPER 1
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2019-070 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.10828 | 112.82 | P11:345:MEC-NPPD:COOPER 1
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2019-073 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.10828 | 112.82 | P11:345:MEC-NPPD:COOPER 1
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2018-065 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.12794 | 112.67 | P22:345:OPPD:S3458 NEBCTY2G:LT::EHV:
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2018-065 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.12794 | 112.67 | P23:345:OPPD:S3458 NEBCTY2G:LT::EHV:
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2018-068 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.12794 | 112.67 | P22:345:OPPD:S3458 NEBCTY2G:LT::EHV:
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2018-068 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.12794 | 112.67 | P23:345:OPPD:S3458 NEBCTY2G:LT::EHV:
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2018-083 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.10828 | 112.67 | P22:345:OPPD:S3458 NEBCTY2G:LT::EHV:
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2018-083 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.10828 | 112.67 | P23:345:OPPD:S3458 NEBCTY2G:LT::EHV:
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2018-090 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.68142 | 112.67 | P22:345:OPPD:S3458 NEBCTY2G:LT::EHV:
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2018-090 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.68142 | 112.67 | P23:345:OPPD:S3458 NEBCTY2G:LT::EHV:
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2018-131 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.12794 | 112.67 | P22:345:OPPD:S3458 NEBCTY2G:LT::EHV:
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2018-131 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.12794 | 112.67 | P23:345:OPPD:S3458 NEBCTY2G:LT::EHV:
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2018-132 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.12794 | 112.67 | P22:345:OPPD:S3458 NEBCTY2G:LT::EHV:
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2018-132 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.12794 | 112.67 | P23:345:OPPD:S3458 NEBCTY2G:LT::EHV:
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2019-069 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.10828 | 112.67 | P22:345:OPPD:S3458 NEBCTY2G:LT::EHV:
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2019-069 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.10828 | 112.67 | P23:345:OPPD:S3458 NEBCTY2G:LT::EHV:
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2019-070 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.10828 | 112.67 | P22:345:OPPD:S3458 NEBCTY2G:LT::EHV:
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2019-070 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.10828 | 112.67 | P23:345:OPPD:S3458 NEBCTY2G:LT::EHV:
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2019-073 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.10828 | 112.67 | P22:345:OPPD:S3458 NEBCTY2G:LT::EHV:
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2019-073 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.10828 | 112.67 | P23:345:OPPD:S3458 NEBCTY2G:LT::EHV:
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2018-065 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.21893 | 108.15 | P42:345:NPPD:BKR-CPR-3310:::::
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2018-068 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.21893 | 108.15 | P42:345:NPPD:BKR-CPR-3310:::::
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2018-083 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.23219 | 108.15 | P42:345:NPPD:BKR-CPR-3310:::::
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2018-090 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.69641 | 108.15 | P42:345:NPPD:BKR-CPR-3310:::::
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2018-131 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.21893 | 108.15 | P42:345:NPPD:BKR-CPR-3310:::::
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2018-132 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.21893 | 108.15 | P42:345:NPPD:BKR-CPR-3310:::::
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2019-069 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.23219 | 108.15 | P42:345:NPPD:BKR-CPR-3310:::::
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2019-070 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.23219 | 108.15 | P42:345:NPPD:BKR-CPR-3310:::::
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2019-073 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.23219 | 108.15 | P42:345:NPPD:BKR-CPR-3310:::::
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2018-065 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.21783 | 107.77 | 640342 SHELCRK3 345 763982 G19-069TAP 345 1
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2018-068 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.21783 | 107.77 | 640342 SHELCRK3 345 763982 G19-069TAP 345 1
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2018-083 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.23124 | 107.77 | 640342 SHELCRK3 345 763982 G19-069TAP 345 1
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2018-090 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.69679 | 107.77 | 640342 SHELCRK3 345 763982 G19-069TAP 345 1
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2018-131 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.21783 | 107.77 | 640342 SHELCRK3 345 763982 G19-069TAP 345 1
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2018-132 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.21783 | 107.77 | 640342 SHELCRK3 345 763982 G19-069TAP 345 1
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2019-069 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.23124 | 107.77 | 640342 SHELCRK3 345 763982 G19-069TAP 345 1
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2019-070 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.23124 | 107.77 | 640342 SHELCRK3 345 763982 G19-069TAP 345 1
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2019-073 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.23124 | 107.77 | 640342 SHELCRK3 345 763982 G19-069TAP 345 1
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2018-065 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.13225 | 106.63 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2018-068 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.13225 | 106.63 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2018-083 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.11258 | 106.63 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2018-090 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.68566 | 106.63 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2018-131 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.13225 | 106.63 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2018-132 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.13225 | 106.63 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2019-069 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.11258 | 106.63 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2019-070 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.11258 | 106.63 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2019-073 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.11258 | 106.63 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2018-065 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.13225 | 105.5 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2018-068 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.13225 | 105.5 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2018-083 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.11258 | 105.5 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2018-090 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.68566 | 105.5 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2018-131 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.13225 | 105.5 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2018-132 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.13225 | 105.5 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2019-069 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.11258 | 105.5 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2019-070 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.11258 | 105.5 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2019-073 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.11258 | 105.5 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2018-065 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 | 956 |  | 0.12794 | 104.94 | System Intact
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2018-068 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 | 956 |  | 0.12794 | 104.94 | System Intact
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2018-083 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 | 956 |  | 0.10828 | 104.94 | System Intact
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2018-090 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 | 956 |  | 0.68142 | 104.94 | System Intact
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2018-131 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 | 956 |  | 0.12794 | 104.94 | System Intact
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2018-132 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 | 956 |  | 0.12794 | 104.94 | System Intact
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2019-069 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 | 956 |  | 0.10828 | 104.94 | System Intact
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2019-070 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 | 956 |  | 0.10828 | 104.94 | System Intact
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2019-073 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 | 956 |  | 0.10828 | 104.94 | System Intact
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2018-065 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.13225 | 104.85 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3
Thermal | 02ALL | 1 | 02ALL-23SP | GEN-2018-065 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.22135 | 104.85 | P42:345:NPPD:BKR-CPR-3310:::::
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2018-068 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.13225 | 104.85 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3
Thermal | 02ALL | 1 | 02ALL-23SP | GEN-2018-068 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.22135 | 104.85 | P42:345:NPPD:BKR-CPR-3310:::::
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2018-083 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.11258 | 104.85 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3
Thermal | 02ALL | 1 | 02ALL-23SP | GEN-2018-083 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.23445 | 104.85 | P42:345:NPPD:BKR-CPR-3310:::::
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2018-090 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.68566 | 104.85 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3
Thermal | 02ALL | 1 | 02ALL-23SP | GEN-2018-090 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.69803 | 104.85 | P42:345:NPPD:BKR-CPR-3310:::::
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2018-131 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.13225 | 104.85 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3
Thermal | 02ALL | 1 | 02ALL-23SP | GEN-2018-131 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.22135 | 104.85 | P42:345:NPPD:BKR-CPR-3310:::::
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2018-132 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.13225 | 104.85 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3
Thermal | 02ALL | 1 | 02ALL-23SP | GEN-2018-132 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.22135 | 104.85 | P42:345:NPPD:BKR-CPR-3310:::::
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2019-069 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.11258 | 104.85 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3
Thermal | 02ALL | 1 | 02ALL-23SP | GEN-2019-069 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.23445 | 104.85 | P42:345:NPPD:BKR-CPR-3310:::::
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2019-070 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.11258 | 104.85 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3
Thermal | 02ALL | 1 | 02ALL-23SP | GEN-2019-070 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.23445 | 104.85 | P42:345:NPPD:BKR-CPR-3310:::::
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2019-073 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.11258 | 104.85 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3
Thermal | 02ALL | 1 | 02ALL-23SP | GEN-2019-073 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.23445 | 104.85 | P42:345:NPPD:BKR-CPR-3310:::::
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2018-065 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.13138 | 104.74 | P23:345:MEC:CBEC 905
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2018-068 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.13138 | 104.74 | P23:345:MEC:CBEC 905
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2018-083 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.11151 | 104.74 | P23:345:MEC:CBEC 905
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2018-090 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.68262 | 104.74 | P23:345:MEC:CBEC 905
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2018-131 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.13138 | 104.74 | P23:345:MEC:CBEC 905
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2018-132 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.13138 | 104.74 | P23:345:MEC:CBEC 905
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2019-069 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.11151 | 104.74 | P23:345:MEC:CBEC 905
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2019-070 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.11151 | 104.74 | P23:345:MEC:CBEC 905
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2019-073 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.11151 | 104.74 | P23:345:MEC:CBEC 905
Thermal | 02ALL | 1 | 02ALL-23SP | GEN-2018-065 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.22023 | 104.47 | 640342 SHELCRK3 345 763982 G19-069TAP 345 1
Thermal | 02ALL | 1 | 02ALL-23SP | GEN-2018-068 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.22023 | 104.47 | 640342 SHELCRK3 345 763982 G19-069TAP 345 1
Thermal | 02ALL | 1 | 02ALL-23SP | GEN-2018-083 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.23347 | 104.47 | 640342 SHELCRK3 345 763982 G19-069TAP 345 1
Thermal | 02ALL | 1 | 02ALL-23SP | GEN-2018-090 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.6984 | 104.47 | 640342 SHELCRK3 345 763982 G19-069TAP 345 1
Thermal | 02ALL | 1 | 02ALL-23SP | GEN-2018-131 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.22023 | 104.47 | 640342 SHELCRK3 345 763982 G19-069TAP 345 1
Thermal | 02ALL | 1 | 02ALL-23SP | GEN-2018-132 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.22023 | 104.47 | 640342 SHELCRK3 345 763982 G19-069TAP 345 1
Thermal | 02ALL | 1 | 02ALL-23SP | GEN-2019-069 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.23347 | 104.47 | 640342 SHELCRK3 345 763982 G19-069TAP 345 1
Thermal | 02ALL | 1 | 02ALL-23SP | GEN-2019-070 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.23347 | 104.47 | 640342 SHELCRK3 345 763982 G19-069TAP 345 1
Thermal | 02ALL | 1 | 02ALL-23SP | GEN-2019-073 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.23347 | 104.47 | 640342 SHELCRK3 345 763982 G19-069TAP 345 1
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2018-065 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.13225 | 104.34 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2018-068 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.13225 | 104.34 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2018-083 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.11258 | 104.34 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2018-090 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.68566 | 104.34 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2018-131 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.13225 | 104.34 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2018-132 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.13225 | 104.34 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2019-069 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.11258 | 104.34 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2019-070 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.11258 | 104.34 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2019-073 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.11258 | 104.34 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2018-065 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.1322 | 104.28 | P23:345:MEC:CBEC 908
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2018-068 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.1322 | 104.28 | P23:345:MEC:CBEC 908
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2018-083 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.11253 | 104.28 | P23:345:MEC:CBEC 908
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2018-090 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.68554 | 104.28 | P23:345:MEC:CBEC 908
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2018-131 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.1322 | 104.28 | P23:345:MEC:CBEC 908
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2018-132 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.1322 | 104.28 | P23:345:MEC:CBEC 908
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2019-069 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.11253 | 104.28 | P23:345:MEC:CBEC 908
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2019-070 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.11253 | 104.28 | P23:345:MEC:CBEC 908
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2019-073 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.11253 | 104.28 | P23:345:MEC:CBEC 908
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2018-065 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.14637 | 104.2 | 635600 GRIMES 3 345 636003 BVR CRK 3 345 1
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2018-068 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.14637 | 104.2 | 635600 GRIMES 3 345 636003 BVR CRK 3 345 1
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2018-083 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.12508 | 104.2 | 635600 GRIMES 3 345 636003 BVR CRK 3 345 1
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2018-090 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.69117 | 104.2 | 635600 GRIMES 3 345 636003 BVR CRK 3 345 1
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2018-131 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.14637 | 104.2 | 635600 GRIMES 3 345 636003 BVR CRK 3 345 1
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2018-132 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.14637 | 104.2 | 635600 GRIMES 3 345 636003 BVR CRK 3 345 1
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2019-069 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.12508 | 104.2 | 635600 GRIMES 3 345 636003 BVR CRK 3 345 1
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2019-070 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.12508 | 104.2 | 635600 GRIMES 3 345 636003 BVR CRK 3 345 1
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2019-073 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.12508 | 104.2 | 635600 GRIMES 3 345 636003 BVR CRK 3 345 1
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2018-065 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.18748 | 104 | P42:345:NPPD:BKR-CPR-3316:::::
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2018-068 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.18748 | 104 | P42:345:NPPD:BKR-CPR-3316:::::
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2018-083 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.18309 | 104 | P42:345:NPPD:BKR-CPR-3316:::::
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2018-090 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.68952 | 104 | P42:345:NPPD:BKR-CPR-3316:::::
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2018-131 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.18748 | 104 | P42:345:NPPD:BKR-CPR-3316:::::
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2018-132 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.18748 | 104 | P42:345:NPPD:BKR-CPR-3316:::::
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2019-039 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.06593 | 104 | P42:345:NPPD:BKR-CPR-3316:::::
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2019-069 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.18309 | 104 | P42:345:NPPD:BKR-CPR-3316:::::
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2019-070 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.18309 | 104 | P42:345:NPPD:BKR-CPR-3316:::::
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2019-073 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.18309 | 104 | P42:345:NPPD:BKR-CPR-3316:::::
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2018-065 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.18019 | 103.28 | P42:345:LES:L3516::NW68&HOLDREGE.MOORE.CB3005
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2018-068 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.18019 | 103.28 | P42:345:LES:L3516::NW68&HOLDREGE.MOORE.CB3005
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2018-083 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.17232 | 103.28 | P42:345:LES:L3516::NW68&HOLDREGE.MOORE.CB3005
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2018-090 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.68734 | 103.28 | P42:345:LES:L3516::NW68&HOLDREGE.MOORE.CB3005
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2018-131 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.18019 | 103.28 | P42:345:LES:L3516::NW68&HOLDREGE.MOORE.CB3005 | 652425 BELFELD4 230 996760 BEF KU2A _1 230 1
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2018-132 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.18019 | 103.28 | P42:345:LES:L3516::NW68&HOLDREGE.MOORE.CB3005
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2019-039 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.08111 | 103.28 | P42:345:LES:L3516::NW68&HOLDREGE.MOORE.CB3005
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2019-069 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.17232 | 103.28 | P42:345:LES:L3516::NW68&HOLDREGE.MOORE.CB3005
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2019-070 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.17232 | 103.28 | P42:345:LES:L3516::NW68&HOLDREGE.MOORE.CB3005
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2019-073 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.17232 | 103.28 | P42:345:LES:L3516::NW68&HOLDREGE.MOORE.CB3005
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2018-065 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.18055 | 102.97 | P42:345:LES:L1485::NW68&HOLDREGE.WAGENER.CB3006
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2018-068 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.18055 | 102.97 | P42:345:LES:L1485::NW68&HOLDREGE.WAGENER.CB3006
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2018-083 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.17275 | 102.97 | P42:345:LES:L1485::NW68&HOLDREGE.WAGENER.CB3006
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2018-090 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.68707 | 102.97 | P42:345:LES:L1485::NW68&HOLDREGE.WAGENER.CB3006
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2018-131 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.18055 | 102.97 | P42:345:LES:L1485::NW68&HOLDREGE.WAGENER.CB3006
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2018-132 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.18055 | 102.97 | P42:345:LES:L1485::NW68&HOLDREGE.WAGENER.CB3006
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2019-039 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.08285 | 102.97 | P42:345:LES:L1485::NW68&HOLDREGE.WAGENER.CB3006
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2019-069 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.17275 | 102.97 | P42:345:LES:L1485::NW68&HOLDREGE.WAGENER.CB3006
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2019-070 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.17275 | 102.97 | P42:345:LES:L1485::NW68&HOLDREGE.WAGENER.CB3006
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2019-073 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.17275 | 102.97 | P42:345:LES:L1485::NW68&HOLDREGE.WAGENER.CB3006
Thermal | 02ALL | 1 | 02ALL-23SP | GEN-2018-065 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.13411 | 102.9 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4
Thermal | 02ALL | 1 | 02ALL-23SP | GEN-2018-068 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.13411 | 102.9 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4
Thermal | 02ALL | 1 | 02ALL-23SP | GEN-2018-083 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.11426 | 102.9 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4
Thermal | 02ALL | 1 | 02ALL-23SP | GEN-2018-090 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.68711 | 102.9 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4
Thermal | 02ALL | 1 | 02ALL-23SP | GEN-2018-131 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.13411 | 102.9 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4
Thermal | 02ALL | 1 | 02ALL-23SP | GEN-2018-132 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.13411 | 102.9 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4
Thermal | 02ALL | 1 | 02ALL-23SP | GEN-2019-069 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.11426 | 102.9 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4
Thermal | 02ALL | 1 | 02ALL-23SP | GEN-2019-070 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.11426 | 102.9 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4
Thermal | 02ALL | 1 | 02ALL-23SP | GEN-2019-073 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.11426 | 102.9 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2018-065 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.14637 | 102.89 | 636003 BVR CRK 3 345 636010 LEHIGH 3 345 1
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2018-068 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.14637 | 102.89 | 636003 BVR CRK 3 345 636010 LEHIGH 3 345 1
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2018-083 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.12508 | 102.89 | 636003 BVR CRK 3 345 636010 LEHIGH 3 345 1
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2018-090 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.69117 | 102.89 | 636003 BVR CRK 3 345 636010 LEHIGH 3 345 1
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2018-131 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.14637 | 102.89 | 636003 BVR CRK 3 345 636010 LEHIGH 3 345 1
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2018-132 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.14637 | 102.89 | 636003 BVR CRK 3 345 636010 LEHIGH 3 345 1
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2019-069 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.12508 | 102.89 | 636003 BVR CRK 3 345 636010 LEHIGH 3 345 1
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2019-070 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.12508 | 102.89 | 636003 BVR CRK 3 345 636010 LEHIGH 3 345 1
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2019-073 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.12508 | 102.89 | 636003 BVR CRK 3 345 636010 LEHIGH 3 345 1
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2018-065 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.13225 | 102.86 | P11:345:MEC-NPPD:COOPER 1
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2018-068 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.13225 | 102.86 | P11:345:MEC-NPPD:COOPER 1
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2018-083 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.11258 | 102.86 | P11:345:MEC-NPPD:COOPER 1
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2018-090 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.68566 | 102.86 | P11:345:MEC-NPPD:COOPER 1
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2018-131 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.13225 | 102.86 | P11:345:MEC-NPPD:COOPER 1
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2018-132 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.13225 | 102.86 | P11:345:MEC-NPPD:COOPER 1
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2019-069 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.11258 | 102.86 | P11:345:MEC-NPPD:COOPER 1
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2019-070 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.11258 | 102.86 | P11:345:MEC-NPPD:COOPER 1
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2019-073 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.11258 | 102.86 | P11:345:MEC-NPPD:COOPER 1
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2018-065 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.18076 | 102.71 | P12:345:NPPD:L3521::NW68&HOLDREGE.COLUMBUSEAST.CKT1
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2018-068 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.18076 | 102.71 | P12:345:NPPD:L3521::NW68&HOLDREGE.COLUMBUSEAST.CKT1
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2018-083 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.17288 | 102.71 | P12:345:NPPD:L3521::NW68&HOLDREGE.COLUMBUSEAST.CKT1
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2018-090 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.68862 | 102.71 | P12:345:NPPD:L3521::NW68&HOLDREGE.COLUMBUSEAST.CKT1
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2018-131 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.18076 | 102.71 | P12:345:NPPD:L3521::NW68&HOLDREGE.COLUMBUSEAST.CKT1
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2018-132 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.18076 | 102.71 | P12:345:NPPD:L3521::NW68&HOLDREGE.COLUMBUSEAST.CKT1
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2019-039 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.08204 | 102.71 | P12:345:NPPD:L3521::NW68&HOLDREGE.COLUMBUSEAST.CKT1
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2019-069 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.17288 | 102.71 | P12:345:NPPD:L3521::NW68&HOLDREGE.COLUMBUSEAST.CKT1
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2019-070 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.17288 | 102.71 | P12:345:NPPD:L3521::NW68&HOLDREGE.COLUMBUSEAST.CKT1
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2019-073 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.17288 | 102.71 | P12:345:NPPD:L3521::NW68&HOLDREGE.COLUMBUSEAST.CKT1
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2018-065 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.13225 | 102.66 | P11:022:NPPD:COOPER1G:1:983:::
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2018-068 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.13225 | 102.66 | P11:022:NPPD:COOPER1G:1:983:::
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2018-083 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.11258 | 102.66 | P11:022:NPPD:COOPER1G:1:983:::
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2018-090 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.68566 | 102.66 | P11:022:NPPD:COOPER1G:1:983:::
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2018-131 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.13225 | 102.66 | P11:022:NPPD:COOPER1G:1:983:::
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2018-132 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.13225 | 102.66 | P11:022:NPPD:COOPER1G:1:983:::
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2019-069 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.11258 | 102.66 | P11:022:NPPD:COOPER1G:1:983:::
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2019-070 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.11258 | 102.66 | P11:022:NPPD:COOPER1G:1:983:::
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2019-073 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.11258 | 102.66 | P11:022:NPPD:COOPER1G:1:983:::
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2018-065 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.13225 | 102.57 | P23:345:OPPD:S3458 NEBCTY2G:LT::EHV:
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2018-065 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.13225 | 102.57 | P22:345:OPPD:S3458 NEBCTY2G:LT::EHV:
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2018-068 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.13225 | 102.57 | P23:345:OPPD:S3458 NEBCTY2G:LT::EHV:
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2018-068 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.13225 | 102.57 | P22:345:OPPD:S3458 NEBCTY2G:LT::EHV:
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2018-083 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.11258 | 102.57 | P23:345:OPPD:S3458 NEBCTY2G:LT::EHV:
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2018-083 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.11258 | 102.57 | P22:345:OPPD:S3458 NEBCTY2G:LT::EHV:
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2018-090 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.68566 | 102.57 | P23:345:OPPD:S3458 NEBCTY2G:LT::EHV:
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2018-090 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.68566 | 102.57 | P22:345:OPPD:S3458 NEBCTY2G:LT::EHV:
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2018-131 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.13225 | 102.57 | P23:345:OPPD:S3458 NEBCTY2G:LT::EHV:
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2018-131 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.13225 | 102.57 | P22:345:OPPD:S3458 NEBCTY2G:LT::EHV:
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2018-132 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.13225 | 102.57 | P23:345:OPPD:S3458 NEBCTY2G:LT::EHV:
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2018-132 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.13225 | 102.57 | P22:345:OPPD:S3458 NEBCTY2G:LT::EHV:
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2019-069 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.11258 | 102.57 | P23:345:OPPD:S3458 NEBCTY2G:LT::EHV:
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2019-069 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.11258 | 102.57 | P22:345:OPPD:S3458 NEBCTY2G:LT::EHV:
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2019-070 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.11258 | 102.57 | P23:345:OPPD:S3458 NEBCTY2G:LT::EHV:
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2019-070 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.11258 | 102.57 | P22:345:OPPD:S3458 NEBCTY2G:LT::EHV:
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2019-073 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.11258 | 102.57 | P23:345:OPPD:S3458 NEBCTY2G:LT::EHV:
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2019-073 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.11258 | 102.57 | P22:345:OPPD:S3458 NEBCTY2G:LT::EHV:
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2018-065 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.14937 | 102.5 | 635219 GARD AVE 3 345 636010 LEHIGH 3 345 1
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2018-068 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.14937 | 102.5 | 635219 GARD AVE 3 345 636010 LEHIGH 3 345 1
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2018-083 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.12863 | 102.5 | 635219 GARD AVE 3 345 636010 LEHIGH 3 345 1
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2018-090 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.69832 | 102.5 | 635219 GARD AVE 3 345 636010 LEHIGH 3 345 1
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2018-131 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.14937 | 102.5 | 635219 GARD AVE 3 345 636010 LEHIGH 3 345 1
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2018-132 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.14937 | 102.5 | 635219 GARD AVE 3 345 636010 LEHIGH 3 345 1
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2019-069 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.12863 | 102.5 | 635219 GARD AVE 3 345 636010 LEHIGH 3 345 1
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2019-070 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.12863 | 102.5 | 635219 GARD AVE 3 345 636010 LEHIGH 3 345 1
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2019-073 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.12863 | 102.5 | 635219 GARD AVE 3 345 636010 LEHIGH 3 345 1
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2018-065 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.13225 | 102 | P22:345:OPPD:S3458 NEBCTY1G:LT::EHV:
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2018-068 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.13225 | 102 | P22:345:OPPD:S3458 NEBCTY1G:LT::EHV:
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2018-083 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.11258 | 102 | P22:345:OPPD:S3458 NEBCTY1G:LT::EHV:
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2018-090 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.68566 | 102 | P22:345:OPPD:S3458 NEBCTY1G:LT::EHV:
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2018-131 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.13225 | 102 | P22:345:OPPD:S3458 NEBCTY1G:LT::EHV:
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2018-132 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.13225 | 102 | P22:345:OPPD:S3458 NEBCTY1G:LT::EHV:
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2019-069 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.11258 | 102 | P22:345:OPPD:S3458 NEBCTY1G:LT::EHV:
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2019-070 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.11258 | 102 | P22:345:OPPD:S3458 NEBCTY1G:LT::EHV:
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2019-073 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.11258 | 102 | P22:345:OPPD:S3458 NEBCTY1G:LT::EHV:
Thermal | 02ALL | 1 | 02ALL-23SP | GEN-2018-065 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.13411 | 101.8 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1
Thermal | 02ALL | 1 | 02ALL-23SP | GEN-2018-068 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.13411 | 101.8 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1
Thermal | 02ALL | 1 | 02ALL-23SP | GEN-2018-083 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.11426 | 101.8 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1
Thermal | 02ALL | 1 | 02ALL-23SP | GEN-2018-090 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.68711 | 101.8 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1
Thermal | 02ALL | 1 | 02ALL-23SP | GEN-2018-131 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.13411 | 101.8 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1
Thermal | 02ALL | 1 | 02ALL-23SP | GEN-2018-132 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.13411 | 101.8 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1
Thermal | 02ALL | 1 | 02ALL-23SP | GEN-2019-069 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.11426 | 101.8 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1
Thermal | 02ALL | 1 | 02ALL-23SP | GEN-2019-070 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.11426 | 101.8 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1
Thermal | 02ALL | 1 | 02ALL-23SP | GEN-2019-073 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.11426 | 101.8 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1
Thermal | 02ALL | 1 | 02ALL-23SP | GEN-2018-065 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.14841 | 101.23 | 635600 GRIMES 3 345 636003 BVR CRK 3 345 1
Thermal | 02ALL | 1 | 02ALL-23SP | GEN-2018-068 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.14841 | 101.23 | 635600 GRIMES 3 345 636003 BVR CRK 3 345 1
Thermal | 02ALL | 1 | 02ALL-23SP | GEN-2018-083 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.12691 | 101.23 | 635600 GRIMES 3 345 636003 BVR CRK 3 345 1
Thermal | 02ALL | 1 | 02ALL-23SP | GEN-2018-090 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.69273 | 101.23 | 635600 GRIMES 3 345 636003 BVR CRK 3 345 1
Thermal | 02ALL | 1 | 02ALL-23SP | GEN-2018-131 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.14841 | 101.23 | 635600 GRIMES 3 345 636003 BVR CRK 3 345 1
Thermal | 02ALL | 1 | 02ALL-23SP | GEN-2018-132 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.14841 | 101.23 | 635600 GRIMES 3 345 636003 BVR CRK 3 345 1
Thermal | 02ALL | 1 | 02ALL-23SP | GEN-2019-069 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.12691 | 101.23 | 635600 GRIMES 3 345 636003 BVR CRK 3 345 1
Thermal | 02ALL | 1 | 02ALL-23SP | GEN-2019-070 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.12691 | 101.23 | 635600 GRIMES 3 345 636003 BVR CRK 3 345 1
Thermal | 02ALL | 1 | 02ALL-23SP | GEN-2019-073 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.12691 | 101.23 | 635600 GRIMES 3 345 636003 BVR CRK 3 345 1
Thermal | 02ALL | 1 | 02ALL-23SP | GEN-2018-065 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.13411 | 101.2 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3
Thermal | 02ALL | 1 | 02ALL-23SP | GEN-2018-068 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.13411 | 101.2 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3
Thermal | 02ALL | 1 | 02ALL-23SP | GEN-2018-083 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.11426 | 101.2 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3
Thermal | 02ALL | 1 | 02ALL-23SP | GEN-2018-090 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.68711 | 101.2 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3
Thermal | 02ALL | 1 | 02ALL-23SP | GEN-2018-131 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.13411 | 101.2 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3
Thermal | 02ALL | 1 | 02ALL-23SP | GEN-2018-132 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.13411 | 101.2 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3
Thermal | 02ALL | 1 | 02ALL-23SP | GEN-2019-069 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.11426 | 101.2 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3
Thermal | 02ALL | 1 | 02ALL-23SP | GEN-2019-070 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.11426 | 101.2 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3
Thermal | 02ALL | 1 | 02ALL-23SP | GEN-2019-073 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.11426 | 101.2 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3
Thermal | 02ALL | 1 | 02ALL-23SP | GEN-2018-065 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.13328 | 100.79 | P23:345:MEC:CBEC 905
Thermal | 02ALL | 1 | 02ALL-23SP | GEN-2018-068 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.13328 | 100.79 | P23:345:MEC:CBEC 905
Thermal | 02ALL | 1 | 02ALL-23SP | GEN-2018-083 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.11321 | 100.79 | P23:345:MEC:CBEC 905
Thermal | 02ALL | 1 | 02ALL-23SP | GEN-2018-090 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.68409 | 100.79 | P23:345:MEC:CBEC 905
Thermal | 02ALL | 1 | 02ALL-23SP | GEN-2018-131 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.13328 | 100.79 | P23:345:MEC:CBEC 905
Thermal | 02ALL | 1 | 02ALL-23SP | GEN-2018-132 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.13328 | 100.79 | P23:345:MEC:CBEC 905
Thermal | 02ALL | 1 | 02ALL-23SP | GEN-2019-069 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.11321 | 100.79 | P23:345:MEC:CBEC 905
Thermal | 02ALL | 1 | 02ALL-23SP | GEN-2019-070 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.11321 | 100.79 | P23:345:MEC:CBEC 905
Thermal | 02ALL | 1 | 02ALL-23SP | GEN-2019-073 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.11321 | 100.79 | P23:345:MEC:CBEC 905
Thermal | 02ALL | 1 | 02ALL-23SP | GEN-2018-065 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.13411 | 100.71 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1
Thermal | 02ALL | 1 | 02ALL-23SP | GEN-2018-068 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.13411 | 100.71 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1
Thermal | 02ALL | 1 | 02ALL-23SP | GEN-2018-083 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.11426 | 100.71 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1
Thermal | 02ALL | 1 | 02ALL-23SP | GEN-2018-090 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.68711 | 100.71 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1
Thermal | 02ALL | 1 | 02ALL-23SP | GEN-2018-131 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.13411 | 100.71 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1
Thermal | 02ALL | 1 | 02ALL-23SP | GEN-2018-132 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.13411 | 100.71 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1
Thermal | 02ALL | 1 | 02ALL-23SP | GEN-2019-069 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.11426 | 100.71 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1
Thermal | 02ALL | 1 | 02ALL-23SP | GEN-2019-070 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.11426 | 100.71 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1
Thermal | 02ALL | 1 | 02ALL-23SP | GEN-2019-073 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.11426 | 100.71 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1
Thermal | 02ALL | 1 | 02ALL-23SP | GEN-2018-065 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.13407 | 100.63 | P23:345:MEC:CBEC 908
Thermal | 02ALL | 1 | 02ALL-23SP | GEN-2018-068 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.13407 | 100.63 | P23:345:MEC:CBEC 908
Thermal | 02ALL | 1 | 02ALL-23SP | GEN-2018-083 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.11421 | 100.63 | P23:345:MEC:CBEC 908
Thermal | 02ALL | 1 | 02ALL-23SP | GEN-2018-090 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.68699 | 100.63 | P23:345:MEC:CBEC 908
Thermal | 02ALL | 1 | 02ALL-23SP | GEN-2018-131 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.13407 | 100.63 | P23:345:MEC:CBEC 908
Thermal | 02ALL | 1 | 02ALL-23SP | GEN-2018-132 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.13407 | 100.63 | P23:345:MEC:CBEC 908
Thermal | 02ALL | 1 | 02ALL-23SP | GEN-2019-069 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.11421 | 100.63 | P23:345:MEC:CBEC 908
Thermal | 02ALL | 1 | 02ALL-23SP | GEN-2019-070 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.11421 | 100.63 | P23:345:MEC:CBEC 908
Thermal | 02ALL | 1 | 02ALL-23SP | GEN-2019-073 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.11421 | 100.63 | P23:345:MEC:CBEC 908
Thermal | 02ALL | 1 | 02ALL-23SP | GEN-2018-065 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.18983 | 100.41 | P42:345:NPPD:BKR-CPR-3316:::::
Thermal | 02ALL | 1 | 02ALL-23SP | GEN-2018-068 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.18983 | 100.41 | P42:345:NPPD:BKR-CPR-3316:::::
Thermal | 02ALL | 1 | 02ALL-23SP | GEN-2018-083 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.18524 | 100.41 | P42:345:NPPD:BKR-CPR-3316:::::
Thermal | 02ALL | 1 | 02ALL-23SP | GEN-2018-090 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.69113 | 100.41 | P42:345:NPPD:BKR-CPR-3316:::::
Thermal | 02ALL | 1 | 02ALL-23SP | GEN-2018-131 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.18983 | 100.41 | P42:345:NPPD:BKR-CPR-3316:::::
Thermal | 02ALL | 1 | 02ALL-23SP | GEN-2018-132 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.18983 | 100.41 | P42:345:NPPD:BKR-CPR-3316:::::
Thermal | 02ALL | 1 | 02ALL-23SP | GEN-2019-039 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.06776 | 100.41 | P42:345:NPPD:BKR-CPR-3316:::::
Thermal | 02ALL | 1 | 02ALL-23SP | GEN-2019-069 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.18524 | 100.41 | P42:345:NPPD:BKR-CPR-3316:::::
Thermal | 02ALL | 1 | 02ALL-23SP | GEN-2019-070 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.18524 | 100.41 | P42:345:NPPD:BKR-CPR-3316:::::
Thermal | 02ALL | 1 | 02ALL-23SP | GEN-2019-073 | FROM->TO | 645451 S3451 3 345 762779 G18-043-TAP 345 1 |  | 956 | 0.18524 | 100.41 | P42:345:NPPD:BKR-CPR-3316:::::
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2018-065 | FROM->TO | 652511 GAVINS 7 115 660006 YANKTON JCT7 115 1 |  | 121 | 0.12006 | 100.37 | 640226 HOSKINS3 345 640520 ANTELOPE 3 345 1
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2018-068 | FROM->TO | 652511 GAVINS 7 115 660006 YANKTON JCT7 115 1 |  | 121 | 0.12006 | 100.37 | 640226 HOSKINS3 345 640520 ANTELOPE 3 345 1
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2018-131 | FROM->TO | 652511 GAVINS 7 115 660006 YANKTON JCT7 115 1 |  | 121 | 0.12006 | 100.37 | 640226 HOSKINS3 345 640520 ANTELOPE 3 345 1
Thermal | 02ALL | 1 | 02ALL-26SP | GEN-2018-132 | FROM->TO | 652511 GAVINS 7 115 660006 YANKTON JCT7 115 1 |  | 121 | 0.12006 | 100.37 | 640226 HOSKINS3 345 640520 ANTELOPE 3 345 1
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2019-029 | FROM->TO | 659807 ELSIETP_-TS7 115 659808 PAXTON__-TS7 115 1 |  | 107 | 0.11286 | 116 | 640183 GENTLMN3 345 640252 KEYSTON3 345 1
Thermal | 02ALL | 1 | 02ALL-26WP | GEN-2019-033 | FROM->TO | 659807 ELSIETP_-TS7 115 659808 PAXTON__-TS7 115 1 |  | 107 | 0.11286 | 116 | 640183 GENTLMN3 345 640252 KEYSTON3 345 1
Non-Converge | 02NR | 0 | N/A | GEN-2018-065 | FROM->TO | None |  |  |  |  | None
Non-Converge | 02NR | 0 | N/A | GEN-2018-068 | FROM->TO | None |  |  |  |  | None
Non-Converge | 02NR | 0 | N/A | GEN-2018-083 | FROM->TO | None |  |  |  |  | None
Non-Converge | 02NR | 0 | N/A | GEN-2018-090 | FROM->TO | None |  |  |  |  | None
Non-Converge | 02NR | 0 | N/A | GEN-2018-125 | FROM->TO | None |  |  |  |  | None
Non-Converge | 02NR | 0 | N/A | GEN-2018-131 | FROM->TO | None |  |  |  |  | None
Non-Converge | 02NR | 0 | N/A | GEN-2018-132 | FROM->TO | None |  |  |  |  | None
Non-Converge | 02NR | 0 | N/A | GEN-2019-009 | FROM->TO | None |  |  |  |  | None
Non-Converge | 02NR | 0 | N/A | GEN-2019-029 | FROM->TO | None |  |  |  |  | None
Non-Converge | 02NR | 0 | N/A | GEN-2019-033 | FROM->TO | None |  |  |  |  | None
Non-Converge | 02NR | 0 | N/A | GEN-2019-039 | FROM->TO | None |  |  |  |  | None
Non-Converge | 02NR | 0 | N/A | GEN-2019-041 | FROM->TO | None |  |  |  |  | None
Non-Converge | 02NR | 0 | N/A | GEN-2019-069 | FROM->TO | None |  |  |  |  | None
Non-Converge | 02NR | 0 | N/A | GEN-2019-070 | FROM->TO | None |  |  |  |  | None
Non-Converge | 02NR | 0 | N/A | GEN-2019-073 | FROM->TO | None |  |  |  |  | None
Non-Converge | 03ALL | 0 | 23SP | N/A | FROM->TO | Non-Converge |  |  |  |  | None
Non-Converge | 03ALL | 0 | 26L | N/A | FROM->TO | Non-Converge |  |  |  |  | None
Non-Converge | 03ALL | 0 | 26SP | N/A | FROM->TO | Non-Converge |  |  |  |  | None
Non-Converge | 03ALL | 0 | 26WP | N/A | FROM->TO | Non-Converge |  |  |  |  | None
Thermal | 03ALL | 1 | 26WP | GEN-2019-001 | FROM->TO | 532791 BENTON 7 345 532796 WICHITA7 345 1 |  | 956 | 0.23867 | 117.49 | P11:345:WERE:WOLFU1-GEN:::EHV:
Thermal | 03ALL | 1 | 26WP | GEN-2019-001 | FROM->TO | 532791 BENTON 7 345 532796 WICHITA7 345 1 |  | 956 | 0.23867 | 117.49 | P11:345:WERE:WOLFU1_GEN::
Thermal | 03ALL | 1 | 26WP | GEN-2019-001 | FROM->TO | 532791 BENTON 7 345 532796 WICHITA7 345 1 |  | 956 | 0.23837 | 116.86 | P23:345:WERE:WOLF-345-60:::EHV:
Thermal | 03ALL | 1 | 26WP | GEN-2019-001 | FROM->TO | 532791 BENTON 7 345 532796 WICHITA7 345 1 |  | 956 | 0.23837 | 116.86 | P23:345:WERE:WOLF_345-60::
Thermal | 03ALL | 1 | 26L | GEN-2019-001 | FROM->TO | 532791 BENTON 7 345 532796 WICHITA7 345 1 |  | 956 | 0.2345 | 108.62 | P42:345:OKGE:SB_REUD7389::::
Thermal | 03ALL | 1 | 26L | GEN-2019-001 | FROM->TO | 532791 BENTON 7 345 532796 WICHITA7 345 1 |  | 956 | 0.2514 | 107.81 | P41:345:OKGE:SB_REUD7383::::
Thermal | 03ALL | 1 | 26L | GEN-2019-001 | FROM->TO | 532791 BENTON 7 345 532796 WICHITA7 345 1 |  | 956 | 0.25238 | 107.46 | P41:345:OKGE:SB_REUD7385::::
Thermal | 03ALL | 1 | 26SP | GEN-2019-001 | FROM->TO | 532791 BENTON 7 345 532796 WICHITA7 345 1 |  | 956 | 0.2408 | 107.4 | P11:345:WERE:WOLFU1-GEN:::EHV:
Thermal | 03ALL | 1 | 26SP | GEN-2019-001 | FROM->TO | 532791 BENTON 7 345 532796 WICHITA7 345 1 |  | 956 | 0.2408 | 107.4 | P11:345:WERE:WOLFU1_GEN::
Thermal | 03ALL | 1 | 26L | GEN-2019-001 | FROM->TO | 532791 BENTON 7 345 532796 WICHITA7 345 1 |  | 956 | 0.25173 | 107.38 | 515543 RENFROW7 345 763421 G18-128-TAP 345 1
Thermal | 03ALL | 1 | 26SP | GEN-2019-001 | FROM->TO | 532791 BENTON 7 345 532796 WICHITA7 345 1 |  | 956 | 0.24049 | 106.73 | P23:345:WERE:WOLF-345-60:::EHV:
Thermal | 03ALL | 1 | 26SP | GEN-2019-001 | FROM->TO | 532791 BENTON 7 345 532796 WICHITA7 345 1 |  | 956 | 0.23481 | 106.37 | P23:345:WERE:WOLF-345-50:::EHV:
Thermal | 03ALL | 1 | 26SP | GEN-2019-001 | FROM->TO | 532791 BENTON 7 345 532796 WICHITA7 345 1 |  | 956 | 0.23481 | 106.37 | P23:345:WERE:WOLF_345-50::
Thermal | 03ALL | 1 | 23SP | GEN-2019-001 | FROM->TO | 532791 BENTON 7 345 532796 WICHITA7 345 1 |  | 956 | 0.23118 | 102.82 | P23:345:WERE:WOLF-345-50:::EHV:
Thermal | 03ALL | 1 | 23SP | GEN-2019-001 | FROM->TO | 532791 BENTON 7 345 532796 WICHITA7 345 1 |  | 956 | 0.23118 | 102.82 | P23:345:WERE:WOLF_345-50::
Thermal | 03ALL | 1 | 23SP | GEN-2019-001 | FROM->TO | 532791 BENTON 7 345 532796 WICHITA7 345 1 |  | 956 | 0.23473 | 102.59 | P11:345:WERE:WOLFU1-GEN:::EHV:
Thermal | 03ALL | 1 | 23SP | GEN-2019-001 | FROM->TO | 532791 BENTON 7 345 532796 WICHITA7 345 1 |  | 956 | 0.23473 | 102.59 | P11:345:WERE:WOLFU1_GEN::
Thermal | 03ALL | 1 | 26WP | GEN-2018-093 | FROM->TO | 532791 BENTON 7 345 532796 WICHITA7 345 1 | 878 |  | 0.07375 | 102.33 | System Intact
Thermal | 03ALL | 1 | 26WP | GEN-2018-108 | FROM->TO | 532791 BENTON 7 345 532796 WICHITA7 345 1 | 878 |  | 0.15109 | 102.33 | System Intact
Thermal | 03ALL | 1 | 26WP | GEN-2018-116 | FROM->TO | 532791 BENTON 7 345 532796 WICHITA7 345 1 | 878 |  | 0.11603 | 102.33 | System Intact
Thermal | 03ALL | 1 | 26WP | GEN-2018-128 | FROM->TO | 532791 BENTON 7 345 532796 WICHITA7 345 1 | 878 |  | 0.10064 | 102.33 | System Intact
Thermal | 03ALL | 1 | 26WP | GEN-2019-001 | FROM->TO | 532791 BENTON 7 345 532796 WICHITA7 345 1 | 878 |  | 0.23867 | 102.33 | System Intact
Thermal | 03ALL | 1 | 26WP | GEN-2019-014 | FROM->TO | 532791 BENTON 7 345 532796 WICHITA7 345 1 | 878 |  | 0.08902 | 102.33 | System Intact
Thermal | 03ALL | 1 | 26WP | GEN-2019-030 | FROM->TO | 532791 BENTON 7 345 532796 WICHITA7 345 1 | 878 |  | 0.11516 | 102.33 | System Intact
Thermal | 03ALL | 1 | 26WP | GEN-2019-044 | FROM->TO | 532791 BENTON 7 345 532796 WICHITA7 345 1 | 878 |  | 0.11318 | 102.33 | System Intact
Thermal | 03ALL | 1 | 26WP | GEN-2019-051 | FROM->TO | 532791 BENTON 7 345 532796 WICHITA7 345 1 | 878 |  | 0.11603 | 102.33 | System Intact
Thermal | 03ALL | 1 | 26WP | GEN-2019-053 | FROM->TO | 532791 BENTON 7 345 532796 WICHITA7 345 1 | 878 |  | 0.11427 | 102.33 | System Intact
Thermal | 03ALL | 1 | 26WP | GEN-2019-054 | FROM->TO | 532791 BENTON 7 345 532796 WICHITA7 345 1 | 878 |  | 0.11843 | 102.33 | System Intact
Thermal | 03ALL | 1 | 26WP | GEN-2019-055 | FROM->TO | 532791 BENTON 7 345 532796 WICHITA7 345 1 | 878 |  | 0.11427 | 102.33 | System Intact
Thermal | 03ALL | 1 | 26WP | GEN-2019-058 | FROM->TO | 532791 BENTON 7 345 532796 WICHITA7 345 1 | 878 |  | 0.12512 | 102.33 | System Intact
Thermal | 03ALL | 1 | 26WP | GEN-2019-063 | FROM->TO | 532791 BENTON 7 345 532796 WICHITA7 345 1 | 878 |  | 0.12512 | 102.33 | System Intact
Thermal | 03ALL | 1 | 26WP | GEN-2019-068 | FROM->TO | 532791 BENTON 7 345 532796 WICHITA7 345 1 | 878 |  | 0.11843 | 102.33 | System Intact
Thermal | 03ALL | 1 | 23SP | GEN-2019-001 | FROM->TO | 532791 BENTON 7 345 532796 WICHITA7 345 1 |  | 956 | 0.2341 | 101.61 | P23:345:WERE:WOLF-345-60:::EHV:
Thermal | 03ALL | 1 | 26WP | GEN-2018-093 | FROM->TO | 532987 BUTLER 4 138 532990 MIDIAN 4 138 1 | 143 |  | 0.04752 | 100.74 | System Intact
Thermal | 03ALL | 1 | 26SP | GEN-2018-116 | FROM->TO | 539642 ELLSWTP3 115 539678 GRTBEND3 115 1 |  | 89.8 | 0.11169 | 114.49 | 532871 CIRCLE 6 230 763862 G19-054-TAP 230 1
Thermal | 03ALL | 1 | 26SP | GEN-2019-051 | FROM->TO | 539642 ELLSWTP3 115 539678 GRTBEND3 115 1 |  | 89.8 | 0.11169 | 114.49 | 532871 CIRCLE 6 230 763862 G19-054-TAP 230 1
Thermal | 03ALL | 1 | 26SP | GEN-2019-054 | FROM->TO | 539642 ELLSWTP3 115 539678 GRTBEND3 115 1 |  | 89.8 | 0.07785 | 114.49 | 532871 CIRCLE 6 230 763862 G19-054-TAP 230 1
Thermal | 03ALL | 1 | 26SP | GEN-2019-068 | FROM->TO | 539642 ELLSWTP3 115 539678 GRTBEND3 115 1 |  | 89.8 | 0.07785 | 114.49 | 532871 CIRCLE 6 230 763862 G19-054-TAP 230 1
Thermal | 03ALL | 1 | 23SP | GEN-2018-116 | FROM->TO | 539642 ELLSWTP3 115 539678 GRTBEND3 115 1 |  | 89.8 | 0.11173 | 114 | 532871 CIRCLE 6 230 763862 G19-054-TAP 230 1
Thermal | 03ALL | 1 | 23SP | GEN-2019-051 | FROM->TO | 539642 ELLSWTP3 115 539678 GRTBEND3 115 1 |  | 89.8 | 0.11173 | 114 | 532871 CIRCLE 6 230 763862 G19-054-TAP 230 1
Thermal | 03ALL | 1 | 23SP | GEN-2019-054 | FROM->TO | 539642 ELLSWTP3 115 539678 GRTBEND3 115 1 |  | 89.8 | 0.0779 | 114 | 532871 CIRCLE 6 230 763862 G19-054-TAP 230 1
Thermal | 03ALL | 1 | 23SP | GEN-2019-068 | FROM->TO | 539642 ELLSWTP3 115 539678 GRTBEND3 115 1 |  | 89.8 | 0.0779 | 114 | 532871 CIRCLE 6 230 763862 G19-054-TAP 230 1
Thermal | 03ALL | 1 | 26SP | GEN-2018-116 | FROM->TO | 539642 ELLSWTP3 115 539678 GRTBEND3 115 1 |  | 89.8 | 0.08518 | 105.52 | P13:115-230:MIDW:RICE COUNTY:::HV:
Thermal | 03ALL | 1 | 26SP | GEN-2019-051 | FROM->TO | 539642 ELLSWTP3 115 539678 GRTBEND3 115 1 |  | 89.8 | 0.08518 | 105.52 | P13:115-230:MIDW:RICE COUNTY:::HV:
Thermal | 03ALL | 1 | 23SP | GEN-2018-116 | FROM->TO | 539642 ELLSWTP3 115 539678 GRTBEND3 115 1 |  | 89.8 | 0.08521 | 105.18 | P13:115-230:MIDW:RICE COUNTY:::HV:
Thermal | 03ALL | 1 | 23SP | GEN-2019-051 | FROM->TO | 539642 ELLSWTP3 115 539678 GRTBEND3 115 1 |  | 89.8 | 0.08521 | 105.18 | P13:115-230:MIDW:RICE COUNTY:::HV:
Thermal | 03ALL | 1 | 23SP | GEN-2019-044 | FROM->TO | 539659 CUDAHY 3 115 539783 CRKCK 3 115 1 | 119.5 |  | 0.11868 | 107.19 | System Intact
Thermal | 03ALL | 1 | 26SP | GEN-2019-044 | FROM->TO | 539659 CUDAHY 3 115 539783 CRKCK 3 115 1 | 119.5 |  | 0.11871 | 104.82 | System Intact
Thermal | 03ALL | 1 | 26WP | GEN-2018-116 | FROM->TO | 539661 24-FREY3 115 539681 N-GBEND3 115 1 |  | 148.2 | 1 | 119.18 | 539661 24-FREY3 115 539689 2ND-KS 3 115 1
Thermal | 03ALL | 1 | 26WP | GEN-2019-051 | FROM->TO | 539661 24-FREY3 115 539681 N-GBEND3 115 1 |  | 148.2 | 1 | 119.18 | 539661 24-FREY3 115 539689 2ND-KS 3 115 1
Thermal | 03ALL | 1 | 23SP | GEN-2018-116 | FROM->TO | 539661 24-FREY3 115 539681 N-GBEND3 115 1 |  | 148.2 | 1 | 116.08 | 539661 24-FREY3 115 539689 2ND-KS 3 115 1
Thermal | 03ALL | 1 | 23SP | GEN-2019-051 | FROM->TO | 539661 24-FREY3 115 539681 N-GBEND3 115 1 |  | 148.2 | 1 | 116.08 | 539661 24-FREY3 115 539689 2ND-KS 3 115 1
Thermal | 03ALL | 1 | 26SP | GEN-2018-116 | FROM->TO | 539661 24-FREY3 115 539681 N-GBEND3 115 1 |  | 148.2 | 1 | 115.87 | 539661 24-FREY3 115 539689 2ND-KS 3 115 1
Thermal | 03ALL | 1 | 26SP | GEN-2019-051 | FROM->TO | 539661 24-FREY3 115 539681 N-GBEND3 115 1 |  | 148.2 | 1 | 115.87 | 539661 24-FREY3 115 539689 2ND-KS 3 115 1
Thermal | 03ALL | 1 | 26WP | GEN-2018-116 | FROM->TO | 539661 24-FREY3 115 539681 N-GBEND3 115 1 |  | 148.2 | 1 | 111.41 | 539666 GBENDTP3 115 539689 2ND-KS 3 115 1
Thermal | 03ALL | 1 | 26WP | GEN-2018-116 | FROM->TO | 539661 24-FREY3 115 539681 N-GBEND3 115 1 |  | 148.2 | 1 | 111.41 | P12:115:SUNC:SAINTJOHN-GREATBEND:::HV:
Thermal | 03ALL | 1 | 26WP | GEN-2019-051 | FROM->TO | 539661 24-FREY3 115 539681 N-GBEND3 115 1 |  | 148.2 | 1 | 111.41 | 539666 GBENDTP3 115 539689 2ND-KS 3 115 1
Thermal | 03ALL | 1 | 26WP | GEN-2019-051 | FROM->TO | 539661 24-FREY3 115 539681 N-GBEND3 115 1 |  | 148.2 | 1 | 111.41 | P12:115:SUNC:SAINTJOHN-GREATBEND:::HV:
Thermal | 03ALL | 1 | 26WP | GEN-2018-116 | FROM->TO | 539661 24-FREY3 115 539681 N-GBEND3 115 1 |  | 148.2 | 1 | 111.39 | P12:115:MIDW:GREAT BEND-SEWARD-ST.JOHN:::HV:
Thermal | 03ALL | 1 | 26WP | GEN-2019-051 | FROM->TO | 539661 24-FREY3 115 539681 N-GBEND3 115 1 |  | 148.2 | 1 | 111.39 | P12:115:MIDW:GREAT BEND-SEWARD-ST.JOHN:::HV:
Thermal | 03ALL | 1 | 23SP | GEN-2018-116 | FROM->TO | 539661 24-FREY3 115 539681 N-GBEND3 115 1 |  | 148.2 | 1 | 104.63 | 539666 GBENDTP3 115 539689 2ND-KS 3 115 1
Thermal | 03ALL | 1 | 23SP | GEN-2019-051 | FROM->TO | 539661 24-FREY3 115 539681 N-GBEND3 115 1 |  | 148.2 | 1 | 104.63 | 539666 GBENDTP3 115 539689 2ND-KS 3 115 1
Thermal | 03ALL | 1 | 23SP | GEN-2018-116 | FROM->TO | 539661 24-FREY3 115 539681 N-GBEND3 115 1 |  | 148.2 | 1 | 104.48 | P12:115:SUNC:SAINTJOHN-GREATBEND:::HV:
Thermal | 03ALL | 1 | 23SP | GEN-2019-051 | FROM->TO | 539661 24-FREY3 115 539681 N-GBEND3 115 1 |  | 148.2 | 1 | 104.48 | P12:115:SUNC:SAINTJOHN-GREATBEND:::HV:
Thermal | 03ALL | 1 | 23SP | GEN-2018-116 | FROM->TO | 539661 24-FREY3 115 539681 N-GBEND3 115 1 |  | 148.2 | 1 | 104.45 | P12:115:MIDW:GREAT BEND-SEWARD-ST.JOHN:::HV:
Thermal | 03ALL | 1 | 23SP | GEN-2019-051 | FROM->TO | 539661 24-FREY3 115 539681 N-GBEND3 115 1 |  | 148.2 | 1 | 104.45 | P12:115:MIDW:GREAT BEND-SEWARD-ST.JOHN:::HV:
Thermal | 03ALL | 1 | 26SP | GEN-2018-116 | FROM->TO | 539661 24-FREY3 115 539681 N-GBEND3 115 1 |  | 148.2 | 1 | 104.02 | 539666 GBENDTP3 115 539689 2ND-KS 3 115 1
Thermal | 03ALL | 1 | 26SP | GEN-2019-051 | FROM->TO | 539661 24-FREY3 115 539681 N-GBEND3 115 1 |  | 148.2 | 1 | 104.02 | 539666 GBENDTP3 115 539689 2ND-KS 3 115 1
Thermal | 03ALL | 1 | 26SP | GEN-2018-116 | FROM->TO | 539661 24-FREY3 115 539681 N-GBEND3 115 1 |  | 148.2 | 1 | 103.93 | P12:115:SUNC:SAINTJOHN-GREATBEND:::HV:
Thermal | 03ALL | 1 | 26SP | GEN-2019-051 | FROM->TO | 539661 24-FREY3 115 539681 N-GBEND3 115 1 |  | 148.2 | 1 | 103.93 | P12:115:SUNC:SAINTJOHN-GREATBEND:::HV:
Thermal | 03ALL | 1 | 26SP | GEN-2018-116 | FROM->TO | 539661 24-FREY3 115 539681 N-GBEND3 115 1 |  | 148.2 | 1 | 103.91 | P12:115:MIDW:GREAT BEND-SEWARD-ST.JOHN:::HV:
Thermal | 03ALL | 1 | 26SP | GEN-2019-051 | FROM->TO | 539661 24-FREY3 115 539681 N-GBEND3 115 1 |  | 148.2 | 1 | 103.91 | P12:115:MIDW:GREAT BEND-SEWARD-ST.JOHN:::HV:
Thermal | 03ALL | 1 | 26WP | GEN-2018-116 | FROM->TO | 539661 24-FREY3 115 539689 2ND-KS 3 115 1 |  | 148.2 | 1 | 119.16 | 539661 24-FREY3 115 539681 N-GBEND3 115 1
Thermal | 03ALL | 1 | 26WP | GEN-2019-051 | FROM->TO | 539661 24-FREY3 115 539689 2ND-KS 3 115 1 |  | 148.2 | 1 | 119.16 | 539661 24-FREY3 115 539681 N-GBEND3 115 1
Thermal | 03ALL | 1 | 23SP | GEN-2018-116 | FROM->TO | 539661 24-FREY3 115 539689 2ND-KS 3 115 1 |  | 148.2 | 1 | 116.05 | 539661 24-FREY3 115 539681 N-GBEND3 115 1
Thermal | 03ALL | 1 | 23SP | GEN-2019-051 | FROM->TO | 539661 24-FREY3 115 539689 2ND-KS 3 115 1 |  | 148.2 | 1 | 116.05 | 539661 24-FREY3 115 539681 N-GBEND3 115 1
Thermal | 03ALL | 1 | 26SP | GEN-2018-116 | FROM->TO | 539661 24-FREY3 115 539689 2ND-KS 3 115 1 |  | 148.2 | 1 | 115.87 | 539661 24-FREY3 115 539681 N-GBEND3 115 1
Thermal | 03ALL | 1 | 26SP | GEN-2019-051 | FROM->TO | 539661 24-FREY3 115 539689 2ND-KS 3 115 1 |  | 148.2 | 1 | 115.87 | 539661 24-FREY3 115 539681 N-GBEND3 115 1
Thermal | 03ALL | 1 | 26WP | GEN-2018-116 | FROM->TO | 539661 24-FREY3 115 539689 2ND-KS 3 115 1 |  | 148.2 | 0.9998 | 114.11 | 539678 GRTBEND3 115 539681 N-GBEND3 115 1
Thermal | 03ALL | 1 | 26WP | GEN-2019-051 | FROM->TO | 539661 24-FREY3 115 539689 2ND-KS 3 115 1 |  | 148.2 | 0.9998 | 114.11 | 539678 GRTBEND3 115 539681 N-GBEND3 115 1
Thermal | 03ALL | 1 | 23SP | GEN-2018-116 | FROM->TO | 539661 24-FREY3 115 539689 2ND-KS 3 115 1 |  | 148.2 | 0.99968 | 110.33 | 539678 GRTBEND3 115 539681 N-GBEND3 115 1
Thermal | 03ALL | 1 | 23SP | GEN-2019-051 | FROM->TO | 539661 24-FREY3 115 539689 2ND-KS 3 115 1 |  | 148.2 | 0.99968 | 110.33 | 539678 GRTBEND3 115 539681 N-GBEND3 115 1
Thermal | 03ALL | 1 | 26SP | GEN-2018-116 | FROM->TO | 539661 24-FREY3 115 539689 2ND-KS 3 115 1 |  | 148.2 | 0.99967 | 109.96 | 539678 GRTBEND3 115 539681 N-GBEND3 115 1
Thermal | 03ALL | 1 | 26SP | GEN-2019-051 | FROM->TO | 539661 24-FREY3 115 539689 2ND-KS 3 115 1 |  | 148.2 | 0.99967 | 109.96 | 539678 GRTBEND3 115 539681 N-GBEND3 115 1
Thermal | 03ALL | 1 | 23SP | GEN-2018-116 | FROM->TO | 539666 GBENDTP3 115 539689 2ND-KS 3 115 1 |  | 91.4 | 1 | 169.99 | 539661 24-FREY3 115 539681 N-GBEND3 115 1
Thermal | 03ALL | 1 | 23SP | GEN-2019-051 | FROM->TO | 539666 GBENDTP3 115 539689 2ND-KS 3 115 1 |  | 91.4 | 1 | 169.99 | 539661 24-FREY3 115 539681 N-GBEND3 115 1
Thermal | 03ALL | 1 | 26SP | GEN-2018-116 | FROM->TO | 539666 GBENDTP3 115 539689 2ND-KS 3 115 1 |  | 91.4 | 1 | 169.04 | 539661 24-FREY3 115 539681 N-GBEND3 115 1
Thermal | 03ALL | 1 | 26SP | GEN-2019-051 | FROM->TO | 539666 GBENDTP3 115 539689 2ND-KS 3 115 1 |  | 91.4 | 1 | 169.04 | 539661 24-FREY3 115 539681 N-GBEND3 115 1
Thermal | 03ALL | 1 | 23SP | GEN-2018-116 | FROM->TO | 539666 GBENDTP3 115 539689 2ND-KS 3 115 1 |  | 91.4 | 0.99968 | 160.78 | 539678 GRTBEND3 115 539681 N-GBEND3 115 1
Thermal | 03ALL | 1 | 23SP | GEN-2019-051 | FROM->TO | 539666 GBENDTP3 115 539689 2ND-KS 3 115 1 |  | 91.4 | 0.99968 | 160.78 | 539678 GRTBEND3 115 539681 N-GBEND3 115 1
Thermal | 03ALL | 1 | 26SP | GEN-2018-116 | FROM->TO | 539666 GBENDTP3 115 539689 2ND-KS 3 115 1 |  | 91.4 | 0.99967 | 159.53 | 539678 GRTBEND3 115 539681 N-GBEND3 115 1
Thermal | 03ALL | 1 | 26SP | GEN-2019-051 | FROM->TO | 539666 GBENDTP3 115 539689 2ND-KS 3 115 1 |  | 91.4 | 0.99967 | 159.53 | 539678 GRTBEND3 115 539681 N-GBEND3 115 1
Thermal | 03ALL | 1 | 26WP | GEN-2018-116 | FROM->TO | 539666 GBENDTP3 115 539689 2ND-KS 3 115 1 |  | 118.5 | 1 | 139.47 | 539661 24-FREY3 115 539681 N-GBEND3 115 1
Thermal | 03ALL | 1 | 26WP | GEN-2019-051 | FROM->TO | 539666 GBENDTP3 115 539689 2ND-KS 3 115 1 |  | 118.5 | 1 | 139.47 | 539661 24-FREY3 115 539681 N-GBEND3 115 1
Thermal | 03ALL | 1 | 26WP | GEN-2018-116 | FROM->TO | 539666 GBENDTP3 115 539689 2ND-KS 3 115 1 |  | 118.5 | 0.9998 | 133.14 | 539678 GRTBEND3 115 539681 N-GBEND3 115 1
Thermal | 03ALL | 1 | 26WP | GEN-2019-051 | FROM->TO | 539666 GBENDTP3 115 539689 2ND-KS 3 115 1 |  | 118.5 | 0.9998 | 133.14 | 539678 GRTBEND3 115 539681 N-GBEND3 115 1
Thermal | 03ALL | 1 | 23SP | GEN-2018-116 | FROM->TO | 539678 GRTBEND3 115 539681 N-GBEND3 115 1 |  | 153.4 | 0.99968 | 106.68 | 539661 24-FREY3 115 539689 2ND-KS 3 115 1
Thermal | 03ALL | 1 | 23SP | GEN-2019-051 | FROM->TO | 539678 GRTBEND3 115 539681 N-GBEND3 115 1 |  | 153.4 | 0.99968 | 106.68 | 539661 24-FREY3 115 539689 2ND-KS 3 115 1
Thermal | 03ALL | 1 | 26SP | GEN-2018-116 | FROM->TO | 539678 GRTBEND3 115 539681 N-GBEND3 115 1 |  | 153.4 | 0.99967 | 106.26 | 539661 24-FREY3 115 539689 2ND-KS 3 115 1
Thermal | 03ALL | 1 | 26SP | GEN-2019-051 | FROM->TO | 539678 GRTBEND3 115 539681 N-GBEND3 115 1 |  | 153.4 | 0.99967 | 106.26 | 539661 24-FREY3 115 539689 2ND-KS 3 115 1
Non-Converge | 03NR | 0 | 26L | N/A | FROM->TO | Non-Converge |  |  |  |  | None
Non-Converge | 04ALL | 0 | 26L | GEN-2018-082 | FROM->TO | Non-Converge |  |  | 0.03106 |  | 511456 O.K.U.-7 345 763215 G18-092-TAP 345 1
Non-Converge | 04ALL | 0 | 26L | GEN-2018-082 | FROM->TO | Non-Converge |  |  | 0.03106 |  | 560022 CRAWFISH_DR 345 762216 G17-151TAP 345 1
Non-Converge | 04ALL | 0 | 26L | GEN-2018-082 | FROM->TO | Non-Converge |  |  | 0.03106 |  | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Non-Converge | 04ALL | 0 | 26L | GEN-2018-082 | FROM->TO | Non-Converge |  |  | 0.03106 |  | 762216 G17-151TAP 345 762467 G18-015-TAP 345 1
Non-Converge | 04ALL | 0 | 26L | GEN-2018-082 | FROM->TO | Non-Converge |  |  | 0.03106 |  | 762467 G18-015-TAP 345 763215 G18-092-TAP 345 1
Non-Converge | 04ALL | 0 | 26L | GEN-2018-082 | FROM->TO | Non-Converge |  |  | 0.03106 |  | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Non-Converge | 04ALL | 0 | 26L | GEN-2018-082 | FROM->TO | Non-Converge |  |  | 0.03106 |  | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Non-Converge | 04ALL | 0 | 23SP | N/A | FROM->TO | None |  |  |  |  | None
Non-Converge | 04ALL | 0 | 26SP | N/A | FROM->TO | None |  |  |  |  | None
Non-Converge | 04ALL | 0 | 26WP | N/A | FROM->TO | None |  |  |  |  | None
Non-Converge | 04ALL | 0 | 26L | GEN-2018-082 | FROM->TO | Non-Converge |  |  | 0.03106 |  | P23:345:AEPW:OKLAUNION CB 3401A NBTB
Non-Converge | 04ALL | 0 | 26L | GEN-2018-082 | FROM->TO | Non-Converge |  |  | 0.03106 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Non-Converge | 04ALL | 0 | 26L | GEN-2018-082 | FROM->TO | Non-Converge |  |  | 0.11934 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Non-Converge | 04ALL | 0 | 26L | GEN-2018-082 | FROM->TO | Non-Converge |  |  | 0.11934 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Thermal | 04ALL | 1 | 23SP | GEN-2018-117 | FROM->TO | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | 349 |  | 0.28742 | 100.91 | System Intact
Thermal | 04ALL | 1 | 23SP | GEN-2018-117 | FROM->TO | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 353 | 1 | 164.55 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1
Thermal | 04ALL | 1 | 23SP | GEN-2018-117 | FROM->TO | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.87401 | 114.63 | 523771 GRAPEVINE 6 230 523777 WHEELER 6 230 1
Thermal | 04ALL | 1 | 23SP | GEN-2018-117 | FROM->TO | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 353 | 1 | 164.55 | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1
Thermal | 04ALL | 1 | 23SP | GEN-2018-117 | FROM->TO | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 353 | 1 | 164.55 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6
Thermal | 04ALL | 1 | 23SP | GEN-2018-117 | FROM->TO | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 |  | 395 | 0.28728 | 100.24 | P43:345:SPS:TUCO:SLG::EHV:
Thermal | 04ALL | 1 | 23SP | GEN-2018-117 | FROM->TO | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 |  | 395 | 0.48719 | 108.77 | P12:345:OKGE-AEPW:BKRBKR371::::
Thermal | 04ALL | 1 | 23SP | GEN-2018-117 | FROM->TO | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 |  | 395 | 0.28654 | 100.42 | 523978 HARRNG_MID 6 230 523972 HARRNGTON2 1 24.0 1
Thermal | 04ALL | 1 | 23SP | GEN-2018-117 | FROM->TO | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 |  | 395 | 0.35177 | 102.14 | P13:138-230:AEPW:ELKCTY-4
Thermal | 04ALL | 1 | 23SP | GEN-2018-117 | FROM->TO | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 |  | 395 | 0.2767 | 115.6 | P42:345:OKGE:SB_BVTY7315_PRE19S
Thermal | 04ALL | 1 | 23SP | GEN-2018-117 | FROM->TO | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 |  | 395 | 0.35177 | 102.12 | P12:230:AEPW:ELKCITY6:CHISHOLM6
Thermal | 04ALL | 1 | 23SP | GEN-2018-117 | FROM->TO | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 |  | 395 | 1 | 148.63 | P12:230:AEPW:SWEETWT6:CHISHOLM6
Thermal | 04ALL | 1 | 23SP | GEN-2018-117 | FROM->TO | 523771 GRAPEVINE 6 230 523777 WHEELER 6 230 1 |  | 319 | 0.23039 | 105.83 | P42:345:OKGE:SB_BVTY7315_PRE19S
Thermal | 04ALL | 1 | 23SP | GEN-2018-117 | FROM->TO | 523771 GRAPEVINE 6 230 523777 WHEELER 6 230 1 |  | 319 | 0.83099 | 135.53 | P12:230:AEPW:SWEETWT6:CHISHOLM6
Thermal | 04ALL | 1 | 23SP | GEN-2018-117 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28748 | 100.1 | P12:345:AEPW-AEPW:CHAMPSP-CLARKSV
Thermal | 04ALL | 1 | 23SP | GEN-2018-117 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28757 | 100 | P23:345:KCPL-WERE:237LACYGNE_R1-6::LACYGU1-LACYGNE-NEOSHO
Thermal | 04ALL | 1 | 23SP | GEN-2018-117 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28729 | 103.97 | P11:115:SPS:HOBBS1&3:145MW::::
Thermal | 04ALL | 1 | 23SP | GEN-2018-117 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28734 | 103.25 | P11:115:SPS:MUSTANG1&3:153MW::::
Thermal | 04ALL | 1 | 23SP | GEN-2018-117 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28714 | 100.29 | P12:230:SPS:K76::1_HITCH_OCHLTR:::
Thermal | 04ALL | 1 | 23SP | GEN-2018-117 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28638 | 100.3 | P12:115:SPS:T51::1_BOWERS_GRAPE:::
Thermal | 04ALL | 1 | 23SP | GEN-2018-117 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.2862 | 100.39 | P12:115:SPS:T87::1_SPRMN_HANSFRD:::
Thermal | 04ALL | 1 | 23SP | GEN-2018-117 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28501 | 100.3 | P12:115:SPS:V35::1_HUTCH_GRAYC:::
Thermal | 04ALL | 1 | 23SP | GEN-2018-117 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28673 | 100.46 | P12:115:SPS:W08::1_HITCH_LASLEY:::
Thermal | 04ALL | 1 | 23SP | GEN-2018-117 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.2862 | 100.4 | P12:115:SPS:W10::1_HITCH_HANSFRD:::
Thermal | 04ALL | 1 | 23SP | GEN-2018-117 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.2867 | 101.4 | P42:345:SPS:HITCHLAND:1R75:SLG:EHV:
Thermal | 04ALL | 1 | 23SP | GEN-2018-117 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.27687 | 104.72 | P42:345:SPS:HITCHLAND:1R15:SLG:EHV:
Thermal | 04ALL | 1 | 23SP | GEN-2018-117 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.27647 | 107.4 | P42:345:SPS:POTTERCO:2R05:SLG:EHV:
Thermal | 04ALL | 1 | 23SP | GEN-2018-117 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28753 | 107.99 | P42:345:SPS:YOAKUM:J18####:SLG1:EHV:
Thermal | 04ALL | 1 | 23SP | GEN-2018-117 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28753 | 107.99 | P43:345:SPS:YOAKUM:TF#####:SLG:EHV:
Thermal | 04ALL | 1 | 23SP | GEN-2018-117 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28753 | 107.99 | P42:345:SPS:YOAKUM:J17####:SLG:EHV:
Thermal | 04ALL | 1 | 23SP | GEN-2018-117 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28728 | 111.68 | P43:345:SPS:TUCO:SLG::EHV:
Thermal | 04ALL | 1 | 23SP | GEN-2018-117 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28753 | 107.99 | P42:345:SPS:YOAKUM:J18####:SLG2:EHV:
Thermal | 04ALL | 1 | 23SP | GEN-2018-117 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28742 | 100.26 | P42:345:SPS:ROADRUNNER:J23####_SLG::::
Thermal | 04ALL | 1 | 23SP | GEN-2018-117 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28748 | 100.1 | P12:345:AEPW-AEPW:CHAMPSP-CLARKSV:::EHV::
Thermal | 04ALL | 1 | 23SP | GEN-2018-117 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28757 | 100 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV:
Thermal | 04ALL | 1 | 23SP | GEN-2018-117 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28744 | 100.16 | P12:345:WERE:BENT-ROSE-345:::EHV:
Thermal | 04ALL | 1 | 23SP | GEN-2018-117 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28757 | 100.29 | P12:345:WERE:N345-PSO-345:::EHV:
Thermal | 04ALL | 1 | 23SP | GEN-2018-117 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28768 | 100.31 | P12:345:WERE:VIOL-WICH-345:::EHV:
Thermal | 04ALL | 1 | 23SP | GEN-2018-117 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28744 | 100.11 | P23:345:WERE:BENT-345-50:::EHV:
Thermal | 04ALL | 1 | 23SP | GEN-2018-117 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28743 | 100.3 | P23:345:WERE:ROSE-345-80:::EHV:
Thermal | 04ALL | 1 | 23SP | GEN-2018-117 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28762 | 100.14 | P23:345:WERE:WICH-345-116:::EHV:
Thermal | 04ALL | 1 | 23SP | GEN-2018-117 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28741 | 100.1 | P23:345:WERE:WICH-345-50:::EHV:
Thermal | 04ALL | 1 | 23SP | GEN-2018-117 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28742 | 100.2 | P11:022:NPPD:COOPER1G:1:983:::
Thermal | 04ALL | 1 | 23SP | GEN-2018-117 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28734 | 100.59 | P11:023:NPPD:GENTLM1G:1:757:::
Thermal | 04ALL | 1 | 23SP | GEN-2018-117 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28734 | 100.67 | P11:024:NPPD:GENTLM2G:2:757:::
Thermal | 04ALL | 1 | 23SP | GEN-2018-117 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28726 | 100.86 | P11:024:UMZB:# 33 #:: LRS IN WY. LARAMIE RIVER STATION 1_MV::
Thermal | 04ALL | 1 | 23SP | GEN-2018-117 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28805 | 100.61 | P12:138:WFEC:ERICK_ELKCTY::::
Thermal | 04ALL | 1 | 23SP | GEN-2018-117 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28943 | 100.42 | P12:069:WFEC:LAKECRK_ELKCTY::::
Thermal | 04ALL | 1 | 23SP | GEN-2018-117 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.2928 | 100.09 | P12:138:WFEC:MOREWD_REDHILLS::::
Thermal | 04ALL | 1 | 23SP | GEN-2018-117 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28539 | 101.64 | P12:138:WFEC:RUSSELL_LKPAUL::::
Thermal | 04ALL | 1 | 23SP | GEN-2018-117 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28629 | 101.02 | P12:138:WFEC:RUSSELL_ALTUSJCT::::
Thermal | 04ALL | 1 | 23SP | GEN-2018-117 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.30832 | 102.83 | P12:345:OKGE:BKRBKR24::::
Thermal | 04ALL | 1 | 23SP | GEN-2018-117 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28809 | 100 | P12:138:OKGE:BKRBKR83::::
Thermal | 04ALL | 1 | 23SP | GEN-2018-117 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28741 | 100.38 | P12:345:OKGE:BKRBKR336::::
Thermal | 04ALL | 1 | 23SP | GEN-2018-117 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28741 | 100.4 | P12:345:OKGE:BKRBKR336_2::::
Thermal | 04ALL | 1 | 23SP | GEN-2018-117 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28831 | 100.1 | P12:138:OKGE:BKRBKR338::::
Thermal | 04ALL | 1 | 23SP | GEN-2018-117 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28831 | 100.1 | P13:138:OKGE:BKRBKR338_2::::
Thermal | 04ALL | 1 | 23SP | GEN-2018-117 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28789 | 101.29 | P12:345:OKGE:BKRBKR357_2::::
Thermal | 04ALL | 1 | 23SP | GEN-2018-117 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.29648 | 108.16 | P12:345:OKGE-AEPW:BKRBKR366::::
Thermal | 04ALL | 1 | 23SP | GEN-2018-117 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.29648 | 103.85 | P12:345:OKGE-AEPW:BKRBKR366::::
Thermal | 04ALL | 1 | 23SP | GEN-2018-117 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.48719 | 103.55 | P12:345:OKGE-AEPW:BKRBKR371::::
Thermal | 04ALL | 1 | 23SP | GEN-2018-117 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.48719 | 121.08 | P12:345:OKGE-AEPW:BKRBKR371::::
Thermal | 04ALL | 1 | 23SP | GEN-2018-117 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28812 | 101.09 | P12:345:OKGE:BKRBKR400::::
Thermal | 04ALL | 1 | 23SP | GEN-2018-117 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28653 | 100.64 | P12:345:OKGE:BKRBKR4191::::
Thermal | 04ALL | 1 | 23SP | GEN-2018-117 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28665 | 101.09 | P12:345:OKGE:BKRBKR4191::::
Thermal | 04ALL | 1 | 23SP | GEN-2018-117 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28653 | 100.64 | P12:345:OKGE:BKRBKR4192::::
Thermal | 04ALL | 1 | 23SP | GEN-2018-117 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28665 | 101.09 | P12:345:OKGE:BKRBKR4192::::
Thermal | 04ALL | 1 | 23SP | GEN-2018-117 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28695 | 100.46 | P12:345:OKGE:BKRBKR4193::::
Thermal | 04ALL | 1 | 23SP | GEN-2018-117 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28695 | 100.46 | P12:345:OKGE:BKRBKR4194::::
Thermal | 04ALL | 1 | 23SP | GEN-2018-117 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.2867 | 101.4 | P12:345:OKGE-SPS:BKRBKR4201::::
Thermal | 04ALL | 1 | 23SP | GEN-2018-117 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.2867 | 101.4 | P12:345:OKGE-SPS:BKRBKR4202::::
Thermal | 04ALL | 1 | 23SP | GEN-2018-117 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28808 | 101.37 | P12:345:OKGE:BKRBKR421::::
Thermal | 04ALL | 1 | 23SP | GEN-2018-117 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28717 | 100.87 | P12:345:OKGE:BKRBKR604::::
Thermal | 04ALL | 1 | 23SP | GEN-2018-117 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28715 | 101.05 | P12:345:OKGE:BKRBKR604_2::::
Thermal | 04ALL | 1 | 23SP | GEN-2018-117 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28826 | 100.16 | P13:138-345:OKGE:BKRBKR_3W082::::
Thermal | 04ALL | 1 | 23SP | GEN-2018-117 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28773 | 101.03 | P13:138-345:OKGE:BKRBKR_3W083::::
Thermal | 04ALL | 1 | 23SP | GEN-2018-117 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28668 | 102.01 | P42:345:OKGE:SB_ARIA7381::::
Thermal | 04ALL | 1 | 23SP | GEN-2018-117 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28617 | 101.63 | P42:345:OKGE:SB_BVTY7387::::
Thermal | 04ALL | 1 | 23SP | GEN-2018-117 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28821 | 101.5 | P41:345:OKGE:SB_REUD7381::::
Thermal | 04ALL | 1 | 23SP | GEN-2018-117 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28814 | 101.52 | P41:345:OKGE:SB_REUD7383::::
Thermal | 04ALL | 1 | 23SP | GEN-2018-117 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28817 | 102.12 | P41:345:OKGE:SB_REUD7385::::
Thermal | 04ALL | 1 | 23SP | GEN-2018-117 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28853 | 100.52 | P42:345:OKGE:SB_REUD7389::::
Thermal | 04ALL | 1 | 23SP | GEN-2018-117 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28679 | 100.06 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV:
Thermal | 04ALL | 1 | 23SP | GEN-2018-117 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28742 | 101.52 | P13:115:SUNC:HOLCOMB_GSU:::HV:
Thermal | 04ALL | 1 | 23SP | GEN-2018-117 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28678 | 100.14 | P23:345:SUNC:BU_BRK488:::EHV:
Thermal | 04ALL | 1 | 23SP | GEN-2018-117 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28679 | 100.06 | P23:345:SUNC:BU_BRK482:::EHV:
Thermal | 04ALL | 1 | 23SP | GEN-2018-117 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28744 | 100 | P12:HV-EHV:EES::8W.MEMPHIS%:8FREEPORTTN%:4BHAM STEEL:1
Thermal | 04ALL | 1 | 23SP | GEN-2018-117 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28748 | 100.1 | P12:EHV:EES::CHAMSPR7!:CLARKSV7!:1
Thermal | 04ALL | 1 | 23SP | GEN-2018-117 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28742 | 100.22 | P11:345:MEC-NPPD:COOPER 1
Thermal | 04ALL | 1 | 23SP | GEN-2018-117 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28742 | 100.09 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3
Thermal | 04ALL | 1 | 23SP | GEN-2018-117 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28742 | 100.2 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4
Thermal | 04ALL | 1 | 23SP | GEN-2018-117 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28742 | 100.06 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4
Thermal | 04ALL | 1 | 23SP | GEN-2018-117 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28742 | 100.05 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1
Thermal | 04ALL | 1 | 23SP | GEN-2018-117 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28742 | 100.13 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1
Thermal | 04ALL | 1 | 23SP | GEN-2018-117 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28742 | 100.03 | P13:345-24:MEC:AUTO-SINGLE:RAUN3:NEAL4G:1
Thermal | 04ALL | 1 | 23SP | GEN-2018-117 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28744 | 100.16 | P12:345:WERE:BENT-ROSE_345::
Thermal | 04ALL | 1 | 23SP | GEN-2018-117 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28757 | 100.29 | P12:345:WERE:N345-PSO_345::
Thermal | 04ALL | 1 | 23SP | GEN-2018-117 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28768 | 100.31 | P12:345:WERE:VIOL-WICH_345::
Thermal | 04ALL | 1 | 23SP | GEN-2018-117 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.29712 | 100.65 | 511446 CL-AFTP4 138 511458 ELKCTY-4 138 1
Thermal | 04ALL | 1 | 23SP | GEN-2018-117 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.29712 | 100.49 | 511446 CL-AFTP4 138 511463 HOB-JCT4 138 1
Thermal | 04ALL | 1 | 23SP | GEN-2018-117 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28769 | 102.08 | 511456 O.K.U.-7 345 763215 G18-092-TAP 345 1
Thermal | 04ALL | 1 | 23SP | GEN-2018-117 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28943 | 100.37 | 511459 ELKCTY-2 69.0 520897 ELKCITY2 69.0 1
Thermal | 04ALL | 1 | 23SP | GEN-2018-117 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28876 | 100.85 | 511463 HOB-JCT4 138 511564 MARTHA 4 138 1
Thermal | 04ALL | 1 | 23SP | GEN-2018-117 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.2877 | 102.67 | 511468 L.E.S.-7 345 762467 G18-015-TAP 345 1
Thermal | 04ALL | 1 | 23SP | GEN-2018-117 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28761 | 101.52 | 511468 L.E.S.-7 345 763215 G18-092-TAP 345 2
Thermal | 04ALL | 1 | 23SP | GEN-2018-117 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.29049 | 100.38 | 511485 CLINTJC4 138 511534 CL-NGTP4 138 1
Thermal | 04ALL | 1 | 23SP | GEN-2018-117 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.29049 | 100.11 | 511506 WTH WF 4 138 511534 CL-NGTP4 138 1
Thermal | 04ALL | 1 | 23SP | GEN-2018-117 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.29048 | 100.18 | 511506 WTH WF 4 138 511536 WEATHTP4 138 1
Thermal | 04ALL | 1 | 23SP | GEN-2018-117 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.48719 | 103.55 | 511557 CHISHOLM6 230 3WXFMR CHISHOLM6 1
Thermal | 04ALL | 1 | 23SP | GEN-2018-117 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28876 | 100.76 | 511564 MARTHA 4 138 529302 OMALTUS4 138 1
Thermal | 04ALL | 1 | 23SP | GEN-2018-117 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28658 | 100.14 | 512093 MEMPHIS2 69.0 512094 REDRIVR2 69.0 1
Thermal | 04ALL | 1 | 23SP | GEN-2018-117 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28658 | 100.17 | 512094 REDRIVR2 69.0 512095 ESTELNE2 69.0 1
Thermal | 04ALL | 1 | 23SP | GEN-2018-117 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28658 | 100.24 | 512095 ESTELNE2 69.0 512096 CAREY 2 69.0 1
Thermal | 04ALL | 1 | 23SP | GEN-2018-117 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28658 | 100.26 | 512096 CAREY 2 69.0 512097 AIRPORT2 69.0 1
Thermal | 04ALL | 1 | 23SP | GEN-2018-117 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28658 | 100.29 | 512097 AIRPORT2 69.0 512098 AMOCOTP2 69.0 1
Thermal | 04ALL | 1 | 23SP | GEN-2018-117 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28658 | 100.48 | 512098 AMOCOTP2 69.0 512100 CHLDR2WT 69.0 1
Thermal | 04ALL | 1 | 23SP | GEN-2018-117 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28482 | 100.83 | 512101 CHILD4WT 138 512103 HOLTP4WT 138 1
Thermal | 04ALL | 1 | 23SP | GEN-2018-117 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28482 | 100.36 | 512103 HOLTP4WT 138 512104 WELL 4WT 138 1
Thermal | 04ALL | 1 | 23SP | GEN-2018-117 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28617 | 101.59 | 515375 WWRDEHV7 345 515458 BORDER 7 345 1
Thermal | 04ALL | 1 | 23SP | GEN-2018-117 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28742 | 100.86 | 515375 WWRDEHV7 345 562024 G11-019-SUB 345 1
Thermal | 04ALL | 1 | 23SP | GEN-2018-117 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28742 | 100.31 | 515375 WWRDEHV7 345 763527 GEN-2019-012 345 1
Thermal | 04ALL | 1 | 23SP | GEN-2018-117 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28617 | 101.63 | 515458 BORDER 7 345 560022 CRAWFISH_DR 345 1
Thermal | 04ALL | 1 | 23SP | GEN-2018-117 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28812 | 101.67 | 515543 RENFROW7 345 763421 G18-128-TAP 345 1
Thermal | 04ALL | 1 | 23SP | GEN-2018-117 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.2873 | 100.16 | 515618 BALKOW 7 345 3WXFMR BALKOW 7 1
Thermal | 04ALL | 1 | 23SP | GEN-2018-117 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.2873 | 100.16 | 515618 BALKOW 7 345 3WXFMR BALKOW 7 1_Dup1
Thermal | 04ALL | 1 | 23SP | GEN-2018-117 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28789 | 102.2 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Thermal | 04ALL | 1 | 23SP | GEN-2018-117 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28715 | 101.03 | 515634 PALDR1W7 345 3WXFMR PALO2 _1 1
Thermal | 04ALL | 1 | 23SP | GEN-2018-117 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28943 | 100.03 | 520876 DILL JT2 69.0 520897 ELKCITY2 69.0 1
Thermal | 04ALL | 1 | 23SP | GEN-2018-117 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28673 | 100.46 | 523093 HITCHLAND 3 115 523160 FRISCO_WND 3 115 1
Thermal | 04ALL | 1 | 23SP | GEN-2018-117 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28713 | 101.24 | 523093 HITCHLAND 3 115 523174 GOODWELLWND3 115 1
Thermal | 04ALL | 1 | 23SP | GEN-2018-117 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28714 | 100.29 | 523095 HITCHLAND 6 230 523155 OCHILTREE 6 230 1
Thermal | 04ALL | 1 | 23SP | GEN-2018-117 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28428 | 102.22 | 523095 HITCHLAND 6 230 523309 MOORE_CNTY 6 230 1
Thermal | 04ALL | 1 | 23SP | GEN-2018-117 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28681 | 100.29 | 523097 HITCHLAND 7 345 3WXFMR H TB80155502 1
Thermal | 04ALL | 1 | 23SP | GEN-2018-117 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28663 | 100.54 | 523097 HITCHLAND 7 345 3WXFMR SIEM 8743067 2
Thermal | 04ALL | 1 | 23SP | GEN-2018-117 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.27687 | 104.8 | 523097 HITCHLAND 7 345 523961 POTTER_CO 7 345 1
Thermal | 04ALL | 1 | 23SP | GEN-2018-117 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28714 | 100.25 | 523155 OCHILTREE 6 230 3WXFMR H TP80219401 1
Thermal | 04ALL | 1 | 23SP | GEN-2018-117 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28673 | 100.46 | 523160 FRISCO_WND 3 115 523175 LASLEY 3 115 1
Thermal | 04ALL | 1 | 23SP | GEN-2018-117 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28728 | 100.33 | 523172 GWELL_COLL11 34.5 523174 GOODWELLWND3 115 1
Thermal | 04ALL | 1 | 23SP | GEN-2018-117 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28727 | 100.37 | 523173 GWELL_COLL21 34.5 523174 GOODWELLWND3 115 1
Thermal | 04ALL | 1 | 23SP | GEN-2018-117 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28725 | 100.47 | 523309 MOORE_CNTY 6 230 3WXFMR ENRCO 136402 1
Thermal | 04ALL | 1 | 23SP | GEN-2018-117 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28742 | 103.88 | 523344 BLKHAWK_W 3 115 523461 BLACKHAWK1 1 13.8 1
Thermal | 04ALL | 1 | 23SP | GEN-2018-117 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28742 | 104.3 | 523346 BLKHAWK_E 3 115 523462 BLACKHAWK2 1 13.8 1
Thermal | 04ALL | 1 | 23SP | GEN-2018-117 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28501 | 100.3 | 523546 HUTCH_S 3 115 523636 GRAY_CNTY 3 115 1
Thermal | 04ALL | 1 | 23SP | GEN-2018-117 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28501 | 100.3 | 523636 GRAY_CNTY 3 115 3WXFMR WH RHP17221 1
Thermal | 04ALL | 1 | 23SP | GEN-2018-117 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28742 | 100.22 | 523853 FINNEY 7 345 762662 G18-030-TAP 345 1
Thermal | 04ALL | 1 | 23SP | GEN-2018-117 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28705 | 101.73 | 523926 MAJESTC_WND3 115 523928 MARTIN 3 115 1
Thermal | 04ALL | 1 | 23SP | GEN-2018-117 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28725 | 100.53 | 523926 MAJESTC_WND3 115 523947 MAJESTC-LV11 34.5 1
Thermal | 04ALL | 1 | 23SP | GEN-2018-117 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28723 | 100.65 | 523926 MAJESTC_WND3 115 523948 MAJESTC-LV21 34.5 1
Thermal | 04ALL | 1 | 23SP | GEN-2018-117 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.27658 | 106.23 | 523961 POTTER_CO 7 345 3WXFMR WAUK 90343-A 1
Thermal | 04ALL | 1 | 23SP | GEN-2018-117 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28715 | 101.2 | 523961 POTTER_CO 7 345 524296 SPNSPUR_WND7 345 1
Thermal | 04ALL | 1 | 23SP | GEN-2018-117 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28661 | 111.3 | 523977 HARRNG_WST 6 230 523971 HARRNGTON1 1 24.0 1
Thermal | 04ALL | 1 | 23SP | GEN-2018-117 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28654 | 111.89 | 523978 HARRNG_MID 6 230 523972 HARRNGTON2 1 24.0 1
Thermal | 04ALL | 1 | 23SP | GEN-2018-117 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28452 | 100.05 | 523978 HARRNG_MID 6 230 523979 HARRNG_EST 6 230 @1
Thermal | 04ALL | 1 | 23SP | GEN-2018-117 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28657 | 111.39 | 523979 HARRNG_EST 6 230 523973 HARRNGTON3 1 24.0 1
Thermal | 04ALL | 1 | 23SP | GEN-2018-117 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28691 | 103.26 | 524043 NICHOLS 3 115 524022 NICHOLS_2 1 13.8 1
Thermal | 04ALL | 1 | 23SP | GEN-2018-117 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28613 | 108.11 | 524044 NICHOLS 6 230 524023 NICHOLS_3 1 22.0 1
Thermal | 04ALL | 1 | 23SP | GEN-2018-117 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28704 | 101.86 | 524267 BUSHLAND 6 230 524290 WILDOR2_JUS6 230 1
Thermal | 04ALL | 1 | 23SP | GEN-2018-117 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.2872 | 100.89 | 524275 WILDOR_WND 1 34.5 524276 WILDOR_WND 6 230 1
Thermal | 04ALL | 1 | 23SP | GEN-2018-117 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.2872 | 100.89 | 524276 WILDOR_WND 6 230 524290 WILDOR2_JUS6 230 1
Thermal | 04ALL | 1 | 23SP | GEN-2018-117 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28727 | 100.43 | 524289 GS-PHWDRNCH1 34.5 524290 WILDOR2_JUS6 230 1
Thermal | 04ALL | 1 | 23SP | GEN-2018-117 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28715 | 101.18 | 524296 SPNSPUR_WND7 345 524299 SPNSPUR_COL7 345 1
Thermal | 04ALL | 1 | 23SP | GEN-2018-117 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28715 | 101.18 | 524299 SPNSPUR_COL7 345 3WXFMR SPNSPUR_COL7 1
Thermal | 04ALL | 1 | 23SP | GEN-2018-117 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28741 | 100.5 | 524909 ROOSEVELT 6 230 525531 TOLK 6 230 2
Thermal | 04ALL | 1 | 23SP | GEN-2018-117 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28742 | 101.72 | 524909 ROOSEVELT 6 230 763483 GEN-2019-003 230 1
Thermal | 04ALL | 1 | 23SP | GEN-2018-117 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28542 | 100.53 | 525213 SWISHER 6 230 525830 TUCO_INT 6 230 1
Thermal | 04ALL | 1 | 23SP | GEN-2018-117 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28742 | 100.68 | 525461 NEWHART 6 230 763186 GEN-2018-089 230 1
Thermal | 04ALL | 1 | 23SP | GEN-2018-117 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28726 | 101.39 | 525480 PLANT_X 3 115 525493 PLANT_X3 1 13.8 1
Thermal | 04ALL | 1 | 23SP | GEN-2018-117 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28703 | 103.31 | 525481 PLANT_X 6 230 525494 PLANT_X4 1 20.0 1
Thermal | 04ALL | 1 | 23SP | GEN-2018-117 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28742 | 101.36 | 525481 PLANT_X 6 230 763120 GEN-2018-081 230 1
Thermal | 04ALL | 1 | 23SP | GEN-2018-117 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28668 | 108.78 | 525531 TOLK 6 230 525561 TOLK_1 1 24.0 1
Thermal | 04ALL | 1 | 23SP | GEN-2018-117 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28649 | 110.16 | 525531 TOLK 6 230 525562 TOLK_2 1 24.0 1
Thermal | 04ALL | 1 | 23SP | GEN-2018-117 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28737 | 100.48 | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1
Thermal | 04ALL | 1 | 23SP | GEN-2018-117 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28742 | 101.03 | 525531 TOLK 6 230 762132 GEN-2017-158 230 1
Thermal | 04ALL | 1 | 23SP | GEN-2018-117 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28742 | 104.61 | 525531 TOLK 6 230 763241 GEN-2018-097 230 1
Thermal | 04ALL | 1 | 23SP | GEN-2018-117 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28742 | 101.05 | 525830 TUCO_INT 6 230 525840 ANTELOPE_1 6 230 1
Thermal | 04ALL | 1 | 23SP | GEN-2018-117 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28727 | 100.51 | 525830 TUCO_INT 6 230 525957 HALE_WNDCL16 230 1
Thermal | 04ALL | 1 | 23SP | GEN-2018-117 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28744 | 100.4 | 525830 TUCO_INT 6 230 526161 CARLISLE 6 230 1
Thermal | 04ALL | 1 | 23SP | GEN-2018-117 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.2872 | 101.73 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2
Thermal | 04ALL | 1 | 23SP | GEN-2018-117 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28714 | 102.37 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _9 1
Thermal | 04ALL | 1 | 23SP | GEN-2018-117 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28716 | 103.84 | 525832 TUCO_INT 7 345 525850 ELK_CT1 345 1
Thermal | 04ALL | 1 | 23SP | GEN-2018-117 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28753 | 107.62 | 525832 TUCO_INT 7 345 526936 YOAKUM_345 345 1
Thermal | 04ALL | 1 | 23SP | GEN-2018-117 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28729 | 101.63 | 525850 ELK_CT1 345 525844 ELK_1 1 18.0 1
Thermal | 04ALL | 1 | 23SP | GEN-2018-117 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28729 | 101.63 | 525850 ELK_CT1 345 525845 ELK_2 1 18.0 1
Thermal | 04ALL | 1 | 23SP | GEN-2018-117 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28732 | 100.37 | 526012 LOST_DRAW 3 115 584560 GEN-2015-014 115 1
Thermal | 04ALL | 1 | 23SP | GEN-2018-117 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.287 | 103.21 | 526337 JONES 6 230 526331 JONES_1 1 22.0 1
Thermal | 04ALL | 1 | 23SP | GEN-2018-117 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.287 | 103.21 | 526337 JONES 6 230 526332 JONES_2 1 22.0 1
Thermal | 04ALL | 1 | 23SP | GEN-2018-117 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.2874 | 100.67 | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1
Thermal | 04ALL | 1 | 23SP | GEN-2018-117 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28744 | 101.96 | 526936 YOAKUM_345 345 527896 HOBBS_INT 7 345 1
Thermal | 04ALL | 1 | 23SP | GEN-2018-117 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28734 | 102.29 | 527146 MUSTANG 3 115 527161 MUSTANG_1 1 18.0 1
Thermal | 04ALL | 1 | 23SP | GEN-2018-117 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28731 | 102.28 | 527146 MUSTANG 3 115 527162 MUSTANG_2 1 18.0 1
Thermal | 04ALL | 1 | 23SP | GEN-2018-117 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28722 | 105.17 | 527149 MUSTANG 6 230 527151 GS-MUSTANG 6 230 @1
Thermal | 04ALL | 1 | 23SP | GEN-2018-117 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28719 | 102.36 | 527149 MUSTANG 6 230 527163 MUSTANG_3 1 19.0 1
Thermal | 04ALL | 1 | 23SP | GEN-2018-117 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28733 | 102.18 | 527151 GS-MUSTANG 6 230 527165 MUSTANG_5 1 18.0 1
Thermal | 04ALL | 1 | 23SP | GEN-2018-117 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28731 | 102.39 | 527151 GS-MUSTANG 6 230 527166 MUSTANG_6 1 18.0 1
Thermal | 04ALL | 1 | 23SP | GEN-2018-117 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28734 | 100.05 | 527455 RSWL_SLRCOL3 115 527454 RSWL_SOLAR11 34.5 1
Thermal | 04ALL | 1 | 23SP | GEN-2018-117 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28734 | 100.05 | 527455 RSWL_SLRCOL3 115 527482 CHAVES_CNTY3 115 1
Thermal | 04ALL | 1 | 23SP | GEN-2018-117 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28733 | 100.06 | 527654 RSVLT_CC_W 7 345 527655 RSVLT_CC_E 7 345 1
Thermal | 04ALL | 1 | 23SP | GEN-2018-117 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28733 | 100.06 | 527654 RSVLT_CC_W 7 345 527666 RSVLT_COL1 7 345 1
Thermal | 04ALL | 1 | 23SP | GEN-2018-117 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28729 | 100.36 | 527655 RSVLT_CC_E 7 345 527656 CROSSROADS 7 345 1
Thermal | 04ALL | 1 | 23SP | GEN-2018-117 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28733 | 100.06 | 527666 RSVLT_COL1 7 345 3WXFMR RSVLT_COL1 7 1
Thermal | 04ALL | 1 | 23SP | GEN-2018-117 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28713 | 102.89 | 527867 CUNNIGHM_S 6 230 527882 CUNINGHAM2 1 20.0 1
Thermal | 04ALL | 1 | 23SP | GEN-2018-117 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28729 | 102.15 | 527891 HOBBS_INT 3 115 527901 HOBBS_PLT1 1 18.0 1
Thermal | 04ALL | 1 | 23SP | GEN-2018-117 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28729 | 102.16 | 527891 HOBBS_INT 3 115 527902 HOBBS_PLT2 1 18.0 1
Thermal | 04ALL | 1 | 23SP | GEN-2018-117 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28721 | 103.99 | 527894 HOBBS_INT 6 230 527903 HOBBS_PLT3 1 18.0 1
Thermal | 04ALL | 1 | 23SP | GEN-2018-117 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28724 | 101.56 | 528355 MADDOX 3 115 528361 MADDOX_1 1 13.8 1
Thermal | 04ALL | 1 | 23SP | GEN-2018-117 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28876 | 100.14 | 529298 OMPVET-4 138 529302 OMALTUS4 138 1
Thermal | 04ALL | 1 | 23SP | GEN-2018-117 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28789 | 103.16 | 532794 ROSEHIL7 345 560053 G15052_T 345 1
Thermal | 04ALL | 1 | 23SP | GEN-2018-117 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28812 | 101.82 | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1
Thermal | 04ALL | 1 | 23SP | GEN-2018-117 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28722 | 100.04 | 539659 CUDAHY 3 115 539783 CRKCK 3 115 1
Thermal | 04ALL | 1 | 23SP | GEN-2018-117 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28764 | 102.28 | 560022 CRAWFISH_DR 345 762216 G17-151TAP 345 1
Thermal | 04ALL | 1 | 23SP | GEN-2018-117 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28761 | 102.13 | 560022 CRAWFISH_DR 345 762467 G18-015-TAP 345 1
Thermal | 04ALL | 1 | 23SP | GEN-2018-117 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28742 | 101.63 | 560022 CRAWFISH_DR 345 763087 GEN-2018-073 345 1
Thermal | 04ALL | 1 | 23SP | GEN-2018-117 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28771 | 103.54 | 560022 CRAWFISH_DR 345 763215 G18-092-TAP 345 2
Thermal | 04ALL | 1 | 23SP | GEN-2018-117 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28742 | 100.33 | 560071 G16-003-TAP 345 587020 GEN-2016-003 345 1
Thermal | 04ALL | 1 | 23SP | GEN-2018-117 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28742 | 100.14 | 562021 G11-020-SUB 345 562024 G11-019-SUB 345 1
Thermal | 04ALL | 1 | 23SP | GEN-2018-117 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28742 | 100.13 | 562022 G11-020-GSU 34.5 562021 G11-020-SUB 345 1
Thermal | 04ALL | 1 | 23SP | GEN-2018-117 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28742 | 100.17 | 562025 G11-019-GSU 34.5 562024 G11-019-SUB 345 1
Thermal | 04ALL | 1 | 23SP | GEN-2018-117 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28876 | 100.79 | P12:138:AEPW-OMPA:HOB-JCT4:OMALTUS4
Thermal | 04ALL | 1 | 23SP | GEN-2018-117 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28629 | 101.02 | P12:138:AEPW-WFEC:ALTUSJT4:RUSSELL4
Thermal | 04ALL | 1 | 23SP | GEN-2018-117 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28539 | 101.64 | P12:138:AEPW-WFEC:LAKEP4WT:RUSSELL4
Thermal | 04ALL | 1 | 23SP | GEN-2018-117 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28732 | 100.37 | 584560 GEN-2015-014 115 584561 G15-014XFMR1 34.5 1
Thermal | 04ALL | 1 | 23SP | GEN-2018-117 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28742 | 100.33 | 587021 G16-003XFMR1 34.5 587020 GEN-2016-003 345 1
Thermal | 04ALL | 1 | 23SP | GEN-2018-117 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28269 | 102.89 | P12:138:AEPW:CHILD4WT:LAKEP4WT
Thermal | 04ALL | 1 | 23SP | GEN-2018-117 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.29826 | 102.68 | P12:138:AEPW:ELKCTY-4:CLINTJC4
Thermal | 04ALL | 1 | 23SP | GEN-2018-117 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.29712 | 100.66 | P12:138:AEPW:HOB-JCT4:ELKCTY-4
Thermal | 04ALL | 1 | 23SP | GEN-2018-117 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.29049 | 100.54 | P12:138:AEPW:WTHWF4:CLINTJC4
Thermal | 04ALL | 1 | 23SP | GEN-2018-117 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.29048 | 100.33 | P12:138:AEPW:WTHWF4:WTH_SE4
Thermal | 04ALL | 1 | 23SP | GEN-2018-117 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28805 | 100.43 | P12:138:WFEC-AEPW:ELKCTY-4:ERICK4
Thermal | 04ALL | 1 | 23SP | GEN-2018-117 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.29648 | 108.16 | P12:345:AEPW-OKGE:L.E.S.-7:GRACMNT7
Thermal | 04ALL | 1 | 23SP | GEN-2018-117 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.29648 | 103.85 | P12:345:AEPW-OKGE:L.E.S.-7:GRACMNT7
Thermal | 04ALL | 1 | 23SP | GEN-2018-117 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28757 | 100.29 | P12:345:AEPW-WERE:DELWARE7:NEOSHO7
Thermal | 04ALL | 1 | 23SP | GEN-2018-117 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28757 | 100.29 | 6111_Dup1
Thermal | 04ALL | 1 | 23SP | GEN-2018-117 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28758 | 100.39 | P12:345:AEPW:DELWARE7:N.E.S.-7
Thermal | 04ALL | 1 | 23SP | GEN-2018-117 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28769 | 102.13 | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Thermal | 04ALL | 1 | 23SP | GEN-2018-117 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28658 | 100.04 | P12:69:AEPW:CHLDR2WT:MEMPHIS2
Thermal | 04ALL | 1 | 23SP | GEN-2018-117 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28943 | 100.42 | P12:69:WFEC-AEPW:LKCREEK2:ELKCTY-2
Thermal | 04ALL | 1 | 23SP | GEN-2018-117 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.35177 | 113.78 | P13:138-230:AEPW:ELKCTY-4
Thermal | 04ALL | 1 | 23SP | GEN-2018-117 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28749 | 100.3 | P23:500:EES-EAI:KEO:B4941
Thermal | 04ALL | 1 | 23SP | GEN-2018-117 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28749 | 100.56 | P23:500:EES-EAI:KEO:B4941
Thermal | 04ALL | 1 | 23SP | GEN-2018-117 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28748 | 100.18 | P23:500:EES-EAI:KEO:B4921
Thermal | 04ALL | 1 | 23SP | GEN-2018-117 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28744 | 100 | P12:500:EES-EAI:WMPEHV:BHMSTL:BHMSTL:NEWPORT
Thermal | 04ALL | 1 | 23SP | GEN-2018-117 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28658 | 100.7 | P13:69-138:AEPW:CHLDR2WT
Thermal | 04ALL | 1 | 23SP | GEN-2018-117 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28943 | 100.57 | P13:69-138:AEPW:ELKCTY-2
Thermal | 04ALL | 1 | 23SP | GEN-2018-117 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28745 | 100.12 | P23:500:EAI-TVA:NBF_WEST M~1
Thermal | 04ALL | 1 | 23SP | GEN-2018-117 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28742 | 100.13 | P23:345:MEC:CBEC 905
Thermal | 04ALL | 1 | 23SP | GEN-2018-117 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28742 | 100.05 | P23:345:MEC:CBEC 908
Thermal | 04ALL | 1 | 23SP | GEN-2018-117 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28742 | 100.03 | P23:345:MEC:RAUN 0210
Thermal | 04ALL | 1 | 23SP | GEN-2018-117 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28742 | 100.24 | 762132 GEN-2017-158 230 763252 G18-099-XFM1 34.5 1
Thermal | 04ALL | 1 | 23SP | GEN-2018-117 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28742 | 100.24 | 762132 GEN-2017-158 230 763255 G18-099-XFM2 34.5 1
Thermal | 04ALL | 1 | 23SP | GEN-2018-117 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28764 | 102.43 | 762216 G17-151TAP 345 762467 G18-015-TAP 345 1
Thermal | 04ALL | 1 | 23SP | GEN-2018-117 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28754 | 101.37 | 762467 G18-015-TAP 345 763215 G18-092-TAP 345 1
Thermal | 04ALL | 1 | 23SP | GEN-2018-117 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28742 | 100.89 | 763087 GEN-2018-073 345 763088 G18-073-XFM1 34.5 1
Thermal | 04ALL | 1 | 23SP | GEN-2018-117 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28742 | 100.18 | 763087 GEN-2018-073 345 763091 G18-073-XFM2 34.5 1
Thermal | 04ALL | 1 | 23SP | GEN-2018-117 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28742 | 101.36 | 763120 GEN-2018-081 230 763121 G18-081-XFM1 34.5 1
Thermal | 04ALL | 1 | 23SP | GEN-2018-117 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28742 | 100.68 | 763186 GEN-2018-089 230 763187 G18-089-XFM1 34.5 1
Thermal | 04ALL | 1 | 23SP | GEN-2018-117 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28742 | 100.1 | 763208 GEN-2018-092 345 763215 G18-092-TAP 345 1
Thermal | 04ALL | 1 | 23SP | GEN-2018-117 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28742 | 100.5 | 763241 GEN-2018-097 230 763242 G18-097-XFM1 34.5 1
Thermal | 04ALL | 1 | 23SP | GEN-2018-117 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28742 | 100.42 | 763241 GEN-2018-097 230 763307 G18-112-XFM1 34.5 1
Thermal | 04ALL | 1 | 23SP | GEN-2018-117 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28742 | 100.42 | 763241 GEN-2018-097 230 763310 G18-112-XFM2 34.5 1
Thermal | 04ALL | 1 | 23SP | GEN-2018-117 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28742 | 100.5 | 763241 GEN-2018-097 230 763395 G18-124-XFM1 34.5 1
Thermal | 04ALL | 1 | 23SP | GEN-2018-117 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28742 | 100.5 | 763241 GEN-2018-097 230 763398 G18-124-XFM2 34.5 1
Thermal | 04ALL | 1 | 23SP | GEN-2018-117 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28742 | 101.15 | 763483 GEN-2019-003 230 763484 G19-003-XFM1 34.5 1
Thermal | 04ALL | 1 | 23SP | GEN-2018-117 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28742 | 100.02 | 763483 GEN-2019-003 230 763605 G19-021-XFM1 34.5 1
Thermal | 04ALL | 1 | 23SP | GEN-2018-117 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28742 | 100.31 | 763527 GEN-2019-012 345 763528 G19-012-XFM1 34.5 1
Thermal | 04ALL | 1 | 23SP | GEN-2018-117 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28665 | 102.2 | P42:345:OKGE:SB_BVTY7305
Thermal | 04ALL | 1 | 23SP | GEN-2018-117 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28744 | 100.11 | P23:345:WERE:BENT_345-50::
Thermal | 04ALL | 1 | 23SP | GEN-2018-117 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28743 | 100.3 | P23:345:WERE:ROSE_345-80::
Thermal | 04ALL | 1 | 23SP | GEN-2018-117 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28762 | 100.14 | P23:345:WERE:WICH_345-116::
Thermal | 04ALL | 1 | 23SP | GEN-2018-117 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28741 | 100.1 | P23:345:WERE:WICH_345-50::
Thermal | 04ALL | 1 | 23SP | GEN-2018-117 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28748 | 100.1 | P43:345:AEPW:CHAMBERS SPRING CB 12720 NBTB+FAULT
Thermal | 04ALL | 1 | 23SP | GEN-2018-117 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28748 | 100.1 | P42:345:AEPW:CHAMBERS SPRING CB 13720 NBTB+FAULT
Thermal | 04ALL | 1 | 23SP | GEN-2018-117 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28748 | 100.1 | P42:345:AEPW:CHAMBERS SPRING CB 13850 NBTB+FAULT
Thermal | 04ALL | 1 | 23SP | GEN-2018-117 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28769 | 102.1 | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Thermal | 04ALL | 1 | 23SP | GEN-2018-117 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.29694 | 107.94 | P42:345:AEPW:LAWTON EASTSIDE CB 3413A NBTB+FAULT
Thermal | 04ALL | 1 | 23SP | GEN-2018-117 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.29744 | 107.73 | P42:345:AEPW:LAWTON EASTSIDE CB 3425A NBTB+FAULT
Thermal | 04ALL | 1 | 23SP | GEN-2018-117 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28775 | 101.8 | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Thermal | 04ALL | 1 | 23SP | GEN-2018-117 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28758 | 100.39 | P42:345:AEPW:NES CB 3445A NBTB+FAULT
Thermal | 04ALL | 1 | 23SP | GEN-2018-117 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28759 | 100.41 | P42:345:AEPW:DELAWARE CB 3401A NBTB+FAULT
Thermal | 04ALL | 1 | 23SP | GEN-2018-117 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28759 | 100.41 | P42:345:AEPW:DELAWARE CB 3405A NBTB+FAULT
Thermal | 04ALL | 1 | 23SP | GEN-2018-117 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28759 | 100.41 | P42:345:AEPW:DELAWARE CB 3409A NBTB+FAULT
Thermal | 04ALL | 1 | 23SP | GEN-2018-117 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28748 | 100.1 | P23:345:AEPW:CHAMBERS SPRING CB 12720 NBTB
Thermal | 04ALL | 1 | 23SP | GEN-2018-117 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28748 | 100.1 | P23:345:AEPW:CHAMBERS SPRING CB 13720 NBTB
Thermal | 04ALL | 1 | 23SP | GEN-2018-117 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28748 | 100.1 | P23:345:AEPW:CHAMBERS SPRING CB 13850 NBTB
Thermal | 04ALL | 1 | 23SP | GEN-2018-117 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28769 | 102.08 | P23:345:AEPW:OKLAUNION CB 3401A NBTB
Thermal | 04ALL | 1 | 23SP | GEN-2018-117 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.29694 | 107.94 | P23:345:AEPW:LAWTON EASTSIDE CB 3413A NBTB
Thermal | 04ALL | 1 | 23SP | GEN-2018-117 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.29744 | 107.73 | P23:345:AEPW:LAWTON EASTSIDE CB 3425A NBTB
Thermal | 04ALL | 1 | 23SP | GEN-2018-117 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28775 | 101.8 | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Thermal | 04ALL | 1 | 23SP | GEN-2018-117 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28758 | 100.39 | P23:345:AEPW:NES CB 3441A NBTB
Thermal | 04ALL | 1 | 23SP | GEN-2018-117 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28759 | 100.41 | P23:345:AEPW:DELAWARE CB 3401A NBTB
Thermal | 04ALL | 1 | 23SP | GEN-2018-117 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28759 | 100.41 | P23:345:AEPW:DELAWARE CB 3405A NBTB
Thermal | 04ALL | 1 | 23SP | GEN-2018-117 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28759 | 100.41 | P23:345:AEPW:DELAWARE CB 3409A NBTB
Thermal | 04ALL | 1 | 23SP | GEN-2018-117 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28742 | 100.03 | P11:115:SUNC:GARDENCITY_S2:97:531459(2)
Thermal | 04ALL | 1 | 23SP | GEN-2018-117 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28868 | 101.87 | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Thermal | 04ALL | 1 | 23SP | GEN-2018-117 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28868 | 101.87 | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Thermal | 04ALL | 1 | 23SP | GEN-2018-117 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.2767 | 128.54 | P42:345:OKGE:SB_BVTY7315_PRE19S
Thermal | 04ALL | 1 | 23SP | GEN-2018-117 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.35177 | 113.77 | P12:230:AEPW:ELKCITY6:CHISHOLM6
Thermal | 04ALL | 1 | 23SP | GEN-2018-117 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 1 | 164.31 | P12:230:AEPW:SWEETWT6:CHISHOLM6
Thermal | 04ALL | 1 | 26L | GEN-2018-117 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.20852 | 105.7 | P42:345:SPS:YOAKUM:J18####:SLG1:EHV:
Thermal | 04ALL | 1 | 26L | GEN-2018-117 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.20852 | 105.7 | P43:345:SPS:YOAKUM:TF#####:SLG:EHV:
Thermal | 04ALL | 1 | 26L | GEN-2018-117 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.20852 | 105.7 | P42:345:SPS:YOAKUM:J17####:SLG:EHV:
Thermal | 04ALL | 1 | 26L | GEN-2018-117 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.20852 | 105.37 | P43:345:SPS:TUCO:SLG::EHV:
Thermal | 04ALL | 1 | 26L | GEN-2018-117 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.20852 | 105.7 | P42:345:SPS:YOAKUM:J18####:SLG2:EHV:
Thermal | 04ALL | 1 | 26L | GEN-2018-117 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.20869 | 105.39 | P12:345:OKGE-AEPW:BKRBKR366::::
Thermal | 04ALL | 1 | 26L | GEN-2018-117 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.20869 | 100.58 | P12:345:OKGE-AEPW:BKRBKR366::::
Thermal | 04ALL | 1 | 26L | GEN-2018-117 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.21802 | 115.9 | P42:345:OKGE:SB_BVTY7387::::
Thermal | 04ALL | 1 | 26L | GEN-2018-117 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.27984 | 103.81 | 511553 CHISHOLM7 345 755000 WWDBORDT 345 1
Thermal | 04ALL | 1 | 26L | GEN-2018-117 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.21802 | 115.94 | 515458 BORDER 7 345 560022 CRAWFISH_DR 345 1
Thermal | 04ALL | 1 | 26L | GEN-2018-117 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.21802 | 115.83 | 515458 BORDER 7 345 755000 WWDBORDT 345 1
Thermal | 04ALL | 1 | 26L | GEN-2018-117 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.20503 | 100.31 | 523095 HITCHLAND 6 230 523309 MOORE_CNTY 6 230 1
Thermal | 04ALL | 1 | 26L | GEN-2018-117 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.20852 | 105.37 | 525832 TUCO_INT 7 345 526936 YOAKUM_345 345 1
Thermal | 04ALL | 1 | 26L | GEN-2018-117 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.20869 | 105.39 | P12:345:AEPW-OKGE:L.E.S.-7:GRACMNT7
Thermal | 04ALL | 1 | 26L | GEN-2018-117 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.20869 | 100.58 | P12:345:AEPW-OKGE:L.E.S.-7:GRACMNT7
Thermal | 04ALL | 1 | 26L | GEN-2018-117 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.2087 | 105.61 | P42:345:AEPW:LAWTON EASTSIDE CB 3413A NBTB+FAULT
Thermal | 04ALL | 1 | 26L | GEN-2018-117 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.20871 | 105.98 | P42:345:AEPW:LAWTON EASTSIDE CB 3425A NBTB+FAULT
Thermal | 04ALL | 1 | 26L | GEN-2018-117 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.2087 | 105.61 | P23:345:AEPW:LAWTON EASTSIDE CB 3413A NBTB
Thermal | 04ALL | 1 | 26L | GEN-2018-117 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.20871 | 105.98 | P23:345:AEPW:LAWTON EASTSIDE CB 3425A NBTB
Thermal | 04ALL | 1 | 26SP | GEN-2018-117 | FROM->TO | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 353 | 1 | 164.6 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1
Thermal | 04ALL | 1 | 26SP | GEN-2018-117 | FROM->TO | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.9111 | 119.22 | 523771 GRAPEVINE 6 230 523777 WHEELER 6 230 1
Thermal | 04ALL | 1 | 26SP | GEN-2018-117 | FROM->TO | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 353 | 1 | 164.59 | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1
Thermal | 04ALL | 1 | 26SP | GEN-2018-117 | FROM->TO | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 353 | 1 | 164.6 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6
Thermal | 04ALL | 1 | 26SP | GEN-2018-117 | FROM->TO | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 |  | 395 | 0.21091 | 118.35 | P42:345:OKGE:SB_BVTY7315_PRE19S
Thermal | 04ALL | 1 | 26SP | GEN-2018-117 | FROM->TO | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 |  | 395 | 1 | 148.63 | P12:230:AEPW:SWEETWT6:CHISHOLM6
Thermal | 04ALL | 1 | 26SP | GEN-2018-117 | FROM->TO | 523771 GRAPEVINE 6 230 523777 WHEELER 6 230 1 |  | 319 | 0.83103 | 134.9 | P12:230:AEPW:SWEETWT6:CHISHOLM6
Thermal | 04ALL | 1 | 26SP | GEN-2018-117 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.20693 | 100.05 | P42:345:SPS:HITCHLAND:1R15:SLG:EHV:
Thermal | 04ALL | 1 | 26SP | GEN-2018-117 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.20651 | 102.81 | P42:345:SPS:POTTERCO:2R05:SLG:EHV:
Thermal | 04ALL | 1 | 26SP | GEN-2018-117 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.216 | 103.72 | P42:345:SPS:YOAKUM:J18####:SLG1:EHV:
Thermal | 04ALL | 1 | 26SP | GEN-2018-117 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.216 | 103.72 | P43:345:SPS:YOAKUM:TF#####:SLG:EHV:
Thermal | 04ALL | 1 | 26SP | GEN-2018-117 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.216 | 103.72 | P42:345:SPS:YOAKUM:J17####:SLG:EHV:
Thermal | 04ALL | 1 | 26SP | GEN-2018-117 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.21579 | 106.61 | P43:345:SPS:TUCO:SLG::EHV:
Thermal | 04ALL | 1 | 26SP | GEN-2018-117 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.216 | 103.72 | P42:345:SPS:YOAKUM:J18####:SLG2:EHV:
Thermal | 04ALL | 1 | 26SP | GEN-2018-117 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.22738 | 103.16 | P42:345:OKGE:SB_BVTY7387::::
Thermal | 04ALL | 1 | 26SP | GEN-2018-117 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28449 | 107.58 | 511553 CHISHOLM7 345 755000 WWDBORDT 345 1
Thermal | 04ALL | 1 | 26SP | GEN-2018-117 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.48663 | 108.22 | 511557 CHISHOLM6 230 3WXFMR CHISHOLM6 1
Thermal | 04ALL | 1 | 26SP | GEN-2018-117 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.22738 | 103.16 | 515458 BORDER 7 345 560022 CRAWFISH_DR 345 1
Thermal | 04ALL | 1 | 26SP | GEN-2018-117 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.22738 | 103.11 | 515458 BORDER 7 345 755000 WWDBORDT 345 1
Thermal | 04ALL | 1 | 26SP | GEN-2018-117 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.20693 | 100.11 | 523097 HITCHLAND 7 345 523961 POTTER_CO 7 345 1
Thermal | 04ALL | 1 | 26SP | GEN-2018-117 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.20659 | 101.84 | 523961 POTTER_CO 7 345 3WXFMR WAUK 90343-A 1
Thermal | 04ALL | 1 | 26SP | GEN-2018-117 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.21488 | 105.61 | 523977 HARRNG_WST 6 230 523971 HARRNGTON1 1 24.0 1
Thermal | 04ALL | 1 | 26SP | GEN-2018-117 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.21481 | 106.21 | 523978 HARRNG_MID 6 230 523972 HARRNGTON2 1 24.0 1
Thermal | 04ALL | 1 | 26SP | GEN-2018-117 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.21484 | 105.7 | 523979 HARRNG_EST 6 230 523973 HARRNGTON3 1 24.0 1
Thermal | 04ALL | 1 | 26SP | GEN-2018-117 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.2144 | 102.37 | 524044 NICHOLS 6 230 524023 NICHOLS_3 1 22.0 1
Thermal | 04ALL | 1 | 26SP | GEN-2018-117 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.21507 | 102.61 | 525531 TOLK 6 230 525561 TOLK_1 1 24.0 1
Thermal | 04ALL | 1 | 26SP | GEN-2018-117 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.2149 | 103.83 | 525531 TOLK 6 230 525562 TOLK_2 1 24.0 1
Thermal | 04ALL | 1 | 26SP | GEN-2018-117 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.216 | 103.23 | 525832 TUCO_INT 7 345 526936 YOAKUM_345 345 1
Thermal | 04ALL | 1 | 26SP | GEN-2018-117 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.21091 | 131.54 | P42:345:OKGE:SB_BVTY7315_PRE19S
Thermal | 04ALL | 1 | 26SP | GEN-2018-117 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 1 | 164.32 | P12:230:AEPW:SWEETWT6:CHISHOLM6
Thermal | 04ALL | 1 | 26WP | GEN-2018-117 | FROM->TO | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 439 | 1 | 132.35 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1
Thermal | 04ALL | 1 | 26WP | GEN-2018-117 | FROM->TO | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 439 | 0.91088 | 102.67 | 523771 GRAPEVINE 6 230 523777 WHEELER 6 230 1
Thermal | 04ALL | 1 | 26WP | GEN-2018-117 | FROM->TO | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 439 | 1 | 132.35 | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1
Thermal | 04ALL | 1 | 26WP | GEN-2018-117 | FROM->TO | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 439 | 1 | 132.35 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6
Thermal | 04ALL | 1 | 26WP | GEN-2018-117 | FROM->TO | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 |  | 441 | 1 | 132.57 | P12:230:AEPW:SWEETWT6:CHISHOLM6
Thermal | 04ALL | 1 | 26WP | GEN-2018-117 | FROM->TO | 523771 GRAPEVINE 6 230 523777 WHEELER 6 230 1 |  | 346 | 0.83104 | 126.97 | P12:230:AEPW:SWEETWT6:CHISHOLM6
Thermal | 04ALL | 1 | 26WP | GEN-2018-117 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 439 | 1 | 131.72 | P12:230:AEPW:SWEETWT6:CHISHOLM6
Thermal | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | 349 |  | 0.28742 | 100.91 | System Intact
Thermal | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 353 | 1 | 164.55 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1
Thermal | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.87401 | 114.63 | 523771 GRAPEVINE 6 230 523777 WHEELER 6 230 1
Thermal | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 353 | 1 | 164.55 | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1
Thermal | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 353 | 1 | 164.55 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6
Thermal | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 |  | 395 | 0.28728 | 100.24 | P43:345:SPS:TUCO:SLG::EHV:
Thermal | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 |  | 395 | 0.48719 | 108.77 | P12:345:OKGE-AEPW:BKRBKR371::::
Thermal | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 |  | 395 | 0.28654 | 100.42 | 523978 HARRNG_MID 6 230 523972 HARRNGTON2 1 24.0 1
Thermal | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 |  | 395 | 0.35177 | 102.14 | P13:138-230:AEPW:ELKCTY-4
Thermal | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 |  | 395 | 0.2767 | 115.6 | P42:345:OKGE:SB_BVTY7315_PRE19S
Thermal | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 |  | 395 | 0.35177 | 102.12 | P12:230:AEPW:ELKCITY6:CHISHOLM6
Thermal | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 |  | 395 | 1 | 148.63 | P12:230:AEPW:SWEETWT6:CHISHOLM6
Thermal | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523771 GRAPEVINE 6 230 523777 WHEELER 6 230 1 |  | 319 | 0.23039 | 105.83 | P42:345:OKGE:SB_BVTY7315_PRE19S
Thermal | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523771 GRAPEVINE 6 230 523777 WHEELER 6 230 1 |  | 319 | 0.83099 | 135.53 | P12:230:AEPW:SWEETWT6:CHISHOLM6
Thermal | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28748 | 100.1 | P12:345:AEPW-AEPW:CHAMPSP-CLARKSV
Thermal | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28757 | 100 | P23:345:KCPL-WERE:237LACYGNE_R1-6::LACYGU1-LACYGNE-NEOSHO
Thermal | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28729 | 103.97 | P11:115:SPS:HOBBS1&3:145MW::::
Thermal | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28734 | 103.25 | P11:115:SPS:MUSTANG1&3:153MW::::
Thermal | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28714 | 100.29 | P12:230:SPS:K76::1_HITCH_OCHLTR:::
Thermal | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28638 | 100.3 | P12:115:SPS:T51::1_BOWERS_GRAPE:::
Thermal | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.2862 | 100.39 | P12:115:SPS:T87::1_SPRMN_HANSFRD:::
Thermal | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28501 | 100.3 | P12:115:SPS:V35::1_HUTCH_GRAYC:::
Thermal | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28673 | 100.46 | P12:115:SPS:W08::1_HITCH_LASLEY:::
Thermal | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.2862 | 100.4 | P12:115:SPS:W10::1_HITCH_HANSFRD:::
Thermal | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.2867 | 101.4 | P42:345:SPS:HITCHLAND:1R75:SLG:EHV:
Thermal | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.27687 | 104.72 | P42:345:SPS:HITCHLAND:1R15:SLG:EHV:
Thermal | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.27647 | 107.4 | P42:345:SPS:POTTERCO:2R05:SLG:EHV:
Thermal | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28753 | 107.99 | P42:345:SPS:YOAKUM:J18####:SLG1:EHV:
Thermal | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28753 | 107.99 | P43:345:SPS:YOAKUM:TF#####:SLG:EHV:
Thermal | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28753 | 107.99 | P42:345:SPS:YOAKUM:J17####:SLG:EHV:
Thermal | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28728 | 111.68 | P43:345:SPS:TUCO:SLG::EHV:
Thermal | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28753 | 107.99 | P42:345:SPS:YOAKUM:J18####:SLG2:EHV:
Thermal | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28742 | 100.26 | P42:345:SPS:ROADRUNNER:J23####_SLG::::
Thermal | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28748 | 100.1 | P12:345:AEPW-AEPW:CHAMPSP-CLARKSV:::EHV::
Thermal | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28757 | 100 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV:
Thermal | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28744 | 100.16 | P12:345:WERE:BENT-ROSE-345:::EHV:
Thermal | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28757 | 100.29 | P12:345:WERE:N345-PSO-345:::EHV:
Thermal | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28768 | 100.31 | P12:345:WERE:VIOL-WICH-345:::EHV:
Thermal | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28744 | 100.11 | P23:345:WERE:BENT-345-50:::EHV:
Thermal | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28743 | 100.3 | P23:345:WERE:ROSE-345-80:::EHV:
Thermal | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28762 | 100.14 | P23:345:WERE:WICH-345-116:::EHV:
Thermal | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28741 | 100.1 | P23:345:WERE:WICH-345-50:::EHV:
Thermal | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28742 | 100.2 | P11:022:NPPD:COOPER1G:1:983:::
Thermal | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28734 | 100.59 | P11:023:NPPD:GENTLM1G:1:757:::
Thermal | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28734 | 100.67 | P11:024:NPPD:GENTLM2G:2:757:::
Thermal | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28726 | 100.86 | P11:024:UMZB:# 33 #:: LRS IN WY. LARAMIE RIVER STATION 1_MV::
Thermal | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28805 | 100.61 | P12:138:WFEC:ERICK_ELKCTY::::
Thermal | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28943 | 100.42 | P12:069:WFEC:LAKECRK_ELKCTY::::
Thermal | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.2928 | 100.09 | P12:138:WFEC:MOREWD_REDHILLS::::
Thermal | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28539 | 101.64 | P12:138:WFEC:RUSSELL_LKPAUL::::
Thermal | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28629 | 101.02 | P12:138:WFEC:RUSSELL_ALTUSJCT::::
Thermal | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.30832 | 102.83 | P12:345:OKGE:BKRBKR24::::
Thermal | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28809 | 100 | P12:138:OKGE:BKRBKR83::::
Thermal | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28741 | 100.38 | P12:345:OKGE:BKRBKR336::::
Thermal | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28741 | 100.4 | P12:345:OKGE:BKRBKR336_2::::
Thermal | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28831 | 100.1 | P12:138:OKGE:BKRBKR338::::
Thermal | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28831 | 100.1 | P13:138:OKGE:BKRBKR338_2::::
Thermal | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28789 | 101.29 | P12:345:OKGE:BKRBKR357_2::::
Thermal | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.29648 | 108.16 | P12:345:OKGE-AEPW:BKRBKR366::::
Thermal | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.29648 | 103.85 | P12:345:OKGE-AEPW:BKRBKR366::::
Thermal | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.48719 | 103.55 | P12:345:OKGE-AEPW:BKRBKR371::::
Thermal | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.48719 | 121.08 | P12:345:OKGE-AEPW:BKRBKR371::::
Thermal | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28812 | 101.09 | P12:345:OKGE:BKRBKR400::::
Thermal | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28653 | 100.64 | P12:345:OKGE:BKRBKR4191::::
Thermal | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28665 | 101.09 | P12:345:OKGE:BKRBKR4191::::
Thermal | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28653 | 100.64 | P12:345:OKGE:BKRBKR4192::::
Thermal | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28665 | 101.09 | P12:345:OKGE:BKRBKR4192::::
Thermal | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28695 | 100.46 | P12:345:OKGE:BKRBKR4193::::
Thermal | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28695 | 100.46 | P12:345:OKGE:BKRBKR4194::::
Thermal | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.2867 | 101.4 | P12:345:OKGE-SPS:BKRBKR4201::::
Thermal | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.2867 | 101.4 | P12:345:OKGE-SPS:BKRBKR4202::::
Thermal | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28808 | 101.37 | P12:345:OKGE:BKRBKR421::::
Thermal | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28717 | 100.87 | P12:345:OKGE:BKRBKR604::::
Thermal | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28715 | 101.05 | P12:345:OKGE:BKRBKR604_2::::
Thermal | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28826 | 100.16 | P13:138-345:OKGE:BKRBKR_3W082::::
Thermal | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28773 | 101.03 | P13:138-345:OKGE:BKRBKR_3W083::::
Thermal | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28668 | 102.01 | P42:345:OKGE:SB_ARIA7381::::
Thermal | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28617 | 101.63 | P42:345:OKGE:SB_BVTY7387::::
Thermal | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28821 | 101.5 | P41:345:OKGE:SB_REUD7381::::
Thermal | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28814 | 101.52 | P41:345:OKGE:SB_REUD7383::::
Thermal | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28817 | 102.12 | P41:345:OKGE:SB_REUD7385::::
Thermal | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28853 | 100.52 | P42:345:OKGE:SB_REUD7389::::
Thermal | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28679 | 100.06 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV:
Thermal | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28742 | 101.52 | P13:115:SUNC:HOLCOMB_GSU:::HV:
Thermal | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28678 | 100.14 | P23:345:SUNC:BU_BRK488:::EHV:
Thermal | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28679 | 100.06 | P23:345:SUNC:BU_BRK482:::EHV:
Thermal | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28744 | 100 | P12:HV-EHV:EES::8W.MEMPHIS%:8FREEPORTTN%:4BHAM STEEL:1
Thermal | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28748 | 100.1 | P12:EHV:EES::CHAMSPR7!:CLARKSV7!:1
Thermal | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28742 | 100.22 | P11:345:MEC-NPPD:COOPER 1
Thermal | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28742 | 100.09 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3
Thermal | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28742 | 100.2 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4
Thermal | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28742 | 100.06 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4
Thermal | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28742 | 100.05 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1
Thermal | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28742 | 100.13 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1
Thermal | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28742 | 100.03 | P13:345-24:MEC:AUTO-SINGLE:RAUN3:NEAL4G:1
Thermal | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28744 | 100.16 | P12:345:WERE:BENT-ROSE_345::
Thermal | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28757 | 100.29 | P12:345:WERE:N345-PSO_345::
Thermal | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28768 | 100.31 | P12:345:WERE:VIOL-WICH_345::
Thermal | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.29712 | 100.65 | 511446 CL-AFTP4 138 511458 ELKCTY-4 138 1
Thermal | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.29712 | 100.49 | 511446 CL-AFTP4 138 511463 HOB-JCT4 138 1
Thermal | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28769 | 102.08 | 511456 O.K.U.-7 345 763215 G18-092-TAP 345 1
Thermal | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28943 | 100.37 | 511459 ELKCTY-2 69.0 520897 ELKCITY2 69.0 1
Thermal | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28876 | 100.85 | 511463 HOB-JCT4 138 511564 MARTHA 4 138 1
Thermal | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.2877 | 102.67 | 511468 L.E.S.-7 345 762467 G18-015-TAP 345 1
Thermal | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28761 | 101.52 | 511468 L.E.S.-7 345 763215 G18-092-TAP 345 2
Thermal | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.29049 | 100.38 | 511485 CLINTJC4 138 511534 CL-NGTP4 138 1
Thermal | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.29049 | 100.11 | 511506 WTH WF 4 138 511534 CL-NGTP4 138 1
Thermal | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.29048 | 100.18 | 511506 WTH WF 4 138 511536 WEATHTP4 138 1
Thermal | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.48719 | 103.55 | 511557 CHISHOLM6 230 3WXFMR CHISHOLM6 1
Thermal | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28876 | 100.76 | 511564 MARTHA 4 138 529302 OMALTUS4 138 1
Thermal | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28658 | 100.14 | 512093 MEMPHIS2 69.0 512094 REDRIVR2 69.0 1
Thermal | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28658 | 100.17 | 512094 REDRIVR2 69.0 512095 ESTELNE2 69.0 1
Thermal | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28658 | 100.24 | 512095 ESTELNE2 69.0 512096 CAREY 2 69.0 1
Thermal | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28658 | 100.26 | 512096 CAREY 2 69.0 512097 AIRPORT2 69.0 1
Thermal | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28658 | 100.29 | 512097 AIRPORT2 69.0 512098 AMOCOTP2 69.0 1
Thermal | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28658 | 100.48 | 512098 AMOCOTP2 69.0 512100 CHLDR2WT 69.0 1
Thermal | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28482 | 100.83 | 512101 CHILD4WT 138 512103 HOLTP4WT 138 1
Thermal | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28482 | 100.36 | 512103 HOLTP4WT 138 512104 WELL 4WT 138 1
Thermal | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28617 | 101.59 | 515375 WWRDEHV7 345 515458 BORDER 7 345 1
Thermal | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28742 | 100.86 | 515375 WWRDEHV7 345 562024 G11-019-SUB 345 1
Thermal | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28742 | 100.31 | 515375 WWRDEHV7 345 763527 GEN-2019-012 345 1
Thermal | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28617 | 101.63 | 515458 BORDER 7 345 560022 CRAWFISH_DR 345 1
Thermal | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28812 | 101.67 | 515543 RENFROW7 345 763421 G18-128-TAP 345 1
Thermal | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.2873 | 100.16 | 515618 BALKOW 7 345 3WXFMR BALKOW 7 1
Thermal | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.2873 | 100.16 | 515618 BALKOW 7 345 3WXFMR BALKOW 7 1_Dup1
Thermal | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28789 | 102.2 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Thermal | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28715 | 101.03 | 515634 PALDR1W7 345 3WXFMR PALO2 _1 1
Thermal | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28943 | 100.03 | 520876 DILL JT2 69.0 520897 ELKCITY2 69.0 1
Thermal | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28673 | 100.46 | 523093 HITCHLAND 3 115 523160 FRISCO_WND 3 115 1
Thermal | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28713 | 101.24 | 523093 HITCHLAND 3 115 523174 GOODWELLWND3 115 1
Thermal | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28714 | 100.29 | 523095 HITCHLAND 6 230 523155 OCHILTREE 6 230 1
Thermal | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28428 | 102.22 | 523095 HITCHLAND 6 230 523309 MOORE_CNTY 6 230 1
Thermal | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28681 | 100.29 | 523097 HITCHLAND 7 345 3WXFMR H TB80155502 1
Thermal | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28663 | 100.54 | 523097 HITCHLAND 7 345 3WXFMR SIEM 8743067 2
Thermal | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.27687 | 104.8 | 523097 HITCHLAND 7 345 523961 POTTER_CO 7 345 1
Thermal | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28714 | 100.25 | 523155 OCHILTREE 6 230 3WXFMR H TP80219401 1
Thermal | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28673 | 100.46 | 523160 FRISCO_WND 3 115 523175 LASLEY 3 115 1
Thermal | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28728 | 100.33 | 523172 GWELL_COLL11 34.5 523174 GOODWELLWND3 115 1
Thermal | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28727 | 100.37 | 523173 GWELL_COLL21 34.5 523174 GOODWELLWND3 115 1
Thermal | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28725 | 100.47 | 523309 MOORE_CNTY 6 230 3WXFMR ENRCO 136402 1
Thermal | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28742 | 103.88 | 523344 BLKHAWK_W 3 115 523461 BLACKHAWK1 1 13.8 1
Thermal | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28742 | 104.3 | 523346 BLKHAWK_E 3 115 523462 BLACKHAWK2 1 13.8 1
Thermal | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28501 | 100.3 | 523546 HUTCH_S 3 115 523636 GRAY_CNTY 3 115 1
Thermal | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28501 | 100.3 | 523636 GRAY_CNTY 3 115 3WXFMR WH RHP17221 1
Thermal | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28742 | 100.22 | 523853 FINNEY 7 345 762662 G18-030-TAP 345 1
Thermal | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28705 | 101.73 | 523926 MAJESTC_WND3 115 523928 MARTIN 3 115 1
Thermal | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28725 | 100.53 | 523926 MAJESTC_WND3 115 523947 MAJESTC-LV11 34.5 1
Thermal | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28723 | 100.65 | 523926 MAJESTC_WND3 115 523948 MAJESTC-LV21 34.5 1
Thermal | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.27658 | 106.23 | 523961 POTTER_CO 7 345 3WXFMR WAUK 90343-A 1
Thermal | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28715 | 101.2 | 523961 POTTER_CO 7 345 524296 SPNSPUR_WND7 345 1
Thermal | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28661 | 111.3 | 523977 HARRNG_WST 6 230 523971 HARRNGTON1 1 24.0 1
Thermal | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28654 | 111.89 | 523978 HARRNG_MID 6 230 523972 HARRNGTON2 1 24.0 1
Thermal | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28452 | 100.05 | 523978 HARRNG_MID 6 230 523979 HARRNG_EST 6 230 @1
Thermal | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28657 | 111.39 | 523979 HARRNG_EST 6 230 523973 HARRNGTON3 1 24.0 1
Thermal | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28691 | 103.26 | 524043 NICHOLS 3 115 524022 NICHOLS_2 1 13.8 1
Thermal | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28613 | 108.11 | 524044 NICHOLS 6 230 524023 NICHOLS_3 1 22.0 1
Thermal | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28704 | 101.86 | 524267 BUSHLAND 6 230 524290 WILDOR2_JUS6 230 1
Thermal | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.2872 | 100.89 | 524275 WILDOR_WND 1 34.5 524276 WILDOR_WND 6 230 1
Thermal | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.2872 | 100.89 | 524276 WILDOR_WND 6 230 524290 WILDOR2_JUS6 230 1
Thermal | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28727 | 100.43 | 524289 GS-PHWDRNCH1 34.5 524290 WILDOR2_JUS6 230 1
Thermal | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28715 | 101.18 | 524296 SPNSPUR_WND7 345 524299 SPNSPUR_COL7 345 1
Thermal | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28715 | 101.18 | 524299 SPNSPUR_COL7 345 3WXFMR SPNSPUR_COL7 1
Thermal | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28741 | 100.5 | 524909 ROOSEVELT 6 230 525531 TOLK 6 230 2
Thermal | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28742 | 101.72 | 524909 ROOSEVELT 6 230 763483 GEN-2019-003 230 1
Thermal | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28542 | 100.53 | 525213 SWISHER 6 230 525830 TUCO_INT 6 230 1
Thermal | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28742 | 100.68 | 525461 NEWHART 6 230 763186 GEN-2018-089 230 1
Thermal | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28726 | 101.39 | 525480 PLANT_X 3 115 525493 PLANT_X3 1 13.8 1
Thermal | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28703 | 103.31 | 525481 PLANT_X 6 230 525494 PLANT_X4 1 20.0 1
Thermal | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28742 | 101.36 | 525481 PLANT_X 6 230 763120 GEN-2018-081 230 1
Thermal | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28668 | 108.78 | 525531 TOLK 6 230 525561 TOLK_1 1 24.0 1
Thermal | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28649 | 110.16 | 525531 TOLK 6 230 525562 TOLK_2 1 24.0 1
Thermal | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28737 | 100.48 | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1
Thermal | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28742 | 101.03 | 525531 TOLK 6 230 762132 GEN-2017-158 230 1
Thermal | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28742 | 104.61 | 525531 TOLK 6 230 763241 GEN-2018-097 230 1
Thermal | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28742 | 101.05 | 525830 TUCO_INT 6 230 525840 ANTELOPE_1 6 230 1
Thermal | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28727 | 100.51 | 525830 TUCO_INT 6 230 525957 HALE_WNDCL16 230 1
Thermal | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28744 | 100.4 | 525830 TUCO_INT 6 230 526161 CARLISLE 6 230 1
Thermal | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.2872 | 101.73 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2
Thermal | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28714 | 102.37 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _9 1
Thermal | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28716 | 103.84 | 525832 TUCO_INT 7 345 525850 ELK_CT1 345 1
Thermal | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28753 | 107.62 | 525832 TUCO_INT 7 345 526936 YOAKUM_345 345 1
Thermal | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28729 | 101.63 | 525850 ELK_CT1 345 525844 ELK_1 1 18.0 1
Thermal | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28729 | 101.63 | 525850 ELK_CT1 345 525845 ELK_2 1 18.0 1
Thermal | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28732 | 100.37 | 526012 LOST_DRAW 3 115 584560 GEN-2015-014 115 1
Thermal | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.287 | 103.21 | 526337 JONES 6 230 526331 JONES_1 1 22.0 1
Thermal | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.287 | 103.21 | 526337 JONES 6 230 526332 JONES_2 1 22.0 1
Thermal | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.2874 | 100.67 | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1
Thermal | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28744 | 101.96 | 526936 YOAKUM_345 345 527896 HOBBS_INT 7 345 1
Thermal | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28734 | 102.29 | 527146 MUSTANG 3 115 527161 MUSTANG_1 1 18.0 1
Thermal | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28731 | 102.28 | 527146 MUSTANG 3 115 527162 MUSTANG_2 1 18.0 1
Thermal | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28722 | 105.17 | 527149 MUSTANG 6 230 527151 GS-MUSTANG 6 230 @1
Thermal | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28719 | 102.36 | 527149 MUSTANG 6 230 527163 MUSTANG_3 1 19.0 1
Thermal | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28733 | 102.18 | 527151 GS-MUSTANG 6 230 527165 MUSTANG_5 1 18.0 1
Thermal | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28731 | 102.39 | 527151 GS-MUSTANG 6 230 527166 MUSTANG_6 1 18.0 1
Thermal | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28734 | 100.05 | 527455 RSWL_SLRCOL3 115 527454 RSWL_SOLAR11 34.5 1
Thermal | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28734 | 100.05 | 527455 RSWL_SLRCOL3 115 527482 CHAVES_CNTY3 115 1
Thermal | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28733 | 100.06 | 527654 RSVLT_CC_W 7 345 527655 RSVLT_CC_E 7 345 1
Thermal | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28733 | 100.06 | 527654 RSVLT_CC_W 7 345 527666 RSVLT_COL1 7 345 1
Thermal | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28729 | 100.36 | 527655 RSVLT_CC_E 7 345 527656 CROSSROADS 7 345 1
Thermal | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28733 | 100.06 | 527666 RSVLT_COL1 7 345 3WXFMR RSVLT_COL1 7 1
Thermal | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28713 | 102.89 | 527867 CUNNIGHM_S 6 230 527882 CUNINGHAM2 1 20.0 1
Thermal | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28729 | 102.15 | 527891 HOBBS_INT 3 115 527901 HOBBS_PLT1 1 18.0 1
Thermal | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28729 | 102.16 | 527891 HOBBS_INT 3 115 527902 HOBBS_PLT2 1 18.0 1
Thermal | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28721 | 103.99 | 527894 HOBBS_INT 6 230 527903 HOBBS_PLT3 1 18.0 1
Thermal | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28724 | 101.56 | 528355 MADDOX 3 115 528361 MADDOX_1 1 13.8 1
Thermal | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28876 | 100.14 | 529298 OMPVET-4 138 529302 OMALTUS4 138 1
Thermal | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28789 | 103.16 | 532794 ROSEHIL7 345 560053 G15052_T 345 1
Thermal | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28812 | 101.82 | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1
Thermal | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28722 | 100.04 | 539659 CUDAHY 3 115 539783 CRKCK 3 115 1
Thermal | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28764 | 102.28 | 560022 CRAWFISH_DR 345 762216 G17-151TAP 345 1
Thermal | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28761 | 102.13 | 560022 CRAWFISH_DR 345 762467 G18-015-TAP 345 1
Thermal | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28742 | 101.63 | 560022 CRAWFISH_DR 345 763087 GEN-2018-073 345 1
Thermal | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28771 | 103.54 | 560022 CRAWFISH_DR 345 763215 G18-092-TAP 345 2
Thermal | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28742 | 100.33 | 560071 G16-003-TAP 345 587020 GEN-2016-003 345 1
Thermal | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28742 | 100.14 | 562021 G11-020-SUB 345 562024 G11-019-SUB 345 1
Thermal | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28742 | 100.13 | 562022 G11-020-GSU 34.5 562021 G11-020-SUB 345 1
Thermal | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28742 | 100.17 | 562025 G11-019-GSU 34.5 562024 G11-019-SUB 345 1
Thermal | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28876 | 100.79 | P12:138:AEPW-OMPA:HOB-JCT4:OMALTUS4
Thermal | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28629 | 101.02 | P12:138:AEPW-WFEC:ALTUSJT4:RUSSELL4
Thermal | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28539 | 101.64 | P12:138:AEPW-WFEC:LAKEP4WT:RUSSELL4
Thermal | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28732 | 100.37 | 584560 GEN-2015-014 115 584561 G15-014XFMR1 34.5 1
Thermal | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28742 | 100.33 | 587021 G16-003XFMR1 34.5 587020 GEN-2016-003 345 1
Thermal | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28269 | 102.89 | P12:138:AEPW:CHILD4WT:LAKEP4WT
Thermal | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.29826 | 102.68 | P12:138:AEPW:ELKCTY-4:CLINTJC4
Thermal | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.29712 | 100.66 | P12:138:AEPW:HOB-JCT4:ELKCTY-4
Thermal | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.29049 | 100.54 | P12:138:AEPW:WTHWF4:CLINTJC4
Thermal | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.29048 | 100.33 | P12:138:AEPW:WTHWF4:WTH_SE4
Thermal | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28805 | 100.43 | P12:138:WFEC-AEPW:ELKCTY-4:ERICK4
Thermal | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.29648 | 108.16 | P12:345:AEPW-OKGE:L.E.S.-7:GRACMNT7
Thermal | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.29648 | 103.85 | P12:345:AEPW-OKGE:L.E.S.-7:GRACMNT7
Thermal | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28757 | 100.29 | P12:345:AEPW-WERE:DELWARE7:NEOSHO7
Thermal | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28757 | 100.29 | 6111_Dup1
Thermal | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28758 | 100.39 | P12:345:AEPW:DELWARE7:N.E.S.-7
Thermal | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28769 | 102.13 | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Thermal | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28658 | 100.04 | P12:69:AEPW:CHLDR2WT:MEMPHIS2
Thermal | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28943 | 100.42 | P12:69:WFEC-AEPW:LKCREEK2:ELKCTY-2
Thermal | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.35177 | 113.78 | P13:138-230:AEPW:ELKCTY-4
Thermal | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28749 | 100.3 | P23:500:EES-EAI:KEO:B4941
Thermal | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28749 | 100.56 | P23:500:EES-EAI:KEO:B4941
Thermal | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28748 | 100.18 | P23:500:EES-EAI:KEO:B4921
Thermal | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28744 | 100 | P12:500:EES-EAI:WMPEHV:BHMSTL:BHMSTL:NEWPORT
Thermal | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28658 | 100.7 | P13:69-138:AEPW:CHLDR2WT
Thermal | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28943 | 100.57 | P13:69-138:AEPW:ELKCTY-2
Thermal | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28745 | 100.12 | P23:500:EAI-TVA:NBF_WEST M~1
Thermal | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28742 | 100.13 | P23:345:MEC:CBEC 905
Thermal | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28742 | 100.05 | P23:345:MEC:CBEC 908
Thermal | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28742 | 100.03 | P23:345:MEC:RAUN 0210
Thermal | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28742 | 100.24 | 762132 GEN-2017-158 230 763252 G18-099-XFM1 34.5 1
Thermal | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28742 | 100.24 | 762132 GEN-2017-158 230 763255 G18-099-XFM2 34.5 1
Thermal | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28764 | 102.43 | 762216 G17-151TAP 345 762467 G18-015-TAP 345 1
Thermal | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28754 | 101.37 | 762467 G18-015-TAP 345 763215 G18-092-TAP 345 1
Thermal | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28742 | 100.89 | 763087 GEN-2018-073 345 763088 G18-073-XFM1 34.5 1
Thermal | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28742 | 100.18 | 763087 GEN-2018-073 345 763091 G18-073-XFM2 34.5 1
Thermal | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28742 | 101.36 | 763120 GEN-2018-081 230 763121 G18-081-XFM1 34.5 1
Thermal | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28742 | 100.68 | 763186 GEN-2018-089 230 763187 G18-089-XFM1 34.5 1
Thermal | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28742 | 100.1 | 763208 GEN-2018-092 345 763215 G18-092-TAP 345 1
Thermal | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28742 | 100.5 | 763241 GEN-2018-097 230 763242 G18-097-XFM1 34.5 1
Thermal | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28742 | 100.42 | 763241 GEN-2018-097 230 763307 G18-112-XFM1 34.5 1
Thermal | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28742 | 100.42 | 763241 GEN-2018-097 230 763310 G18-112-XFM2 34.5 1
Thermal | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28742 | 100.5 | 763241 GEN-2018-097 230 763395 G18-124-XFM1 34.5 1
Thermal | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28742 | 100.5 | 763241 GEN-2018-097 230 763398 G18-124-XFM2 34.5 1
Thermal | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28742 | 101.15 | 763483 GEN-2019-003 230 763484 G19-003-XFM1 34.5 1
Thermal | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28742 | 100.02 | 763483 GEN-2019-003 230 763605 G19-021-XFM1 34.5 1
Thermal | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28742 | 100.31 | 763527 GEN-2019-012 345 763528 G19-012-XFM1 34.5 1
Thermal | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28665 | 102.2 | P42:345:OKGE:SB_BVTY7305
Thermal | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28744 | 100.11 | P23:345:WERE:BENT_345-50::
Thermal | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28743 | 100.3 | P23:345:WERE:ROSE_345-80::
Thermal | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28762 | 100.14 | P23:345:WERE:WICH_345-116::
Thermal | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28741 | 100.1 | P23:345:WERE:WICH_345-50::
Thermal | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28748 | 100.1 | P43:345:AEPW:CHAMBERS SPRING CB 12720 NBTB+FAULT
Thermal | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28748 | 100.1 | P42:345:AEPW:CHAMBERS SPRING CB 13720 NBTB+FAULT
Thermal | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28748 | 100.1 | P42:345:AEPW:CHAMBERS SPRING CB 13850 NBTB+FAULT
Thermal | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28769 | 102.1 | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Thermal | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.29694 | 107.94 | P42:345:AEPW:LAWTON EASTSIDE CB 3413A NBTB+FAULT
Thermal | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.29744 | 107.73 | P42:345:AEPW:LAWTON EASTSIDE CB 3425A NBTB+FAULT
Thermal | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28775 | 101.8 | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Thermal | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28758 | 100.39 | P42:345:AEPW:NES CB 3445A NBTB+FAULT
Thermal | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28759 | 100.41 | P42:345:AEPW:DELAWARE CB 3401A NBTB+FAULT
Thermal | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28759 | 100.41 | P42:345:AEPW:DELAWARE CB 3405A NBTB+FAULT
Thermal | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28759 | 100.41 | P42:345:AEPW:DELAWARE CB 3409A NBTB+FAULT
Thermal | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28748 | 100.1 | P23:345:AEPW:CHAMBERS SPRING CB 12720 NBTB
Thermal | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28748 | 100.1 | P23:345:AEPW:CHAMBERS SPRING CB 13720 NBTB
Thermal | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28748 | 100.1 | P23:345:AEPW:CHAMBERS SPRING CB 13850 NBTB
Thermal | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28769 | 102.08 | P23:345:AEPW:OKLAUNION CB 3401A NBTB
Thermal | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.29694 | 107.94 | P23:345:AEPW:LAWTON EASTSIDE CB 3413A NBTB
Thermal | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.29744 | 107.73 | P23:345:AEPW:LAWTON EASTSIDE CB 3425A NBTB
Thermal | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28775 | 101.8 | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Thermal | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28758 | 100.39 | P23:345:AEPW:NES CB 3441A NBTB
Thermal | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28759 | 100.41 | P23:345:AEPW:DELAWARE CB 3401A NBTB
Thermal | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28759 | 100.41 | P23:345:AEPW:DELAWARE CB 3405A NBTB
Thermal | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28759 | 100.41 | P23:345:AEPW:DELAWARE CB 3409A NBTB
Thermal | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28742 | 100.03 | P11:115:SUNC:GARDENCITY_S2:97:531459(2)
Thermal | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28868 | 101.87 | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Thermal | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28868 | 101.87 | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Thermal | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.2767 | 128.54 | P42:345:OKGE:SB_BVTY7315_PRE19S
Thermal | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.35177 | 113.77 | P12:230:AEPW:ELKCITY6:CHISHOLM6
Thermal | 04ALL | 1 | 23SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 1 | 164.31 | P12:230:AEPW:SWEETWT6:CHISHOLM6
Thermal | 04ALL | 1 | 26L | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.20852 | 105.7 | P42:345:SPS:YOAKUM:J18####:SLG1:EHV:
Thermal | 04ALL | 1 | 26L | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.20852 | 105.7 | P43:345:SPS:YOAKUM:TF#####:SLG:EHV:
Thermal | 04ALL | 1 | 26L | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.20852 | 105.7 | P42:345:SPS:YOAKUM:J17####:SLG:EHV:
Thermal | 04ALL | 1 | 26L | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.20852 | 105.37 | P43:345:SPS:TUCO:SLG::EHV:
Thermal | 04ALL | 1 | 26L | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.20852 | 105.7 | P42:345:SPS:YOAKUM:J18####:SLG2:EHV:
Thermal | 04ALL | 1 | 26L | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.20869 | 105.39 | P12:345:OKGE-AEPW:BKRBKR366::::
Thermal | 04ALL | 1 | 26L | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.20869 | 100.58 | P12:345:OKGE-AEPW:BKRBKR366::::
Thermal | 04ALL | 1 | 26L | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.21802 | 115.9 | P42:345:OKGE:SB_BVTY7387::::
Thermal | 04ALL | 1 | 26L | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.27984 | 103.81 | 511553 CHISHOLM7 345 755000 WWDBORDT 345 1
Thermal | 04ALL | 1 | 26L | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.21802 | 115.94 | 515458 BORDER 7 345 560022 CRAWFISH_DR 345 1
Thermal | 04ALL | 1 | 26L | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.21802 | 115.83 | 515458 BORDER 7 345 755000 WWDBORDT 345 1
Thermal | 04ALL | 1 | 26L | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.20503 | 100.31 | 523095 HITCHLAND 6 230 523309 MOORE_CNTY 6 230 1
Thermal | 04ALL | 1 | 26L | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.20852 | 105.37 | 525832 TUCO_INT 7 345 526936 YOAKUM_345 345 1
Thermal | 04ALL | 1 | 26L | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.20869 | 105.39 | P12:345:AEPW-OKGE:L.E.S.-7:GRACMNT7
Thermal | 04ALL | 1 | 26L | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.20869 | 100.58 | P12:345:AEPW-OKGE:L.E.S.-7:GRACMNT7
Thermal | 04ALL | 1 | 26L | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.2087 | 105.61 | P42:345:AEPW:LAWTON EASTSIDE CB 3413A NBTB+FAULT
Thermal | 04ALL | 1 | 26L | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.20871 | 105.98 | P42:345:AEPW:LAWTON EASTSIDE CB 3425A NBTB+FAULT
Thermal | 04ALL | 1 | 26L | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.2087 | 105.61 | P23:345:AEPW:LAWTON EASTSIDE CB 3413A NBTB
Thermal | 04ALL | 1 | 26L | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.20871 | 105.98 | P23:345:AEPW:LAWTON EASTSIDE CB 3425A NBTB
Thermal | 04ALL | 1 | 26SP | GEN-2019-013 | FROM->TO | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 353 | 1 | 164.6 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1
Thermal | 04ALL | 1 | 26SP | GEN-2019-013 | FROM->TO | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.9111 | 119.22 | 523771 GRAPEVINE 6 230 523777 WHEELER 6 230 1
Thermal | 04ALL | 1 | 26SP | GEN-2019-013 | FROM->TO | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 353 | 1 | 164.59 | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1
Thermal | 04ALL | 1 | 26SP | GEN-2019-013 | FROM->TO | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 353 | 1 | 164.6 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6
Thermal | 04ALL | 1 | 26SP | GEN-2019-013 | FROM->TO | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 |  | 395 | 0.21091 | 118.35 | P42:345:OKGE:SB_BVTY7315_PRE19S
Thermal | 04ALL | 1 | 26SP | GEN-2019-013 | FROM->TO | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 |  | 395 | 1 | 148.63 | P12:230:AEPW:SWEETWT6:CHISHOLM6
Thermal | 04ALL | 1 | 26SP | GEN-2019-013 | FROM->TO | 523771 GRAPEVINE 6 230 523777 WHEELER 6 230 1 |  | 319 | 0.83103 | 134.9 | P12:230:AEPW:SWEETWT6:CHISHOLM6
Thermal | 04ALL | 1 | 26SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.20693 | 100.05 | P42:345:SPS:HITCHLAND:1R15:SLG:EHV:
Thermal | 04ALL | 1 | 26SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.20651 | 102.81 | P42:345:SPS:POTTERCO:2R05:SLG:EHV:
Thermal | 04ALL | 1 | 26SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.216 | 103.72 | P42:345:SPS:YOAKUM:J18####:SLG1:EHV:
Thermal | 04ALL | 1 | 26SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.216 | 103.72 | P43:345:SPS:YOAKUM:TF#####:SLG:EHV:
Thermal | 04ALL | 1 | 26SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.216 | 103.72 | P42:345:SPS:YOAKUM:J17####:SLG:EHV:
Thermal | 04ALL | 1 | 26SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.21579 | 106.61 | P43:345:SPS:TUCO:SLG::EHV:
Thermal | 04ALL | 1 | 26SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.216 | 103.72 | P42:345:SPS:YOAKUM:J18####:SLG2:EHV:
Thermal | 04ALL | 1 | 26SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.22738 | 103.16 | P42:345:OKGE:SB_BVTY7387::::
Thermal | 04ALL | 1 | 26SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28449 | 107.58 | 511553 CHISHOLM7 345 755000 WWDBORDT 345 1
Thermal | 04ALL | 1 | 26SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.48663 | 108.22 | 511557 CHISHOLM6 230 3WXFMR CHISHOLM6 1
Thermal | 04ALL | 1 | 26SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.22738 | 103.16 | 515458 BORDER 7 345 560022 CRAWFISH_DR 345 1
Thermal | 04ALL | 1 | 26SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.22738 | 103.11 | 515458 BORDER 7 345 755000 WWDBORDT 345 1
Thermal | 04ALL | 1 | 26SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.20693 | 100.11 | 523097 HITCHLAND 7 345 523961 POTTER_CO 7 345 1
Thermal | 04ALL | 1 | 26SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.20659 | 101.84 | 523961 POTTER_CO 7 345 3WXFMR WAUK 90343-A 1
Thermal | 04ALL | 1 | 26SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.21488 | 105.61 | 523977 HARRNG_WST 6 230 523971 HARRNGTON1 1 24.0 1
Thermal | 04ALL | 1 | 26SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.21481 | 106.21 | 523978 HARRNG_MID 6 230 523972 HARRNGTON2 1 24.0 1
Thermal | 04ALL | 1 | 26SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.21484 | 105.7 | 523979 HARRNG_EST 6 230 523973 HARRNGTON3 1 24.0 1
Thermal | 04ALL | 1 | 26SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.2144 | 102.37 | 524044 NICHOLS 6 230 524023 NICHOLS_3 1 22.0 1
Thermal | 04ALL | 1 | 26SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.21507 | 102.61 | 525531 TOLK 6 230 525561 TOLK_1 1 24.0 1
Thermal | 04ALL | 1 | 26SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.2149 | 103.83 | 525531 TOLK 6 230 525562 TOLK_2 1 24.0 1
Thermal | 04ALL | 1 | 26SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.216 | 103.23 | 525832 TUCO_INT 7 345 526936 YOAKUM_345 345 1
Thermal | 04ALL | 1 | 26SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.21091 | 131.54 | P42:345:OKGE:SB_BVTY7315_PRE19S
Thermal | 04ALL | 1 | 26SP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 1 | 164.32 | P12:230:AEPW:SWEETWT6:CHISHOLM6
Thermal | 04ALL | 1 | 26WP | GEN-2019-013 | FROM->TO | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 439 | 1 | 132.35 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1
Thermal | 04ALL | 1 | 26WP | GEN-2019-013 | FROM->TO | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 439 | 0.91088 | 102.67 | 523771 GRAPEVINE 6 230 523777 WHEELER 6 230 1
Thermal | 04ALL | 1 | 26WP | GEN-2019-013 | FROM->TO | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 439 | 1 | 132.35 | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1
Thermal | 04ALL | 1 | 26WP | GEN-2019-013 | FROM->TO | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 439 | 1 | 132.35 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6
Thermal | 04ALL | 1 | 26WP | GEN-2019-013 | FROM->TO | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 |  | 441 | 1 | 132.57 | P12:230:AEPW:SWEETWT6:CHISHOLM6
Thermal | 04ALL | 1 | 26WP | GEN-2019-013 | FROM->TO | 523771 GRAPEVINE 6 230 523777 WHEELER 6 230 1 |  | 346 | 0.83104 | 126.97 | P12:230:AEPW:SWEETWT6:CHISHOLM6
Thermal | 04ALL | 1 | 26WP | GEN-2019-013 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 439 | 1 | 131.72 | P12:230:AEPW:SWEETWT6:CHISHOLM6
Thermal | 04ALL | 1 | 23SP | GEN-2019-066 | FROM->TO | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | 349 |  | 0.28742 | 100.91 | System Intact
Thermal | 04ALL | 1 | 23SP | GEN-2019-066 | FROM->TO | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 353 | 1 | 164.55 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1
Thermal | 04ALL | 1 | 23SP | GEN-2019-066 | FROM->TO | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.87401 | 114.63 | 523771 GRAPEVINE 6 230 523777 WHEELER 6 230 1
Thermal | 04ALL | 1 | 23SP | GEN-2019-066 | FROM->TO | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 353 | 1 | 164.55 | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1
Thermal | 04ALL | 1 | 23SP | GEN-2019-066 | FROM->TO | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 353 | 1 | 164.55 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6
Thermal | 04ALL | 1 | 23SP | GEN-2019-066 | FROM->TO | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 |  | 395 | 0.28728 | 100.24 | P43:345:SPS:TUCO:SLG::EHV:
Thermal | 04ALL | 1 | 23SP | GEN-2019-066 | FROM->TO | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 |  | 395 | 0.48719 | 108.77 | P12:345:OKGE-AEPW:BKRBKR371::::
Thermal | 04ALL | 1 | 23SP | GEN-2019-066 | FROM->TO | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 |  | 395 | 0.28654 | 100.42 | 523978 HARRNG_MID 6 230 523972 HARRNGTON2 1 24.0 1
Thermal | 04ALL | 1 | 23SP | GEN-2019-066 | FROM->TO | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 |  | 395 | 0.35177 | 102.14 | P13:138-230:AEPW:ELKCTY-4
Thermal | 04ALL | 1 | 23SP | GEN-2019-066 | FROM->TO | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 |  | 395 | 0.2767 | 115.6 | P42:345:OKGE:SB_BVTY7315_PRE19S
Thermal | 04ALL | 1 | 23SP | GEN-2019-066 | FROM->TO | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 |  | 395 | 0.35177 | 102.12 | P12:230:AEPW:ELKCITY6:CHISHOLM6
Thermal | 04ALL | 1 | 23SP | GEN-2019-066 | FROM->TO | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 |  | 395 | 1 | 148.63 | P12:230:AEPW:SWEETWT6:CHISHOLM6
Thermal | 04ALL | 1 | 23SP | GEN-2019-066 | FROM->TO | 523771 GRAPEVINE 6 230 523777 WHEELER 6 230 1 |  | 319 | 0.23039 | 105.83 | P42:345:OKGE:SB_BVTY7315_PRE19S
Thermal | 04ALL | 1 | 23SP | GEN-2019-066 | FROM->TO | 523771 GRAPEVINE 6 230 523777 WHEELER 6 230 1 |  | 319 | 0.83099 | 135.53 | P12:230:AEPW:SWEETWT6:CHISHOLM6
Thermal | 04ALL | 1 | 23SP | GEN-2019-066 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28748 | 100.1 | P12:345:AEPW-AEPW:CHAMPSP-CLARKSV
Thermal | 04ALL | 1 | 23SP | GEN-2019-066 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28757 | 100 | P23:345:KCPL-WERE:237LACYGNE_R1-6::LACYGU1-LACYGNE-NEOSHO
Thermal | 04ALL | 1 | 23SP | GEN-2019-066 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28729 | 103.97 | P11:115:SPS:HOBBS1&3:145MW::::
Thermal | 04ALL | 1 | 23SP | GEN-2019-066 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28734 | 103.25 | P11:115:SPS:MUSTANG1&3:153MW::::
Thermal | 04ALL | 1 | 23SP | GEN-2019-066 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28714 | 100.29 | P12:230:SPS:K76::1_HITCH_OCHLTR:::
Thermal | 04ALL | 1 | 23SP | GEN-2019-066 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28638 | 100.3 | P12:115:SPS:T51::1_BOWERS_GRAPE:::
Thermal | 04ALL | 1 | 23SP | GEN-2019-066 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.2862 | 100.39 | P12:115:SPS:T87::1_SPRMN_HANSFRD:::
Thermal | 04ALL | 1 | 23SP | GEN-2019-066 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28501 | 100.3 | P12:115:SPS:V35::1_HUTCH_GRAYC:::
Thermal | 04ALL | 1 | 23SP | GEN-2019-066 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28673 | 100.46 | P12:115:SPS:W08::1_HITCH_LASLEY:::
Thermal | 04ALL | 1 | 23SP | GEN-2019-066 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.2862 | 100.4 | P12:115:SPS:W10::1_HITCH_HANSFRD:::
Thermal | 04ALL | 1 | 23SP | GEN-2019-066 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.2867 | 101.4 | P42:345:SPS:HITCHLAND:1R75:SLG:EHV:
Thermal | 04ALL | 1 | 23SP | GEN-2019-066 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.27687 | 104.72 | P42:345:SPS:HITCHLAND:1R15:SLG:EHV:
Thermal | 04ALL | 1 | 23SP | GEN-2019-066 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.27647 | 107.4 | P42:345:SPS:POTTERCO:2R05:SLG:EHV:
Thermal | 04ALL | 1 | 23SP | GEN-2019-066 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28753 | 107.99 | P42:345:SPS:YOAKUM:J18####:SLG1:EHV:
Thermal | 04ALL | 1 | 23SP | GEN-2019-066 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28753 | 107.99 | P43:345:SPS:YOAKUM:TF#####:SLG:EHV:
Thermal | 04ALL | 1 | 23SP | GEN-2019-066 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28753 | 107.99 | P42:345:SPS:YOAKUM:J17####:SLG:EHV:
Thermal | 04ALL | 1 | 23SP | GEN-2019-066 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28728 | 111.68 | P43:345:SPS:TUCO:SLG::EHV:
Thermal | 04ALL | 1 | 23SP | GEN-2019-066 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28753 | 107.99 | P42:345:SPS:YOAKUM:J18####:SLG2:EHV:
Thermal | 04ALL | 1 | 23SP | GEN-2019-066 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28742 | 100.26 | P42:345:SPS:ROADRUNNER:J23####_SLG::::
Thermal | 04ALL | 1 | 23SP | GEN-2019-066 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28748 | 100.1 | P12:345:AEPW-AEPW:CHAMPSP-CLARKSV:::EHV::
Thermal | 04ALL | 1 | 23SP | GEN-2019-066 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28757 | 100 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV:
Thermal | 04ALL | 1 | 23SP | GEN-2019-066 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28744 | 100.16 | P12:345:WERE:BENT-ROSE-345:::EHV:
Thermal | 04ALL | 1 | 23SP | GEN-2019-066 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28757 | 100.29 | P12:345:WERE:N345-PSO-345:::EHV:
Thermal | 04ALL | 1 | 23SP | GEN-2019-066 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28768 | 100.31 | P12:345:WERE:VIOL-WICH-345:::EHV:
Thermal | 04ALL | 1 | 23SP | GEN-2019-066 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28744 | 100.11 | P23:345:WERE:BENT-345-50:::EHV:
Thermal | 04ALL | 1 | 23SP | GEN-2019-066 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28743 | 100.3 | P23:345:WERE:ROSE-345-80:::EHV:
Thermal | 04ALL | 1 | 23SP | GEN-2019-066 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28762 | 100.14 | P23:345:WERE:WICH-345-116:::EHV:
Thermal | 04ALL | 1 | 23SP | GEN-2019-066 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28741 | 100.1 | P23:345:WERE:WICH-345-50:::EHV:
Thermal | 04ALL | 1 | 23SP | GEN-2019-066 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28742 | 100.2 | P11:022:NPPD:COOPER1G:1:983:::
Thermal | 04ALL | 1 | 23SP | GEN-2019-066 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28734 | 100.59 | P11:023:NPPD:GENTLM1G:1:757:::
Thermal | 04ALL | 1 | 23SP | GEN-2019-066 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28734 | 100.67 | P11:024:NPPD:GENTLM2G:2:757:::
Thermal | 04ALL | 1 | 23SP | GEN-2019-066 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28726 | 100.86 | P11:024:UMZB:# 33 #:: LRS IN WY. LARAMIE RIVER STATION 1_MV::
Thermal | 04ALL | 1 | 23SP | GEN-2019-066 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28805 | 100.61 | P12:138:WFEC:ERICK_ELKCTY::::
Thermal | 04ALL | 1 | 23SP | GEN-2019-066 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28943 | 100.42 | P12:069:WFEC:LAKECRK_ELKCTY::::
Thermal | 04ALL | 1 | 23SP | GEN-2019-066 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.2928 | 100.09 | P12:138:WFEC:MOREWD_REDHILLS::::
Thermal | 04ALL | 1 | 23SP | GEN-2019-066 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28539 | 101.64 | P12:138:WFEC:RUSSELL_LKPAUL::::
Thermal | 04ALL | 1 | 23SP | GEN-2019-066 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28629 | 101.02 | P12:138:WFEC:RUSSELL_ALTUSJCT::::
Thermal | 04ALL | 1 | 23SP | GEN-2019-066 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.30832 | 102.83 | P12:345:OKGE:BKRBKR24::::
Thermal | 04ALL | 1 | 23SP | GEN-2019-066 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28809 | 100 | P12:138:OKGE:BKRBKR83::::
Thermal | 04ALL | 1 | 23SP | GEN-2019-066 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28741 | 100.38 | P12:345:OKGE:BKRBKR336::::
Thermal | 04ALL | 1 | 23SP | GEN-2019-066 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28741 | 100.4 | P12:345:OKGE:BKRBKR336_2::::
Thermal | 04ALL | 1 | 23SP | GEN-2019-066 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28831 | 100.1 | P12:138:OKGE:BKRBKR338::::
Thermal | 04ALL | 1 | 23SP | GEN-2019-066 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28831 | 100.1 | P13:138:OKGE:BKRBKR338_2::::
Thermal | 04ALL | 1 | 23SP | GEN-2019-066 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28789 | 101.29 | P12:345:OKGE:BKRBKR357_2::::
Thermal | 04ALL | 1 | 23SP | GEN-2019-066 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.29648 | 108.16 | P12:345:OKGE-AEPW:BKRBKR366::::
Thermal | 04ALL | 1 | 23SP | GEN-2019-066 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.29648 | 103.85 | P12:345:OKGE-AEPW:BKRBKR366::::
Thermal | 04ALL | 1 | 23SP | GEN-2019-066 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.48719 | 103.55 | P12:345:OKGE-AEPW:BKRBKR371::::
Thermal | 04ALL | 1 | 23SP | GEN-2019-066 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.48719 | 121.08 | P12:345:OKGE-AEPW:BKRBKR371::::
Thermal | 04ALL | 1 | 23SP | GEN-2019-066 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28812 | 101.09 | P12:345:OKGE:BKRBKR400::::
Thermal | 04ALL | 1 | 23SP | GEN-2019-066 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28653 | 100.64 | P12:345:OKGE:BKRBKR4191::::
Thermal | 04ALL | 1 | 23SP | GEN-2019-066 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28665 | 101.09 | P12:345:OKGE:BKRBKR4191::::
Thermal | 04ALL | 1 | 23SP | GEN-2019-066 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28653 | 100.64 | P12:345:OKGE:BKRBKR4192::::
Thermal | 04ALL | 1 | 23SP | GEN-2019-066 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28665 | 101.09 | P12:345:OKGE:BKRBKR4192::::
Thermal | 04ALL | 1 | 23SP | GEN-2019-066 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28695 | 100.46 | P12:345:OKGE:BKRBKR4193::::
Thermal | 04ALL | 1 | 23SP | GEN-2019-066 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28695 | 100.46 | P12:345:OKGE:BKRBKR4194::::
Thermal | 04ALL | 1 | 23SP | GEN-2019-066 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.2867 | 101.4 | P12:345:OKGE-SPS:BKRBKR4201::::
Thermal | 04ALL | 1 | 23SP | GEN-2019-066 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.2867 | 101.4 | P12:345:OKGE-SPS:BKRBKR4202::::
Thermal | 04ALL | 1 | 23SP | GEN-2019-066 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28808 | 101.37 | P12:345:OKGE:BKRBKR421::::
Thermal | 04ALL | 1 | 23SP | GEN-2019-066 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28717 | 100.87 | P12:345:OKGE:BKRBKR604::::
Thermal | 04ALL | 1 | 23SP | GEN-2019-066 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28715 | 101.05 | P12:345:OKGE:BKRBKR604_2::::
Thermal | 04ALL | 1 | 23SP | GEN-2019-066 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28826 | 100.16 | P13:138-345:OKGE:BKRBKR_3W082::::
Thermal | 04ALL | 1 | 23SP | GEN-2019-066 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28773 | 101.03 | P13:138-345:OKGE:BKRBKR_3W083::::
Thermal | 04ALL | 1 | 23SP | GEN-2019-066 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28668 | 102.01 | P42:345:OKGE:SB_ARIA7381::::
Thermal | 04ALL | 1 | 23SP | GEN-2019-066 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28617 | 101.63 | P42:345:OKGE:SB_BVTY7387::::
Thermal | 04ALL | 1 | 23SP | GEN-2019-066 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28821 | 101.5 | P41:345:OKGE:SB_REUD7381::::
Thermal | 04ALL | 1 | 23SP | GEN-2019-066 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28814 | 101.52 | P41:345:OKGE:SB_REUD7383::::
Thermal | 04ALL | 1 | 23SP | GEN-2019-066 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28817 | 102.12 | P41:345:OKGE:SB_REUD7385::::
Thermal | 04ALL | 1 | 23SP | GEN-2019-066 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28853 | 100.52 | P42:345:OKGE:SB_REUD7389::::
Thermal | 04ALL | 1 | 23SP | GEN-2019-066 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28679 | 100.06 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV:
Thermal | 04ALL | 1 | 23SP | GEN-2019-066 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28742 | 101.52 | P13:115:SUNC:HOLCOMB_GSU:::HV:
Thermal | 04ALL | 1 | 23SP | GEN-2019-066 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28678 | 100.14 | P23:345:SUNC:BU_BRK488:::EHV:
Thermal | 04ALL | 1 | 23SP | GEN-2019-066 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28679 | 100.06 | P23:345:SUNC:BU_BRK482:::EHV:
Thermal | 04ALL | 1 | 23SP | GEN-2019-066 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28744 | 100 | P12:HV-EHV:EES::8W.MEMPHIS%:8FREEPORTTN%:4BHAM STEEL:1
Thermal | 04ALL | 1 | 23SP | GEN-2019-066 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28748 | 100.1 | P12:EHV:EES::CHAMSPR7!:CLARKSV7!:1
Thermal | 04ALL | 1 | 23SP | GEN-2019-066 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28742 | 100.22 | P11:345:MEC-NPPD:COOPER 1
Thermal | 04ALL | 1 | 23SP | GEN-2019-066 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28742 | 100.09 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3
Thermal | 04ALL | 1 | 23SP | GEN-2019-066 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28742 | 100.2 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4
Thermal | 04ALL | 1 | 23SP | GEN-2019-066 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28742 | 100.06 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4
Thermal | 04ALL | 1 | 23SP | GEN-2019-066 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28742 | 100.05 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1
Thermal | 04ALL | 1 | 23SP | GEN-2019-066 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28742 | 100.13 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1
Thermal | 04ALL | 1 | 23SP | GEN-2019-066 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28742 | 100.03 | P13:345-24:MEC:AUTO-SINGLE:RAUN3:NEAL4G:1
Thermal | 04ALL | 1 | 23SP | GEN-2019-066 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28744 | 100.16 | P12:345:WERE:BENT-ROSE_345::
Thermal | 04ALL | 1 | 23SP | GEN-2019-066 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28757 | 100.29 | P12:345:WERE:N345-PSO_345::
Thermal | 04ALL | 1 | 23SP | GEN-2019-066 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28768 | 100.31 | P12:345:WERE:VIOL-WICH_345::
Thermal | 04ALL | 1 | 23SP | GEN-2019-066 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.29712 | 100.65 | 511446 CL-AFTP4 138 511458 ELKCTY-4 138 1
Thermal | 04ALL | 1 | 23SP | GEN-2019-066 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.29712 | 100.49 | 511446 CL-AFTP4 138 511463 HOB-JCT4 138 1
Thermal | 04ALL | 1 | 23SP | GEN-2019-066 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28769 | 102.08 | 511456 O.K.U.-7 345 763215 G18-092-TAP 345 1
Thermal | 04ALL | 1 | 23SP | GEN-2019-066 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28943 | 100.37 | 511459 ELKCTY-2 69.0 520897 ELKCITY2 69.0 1
Thermal | 04ALL | 1 | 23SP | GEN-2019-066 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28876 | 100.85 | 511463 HOB-JCT4 138 511564 MARTHA 4 138 1
Thermal | 04ALL | 1 | 23SP | GEN-2019-066 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.2877 | 102.67 | 511468 L.E.S.-7 345 762467 G18-015-TAP 345 1
Thermal | 04ALL | 1 | 23SP | GEN-2019-066 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28761 | 101.52 | 511468 L.E.S.-7 345 763215 G18-092-TAP 345 2
Thermal | 04ALL | 1 | 23SP | GEN-2019-066 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.29049 | 100.38 | 511485 CLINTJC4 138 511534 CL-NGTP4 138 1
Thermal | 04ALL | 1 | 23SP | GEN-2019-066 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.29049 | 100.11 | 511506 WTH WF 4 138 511534 CL-NGTP4 138 1
Thermal | 04ALL | 1 | 23SP | GEN-2019-066 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.29048 | 100.18 | 511506 WTH WF 4 138 511536 WEATHTP4 138 1
Thermal | 04ALL | 1 | 23SP | GEN-2019-066 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.48719 | 103.55 | 511557 CHISHOLM6 230 3WXFMR CHISHOLM6 1
Thermal | 04ALL | 1 | 23SP | GEN-2019-066 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28876 | 100.76 | 511564 MARTHA 4 138 529302 OMALTUS4 138 1
Thermal | 04ALL | 1 | 23SP | GEN-2019-066 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28658 | 100.14 | 512093 MEMPHIS2 69.0 512094 REDRIVR2 69.0 1
Thermal | 04ALL | 1 | 23SP | GEN-2019-066 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28658 | 100.17 | 512094 REDRIVR2 69.0 512095 ESTELNE2 69.0 1
Thermal | 04ALL | 1 | 23SP | GEN-2019-066 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28658 | 100.24 | 512095 ESTELNE2 69.0 512096 CAREY 2 69.0 1
Thermal | 04ALL | 1 | 23SP | GEN-2019-066 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28658 | 100.26 | 512096 CAREY 2 69.0 512097 AIRPORT2 69.0 1
Thermal | 04ALL | 1 | 23SP | GEN-2019-066 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28658 | 100.29 | 512097 AIRPORT2 69.0 512098 AMOCOTP2 69.0 1
Thermal | 04ALL | 1 | 23SP | GEN-2019-066 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28658 | 100.48 | 512098 AMOCOTP2 69.0 512100 CHLDR2WT 69.0 1
Thermal | 04ALL | 1 | 23SP | GEN-2019-066 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28482 | 100.83 | 512101 CHILD4WT 138 512103 HOLTP4WT 138 1
Thermal | 04ALL | 1 | 23SP | GEN-2019-066 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28482 | 100.36 | 512103 HOLTP4WT 138 512104 WELL 4WT 138 1
Thermal | 04ALL | 1 | 23SP | GEN-2019-066 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28617 | 101.59 | 515375 WWRDEHV7 345 515458 BORDER 7 345 1
Thermal | 04ALL | 1 | 23SP | GEN-2019-066 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28742 | 100.86 | 515375 WWRDEHV7 345 562024 G11-019-SUB 345 1
Thermal | 04ALL | 1 | 23SP | GEN-2019-066 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28742 | 100.31 | 515375 WWRDEHV7 345 763527 GEN-2019-012 345 1
Thermal | 04ALL | 1 | 23SP | GEN-2019-066 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28617 | 101.63 | 515458 BORDER 7 345 560022 CRAWFISH_DR 345 1
Thermal | 04ALL | 1 | 23SP | GEN-2019-066 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28812 | 101.67 | 515543 RENFROW7 345 763421 G18-128-TAP 345 1
Thermal | 04ALL | 1 | 23SP | GEN-2019-066 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.2873 | 100.16 | 515618 BALKOW 7 345 3WXFMR BALKOW 7 1
Thermal | 04ALL | 1 | 23SP | GEN-2019-066 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.2873 | 100.16 | 515618 BALKOW 7 345 3WXFMR BALKOW 7 1_Dup1
Thermal | 04ALL | 1 | 23SP | GEN-2019-066 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28789 | 102.2 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Thermal | 04ALL | 1 | 23SP | GEN-2019-066 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28715 | 101.03 | 515634 PALDR1W7 345 3WXFMR PALO2 _1 1
Thermal | 04ALL | 1 | 23SP | GEN-2019-066 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28943 | 100.03 | 520876 DILL JT2 69.0 520897 ELKCITY2 69.0 1
Thermal | 04ALL | 1 | 23SP | GEN-2019-066 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28673 | 100.46 | 523093 HITCHLAND 3 115 523160 FRISCO_WND 3 115 1
Thermal | 04ALL | 1 | 23SP | GEN-2019-066 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28713 | 101.24 | 523093 HITCHLAND 3 115 523174 GOODWELLWND3 115 1
Thermal | 04ALL | 1 | 23SP | GEN-2019-066 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28714 | 100.29 | 523095 HITCHLAND 6 230 523155 OCHILTREE 6 230 1
Thermal | 04ALL | 1 | 23SP | GEN-2019-066 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28428 | 102.22 | 523095 HITCHLAND 6 230 523309 MOORE_CNTY 6 230 1
Thermal | 04ALL | 1 | 23SP | GEN-2019-066 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28681 | 100.29 | 523097 HITCHLAND 7 345 3WXFMR H TB80155502 1
Thermal | 04ALL | 1 | 23SP | GEN-2019-066 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28663 | 100.54 | 523097 HITCHLAND 7 345 3WXFMR SIEM 8743067 2
Thermal | 04ALL | 1 | 23SP | GEN-2019-066 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.27687 | 104.8 | 523097 HITCHLAND 7 345 523961 POTTER_CO 7 345 1
Thermal | 04ALL | 1 | 23SP | GEN-2019-066 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28714 | 100.25 | 523155 OCHILTREE 6 230 3WXFMR H TP80219401 1
Thermal | 04ALL | 1 | 23SP | GEN-2019-066 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28673 | 100.46 | 523160 FRISCO_WND 3 115 523175 LASLEY 3 115 1
Thermal | 04ALL | 1 | 23SP | GEN-2019-066 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28728 | 100.33 | 523172 GWELL_COLL11 34.5 523174 GOODWELLWND3 115 1
Thermal | 04ALL | 1 | 23SP | GEN-2019-066 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28727 | 100.37 | 523173 GWELL_COLL21 34.5 523174 GOODWELLWND3 115 1
Thermal | 04ALL | 1 | 23SP | GEN-2019-066 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28725 | 100.47 | 523309 MOORE_CNTY 6 230 3WXFMR ENRCO 136402 1
Thermal | 04ALL | 1 | 23SP | GEN-2019-066 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28742 | 103.88 | 523344 BLKHAWK_W 3 115 523461 BLACKHAWK1 1 13.8 1
Thermal | 04ALL | 1 | 23SP | GEN-2019-066 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28742 | 104.3 | 523346 BLKHAWK_E 3 115 523462 BLACKHAWK2 1 13.8 1
Thermal | 04ALL | 1 | 23SP | GEN-2019-066 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28501 | 100.3 | 523546 HUTCH_S 3 115 523636 GRAY_CNTY 3 115 1
Thermal | 04ALL | 1 | 23SP | GEN-2019-066 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28501 | 100.3 | 523636 GRAY_CNTY 3 115 3WXFMR WH RHP17221 1
Thermal | 04ALL | 1 | 23SP | GEN-2019-066 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28742 | 100.22 | 523853 FINNEY 7 345 762662 G18-030-TAP 345 1
Thermal | 04ALL | 1 | 23SP | GEN-2019-066 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28705 | 101.73 | 523926 MAJESTC_WND3 115 523928 MARTIN 3 115 1
Thermal | 04ALL | 1 | 23SP | GEN-2019-066 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28725 | 100.53 | 523926 MAJESTC_WND3 115 523947 MAJESTC-LV11 34.5 1
Thermal | 04ALL | 1 | 23SP | GEN-2019-066 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28723 | 100.65 | 523926 MAJESTC_WND3 115 523948 MAJESTC-LV21 34.5 1
Thermal | 04ALL | 1 | 23SP | GEN-2019-066 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.27658 | 106.23 | 523961 POTTER_CO 7 345 3WXFMR WAUK 90343-A 1
Thermal | 04ALL | 1 | 23SP | GEN-2019-066 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28715 | 101.2 | 523961 POTTER_CO 7 345 524296 SPNSPUR_WND7 345 1
Thermal | 04ALL | 1 | 23SP | GEN-2019-066 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28661 | 111.3 | 523977 HARRNG_WST 6 230 523971 HARRNGTON1 1 24.0 1
Thermal | 04ALL | 1 | 23SP | GEN-2019-066 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28654 | 111.89 | 523978 HARRNG_MID 6 230 523972 HARRNGTON2 1 24.0 1
Thermal | 04ALL | 1 | 23SP | GEN-2019-066 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28452 | 100.05 | 523978 HARRNG_MID 6 230 523979 HARRNG_EST 6 230 @1
Thermal | 04ALL | 1 | 23SP | GEN-2019-066 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28657 | 111.39 | 523979 HARRNG_EST 6 230 523973 HARRNGTON3 1 24.0 1
Thermal | 04ALL | 1 | 23SP | GEN-2019-066 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28691 | 103.26 | 524043 NICHOLS 3 115 524022 NICHOLS_2 1 13.8 1
Thermal | 04ALL | 1 | 23SP | GEN-2019-066 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28613 | 108.11 | 524044 NICHOLS 6 230 524023 NICHOLS_3 1 22.0 1
Thermal | 04ALL | 1 | 23SP | GEN-2019-066 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28704 | 101.86 | 524267 BUSHLAND 6 230 524290 WILDOR2_JUS6 230 1
Thermal | 04ALL | 1 | 23SP | GEN-2019-066 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.2872 | 100.89 | 524275 WILDOR_WND 1 34.5 524276 WILDOR_WND 6 230 1
Thermal | 04ALL | 1 | 23SP | GEN-2019-066 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.2872 | 100.89 | 524276 WILDOR_WND 6 230 524290 WILDOR2_JUS6 230 1
Thermal | 04ALL | 1 | 23SP | GEN-2019-066 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28727 | 100.43 | 524289 GS-PHWDRNCH1 34.5 524290 WILDOR2_JUS6 230 1
Thermal | 04ALL | 1 | 23SP | GEN-2019-066 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28715 | 101.18 | 524296 SPNSPUR_WND7 345 524299 SPNSPUR_COL7 345 1
Thermal | 04ALL | 1 | 23SP | GEN-2019-066 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28715 | 101.18 | 524299 SPNSPUR_COL7 345 3WXFMR SPNSPUR_COL7 1
Thermal | 04ALL | 1 | 23SP | GEN-2019-066 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28741 | 100.5 | 524909 ROOSEVELT 6 230 525531 TOLK 6 230 2
Thermal | 04ALL | 1 | 23SP | GEN-2019-066 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28742 | 101.72 | 524909 ROOSEVELT 6 230 763483 GEN-2019-003 230 1
Thermal | 04ALL | 1 | 23SP | GEN-2019-066 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28542 | 100.53 | 525213 SWISHER 6 230 525830 TUCO_INT 6 230 1
Thermal | 04ALL | 1 | 23SP | GEN-2019-066 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28742 | 100.68 | 525461 NEWHART 6 230 763186 GEN-2018-089 230 1
Thermal | 04ALL | 1 | 23SP | GEN-2019-066 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28726 | 101.39 | 525480 PLANT_X 3 115 525493 PLANT_X3 1 13.8 1
Thermal | 04ALL | 1 | 23SP | GEN-2019-066 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28703 | 103.31 | 525481 PLANT_X 6 230 525494 PLANT_X4 1 20.0 1
Thermal | 04ALL | 1 | 23SP | GEN-2019-066 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28742 | 101.36 | 525481 PLANT_X 6 230 763120 GEN-2018-081 230 1
Thermal | 04ALL | 1 | 23SP | GEN-2019-066 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28668 | 108.78 | 525531 TOLK 6 230 525561 TOLK_1 1 24.0 1
Thermal | 04ALL | 1 | 23SP | GEN-2019-066 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28649 | 110.16 | 525531 TOLK 6 230 525562 TOLK_2 1 24.0 1
Thermal | 04ALL | 1 | 23SP | GEN-2019-066 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28737 | 100.48 | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1
Thermal | 04ALL | 1 | 23SP | GEN-2019-066 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28742 | 101.03 | 525531 TOLK 6 230 762132 GEN-2017-158 230 1
Thermal | 04ALL | 1 | 23SP | GEN-2019-066 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28742 | 104.61 | 525531 TOLK 6 230 763241 GEN-2018-097 230 1
Thermal | 04ALL | 1 | 23SP | GEN-2019-066 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28742 | 101.05 | 525830 TUCO_INT 6 230 525840 ANTELOPE_1 6 230 1
Thermal | 04ALL | 1 | 23SP | GEN-2019-066 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28727 | 100.51 | 525830 TUCO_INT 6 230 525957 HALE_WNDCL16 230 1
Thermal | 04ALL | 1 | 23SP | GEN-2019-066 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28744 | 100.4 | 525830 TUCO_INT 6 230 526161 CARLISLE 6 230 1
Thermal | 04ALL | 1 | 23SP | GEN-2019-066 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.2872 | 101.73 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2
Thermal | 04ALL | 1 | 23SP | GEN-2019-066 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28714 | 102.37 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _9 1
Thermal | 04ALL | 1 | 23SP | GEN-2019-066 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28716 | 103.84 | 525832 TUCO_INT 7 345 525850 ELK_CT1 345 1
Thermal | 04ALL | 1 | 23SP | GEN-2019-066 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28753 | 107.62 | 525832 TUCO_INT 7 345 526936 YOAKUM_345 345 1
Thermal | 04ALL | 1 | 23SP | GEN-2019-066 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28729 | 101.63 | 525850 ELK_CT1 345 525844 ELK_1 1 18.0 1
Thermal | 04ALL | 1 | 23SP | GEN-2019-066 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28729 | 101.63 | 525850 ELK_CT1 345 525845 ELK_2 1 18.0 1
Thermal | 04ALL | 1 | 23SP | GEN-2019-066 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28732 | 100.37 | 526012 LOST_DRAW 3 115 584560 GEN-2015-014 115 1
Thermal | 04ALL | 1 | 23SP | GEN-2019-066 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.287 | 103.21 | 526337 JONES 6 230 526331 JONES_1 1 22.0 1
Thermal | 04ALL | 1 | 23SP | GEN-2019-066 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.287 | 103.21 | 526337 JONES 6 230 526332 JONES_2 1 22.0 1
Thermal | 04ALL | 1 | 23SP | GEN-2019-066 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.2874 | 100.67 | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1
Thermal | 04ALL | 1 | 23SP | GEN-2019-066 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28744 | 101.96 | 526936 YOAKUM_345 345 527896 HOBBS_INT 7 345 1
Thermal | 04ALL | 1 | 23SP | GEN-2019-066 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28734 | 102.29 | 527146 MUSTANG 3 115 527161 MUSTANG_1 1 18.0 1
Thermal | 04ALL | 1 | 23SP | GEN-2019-066 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28731 | 102.28 | 527146 MUSTANG 3 115 527162 MUSTANG_2 1 18.0 1
Thermal | 04ALL | 1 | 23SP | GEN-2019-066 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28722 | 105.17 | 527149 MUSTANG 6 230 527151 GS-MUSTANG 6 230 @1
Thermal | 04ALL | 1 | 23SP | GEN-2019-066 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28719 | 102.36 | 527149 MUSTANG 6 230 527163 MUSTANG_3 1 19.0 1
Thermal | 04ALL | 1 | 23SP | GEN-2019-066 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28733 | 102.18 | 527151 GS-MUSTANG 6 230 527165 MUSTANG_5 1 18.0 1
Thermal | 04ALL | 1 | 23SP | GEN-2019-066 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28731 | 102.39 | 527151 GS-MUSTANG 6 230 527166 MUSTANG_6 1 18.0 1
Thermal | 04ALL | 1 | 23SP | GEN-2019-066 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28734 | 100.05 | 527455 RSWL_SLRCOL3 115 527454 RSWL_SOLAR11 34.5 1
Thermal | 04ALL | 1 | 23SP | GEN-2019-066 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28734 | 100.05 | 527455 RSWL_SLRCOL3 115 527482 CHAVES_CNTY3 115 1
Thermal | 04ALL | 1 | 23SP | GEN-2019-066 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28733 | 100.06 | 527654 RSVLT_CC_W 7 345 527655 RSVLT_CC_E 7 345 1
Thermal | 04ALL | 1 | 23SP | GEN-2019-066 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28733 | 100.06 | 527654 RSVLT_CC_W 7 345 527666 RSVLT_COL1 7 345 1
Thermal | 04ALL | 1 | 23SP | GEN-2019-066 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28729 | 100.36 | 527655 RSVLT_CC_E 7 345 527656 CROSSROADS 7 345 1
Thermal | 04ALL | 1 | 23SP | GEN-2019-066 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28733 | 100.06 | 527666 RSVLT_COL1 7 345 3WXFMR RSVLT_COL1 7 1
Thermal | 04ALL | 1 | 23SP | GEN-2019-066 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28713 | 102.89 | 527867 CUNNIGHM_S 6 230 527882 CUNINGHAM2 1 20.0 1
Thermal | 04ALL | 1 | 23SP | GEN-2019-066 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28729 | 102.15 | 527891 HOBBS_INT 3 115 527901 HOBBS_PLT1 1 18.0 1
Thermal | 04ALL | 1 | 23SP | GEN-2019-066 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28729 | 102.16 | 527891 HOBBS_INT 3 115 527902 HOBBS_PLT2 1 18.0 1
Thermal | 04ALL | 1 | 23SP | GEN-2019-066 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28721 | 103.99 | 527894 HOBBS_INT 6 230 527903 HOBBS_PLT3 1 18.0 1
Thermal | 04ALL | 1 | 23SP | GEN-2019-066 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28724 | 101.56 | 528355 MADDOX 3 115 528361 MADDOX_1 1 13.8 1
Thermal | 04ALL | 1 | 23SP | GEN-2019-066 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28876 | 100.14 | 529298 OMPVET-4 138 529302 OMALTUS4 138 1
Thermal | 04ALL | 1 | 23SP | GEN-2019-066 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28789 | 103.16 | 532794 ROSEHIL7 345 560053 G15052_T 345 1
Thermal | 04ALL | 1 | 23SP | GEN-2019-066 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28812 | 101.82 | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1
Thermal | 04ALL | 1 | 23SP | GEN-2019-066 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28722 | 100.04 | 539659 CUDAHY 3 115 539783 CRKCK 3 115 1
Thermal | 04ALL | 1 | 23SP | GEN-2019-066 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28764 | 102.28 | 560022 CRAWFISH_DR 345 762216 G17-151TAP 345 1
Thermal | 04ALL | 1 | 23SP | GEN-2019-066 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28761 | 102.13 | 560022 CRAWFISH_DR 345 762467 G18-015-TAP 345 1
Thermal | 04ALL | 1 | 23SP | GEN-2019-066 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28742 | 101.63 | 560022 CRAWFISH_DR 345 763087 GEN-2018-073 345 1
Thermal | 04ALL | 1 | 23SP | GEN-2019-066 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28771 | 103.54 | 560022 CRAWFISH_DR 345 763215 G18-092-TAP 345 2
Thermal | 04ALL | 1 | 23SP | GEN-2019-066 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28742 | 100.33 | 560071 G16-003-TAP 345 587020 GEN-2016-003 345 1
Thermal | 04ALL | 1 | 23SP | GEN-2019-066 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28742 | 100.14 | 562021 G11-020-SUB 345 562024 G11-019-SUB 345 1
Thermal | 04ALL | 1 | 23SP | GEN-2019-066 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28742 | 100.13 | 562022 G11-020-GSU 34.5 562021 G11-020-SUB 345 1
Thermal | 04ALL | 1 | 23SP | GEN-2019-066 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28742 | 100.17 | 562025 G11-019-GSU 34.5 562024 G11-019-SUB 345 1
Thermal | 04ALL | 1 | 23SP | GEN-2019-066 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28876 | 100.79 | P12:138:AEPW-OMPA:HOB-JCT4:OMALTUS4
Thermal | 04ALL | 1 | 23SP | GEN-2019-066 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28629 | 101.02 | P12:138:AEPW-WFEC:ALTUSJT4:RUSSELL4
Thermal | 04ALL | 1 | 23SP | GEN-2019-066 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28539 | 101.64 | P12:138:AEPW-WFEC:LAKEP4WT:RUSSELL4
Thermal | 04ALL | 1 | 23SP | GEN-2019-066 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28732 | 100.37 | 584560 GEN-2015-014 115 584561 G15-014XFMR1 34.5 1
Thermal | 04ALL | 1 | 23SP | GEN-2019-066 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28742 | 100.33 | 587021 G16-003XFMR1 34.5 587020 GEN-2016-003 345 1
Thermal | 04ALL | 1 | 23SP | GEN-2019-066 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28269 | 102.89 | P12:138:AEPW:CHILD4WT:LAKEP4WT
Thermal | 04ALL | 1 | 23SP | GEN-2019-066 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.29826 | 102.68 | P12:138:AEPW:ELKCTY-4:CLINTJC4
Thermal | 04ALL | 1 | 23SP | GEN-2019-066 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.29712 | 100.66 | P12:138:AEPW:HOB-JCT4:ELKCTY-4
Thermal | 04ALL | 1 | 23SP | GEN-2019-066 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.29049 | 100.54 | P12:138:AEPW:WTHWF4:CLINTJC4
Thermal | 04ALL | 1 | 23SP | GEN-2019-066 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.29048 | 100.33 | P12:138:AEPW:WTHWF4:WTH_SE4
Thermal | 04ALL | 1 | 23SP | GEN-2019-066 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28805 | 100.43 | P12:138:WFEC-AEPW:ELKCTY-4:ERICK4
Thermal | 04ALL | 1 | 23SP | GEN-2019-066 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.29648 | 108.16 | P12:345:AEPW-OKGE:L.E.S.-7:GRACMNT7
Thermal | 04ALL | 1 | 23SP | GEN-2019-066 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.29648 | 103.85 | P12:345:AEPW-OKGE:L.E.S.-7:GRACMNT7
Thermal | 04ALL | 1 | 23SP | GEN-2019-066 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28757 | 100.29 | P12:345:AEPW-WERE:DELWARE7:NEOSHO7
Thermal | 04ALL | 1 | 23SP | GEN-2019-066 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28757 | 100.29 | 6111_Dup1
Thermal | 04ALL | 1 | 23SP | GEN-2019-066 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28758 | 100.39 | P12:345:AEPW:DELWARE7:N.E.S.-7
Thermal | 04ALL | 1 | 23SP | GEN-2019-066 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28769 | 102.13 | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Thermal | 04ALL | 1 | 23SP | GEN-2019-066 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28658 | 100.04 | P12:69:AEPW:CHLDR2WT:MEMPHIS2
Thermal | 04ALL | 1 | 23SP | GEN-2019-066 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28943 | 100.42 | P12:69:WFEC-AEPW:LKCREEK2:ELKCTY-2
Thermal | 04ALL | 1 | 23SP | GEN-2019-066 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.35177 | 113.78 | P13:138-230:AEPW:ELKCTY-4
Thermal | 04ALL | 1 | 23SP | GEN-2019-066 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28749 | 100.3 | P23:500:EES-EAI:KEO:B4941
Thermal | 04ALL | 1 | 23SP | GEN-2019-066 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28749 | 100.56 | P23:500:EES-EAI:KEO:B4941
Thermal | 04ALL | 1 | 23SP | GEN-2019-066 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28748 | 100.18 | P23:500:EES-EAI:KEO:B4921
Thermal | 04ALL | 1 | 23SP | GEN-2019-066 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28744 | 100 | P12:500:EES-EAI:WMPEHV:BHMSTL:BHMSTL:NEWPORT
Thermal | 04ALL | 1 | 23SP | GEN-2019-066 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28658 | 100.7 | P13:69-138:AEPW:CHLDR2WT
Thermal | 04ALL | 1 | 23SP | GEN-2019-066 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28943 | 100.57 | P13:69-138:AEPW:ELKCTY-2
Thermal | 04ALL | 1 | 23SP | GEN-2019-066 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28745 | 100.12 | P23:500:EAI-TVA:NBF_WEST M~1
Thermal | 04ALL | 1 | 23SP | GEN-2019-066 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28742 | 100.13 | P23:345:MEC:CBEC 905
Thermal | 04ALL | 1 | 23SP | GEN-2019-066 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28742 | 100.05 | P23:345:MEC:CBEC 908
Thermal | 04ALL | 1 | 23SP | GEN-2019-066 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28742 | 100.03 | P23:345:MEC:RAUN 0210
Thermal | 04ALL | 1 | 23SP | GEN-2019-066 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28742 | 100.24 | 762132 GEN-2017-158 230 763252 G18-099-XFM1 34.5 1
Thermal | 04ALL | 1 | 23SP | GEN-2019-066 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28742 | 100.24 | 762132 GEN-2017-158 230 763255 G18-099-XFM2 34.5 1
Thermal | 04ALL | 1 | 23SP | GEN-2019-066 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28764 | 102.43 | 762216 G17-151TAP 345 762467 G18-015-TAP 345 1
Thermal | 04ALL | 1 | 23SP | GEN-2019-066 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28754 | 101.37 | 762467 G18-015-TAP 345 763215 G18-092-TAP 345 1
Thermal | 04ALL | 1 | 23SP | GEN-2019-066 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28742 | 100.89 | 763087 GEN-2018-073 345 763088 G18-073-XFM1 34.5 1
Thermal | 04ALL | 1 | 23SP | GEN-2019-066 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28742 | 100.18 | 763087 GEN-2018-073 345 763091 G18-073-XFM2 34.5 1
Thermal | 04ALL | 1 | 23SP | GEN-2019-066 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28742 | 101.36 | 763120 GEN-2018-081 230 763121 G18-081-XFM1 34.5 1
Thermal | 04ALL | 1 | 23SP | GEN-2019-066 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28742 | 100.68 | 763186 GEN-2018-089 230 763187 G18-089-XFM1 34.5 1
Thermal | 04ALL | 1 | 23SP | GEN-2019-066 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28742 | 100.1 | 763208 GEN-2018-092 345 763215 G18-092-TAP 345 1
Thermal | 04ALL | 1 | 23SP | GEN-2019-066 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28742 | 100.5 | 763241 GEN-2018-097 230 763242 G18-097-XFM1 34.5 1
Thermal | 04ALL | 1 | 23SP | GEN-2019-066 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28742 | 100.42 | 763241 GEN-2018-097 230 763307 G18-112-XFM1 34.5 1
Thermal | 04ALL | 1 | 23SP | GEN-2019-066 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28742 | 100.42 | 763241 GEN-2018-097 230 763310 G18-112-XFM2 34.5 1
Thermal | 04ALL | 1 | 23SP | GEN-2019-066 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28742 | 100.5 | 763241 GEN-2018-097 230 763395 G18-124-XFM1 34.5 1
Thermal | 04ALL | 1 | 23SP | GEN-2019-066 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28742 | 100.5 | 763241 GEN-2018-097 230 763398 G18-124-XFM2 34.5 1
Thermal | 04ALL | 1 | 23SP | GEN-2019-066 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28742 | 101.15 | 763483 GEN-2019-003 230 763484 G19-003-XFM1 34.5 1
Thermal | 04ALL | 1 | 23SP | GEN-2019-066 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28742 | 100.02 | 763483 GEN-2019-003 230 763605 G19-021-XFM1 34.5 1
Thermal | 04ALL | 1 | 23SP | GEN-2019-066 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28742 | 100.31 | 763527 GEN-2019-012 345 763528 G19-012-XFM1 34.5 1
Thermal | 04ALL | 1 | 23SP | GEN-2019-066 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28665 | 102.2 | P42:345:OKGE:SB_BVTY7305
Thermal | 04ALL | 1 | 23SP | GEN-2019-066 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28744 | 100.11 | P23:345:WERE:BENT_345-50::
Thermal | 04ALL | 1 | 23SP | GEN-2019-066 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28743 | 100.3 | P23:345:WERE:ROSE_345-80::
Thermal | 04ALL | 1 | 23SP | GEN-2019-066 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28762 | 100.14 | P23:345:WERE:WICH_345-116::
Thermal | 04ALL | 1 | 23SP | GEN-2019-066 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28741 | 100.1 | P23:345:WERE:WICH_345-50::
Thermal | 04ALL | 1 | 23SP | GEN-2019-066 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28748 | 100.1 | P43:345:AEPW:CHAMBERS SPRING CB 12720 NBTB+FAULT
Thermal | 04ALL | 1 | 23SP | GEN-2019-066 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28748 | 100.1 | P42:345:AEPW:CHAMBERS SPRING CB 13720 NBTB+FAULT
Thermal | 04ALL | 1 | 23SP | GEN-2019-066 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28748 | 100.1 | P42:345:AEPW:CHAMBERS SPRING CB 13850 NBTB+FAULT
Thermal | 04ALL | 1 | 23SP | GEN-2019-066 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28769 | 102.1 | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Thermal | 04ALL | 1 | 23SP | GEN-2019-066 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.29694 | 107.94 | P42:345:AEPW:LAWTON EASTSIDE CB 3413A NBTB+FAULT
Thermal | 04ALL | 1 | 23SP | GEN-2019-066 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.29744 | 107.73 | P42:345:AEPW:LAWTON EASTSIDE CB 3425A NBTB+FAULT
Thermal | 04ALL | 1 | 23SP | GEN-2019-066 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28775 | 101.8 | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Thermal | 04ALL | 1 | 23SP | GEN-2019-066 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28758 | 100.39 | P42:345:AEPW:NES CB 3445A NBTB+FAULT
Thermal | 04ALL | 1 | 23SP | GEN-2019-066 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28759 | 100.41 | P42:345:AEPW:DELAWARE CB 3401A NBTB+FAULT
Thermal | 04ALL | 1 | 23SP | GEN-2019-066 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28759 | 100.41 | P42:345:AEPW:DELAWARE CB 3405A NBTB+FAULT
Thermal | 04ALL | 1 | 23SP | GEN-2019-066 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28759 | 100.41 | P42:345:AEPW:DELAWARE CB 3409A NBTB+FAULT
Thermal | 04ALL | 1 | 23SP | GEN-2019-066 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28748 | 100.1 | P23:345:AEPW:CHAMBERS SPRING CB 12720 NBTB
Thermal | 04ALL | 1 | 23SP | GEN-2019-066 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28748 | 100.1 | P23:345:AEPW:CHAMBERS SPRING CB 13720 NBTB
Thermal | 04ALL | 1 | 23SP | GEN-2019-066 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28748 | 100.1 | P23:345:AEPW:CHAMBERS SPRING CB 13850 NBTB
Thermal | 04ALL | 1 | 23SP | GEN-2019-066 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28769 | 102.08 | P23:345:AEPW:OKLAUNION CB 3401A NBTB
Thermal | 04ALL | 1 | 23SP | GEN-2019-066 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.29694 | 107.94 | P23:345:AEPW:LAWTON EASTSIDE CB 3413A NBTB
Thermal | 04ALL | 1 | 23SP | GEN-2019-066 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.29744 | 107.73 | P23:345:AEPW:LAWTON EASTSIDE CB 3425A NBTB
Thermal | 04ALL | 1 | 23SP | GEN-2019-066 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28775 | 101.8 | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Thermal | 04ALL | 1 | 23SP | GEN-2019-066 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28758 | 100.39 | P23:345:AEPW:NES CB 3441A NBTB
Thermal | 04ALL | 1 | 23SP | GEN-2019-066 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28759 | 100.41 | P23:345:AEPW:DELAWARE CB 3401A NBTB
Thermal | 04ALL | 1 | 23SP | GEN-2019-066 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28759 | 100.41 | P23:345:AEPW:DELAWARE CB 3405A NBTB
Thermal | 04ALL | 1 | 23SP | GEN-2019-066 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28759 | 100.41 | P23:345:AEPW:DELAWARE CB 3409A NBTB
Thermal | 04ALL | 1 | 23SP | GEN-2019-066 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28742 | 100.03 | P11:115:SUNC:GARDENCITY_S2:97:531459(2)
Thermal | 04ALL | 1 | 23SP | GEN-2019-066 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28868 | 101.87 | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Thermal | 04ALL | 1 | 23SP | GEN-2019-066 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28868 | 101.87 | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Thermal | 04ALL | 1 | 23SP | GEN-2019-066 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.2767 | 128.54 | P42:345:OKGE:SB_BVTY7315_PRE19S
Thermal | 04ALL | 1 | 23SP | GEN-2019-066 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.35177 | 113.77 | P12:230:AEPW:ELKCITY6:CHISHOLM6
Thermal | 04ALL | 1 | 23SP | GEN-2019-066 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 1 | 164.31 | P12:230:AEPW:SWEETWT6:CHISHOLM6
Thermal | 04ALL | 1 | 26L | GEN-2019-066 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.20852 | 105.7 | P42:345:SPS:YOAKUM:J18####:SLG1:EHV:
Thermal | 04ALL | 1 | 26L | GEN-2019-066 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.20852 | 105.7 | P43:345:SPS:YOAKUM:TF#####:SLG:EHV:
Thermal | 04ALL | 1 | 26L | GEN-2019-066 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.20852 | 105.7 | P42:345:SPS:YOAKUM:J17####:SLG:EHV:
Thermal | 04ALL | 1 | 26L | GEN-2019-066 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.20852 | 105.37 | P43:345:SPS:TUCO:SLG::EHV:
Thermal | 04ALL | 1 | 26L | GEN-2019-066 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.20852 | 105.7 | P42:345:SPS:YOAKUM:J18####:SLG2:EHV:
Thermal | 04ALL | 1 | 26L | GEN-2019-066 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.20869 | 105.39 | P12:345:OKGE-AEPW:BKRBKR366::::
Thermal | 04ALL | 1 | 26L | GEN-2019-066 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.20869 | 100.58 | P12:345:OKGE-AEPW:BKRBKR366::::
Thermal | 04ALL | 1 | 26L | GEN-2019-066 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.21802 | 115.9 | P42:345:OKGE:SB_BVTY7387::::
Thermal | 04ALL | 1 | 26L | GEN-2019-066 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.27984 | 103.81 | 511553 CHISHOLM7 345 755000 WWDBORDT 345 1
Thermal | 04ALL | 1 | 26L | GEN-2019-066 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.21802 | 115.94 | 515458 BORDER 7 345 560022 CRAWFISH_DR 345 1
Thermal | 04ALL | 1 | 26L | GEN-2019-066 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.21802 | 115.83 | 515458 BORDER 7 345 755000 WWDBORDT 345 1
Thermal | 04ALL | 1 | 26L | GEN-2019-066 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.20503 | 100.31 | 523095 HITCHLAND 6 230 523309 MOORE_CNTY 6 230 1
Thermal | 04ALL | 1 | 26L | GEN-2019-066 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.20852 | 105.37 | 525832 TUCO_INT 7 345 526936 YOAKUM_345 345 1
Thermal | 04ALL | 1 | 26L | GEN-2019-066 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.20869 | 105.39 | P12:345:AEPW-OKGE:L.E.S.-7:GRACMNT7
Thermal | 04ALL | 1 | 26L | GEN-2019-066 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.20869 | 100.58 | P12:345:AEPW-OKGE:L.E.S.-7:GRACMNT7
Thermal | 04ALL | 1 | 26L | GEN-2019-066 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.2087 | 105.61 | P42:345:AEPW:LAWTON EASTSIDE CB 3413A NBTB+FAULT
Thermal | 04ALL | 1 | 26L | GEN-2019-066 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.20871 | 105.98 | P42:345:AEPW:LAWTON EASTSIDE CB 3425A NBTB+FAULT
Thermal | 04ALL | 1 | 26L | GEN-2019-066 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.2087 | 105.61 | P23:345:AEPW:LAWTON EASTSIDE CB 3413A NBTB
Thermal | 04ALL | 1 | 26L | GEN-2019-066 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.20871 | 105.98 | P23:345:AEPW:LAWTON EASTSIDE CB 3425A NBTB
Thermal | 04ALL | 1 | 26SP | GEN-2019-066 | FROM->TO | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 353 | 1 | 164.6 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1
Thermal | 04ALL | 1 | 26SP | GEN-2019-066 | FROM->TO | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.9111 | 119.22 | 523771 GRAPEVINE 6 230 523777 WHEELER 6 230 1
Thermal | 04ALL | 1 | 26SP | GEN-2019-066 | FROM->TO | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 353 | 1 | 164.59 | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1
Thermal | 04ALL | 1 | 26SP | GEN-2019-066 | FROM->TO | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 353 | 1 | 164.6 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6
Thermal | 04ALL | 1 | 26SP | GEN-2019-066 | FROM->TO | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 |  | 395 | 0.21091 | 118.35 | P42:345:OKGE:SB_BVTY7315_PRE19S
Thermal | 04ALL | 1 | 26SP | GEN-2019-066 | FROM->TO | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 |  | 395 | 1 | 148.63 | P12:230:AEPW:SWEETWT6:CHISHOLM6
Thermal | 04ALL | 1 | 26SP | GEN-2019-066 | FROM->TO | 523771 GRAPEVINE 6 230 523777 WHEELER 6 230 1 |  | 319 | 0.83103 | 134.9 | P12:230:AEPW:SWEETWT6:CHISHOLM6
Thermal | 04ALL | 1 | 26SP | GEN-2019-066 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.20693 | 100.05 | P42:345:SPS:HITCHLAND:1R15:SLG:EHV:
Thermal | 04ALL | 1 | 26SP | GEN-2019-066 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.20651 | 102.81 | P42:345:SPS:POTTERCO:2R05:SLG:EHV:
Thermal | 04ALL | 1 | 26SP | GEN-2019-066 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.216 | 103.72 | P42:345:SPS:YOAKUM:J18####:SLG1:EHV:
Thermal | 04ALL | 1 | 26SP | GEN-2019-066 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.216 | 103.72 | P43:345:SPS:YOAKUM:TF#####:SLG:EHV:
Thermal | 04ALL | 1 | 26SP | GEN-2019-066 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.216 | 103.72 | P42:345:SPS:YOAKUM:J17####:SLG:EHV:
Thermal | 04ALL | 1 | 26SP | GEN-2019-066 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.21579 | 106.61 | P43:345:SPS:TUCO:SLG::EHV:
Thermal | 04ALL | 1 | 26SP | GEN-2019-066 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.216 | 103.72 | P42:345:SPS:YOAKUM:J18####:SLG2:EHV:
Thermal | 04ALL | 1 | 26SP | GEN-2019-066 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.22738 | 103.16 | P42:345:OKGE:SB_BVTY7387::::
Thermal | 04ALL | 1 | 26SP | GEN-2019-066 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.28449 | 107.58 | 511553 CHISHOLM7 345 755000 WWDBORDT 345 1
Thermal | 04ALL | 1 | 26SP | GEN-2019-066 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.48663 | 108.22 | 511557 CHISHOLM6 230 3WXFMR CHISHOLM6 1
Thermal | 04ALL | 1 | 26SP | GEN-2019-066 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.22738 | 103.16 | 515458 BORDER 7 345 560022 CRAWFISH_DR 345 1
Thermal | 04ALL | 1 | 26SP | GEN-2019-066 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.22738 | 103.11 | 515458 BORDER 7 345 755000 WWDBORDT 345 1
Thermal | 04ALL | 1 | 26SP | GEN-2019-066 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.20693 | 100.11 | 523097 HITCHLAND 7 345 523961 POTTER_CO 7 345 1
Thermal | 04ALL | 1 | 26SP | GEN-2019-066 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.20659 | 101.84 | 523961 POTTER_CO 7 345 3WXFMR WAUK 90343-A 1
Thermal | 04ALL | 1 | 26SP | GEN-2019-066 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.21488 | 105.61 | 523977 HARRNG_WST 6 230 523971 HARRNGTON1 1 24.0 1
Thermal | 04ALL | 1 | 26SP | GEN-2019-066 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.21481 | 106.21 | 523978 HARRNG_MID 6 230 523972 HARRNGTON2 1 24.0 1
Thermal | 04ALL | 1 | 26SP | GEN-2019-066 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.21484 | 105.7 | 523979 HARRNG_EST 6 230 523973 HARRNGTON3 1 24.0 1
Thermal | 04ALL | 1 | 26SP | GEN-2019-066 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.2144 | 102.37 | 524044 NICHOLS 6 230 524023 NICHOLS_3 1 22.0 1
Thermal | 04ALL | 1 | 26SP | GEN-2019-066 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.21507 | 102.61 | 525531 TOLK 6 230 525561 TOLK_1 1 24.0 1
Thermal | 04ALL | 1 | 26SP | GEN-2019-066 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.2149 | 103.83 | 525531 TOLK 6 230 525562 TOLK_2 1 24.0 1
Thermal | 04ALL | 1 | 26SP | GEN-2019-066 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.216 | 103.23 | 525832 TUCO_INT 7 345 526936 YOAKUM_345 345 1
Thermal | 04ALL | 1 | 26SP | GEN-2019-066 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 0.21091 | 131.54 | P42:345:OKGE:SB_BVTY7315_PRE19S
Thermal | 04ALL | 1 | 26SP | GEN-2019-066 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 353 | 1 | 164.32 | P12:230:AEPW:SWEETWT6:CHISHOLM6
Thermal | 04ALL | 1 | 26WP | GEN-2019-066 | FROM->TO | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 439 | 1 | 132.35 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1
Thermal | 04ALL | 1 | 26WP | GEN-2019-066 | FROM->TO | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 439 | 0.91088 | 102.67 | 523771 GRAPEVINE 6 230 523777 WHEELER 6 230 1
Thermal | 04ALL | 1 | 26WP | GEN-2019-066 | FROM->TO | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 439 | 1 | 132.35 | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1
Thermal | 04ALL | 1 | 26WP | GEN-2019-066 | FROM->TO | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 439 | 1 | 132.35 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6
Thermal | 04ALL | 1 | 26WP | GEN-2019-066 | FROM->TO | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 |  | 441 | 1 | 132.57 | P12:230:AEPW:SWEETWT6:CHISHOLM6
Thermal | 04ALL | 1 | 26WP | GEN-2019-066 | FROM->TO | 523771 GRAPEVINE 6 230 523777 WHEELER 6 230 1 |  | 346 | 0.83104 | 126.97 | P12:230:AEPW:SWEETWT6:CHISHOLM6
Thermal | 04ALL | 1 | 26WP | GEN-2019-066 | FROM->TO | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1 |  | 439 | 1 | 131.72 | P12:230:AEPW:SWEETWT6:CHISHOLM6
Non-Converge | 04NR | 0 | 26L | N/A | FROM->TO | None |  |  |  |  | None
Thermal | 04NR | 1 | 26L | N/A | FROM->TO | None |  |  |  |  | None
Non-Converge | 05ALL | 0 | 23SP | GEN-2018-073 | FROM->TO | Non-Converge |  |  | 0.30283 |  | 511456 O.K.U.-7 345 763215 G18-092-TAP 345 1
Non-Converge | 05ALL | 0 | 23SP | GEN-2018-073 | FROM->TO | Non-Converge |  |  | 0.30283 |  | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Non-Converge | 05ALL | 0 | 23SP | GEN-2018-073 | FROM->TO | Non-Converge |  |  | 0.30283 |  | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Non-Converge | 05ALL | 0 | 23SP | GEN-2018-073 | FROM->TO | Non-Converge |  |  | 0.30283 |  | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Non-Converge | 05ALL | 0 | 23SP | GEN-2018-073 | FROM->TO | Non-Converge |  |  | 0.30283 |  | P23:345:AEPW:OKLAUNION CB 3401A NBTB
Non-Converge | 05ALL | 0 | 23SP | GEN-2018-073 | FROM->TO | Non-Converge |  |  | 0.30283 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Non-Converge | 05ALL | 0 | 23SP | GEN-2018-073 | FROM->TO | Non-Converge |  |  | 0.30283 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Non-Converge | 05ALL | 0 | 23SP | GEN-2018-073 | FROM->TO | Non-Converge |  |  | 0.30283 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Non-Converge | 05ALL | 0 | 23SP | GEN-2018-081 | FROM->TO | Non-Converge |  |  | 0.23564 |  | 511456 O.K.U.-7 345 763215 G18-092-TAP 345 1
Non-Converge | 05ALL | 0 | 23SP | GEN-2018-081 | FROM->TO | Non-Converge |  |  | 0.23564 |  | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Non-Converge | 05ALL | 0 | 23SP | GEN-2018-081 | FROM->TO | Non-Converge |  |  | 0.23564 |  | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Non-Converge | 05ALL | 0 | 23SP | GEN-2018-081 | FROM->TO | Non-Converge |  |  | 0.23564 |  | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Non-Converge | 05ALL | 0 | 23SP | GEN-2018-081 | FROM->TO | Non-Converge |  |  | 0.23564 |  | P23:345:AEPW:OKLAUNION CB 3401A NBTB
Non-Converge | 05ALL | 0 | 23SP | GEN-2018-081 | FROM->TO | Non-Converge |  |  | 0.23564 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Non-Converge | 05ALL | 0 | 23SP | GEN-2018-081 | FROM->TO | Non-Converge |  |  | 0.23564 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Non-Converge | 05ALL | 0 | 23SP | GEN-2018-081 | FROM->TO | Non-Converge |  |  | 0.23564 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Non-Converge | 05ALL | 0 | 23SP | GEN-2018-089 | FROM->TO | Non-Converge |  |  | 0.20911 |  | 511456 O.K.U.-7 345 763215 G18-092-TAP 345 1
Non-Converge | 05ALL | 0 | 23SP | GEN-2018-089 | FROM->TO | Non-Converge |  |  | 0.20911 |  | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Non-Converge | 05ALL | 0 | 23SP | GEN-2018-089 | FROM->TO | Non-Converge |  |  | 0.20911 |  | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Non-Converge | 05ALL | 0 | 23SP | GEN-2018-089 | FROM->TO | Non-Converge |  |  | 0.20911 |  | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Non-Converge | 05ALL | 0 | 23SP | GEN-2018-089 | FROM->TO | Non-Converge |  |  | 0.20911 |  | P23:345:AEPW:OKLAUNION CB 3401A NBTB
Non-Converge | 05ALL | 0 | 23SP | GEN-2018-089 | FROM->TO | Non-Converge |  |  | 0.20911 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Non-Converge | 05ALL | 0 | 23SP | GEN-2018-089 | FROM->TO | Non-Converge |  |  | 0.20911 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Non-Converge | 05ALL | 0 | 23SP | GEN-2018-089 | FROM->TO | Non-Converge |  |  | 0.20911 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Non-Converge | 05ALL | 0 | 23SP | GEN-2018-092 | FROM->TO | Non-Converge |  |  | 0.62268 |  | 511456 O.K.U.-7 345 763215 G18-092-TAP 345 1
Non-Converge | 05ALL | 0 | 23SP | GEN-2018-092 | FROM->TO | Non-Converge |  |  | 0.62268 |  | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Non-Converge | 05ALL | 0 | 23SP | GEN-2018-092 | FROM->TO | Non-Converge |  |  | 0.62268 |  | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Non-Converge | 05ALL | 0 | 23SP | GEN-2018-092 | FROM->TO | Non-Converge |  |  | 0.62268 |  | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Non-Converge | 05ALL | 0 | 23SP | GEN-2018-092 | FROM->TO | Non-Converge |  |  | 0.62268 |  | P23:345:AEPW:OKLAUNION CB 3401A NBTB
Non-Converge | 05ALL | 0 | 23SP | GEN-2018-092 | FROM->TO | Non-Converge |  |  | 0.62268 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Non-Converge | 05ALL | 0 | 23SP | GEN-2018-092 | FROM->TO | Non-Converge |  |  | 0.62268 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Non-Converge | 05ALL | 0 | 23SP | GEN-2018-092 | FROM->TO | Non-Converge |  |  | 0.62268 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Non-Converge | 05ALL | 0 | 23SP | GEN-2018-097 | FROM->TO | Non-Converge |  |  | 0.24198 |  | 511456 O.K.U.-7 345 763215 G18-092-TAP 345 1
Non-Converge | 05ALL | 0 | 23SP | GEN-2018-097 | FROM->TO | Non-Converge |  |  | 0.24198 |  | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Non-Converge | 05ALL | 0 | 23SP | GEN-2018-097 | FROM->TO | Non-Converge |  |  | 0.24198 |  | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Non-Converge | 05ALL | 0 | 23SP | GEN-2018-097 | FROM->TO | Non-Converge |  |  | 0.24198 |  | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Non-Converge | 05ALL | 0 | 23SP | GEN-2018-097 | FROM->TO | Non-Converge |  |  | 0.24198 |  | P23:345:AEPW:OKLAUNION CB 3401A NBTB
Non-Converge | 05ALL | 0 | 23SP | GEN-2018-097 | FROM->TO | Non-Converge |  |  | 0.24198 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Non-Converge | 05ALL | 0 | 23SP | GEN-2018-097 | FROM->TO | Non-Converge |  |  | 0.24198 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Non-Converge | 05ALL | 0 | 23SP | GEN-2018-097 | FROM->TO | Non-Converge |  |  | 0.24198 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Non-Converge | 05ALL | 0 | 23SP | GEN-2018-099 | FROM->TO | Non-Converge |  |  | 0.24198 |  | 511456 O.K.U.-7 345 763215 G18-092-TAP 345 1
Non-Converge | 05ALL | 0 | 23SP | GEN-2018-099 | FROM->TO | Non-Converge |  |  | 0.24198 |  | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Non-Converge | 05ALL | 0 | 23SP | GEN-2018-099 | FROM->TO | Non-Converge |  |  | 0.24198 |  | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Non-Converge | 05ALL | 0 | 23SP | GEN-2018-099 | FROM->TO | Non-Converge |  |  | 0.24198 |  | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Non-Converge | 05ALL | 0 | 23SP | GEN-2018-099 | FROM->TO | Non-Converge |  |  | 0.24198 |  | P23:345:AEPW:OKLAUNION CB 3401A NBTB
Non-Converge | 05ALL | 0 | 23SP | GEN-2018-099 | FROM->TO | Non-Converge |  |  | 0.24198 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Non-Converge | 05ALL | 0 | 23SP | GEN-2018-099 | FROM->TO | Non-Converge |  |  | 0.24198 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Non-Converge | 05ALL | 0 | 23SP | GEN-2018-099 | FROM->TO | Non-Converge |  |  | 0.24198 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Non-Converge | 05ALL | 0 | 23SP | GEN-2018-111 | FROM->TO | Non-Converge |  |  | 0.24198 |  | 511456 O.K.U.-7 345 763215 G18-092-TAP 345 1
Non-Converge | 05ALL | 0 | 23SP | GEN-2018-111 | FROM->TO | Non-Converge |  |  | 0.24198 |  | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Non-Converge | 05ALL | 0 | 23SP | GEN-2018-111 | FROM->TO | Non-Converge |  |  | 0.24198 |  | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Non-Converge | 05ALL | 0 | 23SP | GEN-2018-111 | FROM->TO | Non-Converge |  |  | 0.24198 |  | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Non-Converge | 05ALL | 0 | 23SP | GEN-2018-111 | FROM->TO | Non-Converge |  |  | 0.24198 |  | P23:345:AEPW:OKLAUNION CB 3401A NBTB
Non-Converge | 05ALL | 0 | 23SP | GEN-2018-111 | FROM->TO | Non-Converge |  |  | 0.24198 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Non-Converge | 05ALL | 0 | 23SP | GEN-2018-111 | FROM->TO | Non-Converge |  |  | 0.24198 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Non-Converge | 05ALL | 0 | 23SP | GEN-2018-111 | FROM->TO | Non-Converge |  |  | 0.24198 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Non-Converge | 05ALL | 0 | 23SP | GEN-2018-112 | FROM->TO | Non-Converge |  |  | 0.24198 |  | 511456 O.K.U.-7 345 763215 G18-092-TAP 345 1
Non-Converge | 05ALL | 0 | 23SP | GEN-2018-112 | FROM->TO | Non-Converge |  |  | 0.24198 |  | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Non-Converge | 05ALL | 0 | 23SP | GEN-2018-112 | FROM->TO | Non-Converge |  |  | 0.24198 |  | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Non-Converge | 05ALL | 0 | 23SP | GEN-2018-112 | FROM->TO | Non-Converge |  |  | 0.24198 |  | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Non-Converge | 05ALL | 0 | 23SP | GEN-2018-112 | FROM->TO | Non-Converge |  |  | 0.24198 |  | P23:345:AEPW:OKLAUNION CB 3401A NBTB
Non-Converge | 05ALL | 0 | 23SP | GEN-2018-112 | FROM->TO | Non-Converge |  |  | 0.24198 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Non-Converge | 05ALL | 0 | 23SP | GEN-2018-112 | FROM->TO | Non-Converge |  |  | 0.24198 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Non-Converge | 05ALL | 0 | 23SP | GEN-2018-112 | FROM->TO | Non-Converge |  |  | 0.24198 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Non-Converge | 05ALL | 0 | 23SP | GEN-2018-124 | FROM->TO | Non-Converge |  |  | 0.24198 |  | 511456 O.K.U.-7 345 763215 G18-092-TAP 345 1
Non-Converge | 05ALL | 0 | 23SP | GEN-2018-124 | FROM->TO | Non-Converge |  |  | 0.24198 |  | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Non-Converge | 05ALL | 0 | 23SP | GEN-2018-124 | FROM->TO | Non-Converge |  |  | 0.24198 |  | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Non-Converge | 05ALL | 0 | 23SP | GEN-2018-124 | FROM->TO | Non-Converge |  |  | 0.24198 |  | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Non-Converge | 05ALL | 0 | 23SP | GEN-2018-124 | FROM->TO | Non-Converge |  |  | 0.24198 |  | P23:345:AEPW:OKLAUNION CB 3401A NBTB
Non-Converge | 05ALL | 0 | 23SP | GEN-2018-124 | FROM->TO | Non-Converge |  |  | 0.24198 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Non-Converge | 05ALL | 0 | 23SP | GEN-2018-124 | FROM->TO | Non-Converge |  |  | 0.24198 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Non-Converge | 05ALL | 0 | 23SP | GEN-2018-124 | FROM->TO | Non-Converge |  |  | 0.24198 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Non-Converge | 05ALL | 0 | 23SP | GEN-2019-003 | FROM->TO | Non-Converge |  |  | 0.2373 |  | 511456 O.K.U.-7 345 763215 G18-092-TAP 345 1
Non-Converge | 05ALL | 0 | 23SP | GEN-2019-003 | FROM->TO | Non-Converge |  |  | 0.2373 |  | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Non-Converge | 05ALL | 0 | 23SP | GEN-2019-003 | FROM->TO | Non-Converge |  |  | 0.2373 |  | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Non-Converge | 05ALL | 0 | 23SP | GEN-2019-003 | FROM->TO | Non-Converge |  |  | 0.2373 |  | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Non-Converge | 05ALL | 0 | 23SP | GEN-2019-003 | FROM->TO | Non-Converge |  |  | 0.2373 |  | P23:345:AEPW:OKLAUNION CB 3401A NBTB
Non-Converge | 05ALL | 0 | 23SP | GEN-2019-003 | FROM->TO | Non-Converge |  |  | 0.2373 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Non-Converge | 05ALL | 0 | 23SP | GEN-2019-003 | FROM->TO | Non-Converge |  |  | 0.2373 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Non-Converge | 05ALL | 0 | 23SP | GEN-2019-003 | FROM->TO | Non-Converge |  |  | 0.2373 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Non-Converge | 05ALL | 0 | 23SP | GEN-2019-011 | FROM->TO | Non-Converge |  |  | 0.26732 |  | 511456 O.K.U.-7 345 763215 G18-092-TAP 345 1
Non-Converge | 05ALL | 0 | 23SP | GEN-2019-011 | FROM->TO | Non-Converge |  |  | 0.26732 |  | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Non-Converge | 05ALL | 0 | 23SP | GEN-2019-011 | FROM->TO | Non-Converge |  |  | 0.26732 |  | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Non-Converge | 05ALL | 0 | 23SP | GEN-2019-011 | FROM->TO | Non-Converge |  |  | 0.26732 |  | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Non-Converge | 05ALL | 0 | 23SP | GEN-2019-011 | FROM->TO | Non-Converge |  |  | 0.26732 |  | P23:345:AEPW:OKLAUNION CB 3401A NBTB
Non-Converge | 05ALL | 0 | 23SP | GEN-2019-011 | FROM->TO | Non-Converge |  |  | 0.26732 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Non-Converge | 05ALL | 0 | 23SP | GEN-2019-011 | FROM->TO | Non-Converge |  |  | 0.26732 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Non-Converge | 05ALL | 0 | 23SP | GEN-2019-011 | FROM->TO | Non-Converge |  |  | 0.26732 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Non-Converge | 05ALL | 0 | 23SP | GEN-2019-021 | FROM->TO | Non-Converge |  |  | 0.2373 |  | 511456 O.K.U.-7 345 763215 G18-092-TAP 345 1
Non-Converge | 05ALL | 0 | 23SP | GEN-2019-021 | FROM->TO | Non-Converge |  |  | 0.2373 |  | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Non-Converge | 05ALL | 0 | 23SP | GEN-2019-021 | FROM->TO | Non-Converge |  |  | 0.2373 |  | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Non-Converge | 05ALL | 0 | 23SP | GEN-2019-021 | FROM->TO | Non-Converge |  |  | 0.2373 |  | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Non-Converge | 05ALL | 0 | 23SP | GEN-2019-021 | FROM->TO | Non-Converge |  |  | 0.2373 |  | P23:345:AEPW:OKLAUNION CB 3401A NBTB
Non-Converge | 05ALL | 0 | 23SP | GEN-2019-021 | FROM->TO | Non-Converge |  |  | 0.2373 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Non-Converge | 05ALL | 0 | 23SP | GEN-2019-021 | FROM->TO | Non-Converge |  |  | 0.2373 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Non-Converge | 05ALL | 0 | 23SP | GEN-2019-021 | FROM->TO | Non-Converge |  |  | 0.2373 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Non-Converge | 05ALL | 0 | 23SP | GEN-2019-056 | FROM->TO | Non-Converge |  |  | 0.14021 |  | 511456 O.K.U.-7 345 763215 G18-092-TAP 345 1
Non-Converge | 05ALL | 0 | 23SP | GEN-2019-056 | FROM->TO | Non-Converge |  |  | 0.14021 |  | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Non-Converge | 05ALL | 0 | 23SP | GEN-2019-056 | FROM->TO | Non-Converge |  |  | 0.14021 |  | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Non-Converge | 05ALL | 0 | 23SP | GEN-2019-056 | FROM->TO | Non-Converge |  |  | 0.14021 |  | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Non-Converge | 05ALL | 0 | 23SP | GEN-2019-056 | FROM->TO | Non-Converge |  |  | 0.14021 |  | P23:345:AEPW:OKLAUNION CB 3401A NBTB
Non-Converge | 05ALL | 0 | 23SP | GEN-2019-056 | FROM->TO | Non-Converge |  |  | 0.14021 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Non-Converge | 05ALL | 0 | 23SP | GEN-2019-056 | FROM->TO | Non-Converge |  |  | 0.14021 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Non-Converge | 05ALL | 0 | 23SP | GEN-2019-056 | FROM->TO | Non-Converge |  |  | 0.14021 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Non-Converge | 05ALL | 0 | 23SP | GEN-2019-074 | FROM->TO | Non-Converge |  |  | 0.23564 |  | 511456 O.K.U.-7 345 763215 G18-092-TAP 345 1
Non-Converge | 05ALL | 0 | 23SP | GEN-2019-074 | FROM->TO | Non-Converge |  |  | 0.23564 |  | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Non-Converge | 05ALL | 0 | 23SP | GEN-2019-074 | FROM->TO | Non-Converge |  |  | 0.23564 |  | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Non-Converge | 05ALL | 0 | 23SP | GEN-2019-074 | FROM->TO | Non-Converge |  |  | 0.23564 |  | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Non-Converge | 05ALL | 0 | 23SP | GEN-2019-074 | FROM->TO | Non-Converge |  |  | 0.23564 |  | P23:345:AEPW:OKLAUNION CB 3401A NBTB
Non-Converge | 05ALL | 0 | 23SP | GEN-2019-074 | FROM->TO | Non-Converge |  |  | 0.23564 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Non-Converge | 05ALL | 0 | 23SP | GEN-2019-074 | FROM->TO | Non-Converge |  |  | 0.23564 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Non-Converge | 05ALL | 0 | 23SP | GEN-2019-074 | FROM->TO | Non-Converge |  |  | 0.23564 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Non-Converge | 05ALL | 0 | 26SP | GEN-2018-073 | FROM->TO | Non-Converge |  |  | 0.28993 |  | 511456 O.K.U.-7 345 763215 G18-092-TAP 345 1
Non-Converge | 05ALL | 0 | 26SP | GEN-2018-073 | FROM->TO | Non-Converge |  |  | 0.28993 |  | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Non-Converge | 05ALL | 0 | 26SP | GEN-2018-073 | FROM->TO | Non-Converge |  |  | 0.28993 |  | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Non-Converge | 05ALL | 0 | 26SP | GEN-2018-073 | FROM->TO | Non-Converge |  |  | 0.28993 |  | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Non-Converge | 05ALL | 0 | 26SP | GEN-2018-073 | FROM->TO | Non-Converge |  |  | 0.28993 |  | P23:345:AEPW:OKLAUNION CB 3401A NBTB
Non-Converge | 05ALL | 0 | 26SP | GEN-2018-073 | FROM->TO | Non-Converge |  |  | 0.28993 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Non-Converge | 05ALL | 0 | 26SP | GEN-2018-073 | FROM->TO | Non-Converge |  |  | 0.28993 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Non-Converge | 05ALL | 0 | 26SP | GEN-2018-073 | FROM->TO | Non-Converge |  |  | 0.28993 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Non-Converge | 05ALL | 0 | 26SP | GEN-2018-081 | FROM->TO | Non-Converge |  |  | 0.22764 |  | 511456 O.K.U.-7 345 763215 G18-092-TAP 345 1
Non-Converge | 05ALL | 0 | 26SP | GEN-2018-081 | FROM->TO | Non-Converge |  |  | 0.22764 |  | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Non-Converge | 05ALL | 0 | 26SP | GEN-2018-081 | FROM->TO | Non-Converge |  |  | 0.22764 |  | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Non-Converge | 05ALL | 0 | 26SP | GEN-2018-081 | FROM->TO | Non-Converge |  |  | 0.22764 |  | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Non-Converge | 05ALL | 0 | 26SP | GEN-2018-081 | FROM->TO | Non-Converge |  |  | 0.22764 |  | P23:345:AEPW:OKLAUNION CB 3401A NBTB
Non-Converge | 05ALL | 0 | 26SP | GEN-2018-081 | FROM->TO | Non-Converge |  |  | 0.22764 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Non-Converge | 05ALL | 0 | 26SP | GEN-2018-081 | FROM->TO | Non-Converge |  |  | 0.22764 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Non-Converge | 05ALL | 0 | 26SP | GEN-2018-081 | FROM->TO | Non-Converge |  |  | 0.22764 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Non-Converge | 05ALL | 0 | 26SP | GEN-2018-089 | FROM->TO | Non-Converge |  |  | 0.20304 |  | 511456 O.K.U.-7 345 763215 G18-092-TAP 345 1
Non-Converge | 05ALL | 0 | 26SP | GEN-2018-089 | FROM->TO | Non-Converge |  |  | 0.20304 |  | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Non-Converge | 05ALL | 0 | 26SP | GEN-2018-089 | FROM->TO | Non-Converge |  |  | 0.20304 |  | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Non-Converge | 05ALL | 0 | 26SP | GEN-2018-089 | FROM->TO | Non-Converge |  |  | 0.20304 |  | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Non-Converge | 05ALL | 0 | 26SP | GEN-2018-089 | FROM->TO | Non-Converge |  |  | 0.20304 |  | P23:345:AEPW:OKLAUNION CB 3401A NBTB
Non-Converge | 05ALL | 0 | 26SP | GEN-2018-089 | FROM->TO | Non-Converge |  |  | 0.20304 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Non-Converge | 05ALL | 0 | 26SP | GEN-2018-089 | FROM->TO | Non-Converge |  |  | 0.20304 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Non-Converge | 05ALL | 0 | 26SP | GEN-2018-089 | FROM->TO | Non-Converge |  |  | 0.20304 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Non-Converge | 05ALL | 0 | 26SP | GEN-2018-092 | FROM->TO | Non-Converge |  |  | 0.62504 |  | 511456 O.K.U.-7 345 763215 G18-092-TAP 345 1
Non-Converge | 05ALL | 0 | 26SP | GEN-2018-092 | FROM->TO | Non-Converge |  |  | 0.62504 |  | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Non-Converge | 05ALL | 0 | 26SP | GEN-2018-092 | FROM->TO | Non-Converge |  |  | 0.62504 |  | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Non-Converge | 05ALL | 0 | 26SP | GEN-2018-092 | FROM->TO | Non-Converge |  |  | 0.62504 |  | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Non-Converge | 05ALL | 0 | 26SP | GEN-2018-092 | FROM->TO | Non-Converge |  |  | 0.62504 |  | P23:345:AEPW:OKLAUNION CB 3401A NBTB
Non-Converge | 05ALL | 0 | 26SP | GEN-2018-092 | FROM->TO | Non-Converge |  |  | 0.62504 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Non-Converge | 05ALL | 0 | 26SP | GEN-2018-092 | FROM->TO | Non-Converge |  |  | 0.62504 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Non-Converge | 05ALL | 0 | 26SP | GEN-2018-092 | FROM->TO | Non-Converge |  |  | 0.62504 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Non-Converge | 05ALL | 0 | 26SP | GEN-2018-097 | FROM->TO | Non-Converge |  |  | 0.23352 |  | 511456 O.K.U.-7 345 763215 G18-092-TAP 345 1
Non-Converge | 05ALL | 0 | 26SP | GEN-2018-097 | FROM->TO | Non-Converge |  |  | 0.23352 |  | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Non-Converge | 05ALL | 0 | 26SP | GEN-2018-097 | FROM->TO | Non-Converge |  |  | 0.23352 |  | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Non-Converge | 05ALL | 0 | 26SP | GEN-2018-097 | FROM->TO | Non-Converge |  |  | 0.23352 |  | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Non-Converge | 05ALL | 0 | 26SP | GEN-2018-097 | FROM->TO | Non-Converge |  |  | 0.23352 |  | P23:345:AEPW:OKLAUNION CB 3401A NBTB
Non-Converge | 05ALL | 0 | 26SP | GEN-2018-097 | FROM->TO | Non-Converge |  |  | 0.23352 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Non-Converge | 05ALL | 0 | 26SP | GEN-2018-097 | FROM->TO | Non-Converge |  |  | 0.23352 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Non-Converge | 05ALL | 0 | 26SP | GEN-2018-097 | FROM->TO | Non-Converge |  |  | 0.23352 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Non-Converge | 05ALL | 0 | 26SP | GEN-2018-099 | FROM->TO | Non-Converge |  |  | 0.23352 |  | 511456 O.K.U.-7 345 763215 G18-092-TAP 345 1
Non-Converge | 05ALL | 0 | 26SP | GEN-2018-099 | FROM->TO | Non-Converge |  |  | 0.23352 |  | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Non-Converge | 05ALL | 0 | 26SP | GEN-2018-099 | FROM->TO | Non-Converge |  |  | 0.23352 |  | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Non-Converge | 05ALL | 0 | 26SP | GEN-2018-099 | FROM->TO | Non-Converge |  |  | 0.23352 |  | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Non-Converge | 05ALL | 0 | 26SP | GEN-2018-099 | FROM->TO | Non-Converge |  |  | 0.23352 |  | P23:345:AEPW:OKLAUNION CB 3401A NBTB
Non-Converge | 05ALL | 0 | 26SP | GEN-2018-099 | FROM->TO | Non-Converge |  |  | 0.23352 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Non-Converge | 05ALL | 0 | 26SP | GEN-2018-099 | FROM->TO | Non-Converge |  |  | 0.23352 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Non-Converge | 05ALL | 0 | 26SP | GEN-2018-099 | FROM->TO | Non-Converge |  |  | 0.23352 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Non-Converge | 05ALL | 0 | 26SP | GEN-2018-111 | FROM->TO | Non-Converge |  |  | 0.23352 |  | 511456 O.K.U.-7 345 763215 G18-092-TAP 345 1
Non-Converge | 05ALL | 0 | 26SP | GEN-2018-111 | FROM->TO | Non-Converge |  |  | 0.23352 |  | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Non-Converge | 05ALL | 0 | 26SP | GEN-2018-111 | FROM->TO | Non-Converge |  |  | 0.23352 |  | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Non-Converge | 05ALL | 0 | 26SP | GEN-2018-111 | FROM->TO | Non-Converge |  |  | 0.23352 |  | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Non-Converge | 05ALL | 0 | 26SP | GEN-2018-111 | FROM->TO | Non-Converge |  |  | 0.23352 |  | P23:345:AEPW:OKLAUNION CB 3401A NBTB
Non-Converge | 05ALL | 0 | 26SP | GEN-2018-111 | FROM->TO | Non-Converge |  |  | 0.23352 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Non-Converge | 05ALL | 0 | 26SP | GEN-2018-111 | FROM->TO | Non-Converge |  |  | 0.23352 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Non-Converge | 05ALL | 0 | 26SP | GEN-2018-111 | FROM->TO | Non-Converge |  |  | 0.23352 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Non-Converge | 05ALL | 0 | 26SP | GEN-2018-112 | FROM->TO | Non-Converge |  |  | 0.23352 |  | 511456 O.K.U.-7 345 763215 G18-092-TAP 345 1
Non-Converge | 05ALL | 0 | 26SP | GEN-2018-112 | FROM->TO | Non-Converge |  |  | 0.23352 |  | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Non-Converge | 05ALL | 0 | 26SP | GEN-2018-112 | FROM->TO | Non-Converge |  |  | 0.23352 |  | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Non-Converge | 05ALL | 0 | 26SP | GEN-2018-112 | FROM->TO | Non-Converge |  |  | 0.23352 |  | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Non-Converge | 05ALL | 0 | 26SP | GEN-2018-112 | FROM->TO | Non-Converge |  |  | 0.23352 |  | P23:345:AEPW:OKLAUNION CB 3401A NBTB
Non-Converge | 05ALL | 0 | 26SP | GEN-2018-112 | FROM->TO | Non-Converge |  |  | 0.23352 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Non-Converge | 05ALL | 0 | 26SP | GEN-2018-112 | FROM->TO | Non-Converge |  |  | 0.23352 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Non-Converge | 05ALL | 0 | 26SP | GEN-2018-112 | FROM->TO | Non-Converge |  |  | 0.23352 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Non-Converge | 05ALL | 0 | 26SP | GEN-2018-124 | FROM->TO | Non-Converge |  |  | 0.23352 |  | 511456 O.K.U.-7 345 763215 G18-092-TAP 345 1
Non-Converge | 05ALL | 0 | 26SP | GEN-2018-124 | FROM->TO | Non-Converge |  |  | 0.23352 |  | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Non-Converge | 05ALL | 0 | 26SP | GEN-2018-124 | FROM->TO | Non-Converge |  |  | 0.23352 |  | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Non-Converge | 05ALL | 0 | 26SP | GEN-2018-124 | FROM->TO | Non-Converge |  |  | 0.23352 |  | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Non-Converge | 05ALL | 0 | 26SP | GEN-2018-124 | FROM->TO | Non-Converge |  |  | 0.23352 |  | P23:345:AEPW:OKLAUNION CB 3401A NBTB
Non-Converge | 05ALL | 0 | 26SP | GEN-2018-124 | FROM->TO | Non-Converge |  |  | 0.23352 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Non-Converge | 05ALL | 0 | 26SP | GEN-2018-124 | FROM->TO | Non-Converge |  |  | 0.23352 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Non-Converge | 05ALL | 0 | 26SP | GEN-2018-124 | FROM->TO | Non-Converge |  |  | 0.23352 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Non-Converge | 05ALL | 0 | 26SP | GEN-2019-003 | FROM->TO | Non-Converge |  |  | 0.22917 |  | 511456 O.K.U.-7 345 763215 G18-092-TAP 345 1
Non-Converge | 05ALL | 0 | 26SP | GEN-2019-003 | FROM->TO | Non-Converge |  |  | 0.22917 |  | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Non-Converge | 05ALL | 0 | 26SP | GEN-2019-003 | FROM->TO | Non-Converge |  |  | 0.22917 |  | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Non-Converge | 05ALL | 0 | 26SP | GEN-2019-003 | FROM->TO | Non-Converge |  |  | 0.22917 |  | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Non-Converge | 05ALL | 0 | 26SP | GEN-2019-003 | FROM->TO | Non-Converge |  |  | 0.22917 |  | P23:345:AEPW:OKLAUNION CB 3401A NBTB
Non-Converge | 05ALL | 0 | 26SP | GEN-2019-003 | FROM->TO | Non-Converge |  |  | 0.22917 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Non-Converge | 05ALL | 0 | 26SP | GEN-2019-003 | FROM->TO | Non-Converge |  |  | 0.22917 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Non-Converge | 05ALL | 0 | 26SP | GEN-2019-003 | FROM->TO | Non-Converge |  |  | 0.22917 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Non-Converge | 05ALL | 0 | 26SP | GEN-2019-011 | FROM->TO | Non-Converge |  |  | 0.25701 |  | 511456 O.K.U.-7 345 763215 G18-092-TAP 345 1
Non-Converge | 05ALL | 0 | 26SP | GEN-2019-011 | FROM->TO | Non-Converge |  |  | 0.25701 |  | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Non-Converge | 05ALL | 0 | 26SP | GEN-2019-011 | FROM->TO | Non-Converge |  |  | 0.25701 |  | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Non-Converge | 05ALL | 0 | 26SP | GEN-2019-011 | FROM->TO | Non-Converge |  |  | 0.25701 |  | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Non-Converge | 05ALL | 0 | 26SP | GEN-2019-011 | FROM->TO | Non-Converge |  |  | 0.25701 |  | P23:345:AEPW:OKLAUNION CB 3401A NBTB
Non-Converge | 05ALL | 0 | 26SP | GEN-2019-011 | FROM->TO | Non-Converge |  |  | 0.25701 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Non-Converge | 05ALL | 0 | 26SP | GEN-2019-011 | FROM->TO | Non-Converge |  |  | 0.25701 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Non-Converge | 05ALL | 0 | 26SP | GEN-2019-011 | FROM->TO | Non-Converge |  |  | 0.25701 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Non-Converge | 05ALL | 0 | 26SP | GEN-2019-021 | FROM->TO | Non-Converge |  |  | 0.22917 |  | 511456 O.K.U.-7 345 763215 G18-092-TAP 345 1
Non-Converge | 05ALL | 0 | 26SP | GEN-2019-021 | FROM->TO | Non-Converge |  |  | 0.22917 |  | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Non-Converge | 05ALL | 0 | 26SP | GEN-2019-021 | FROM->TO | Non-Converge |  |  | 0.22917 |  | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Non-Converge | 05ALL | 0 | 26SP | GEN-2019-021 | FROM->TO | Non-Converge |  |  | 0.22917 |  | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Non-Converge | 05ALL | 0 | 26SP | GEN-2019-021 | FROM->TO | Non-Converge |  |  | 0.22917 |  | P23:345:AEPW:OKLAUNION CB 3401A NBTB
Non-Converge | 05ALL | 0 | 26SP | GEN-2019-021 | FROM->TO | Non-Converge |  |  | 0.22917 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Non-Converge | 05ALL | 0 | 26SP | GEN-2019-021 | FROM->TO | Non-Converge |  |  | 0.22917 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Non-Converge | 05ALL | 0 | 26SP | GEN-2019-021 | FROM->TO | Non-Converge |  |  | 0.22917 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Non-Converge | 05ALL | 0 | 26SP | GEN-2019-056 | FROM->TO | Non-Converge |  |  | 0.13994 |  | 511456 O.K.U.-7 345 763215 G18-092-TAP 345 1
Non-Converge | 05ALL | 0 | 26SP | GEN-2019-056 | FROM->TO | Non-Converge |  |  | 0.13994 |  | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Non-Converge | 05ALL | 0 | 26SP | GEN-2019-056 | FROM->TO | Non-Converge |  |  | 0.13994 |  | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Non-Converge | 05ALL | 0 | 26SP | GEN-2019-056 | FROM->TO | Non-Converge |  |  | 0.13994 |  | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Non-Converge | 05ALL | 0 | 26SP | GEN-2019-056 | FROM->TO | Non-Converge |  |  | 0.13994 |  | P23:345:AEPW:OKLAUNION CB 3401A NBTB
Non-Converge | 05ALL | 0 | 26SP | GEN-2019-056 | FROM->TO | Non-Converge |  |  | 0.13994 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Non-Converge | 05ALL | 0 | 26SP | GEN-2019-056 | FROM->TO | Non-Converge |  |  | 0.13994 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Non-Converge | 05ALL | 0 | 26SP | GEN-2019-056 | FROM->TO | Non-Converge |  |  | 0.13994 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Non-Converge | 05ALL | 0 | 26SP | GEN-2019-074 | FROM->TO | Non-Converge |  |  | 0.22764 |  | 511456 O.K.U.-7 345 763215 G18-092-TAP 345 1
Non-Converge | 05ALL | 0 | 26SP | GEN-2019-074 | FROM->TO | Non-Converge |  |  | 0.22764 |  | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Non-Converge | 05ALL | 0 | 26SP | GEN-2019-074 | FROM->TO | Non-Converge |  |  | 0.22764 |  | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Non-Converge | 05ALL | 0 | 26SP | GEN-2019-074 | FROM->TO | Non-Converge |  |  | 0.22764 |  | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Non-Converge | 05ALL | 0 | 26SP | GEN-2019-074 | FROM->TO | Non-Converge |  |  | 0.22764 |  | P23:345:AEPW:OKLAUNION CB 3401A NBTB
Non-Converge | 05ALL | 0 | 26SP | GEN-2019-074 | FROM->TO | Non-Converge |  |  | 0.22764 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Non-Converge | 05ALL | 0 | 26SP | GEN-2019-074 | FROM->TO | Non-Converge |  |  | 0.22764 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Non-Converge | 05ALL | 0 | 26SP | GEN-2019-074 | FROM->TO | Non-Converge |  |  | 0.22764 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Non-Converge | 05ALL | 0 | 26WP | GEN-2018-073 | FROM->TO | Non-Converge |  |  | 0.29049 |  | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Non-Converge | 05ALL | 0 | 26WP | GEN-2018-073 | FROM->TO | Non-Converge |  |  | 0.29049 |  | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Non-Converge | 05ALL | 0 | 26WP | GEN-2018-073 | FROM->TO | Non-Converge |  |  | 0.29049 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Non-Converge | 05ALL | 0 | 26WP | GEN-2018-073 | FROM->TO | Non-Converge |  |  | 0.29049 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Non-Converge | 05ALL | 0 | 26WP | GEN-2018-073 | FROM->TO | Non-Converge |  |  | 0.29049 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Non-Converge | 05ALL | 0 | 26WP | GEN-2018-081 | FROM->TO | Non-Converge |  |  | 0.22819 |  | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Non-Converge | 05ALL | 0 | 26WP | GEN-2018-081 | FROM->TO | Non-Converge |  |  | 0.22819 |  | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Non-Converge | 05ALL | 0 | 26WP | GEN-2018-081 | FROM->TO | Non-Converge |  |  | 0.22819 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Non-Converge | 05ALL | 0 | 26WP | GEN-2018-081 | FROM->TO | Non-Converge |  |  | 0.22819 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Non-Converge | 05ALL | 0 | 26WP | GEN-2018-081 | FROM->TO | Non-Converge |  |  | 0.22819 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Non-Converge | 05ALL | 0 | 26WP | GEN-2018-089 | FROM->TO | Non-Converge |  |  | 0.2036 |  | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Non-Converge | 05ALL | 0 | 26WP | GEN-2018-089 | FROM->TO | Non-Converge |  |  | 0.2036 |  | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Non-Converge | 05ALL | 0 | 26WP | GEN-2018-089 | FROM->TO | Non-Converge |  |  | 0.2036 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Non-Converge | 05ALL | 0 | 26WP | GEN-2018-089 | FROM->TO | Non-Converge |  |  | 0.2036 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Non-Converge | 05ALL | 0 | 26WP | GEN-2018-089 | FROM->TO | Non-Converge |  |  | 0.2036 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Non-Converge | 05ALL | 0 | 26WP | GEN-2018-092 | FROM->TO | Non-Converge |  |  | 0.62559 |  | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Non-Converge | 05ALL | 0 | 26WP | GEN-2018-092 | FROM->TO | Non-Converge |  |  | 0.62559 |  | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Non-Converge | 05ALL | 0 | 26WP | GEN-2018-092 | FROM->TO | Non-Converge |  |  | 0.62559 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Non-Converge | 05ALL | 0 | 26WP | GEN-2018-092 | FROM->TO | Non-Converge |  |  | 0.62559 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Non-Converge | 05ALL | 0 | 26WP | GEN-2018-092 | FROM->TO | Non-Converge |  |  | 0.62559 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Non-Converge | 05ALL | 0 | 26WP | GEN-2018-097 | FROM->TO | Non-Converge |  |  | 0.23407 |  | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Non-Converge | 05ALL | 0 | 26WP | GEN-2018-097 | FROM->TO | Non-Converge |  |  | 0.23407 |  | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Non-Converge | 05ALL | 0 | 26WP | GEN-2018-097 | FROM->TO | Non-Converge |  |  | 0.23407 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Non-Converge | 05ALL | 0 | 26WP | GEN-2018-097 | FROM->TO | Non-Converge |  |  | 0.23407 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Non-Converge | 05ALL | 0 | 26WP | GEN-2018-097 | FROM->TO | Non-Converge |  |  | 0.23407 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Non-Converge | 05ALL | 0 | 26WP | GEN-2018-099 | FROM->TO | Non-Converge |  |  | 0.23407 |  | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Non-Converge | 05ALL | 0 | 26WP | GEN-2018-099 | FROM->TO | Non-Converge |  |  | 0.23407 |  | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Non-Converge | 05ALL | 0 | 26WP | GEN-2018-099 | FROM->TO | Non-Converge |  |  | 0.23407 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Non-Converge | 05ALL | 0 | 26WP | GEN-2018-099 | FROM->TO | Non-Converge |  |  | 0.23407 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Non-Converge | 05ALL | 0 | 26WP | GEN-2018-099 | FROM->TO | Non-Converge |  |  | 0.23407 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Non-Converge | 05ALL | 0 | 26WP | GEN-2018-111 | FROM->TO | Non-Converge |  |  | 0.23407 |  | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Non-Converge | 05ALL | 0 | 26WP | GEN-2018-111 | FROM->TO | Non-Converge |  |  | 0.23407 |  | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Non-Converge | 05ALL | 0 | 26WP | GEN-2018-111 | FROM->TO | Non-Converge |  |  | 0.23407 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Non-Converge | 05ALL | 0 | 26WP | GEN-2018-111 | FROM->TO | Non-Converge |  |  | 0.23407 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Non-Converge | 05ALL | 0 | 26WP | GEN-2018-111 | FROM->TO | Non-Converge |  |  | 0.23407 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Non-Converge | 05ALL | 0 | 26WP | GEN-2018-112 | FROM->TO | Non-Converge |  |  | 0.23407 |  | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Non-Converge | 05ALL | 0 | 26WP | GEN-2018-112 | FROM->TO | Non-Converge |  |  | 0.23407 |  | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Non-Converge | 05ALL | 0 | 26WP | GEN-2018-112 | FROM->TO | Non-Converge |  |  | 0.23407 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Non-Converge | 05ALL | 0 | 26WP | GEN-2018-112 | FROM->TO | Non-Converge |  |  | 0.23407 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Non-Converge | 05ALL | 0 | 26WP | GEN-2018-112 | FROM->TO | Non-Converge |  |  | 0.23407 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Non-Converge | 05ALL | 0 | 26WP | GEN-2018-124 | FROM->TO | Non-Converge |  |  | 0.23407 |  | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Non-Converge | 05ALL | 0 | 26WP | GEN-2018-124 | FROM->TO | Non-Converge |  |  | 0.23407 |  | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Non-Converge | 05ALL | 0 | 26WP | GEN-2018-124 | FROM->TO | Non-Converge |  |  | 0.23407 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Non-Converge | 05ALL | 0 | 26WP | GEN-2018-124 | FROM->TO | Non-Converge |  |  | 0.23407 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Non-Converge | 05ALL | 0 | 26WP | GEN-2018-124 | FROM->TO | Non-Converge |  |  | 0.23407 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Non-Converge | 05ALL | 0 | 26WP | GEN-2019-003 | FROM->TO | Non-Converge |  |  | 0.22973 |  | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Non-Converge | 05ALL | 0 | 26WP | GEN-2019-003 | FROM->TO | Non-Converge |  |  | 0.22973 |  | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Non-Converge | 05ALL | 0 | 26WP | GEN-2019-003 | FROM->TO | Non-Converge |  |  | 0.22973 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Non-Converge | 05ALL | 0 | 26WP | GEN-2019-003 | FROM->TO | Non-Converge |  |  | 0.22973 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Non-Converge | 05ALL | 0 | 26WP | GEN-2019-003 | FROM->TO | Non-Converge |  |  | 0.22973 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Non-Converge | 05ALL | 0 | 26WP | GEN-2019-011 | FROM->TO | Non-Converge |  |  | 0.25757 |  | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Non-Converge | 05ALL | 0 | 26WP | GEN-2019-011 | FROM->TO | Non-Converge |  |  | 0.25757 |  | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Non-Converge | 05ALL | 0 | 26WP | GEN-2019-011 | FROM->TO | Non-Converge |  |  | 0.25757 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Non-Converge | 05ALL | 0 | 26WP | GEN-2019-011 | FROM->TO | Non-Converge |  |  | 0.25757 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Non-Converge | 05ALL | 0 | 26WP | GEN-2019-011 | FROM->TO | Non-Converge |  |  | 0.25757 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Non-Converge | 05ALL | 0 | 26WP | GEN-2019-021 | FROM->TO | Non-Converge |  |  | 0.22973 |  | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Non-Converge | 05ALL | 0 | 26WP | GEN-2019-021 | FROM->TO | Non-Converge |  |  | 0.22973 |  | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Non-Converge | 05ALL | 0 | 26WP | GEN-2019-021 | FROM->TO | Non-Converge |  |  | 0.22973 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Non-Converge | 05ALL | 0 | 26WP | GEN-2019-021 | FROM->TO | Non-Converge |  |  | 0.22973 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Non-Converge | 05ALL | 0 | 26WP | GEN-2019-021 | FROM->TO | Non-Converge |  |  | 0.22973 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Non-Converge | 05ALL | 0 | 26WP | GEN-2019-056 | FROM->TO | Non-Converge |  |  | 0.1405 |  | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Non-Converge | 05ALL | 0 | 26WP | GEN-2019-056 | FROM->TO | Non-Converge |  |  | 0.1405 |  | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Non-Converge | 05ALL | 0 | 26WP | GEN-2019-056 | FROM->TO | Non-Converge |  |  | 0.1405 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Non-Converge | 05ALL | 0 | 26WP | GEN-2019-056 | FROM->TO | Non-Converge |  |  | 0.1405 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Non-Converge | 05ALL | 0 | 26WP | GEN-2019-056 | FROM->TO | Non-Converge |  |  | 0.1405 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Non-Converge | 05ALL | 0 | 26WP | GEN-2019-074 | FROM->TO | Non-Converge |  |  | 0.22819 |  | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Non-Converge | 05ALL | 0 | 26WP | GEN-2019-074 | FROM->TO | Non-Converge |  |  | 0.22819 |  | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Non-Converge | 05ALL | 0 | 26WP | GEN-2019-074 | FROM->TO | Non-Converge |  |  | 0.22819 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Non-Converge | 05ALL | 0 | 26WP | GEN-2019-074 | FROM->TO | Non-Converge |  |  | 0.22819 |  | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Non-Converge | 05ALL | 0 | 26WP | GEN-2019-074 | FROM->TO | Non-Converge |  |  | 0.22819 |  | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Non-Converge | 05ALL | 0 | 26L | N/A | FROM->TO | None |  |  |  |  | None
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 | 560 |  | 0.05094 | 112.52 | System Intact
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525549 TOLK 7 345 997715 ABBXNL844501 230 1 | 478 |  | 0.05094 | 137.79 | System Intact
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 | 560 |  | 0.17492 | 112.52 | System Intact
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525549 TOLK 7 345 997715 ABBXNL844501 230 1 | 478 |  | 0.17492 | 137.79 | System Intact
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 | 560 |  | 0.08979 | 112.52 | System Intact
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525549 TOLK 7 345 997715 ABBXNL844501 230 1 | 478 |  | 0.08979 | 137.79 | System Intact
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 | 560 |  | 0.20705 | 112.52 | System Intact
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525549 TOLK 7 345 997715 ABBXNL844501 230 1 | 478 |  | 0.20705 | 137.79 | System Intact
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 | 560 |  | 0.20705 | 112.52 | System Intact
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525549 TOLK 7 345 997715 ABBXNL844501 230 1 | 478 |  | 0.20705 | 137.79 | System Intact
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 | 560 |  | 0.20705 | 112.52 | System Intact
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525549 TOLK 7 345 997715 ABBXNL844501 230 1 | 478 |  | 0.20705 | 137.79 | System Intact
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 | 560 |  | 0.20705 | 112.52 | System Intact
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525549 TOLK 7 345 997715 ABBXNL844501 230 1 | 478 |  | 0.20705 | 137.79 | System Intact
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 | 560 |  | 0.20705 | 112.52 | System Intact
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525549 TOLK 7 345 997715 ABBXNL844501 230 1 | 478 |  | 0.20705 | 137.79 | System Intact
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 | 560 |  | 0.14903 | 112.52 | System Intact
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525549 TOLK 7 345 997715 ABBXNL844501 230 1 | 478 |  | 0.14903 | 137.79 | System Intact
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 | 560 |  | 0.14903 | 112.52 | System Intact
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525549 TOLK 7 345 997715 ABBXNL844501 230 1 | 478 |  | 0.14903 | 137.79 | System Intact
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 | 560 |  | 0.17492 | 112.52 | System Intact
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525549 TOLK 7 345 997715 ABBXNL844501 230 1 | 478 |  | 0.17492 | 137.79 | System Intact
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 | 560 |  | 0.05074 | 115.92 | System Intact
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525549 TOLK 7 345 997713 ABBXNL844501 230 1 | 478 |  | 0.05074 | 141.34 | System Intact
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 | 560 |  | 0.17809 | 115.92 | System Intact
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525549 TOLK 7 345 997713 ABBXNL844501 230 1 | 478 |  | 0.17809 | 141.34 | System Intact
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 | 560 |  | 0.093 | 115.92 | System Intact
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525549 TOLK 7 345 997713 ABBXNL844501 230 1 | 478 |  | 0.093 | 141.34 | System Intact
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 | 560 |  | 0.21027 | 115.92 | System Intact
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525549 TOLK 7 345 997713 ABBXNL844501 230 1 | 478 |  | 0.21027 | 141.34 | System Intact
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 | 560 |  | 0.21027 | 115.92 | System Intact
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525549 TOLK 7 345 997713 ABBXNL844501 230 1 | 478 |  | 0.21027 | 141.34 | System Intact
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 | 560 |  | 0.21027 | 115.92 | System Intact
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525549 TOLK 7 345 997713 ABBXNL844501 230 1 | 478 |  | 0.21027 | 141.34 | System Intact
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 | 560 |  | 0.21027 | 115.92 | System Intact
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525549 TOLK 7 345 997713 ABBXNL844501 230 1 | 478 |  | 0.21027 | 141.34 | System Intact
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 | 560 |  | 0.21027 | 115.92 | System Intact
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525549 TOLK 7 345 997713 ABBXNL844501 230 1 | 478 |  | 0.21027 | 141.34 | System Intact
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 | 560 |  | 0.15221 | 115.92 | System Intact
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525549 TOLK 7 345 997713 ABBXNL844501 230 1 | 478 |  | 0.15221 | 141.34 | System Intact
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 | 560 |  | 0.15221 | 115.92 | System Intact
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525549 TOLK 7 345 997713 ABBXNL844501 230 1 | 478 |  | 0.15221 | 141.34 | System Intact
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 | 560 |  | 0.17809 | 115.92 | System Intact
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525549 TOLK 7 345 997713 ABBXNL844501 230 1 | 478 |  | 0.17809 | 141.34 | System Intact
Thermal | 05ALL | 1 | 26WP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 | 560 |  | 0.04972 | 120.39 | System Intact
Thermal | 05ALL | 1 | 26WP | GEN-2018-073 | FROM->TO | 525549 TOLK 7 345 997711 ABBXNL844501 230 1 | 552.5 |  | 0.04972 | 126.78 | System Intact
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 | 560 |  | 0.17708 | 120.39 | System Intact
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525549 TOLK 7 345 997711 ABBXNL844501 230 1 | 552.5 |  | 0.17708 | 126.78 | System Intact
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 | 560 |  | 0.09198 | 120.39 | System Intact
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525549 TOLK 7 345 997711 ABBXNL844501 230 1 | 552.5 |  | 0.09198 | 126.78 | System Intact
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 | 560 |  | 0.20926 | 120.39 | System Intact
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525549 TOLK 7 345 997711 ABBXNL844501 230 1 | 552.5 |  | 0.20926 | 126.78 | System Intact
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 | 560 |  | 0.20926 | 120.39 | System Intact
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525549 TOLK 7 345 997711 ABBXNL844501 230 1 | 552.5 |  | 0.20926 | 126.78 | System Intact
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 | 560 |  | 0.20926 | 120.39 | System Intact
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525549 TOLK 7 345 997711 ABBXNL844501 230 1 | 552.5 |  | 0.20926 | 126.78 | System Intact
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 | 560 |  | 0.20926 | 120.39 | System Intact
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525549 TOLK 7 345 997711 ABBXNL844501 230 1 | 552.5 |  | 0.20926 | 126.78 | System Intact
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 | 560 |  | 0.20926 | 120.39 | System Intact
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525549 TOLK 7 345 997711 ABBXNL844501 230 1 | 552.5 |  | 0.20926 | 126.78 | System Intact
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 | 560 |  | 0.1512 | 120.39 | System Intact
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525549 TOLK 7 345 997711 ABBXNL844501 230 1 | 552.5 |  | 0.1512 | 126.78 | System Intact
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 | 560 |  | 0.1512 | 120.39 | System Intact
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525549 TOLK 7 345 997711 ABBXNL844501 230 1 | 552.5 |  | 0.1512 | 126.78 | System Intact
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 | 560 |  | 0.17708 | 120.39 | System Intact
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525549 TOLK 7 345 997711 ABBXNL844501 230 1 | 552.5 |  | 0.17708 | 126.78 | System Intact
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997715 ABBXNL844501 230 1 |  | 553 | 0.28547 | 150.96 | 525531 TOLK 6 230 3WXFMR TOLK 6 2
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.28547 | 149.08 | 525549 TOLK 7 345 3WXFMR ABBXNL844501 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997715 ABBXNL844501 230 1 |  | 553 | 0.33791 | 150.96 | 525531 TOLK 6 230 3WXFMR TOLK 6 2
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20706 | 112.73 | P23:345:KCPL-WERE:237LACYGNE_R1-6::LACYGU1-LACYGNE-NEOSHO
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20703 | 112.64 | P11:230:WERE:LECU5_GEN::
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20704 | 112.63 | P11:161:GMO:DOGWOOD_COMBINED_CYCLE_UNIT_OUTAGE_1_1
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.2071 | 111.16 | P11:115:SPS:MUSTANG1&3:153MW::::
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20963 | 114.61 | P12:230:SPS:K37::1_TOLK_LAMB:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20723 | 112.61 | P12:230:SPS:K43::1_PRNGLE_HARR_E:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20707 | 112.37 | P12:230:SPS:K44::1_EPLNT_HARRW:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20718 | 112.79 | P12:115:SPS:T04::1_TRBLNC_CASTRO:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20704 | 112.19 | P12:115:SPS:T13::1_TAYLOR_WHOBBS:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20704 | 112.31 | P12:115:SPS:T14::1_MADDOX_TAYLOR:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 113.09 | P12:115:SPS:T21::1_GRSSLND_GRAHAM:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20704 | 112.41 | P12:115:SPS:T23::1_PCA_POTJCT:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.62 | P12:115:SPS:T24B::1_RSWLL_BRSHRF:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.64 | P12:115:SPS:T26::1_CHAVES_RSWLCTY:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20825 | 113.18 | P12:115:SPS:T28A::1_LAMTON_PLANTX:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20749 | 112.67 | P12:115:SPS:T29::1_LAMTON_HALECTR:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20876 | 113.96 | P12:115:SPS:T30::1_LAMB_HOCKLY:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20876 | 113.13 | P12:115:SPS:T31::1_HOCKLY_SUNDWN:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.207 | 112.63 | P12:115:SPS:T35::1_TERRY_YOAKUM:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 113.32 | P12:115:SPS:T45::1_NORRIS_OASIS:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20703 | 112.4 | P12:115:SPS:T57::1_MUSTG_SEGRVS:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20831 | 113.15 | P12:115:SPS:T59::1_CARGIL_CURRY:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.208 | 112.42 | P12:115:SPS:T66::1_RNDALL_HAPPY:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.208 | 112.9 | P12:115:SPS:T67::1_HAPPY_KRESS:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20709 | 112.39 | P12:115:SPS:T68::1_TUCO_FLOYD:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20699 | 113.2 | P12:115:SPS:T71::1_CRLSLE_YUMA:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20713 | 112.7 | P12:115:SPS:T81::1_COX_FLOYD:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20704 | 112.85 | P12:115:SPS:T83::1_SP-FKFD_ALLEN:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20699 | 113.01 | P12:115:SPS:T89::1_DC_N_HIGG:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.66 | P12:115:SPS:T91::1_HIGG_RUSSELL:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20727 | 112.62 | P12:115:SPS:V04::1_EPLANT_RNDALL:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20718 | 112.67 | P12:115:SPS:V07::1_COX_HALECTR:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20817 | 112.95 | P12:115:SPS:V09::1_HALECTR_PLANTX:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20703 | 112.83 | P12:115:SPS:V12::1_PLANTX_BAILEY:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20704 | 112.62 | P12:115:SPS:V15::1_TUCO_INDANA:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20667 | 112.67 | P12:115:SPS:V24::1_WOLFTH_TERRY:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20722 | 112.64 | P12:115:SPS:V26::1_RSWLL_EDDY_N:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.98 | P12:115:SPS:V33::1_LUBBS_LYNN:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20807 | 113.85 | P12:115:SPS:V37::1_CASTRO_PLANTX:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.75 | P12:115:SPS:V46::1_ALLEN_WHEELCK:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20706 | 113.09 | P12:115:SPS:V49::1_YOAKUM_SHLCO2:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20748 | 113.26 | P12:115:SPS:V55::1_SUNDWN_TERRY:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20718 | 113.09 | P12:115:SPS:V56::1_COCHRAN_SUNDWN:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20704 | 112.68 | P12:115:SPS:V62::1_CRLSLE_INDANA:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20706 | 112.62 | P12:115:SPS:V70::1_S_GORG_RNDALL:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20717 | 112.65 | P12:115:SPS:V78::2_CURRY_RSVLT:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20703 | 112.79 | P12:115:SPS:V81::1_LE-WAIT_LE-LVN:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.65 | P12:115:SPS:V95::1_DC_N_SHLCO2:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.61 | P12:115:SPS:W11::1_DC_S_SMINLE:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20704 | 112.61 | P12:115:SPS:W12::1_SMINLE_DOSS:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20704 | 112.68 | P12:115:SPS:W14::1_SMINLE_GAINES:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 113.14 | P12:115:SPS:W32::1_PRMTR_FE-CLSIN:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.61 | P12:115:SPS:W34::1_JNSDRW_MAPCO:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20702 | 112.85 | P12:115:SPS:W35::1_GAINES_JNSDRW:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20699 | 112.64 | P12:115:SPS:W36::1_TAYLOR_JNSDRW:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20895 | 113.15 | P12:115:SPS:W40::1_WCANYON_TRBLNC:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20732 | 112.71 | P12:115:SPS:W52::1_NEWHART_KRESS:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 113.2 | P12:115:SPS:W58::1_NORTON_LOPEZ:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.82 | P12:115:SPS:W59::1_LOPEZ_CMPBLL:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20706 | 113.15 | P12:115:SPS:W62::1_PLSTHL_CURRY:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20717 | 112.62 | P12:115:SPS:W63::1_PLSTHL_CURRY:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.96 | P12:115:SPS:W64::1_PLSTHL_FE-CLV:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20706 | 113.12 | P12:115:SPS:W65::1_PLSTHL_CURRY:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.81 | P12:115:SPS:W66::1_PORTA_GREYHUND:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20895 | 112.61 | P12:115:SPS:W77::1_RNDAL_WCANYON:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.64 | P12:115:SPS:W99::1_CAPITAN_CHAVES:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.207 | 113.08 | P12:115:SPS:U14::1_DC_STH_INKBSN:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20703 | 113.02 | P12:115:SPS:V15::1_INKBSN_LE-WAT:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20727 | 112.74 | P12:115:SPS:U16::1_BSHLND_OUTPST:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20727 | 112.73 | P12:115:SPS:U17::1_COLTR_OUTPST:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20711 | 112.8 | P12:115:SPS:U19::1_DEAN_PLAINS:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20727 | 112.67 | P12:115:SPS:U23::1_COLTR_HILSDE:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20704 | 112.62 | P11:18:HAST:::EGYCTR2G WEC2_LOSS OF WEC 2 GEN_:HV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20704 | 112.62 | P13:18-115:HAST:::EGYCNTR7 XFMR G2WEC 2 GSU_:HV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20704 | 112.63 | P11:161:GMO:DOGWOOD-COMBINED-CYCLE-UNIT-OUTA:::HV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20706 | 112.73 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20703 | 112.75 | P23:345:KCPL:LACYGNE-R2-5:::EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20701 | 112.78 | P11:230:WERE:JECU1-GEN:::HV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20703 | 112.64 | P11:230:WERE:LECU5-GEN:::HV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20701 | 112.78 | P11:345:WERE:JECU2-GEN:::EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20701 | 112.78 | P11:345:WERE:JECU3-GEN:::EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.95 | P11:345:WERE:WOLFU1-GEN:::EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20697 | 112.43 | P23:345:WERE:BUFF-345-534:::EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20697 | 112.43 | P23:345:WERE:BUFF-345-543:::EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20701 | 112.78 | P23:345:WERE:JEC-345-15:::EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.207 | 112.75 | P23:345:WERE:JEC-345-16:::EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20701 | 112.78 | P23:345:WERE:JEC-345-19:::EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20701 | 112.78 | P23:345:WERE:JEC-345-20:::EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.95 | P23:345:WERE:WOLF-345-50:::EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.95 | P23:345:WERE:WOLF-345-60:::EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.89 | P11:022:NPPD:COOPER1G:1:983:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.207 | 112.92 | P11:023:NPPD:GENTLM1G:1:757:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.207 | 112.94 | P11:024:NPPD:GENTLM2G:2:757:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20702 | 112.75 | P13:345:OPPD:NEBCTY1G:::EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.207 | 112.78 | P13:345:OPPD:NEBCTY2G:::EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.77 | P22:345:OPPD:S3458 NEBCTY1G:LT::EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20702 | 112.75 | P22:345:OPPD:S3458 NEBCTY1G:::EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.81 | P22:345:OPPD:S3458 NEBCTY2G:LT::EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.207 | 112.78 | P22:345:OPPD:S3458 NEBCTY2G:::EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.77 | P23:345:OPPD:S3458 NEBCTY1G:LT::EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20702 | 112.75 | P23:345:OPPD:S3458 NEBCTY1G:::EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.81 | P23:345:OPPD:S3458 NEBCTY2G:LT::EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.207 | 112.78 | P23:345:OPPD:S3458 NEBCTY2G:::EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.4 | P12:115:SUNC:PLYMELL-PIERCEVILLE:::HV::
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20703 | 112.64 | P11:018:UMZB:# 5 #:: DCS IN SD. DEERCREEK_MV::
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20704 | 112.61 | P11:022:UMZB:# 15 #:: LO IN ND. LELAND OLDS 1_MV::
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20703 | 112.65 | P11:020:UMZB:# 16 #:: LO IN ND. LELAND OLDS 2_MV::
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20702 | 112.7 | P11:023:UMZB:# 31 #:: AVS IN ND. ANTELOPE VALLEY 1_MV::
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20702 | 112.7 | P11:023:UMZB:# 32 #:: AVS IN ND. ANTELOPE VALLEY 2_MV::
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20699 | 112.9 | P11:024:UMZB:# 33 #:: LRS IN WY. LARAMIE RIVER STATION 1_MV::
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.63 | P12:230:UMZW:# 687 #:: FT IN SD. FT-BG1 BRANCH FAULT:HV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.63 | P12:230:UMZW:# 3617 #:: FT IN SD. FT-BG2 BRANCH FAULT:HV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.63 | P12:230:UMZW:# 4038 #:: BG-FT IN SD. FAULT FOR TRANSMISSION CIRCUIT (BG-FT).:HV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.63 | P12:230:UMZW:# 4039 #:: BG-FT IN SD. FAULT FOR TRANSMISSION CIRCUIT (BG-FT).:HV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.61 | P13:230:UMZW:# 5135 #:: OA IN SD. FAULT ON TRANSFORMER (2).:HV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.61 | P13:230:UMZW:# 5136 #:: OA IN SD. FAULT ON TRANSFORMER (3).:HV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20702 | 112.42 | P21:345:UMZW:# 725 #:: GI IN NE. GI-SWEET BRANCH FAULT:EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20702 | 112.42 | P23:345:UMZW:# 2430 #:: GI IN NE. GI 1492 BKR FAULT:EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20702 | 112.42 | P23:345:UMZW:# 2438 #:: GI IN NE. GI-SWEET BRANCH FAULT & GI 1492 STUCK BKR:EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20707 | 112.37 | P11:138:WFEC:HUGO1:465MW :::
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20701 | 112.4 | P12:345:OKGE-AEPW:BKRBKR20::::
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.2074 | 112.75 | P12:345:OKGE:BKRBKR21::::
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20759 | 112.95 | P12:345:OKGE:BKRBKR24::::
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20947 | 114.47 | P12:345:OKGE-AEPW:BKRBKR25::::
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20695 | 112.42 | P12:345:OKGE:BKRBKR336::::
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20695 | 112.41 | P12:345:OKGE:BKRBKR336_2::::
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.2101 | 114.61 | P12:345:OKGE-AEPW:BKRBKR366::::
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.2101 | 114.58 | P12:345:OKGE-AEPW:BKRBKR366::::
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.2076 | 112.87 | P12:345:OKGE:BKRBKR367::::
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20736 | 112.62 | P12:345:OKGE-WFEC:BKRBKR374::::
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20663 | 112.22 | P12:345:OKGE:BKRBKR4193::::
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20663 | 112.22 | P12:345:OKGE:BKRBKR4194::::
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20647 | 112.28 | P12:345:OKGE-SPS:BKRBKR4201::::
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20647 | 112.28 | P12:345:OKGE-SPS:BKRBKR4202::::
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20694 | 112.35 | P12:345:OKGE:BKRBKR443NEW::::
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20694 | 112.35 | P12:345:OKGE:BKRBKR443NEW2::::
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20698 | 112.88 | P12:345:OKGE:BKRBKR604::::
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20698 | 112.94 | P12:345:OKGE:BKRBKR604_2::::
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20656 | 112.62 | P42:345:OKGE:SB_ARIA7381::::
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.21489 | 116.05 | P42:345:OKGE:SB_BVTY7387::::
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.2074 | 112.68 | P42:345:OKGE:SB_SPCK7383::::
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20703 | 112.64 | P11:115:SUNC:GARDENCITY_S2:103:531459(2):HV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20703 | 112.64 | P11:115:SUNC:FORTDDODGE_4:157:539670(4):HV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.62 | P11:345:599:CIMARRON1WIND:200:531603(1):EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.92 | P13:115:SUNC:HOLCOMB_GSU:::HV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20703 | 112.64 | P13:115:SUNC:S2_GSU:::HV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20703 | 112.64 | P13:115:SUNC:FORTDODGE_GSU:::HV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20703 | 112.62 | P23:345:SUNC:BU_BRK682:::EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.71 | 300003 1THLG3 24.0 301503 7THOMHLGSU3 345 3
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.71 | 300049 7THOMHL 345 301503 7THOMHLGSU3 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.66 | P11:20:AMMO:1LAB�� G1:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.66 | P11:20:AMMO:1LAB�� G2:2
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.83 | P11:345:AMMO::CALLAWAY:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.66 | P11:345:AMMO::LABADIE:3
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.66 | P11:345:AMMO::LABADIE:4
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.66 | P11:345:AMMO::RUSHISLAND:U1
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.66 | P11:345:AMMO::RUSHISLAND:U2
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.64 | P11:138:AMMO::SIOUX:2
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.64 | P12:765:AEP:AEP ROCKP-AEP JEFF 765
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.61 | P11:HV:EES::1ISES U1:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.61 | P11:EHV:EES::1ISES U2:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.42 | P11:HV:EES::PIRKEY 1:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.42 | P11:EHV:EES::WELSH3-1:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.39 | P11:HV:EES::TURKCOAL:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.61 | P12:HV:EES::5ISES%:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.61 | P12:EHV:EES::8ISES%:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.82 | P12:EHV:EES::7CALAWY 1:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20706 | 112.39 | P12:HV:EES::TURK 4%:1(1)
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.64 | 344011 7HUGHES 345 344012 7HPW-N 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.66 | 344884 7LABADIE1 345 344894 1LAB G1 20.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.66 | 344885 7LABADIE2 345 344895 1LAB G2 20.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.66 | 344886 7LABADIE3 345 344896 1LAB G3 20.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.66 | 344887 7LABADIE4 345 344897 1LAB G4 20.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.65 | 345667 7RUSH 1 345 345670 1RUSH G1 18.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.65 | 345668 7RUSH 2 345 345671 1RUSH G2 18.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.64 | 345755 4SIOUX 1 138 345756 1SIOUX 1 18.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.64 | 345764 4SIOUX 2 138 345765 1SIOUX 2 18.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.69 | P12:345:MDU::CENTER:COYOTE:1::::
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.69 | P13:345:MDU:COYOTE GSU LOSS:COYOTE::1::::
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.61 | P11:345:MEC:GDMEC CT1
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.61 | P11:345:MEC:GDMEC CT2
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.71 | P11:345:MEC:GDMEC ST
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.9 | P11:345:MEC-NPPD:COOPER 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.8 | P11:24:XEL:AUTO-SINGLE:SHERC31G:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.8 | P11:24:XEL:AUTO-SINGLE:SHERC32G:2
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.87 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.73 | P11:20:XEL:AUTO-SINGLE:PRIS31G:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.73 | P11:20:XEL:AUTO-SINGLE:PRIS32G:2
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.76 | P11:22:XEL:AUTO-SINGLE:MNTCE31G:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.73 | P11:20:XEL:AUTO-SINGLE:KING31G:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.77 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.77 | P11:22:GRE:AUTO-SINGLE:GRE-COAL42G:2
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.71 | P11:24:OTP:AUTO-SINGLE:BIGSTN1G:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.71 | P11:20:OTP:AUTO-SINGLE:CENTER2G:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.63 | P11:22:OTP:AUTO-SINGLE:CENTER1G:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.7 | P11:24:OTP:AUTO-SINGLE:COYOTE1G:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.63 | P11:24:DPC:AUTO-SINGLE:GENOA53G:3
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.61 | P12:115:XEL:AUTO-SINGLE:CHEMOLT7:LSPOWER7:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.65 | P12:115:XEL:AUTO-SINGLE:COLVILL7:CANONFLSG7:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.61 | P12:115:XEL:AUTO-SINGLE:FARIBALTP7:FARIBALTGEN:Z
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.7 | P12:230:OTP:AUTO-SINGLE:SQBUTTE4:YNG24:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.78 | P13:24-345:XEL:AUTO-SINGLE:SHERC31G:SHERCO3:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.78 | P13:24-345:XEL:AUTO-SINGLE:SHERC32G:SHERCO3:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.85 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.73 | P13:20-345:XEL:AUTO-SINGLE:PRIS31G:PRISLD3:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.73 | P13:20-345:XEL:AUTO-SINGLE:PRIS32G:PRISLD3:2
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.76 | P13:22-345:XEL:AUTO-SINGLE:MNTCE31G:MNTCELO3:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.72 | P13:20-345:XEL:AUTO-SINGLE:KING31G:ASKING3:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.76 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL41G:GRE-COALCR4:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.75 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL42G:GRE-COALCR4:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.7 | P13:230-24:OTP:AUTO-SINGLE:BIGSTON4:BIGSTN1G:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.7 | P13:20-230:OTP:AUTO-SINGLE:CENTER2G:YNG24:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.62 | P13:22-230:OTP:AUTO-SINGLE:CENTER1G:CENTER4:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.69 | P13:24-345:OTP:AUTO-SINGLE:COYOTE1G:COYOTE3:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.63 | P13:24-161:DPC:AUTO-SINGLE:GENOA53G:GENOA5:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.64 | P13:24-161:DPC:AUTO-SINGLE:JPM:ALMA5:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.7 | P11:115:XEL:RIV COMBINE CYCLE
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.62 | P12:115:XEL:BDS #2 5
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.62 | P11:115:XEL:HBR #6
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.62 | P11:115:XEL:HBR #7
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.73 | P11:115:XEL:HBR #6 7 8
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.73 | P23:345:XEL:8H14 PRI
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.73 | P23:345:XEL:8H17 PRI AS
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.85 | P23:345:XEL:8N28 SHC
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.78 | P23:345:XEL:8N22 SHC
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.78 | P23:345:XEL:8N17 SHC
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.77 | P23:345:XEL:8N8 MNN
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.72 | P23:345:XEL:8P1 KING
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.72 | P23:345:XEL:8P2 KING
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.62 | P23:115:XEL:5P147 IVH AS
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.61 | P11:18:ALTW:AUTO-SINGLE:EMERYST1:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.61 | P11:22:ALTW:AUTO-SINGLE:LANS54G:4
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.74 | P11:22:ALTW:AUTO-SINGLE:ARNOLD1G:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.77 | P11:24:ALTW:AUTO-SINGLE:OTTUMW1G:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.61 | P13:18-161:ALTW:AUTO-SINGLE:EMERYST1:EMERY5:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.61 | P13:22-161:ALTW:AUTO-SINGLE:LANS54G:LANSINGL15:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.73 | P13:22-161:ALTW:AUTO-SINGLE:ARNOLD1G:ARNOLD5:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.76 | P13:24-161:ALTW:AUTO-SINGLE:OTTUMW1G:OTTUMWA5:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.82 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.88 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.75 | P11:22:MEC:AUTO-SINGLE:NEAL3G:3
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.81 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.76 | P11:24:MEC:AUTO-SINGLE:LOUIS31G:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.81 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.84 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.74 | P13:345-22:MEC:AUTO-SINGLE:RAUN3:NEAL3G:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.8 | P13:345-24:MEC:AUTO-SINGLE:RAUN3:NEAL4G:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.74 | P13:345-24:MEC:AUTO-SINGLE:LOUISA3:LOUIS31G:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20701 | 112.78 | P11:230:WERE:JECU1_GEN::
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20701 | 112.78 | P11:345:WERE:JECU2_GEN::
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20701 | 112.78 | P11:345:WERE:JECU3_GEN::
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.95 | P11:345:WERE:WOLFU1_GEN::
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20706 | 112.63 | 511435 SNYDER-4 138 588779 TAP_G17-036 138 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20679 | 112.38 | 511446 CL-AFTP4 138 511458 ELKCTY-4 138 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20679 | 112.4 | 511446 CL-AFTP4 138 511463 HOB-JCT4 138 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20713 | 112.63 | 511453 DUNCAN-4 138 511552 DUNCHERTP4 138 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20713 | 112.62 | 511455 D.E.S.-4 138 511552 DUNCHERTP4 138 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20713 | 112.62 | 511455 D.E.S.-4 138 529344 OMDUNE-4 138 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.63 | 511456 O.K.U.-7 345 511565 OKLAUN HVDC7 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 111.6 | 511456 O.K.U.-7 345 588760 GEN-2017-033 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.21019 | 114.54 | 511456 O.K.U.-7 345 763215 G18-092-TAP 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.21033 | 115.11 | 511468 L.E.S.-7 345 762467 G18-015-TAP 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20927 | 114.48 | 511468 L.E.S.-7 345 763215 G18-092-TAP 345 2
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.29 | 511468 L.E.S.-7 345 763318 GEN-2018-115 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20706 | 112.66 | 511488 112GORE4 138 511510 LAIRGST4 138 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20717 | 112.7 | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20706 | 112.65 | 511500 CACHE4 138 511510 LAIRGST4 138 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20706 | 112.64 | 511500 CACHE4 138 588779 TAP_G17-036 138 2
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.2086 | 112.8 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.75 | 511541 SWEETWT6 230 763340 GEN-2018-117 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20224 | 109.9 | 511553 CHISHOLM7 345 523961 POTTER_CO 7 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20224 | 109.9 | 511553 CHISHOLM7 345 523961 POTTER_CO 7 345 2
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.21489 | 116.03 | 515375 WWRDEHV7 345 515458 BORDER 7 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.21489 | 116.05 | 515458 BORDER 7 345 560022 CRAWFISH_DR 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20702 | 112.7 | 515618 BALKOW 7 345 3WXFMR BALKOW 7 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20702 | 112.7 | 515618 BALKOW 7 345 3WXFMR BALKOW 7 1_Dup1
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20698 | 112.95 | 515634 PALDR1W7 345 3WXFMR PALO2 _1 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.7 | 515677 BADGER 7 345 563170 G15082_1 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20698 | 112.61 | 520827 BINGERJ4 138 521017 ONEY 4 138 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20698 | 112.62 | 521017 ONEY 4 138 521089 WASHITA4 138 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.61 | 522800 MU-TULIA 3 115 525179 TULIA_TP 3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.75 | 522892 MU-BROWNFLD2 69.0 526761 BROWNFLD_TP2 69.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.64 | 523090 TEXAS_CNTY 3 115 589380 GEN-2017-100 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.207 | 112.78 | 523093 HITCHLAND 3 115 523174 GOODWELLWND3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.95 | 523097 HITCHLAND 7 345 523112 NOVUS1 7 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 113 | 523097 HITCHLAND 7 345 523215 FREWHELCOL17 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20478 | 111.48 | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 113.05 | 523097 HITCHLAND 7 345 560252 G10-14 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.62 | 523099 TC-DRYTRLS 3 115 588480 A16-010_SUB 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.82 | 523112 NOVUS1 7 345 3WXFMR NOVUS XF2 2
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.63 | 523112 NOVUS1 7 345 3WXFMR XIANA2011198 _1 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20703 | 112.61 | 523118 BUFF_DUNES 7 345 523853 FINNEY 7 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.63 | 523120 COLE 3 115 588860 GEN-2017-047 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20703 | 112.64 | 523172 GWELL_COLL11 34.5 523174 GOODWELLWND3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20703 | 112.65 | 523173 GWELL_COLL21 34.5 523174 GOODWELLWND3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20723 | 112.61 | 523267 PRINGLE 6 230 3WXFMR ENRCO13617-1 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20723 | 112.61 | 523267 PRINGLE 6 230 523979 HARRNG_EST 6 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20792 | 113.07 | 523771 GRAPEVINE 6 230 524044 NICHOLS 6 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.21511 | 113.75 | 523959 POTTER_CO 6 230 524267 BUSHLAND 6 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.21476 | 114.67 | 523959 POTTER_CO 6 230 525461 NEWHART 6 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20929 | 118.42 | 523961 POTTER_CO 7 345 3WXFMR WAUK 90343-A 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20703 | 112.4 | 523978 HARRNG_MID 6 230 523979 HARRNG_EST 6 230 @1
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20704 | 112.39 | 524010 ROLLHILLS 6 230 3WXFMR WAUK WT01104 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20727 | 112.74 | 524267 BUSHLAND 6 230 3WXFMR WH 7001795 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.22157 | 114.31 | 524267 BUSHLAND 6 230 524623 DEAFSMITH 6 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20691 | 113.07 | 524296 SPNSPUR_WND7 345 524299 SPNSPUR_COL7 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20691 | 113.07 | 524299 SPNSPUR_COL7 345 3WXFMR SPNSPUR_COL7 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.21086 | 113.32 | 524415 AMA_SOUTH 6 230 525213 SWISHER 6 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 113.2 | 524502 NORTON 3 115 524509 FE-TUCMCARI3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20895 | 113.01 | 524575 DS-#25+ 3 115 524597 PANDAHFD 3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20895 | 113.12 | 524575 DS-#25+ 3 115 524630 TIERABLANCA3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.7 | 524604 HEREFRD_SB 2 69.0 524608 HERFRD_STH 2 69.0 *1
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.2201 | 119.12 | 524623 DEAFSMITH 6 230 760498 G17-146-TAP 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 113.1 | 524721 DS-#15&#19+2 69.0 524745 CASTRO_CNTY2 69.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20711 | 112.61 | 524770 PLSNT_HILL 6 230 3WXFMR EFAE1100068A 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.21135 | 117.92 | 524875 OASIS 6 230 524885 SN_JUAN_TAP6 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20779 | 113.69 | 524875 OASIS 6 230 524909 ROOSEVELT 6 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.21126 | 118.38 | 524885 SN_JUAN_TAP6 230 527483 CHAVES_CNTY6 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20721 | 112.8 | 524909 ROOSEVELT 6 230 3WXFMR ABB LMM60042 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.21401 | 118.36 | 524909 ROOSEVELT 6 230 525531 TOLK 6 230 2
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 113.33 | 524923 PORTALES 2 69.0 524929 RO-PORT_MTR2 69.0 @1
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 113 | 525001 W_MULESHOE 2 69.0 525008 MULESH_CTY 2 69.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 113 | 525008 MULESH_CTY 2 69.0 525027 BAILEYCO 2 69.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 113.28 | 525023 BC-BAIL_MTR2 69.0 525027 BAILEYCO 2 69.0 @1
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20807 | 113.27 | 525056 BC-EARTH 3 115 525480 PLANT_X 3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 113.09 | 525191 KRESS_INT 2 69.0 525203 SW-KRESS 2 69.0 Z1
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 113.17 | 525192 KRESS_INT 3 115 3WXFMR ENRCO 136155 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.21005 | 113.6 | 525213 SWISHER 6 230 525461 NEWHART 6 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.73 | 525272 KISER 3 115 3WXFMR VON 13819/1 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 113.19 | 525326 COX 3 115 3WXFMR ELCO 13474-3 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 113.21 | 525414 LAMTON 3 115 3WXFMR ASEA MLL9204 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20825 | 113.03 | 525440 LC-S_OLTON+3 115 525446 RKYFORD_TP 3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20825 | 113.03 | 525446 RKYFORD_TP 3 115 525480 PLANT_X 3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.2232 | 116.34 | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20984 | 114.35 | 525481 PLANT_X 6 230 3WXFMR WH ALM20171 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.2166 | 118.3 | 525481 PLANT_X 6 230 526435 SUNDOWN 6 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.2201 | 117.38 | 525481 PLANT_X 6 230 760498 G17-146-TAP 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.21052 | 113.07 | 525481 PLANT_X 6 230 762174 G17-218TAP 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.21094 | 113.14 | 525481 PLANT_X 6 230 762174 G17-218TAP 230 2
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.21867 | 118.38 | 525531 TOLK 6 230 525586 NEEDMORE 6 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20963 | 114.61 | 525531 TOLK 6 230 525637 LAMB_CNTY 6 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.23641 | 118.52 | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.21218 | 113.33 | 525531 TOLK 6 230 762174 G17-218TAP 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.21254 | 113.39 | 525531 TOLK 6 230 762174 G17-218TAP 230 2
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.33791 | 149.08 | 525549 TOLK 7 345 3WXFMR ABBXNL844501 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.21867 | 118.36 | 525586 NEEDMORE 6 230 526935 YOAKUM 6 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 113.01 | 525599 LC-SANDHLL+2 69.0 525606 AMHERST 2 69.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 113.04 | 525606 AMHERST 2 69.0 525613 W_LITTLFLD 2 69.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 113.07 | 525613 W_LITTLFLD 2 69.0 525635 LAMB_CNTY 2 69.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 113.02 | 525635 LAMB_CNTY 2 69.0 525650 LC-LTTLFLD+2 69.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20963 | 114.61 | 525637 LAMB_CNTY 6 230 3WXFMR WH ALM20172 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.87 | 525828 TUCO_INT 3 115 3WXFMR DS F78800913 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20714 | 112.4 | 525830 TUCO_INT 6 230 3WXFMR ENRCO 136401 2
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 113.07 | 526086 SW_6786_N 2 69.0 526087 SW_6786_S 2 69.0 Z1
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 113.07 | 526086 SW_6786_N 2 69.0 526102 SP-HETTLER 2 69.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 113.14 | 526087 SW_6786_S 2 69.0 526284 PLANTERS 2 69.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.69 | 526160 CARLISLE 3 115 3WXFMR WH RLP38371 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 113.03 | 526195 QUINCY 3 115 526196 SP-MILWAUKEE 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.93 | 526268 LUBBCK_STH 3 115 3WXFMR NA 70454A 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 113.19 | 526284 PLANTERS 2 69.0 526297 LUBBCK_EST 2 69.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.207 | 112.63 | 526435 SUNDOWN 6 230 3WXFMR UPDATE LATER _12 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20729 | 115 | 526435 SUNDOWN 6 230 526460 AMOCO_SS 6 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20702 | 112.65 | 526525 WOLFFORTH 6 230 3WXFMR UPDATE LATER _13 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 113.07 | 526735 TERRY_CNTY 2 69.0 526747 LG-BROWNFLD2 69.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 113 | 526747 LG-BROWNFLD2 69.0 526754 BROWNFIELD 2 69.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20694 | 114.41 | 526935 YOAKUM 6 230 527028 INK_BASIN 6 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20683 | 113.76 | 527028 INK_BASIN 6 230 527894 HOBBS_INT 6 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20699 | 113 | 527130 DENVER_N 3 115 527286 HIGGEAST 3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.61 | 527149 MUSTANG 6 230 3WXFMR ENRCO 136161 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20719 | 110.49 | 527149 MUSTANG 6 230 527151 GS-MUSTANG 6 230 @1
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.86 | 527202 SEAGRAVES 3 115 3WXFMR ABB MLL92408 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.76 | 527212 DIAMONDBACK3 115 3WXFMR HOW 36773714 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.68 | 527261 SULPHUR 2 69.0 527271 LG-FOSTER +2 69.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20699 | 112.98 | 527286 HIGGEAST 3 115 527363 HIGG 3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20702 | 112.82 | 527322 GAINES 3 115 527325 OXY_WSEM_TP3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20702 | 112.74 | 527325 OXY_WSEM_TP3 115 527362 JOHNSON_DRW3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.73 | 527340 DOSS 3 115 3WXFMR ELCO 13566/1 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.71 | 527345 LEGACY 2 69.0 527350 XTO_ROBRTSN2 69.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.71 | 527346 LEGACY 3 115 3WXFMR VROL 13735-1 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.69 | 527350 XTO_ROBRTSN2 69.0 527355 BOARDMAN 2 69.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.63 | 527355 BOARDMAN 2 69.0 527365 FLANNAGAN 2 69.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.61 | 527360 MAPCO 3 115 527362 JOHNSON_DRW3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.65 | 527362 JOHNSON_DRW3 115 528775 LE-ERF 3 115 @1
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20707 | 112.39 | 527455 RSWL_SLRCOL3 115 527482 CHAVES_CNTY3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20707 | 112.41 | 527470 CHVS_SLRCOL3 115 527464 CHVS_SOLAR11 34.5 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20707 | 112.34 | 527470 CHVS_SLRCOL3 115 527482 CHAVES_CNTY3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20887 | 112.88 | 527483 CHAVES_CNTY6 230 527799 EDDY_NORTH 6 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.62 | 527508 PRICE 3 115 527509 PRICE_TAP 3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.62 | 527529 RIACBRSH_TP3 115 527533 SW4J795_E 3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.62 | 527533 SW4J795_E 3 115 527564 ROSWLL_INT 3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.62 | 527563 ROSWLL_INT 2 69.0 527575 SW_4702 2 69.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20722 | 112.67 | 527564 ROSWLL_INT 3 115 527597 TWEEDY 3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.62 | 527575 SW_4702 2 69.0 527589 CV-ORCHARD 2 69.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.207 | 112.78 | 527653 MILO_WIND 1 34.5 527655 RSVLT_CC_E 7 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20692 | 112.66 | 527654 RSVLT_CC_W 7 345 527655 RSVLT_CC_E 7 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20692 | 112.95 | 527654 RSVLT_CC_W 7 345 527666 RSVLT_COL1 7 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20687 | 112.86 | 527655 RSVLT_CC_E 7 345 527656 CROSSROADS 7 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20692 | 112.95 | 527666 RSVLT_COL1 7 345 3WXFMR RSVLT_COL1 7 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.36 | 527736 NAVAJO_5TP 3 115 527739 NAVAJO_4 3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20704 | 112.35 | 527864 CUNNINHAM 3 115 528348 BUCKEYE_TP 3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20704 | 112.63 | 527864 CUNNINHAM 3 115 528568 MONUMNT_TP 3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20688 | 112.91 | 527865 CUNNIGHM_N 6 230 527867 CUNNIGHM_S 6 230 *1
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20699 | 112.64 | 527865 CUNNIGHM_N 6 230 527963 POTASH_JCT 6 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20704 | 112.4 | 527867 CUNNIGHM_S 6 230 3WXFMR WH 7000266 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.207 | 112.86 | 527867 CUNNIGHM_S 6 230 527882 CUNINGHAM2 1 20.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20701 | 112.79 | 527894 HOBBS_INT 6 230 527903 HOBBS_PLT3 1 18.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20704 | 112.36 | 527965 KIOWA 7 345 528027 RDRUNNER 7 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.36 | 528015 PHANTOM 7 345 528027 RDRUNNER 7 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.41 | 528024 RR_SVC_HV 3 115 528021 RDRUNNR_SVC1 15.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.68 | 528025 RDRUNNER 3 115 587990 GEN-2016-121 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.42 | 528185 N_LOVING 7 345 3WXFMR HYO1063400-1 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20704 | 112.41 | 528185 N_LOVING 7 345 528223 CHINA_DRAW 7 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.36 | 528222 CHINA_DRAW 3 115 528225 CD_SVC_HV 3 115 Z1
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20703 | 112.34 | 528333 LE-WEST_SUB3 115 528334 LE-NRTH_INT3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20704 | 112.42 | 528341 LE-SANANDRS3 115 528627 LE-TXACO_TP3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20704 | 112.38 | 528348 BUCKEYE_TP 3 115 528627 LE-TXACO_TP3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20701 | 112.62 | 528394 QUAHADA 3 115 528396 XTO_BIGEDDY3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20704 | 112.33 | 528463 SANGER_SW 3 115 528575 OXYPERMIAN 3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20704 | 112.33 | 528463 SANGER_SW 3 115 762442 G18-004-TAP 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20704 | 112.63 | 528568 MONUMNT_TP 3 115 528581 BYRD_TP 3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20704 | 112.38 | 528574 OXY_NHU_RCF3 115 528575 OXYPERMIAN 3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.69 | 528617 LE-WAITS 2 69.0 528325 LE-WAITS 3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.61 | 528617 LE-WAITS 2 69.0 528714 LE-FORT_SW 2 69.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20704 | 112.42 | 528622 LE-SANANDRS2 69.0 528341 LE-SANANDRS3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.97 | 528626 LE-PLNSINT 2 69.0 526928 PLAINS_INT 3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.97 | 528626 LE-PLNSINT 2 69.0 528709 LE-PLNSGOAB2 69.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.63 | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.69 | 528669 LE-STKLDRTP2 69.0 528740 LE-PLANS_SW2 69.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.85 | 528709 LE-PLNSGOAB2 69.0 528740 LE-PLANS_SW2 69.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.63 | 528709 LE-PLNSGOAB2 69.0 528747 LE-ALLRED 2 69.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.61 | 528714 LE-FORT_SW 2 69.0 528718 LE-NEWTEX 2 69.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.69 | 528735 LE-PLAINSUB2 69.0 528740 LE-PLANS_SW2 69.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20694 | 112.41 | 530583 POSTROCK7 345 588654 G17-021-TAP 345 2
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.41 | 531213 SANTAFE3 115 531408 PIERCVL3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20674 | 112.33 | 531451 MINGO 7 345 531465 SETAB 7 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20703 | 112.62 | 531501 BUCKNER7 345 531502 CIMRRN 7 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20703 | 112.62 | 531502 CIMRRN 7 345 531503 CIMRRN 1 34.5 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20691 | 112.32 | 531510 HARBNGR3 115 3WXFMR HARBGR345 _1 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20703 | 112.64 | 532663 LEC U5 24.0 532854 LEC U5 6 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20703 | 112.64 | 532853 LAWHILL6 230 532854 LEC U5 6 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20704 | 112.69 | 542951 HAW G5 1 22.0 543665 HAWTHN5 161 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20703 | 112.74 | 542955 LAC G1 1 22.0 542981 LACYGNE7 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20703 | 112.72 | 542956 LAC G2 1 24.0 542981 LACYGNE7 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20702 | 112.76 | 542957 IAT G1 1 24.0 542982 IATAN 7 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20703 | 112.82 | 542962 IAT G2 1 24.5 542982 IATAN 7 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20704 | 112.61 | 542966 WGARDNR5 161 543105 BULLCRK5 161 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20959 | 112.16 | 560022 CRAWFISH_DR 345 762216 G17-151TAP 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20926 | 113.18 | 560022 CRAWFISH_DR 345 762467 G18-015-TAP 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 108.98 | 560022 CRAWFISH_DR 345 763087 GEN-2018-073 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.21041 | 113.55 | 560022 CRAWFISH_DR 345 763215 G18-092-TAP 345 2
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 113.05 | 560252 G10-14 345 560253 G10-14-1 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.78 | 560253 G10-14-1 115 560254 G10-14-SUB1 34.5 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.78 | 560253 G10-14-1 115 560255 G10-14-SUB2 34.5 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.63 | 560581 G06-44-2 34.5 523111 NOVUS1 3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.68 | 560582 G06-44-3 34.5 560577 G06-44 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.66 | 560583 G06-44-4 34.5 560577 G06-44 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.32 | 560757 ASGI13_02_1 69.0 560758 ASGI13_02_2 34.5 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.32 | 560757 ASGI13_02_1 69.0 562731 WHEATLAND 69.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.33 | 560763 ASGI13_03_1 115 560761 ASGI13_03_2 34.5 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.76 | 562015 FIREWHEEL1 34.5 523215 FREWHELCOL17 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.76 | 562016 FIREWHEEL2 34.5 523215 FREWHELCOL17 345 2
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.31 | 562323 AGI1202&1305 115 562324 AGI1202&1305 34.5 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.32 | 562727 LESBIA 115 562728 SANJONTAP 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.32 | 562728 SANJONTAP 115 562729 CAPROCKTAP1 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.32 | 562730 CAPROCKTAP2 69.0 562729 CAPROCKTAP1 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.32 | 562730 CAPROCKTAP2 69.0 562731 WHEATLAND 69.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.72 | 563171 G15082_2 34.5 563170 G15082_1 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.4 | P11:13.8:AEPW:COM1-1
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.41 | P11:13.8:AEPW:COM2-1
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.41 | P11:13.8:AEPW:COM3-1
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.42 | P11:18:AEPW:WELSH1-1
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.42 | P11:18:AEPW:WELSH3-1
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.42 | P11:24:AEPW:PIRKEY 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.39 | P11:24:AEPW:SWS3-1
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.39 | P11:24:AEPW:TURKCOAL
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20717 | 112.7 | P12:138:AEPW-OMPA:DUNCAN-4:OMDUNCN4
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20706 | 112.66 | P12:138:AEPW:112GORE4:SNYDER-4
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20706 | 112.66 | 5841_Dup1
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20714 | 111.96 | 584560 GEN-2015-014 115 584561 G15-014XFMR1 34.5 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20713 | 112.65 | P12:138:AEPW:SANTAFE:DUNCAN-4
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.68 | 587991 G16-121XFMR1 34.5 587990 GEN-2016-121 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.62 | 588480 A16-010_SUB 115 3WXFMR A16-010_SUB 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20717 | 112.7 | P12:138:AEPW:DUNCAN-4:L.E.S.-4
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.06 | 588761 G17-033XFMR1 34.5 588760 GEN-2017-033 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.06 | 588765 G17-033XFMR2 34.5 588760 GEN-2017-033 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.63 | 588861 G17-047XFMR1 34.5 588860 GEN-2017-047 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20667 | 112.2 | P12:138:AEPW:ELKCTY-4:CLINTJC4
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.64 | 589381 G17-100XFMR1 34.5 589380 GEN-2017-100 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20679 | 112.39 | P12:138:AEPW:HOB-JCT4:ELKCTY-4
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.64 | P12:138:AEPW:SHERID4:112GORE4
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20703 | 112.61 | P12:230:AEPW:SWEETWT6:BUFFCK6
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20702 | 112.66 | P12:230:AEPW:SWEETWT6:ROARK6
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20947 | 114.5 | P12:345:AEPW:L.E.S7:TERRYRD7
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20947 | 114.49 | P12:345:AEPW:L.E.S7:TERRYRD7
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20947 | 114.47 | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.2101 | 114.61 | P12:345:AEPW-OKGE:L.E.S.-7:GRACMNT7
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.2101 | 114.58 | P12:345:AEPW-OKGE:L.E.S.-7:GRACMNT7
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20701 | 112.4 | P12:345:AEPW-OKGE:PITTSB-7:SEMINOL7
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.21019 | 115.66 | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.66 | P22:345:AMMO::LABADIE:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.66 | P22:345:AMMO::LABADIE:2
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.66 | P22:345:AMMO::LABADIE:3
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.66 | P22:345:AMMO::LABADIE:4
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.65 | P22:345:AMMO::RUSHISLAND:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.64 | P22:345:AMMO::RUSHISLAND:2
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20706 | 112.41 | P13:138-13.8:AEPW:COMANC-4_#2
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.2053 | 111.28 | P13:138-230:AEPW:ELKCTY-4
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20707 | 112.4 | P13:138-24:AEPW:S.W.S.-4
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20706 | 112.39 | P13:138-24:AEPW:TURK 4
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20713 | 112.63 | P13:138-345:AEPW:L.E.S.-4_#1
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20722 | 112.75 | P13:138-345:AEPW:L.E.S.-4_#2
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20706 | 112.67 | P23:500:EES-EAI:KEO:B4941
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20706 | 112.66 | P23:500:EES-EAI:KEO:B4921
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.61 | P11:26:EES-EAI:INDEP2:1:D401
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.61 | P11:26:EES-EAI:INDEP2:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.61 | P13:500:EES-EAI:INDEP2:MT2
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.65 | P23:500:EES-EAI:INDEP2:B6126
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.64 | P23:500:EES-EAI:PD:INDEP2:LN:FK479
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20703 | 112.61 | P13:230-34.5:AEPW:BUFFCK6
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20702 | 112.67 | P13:230-34.5:AEPW:ROARK6
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.41 | P13:69-13.8:AEPW:COMANC-2
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.66 | P11:024:DPC:ALMA2:6
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.62 | P11:18:ITCM:EMERYGT1:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.63 | P11:18:ITCM:EMERYGT2:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.63 | P11:161:ITCM:MGS CT1:1C
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.63 | P11:161:ITCM:MGS CT2:2C
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20703 | 112.64 | 652537 WHITE 3 345 659286 DEERCREK-BE3 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20703 | 112.64 | 659286 DEERCREK-BE3 345 3WXFMR DEERCRK KU1A 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.63 | 672601 BD 4 230 672306 BD 6G 18.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.63 | 672610 POPLAR 4 230 672310 POPLAR 1G 18.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.63 | 672610 POPLAR 4 230 672311 POPLAR 2G 18.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.62 | 672621 SHAND 4 230 672321 SHAND 1G 18.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.61 | 672649 CODETTE 4 230 672650 NIPAWIN 4 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.62 | 672696 BRADA 4 230 672699 NBEC 4 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.69 | P23:345:MDU::COYOTE::5707-5712-5715::::
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.84 | P23:345:MEC:CBEC 905
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.81 | P23:345:MEC:CBEC 908
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.64 | P23:345:MEC:GDMEC 908
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.74 | P23:345:MEC:RAUN 0180
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.8 | P23:345:MEC:RAUN 0210
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.75 | P23:345:MEC:LOUISA 954
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.75 | P23:345:MEC:LOUISA 964
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.61 | P21:115:XEL:AUTO-SINGLE:CHEMOLT7:LSPOWER7:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.65 | P21:115:XEL:AUTO-SINGLE:COLVILL7:CANONFLSG7:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.61 | P21:115:XEL:AUTO-SINGLE:FARIBALTP7:FARIBALTGEN:Z
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.7 | P21:230:OTP:AUTO-SINGLE:SQBUTTE4:YNG24:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.69 | P23:345:OTP:CENTER 3:3215(1)
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.69 | P23:345:OTP:CENTER 3:3225(1)
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.63 | P12:230:UMZW:# 687 #: FT IN SD. FT-BG1 LINE FAULT
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.63 | P12:230:UMZW:# 3617 #: FT IN SD. FT-BG2 LINE FAULT
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 111.33 | 760494 GEN-2017-146 230 760498 G17-146-TAP 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 111.32 | 760495 G17-146-XFM1 34.5 760494 GEN-2017-146 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.05 | 761356 G17-239-XFMR 34.5 761355 GEN-2017-239 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.05 | 761359 G17-239-XFMR 34.5 761355 GEN-2017-239 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.23 | 761797 G17-187XFM1 34.5 761796 GEN-2017-187 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.23 | 761800 G17-187XFM2 34.5 761796 GEN-2017-187 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 107.16 | 762132 GEN-2017-158 230 763252 G18-099-XFM1 34.5 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 107.16 | 762132 GEN-2017-158 230 763255 G18-099-XFM2 34.5 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 107.74 | 762133 G17-158XFM1 34.5 762132 GEN-2017-158 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 107.74 | 762136 G17-158XFM2 34.5 762132 GEN-2017-158 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 109.9 | 762216 G17-151TAP 345 762217 GEN-2017-151 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20959 | 113.55 | 762216 G17-151TAP 345 762467 G18-015-TAP 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 111.85 | 762218 G17-151XFM1 34.5 762217 GEN-2017-151 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 111.85 | 762221 G17-151XFM2 34.5 762217 GEN-2017-151 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 111.85 | 762224 G17-151XFM3 34.5 762217 GEN-2017-151 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 111.85 | 762227 G17-151XFM4 34.5 762217 GEN-2017-151 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.36 | 762438 GEN-2018-004 115 762442 G18-004-TAP 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 110.89 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 111.7 | 762461 G18-015-XFM1 34.5 762460 GEN-2018-015 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 111.7 | 762464 G18-015-XFM2 34.5 762460 GEN-2018-015 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20843 | 113.07 | 762467 G18-015-TAP 345 763215 G18-092-TAP 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 110.18 | 763087 GEN-2018-073 345 763088 G18-073-XFM1 34.5 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 111.33 | 763087 GEN-2018-073 345 763091 G18-073-XFM2 34.5 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 107.16 | 763120 GEN-2018-081 230 763121 G18-081-XFM1 34.5 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 109.42 | 763120 GEN-2018-081 230 764011 G19-074-XFM1 34.5 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 109.44 | 763186 GEN-2018-089 230 763187 G18-089-XFM1 34.5 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 110.21 | 763208 GEN-2018-092 345 763215 G18-092-TAP 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 111.37 | 763208 GEN-2018-092 345 763220 G18-092-XFM1 34.5 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 111.37 | 763208 GEN-2018-092 345 763223 G18-092-XFM2 34.5 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 109.78 | 763241 GEN-2018-097 230 763296 G18-111-XFM1 34.5 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 109.14 | 763241 GEN-2018-097 230 763307 G18-112-XFM1 34.5 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 109.14 | 763241 GEN-2018-097 230 763310 G18-112-XFM2 34.5 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 108.87 | 763241 GEN-2018-097 230 763395 G18-124-XFM1 34.5 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 108.87 | 763241 GEN-2018-097 230 763398 G18-124-XFM2 34.5 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.29 | 763318 GEN-2018-115 345 763319 G18-115-XFM1 34.5 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.75 | 763340 GEN-2018-117 230 763341 G18-117-XFM1 34.5 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 108.51 | 763483 GEN-2019-003 230 763484 G19-003-XFM1 34.5 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 111.19 | 763483 GEN-2019-003 230 763605 G19-021-XFM1 34.5 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 111.9 | 763516 GEN-2019-011 345 763517 G19-011-XFM1 34.5 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.26 | 763879 GEN-2019-056 115 763880 G19-056XFM1 34.5 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20655 | 112.68 | P42:345:OKGE:SB_BVTY7305
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20697 | 112.43 | P23:345:WERE:BUFF_345-534::
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20697 | 112.43 | P23:345:WERE:BUFF_345-543::
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20701 | 112.78 | P23:345:WERE:JEC_345-15::
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.207 | 112.75 | P23:345:WERE:JEC_345-16::
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20701 | 112.78 | P23:345:WERE:JEC_345-19::
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20701 | 112.78 | P23:345:WERE:JEC_345-20::
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.95 | P23:345:WERE:WOLF_345-50::
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.95 | P23:345:WERE:WOLF_345-60::
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20706 | 112.43 | P42:345:AEPW:WELSH CB 10620 NBTB+FAULT
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.21019 | 114.21 | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.21043 | 114.99 | P42:345:AEPW:LAWTON EASTSIDE CB 3413A NBTB+FAULT
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.21079 | 115.4 | P42:345:AEPW:LAWTON EASTSIDE CB 3425A NBTB+FAULT
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.21033 | 115.86 | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20719 | 112.31 | P42:345:AEPW:PITTSBURG CB 3441A NBTB+FAULT
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20701 | 112.4 | P42:345:AEPW:PITTSBURG CB 3445A NBTB+FAULT
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20947 | 114.49 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20947 | 114.49 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20947 | 114.47 | P42:345:AEPW:TERRYRD_CB_3421A_NBTB
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20703 | 112.75 | P23:345:KCPL:LACYGNE_R2-5::LACYGU2-LACYGNE-STILWELL
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20706 | 112.43 | P23:345:AEPW:WELSH CB 10620 NBTB
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.21019 | 114.54 | P23:345:AEPW:OKLAUNION CB 3401A NBTB
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.21043 | 114.99 | P23:345:AEPW:LAWTON EASTSIDE CB 3413A NBTB
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.21079 | 115.4 | P23:345:AEPW:LAWTON EASTSIDE CB 3425A NBTB
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.21033 | 115.86 | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20719 | 112.31 | P23:345:AEPW:PITTSBURG CB 3441A NBTB
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20701 | 112.4 | P23:345:AEPW:PITTSBURG CB 3445A NBTB
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20947 | 114.49 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20947 | 114.49 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20947 | 114.47 | P23:345:AEPW:TERRYRD_CB_3421A_NBTB
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20736 | 112.62 | P12:138:AEPW:S.W.S.-4:L.E.S.-4
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.65 | P11:115:SUNC:GARDENCITY_S2:97:531459(2)
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20966 | 114.72 | P23:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.21223 | 117.32 | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20966 | 114.72 | P42:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB+FAULT
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.21223 | 117.32 | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20674 | 112.33 | P23:345:SUNC:MO_BRK182
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20674 | 112.33 | P23:345:SUNC:MO_BRK382
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20702 | 112.42 | P21:345:UMZW:# 725 #: GI IN NE. GI-SWEET LINE FAULT
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.2086 | 112.8 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20706 | 112.41 | P12:138-13.8:AEPW:COMANC-4_#1
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.2053 | 111.26 | P12:230:AEPW:ELKCITY6:CHISHOLM6
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20849 | 113.54 | P12:230:AEPW:SWEETWT6:CHISHOLM6
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997715 ABBXNL844501 230 1 |  | 553 | 0.33791 | 150.96 | 525531 TOLK 6 230 3WXFMR TOLK 6 2
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20706 | 112.73 | P23:345:KCPL-WERE:237LACYGNE_R1-6::LACYGU1-LACYGNE-NEOSHO
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20703 | 112.64 | P11:230:WERE:LECU5_GEN::
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20704 | 112.63 | P11:161:GMO:DOGWOOD_COMBINED_CYCLE_UNIT_OUTAGE_1_1
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.2071 | 111.16 | P11:115:SPS:MUSTANG1&3:153MW::::
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20963 | 114.61 | P12:230:SPS:K37::1_TOLK_LAMB:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20723 | 112.61 | P12:230:SPS:K43::1_PRNGLE_HARR_E:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20707 | 112.37 | P12:230:SPS:K44::1_EPLNT_HARRW:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20718 | 112.79 | P12:115:SPS:T04::1_TRBLNC_CASTRO:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20704 | 112.19 | P12:115:SPS:T13::1_TAYLOR_WHOBBS:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20704 | 112.31 | P12:115:SPS:T14::1_MADDOX_TAYLOR:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 113.09 | P12:115:SPS:T21::1_GRSSLND_GRAHAM:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20704 | 112.41 | P12:115:SPS:T23::1_PCA_POTJCT:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.62 | P12:115:SPS:T24B::1_RSWLL_BRSHRF:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.64 | P12:115:SPS:T26::1_CHAVES_RSWLCTY:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20825 | 113.18 | P12:115:SPS:T28A::1_LAMTON_PLANTX:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20749 | 112.67 | P12:115:SPS:T29::1_LAMTON_HALECTR:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20876 | 113.96 | P12:115:SPS:T30::1_LAMB_HOCKLY:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20876 | 113.13 | P12:115:SPS:T31::1_HOCKLY_SUNDWN:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.207 | 112.63 | P12:115:SPS:T35::1_TERRY_YOAKUM:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 113.32 | P12:115:SPS:T45::1_NORRIS_OASIS:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20703 | 112.4 | P12:115:SPS:T57::1_MUSTG_SEGRVS:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20831 | 113.15 | P12:115:SPS:T59::1_CARGIL_CURRY:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.208 | 112.42 | P12:115:SPS:T66::1_RNDALL_HAPPY:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.208 | 112.9 | P12:115:SPS:T67::1_HAPPY_KRESS:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20709 | 112.39 | P12:115:SPS:T68::1_TUCO_FLOYD:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20699 | 113.2 | P12:115:SPS:T71::1_CRLSLE_YUMA:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20713 | 112.7 | P12:115:SPS:T81::1_COX_FLOYD:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20704 | 112.85 | P12:115:SPS:T83::1_SP-FKFD_ALLEN:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20699 | 113.01 | P12:115:SPS:T89::1_DC_N_HIGG:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.66 | P12:115:SPS:T91::1_HIGG_RUSSELL:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20727 | 112.62 | P12:115:SPS:V04::1_EPLANT_RNDALL:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20718 | 112.67 | P12:115:SPS:V07::1_COX_HALECTR:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20817 | 112.95 | P12:115:SPS:V09::1_HALECTR_PLANTX:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20703 | 112.83 | P12:115:SPS:V12::1_PLANTX_BAILEY:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20704 | 112.62 | P12:115:SPS:V15::1_TUCO_INDANA:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20667 | 112.67 | P12:115:SPS:V24::1_WOLFTH_TERRY:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20722 | 112.64 | P12:115:SPS:V26::1_RSWLL_EDDY_N:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.98 | P12:115:SPS:V33::1_LUBBS_LYNN:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20807 | 113.85 | P12:115:SPS:V37::1_CASTRO_PLANTX:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.75 | P12:115:SPS:V46::1_ALLEN_WHEELCK:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20706 | 113.09 | P12:115:SPS:V49::1_YOAKUM_SHLCO2:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20748 | 113.26 | P12:115:SPS:V55::1_SUNDWN_TERRY:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20718 | 113.09 | P12:115:SPS:V56::1_COCHRAN_SUNDWN:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20704 | 112.68 | P12:115:SPS:V62::1_CRLSLE_INDANA:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20706 | 112.62 | P12:115:SPS:V70::1_S_GORG_RNDALL:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20717 | 112.65 | P12:115:SPS:V78::2_CURRY_RSVLT:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20703 | 112.79 | P12:115:SPS:V81::1_LE-WAIT_LE-LVN:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.65 | P12:115:SPS:V95::1_DC_N_SHLCO2:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.61 | P12:115:SPS:W11::1_DC_S_SMINLE:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20704 | 112.61 | P12:115:SPS:W12::1_SMINLE_DOSS:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20704 | 112.68 | P12:115:SPS:W14::1_SMINLE_GAINES:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 113.14 | P12:115:SPS:W32::1_PRMTR_FE-CLSIN:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.61 | P12:115:SPS:W34::1_JNSDRW_MAPCO:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20702 | 112.85 | P12:115:SPS:W35::1_GAINES_JNSDRW:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20699 | 112.64 | P12:115:SPS:W36::1_TAYLOR_JNSDRW:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20895 | 113.15 | P12:115:SPS:W40::1_WCANYON_TRBLNC:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20732 | 112.71 | P12:115:SPS:W52::1_NEWHART_KRESS:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 113.2 | P12:115:SPS:W58::1_NORTON_LOPEZ:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.82 | P12:115:SPS:W59::1_LOPEZ_CMPBLL:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20706 | 113.15 | P12:115:SPS:W62::1_PLSTHL_CURRY:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20717 | 112.62 | P12:115:SPS:W63::1_PLSTHL_CURRY:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.96 | P12:115:SPS:W64::1_PLSTHL_FE-CLV:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20706 | 113.12 | P12:115:SPS:W65::1_PLSTHL_CURRY:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.81 | P12:115:SPS:W66::1_PORTA_GREYHUND:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20895 | 112.61 | P12:115:SPS:W77::1_RNDAL_WCANYON:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.64 | P12:115:SPS:W99::1_CAPITAN_CHAVES:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.207 | 113.08 | P12:115:SPS:U14::1_DC_STH_INKBSN:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20703 | 113.02 | P12:115:SPS:V15::1_INKBSN_LE-WAT:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20727 | 112.74 | P12:115:SPS:U16::1_BSHLND_OUTPST:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20727 | 112.73 | P12:115:SPS:U17::1_COLTR_OUTPST:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20711 | 112.8 | P12:115:SPS:U19::1_DEAN_PLAINS:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20727 | 112.67 | P12:115:SPS:U23::1_COLTR_HILSDE:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20704 | 112.62 | P11:18:HAST:::EGYCTR2G WEC2_LOSS OF WEC 2 GEN_:HV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20704 | 112.62 | P13:18-115:HAST:::EGYCNTR7 XFMR G2WEC 2 GSU_:HV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20704 | 112.63 | P11:161:GMO:DOGWOOD-COMBINED-CYCLE-UNIT-OUTA:::HV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20706 | 112.73 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20703 | 112.75 | P23:345:KCPL:LACYGNE-R2-5:::EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20701 | 112.78 | P11:230:WERE:JECU1-GEN:::HV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20703 | 112.64 | P11:230:WERE:LECU5-GEN:::HV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20701 | 112.78 | P11:345:WERE:JECU2-GEN:::EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20701 | 112.78 | P11:345:WERE:JECU3-GEN:::EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.95 | P11:345:WERE:WOLFU1-GEN:::EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20697 | 112.43 | P23:345:WERE:BUFF-345-534:::EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20697 | 112.43 | P23:345:WERE:BUFF-345-543:::EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20701 | 112.78 | P23:345:WERE:JEC-345-15:::EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.207 | 112.75 | P23:345:WERE:JEC-345-16:::EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20701 | 112.78 | P23:345:WERE:JEC-345-19:::EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20701 | 112.78 | P23:345:WERE:JEC-345-20:::EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.95 | P23:345:WERE:WOLF-345-50:::EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.95 | P23:345:WERE:WOLF-345-60:::EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.89 | P11:022:NPPD:COOPER1G:1:983:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.207 | 112.92 | P11:023:NPPD:GENTLM1G:1:757:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.207 | 112.94 | P11:024:NPPD:GENTLM2G:2:757:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20702 | 112.75 | P13:345:OPPD:NEBCTY1G:::EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.207 | 112.78 | P13:345:OPPD:NEBCTY2G:::EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.77 | P22:345:OPPD:S3458 NEBCTY1G:LT::EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20702 | 112.75 | P22:345:OPPD:S3458 NEBCTY1G:::EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.81 | P22:345:OPPD:S3458 NEBCTY2G:LT::EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.207 | 112.78 | P22:345:OPPD:S3458 NEBCTY2G:::EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.77 | P23:345:OPPD:S3458 NEBCTY1G:LT::EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20702 | 112.75 | P23:345:OPPD:S3458 NEBCTY1G:::EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.81 | P23:345:OPPD:S3458 NEBCTY2G:LT::EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.207 | 112.78 | P23:345:OPPD:S3458 NEBCTY2G:::EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.4 | P12:115:SUNC:PLYMELL-PIERCEVILLE:::HV::
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20703 | 112.64 | P11:018:UMZB:# 5 #:: DCS IN SD. DEERCREEK_MV::
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20704 | 112.61 | P11:022:UMZB:# 15 #:: LO IN ND. LELAND OLDS 1_MV::
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20703 | 112.65 | P11:020:UMZB:# 16 #:: LO IN ND. LELAND OLDS 2_MV::
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20702 | 112.7 | P11:023:UMZB:# 31 #:: AVS IN ND. ANTELOPE VALLEY 1_MV::
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20702 | 112.7 | P11:023:UMZB:# 32 #:: AVS IN ND. ANTELOPE VALLEY 2_MV::
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20699 | 112.9 | P11:024:UMZB:# 33 #:: LRS IN WY. LARAMIE RIVER STATION 1_MV::
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.63 | P12:230:UMZW:# 687 #:: FT IN SD. FT-BG1 BRANCH FAULT:HV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.63 | P12:230:UMZW:# 3617 #:: FT IN SD. FT-BG2 BRANCH FAULT:HV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.63 | P12:230:UMZW:# 4038 #:: BG-FT IN SD. FAULT FOR TRANSMISSION CIRCUIT (BG-FT).:HV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.63 | P12:230:UMZW:# 4039 #:: BG-FT IN SD. FAULT FOR TRANSMISSION CIRCUIT (BG-FT).:HV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.61 | P13:230:UMZW:# 5135 #:: OA IN SD. FAULT ON TRANSFORMER (2).:HV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.61 | P13:230:UMZW:# 5136 #:: OA IN SD. FAULT ON TRANSFORMER (3).:HV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20702 | 112.42 | P21:345:UMZW:# 725 #:: GI IN NE. GI-SWEET BRANCH FAULT:EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20702 | 112.42 | P23:345:UMZW:# 2430 #:: GI IN NE. GI 1492 BKR FAULT:EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20702 | 112.42 | P23:345:UMZW:# 2438 #:: GI IN NE. GI-SWEET BRANCH FAULT & GI 1492 STUCK BKR:EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20707 | 112.37 | P11:138:WFEC:HUGO1:465MW :::
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20701 | 112.4 | P12:345:OKGE-AEPW:BKRBKR20::::
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.2074 | 112.75 | P12:345:OKGE:BKRBKR21::::
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20759 | 112.95 | P12:345:OKGE:BKRBKR24::::
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20947 | 114.47 | P12:345:OKGE-AEPW:BKRBKR25::::
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20695 | 112.42 | P12:345:OKGE:BKRBKR336::::
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20695 | 112.41 | P12:345:OKGE:BKRBKR336_2::::
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.2101 | 114.61 | P12:345:OKGE-AEPW:BKRBKR366::::
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.2101 | 114.58 | P12:345:OKGE-AEPW:BKRBKR366::::
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.2076 | 112.87 | P12:345:OKGE:BKRBKR367::::
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20736 | 112.62 | P12:345:OKGE-WFEC:BKRBKR374::::
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20663 | 112.22 | P12:345:OKGE:BKRBKR4193::::
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20663 | 112.22 | P12:345:OKGE:BKRBKR4194::::
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20647 | 112.28 | P12:345:OKGE-SPS:BKRBKR4201::::
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20647 | 112.28 | P12:345:OKGE-SPS:BKRBKR4202::::
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20694 | 112.35 | P12:345:OKGE:BKRBKR443NEW::::
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20694 | 112.35 | P12:345:OKGE:BKRBKR443NEW2::::
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20698 | 112.88 | P12:345:OKGE:BKRBKR604::::
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20698 | 112.94 | P12:345:OKGE:BKRBKR604_2::::
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20656 | 112.62 | P42:345:OKGE:SB_ARIA7381::::
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.21489 | 116.05 | P42:345:OKGE:SB_BVTY7387::::
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.2074 | 112.68 | P42:345:OKGE:SB_SPCK7383::::
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20703 | 112.64 | P11:115:SUNC:GARDENCITY_S2:103:531459(2):HV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20703 | 112.64 | P11:115:SUNC:FORTDDODGE_4:157:539670(4):HV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.62 | P11:345:599:CIMARRON1WIND:200:531603(1):EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.92 | P13:115:SUNC:HOLCOMB_GSU:::HV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20703 | 112.64 | P13:115:SUNC:S2_GSU:::HV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20703 | 112.64 | P13:115:SUNC:FORTDODGE_GSU:::HV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20703 | 112.62 | P23:345:SUNC:BU_BRK682:::EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.71 | 300003 1THLG3 24.0 301503 7THOMHLGSU3 345 3
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.71 | 300049 7THOMHL 345 301503 7THOMHLGSU3 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.66 | P11:20:AMMO:1LAB�� G1:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.66 | P11:20:AMMO:1LAB�� G2:2
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.83 | P11:345:AMMO::CALLAWAY:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.66 | P11:345:AMMO::LABADIE:3
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.66 | P11:345:AMMO::LABADIE:4
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.66 | P11:345:AMMO::RUSHISLAND:U1
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.66 | P11:345:AMMO::RUSHISLAND:U2
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.64 | P11:138:AMMO::SIOUX:2
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.64 | P12:765:AEP:AEP ROCKP-AEP JEFF 765
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.61 | P11:HV:EES::1ISES U1:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.61 | P11:EHV:EES::1ISES U2:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.42 | P11:HV:EES::PIRKEY 1:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.42 | P11:EHV:EES::WELSH3-1:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.39 | P11:HV:EES::TURKCOAL:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.61 | P12:HV:EES::5ISES%:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.61 | P12:EHV:EES::8ISES%:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.82 | P12:EHV:EES::7CALAWY 1:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20706 | 112.39 | P12:HV:EES::TURK 4%:1(1)
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.64 | 344011 7HUGHES 345 344012 7HPW-N 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.66 | 344884 7LABADIE1 345 344894 1LAB G1 20.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.66 | 344885 7LABADIE2 345 344895 1LAB G2 20.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.66 | 344886 7LABADIE3 345 344896 1LAB G3 20.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.66 | 344887 7LABADIE4 345 344897 1LAB G4 20.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.65 | 345667 7RUSH 1 345 345670 1RUSH G1 18.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.65 | 345668 7RUSH 2 345 345671 1RUSH G2 18.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.64 | 345755 4SIOUX 1 138 345756 1SIOUX 1 18.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.64 | 345764 4SIOUX 2 138 345765 1SIOUX 2 18.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.69 | P12:345:MDU::CENTER:COYOTE:1::::
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.69 | P13:345:MDU:COYOTE GSU LOSS:COYOTE::1::::
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.61 | P11:345:MEC:GDMEC CT1
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.61 | P11:345:MEC:GDMEC CT2
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.71 | P11:345:MEC:GDMEC ST
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.9 | P11:345:MEC-NPPD:COOPER 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.8 | P11:24:XEL:AUTO-SINGLE:SHERC31G:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.8 | P11:24:XEL:AUTO-SINGLE:SHERC32G:2
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.87 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.73 | P11:20:XEL:AUTO-SINGLE:PRIS31G:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.73 | P11:20:XEL:AUTO-SINGLE:PRIS32G:2
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.76 | P11:22:XEL:AUTO-SINGLE:MNTCE31G:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.73 | P11:20:XEL:AUTO-SINGLE:KING31G:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.77 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.77 | P11:22:GRE:AUTO-SINGLE:GRE-COAL42G:2
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.71 | P11:24:OTP:AUTO-SINGLE:BIGSTN1G:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.71 | P11:20:OTP:AUTO-SINGLE:CENTER2G:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.63 | P11:22:OTP:AUTO-SINGLE:CENTER1G:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.7 | P11:24:OTP:AUTO-SINGLE:COYOTE1G:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.63 | P11:24:DPC:AUTO-SINGLE:GENOA53G:3
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.61 | P12:115:XEL:AUTO-SINGLE:CHEMOLT7:LSPOWER7:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.65 | P12:115:XEL:AUTO-SINGLE:COLVILL7:CANONFLSG7:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.61 | P12:115:XEL:AUTO-SINGLE:FARIBALTP7:FARIBALTGEN:Z
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.7 | P12:230:OTP:AUTO-SINGLE:SQBUTTE4:YNG24:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.78 | P13:24-345:XEL:AUTO-SINGLE:SHERC31G:SHERCO3:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.78 | P13:24-345:XEL:AUTO-SINGLE:SHERC32G:SHERCO3:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.85 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.73 | P13:20-345:XEL:AUTO-SINGLE:PRIS31G:PRISLD3:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.73 | P13:20-345:XEL:AUTO-SINGLE:PRIS32G:PRISLD3:2
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.76 | P13:22-345:XEL:AUTO-SINGLE:MNTCE31G:MNTCELO3:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.72 | P13:20-345:XEL:AUTO-SINGLE:KING31G:ASKING3:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.76 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL41G:GRE-COALCR4:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.75 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL42G:GRE-COALCR4:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.7 | P13:230-24:OTP:AUTO-SINGLE:BIGSTON4:BIGSTN1G:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.7 | P13:20-230:OTP:AUTO-SINGLE:CENTER2G:YNG24:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.62 | P13:22-230:OTP:AUTO-SINGLE:CENTER1G:CENTER4:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.69 | P13:24-345:OTP:AUTO-SINGLE:COYOTE1G:COYOTE3:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.63 | P13:24-161:DPC:AUTO-SINGLE:GENOA53G:GENOA5:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.64 | P13:24-161:DPC:AUTO-SINGLE:JPM:ALMA5:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.7 | P11:115:XEL:RIV COMBINE CYCLE
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.62 | P12:115:XEL:BDS #2 5
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.62 | P11:115:XEL:HBR #6
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.62 | P11:115:XEL:HBR #7
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.73 | P11:115:XEL:HBR #6 7 8
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.73 | P23:345:XEL:8H14 PRI
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.73 | P23:345:XEL:8H17 PRI AS
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.85 | P23:345:XEL:8N28 SHC
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.78 | P23:345:XEL:8N22 SHC
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.78 | P23:345:XEL:8N17 SHC
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.77 | P23:345:XEL:8N8 MNN
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.72 | P23:345:XEL:8P1 KING
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.72 | P23:345:XEL:8P2 KING
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.62 | P23:115:XEL:5P147 IVH AS
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.61 | P11:18:ALTW:AUTO-SINGLE:EMERYST1:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.61 | P11:22:ALTW:AUTO-SINGLE:LANS54G:4
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.74 | P11:22:ALTW:AUTO-SINGLE:ARNOLD1G:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.77 | P11:24:ALTW:AUTO-SINGLE:OTTUMW1G:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.61 | P13:18-161:ALTW:AUTO-SINGLE:EMERYST1:EMERY5:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.61 | P13:22-161:ALTW:AUTO-SINGLE:LANS54G:LANSINGL15:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.73 | P13:22-161:ALTW:AUTO-SINGLE:ARNOLD1G:ARNOLD5:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.76 | P13:24-161:ALTW:AUTO-SINGLE:OTTUMW1G:OTTUMWA5:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.82 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.88 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.75 | P11:22:MEC:AUTO-SINGLE:NEAL3G:3
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.81 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.76 | P11:24:MEC:AUTO-SINGLE:LOUIS31G:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.81 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.84 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.74 | P13:345-22:MEC:AUTO-SINGLE:RAUN3:NEAL3G:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.8 | P13:345-24:MEC:AUTO-SINGLE:RAUN3:NEAL4G:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.74 | P13:345-24:MEC:AUTO-SINGLE:LOUISA3:LOUIS31G:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20701 | 112.78 | P11:230:WERE:JECU1_GEN::
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20701 | 112.78 | P11:345:WERE:JECU2_GEN::
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20701 | 112.78 | P11:345:WERE:JECU3_GEN::
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.95 | P11:345:WERE:WOLFU1_GEN::
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20706 | 112.63 | 511435 SNYDER-4 138 588779 TAP_G17-036 138 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20679 | 112.38 | 511446 CL-AFTP4 138 511458 ELKCTY-4 138 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20679 | 112.4 | 511446 CL-AFTP4 138 511463 HOB-JCT4 138 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20713 | 112.63 | 511453 DUNCAN-4 138 511552 DUNCHERTP4 138 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20713 | 112.62 | 511455 D.E.S.-4 138 511552 DUNCHERTP4 138 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20713 | 112.62 | 511455 D.E.S.-4 138 529344 OMDUNE-4 138 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.63 | 511456 O.K.U.-7 345 511565 OKLAUN HVDC7 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 111.6 | 511456 O.K.U.-7 345 588760 GEN-2017-033 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.21019 | 114.54 | 511456 O.K.U.-7 345 763215 G18-092-TAP 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.21033 | 115.11 | 511468 L.E.S.-7 345 762467 G18-015-TAP 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20927 | 114.48 | 511468 L.E.S.-7 345 763215 G18-092-TAP 345 2
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.29 | 511468 L.E.S.-7 345 763318 GEN-2018-115 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20706 | 112.66 | 511488 112GORE4 138 511510 LAIRGST4 138 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20717 | 112.7 | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20706 | 112.65 | 511500 CACHE4 138 511510 LAIRGST4 138 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20706 | 112.64 | 511500 CACHE4 138 588779 TAP_G17-036 138 2
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.2086 | 112.8 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.75 | 511541 SWEETWT6 230 763340 GEN-2018-117 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20224 | 109.9 | 511553 CHISHOLM7 345 523961 POTTER_CO 7 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20224 | 109.9 | 511553 CHISHOLM7 345 523961 POTTER_CO 7 345 2
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.21489 | 116.03 | 515375 WWRDEHV7 345 515458 BORDER 7 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.21489 | 116.05 | 515458 BORDER 7 345 560022 CRAWFISH_DR 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20702 | 112.7 | 515618 BALKOW 7 345 3WXFMR BALKOW 7 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20702 | 112.7 | 515618 BALKOW 7 345 3WXFMR BALKOW 7 1_Dup1
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20698 | 112.95 | 515634 PALDR1W7 345 3WXFMR PALO2 _1 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.7 | 515677 BADGER 7 345 563170 G15082_1 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20698 | 112.61 | 520827 BINGERJ4 138 521017 ONEY 4 138 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20698 | 112.62 | 521017 ONEY 4 138 521089 WASHITA4 138 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.61 | 522800 MU-TULIA 3 115 525179 TULIA_TP 3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.75 | 522892 MU-BROWNFLD2 69.0 526761 BROWNFLD_TP2 69.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.64 | 523090 TEXAS_CNTY 3 115 589380 GEN-2017-100 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.207 | 112.78 | 523093 HITCHLAND 3 115 523174 GOODWELLWND3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.95 | 523097 HITCHLAND 7 345 523112 NOVUS1 7 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 113 | 523097 HITCHLAND 7 345 523215 FREWHELCOL17 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20478 | 111.48 | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 113.05 | 523097 HITCHLAND 7 345 560252 G10-14 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.62 | 523099 TC-DRYTRLS 3 115 588480 A16-010_SUB 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.82 | 523112 NOVUS1 7 345 3WXFMR NOVUS XF2 2
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.63 | 523112 NOVUS1 7 345 3WXFMR XIANA2011198 _1 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20703 | 112.61 | 523118 BUFF_DUNES 7 345 523853 FINNEY 7 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.63 | 523120 COLE 3 115 588860 GEN-2017-047 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20703 | 112.64 | 523172 GWELL_COLL11 34.5 523174 GOODWELLWND3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20703 | 112.65 | 523173 GWELL_COLL21 34.5 523174 GOODWELLWND3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20723 | 112.61 | 523267 PRINGLE 6 230 3WXFMR ENRCO13617-1 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20723 | 112.61 | 523267 PRINGLE 6 230 523979 HARRNG_EST 6 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20792 | 113.07 | 523771 GRAPEVINE 6 230 524044 NICHOLS 6 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.21511 | 113.75 | 523959 POTTER_CO 6 230 524267 BUSHLAND 6 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.21476 | 114.67 | 523959 POTTER_CO 6 230 525461 NEWHART 6 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20929 | 118.42 | 523961 POTTER_CO 7 345 3WXFMR WAUK 90343-A 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20703 | 112.4 | 523978 HARRNG_MID 6 230 523979 HARRNG_EST 6 230 @1
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20704 | 112.39 | 524010 ROLLHILLS 6 230 3WXFMR WAUK WT01104 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20727 | 112.74 | 524267 BUSHLAND 6 230 3WXFMR WH 7001795 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.22157 | 114.31 | 524267 BUSHLAND 6 230 524623 DEAFSMITH 6 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20691 | 113.07 | 524296 SPNSPUR_WND7 345 524299 SPNSPUR_COL7 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20691 | 113.07 | 524299 SPNSPUR_COL7 345 3WXFMR SPNSPUR_COL7 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.21086 | 113.32 | 524415 AMA_SOUTH 6 230 525213 SWISHER 6 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 113.2 | 524502 NORTON 3 115 524509 FE-TUCMCARI3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20895 | 113.01 | 524575 DS-#25+ 3 115 524597 PANDAHFD 3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20895 | 113.12 | 524575 DS-#25+ 3 115 524630 TIERABLANCA3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.7 | 524604 HEREFRD_SB 2 69.0 524608 HERFRD_STH 2 69.0 *1
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.2201 | 119.12 | 524623 DEAFSMITH 6 230 760498 G17-146-TAP 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 113.1 | 524721 DS-#15&#19+2 69.0 524745 CASTRO_CNTY2 69.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20711 | 112.61 | 524770 PLSNT_HILL 6 230 3WXFMR EFAE1100068A 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.21135 | 117.92 | 524875 OASIS 6 230 524885 SN_JUAN_TAP6 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20779 | 113.69 | 524875 OASIS 6 230 524909 ROOSEVELT 6 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.21126 | 118.38 | 524885 SN_JUAN_TAP6 230 527483 CHAVES_CNTY6 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20721 | 112.8 | 524909 ROOSEVELT 6 230 3WXFMR ABB LMM60042 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.21401 | 118.36 | 524909 ROOSEVELT 6 230 525531 TOLK 6 230 2
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 113.33 | 524923 PORTALES 2 69.0 524929 RO-PORT_MTR2 69.0 @1
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 113 | 525001 W_MULESHOE 2 69.0 525008 MULESH_CTY 2 69.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 113 | 525008 MULESH_CTY 2 69.0 525027 BAILEYCO 2 69.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 113.28 | 525023 BC-BAIL_MTR2 69.0 525027 BAILEYCO 2 69.0 @1
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20807 | 113.27 | 525056 BC-EARTH 3 115 525480 PLANT_X 3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 113.09 | 525191 KRESS_INT 2 69.0 525203 SW-KRESS 2 69.0 Z1
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 113.17 | 525192 KRESS_INT 3 115 3WXFMR ENRCO 136155 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.21005 | 113.6 | 525213 SWISHER 6 230 525461 NEWHART 6 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.73 | 525272 KISER 3 115 3WXFMR VON 13819/1 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 113.19 | 525326 COX 3 115 3WXFMR ELCO 13474-3 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 113.21 | 525414 LAMTON 3 115 3WXFMR ASEA MLL9204 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20825 | 113.03 | 525440 LC-S_OLTON+3 115 525446 RKYFORD_TP 3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20825 | 113.03 | 525446 RKYFORD_TP 3 115 525480 PLANT_X 3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.2232 | 116.34 | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20984 | 114.35 | 525481 PLANT_X 6 230 3WXFMR WH ALM20171 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.2166 | 118.3 | 525481 PLANT_X 6 230 526435 SUNDOWN 6 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.2201 | 117.38 | 525481 PLANT_X 6 230 760498 G17-146-TAP 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.21052 | 113.07 | 525481 PLANT_X 6 230 762174 G17-218TAP 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.21094 | 113.14 | 525481 PLANT_X 6 230 762174 G17-218TAP 230 2
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.21867 | 118.38 | 525531 TOLK 6 230 525586 NEEDMORE 6 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20963 | 114.61 | 525531 TOLK 6 230 525637 LAMB_CNTY 6 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.23641 | 118.52 | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.21218 | 113.33 | 525531 TOLK 6 230 762174 G17-218TAP 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.21254 | 113.39 | 525531 TOLK 6 230 762174 G17-218TAP 230 2
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.33791 | 149.08 | 525549 TOLK 7 345 3WXFMR ABBXNL844501 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.21867 | 118.36 | 525586 NEEDMORE 6 230 526935 YOAKUM 6 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 113.01 | 525599 LC-SANDHLL+2 69.0 525606 AMHERST 2 69.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 113.04 | 525606 AMHERST 2 69.0 525613 W_LITTLFLD 2 69.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 113.07 | 525613 W_LITTLFLD 2 69.0 525635 LAMB_CNTY 2 69.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 113.02 | 525635 LAMB_CNTY 2 69.0 525650 LC-LTTLFLD+2 69.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20963 | 114.61 | 525637 LAMB_CNTY 6 230 3WXFMR WH ALM20172 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.87 | 525828 TUCO_INT 3 115 3WXFMR DS F78800913 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20714 | 112.4 | 525830 TUCO_INT 6 230 3WXFMR ENRCO 136401 2
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 113.07 | 526086 SW_6786_N 2 69.0 526087 SW_6786_S 2 69.0 Z1
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 113.07 | 526086 SW_6786_N 2 69.0 526102 SP-HETTLER 2 69.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 113.14 | 526087 SW_6786_S 2 69.0 526284 PLANTERS 2 69.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.69 | 526160 CARLISLE 3 115 3WXFMR WH RLP38371 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 113.03 | 526195 QUINCY 3 115 526196 SP-MILWAUKEE 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.93 | 526268 LUBBCK_STH 3 115 3WXFMR NA 70454A 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 113.19 | 526284 PLANTERS 2 69.0 526297 LUBBCK_EST 2 69.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.207 | 112.63 | 526435 SUNDOWN 6 230 3WXFMR UPDATE LATER _12 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20729 | 115 | 526435 SUNDOWN 6 230 526460 AMOCO_SS 6 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20702 | 112.65 | 526525 WOLFFORTH 6 230 3WXFMR UPDATE LATER _13 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 113.07 | 526735 TERRY_CNTY 2 69.0 526747 LG-BROWNFLD2 69.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 113 | 526747 LG-BROWNFLD2 69.0 526754 BROWNFIELD 2 69.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20694 | 114.41 | 526935 YOAKUM 6 230 527028 INK_BASIN 6 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20683 | 113.76 | 527028 INK_BASIN 6 230 527894 HOBBS_INT 6 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20699 | 113 | 527130 DENVER_N 3 115 527286 HIGGEAST 3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.61 | 527149 MUSTANG 6 230 3WXFMR ENRCO 136161 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20719 | 110.49 | 527149 MUSTANG 6 230 527151 GS-MUSTANG 6 230 @1
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.86 | 527202 SEAGRAVES 3 115 3WXFMR ABB MLL92408 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.76 | 527212 DIAMONDBACK3 115 3WXFMR HOW 36773714 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.68 | 527261 SULPHUR 2 69.0 527271 LG-FOSTER +2 69.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20699 | 112.98 | 527286 HIGGEAST 3 115 527363 HIGG 3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20702 | 112.82 | 527322 GAINES 3 115 527325 OXY_WSEM_TP3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20702 | 112.74 | 527325 OXY_WSEM_TP3 115 527362 JOHNSON_DRW3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.73 | 527340 DOSS 3 115 3WXFMR ELCO 13566/1 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.71 | 527345 LEGACY 2 69.0 527350 XTO_ROBRTSN2 69.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.71 | 527346 LEGACY 3 115 3WXFMR VROL 13735-1 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.69 | 527350 XTO_ROBRTSN2 69.0 527355 BOARDMAN 2 69.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.63 | 527355 BOARDMAN 2 69.0 527365 FLANNAGAN 2 69.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.61 | 527360 MAPCO 3 115 527362 JOHNSON_DRW3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.65 | 527362 JOHNSON_DRW3 115 528775 LE-ERF 3 115 @1
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20707 | 112.39 | 527455 RSWL_SLRCOL3 115 527482 CHAVES_CNTY3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20707 | 112.41 | 527470 CHVS_SLRCOL3 115 527464 CHVS_SOLAR11 34.5 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20707 | 112.34 | 527470 CHVS_SLRCOL3 115 527482 CHAVES_CNTY3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20887 | 112.88 | 527483 CHAVES_CNTY6 230 527799 EDDY_NORTH 6 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.62 | 527508 PRICE 3 115 527509 PRICE_TAP 3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.62 | 527529 RIACBRSH_TP3 115 527533 SW4J795_E 3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.62 | 527533 SW4J795_E 3 115 527564 ROSWLL_INT 3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.62 | 527563 ROSWLL_INT 2 69.0 527575 SW_4702 2 69.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20722 | 112.67 | 527564 ROSWLL_INT 3 115 527597 TWEEDY 3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.62 | 527575 SW_4702 2 69.0 527589 CV-ORCHARD 2 69.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.207 | 112.78 | 527653 MILO_WIND 1 34.5 527655 RSVLT_CC_E 7 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20692 | 112.66 | 527654 RSVLT_CC_W 7 345 527655 RSVLT_CC_E 7 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20692 | 112.95 | 527654 RSVLT_CC_W 7 345 527666 RSVLT_COL1 7 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20687 | 112.86 | 527655 RSVLT_CC_E 7 345 527656 CROSSROADS 7 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20692 | 112.95 | 527666 RSVLT_COL1 7 345 3WXFMR RSVLT_COL1 7 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.36 | 527736 NAVAJO_5TP 3 115 527739 NAVAJO_4 3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20704 | 112.35 | 527864 CUNNINHAM 3 115 528348 BUCKEYE_TP 3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20704 | 112.63 | 527864 CUNNINHAM 3 115 528568 MONUMNT_TP 3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20688 | 112.91 | 527865 CUNNIGHM_N 6 230 527867 CUNNIGHM_S 6 230 *1
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20699 | 112.64 | 527865 CUNNIGHM_N 6 230 527963 POTASH_JCT 6 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20704 | 112.4 | 527867 CUNNIGHM_S 6 230 3WXFMR WH 7000266 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.207 | 112.86 | 527867 CUNNIGHM_S 6 230 527882 CUNINGHAM2 1 20.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20701 | 112.79 | 527894 HOBBS_INT 6 230 527903 HOBBS_PLT3 1 18.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20704 | 112.36 | 527965 KIOWA 7 345 528027 RDRUNNER 7 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.36 | 528015 PHANTOM 7 345 528027 RDRUNNER 7 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.41 | 528024 RR_SVC_HV 3 115 528021 RDRUNNR_SVC1 15.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.68 | 528025 RDRUNNER 3 115 587990 GEN-2016-121 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.42 | 528185 N_LOVING 7 345 3WXFMR HYO1063400-1 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20704 | 112.41 | 528185 N_LOVING 7 345 528223 CHINA_DRAW 7 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.36 | 528222 CHINA_DRAW 3 115 528225 CD_SVC_HV 3 115 Z1
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20703 | 112.34 | 528333 LE-WEST_SUB3 115 528334 LE-NRTH_INT3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20704 | 112.42 | 528341 LE-SANANDRS3 115 528627 LE-TXACO_TP3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20704 | 112.38 | 528348 BUCKEYE_TP 3 115 528627 LE-TXACO_TP3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20701 | 112.62 | 528394 QUAHADA 3 115 528396 XTO_BIGEDDY3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20704 | 112.33 | 528463 SANGER_SW 3 115 528575 OXYPERMIAN 3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20704 | 112.33 | 528463 SANGER_SW 3 115 762442 G18-004-TAP 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20704 | 112.63 | 528568 MONUMNT_TP 3 115 528581 BYRD_TP 3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20704 | 112.38 | 528574 OXY_NHU_RCF3 115 528575 OXYPERMIAN 3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.69 | 528617 LE-WAITS 2 69.0 528325 LE-WAITS 3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.61 | 528617 LE-WAITS 2 69.0 528714 LE-FORT_SW 2 69.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20704 | 112.42 | 528622 LE-SANANDRS2 69.0 528341 LE-SANANDRS3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.97 | 528626 LE-PLNSINT 2 69.0 526928 PLAINS_INT 3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.97 | 528626 LE-PLNSINT 2 69.0 528709 LE-PLNSGOAB2 69.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.63 | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.69 | 528669 LE-STKLDRTP2 69.0 528740 LE-PLANS_SW2 69.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.85 | 528709 LE-PLNSGOAB2 69.0 528740 LE-PLANS_SW2 69.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.63 | 528709 LE-PLNSGOAB2 69.0 528747 LE-ALLRED 2 69.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.61 | 528714 LE-FORT_SW 2 69.0 528718 LE-NEWTEX 2 69.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.69 | 528735 LE-PLAINSUB2 69.0 528740 LE-PLANS_SW2 69.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20694 | 112.41 | 530583 POSTROCK7 345 588654 G17-021-TAP 345 2
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.41 | 531213 SANTAFE3 115 531408 PIERCVL3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20674 | 112.33 | 531451 MINGO 7 345 531465 SETAB 7 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20703 | 112.62 | 531501 BUCKNER7 345 531502 CIMRRN 7 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20703 | 112.62 | 531502 CIMRRN 7 345 531503 CIMRRN 1 34.5 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20691 | 112.32 | 531510 HARBNGR3 115 3WXFMR HARBGR345 _1 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20703 | 112.64 | 532663 LEC U5 24.0 532854 LEC U5 6 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20703 | 112.64 | 532853 LAWHILL6 230 532854 LEC U5 6 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20704 | 112.69 | 542951 HAW G5 1 22.0 543665 HAWTHN5 161 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20703 | 112.74 | 542955 LAC G1 1 22.0 542981 LACYGNE7 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20703 | 112.72 | 542956 LAC G2 1 24.0 542981 LACYGNE7 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20702 | 112.76 | 542957 IAT G1 1 24.0 542982 IATAN 7 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20703 | 112.82 | 542962 IAT G2 1 24.5 542982 IATAN 7 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20704 | 112.61 | 542966 WGARDNR5 161 543105 BULLCRK5 161 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20959 | 112.16 | 560022 CRAWFISH_DR 345 762216 G17-151TAP 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20926 | 113.18 | 560022 CRAWFISH_DR 345 762467 G18-015-TAP 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 108.98 | 560022 CRAWFISH_DR 345 763087 GEN-2018-073 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.21041 | 113.55 | 560022 CRAWFISH_DR 345 763215 G18-092-TAP 345 2
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 113.05 | 560252 G10-14 345 560253 G10-14-1 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.78 | 560253 G10-14-1 115 560254 G10-14-SUB1 34.5 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.78 | 560253 G10-14-1 115 560255 G10-14-SUB2 34.5 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.63 | 560581 G06-44-2 34.5 523111 NOVUS1 3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.68 | 560582 G06-44-3 34.5 560577 G06-44 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.66 | 560583 G06-44-4 34.5 560577 G06-44 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.32 | 560757 ASGI13_02_1 69.0 560758 ASGI13_02_2 34.5 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.32 | 560757 ASGI13_02_1 69.0 562731 WHEATLAND 69.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.33 | 560763 ASGI13_03_1 115 560761 ASGI13_03_2 34.5 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.76 | 562015 FIREWHEEL1 34.5 523215 FREWHELCOL17 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.76 | 562016 FIREWHEEL2 34.5 523215 FREWHELCOL17 345 2
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.31 | 562323 AGI1202&1305 115 562324 AGI1202&1305 34.5 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.32 | 562727 LESBIA 115 562728 SANJONTAP 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.32 | 562728 SANJONTAP 115 562729 CAPROCKTAP1 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.32 | 562730 CAPROCKTAP2 69.0 562729 CAPROCKTAP1 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.32 | 562730 CAPROCKTAP2 69.0 562731 WHEATLAND 69.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.72 | 563171 G15082_2 34.5 563170 G15082_1 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.4 | P11:13.8:AEPW:COM1-1
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.41 | P11:13.8:AEPW:COM2-1
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.41 | P11:13.8:AEPW:COM3-1
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.42 | P11:18:AEPW:WELSH1-1
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.42 | P11:18:AEPW:WELSH3-1
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.42 | P11:24:AEPW:PIRKEY 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.39 | P11:24:AEPW:SWS3-1
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.39 | P11:24:AEPW:TURKCOAL
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20717 | 112.7 | P12:138:AEPW-OMPA:DUNCAN-4:OMDUNCN4
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20706 | 112.66 | P12:138:AEPW:112GORE4:SNYDER-4
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20706 | 112.66 | 5841_Dup1
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20714 | 111.96 | 584560 GEN-2015-014 115 584561 G15-014XFMR1 34.5 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20713 | 112.65 | P12:138:AEPW:SANTAFE:DUNCAN-4
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.68 | 587991 G16-121XFMR1 34.5 587990 GEN-2016-121 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.62 | 588480 A16-010_SUB 115 3WXFMR A16-010_SUB 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20717 | 112.7 | P12:138:AEPW:DUNCAN-4:L.E.S.-4
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.06 | 588761 G17-033XFMR1 34.5 588760 GEN-2017-033 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.06 | 588765 G17-033XFMR2 34.5 588760 GEN-2017-033 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.63 | 588861 G17-047XFMR1 34.5 588860 GEN-2017-047 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20667 | 112.2 | P12:138:AEPW:ELKCTY-4:CLINTJC4
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.64 | 589381 G17-100XFMR1 34.5 589380 GEN-2017-100 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20679 | 112.39 | P12:138:AEPW:HOB-JCT4:ELKCTY-4
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.64 | P12:138:AEPW:SHERID4:112GORE4
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20703 | 112.61 | P12:230:AEPW:SWEETWT6:BUFFCK6
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20702 | 112.66 | P12:230:AEPW:SWEETWT6:ROARK6
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20947 | 114.5 | P12:345:AEPW:L.E.S7:TERRYRD7
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20947 | 114.49 | P12:345:AEPW:L.E.S7:TERRYRD7
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20947 | 114.47 | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.2101 | 114.61 | P12:345:AEPW-OKGE:L.E.S.-7:GRACMNT7
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.2101 | 114.58 | P12:345:AEPW-OKGE:L.E.S.-7:GRACMNT7
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20701 | 112.4 | P12:345:AEPW-OKGE:PITTSB-7:SEMINOL7
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.21019 | 115.66 | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.66 | P22:345:AMMO::LABADIE:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.66 | P22:345:AMMO::LABADIE:2
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.66 | P22:345:AMMO::LABADIE:3
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.66 | P22:345:AMMO::LABADIE:4
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.65 | P22:345:AMMO::RUSHISLAND:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.64 | P22:345:AMMO::RUSHISLAND:2
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20706 | 112.41 | P13:138-13.8:AEPW:COMANC-4_#2
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.2053 | 111.28 | P13:138-230:AEPW:ELKCTY-4
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20707 | 112.4 | P13:138-24:AEPW:S.W.S.-4
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20706 | 112.39 | P13:138-24:AEPW:TURK 4
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20713 | 112.63 | P13:138-345:AEPW:L.E.S.-4_#1
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20722 | 112.75 | P13:138-345:AEPW:L.E.S.-4_#2
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20706 | 112.67 | P23:500:EES-EAI:KEO:B4941
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20706 | 112.66 | P23:500:EES-EAI:KEO:B4921
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.61 | P11:26:EES-EAI:INDEP2:1:D401
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.61 | P11:26:EES-EAI:INDEP2:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.61 | P13:500:EES-EAI:INDEP2:MT2
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.65 | P23:500:EES-EAI:INDEP2:B6126
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.64 | P23:500:EES-EAI:PD:INDEP2:LN:FK479
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20703 | 112.61 | P13:230-34.5:AEPW:BUFFCK6
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20702 | 112.67 | P13:230-34.5:AEPW:ROARK6
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.41 | P13:69-13.8:AEPW:COMANC-2
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.66 | P11:024:DPC:ALMA2:6
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.62 | P11:18:ITCM:EMERYGT1:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.63 | P11:18:ITCM:EMERYGT2:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.63 | P11:161:ITCM:MGS CT1:1C
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.63 | P11:161:ITCM:MGS CT2:2C
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20703 | 112.64 | 652537 WHITE 3 345 659286 DEERCREK-BE3 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20703 | 112.64 | 659286 DEERCREK-BE3 345 3WXFMR DEERCRK KU1A 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.63 | 672601 BD 4 230 672306 BD 6G 18.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.63 | 672610 POPLAR 4 230 672310 POPLAR 1G 18.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.63 | 672610 POPLAR 4 230 672311 POPLAR 2G 18.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.62 | 672621 SHAND 4 230 672321 SHAND 1G 18.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.61 | 672649 CODETTE 4 230 672650 NIPAWIN 4 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.62 | 672696 BRADA 4 230 672699 NBEC 4 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.69 | P23:345:MDU::COYOTE::5707-5712-5715::::
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.84 | P23:345:MEC:CBEC 905
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.81 | P23:345:MEC:CBEC 908
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.64 | P23:345:MEC:GDMEC 908
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.74 | P23:345:MEC:RAUN 0180
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.8 | P23:345:MEC:RAUN 0210
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.75 | P23:345:MEC:LOUISA 954
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.75 | P23:345:MEC:LOUISA 964
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.61 | P21:115:XEL:AUTO-SINGLE:CHEMOLT7:LSPOWER7:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.65 | P21:115:XEL:AUTO-SINGLE:COLVILL7:CANONFLSG7:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.61 | P21:115:XEL:AUTO-SINGLE:FARIBALTP7:FARIBALTGEN:Z
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.7 | P21:230:OTP:AUTO-SINGLE:SQBUTTE4:YNG24:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.69 | P23:345:OTP:CENTER 3:3215(1)
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.69 | P23:345:OTP:CENTER 3:3225(1)
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.63 | P12:230:UMZW:# 687 #: FT IN SD. FT-BG1 LINE FAULT
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.63 | P12:230:UMZW:# 3617 #: FT IN SD. FT-BG2 LINE FAULT
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 111.33 | 760494 GEN-2017-146 230 760498 G17-146-TAP 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 111.32 | 760495 G17-146-XFM1 34.5 760494 GEN-2017-146 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.05 | 761356 G17-239-XFMR 34.5 761355 GEN-2017-239 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.05 | 761359 G17-239-XFMR 34.5 761355 GEN-2017-239 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.23 | 761797 G17-187XFM1 34.5 761796 GEN-2017-187 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.23 | 761800 G17-187XFM2 34.5 761796 GEN-2017-187 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 107.16 | 762132 GEN-2017-158 230 763252 G18-099-XFM1 34.5 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 107.16 | 762132 GEN-2017-158 230 763255 G18-099-XFM2 34.5 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 107.74 | 762133 G17-158XFM1 34.5 762132 GEN-2017-158 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 107.74 | 762136 G17-158XFM2 34.5 762132 GEN-2017-158 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 109.9 | 762216 G17-151TAP 345 762217 GEN-2017-151 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20959 | 113.55 | 762216 G17-151TAP 345 762467 G18-015-TAP 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 111.85 | 762218 G17-151XFM1 34.5 762217 GEN-2017-151 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 111.85 | 762221 G17-151XFM2 34.5 762217 GEN-2017-151 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 111.85 | 762224 G17-151XFM3 34.5 762217 GEN-2017-151 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 111.85 | 762227 G17-151XFM4 34.5 762217 GEN-2017-151 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.36 | 762438 GEN-2018-004 115 762442 G18-004-TAP 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 110.89 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 111.7 | 762461 G18-015-XFM1 34.5 762460 GEN-2018-015 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 111.7 | 762464 G18-015-XFM2 34.5 762460 GEN-2018-015 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20843 | 113.07 | 762467 G18-015-TAP 345 763215 G18-092-TAP 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 110.18 | 763087 GEN-2018-073 345 763088 G18-073-XFM1 34.5 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 111.33 | 763087 GEN-2018-073 345 763091 G18-073-XFM2 34.5 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 107.16 | 763120 GEN-2018-081 230 763121 G18-081-XFM1 34.5 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 109.42 | 763120 GEN-2018-081 230 764011 G19-074-XFM1 34.5 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 109.44 | 763186 GEN-2018-089 230 763187 G18-089-XFM1 34.5 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 110.21 | 763208 GEN-2018-092 345 763215 G18-092-TAP 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 111.37 | 763208 GEN-2018-092 345 763220 G18-092-XFM1 34.5 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 111.37 | 763208 GEN-2018-092 345 763223 G18-092-XFM2 34.5 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 108.87 | 763241 GEN-2018-097 230 763242 G18-097-XFM1 34.5 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 109.78 | 763241 GEN-2018-097 230 763296 G18-111-XFM1 34.5 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 109.14 | 763241 GEN-2018-097 230 763307 G18-112-XFM1 34.5 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 109.14 | 763241 GEN-2018-097 230 763310 G18-112-XFM2 34.5 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 108.87 | 763241 GEN-2018-097 230 763395 G18-124-XFM1 34.5 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 108.87 | 763241 GEN-2018-097 230 763398 G18-124-XFM2 34.5 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.29 | 763318 GEN-2018-115 345 763319 G18-115-XFM1 34.5 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.75 | 763340 GEN-2018-117 230 763341 G18-117-XFM1 34.5 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 108.51 | 763483 GEN-2019-003 230 763484 G19-003-XFM1 34.5 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 111.19 | 763483 GEN-2019-003 230 763605 G19-021-XFM1 34.5 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 111.9 | 763516 GEN-2019-011 345 763517 G19-011-XFM1 34.5 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.26 | 763879 GEN-2019-056 115 763880 G19-056XFM1 34.5 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20655 | 112.68 | P42:345:OKGE:SB_BVTY7305
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20697 | 112.43 | P23:345:WERE:BUFF_345-534::
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20697 | 112.43 | P23:345:WERE:BUFF_345-543::
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20701 | 112.78 | P23:345:WERE:JEC_345-15::
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.207 | 112.75 | P23:345:WERE:JEC_345-16::
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20701 | 112.78 | P23:345:WERE:JEC_345-19::
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20701 | 112.78 | P23:345:WERE:JEC_345-20::
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.95 | P23:345:WERE:WOLF_345-50::
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.95 | P23:345:WERE:WOLF_345-60::
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20706 | 112.43 | P42:345:AEPW:WELSH CB 10620 NBTB+FAULT
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.21019 | 114.21 | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.21043 | 114.99 | P42:345:AEPW:LAWTON EASTSIDE CB 3413A NBTB+FAULT
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.21079 | 115.4 | P42:345:AEPW:LAWTON EASTSIDE CB 3425A NBTB+FAULT
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.21033 | 115.86 | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20719 | 112.31 | P42:345:AEPW:PITTSBURG CB 3441A NBTB+FAULT
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20701 | 112.4 | P42:345:AEPW:PITTSBURG CB 3445A NBTB+FAULT
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20947 | 114.49 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20947 | 114.49 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20947 | 114.47 | P42:345:AEPW:TERRYRD_CB_3421A_NBTB
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20703 | 112.75 | P23:345:KCPL:LACYGNE_R2-5::LACYGU2-LACYGNE-STILWELL
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20706 | 112.43 | P23:345:AEPW:WELSH CB 10620 NBTB
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.21019 | 114.54 | P23:345:AEPW:OKLAUNION CB 3401A NBTB
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.21043 | 114.99 | P23:345:AEPW:LAWTON EASTSIDE CB 3413A NBTB
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.21079 | 115.4 | P23:345:AEPW:LAWTON EASTSIDE CB 3425A NBTB
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.21033 | 115.86 | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20719 | 112.31 | P23:345:AEPW:PITTSBURG CB 3441A NBTB
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20701 | 112.4 | P23:345:AEPW:PITTSBURG CB 3445A NBTB
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20947 | 114.49 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20947 | 114.49 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20947 | 114.47 | P23:345:AEPW:TERRYRD_CB_3421A_NBTB
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20736 | 112.62 | P12:138:AEPW:S.W.S.-4:L.E.S.-4
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.65 | P11:115:SUNC:GARDENCITY_S2:97:531459(2)
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20966 | 114.72 | P23:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.21223 | 117.32 | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20966 | 114.72 | P42:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB+FAULT
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.21223 | 117.32 | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20674 | 112.33 | P23:345:SUNC:MO_BRK182
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20674 | 112.33 | P23:345:SUNC:MO_BRK382
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20702 | 112.42 | P21:345:UMZW:# 725 #: GI IN NE. GI-SWEET LINE FAULT
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.2086 | 112.8 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20706 | 112.41 | P12:138-13.8:AEPW:COMANC-4_#1
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.2053 | 111.26 | P12:230:AEPW:ELKCITY6:CHISHOLM6
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20849 | 113.54 | P12:230:AEPW:SWEETWT6:CHISHOLM6
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997715 ABBXNL844501 230 1 |  | 553 | 0.33791 | 150.96 | 525531 TOLK 6 230 3WXFMR TOLK 6 2
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20706 | 112.73 | P23:345:KCPL-WERE:237LACYGNE_R1-6::LACYGU1-LACYGNE-NEOSHO
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20703 | 112.64 | P11:230:WERE:LECU5_GEN::
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20704 | 112.63 | P11:161:GMO:DOGWOOD_COMBINED_CYCLE_UNIT_OUTAGE_1_1
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.2071 | 111.16 | P11:115:SPS:MUSTANG1&3:153MW::::
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20963 | 114.61 | P12:230:SPS:K37::1_TOLK_LAMB:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20723 | 112.61 | P12:230:SPS:K43::1_PRNGLE_HARR_E:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20707 | 112.37 | P12:230:SPS:K44::1_EPLNT_HARRW:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20718 | 112.79 | P12:115:SPS:T04::1_TRBLNC_CASTRO:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20704 | 112.19 | P12:115:SPS:T13::1_TAYLOR_WHOBBS:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20704 | 112.31 | P12:115:SPS:T14::1_MADDOX_TAYLOR:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 113.09 | P12:115:SPS:T21::1_GRSSLND_GRAHAM:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20704 | 112.41 | P12:115:SPS:T23::1_PCA_POTJCT:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.62 | P12:115:SPS:T24B::1_RSWLL_BRSHRF:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.64 | P12:115:SPS:T26::1_CHAVES_RSWLCTY:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20825 | 113.18 | P12:115:SPS:T28A::1_LAMTON_PLANTX:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20749 | 112.67 | P12:115:SPS:T29::1_LAMTON_HALECTR:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20876 | 113.96 | P12:115:SPS:T30::1_LAMB_HOCKLY:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20876 | 113.13 | P12:115:SPS:T31::1_HOCKLY_SUNDWN:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.207 | 112.63 | P12:115:SPS:T35::1_TERRY_YOAKUM:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 113.32 | P12:115:SPS:T45::1_NORRIS_OASIS:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20703 | 112.4 | P12:115:SPS:T57::1_MUSTG_SEGRVS:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20831 | 113.15 | P12:115:SPS:T59::1_CARGIL_CURRY:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.208 | 112.42 | P12:115:SPS:T66::1_RNDALL_HAPPY:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.208 | 112.9 | P12:115:SPS:T67::1_HAPPY_KRESS:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20709 | 112.39 | P12:115:SPS:T68::1_TUCO_FLOYD:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20699 | 113.2 | P12:115:SPS:T71::1_CRLSLE_YUMA:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20713 | 112.7 | P12:115:SPS:T81::1_COX_FLOYD:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20704 | 112.85 | P12:115:SPS:T83::1_SP-FKFD_ALLEN:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20699 | 113.01 | P12:115:SPS:T89::1_DC_N_HIGG:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.66 | P12:115:SPS:T91::1_HIGG_RUSSELL:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20727 | 112.62 | P12:115:SPS:V04::1_EPLANT_RNDALL:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20718 | 112.67 | P12:115:SPS:V07::1_COX_HALECTR:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20817 | 112.95 | P12:115:SPS:V09::1_HALECTR_PLANTX:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20703 | 112.83 | P12:115:SPS:V12::1_PLANTX_BAILEY:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20704 | 112.62 | P12:115:SPS:V15::1_TUCO_INDANA:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20667 | 112.67 | P12:115:SPS:V24::1_WOLFTH_TERRY:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20722 | 112.64 | P12:115:SPS:V26::1_RSWLL_EDDY_N:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.98 | P12:115:SPS:V33::1_LUBBS_LYNN:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20807 | 113.85 | P12:115:SPS:V37::1_CASTRO_PLANTX:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.75 | P12:115:SPS:V46::1_ALLEN_WHEELCK:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20706 | 113.09 | P12:115:SPS:V49::1_YOAKUM_SHLCO2:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20748 | 113.26 | P12:115:SPS:V55::1_SUNDWN_TERRY:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20718 | 113.09 | P12:115:SPS:V56::1_COCHRAN_SUNDWN:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20704 | 112.68 | P12:115:SPS:V62::1_CRLSLE_INDANA:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20706 | 112.62 | P12:115:SPS:V70::1_S_GORG_RNDALL:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20717 | 112.65 | P12:115:SPS:V78::2_CURRY_RSVLT:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20703 | 112.79 | P12:115:SPS:V81::1_LE-WAIT_LE-LVN:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.65 | P12:115:SPS:V95::1_DC_N_SHLCO2:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.61 | P12:115:SPS:W11::1_DC_S_SMINLE:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20704 | 112.61 | P12:115:SPS:W12::1_SMINLE_DOSS:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20704 | 112.68 | P12:115:SPS:W14::1_SMINLE_GAINES:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 113.14 | P12:115:SPS:W32::1_PRMTR_FE-CLSIN:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.61 | P12:115:SPS:W34::1_JNSDRW_MAPCO:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20702 | 112.85 | P12:115:SPS:W35::1_GAINES_JNSDRW:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20699 | 112.64 | P12:115:SPS:W36::1_TAYLOR_JNSDRW:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20895 | 113.15 | P12:115:SPS:W40::1_WCANYON_TRBLNC:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20732 | 112.71 | P12:115:SPS:W52::1_NEWHART_KRESS:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 113.2 | P12:115:SPS:W58::1_NORTON_LOPEZ:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.82 | P12:115:SPS:W59::1_LOPEZ_CMPBLL:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20706 | 113.15 | P12:115:SPS:W62::1_PLSTHL_CURRY:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20717 | 112.62 | P12:115:SPS:W63::1_PLSTHL_CURRY:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.96 | P12:115:SPS:W64::1_PLSTHL_FE-CLV:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20706 | 113.12 | P12:115:SPS:W65::1_PLSTHL_CURRY:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.81 | P12:115:SPS:W66::1_PORTA_GREYHUND:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20895 | 112.61 | P12:115:SPS:W77::1_RNDAL_WCANYON:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.64 | P12:115:SPS:W99::1_CAPITAN_CHAVES:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.207 | 113.08 | P12:115:SPS:U14::1_DC_STH_INKBSN:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20703 | 113.02 | P12:115:SPS:V15::1_INKBSN_LE-WAT:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20727 | 112.74 | P12:115:SPS:U16::1_BSHLND_OUTPST:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20727 | 112.73 | P12:115:SPS:U17::1_COLTR_OUTPST:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20711 | 112.8 | P12:115:SPS:U19::1_DEAN_PLAINS:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20727 | 112.67 | P12:115:SPS:U23::1_COLTR_HILSDE:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20704 | 112.62 | P11:18:HAST:::EGYCTR2G WEC2_LOSS OF WEC 2 GEN_:HV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20704 | 112.62 | P13:18-115:HAST:::EGYCNTR7 XFMR G2WEC 2 GSU_:HV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20704 | 112.63 | P11:161:GMO:DOGWOOD-COMBINED-CYCLE-UNIT-OUTA:::HV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20706 | 112.73 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20703 | 112.75 | P23:345:KCPL:LACYGNE-R2-5:::EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20701 | 112.78 | P11:230:WERE:JECU1-GEN:::HV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20703 | 112.64 | P11:230:WERE:LECU5-GEN:::HV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20701 | 112.78 | P11:345:WERE:JECU2-GEN:::EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20701 | 112.78 | P11:345:WERE:JECU3-GEN:::EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.95 | P11:345:WERE:WOLFU1-GEN:::EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20697 | 112.43 | P23:345:WERE:BUFF-345-534:::EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20697 | 112.43 | P23:345:WERE:BUFF-345-543:::EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20701 | 112.78 | P23:345:WERE:JEC-345-15:::EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.207 | 112.75 | P23:345:WERE:JEC-345-16:::EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20701 | 112.78 | P23:345:WERE:JEC-345-19:::EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20701 | 112.78 | P23:345:WERE:JEC-345-20:::EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.95 | P23:345:WERE:WOLF-345-50:::EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.95 | P23:345:WERE:WOLF-345-60:::EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.89 | P11:022:NPPD:COOPER1G:1:983:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.207 | 112.92 | P11:023:NPPD:GENTLM1G:1:757:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.207 | 112.94 | P11:024:NPPD:GENTLM2G:2:757:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20702 | 112.75 | P13:345:OPPD:NEBCTY1G:::EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.207 | 112.78 | P13:345:OPPD:NEBCTY2G:::EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.77 | P22:345:OPPD:S3458 NEBCTY1G:LT::EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20702 | 112.75 | P22:345:OPPD:S3458 NEBCTY1G:::EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.81 | P22:345:OPPD:S3458 NEBCTY2G:LT::EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.207 | 112.78 | P22:345:OPPD:S3458 NEBCTY2G:::EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.77 | P23:345:OPPD:S3458 NEBCTY1G:LT::EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20702 | 112.75 | P23:345:OPPD:S3458 NEBCTY1G:::EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.81 | P23:345:OPPD:S3458 NEBCTY2G:LT::EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.207 | 112.78 | P23:345:OPPD:S3458 NEBCTY2G:::EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.4 | P12:115:SUNC:PLYMELL-PIERCEVILLE:::HV::
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20703 | 112.64 | P11:018:UMZB:# 5 #:: DCS IN SD. DEERCREEK_MV::
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20704 | 112.61 | P11:022:UMZB:# 15 #:: LO IN ND. LELAND OLDS 1_MV::
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20703 | 112.65 | P11:020:UMZB:# 16 #:: LO IN ND. LELAND OLDS 2_MV::
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20702 | 112.7 | P11:023:UMZB:# 31 #:: AVS IN ND. ANTELOPE VALLEY 1_MV::
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20702 | 112.7 | P11:023:UMZB:# 32 #:: AVS IN ND. ANTELOPE VALLEY 2_MV::
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20699 | 112.9 | P11:024:UMZB:# 33 #:: LRS IN WY. LARAMIE RIVER STATION 1_MV::
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.63 | P12:230:UMZW:# 687 #:: FT IN SD. FT-BG1 BRANCH FAULT:HV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.63 | P12:230:UMZW:# 3617 #:: FT IN SD. FT-BG2 BRANCH FAULT:HV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.63 | P12:230:UMZW:# 4038 #:: BG-FT IN SD. FAULT FOR TRANSMISSION CIRCUIT (BG-FT).:HV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.63 | P12:230:UMZW:# 4039 #:: BG-FT IN SD. FAULT FOR TRANSMISSION CIRCUIT (BG-FT).:HV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.61 | P13:230:UMZW:# 5135 #:: OA IN SD. FAULT ON TRANSFORMER (2).:HV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.61 | P13:230:UMZW:# 5136 #:: OA IN SD. FAULT ON TRANSFORMER (3).:HV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20702 | 112.42 | P21:345:UMZW:# 725 #:: GI IN NE. GI-SWEET BRANCH FAULT:EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20702 | 112.42 | P23:345:UMZW:# 2430 #:: GI IN NE. GI 1492 BKR FAULT:EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20702 | 112.42 | P23:345:UMZW:# 2438 #:: GI IN NE. GI-SWEET BRANCH FAULT & GI 1492 STUCK BKR:EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20707 | 112.37 | P11:138:WFEC:HUGO1:465MW :::
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20701 | 112.4 | P12:345:OKGE-AEPW:BKRBKR20::::
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.2074 | 112.75 | P12:345:OKGE:BKRBKR21::::
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20759 | 112.95 | P12:345:OKGE:BKRBKR24::::
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20947 | 114.47 | P12:345:OKGE-AEPW:BKRBKR25::::
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20695 | 112.42 | P12:345:OKGE:BKRBKR336::::
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20695 | 112.41 | P12:345:OKGE:BKRBKR336_2::::
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.2101 | 114.61 | P12:345:OKGE-AEPW:BKRBKR366::::
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.2101 | 114.58 | P12:345:OKGE-AEPW:BKRBKR366::::
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.2076 | 112.87 | P12:345:OKGE:BKRBKR367::::
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20736 | 112.62 | P12:345:OKGE-WFEC:BKRBKR374::::
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20663 | 112.22 | P12:345:OKGE:BKRBKR4193::::
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20663 | 112.22 | P12:345:OKGE:BKRBKR4194::::
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20647 | 112.28 | P12:345:OKGE-SPS:BKRBKR4201::::
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20647 | 112.28 | P12:345:OKGE-SPS:BKRBKR4202::::
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20694 | 112.35 | P12:345:OKGE:BKRBKR443NEW::::
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20694 | 112.35 | P12:345:OKGE:BKRBKR443NEW2::::
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20698 | 112.88 | P12:345:OKGE:BKRBKR604::::
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20698 | 112.94 | P12:345:OKGE:BKRBKR604_2::::
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20656 | 112.62 | P42:345:OKGE:SB_ARIA7381::::
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.21489 | 116.05 | P42:345:OKGE:SB_BVTY7387::::
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.2074 | 112.68 | P42:345:OKGE:SB_SPCK7383::::
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20703 | 112.64 | P11:115:SUNC:GARDENCITY_S2:103:531459(2):HV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20703 | 112.64 | P11:115:SUNC:FORTDDODGE_4:157:539670(4):HV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.62 | P11:345:599:CIMARRON1WIND:200:531603(1):EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.92 | P13:115:SUNC:HOLCOMB_GSU:::HV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20703 | 112.64 | P13:115:SUNC:S2_GSU:::HV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20703 | 112.64 | P13:115:SUNC:FORTDODGE_GSU:::HV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20703 | 112.62 | P23:345:SUNC:BU_BRK682:::EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.71 | 300003 1THLG3 24.0 301503 7THOMHLGSU3 345 3
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.71 | 300049 7THOMHL 345 301503 7THOMHLGSU3 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.66 | P11:20:AMMO:1LAB�� G1:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.66 | P11:20:AMMO:1LAB�� G2:2
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.83 | P11:345:AMMO::CALLAWAY:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.66 | P11:345:AMMO::LABADIE:3
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.66 | P11:345:AMMO::LABADIE:4
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.66 | P11:345:AMMO::RUSHISLAND:U1
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.66 | P11:345:AMMO::RUSHISLAND:U2
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.64 | P11:138:AMMO::SIOUX:2
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.64 | P12:765:AEP:AEP ROCKP-AEP JEFF 765
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.61 | P11:HV:EES::1ISES U1:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.61 | P11:EHV:EES::1ISES U2:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.42 | P11:HV:EES::PIRKEY 1:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.42 | P11:EHV:EES::WELSH3-1:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.39 | P11:HV:EES::TURKCOAL:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.61 | P12:HV:EES::5ISES%:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.61 | P12:EHV:EES::8ISES%:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.82 | P12:EHV:EES::7CALAWY 1:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20706 | 112.39 | P12:HV:EES::TURK 4%:1(1)
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.64 | 344011 7HUGHES 345 344012 7HPW-N 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.66 | 344884 7LABADIE1 345 344894 1LAB G1 20.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.66 | 344885 7LABADIE2 345 344895 1LAB G2 20.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.66 | 344886 7LABADIE3 345 344896 1LAB G3 20.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.66 | 344887 7LABADIE4 345 344897 1LAB G4 20.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.65 | 345667 7RUSH 1 345 345670 1RUSH G1 18.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.65 | 345668 7RUSH 2 345 345671 1RUSH G2 18.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.64 | 345755 4SIOUX 1 138 345756 1SIOUX 1 18.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.64 | 345764 4SIOUX 2 138 345765 1SIOUX 2 18.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.69 | P12:345:MDU::CENTER:COYOTE:1::::
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.69 | P13:345:MDU:COYOTE GSU LOSS:COYOTE::1::::
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.61 | P11:345:MEC:GDMEC CT1
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.61 | P11:345:MEC:GDMEC CT2
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.71 | P11:345:MEC:GDMEC ST
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.9 | P11:345:MEC-NPPD:COOPER 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.8 | P11:24:XEL:AUTO-SINGLE:SHERC31G:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.8 | P11:24:XEL:AUTO-SINGLE:SHERC32G:2
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.87 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.73 | P11:20:XEL:AUTO-SINGLE:PRIS31G:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.73 | P11:20:XEL:AUTO-SINGLE:PRIS32G:2
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.76 | P11:22:XEL:AUTO-SINGLE:MNTCE31G:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.73 | P11:20:XEL:AUTO-SINGLE:KING31G:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.77 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.77 | P11:22:GRE:AUTO-SINGLE:GRE-COAL42G:2
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.71 | P11:24:OTP:AUTO-SINGLE:BIGSTN1G:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.71 | P11:20:OTP:AUTO-SINGLE:CENTER2G:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.63 | P11:22:OTP:AUTO-SINGLE:CENTER1G:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.7 | P11:24:OTP:AUTO-SINGLE:COYOTE1G:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.63 | P11:24:DPC:AUTO-SINGLE:GENOA53G:3
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.61 | P12:115:XEL:AUTO-SINGLE:CHEMOLT7:LSPOWER7:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.65 | P12:115:XEL:AUTO-SINGLE:COLVILL7:CANONFLSG7:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.61 | P12:115:XEL:AUTO-SINGLE:FARIBALTP7:FARIBALTGEN:Z
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.7 | P12:230:OTP:AUTO-SINGLE:SQBUTTE4:YNG24:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.78 | P13:24-345:XEL:AUTO-SINGLE:SHERC31G:SHERCO3:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.78 | P13:24-345:XEL:AUTO-SINGLE:SHERC32G:SHERCO3:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.85 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.73 | P13:20-345:XEL:AUTO-SINGLE:PRIS31G:PRISLD3:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.73 | P13:20-345:XEL:AUTO-SINGLE:PRIS32G:PRISLD3:2
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.76 | P13:22-345:XEL:AUTO-SINGLE:MNTCE31G:MNTCELO3:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.72 | P13:20-345:XEL:AUTO-SINGLE:KING31G:ASKING3:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.76 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL41G:GRE-COALCR4:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.75 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL42G:GRE-COALCR4:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.7 | P13:230-24:OTP:AUTO-SINGLE:BIGSTON4:BIGSTN1G:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.7 | P13:20-230:OTP:AUTO-SINGLE:CENTER2G:YNG24:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.62 | P13:22-230:OTP:AUTO-SINGLE:CENTER1G:CENTER4:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.69 | P13:24-345:OTP:AUTO-SINGLE:COYOTE1G:COYOTE3:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.63 | P13:24-161:DPC:AUTO-SINGLE:GENOA53G:GENOA5:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.64 | P13:24-161:DPC:AUTO-SINGLE:JPM:ALMA5:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.7 | P11:115:XEL:RIV COMBINE CYCLE
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.62 | P12:115:XEL:BDS #2 5
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.62 | P11:115:XEL:HBR #6
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.62 | P11:115:XEL:HBR #7
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.73 | P11:115:XEL:HBR #6 7 8
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.73 | P23:345:XEL:8H14 PRI
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.73 | P23:345:XEL:8H17 PRI AS
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.85 | P23:345:XEL:8N28 SHC
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.78 | P23:345:XEL:8N22 SHC
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.78 | P23:345:XEL:8N17 SHC
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.77 | P23:345:XEL:8N8 MNN
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.72 | P23:345:XEL:8P1 KING
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.72 | P23:345:XEL:8P2 KING
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.62 | P23:115:XEL:5P147 IVH AS
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.61 | P11:18:ALTW:AUTO-SINGLE:EMERYST1:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.61 | P11:22:ALTW:AUTO-SINGLE:LANS54G:4
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.74 | P11:22:ALTW:AUTO-SINGLE:ARNOLD1G:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.77 | P11:24:ALTW:AUTO-SINGLE:OTTUMW1G:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.61 | P13:18-161:ALTW:AUTO-SINGLE:EMERYST1:EMERY5:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.61 | P13:22-161:ALTW:AUTO-SINGLE:LANS54G:LANSINGL15:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.73 | P13:22-161:ALTW:AUTO-SINGLE:ARNOLD1G:ARNOLD5:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.76 | P13:24-161:ALTW:AUTO-SINGLE:OTTUMW1G:OTTUMWA5:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.82 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.88 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.75 | P11:22:MEC:AUTO-SINGLE:NEAL3G:3
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.81 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.76 | P11:24:MEC:AUTO-SINGLE:LOUIS31G:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.81 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.84 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.74 | P13:345-22:MEC:AUTO-SINGLE:RAUN3:NEAL3G:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.8 | P13:345-24:MEC:AUTO-SINGLE:RAUN3:NEAL4G:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.74 | P13:345-24:MEC:AUTO-SINGLE:LOUISA3:LOUIS31G:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20701 | 112.78 | P11:230:WERE:JECU1_GEN::
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20701 | 112.78 | P11:345:WERE:JECU2_GEN::
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20701 | 112.78 | P11:345:WERE:JECU3_GEN::
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.95 | P11:345:WERE:WOLFU1_GEN::
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20706 | 112.63 | 511435 SNYDER-4 138 588779 TAP_G17-036 138 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20679 | 112.38 | 511446 CL-AFTP4 138 511458 ELKCTY-4 138 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20679 | 112.4 | 511446 CL-AFTP4 138 511463 HOB-JCT4 138 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20713 | 112.63 | 511453 DUNCAN-4 138 511552 DUNCHERTP4 138 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20713 | 112.62 | 511455 D.E.S.-4 138 511552 DUNCHERTP4 138 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20713 | 112.62 | 511455 D.E.S.-4 138 529344 OMDUNE-4 138 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.63 | 511456 O.K.U.-7 345 511565 OKLAUN HVDC7 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 111.6 | 511456 O.K.U.-7 345 588760 GEN-2017-033 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.21019 | 114.54 | 511456 O.K.U.-7 345 763215 G18-092-TAP 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.21033 | 115.11 | 511468 L.E.S.-7 345 762467 G18-015-TAP 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20927 | 114.48 | 511468 L.E.S.-7 345 763215 G18-092-TAP 345 2
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.29 | 511468 L.E.S.-7 345 763318 GEN-2018-115 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20706 | 112.66 | 511488 112GORE4 138 511510 LAIRGST4 138 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20717 | 112.7 | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20706 | 112.65 | 511500 CACHE4 138 511510 LAIRGST4 138 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20706 | 112.64 | 511500 CACHE4 138 588779 TAP_G17-036 138 2
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.2086 | 112.8 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.75 | 511541 SWEETWT6 230 763340 GEN-2018-117 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20224 | 109.9 | 511553 CHISHOLM7 345 523961 POTTER_CO 7 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20224 | 109.9 | 511553 CHISHOLM7 345 523961 POTTER_CO 7 345 2
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.21489 | 116.03 | 515375 WWRDEHV7 345 515458 BORDER 7 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.21489 | 116.05 | 515458 BORDER 7 345 560022 CRAWFISH_DR 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20702 | 112.7 | 515618 BALKOW 7 345 3WXFMR BALKOW 7 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20702 | 112.7 | 515618 BALKOW 7 345 3WXFMR BALKOW 7 1_Dup1
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20698 | 112.95 | 515634 PALDR1W7 345 3WXFMR PALO2 _1 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.7 | 515677 BADGER 7 345 563170 G15082_1 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20698 | 112.61 | 520827 BINGERJ4 138 521017 ONEY 4 138 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20698 | 112.62 | 521017 ONEY 4 138 521089 WASHITA4 138 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.61 | 522800 MU-TULIA 3 115 525179 TULIA_TP 3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.75 | 522892 MU-BROWNFLD2 69.0 526761 BROWNFLD_TP2 69.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.64 | 523090 TEXAS_CNTY 3 115 589380 GEN-2017-100 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.207 | 112.78 | 523093 HITCHLAND 3 115 523174 GOODWELLWND3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.95 | 523097 HITCHLAND 7 345 523112 NOVUS1 7 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 113 | 523097 HITCHLAND 7 345 523215 FREWHELCOL17 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20478 | 111.48 | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 113.05 | 523097 HITCHLAND 7 345 560252 G10-14 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.62 | 523099 TC-DRYTRLS 3 115 588480 A16-010_SUB 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.82 | 523112 NOVUS1 7 345 3WXFMR NOVUS XF2 2
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.63 | 523112 NOVUS1 7 345 3WXFMR XIANA2011198 _1 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20703 | 112.61 | 523118 BUFF_DUNES 7 345 523853 FINNEY 7 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.63 | 523120 COLE 3 115 588860 GEN-2017-047 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20703 | 112.64 | 523172 GWELL_COLL11 34.5 523174 GOODWELLWND3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20703 | 112.65 | 523173 GWELL_COLL21 34.5 523174 GOODWELLWND3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20723 | 112.61 | 523267 PRINGLE 6 230 3WXFMR ENRCO13617-1 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20723 | 112.61 | 523267 PRINGLE 6 230 523979 HARRNG_EST 6 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20792 | 113.07 | 523771 GRAPEVINE 6 230 524044 NICHOLS 6 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.21511 | 113.75 | 523959 POTTER_CO 6 230 524267 BUSHLAND 6 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.21476 | 114.67 | 523959 POTTER_CO 6 230 525461 NEWHART 6 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20929 | 118.42 | 523961 POTTER_CO 7 345 3WXFMR WAUK 90343-A 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20703 | 112.4 | 523978 HARRNG_MID 6 230 523979 HARRNG_EST 6 230 @1
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20704 | 112.39 | 524010 ROLLHILLS 6 230 3WXFMR WAUK WT01104 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20727 | 112.74 | 524267 BUSHLAND 6 230 3WXFMR WH 7001795 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.22157 | 114.31 | 524267 BUSHLAND 6 230 524623 DEAFSMITH 6 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20691 | 113.07 | 524296 SPNSPUR_WND7 345 524299 SPNSPUR_COL7 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20691 | 113.07 | 524299 SPNSPUR_COL7 345 3WXFMR SPNSPUR_COL7 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.21086 | 113.32 | 524415 AMA_SOUTH 6 230 525213 SWISHER 6 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 113.2 | 524502 NORTON 3 115 524509 FE-TUCMCARI3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20895 | 113.01 | 524575 DS-#25+ 3 115 524597 PANDAHFD 3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20895 | 113.12 | 524575 DS-#25+ 3 115 524630 TIERABLANCA3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.7 | 524604 HEREFRD_SB 2 69.0 524608 HERFRD_STH 2 69.0 *1
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.2201 | 119.12 | 524623 DEAFSMITH 6 230 760498 G17-146-TAP 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 113.1 | 524721 DS-#15&#19+2 69.0 524745 CASTRO_CNTY2 69.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20711 | 112.61 | 524770 PLSNT_HILL 6 230 3WXFMR EFAE1100068A 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.21135 | 117.92 | 524875 OASIS 6 230 524885 SN_JUAN_TAP6 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20779 | 113.69 | 524875 OASIS 6 230 524909 ROOSEVELT 6 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.21126 | 118.38 | 524885 SN_JUAN_TAP6 230 527483 CHAVES_CNTY6 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20721 | 112.8 | 524909 ROOSEVELT 6 230 3WXFMR ABB LMM60042 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.21401 | 118.36 | 524909 ROOSEVELT 6 230 525531 TOLK 6 230 2
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 113.33 | 524923 PORTALES 2 69.0 524929 RO-PORT_MTR2 69.0 @1
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 113 | 525001 W_MULESHOE 2 69.0 525008 MULESH_CTY 2 69.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 113 | 525008 MULESH_CTY 2 69.0 525027 BAILEYCO 2 69.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 113.28 | 525023 BC-BAIL_MTR2 69.0 525027 BAILEYCO 2 69.0 @1
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20807 | 113.27 | 525056 BC-EARTH 3 115 525480 PLANT_X 3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 113.09 | 525191 KRESS_INT 2 69.0 525203 SW-KRESS 2 69.0 Z1
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 113.17 | 525192 KRESS_INT 3 115 3WXFMR ENRCO 136155 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.21005 | 113.6 | 525213 SWISHER 6 230 525461 NEWHART 6 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.73 | 525272 KISER 3 115 3WXFMR VON 13819/1 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 113.19 | 525326 COX 3 115 3WXFMR ELCO 13474-3 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 113.21 | 525414 LAMTON 3 115 3WXFMR ASEA MLL9204 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20825 | 113.03 | 525440 LC-S_OLTON+3 115 525446 RKYFORD_TP 3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20825 | 113.03 | 525446 RKYFORD_TP 3 115 525480 PLANT_X 3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.2232 | 116.34 | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20984 | 114.35 | 525481 PLANT_X 6 230 3WXFMR WH ALM20171 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.2166 | 118.3 | 525481 PLANT_X 6 230 526435 SUNDOWN 6 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.2201 | 117.38 | 525481 PLANT_X 6 230 760498 G17-146-TAP 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.21052 | 113.07 | 525481 PLANT_X 6 230 762174 G17-218TAP 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.21094 | 113.14 | 525481 PLANT_X 6 230 762174 G17-218TAP 230 2
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.21867 | 118.38 | 525531 TOLK 6 230 525586 NEEDMORE 6 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20963 | 114.61 | 525531 TOLK 6 230 525637 LAMB_CNTY 6 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.23641 | 118.52 | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.21218 | 113.33 | 525531 TOLK 6 230 762174 G17-218TAP 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.21254 | 113.39 | 525531 TOLK 6 230 762174 G17-218TAP 230 2
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.33791 | 149.08 | 525549 TOLK 7 345 3WXFMR ABBXNL844501 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.21867 | 118.36 | 525586 NEEDMORE 6 230 526935 YOAKUM 6 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 113.01 | 525599 LC-SANDHLL+2 69.0 525606 AMHERST 2 69.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 113.04 | 525606 AMHERST 2 69.0 525613 W_LITTLFLD 2 69.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 113.07 | 525613 W_LITTLFLD 2 69.0 525635 LAMB_CNTY 2 69.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 113.02 | 525635 LAMB_CNTY 2 69.0 525650 LC-LTTLFLD+2 69.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20963 | 114.61 | 525637 LAMB_CNTY 6 230 3WXFMR WH ALM20172 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.87 | 525828 TUCO_INT 3 115 3WXFMR DS F78800913 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20714 | 112.4 | 525830 TUCO_INT 6 230 3WXFMR ENRCO 136401 2
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 113.07 | 526086 SW_6786_N 2 69.0 526087 SW_6786_S 2 69.0 Z1
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 113.07 | 526086 SW_6786_N 2 69.0 526102 SP-HETTLER 2 69.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 113.14 | 526087 SW_6786_S 2 69.0 526284 PLANTERS 2 69.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.69 | 526160 CARLISLE 3 115 3WXFMR WH RLP38371 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 113.03 | 526195 QUINCY 3 115 526196 SP-MILWAUKEE 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.93 | 526268 LUBBCK_STH 3 115 3WXFMR NA 70454A 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 113.19 | 526284 PLANTERS 2 69.0 526297 LUBBCK_EST 2 69.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.207 | 112.63 | 526435 SUNDOWN 6 230 3WXFMR UPDATE LATER _12 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20729 | 115 | 526435 SUNDOWN 6 230 526460 AMOCO_SS 6 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20702 | 112.65 | 526525 WOLFFORTH 6 230 3WXFMR UPDATE LATER _13 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 113.07 | 526735 TERRY_CNTY 2 69.0 526747 LG-BROWNFLD2 69.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 113 | 526747 LG-BROWNFLD2 69.0 526754 BROWNFIELD 2 69.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20694 | 114.41 | 526935 YOAKUM 6 230 527028 INK_BASIN 6 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20683 | 113.76 | 527028 INK_BASIN 6 230 527894 HOBBS_INT 6 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20699 | 113 | 527130 DENVER_N 3 115 527286 HIGGEAST 3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.61 | 527149 MUSTANG 6 230 3WXFMR ENRCO 136161 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20719 | 110.49 | 527149 MUSTANG 6 230 527151 GS-MUSTANG 6 230 @1
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.86 | 527202 SEAGRAVES 3 115 3WXFMR ABB MLL92408 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.76 | 527212 DIAMONDBACK3 115 3WXFMR HOW 36773714 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.68 | 527261 SULPHUR 2 69.0 527271 LG-FOSTER +2 69.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20699 | 112.98 | 527286 HIGGEAST 3 115 527363 HIGG 3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20702 | 112.82 | 527322 GAINES 3 115 527325 OXY_WSEM_TP3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20702 | 112.74 | 527325 OXY_WSEM_TP3 115 527362 JOHNSON_DRW3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.73 | 527340 DOSS 3 115 3WXFMR ELCO 13566/1 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.71 | 527345 LEGACY 2 69.0 527350 XTO_ROBRTSN2 69.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.71 | 527346 LEGACY 3 115 3WXFMR VROL 13735-1 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.69 | 527350 XTO_ROBRTSN2 69.0 527355 BOARDMAN 2 69.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.63 | 527355 BOARDMAN 2 69.0 527365 FLANNAGAN 2 69.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.61 | 527360 MAPCO 3 115 527362 JOHNSON_DRW3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.65 | 527362 JOHNSON_DRW3 115 528775 LE-ERF 3 115 @1
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20707 | 112.39 | 527455 RSWL_SLRCOL3 115 527482 CHAVES_CNTY3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20707 | 112.41 | 527470 CHVS_SLRCOL3 115 527464 CHVS_SOLAR11 34.5 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20707 | 112.34 | 527470 CHVS_SLRCOL3 115 527482 CHAVES_CNTY3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20887 | 112.88 | 527483 CHAVES_CNTY6 230 527799 EDDY_NORTH 6 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.62 | 527508 PRICE 3 115 527509 PRICE_TAP 3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.62 | 527529 RIACBRSH_TP3 115 527533 SW4J795_E 3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.62 | 527533 SW4J795_E 3 115 527564 ROSWLL_INT 3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.62 | 527563 ROSWLL_INT 2 69.0 527575 SW_4702 2 69.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20722 | 112.67 | 527564 ROSWLL_INT 3 115 527597 TWEEDY 3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.62 | 527575 SW_4702 2 69.0 527589 CV-ORCHARD 2 69.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.207 | 112.78 | 527653 MILO_WIND 1 34.5 527655 RSVLT_CC_E 7 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20692 | 112.66 | 527654 RSVLT_CC_W 7 345 527655 RSVLT_CC_E 7 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20692 | 112.95 | 527654 RSVLT_CC_W 7 345 527666 RSVLT_COL1 7 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20687 | 112.86 | 527655 RSVLT_CC_E 7 345 527656 CROSSROADS 7 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20692 | 112.95 | 527666 RSVLT_COL1 7 345 3WXFMR RSVLT_COL1 7 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.36 | 527736 NAVAJO_5TP 3 115 527739 NAVAJO_4 3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20704 | 112.35 | 527864 CUNNINHAM 3 115 528348 BUCKEYE_TP 3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20704 | 112.63 | 527864 CUNNINHAM 3 115 528568 MONUMNT_TP 3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20688 | 112.91 | 527865 CUNNIGHM_N 6 230 527867 CUNNIGHM_S 6 230 *1
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20699 | 112.64 | 527865 CUNNIGHM_N 6 230 527963 POTASH_JCT 6 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20704 | 112.4 | 527867 CUNNIGHM_S 6 230 3WXFMR WH 7000266 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.207 | 112.86 | 527867 CUNNIGHM_S 6 230 527882 CUNINGHAM2 1 20.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20701 | 112.79 | 527894 HOBBS_INT 6 230 527903 HOBBS_PLT3 1 18.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20704 | 112.36 | 527965 KIOWA 7 345 528027 RDRUNNER 7 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.36 | 528015 PHANTOM 7 345 528027 RDRUNNER 7 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.41 | 528024 RR_SVC_HV 3 115 528021 RDRUNNR_SVC1 15.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.68 | 528025 RDRUNNER 3 115 587990 GEN-2016-121 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.42 | 528185 N_LOVING 7 345 3WXFMR HYO1063400-1 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20704 | 112.41 | 528185 N_LOVING 7 345 528223 CHINA_DRAW 7 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.36 | 528222 CHINA_DRAW 3 115 528225 CD_SVC_HV 3 115 Z1
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20703 | 112.34 | 528333 LE-WEST_SUB3 115 528334 LE-NRTH_INT3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20704 | 112.42 | 528341 LE-SANANDRS3 115 528627 LE-TXACO_TP3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20704 | 112.38 | 528348 BUCKEYE_TP 3 115 528627 LE-TXACO_TP3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20701 | 112.62 | 528394 QUAHADA 3 115 528396 XTO_BIGEDDY3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20704 | 112.33 | 528463 SANGER_SW 3 115 528575 OXYPERMIAN 3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20704 | 112.33 | 528463 SANGER_SW 3 115 762442 G18-004-TAP 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20704 | 112.63 | 528568 MONUMNT_TP 3 115 528581 BYRD_TP 3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20704 | 112.38 | 528574 OXY_NHU_RCF3 115 528575 OXYPERMIAN 3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.69 | 528617 LE-WAITS 2 69.0 528325 LE-WAITS 3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.61 | 528617 LE-WAITS 2 69.0 528714 LE-FORT_SW 2 69.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20704 | 112.42 | 528622 LE-SANANDRS2 69.0 528341 LE-SANANDRS3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.97 | 528626 LE-PLNSINT 2 69.0 526928 PLAINS_INT 3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.97 | 528626 LE-PLNSINT 2 69.0 528709 LE-PLNSGOAB2 69.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.63 | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.69 | 528669 LE-STKLDRTP2 69.0 528740 LE-PLANS_SW2 69.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.85 | 528709 LE-PLNSGOAB2 69.0 528740 LE-PLANS_SW2 69.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.63 | 528709 LE-PLNSGOAB2 69.0 528747 LE-ALLRED 2 69.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.61 | 528714 LE-FORT_SW 2 69.0 528718 LE-NEWTEX 2 69.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.69 | 528735 LE-PLAINSUB2 69.0 528740 LE-PLANS_SW2 69.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20694 | 112.41 | 530583 POSTROCK7 345 588654 G17-021-TAP 345 2
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.41 | 531213 SANTAFE3 115 531408 PIERCVL3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20674 | 112.33 | 531451 MINGO 7 345 531465 SETAB 7 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20703 | 112.62 | 531501 BUCKNER7 345 531502 CIMRRN 7 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20703 | 112.62 | 531502 CIMRRN 7 345 531503 CIMRRN 1 34.5 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20691 | 112.32 | 531510 HARBNGR3 115 3WXFMR HARBGR345 _1 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20703 | 112.64 | 532663 LEC U5 24.0 532854 LEC U5 6 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20703 | 112.64 | 532853 LAWHILL6 230 532854 LEC U5 6 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20704 | 112.69 | 542951 HAW G5 1 22.0 543665 HAWTHN5 161 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20703 | 112.74 | 542955 LAC G1 1 22.0 542981 LACYGNE7 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20703 | 112.72 | 542956 LAC G2 1 24.0 542981 LACYGNE7 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20702 | 112.76 | 542957 IAT G1 1 24.0 542982 IATAN 7 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20703 | 112.82 | 542962 IAT G2 1 24.5 542982 IATAN 7 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20704 | 112.61 | 542966 WGARDNR5 161 543105 BULLCRK5 161 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20959 | 112.16 | 560022 CRAWFISH_DR 345 762216 G17-151TAP 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20926 | 113.18 | 560022 CRAWFISH_DR 345 762467 G18-015-TAP 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 108.98 | 560022 CRAWFISH_DR 345 763087 GEN-2018-073 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.21041 | 113.55 | 560022 CRAWFISH_DR 345 763215 G18-092-TAP 345 2
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 113.05 | 560252 G10-14 345 560253 G10-14-1 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.78 | 560253 G10-14-1 115 560254 G10-14-SUB1 34.5 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.78 | 560253 G10-14-1 115 560255 G10-14-SUB2 34.5 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.63 | 560581 G06-44-2 34.5 523111 NOVUS1 3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.68 | 560582 G06-44-3 34.5 560577 G06-44 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.66 | 560583 G06-44-4 34.5 560577 G06-44 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.32 | 560757 ASGI13_02_1 69.0 560758 ASGI13_02_2 34.5 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.32 | 560757 ASGI13_02_1 69.0 562731 WHEATLAND 69.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.33 | 560763 ASGI13_03_1 115 560761 ASGI13_03_2 34.5 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.76 | 562015 FIREWHEEL1 34.5 523215 FREWHELCOL17 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.76 | 562016 FIREWHEEL2 34.5 523215 FREWHELCOL17 345 2
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.31 | 562323 AGI1202&1305 115 562324 AGI1202&1305 34.5 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.32 | 562727 LESBIA 115 562728 SANJONTAP 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.32 | 562728 SANJONTAP 115 562729 CAPROCKTAP1 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.32 | 562730 CAPROCKTAP2 69.0 562729 CAPROCKTAP1 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.32 | 562730 CAPROCKTAP2 69.0 562731 WHEATLAND 69.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.72 | 563171 G15082_2 34.5 563170 G15082_1 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.4 | P11:13.8:AEPW:COM1-1
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.41 | P11:13.8:AEPW:COM2-1
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.41 | P11:13.8:AEPW:COM3-1
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.42 | P11:18:AEPW:WELSH1-1
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.42 | P11:18:AEPW:WELSH3-1
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.42 | P11:24:AEPW:PIRKEY 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.39 | P11:24:AEPW:SWS3-1
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.39 | P11:24:AEPW:TURKCOAL
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20717 | 112.7 | P12:138:AEPW-OMPA:DUNCAN-4:OMDUNCN4
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20706 | 112.66 | P12:138:AEPW:112GORE4:SNYDER-4
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20706 | 112.66 | 5841_Dup1
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20714 | 111.96 | 584560 GEN-2015-014 115 584561 G15-014XFMR1 34.5 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20713 | 112.65 | P12:138:AEPW:SANTAFE:DUNCAN-4
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.68 | 587991 G16-121XFMR1 34.5 587990 GEN-2016-121 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.62 | 588480 A16-010_SUB 115 3WXFMR A16-010_SUB 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20717 | 112.7 | P12:138:AEPW:DUNCAN-4:L.E.S.-4
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.06 | 588761 G17-033XFMR1 34.5 588760 GEN-2017-033 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.06 | 588765 G17-033XFMR2 34.5 588760 GEN-2017-033 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.63 | 588861 G17-047XFMR1 34.5 588860 GEN-2017-047 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20667 | 112.2 | P12:138:AEPW:ELKCTY-4:CLINTJC4
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.64 | 589381 G17-100XFMR1 34.5 589380 GEN-2017-100 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20679 | 112.39 | P12:138:AEPW:HOB-JCT4:ELKCTY-4
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.64 | P12:138:AEPW:SHERID4:112GORE4
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20703 | 112.61 | P12:230:AEPW:SWEETWT6:BUFFCK6
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20702 | 112.66 | P12:230:AEPW:SWEETWT6:ROARK6
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20947 | 114.5 | P12:345:AEPW:L.E.S7:TERRYRD7
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20947 | 114.49 | P12:345:AEPW:L.E.S7:TERRYRD7
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20947 | 114.47 | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.2101 | 114.61 | P12:345:AEPW-OKGE:L.E.S.-7:GRACMNT7
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.2101 | 114.58 | P12:345:AEPW-OKGE:L.E.S.-7:GRACMNT7
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20701 | 112.4 | P12:345:AEPW-OKGE:PITTSB-7:SEMINOL7
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.21019 | 115.66 | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.66 | P22:345:AMMO::LABADIE:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.66 | P22:345:AMMO::LABADIE:2
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.66 | P22:345:AMMO::LABADIE:3
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.66 | P22:345:AMMO::LABADIE:4
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.65 | P22:345:AMMO::RUSHISLAND:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.64 | P22:345:AMMO::RUSHISLAND:2
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20706 | 112.41 | P13:138-13.8:AEPW:COMANC-4_#2
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.2053 | 111.28 | P13:138-230:AEPW:ELKCTY-4
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20707 | 112.4 | P13:138-24:AEPW:S.W.S.-4
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20706 | 112.39 | P13:138-24:AEPW:TURK 4
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20713 | 112.63 | P13:138-345:AEPW:L.E.S.-4_#1
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20722 | 112.75 | P13:138-345:AEPW:L.E.S.-4_#2
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20706 | 112.67 | P23:500:EES-EAI:KEO:B4941
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20706 | 112.66 | P23:500:EES-EAI:KEO:B4921
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.61 | P11:26:EES-EAI:INDEP2:1:D401
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.61 | P11:26:EES-EAI:INDEP2:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.61 | P13:500:EES-EAI:INDEP2:MT2
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.65 | P23:500:EES-EAI:INDEP2:B6126
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.64 | P23:500:EES-EAI:PD:INDEP2:LN:FK479
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20703 | 112.61 | P13:230-34.5:AEPW:BUFFCK6
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20702 | 112.67 | P13:230-34.5:AEPW:ROARK6
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.41 | P13:69-13.8:AEPW:COMANC-2
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.66 | P11:024:DPC:ALMA2:6
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.62 | P11:18:ITCM:EMERYGT1:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.63 | P11:18:ITCM:EMERYGT2:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.63 | P11:161:ITCM:MGS CT1:1C
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.63 | P11:161:ITCM:MGS CT2:2C
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20703 | 112.64 | 652537 WHITE 3 345 659286 DEERCREK-BE3 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20703 | 112.64 | 659286 DEERCREK-BE3 345 3WXFMR DEERCRK KU1A 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.63 | 672601 BD 4 230 672306 BD 6G 18.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.63 | 672610 POPLAR 4 230 672310 POPLAR 1G 18.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.63 | 672610 POPLAR 4 230 672311 POPLAR 2G 18.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.62 | 672621 SHAND 4 230 672321 SHAND 1G 18.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.61 | 672649 CODETTE 4 230 672650 NIPAWIN 4 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.62 | 672696 BRADA 4 230 672699 NBEC 4 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.69 | P23:345:MDU::COYOTE::5707-5712-5715::::
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.84 | P23:345:MEC:CBEC 905
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.81 | P23:345:MEC:CBEC 908
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.64 | P23:345:MEC:GDMEC 908
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.74 | P23:345:MEC:RAUN 0180
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.8 | P23:345:MEC:RAUN 0210
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.75 | P23:345:MEC:LOUISA 954
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.75 | P23:345:MEC:LOUISA 964
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.61 | P21:115:XEL:AUTO-SINGLE:CHEMOLT7:LSPOWER7:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.65 | P21:115:XEL:AUTO-SINGLE:COLVILL7:CANONFLSG7:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.61 | P21:115:XEL:AUTO-SINGLE:FARIBALTP7:FARIBALTGEN:Z
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.7 | P21:230:OTP:AUTO-SINGLE:SQBUTTE4:YNG24:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.69 | P23:345:OTP:CENTER 3:3215(1)
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.69 | P23:345:OTP:CENTER 3:3225(1)
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.63 | P12:230:UMZW:# 687 #: FT IN SD. FT-BG1 LINE FAULT
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.63 | P12:230:UMZW:# 3617 #: FT IN SD. FT-BG2 LINE FAULT
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 111.33 | 760494 GEN-2017-146 230 760498 G17-146-TAP 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 111.32 | 760495 G17-146-XFM1 34.5 760494 GEN-2017-146 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.05 | 761356 G17-239-XFMR 34.5 761355 GEN-2017-239 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.05 | 761359 G17-239-XFMR 34.5 761355 GEN-2017-239 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.23 | 761797 G17-187XFM1 34.5 761796 GEN-2017-187 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.23 | 761800 G17-187XFM2 34.5 761796 GEN-2017-187 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 107.16 | 762132 GEN-2017-158 230 763252 G18-099-XFM1 34.5 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 107.16 | 762132 GEN-2017-158 230 763255 G18-099-XFM2 34.5 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 107.74 | 762133 G17-158XFM1 34.5 762132 GEN-2017-158 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 107.74 | 762136 G17-158XFM2 34.5 762132 GEN-2017-158 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 109.9 | 762216 G17-151TAP 345 762217 GEN-2017-151 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20959 | 113.55 | 762216 G17-151TAP 345 762467 G18-015-TAP 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 111.85 | 762218 G17-151XFM1 34.5 762217 GEN-2017-151 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 111.85 | 762221 G17-151XFM2 34.5 762217 GEN-2017-151 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 111.85 | 762224 G17-151XFM3 34.5 762217 GEN-2017-151 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 111.85 | 762227 G17-151XFM4 34.5 762217 GEN-2017-151 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.36 | 762438 GEN-2018-004 115 762442 G18-004-TAP 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 110.89 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 111.7 | 762461 G18-015-XFM1 34.5 762460 GEN-2018-015 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 111.7 | 762464 G18-015-XFM2 34.5 762460 GEN-2018-015 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20843 | 113.07 | 762467 G18-015-TAP 345 763215 G18-092-TAP 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 110.18 | 763087 GEN-2018-073 345 763088 G18-073-XFM1 34.5 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 111.33 | 763087 GEN-2018-073 345 763091 G18-073-XFM2 34.5 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 107.16 | 763120 GEN-2018-081 230 763121 G18-081-XFM1 34.5 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 109.42 | 763120 GEN-2018-081 230 764011 G19-074-XFM1 34.5 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 109.44 | 763186 GEN-2018-089 230 763187 G18-089-XFM1 34.5 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 110.21 | 763208 GEN-2018-092 345 763215 G18-092-TAP 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 111.37 | 763208 GEN-2018-092 345 763220 G18-092-XFM1 34.5 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 111.37 | 763208 GEN-2018-092 345 763223 G18-092-XFM2 34.5 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 108.87 | 763241 GEN-2018-097 230 763242 G18-097-XFM1 34.5 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 109.14 | 763241 GEN-2018-097 230 763307 G18-112-XFM1 34.5 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 109.14 | 763241 GEN-2018-097 230 763310 G18-112-XFM2 34.5 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 108.87 | 763241 GEN-2018-097 230 763395 G18-124-XFM1 34.5 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 108.87 | 763241 GEN-2018-097 230 763398 G18-124-XFM2 34.5 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.29 | 763318 GEN-2018-115 345 763319 G18-115-XFM1 34.5 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.75 | 763340 GEN-2018-117 230 763341 G18-117-XFM1 34.5 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 108.51 | 763483 GEN-2019-003 230 763484 G19-003-XFM1 34.5 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 111.19 | 763483 GEN-2019-003 230 763605 G19-021-XFM1 34.5 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 111.9 | 763516 GEN-2019-011 345 763517 G19-011-XFM1 34.5 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.26 | 763879 GEN-2019-056 115 763880 G19-056XFM1 34.5 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20655 | 112.68 | P42:345:OKGE:SB_BVTY7305
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20697 | 112.43 | P23:345:WERE:BUFF_345-534::
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20697 | 112.43 | P23:345:WERE:BUFF_345-543::
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20701 | 112.78 | P23:345:WERE:JEC_345-15::
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.207 | 112.75 | P23:345:WERE:JEC_345-16::
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20701 | 112.78 | P23:345:WERE:JEC_345-19::
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20701 | 112.78 | P23:345:WERE:JEC_345-20::
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.95 | P23:345:WERE:WOLF_345-50::
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.95 | P23:345:WERE:WOLF_345-60::
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20706 | 112.43 | P42:345:AEPW:WELSH CB 10620 NBTB+FAULT
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.21019 | 114.21 | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.21043 | 114.99 | P42:345:AEPW:LAWTON EASTSIDE CB 3413A NBTB+FAULT
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.21079 | 115.4 | P42:345:AEPW:LAWTON EASTSIDE CB 3425A NBTB+FAULT
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.21033 | 115.86 | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20719 | 112.31 | P42:345:AEPW:PITTSBURG CB 3441A NBTB+FAULT
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20701 | 112.4 | P42:345:AEPW:PITTSBURG CB 3445A NBTB+FAULT
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20947 | 114.49 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20947 | 114.49 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20947 | 114.47 | P42:345:AEPW:TERRYRD_CB_3421A_NBTB
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20703 | 112.75 | P23:345:KCPL:LACYGNE_R2-5::LACYGU2-LACYGNE-STILWELL
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20706 | 112.43 | P23:345:AEPW:WELSH CB 10620 NBTB
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.21019 | 114.54 | P23:345:AEPW:OKLAUNION CB 3401A NBTB
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.21043 | 114.99 | P23:345:AEPW:LAWTON EASTSIDE CB 3413A NBTB
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.21079 | 115.4 | P23:345:AEPW:LAWTON EASTSIDE CB 3425A NBTB
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.21033 | 115.86 | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20719 | 112.31 | P23:345:AEPW:PITTSBURG CB 3441A NBTB
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20701 | 112.4 | P23:345:AEPW:PITTSBURG CB 3445A NBTB
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20947 | 114.49 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20947 | 114.49 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20947 | 114.47 | P23:345:AEPW:TERRYRD_CB_3421A_NBTB
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20736 | 112.62 | P12:138:AEPW:S.W.S.-4:L.E.S.-4
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.65 | P11:115:SUNC:GARDENCITY_S2:97:531459(2)
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20966 | 114.72 | P23:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.21223 | 117.32 | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20966 | 114.72 | P42:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB+FAULT
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.21223 | 117.32 | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20674 | 112.33 | P23:345:SUNC:MO_BRK182
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20674 | 112.33 | P23:345:SUNC:MO_BRK382
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20702 | 112.42 | P21:345:UMZW:# 725 #: GI IN NE. GI-SWEET LINE FAULT
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.2086 | 112.8 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20706 | 112.41 | P12:138-13.8:AEPW:COMANC-4_#1
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.2053 | 111.26 | P12:230:AEPW:ELKCITY6:CHISHOLM6
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20849 | 113.54 | P12:230:AEPW:SWEETWT6:CHISHOLM6
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997715 ABBXNL844501 230 1 |  | 553 | 0.33791 | 150.96 | 525531 TOLK 6 230 3WXFMR TOLK 6 2
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20706 | 112.73 | P23:345:KCPL-WERE:237LACYGNE_R1-6::LACYGU1-LACYGNE-NEOSHO
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20703 | 112.64 | P11:230:WERE:LECU5_GEN::
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20704 | 112.63 | P11:161:GMO:DOGWOOD_COMBINED_CYCLE_UNIT_OUTAGE_1_1
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.2071 | 111.16 | P11:115:SPS:MUSTANG1&3:153MW::::
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20963 | 114.61 | P12:230:SPS:K37::1_TOLK_LAMB:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20723 | 112.61 | P12:230:SPS:K43::1_PRNGLE_HARR_E:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20707 | 112.37 | P12:230:SPS:K44::1_EPLNT_HARRW:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20718 | 112.79 | P12:115:SPS:T04::1_TRBLNC_CASTRO:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20704 | 112.19 | P12:115:SPS:T13::1_TAYLOR_WHOBBS:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20704 | 112.31 | P12:115:SPS:T14::1_MADDOX_TAYLOR:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 113.09 | P12:115:SPS:T21::1_GRSSLND_GRAHAM:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20704 | 112.41 | P12:115:SPS:T23::1_PCA_POTJCT:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.62 | P12:115:SPS:T24B::1_RSWLL_BRSHRF:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.64 | P12:115:SPS:T26::1_CHAVES_RSWLCTY:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20825 | 113.18 | P12:115:SPS:T28A::1_LAMTON_PLANTX:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20749 | 112.67 | P12:115:SPS:T29::1_LAMTON_HALECTR:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20876 | 113.96 | P12:115:SPS:T30::1_LAMB_HOCKLY:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20876 | 113.13 | P12:115:SPS:T31::1_HOCKLY_SUNDWN:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.207 | 112.63 | P12:115:SPS:T35::1_TERRY_YOAKUM:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 113.32 | P12:115:SPS:T45::1_NORRIS_OASIS:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20703 | 112.4 | P12:115:SPS:T57::1_MUSTG_SEGRVS:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20831 | 113.15 | P12:115:SPS:T59::1_CARGIL_CURRY:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.208 | 112.42 | P12:115:SPS:T66::1_RNDALL_HAPPY:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.208 | 112.9 | P12:115:SPS:T67::1_HAPPY_KRESS:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20709 | 112.39 | P12:115:SPS:T68::1_TUCO_FLOYD:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20699 | 113.2 | P12:115:SPS:T71::1_CRLSLE_YUMA:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20713 | 112.7 | P12:115:SPS:T81::1_COX_FLOYD:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20704 | 112.85 | P12:115:SPS:T83::1_SP-FKFD_ALLEN:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20699 | 113.01 | P12:115:SPS:T89::1_DC_N_HIGG:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.66 | P12:115:SPS:T91::1_HIGG_RUSSELL:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20727 | 112.62 | P12:115:SPS:V04::1_EPLANT_RNDALL:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20718 | 112.67 | P12:115:SPS:V07::1_COX_HALECTR:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20817 | 112.95 | P12:115:SPS:V09::1_HALECTR_PLANTX:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20703 | 112.83 | P12:115:SPS:V12::1_PLANTX_BAILEY:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20704 | 112.62 | P12:115:SPS:V15::1_TUCO_INDANA:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20667 | 112.67 | P12:115:SPS:V24::1_WOLFTH_TERRY:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20722 | 112.64 | P12:115:SPS:V26::1_RSWLL_EDDY_N:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.98 | P12:115:SPS:V33::1_LUBBS_LYNN:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20807 | 113.85 | P12:115:SPS:V37::1_CASTRO_PLANTX:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.75 | P12:115:SPS:V46::1_ALLEN_WHEELCK:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20706 | 113.09 | P12:115:SPS:V49::1_YOAKUM_SHLCO2:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20748 | 113.26 | P12:115:SPS:V55::1_SUNDWN_TERRY:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20718 | 113.09 | P12:115:SPS:V56::1_COCHRAN_SUNDWN:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20704 | 112.68 | P12:115:SPS:V62::1_CRLSLE_INDANA:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20706 | 112.62 | P12:115:SPS:V70::1_S_GORG_RNDALL:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20717 | 112.65 | P12:115:SPS:V78::2_CURRY_RSVLT:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20703 | 112.79 | P12:115:SPS:V81::1_LE-WAIT_LE-LVN:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.65 | P12:115:SPS:V95::1_DC_N_SHLCO2:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.61 | P12:115:SPS:W11::1_DC_S_SMINLE:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20704 | 112.61 | P12:115:SPS:W12::1_SMINLE_DOSS:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20704 | 112.68 | P12:115:SPS:W14::1_SMINLE_GAINES:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 113.14 | P12:115:SPS:W32::1_PRMTR_FE-CLSIN:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.61 | P12:115:SPS:W34::1_JNSDRW_MAPCO:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20702 | 112.85 | P12:115:SPS:W35::1_GAINES_JNSDRW:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20699 | 112.64 | P12:115:SPS:W36::1_TAYLOR_JNSDRW:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20895 | 113.15 | P12:115:SPS:W40::1_WCANYON_TRBLNC:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20732 | 112.71 | P12:115:SPS:W52::1_NEWHART_KRESS:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 113.2 | P12:115:SPS:W58::1_NORTON_LOPEZ:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.82 | P12:115:SPS:W59::1_LOPEZ_CMPBLL:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20706 | 113.15 | P12:115:SPS:W62::1_PLSTHL_CURRY:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20717 | 112.62 | P12:115:SPS:W63::1_PLSTHL_CURRY:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.96 | P12:115:SPS:W64::1_PLSTHL_FE-CLV:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20706 | 113.12 | P12:115:SPS:W65::1_PLSTHL_CURRY:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.81 | P12:115:SPS:W66::1_PORTA_GREYHUND:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20895 | 112.61 | P12:115:SPS:W77::1_RNDAL_WCANYON:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.64 | P12:115:SPS:W99::1_CAPITAN_CHAVES:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.207 | 113.08 | P12:115:SPS:U14::1_DC_STH_INKBSN:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20703 | 113.02 | P12:115:SPS:V15::1_INKBSN_LE-WAT:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20727 | 112.74 | P12:115:SPS:U16::1_BSHLND_OUTPST:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20727 | 112.73 | P12:115:SPS:U17::1_COLTR_OUTPST:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20711 | 112.8 | P12:115:SPS:U19::1_DEAN_PLAINS:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20727 | 112.67 | P12:115:SPS:U23::1_COLTR_HILSDE:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20704 | 112.62 | P11:18:HAST:::EGYCTR2G WEC2_LOSS OF WEC 2 GEN_:HV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20704 | 112.62 | P13:18-115:HAST:::EGYCNTR7 XFMR G2WEC 2 GSU_:HV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20704 | 112.63 | P11:161:GMO:DOGWOOD-COMBINED-CYCLE-UNIT-OUTA:::HV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20706 | 112.73 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20703 | 112.75 | P23:345:KCPL:LACYGNE-R2-5:::EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20701 | 112.78 | P11:230:WERE:JECU1-GEN:::HV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20703 | 112.64 | P11:230:WERE:LECU5-GEN:::HV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20701 | 112.78 | P11:345:WERE:JECU2-GEN:::EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20701 | 112.78 | P11:345:WERE:JECU3-GEN:::EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.95 | P11:345:WERE:WOLFU1-GEN:::EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20697 | 112.43 | P23:345:WERE:BUFF-345-534:::EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20697 | 112.43 | P23:345:WERE:BUFF-345-543:::EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20701 | 112.78 | P23:345:WERE:JEC-345-15:::EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.207 | 112.75 | P23:345:WERE:JEC-345-16:::EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20701 | 112.78 | P23:345:WERE:JEC-345-19:::EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20701 | 112.78 | P23:345:WERE:JEC-345-20:::EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.95 | P23:345:WERE:WOLF-345-50:::EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.95 | P23:345:WERE:WOLF-345-60:::EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.89 | P11:022:NPPD:COOPER1G:1:983:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.207 | 112.92 | P11:023:NPPD:GENTLM1G:1:757:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.207 | 112.94 | P11:024:NPPD:GENTLM2G:2:757:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20702 | 112.75 | P13:345:OPPD:NEBCTY1G:::EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.207 | 112.78 | P13:345:OPPD:NEBCTY2G:::EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.77 | P22:345:OPPD:S3458 NEBCTY1G:LT::EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20702 | 112.75 | P22:345:OPPD:S3458 NEBCTY1G:::EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.81 | P22:345:OPPD:S3458 NEBCTY2G:LT::EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.207 | 112.78 | P22:345:OPPD:S3458 NEBCTY2G:::EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.77 | P23:345:OPPD:S3458 NEBCTY1G:LT::EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20702 | 112.75 | P23:345:OPPD:S3458 NEBCTY1G:::EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.81 | P23:345:OPPD:S3458 NEBCTY2G:LT::EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.207 | 112.78 | P23:345:OPPD:S3458 NEBCTY2G:::EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.4 | P12:115:SUNC:PLYMELL-PIERCEVILLE:::HV::
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20703 | 112.64 | P11:018:UMZB:# 5 #:: DCS IN SD. DEERCREEK_MV::
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20704 | 112.61 | P11:022:UMZB:# 15 #:: LO IN ND. LELAND OLDS 1_MV::
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20703 | 112.65 | P11:020:UMZB:# 16 #:: LO IN ND. LELAND OLDS 2_MV::
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20702 | 112.7 | P11:023:UMZB:# 31 #:: AVS IN ND. ANTELOPE VALLEY 1_MV::
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20702 | 112.7 | P11:023:UMZB:# 32 #:: AVS IN ND. ANTELOPE VALLEY 2_MV::
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20699 | 112.9 | P11:024:UMZB:# 33 #:: LRS IN WY. LARAMIE RIVER STATION 1_MV::
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.63 | P12:230:UMZW:# 687 #:: FT IN SD. FT-BG1 BRANCH FAULT:HV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.63 | P12:230:UMZW:# 3617 #:: FT IN SD. FT-BG2 BRANCH FAULT:HV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.63 | P12:230:UMZW:# 4038 #:: BG-FT IN SD. FAULT FOR TRANSMISSION CIRCUIT (BG-FT).:HV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.63 | P12:230:UMZW:# 4039 #:: BG-FT IN SD. FAULT FOR TRANSMISSION CIRCUIT (BG-FT).:HV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.61 | P13:230:UMZW:# 5135 #:: OA IN SD. FAULT ON TRANSFORMER (2).:HV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.61 | P13:230:UMZW:# 5136 #:: OA IN SD. FAULT ON TRANSFORMER (3).:HV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20702 | 112.42 | P21:345:UMZW:# 725 #:: GI IN NE. GI-SWEET BRANCH FAULT:EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20702 | 112.42 | P23:345:UMZW:# 2430 #:: GI IN NE. GI 1492 BKR FAULT:EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20702 | 112.42 | P23:345:UMZW:# 2438 #:: GI IN NE. GI-SWEET BRANCH FAULT & GI 1492 STUCK BKR:EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20707 | 112.37 | P11:138:WFEC:HUGO1:465MW :::
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20701 | 112.4 | P12:345:OKGE-AEPW:BKRBKR20::::
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.2074 | 112.75 | P12:345:OKGE:BKRBKR21::::
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20759 | 112.95 | P12:345:OKGE:BKRBKR24::::
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20947 | 114.47 | P12:345:OKGE-AEPW:BKRBKR25::::
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20695 | 112.42 | P12:345:OKGE:BKRBKR336::::
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20695 | 112.41 | P12:345:OKGE:BKRBKR336_2::::
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.2101 | 114.61 | P12:345:OKGE-AEPW:BKRBKR366::::
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.2101 | 114.58 | P12:345:OKGE-AEPW:BKRBKR366::::
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.2076 | 112.87 | P12:345:OKGE:BKRBKR367::::
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20736 | 112.62 | P12:345:OKGE-WFEC:BKRBKR374::::
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20663 | 112.22 | P12:345:OKGE:BKRBKR4193::::
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20663 | 112.22 | P12:345:OKGE:BKRBKR4194::::
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20647 | 112.28 | P12:345:OKGE-SPS:BKRBKR4201::::
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20647 | 112.28 | P12:345:OKGE-SPS:BKRBKR4202::::
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20694 | 112.35 | P12:345:OKGE:BKRBKR443NEW::::
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20694 | 112.35 | P12:345:OKGE:BKRBKR443NEW2::::
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20698 | 112.88 | P12:345:OKGE:BKRBKR604::::
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20698 | 112.94 | P12:345:OKGE:BKRBKR604_2::::
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20656 | 112.62 | P42:345:OKGE:SB_ARIA7381::::
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.21489 | 116.05 | P42:345:OKGE:SB_BVTY7387::::
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.2074 | 112.68 | P42:345:OKGE:SB_SPCK7383::::
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20703 | 112.64 | P11:115:SUNC:GARDENCITY_S2:103:531459(2):HV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20703 | 112.64 | P11:115:SUNC:FORTDDODGE_4:157:539670(4):HV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.62 | P11:345:599:CIMARRON1WIND:200:531603(1):EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.92 | P13:115:SUNC:HOLCOMB_GSU:::HV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20703 | 112.64 | P13:115:SUNC:S2_GSU:::HV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20703 | 112.64 | P13:115:SUNC:FORTDODGE_GSU:::HV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20703 | 112.62 | P23:345:SUNC:BU_BRK682:::EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.71 | 300003 1THLG3 24.0 301503 7THOMHLGSU3 345 3
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.71 | 300049 7THOMHL 345 301503 7THOMHLGSU3 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.66 | P11:20:AMMO:1LAB�� G1:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.66 | P11:20:AMMO:1LAB�� G2:2
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.83 | P11:345:AMMO::CALLAWAY:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.66 | P11:345:AMMO::LABADIE:3
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.66 | P11:345:AMMO::LABADIE:4
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.66 | P11:345:AMMO::RUSHISLAND:U1
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.66 | P11:345:AMMO::RUSHISLAND:U2
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.64 | P11:138:AMMO::SIOUX:2
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.64 | P12:765:AEP:AEP ROCKP-AEP JEFF 765
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.61 | P11:HV:EES::1ISES U1:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.61 | P11:EHV:EES::1ISES U2:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.42 | P11:HV:EES::PIRKEY 1:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.42 | P11:EHV:EES::WELSH3-1:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.39 | P11:HV:EES::TURKCOAL:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.61 | P12:HV:EES::5ISES%:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.61 | P12:EHV:EES::8ISES%:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.82 | P12:EHV:EES::7CALAWY 1:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20706 | 112.39 | P12:HV:EES::TURK 4%:1(1)
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.64 | 344011 7HUGHES 345 344012 7HPW-N 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.66 | 344884 7LABADIE1 345 344894 1LAB G1 20.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.66 | 344885 7LABADIE2 345 344895 1LAB G2 20.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.66 | 344886 7LABADIE3 345 344896 1LAB G3 20.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.66 | 344887 7LABADIE4 345 344897 1LAB G4 20.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.65 | 345667 7RUSH 1 345 345670 1RUSH G1 18.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.65 | 345668 7RUSH 2 345 345671 1RUSH G2 18.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.64 | 345755 4SIOUX 1 138 345756 1SIOUX 1 18.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.64 | 345764 4SIOUX 2 138 345765 1SIOUX 2 18.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.69 | P12:345:MDU::CENTER:COYOTE:1::::
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.69 | P13:345:MDU:COYOTE GSU LOSS:COYOTE::1::::
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.61 | P11:345:MEC:GDMEC CT1
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.61 | P11:345:MEC:GDMEC CT2
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.71 | P11:345:MEC:GDMEC ST
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.9 | P11:345:MEC-NPPD:COOPER 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.8 | P11:24:XEL:AUTO-SINGLE:SHERC31G:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.8 | P11:24:XEL:AUTO-SINGLE:SHERC32G:2
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.87 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.73 | P11:20:XEL:AUTO-SINGLE:PRIS31G:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.73 | P11:20:XEL:AUTO-SINGLE:PRIS32G:2
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.76 | P11:22:XEL:AUTO-SINGLE:MNTCE31G:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.73 | P11:20:XEL:AUTO-SINGLE:KING31G:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.77 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.77 | P11:22:GRE:AUTO-SINGLE:GRE-COAL42G:2
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.71 | P11:24:OTP:AUTO-SINGLE:BIGSTN1G:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.71 | P11:20:OTP:AUTO-SINGLE:CENTER2G:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.63 | P11:22:OTP:AUTO-SINGLE:CENTER1G:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.7 | P11:24:OTP:AUTO-SINGLE:COYOTE1G:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.63 | P11:24:DPC:AUTO-SINGLE:GENOA53G:3
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.61 | P12:115:XEL:AUTO-SINGLE:CHEMOLT7:LSPOWER7:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.65 | P12:115:XEL:AUTO-SINGLE:COLVILL7:CANONFLSG7:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.61 | P12:115:XEL:AUTO-SINGLE:FARIBALTP7:FARIBALTGEN:Z
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.7 | P12:230:OTP:AUTO-SINGLE:SQBUTTE4:YNG24:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.78 | P13:24-345:XEL:AUTO-SINGLE:SHERC31G:SHERCO3:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.78 | P13:24-345:XEL:AUTO-SINGLE:SHERC32G:SHERCO3:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.85 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.73 | P13:20-345:XEL:AUTO-SINGLE:PRIS31G:PRISLD3:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.73 | P13:20-345:XEL:AUTO-SINGLE:PRIS32G:PRISLD3:2
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.76 | P13:22-345:XEL:AUTO-SINGLE:MNTCE31G:MNTCELO3:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.72 | P13:20-345:XEL:AUTO-SINGLE:KING31G:ASKING3:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.76 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL41G:GRE-COALCR4:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.75 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL42G:GRE-COALCR4:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.7 | P13:230-24:OTP:AUTO-SINGLE:BIGSTON4:BIGSTN1G:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.7 | P13:20-230:OTP:AUTO-SINGLE:CENTER2G:YNG24:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.62 | P13:22-230:OTP:AUTO-SINGLE:CENTER1G:CENTER4:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.69 | P13:24-345:OTP:AUTO-SINGLE:COYOTE1G:COYOTE3:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.63 | P13:24-161:DPC:AUTO-SINGLE:GENOA53G:GENOA5:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.64 | P13:24-161:DPC:AUTO-SINGLE:JPM:ALMA5:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.7 | P11:115:XEL:RIV COMBINE CYCLE
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.62 | P12:115:XEL:BDS #2 5
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.62 | P11:115:XEL:HBR #6
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.62 | P11:115:XEL:HBR #7
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.73 | P11:115:XEL:HBR #6 7 8
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.73 | P23:345:XEL:8H14 PRI
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.73 | P23:345:XEL:8H17 PRI AS
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.85 | P23:345:XEL:8N28 SHC
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.78 | P23:345:XEL:8N22 SHC
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.78 | P23:345:XEL:8N17 SHC
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.77 | P23:345:XEL:8N8 MNN
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.72 | P23:345:XEL:8P1 KING
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.72 | P23:345:XEL:8P2 KING
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.62 | P23:115:XEL:5P147 IVH AS
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.61 | P11:18:ALTW:AUTO-SINGLE:EMERYST1:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.61 | P11:22:ALTW:AUTO-SINGLE:LANS54G:4
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.74 | P11:22:ALTW:AUTO-SINGLE:ARNOLD1G:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.77 | P11:24:ALTW:AUTO-SINGLE:OTTUMW1G:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.61 | P13:18-161:ALTW:AUTO-SINGLE:EMERYST1:EMERY5:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.61 | P13:22-161:ALTW:AUTO-SINGLE:LANS54G:LANSINGL15:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.73 | P13:22-161:ALTW:AUTO-SINGLE:ARNOLD1G:ARNOLD5:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.76 | P13:24-161:ALTW:AUTO-SINGLE:OTTUMW1G:OTTUMWA5:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.82 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.88 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.75 | P11:22:MEC:AUTO-SINGLE:NEAL3G:3
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.81 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.76 | P11:24:MEC:AUTO-SINGLE:LOUIS31G:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.81 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.84 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.74 | P13:345-22:MEC:AUTO-SINGLE:RAUN3:NEAL3G:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.8 | P13:345-24:MEC:AUTO-SINGLE:RAUN3:NEAL4G:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.74 | P13:345-24:MEC:AUTO-SINGLE:LOUISA3:LOUIS31G:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20701 | 112.78 | P11:230:WERE:JECU1_GEN::
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20701 | 112.78 | P11:345:WERE:JECU2_GEN::
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20701 | 112.78 | P11:345:WERE:JECU3_GEN::
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.95 | P11:345:WERE:WOLFU1_GEN::
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20706 | 112.63 | 511435 SNYDER-4 138 588779 TAP_G17-036 138 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20679 | 112.38 | 511446 CL-AFTP4 138 511458 ELKCTY-4 138 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20679 | 112.4 | 511446 CL-AFTP4 138 511463 HOB-JCT4 138 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20713 | 112.63 | 511453 DUNCAN-4 138 511552 DUNCHERTP4 138 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20713 | 112.62 | 511455 D.E.S.-4 138 511552 DUNCHERTP4 138 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20713 | 112.62 | 511455 D.E.S.-4 138 529344 OMDUNE-4 138 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.63 | 511456 O.K.U.-7 345 511565 OKLAUN HVDC7 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 111.6 | 511456 O.K.U.-7 345 588760 GEN-2017-033 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.21019 | 114.54 | 511456 O.K.U.-7 345 763215 G18-092-TAP 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.21033 | 115.11 | 511468 L.E.S.-7 345 762467 G18-015-TAP 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20927 | 114.48 | 511468 L.E.S.-7 345 763215 G18-092-TAP 345 2
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.29 | 511468 L.E.S.-7 345 763318 GEN-2018-115 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20706 | 112.66 | 511488 112GORE4 138 511510 LAIRGST4 138 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20717 | 112.7 | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20706 | 112.65 | 511500 CACHE4 138 511510 LAIRGST4 138 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20706 | 112.64 | 511500 CACHE4 138 588779 TAP_G17-036 138 2
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.2086 | 112.8 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.75 | 511541 SWEETWT6 230 763340 GEN-2018-117 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20224 | 109.9 | 511553 CHISHOLM7 345 523961 POTTER_CO 7 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20224 | 109.9 | 511553 CHISHOLM7 345 523961 POTTER_CO 7 345 2
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.21489 | 116.03 | 515375 WWRDEHV7 345 515458 BORDER 7 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.21489 | 116.05 | 515458 BORDER 7 345 560022 CRAWFISH_DR 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20702 | 112.7 | 515618 BALKOW 7 345 3WXFMR BALKOW 7 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20702 | 112.7 | 515618 BALKOW 7 345 3WXFMR BALKOW 7 1_Dup1
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20698 | 112.95 | 515634 PALDR1W7 345 3WXFMR PALO2 _1 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.7 | 515677 BADGER 7 345 563170 G15082_1 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20698 | 112.61 | 520827 BINGERJ4 138 521017 ONEY 4 138 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20698 | 112.62 | 521017 ONEY 4 138 521089 WASHITA4 138 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.61 | 522800 MU-TULIA 3 115 525179 TULIA_TP 3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.75 | 522892 MU-BROWNFLD2 69.0 526761 BROWNFLD_TP2 69.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.64 | 523090 TEXAS_CNTY 3 115 589380 GEN-2017-100 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.207 | 112.78 | 523093 HITCHLAND 3 115 523174 GOODWELLWND3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.95 | 523097 HITCHLAND 7 345 523112 NOVUS1 7 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 113 | 523097 HITCHLAND 7 345 523215 FREWHELCOL17 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20478 | 111.48 | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 113.05 | 523097 HITCHLAND 7 345 560252 G10-14 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.62 | 523099 TC-DRYTRLS 3 115 588480 A16-010_SUB 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.82 | 523112 NOVUS1 7 345 3WXFMR NOVUS XF2 2
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.63 | 523112 NOVUS1 7 345 3WXFMR XIANA2011198 _1 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20703 | 112.61 | 523118 BUFF_DUNES 7 345 523853 FINNEY 7 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.63 | 523120 COLE 3 115 588860 GEN-2017-047 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20703 | 112.64 | 523172 GWELL_COLL11 34.5 523174 GOODWELLWND3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20703 | 112.65 | 523173 GWELL_COLL21 34.5 523174 GOODWELLWND3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20723 | 112.61 | 523267 PRINGLE 6 230 3WXFMR ENRCO13617-1 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20723 | 112.61 | 523267 PRINGLE 6 230 523979 HARRNG_EST 6 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20792 | 113.07 | 523771 GRAPEVINE 6 230 524044 NICHOLS 6 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.21511 | 113.75 | 523959 POTTER_CO 6 230 524267 BUSHLAND 6 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.21476 | 114.67 | 523959 POTTER_CO 6 230 525461 NEWHART 6 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20929 | 118.42 | 523961 POTTER_CO 7 345 3WXFMR WAUK 90343-A 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20703 | 112.4 | 523978 HARRNG_MID 6 230 523979 HARRNG_EST 6 230 @1
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20704 | 112.39 | 524010 ROLLHILLS 6 230 3WXFMR WAUK WT01104 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20727 | 112.74 | 524267 BUSHLAND 6 230 3WXFMR WH 7001795 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.22157 | 114.31 | 524267 BUSHLAND 6 230 524623 DEAFSMITH 6 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20691 | 113.07 | 524296 SPNSPUR_WND7 345 524299 SPNSPUR_COL7 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20691 | 113.07 | 524299 SPNSPUR_COL7 345 3WXFMR SPNSPUR_COL7 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.21086 | 113.32 | 524415 AMA_SOUTH 6 230 525213 SWISHER 6 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 113.2 | 524502 NORTON 3 115 524509 FE-TUCMCARI3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20895 | 113.01 | 524575 DS-#25+ 3 115 524597 PANDAHFD 3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20895 | 113.12 | 524575 DS-#25+ 3 115 524630 TIERABLANCA3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.7 | 524604 HEREFRD_SB 2 69.0 524608 HERFRD_STH 2 69.0 *1
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.2201 | 119.12 | 524623 DEAFSMITH 6 230 760498 G17-146-TAP 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 113.1 | 524721 DS-#15&#19+2 69.0 524745 CASTRO_CNTY2 69.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20711 | 112.61 | 524770 PLSNT_HILL 6 230 3WXFMR EFAE1100068A 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.21135 | 117.92 | 524875 OASIS 6 230 524885 SN_JUAN_TAP6 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20779 | 113.69 | 524875 OASIS 6 230 524909 ROOSEVELT 6 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.21126 | 118.38 | 524885 SN_JUAN_TAP6 230 527483 CHAVES_CNTY6 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20721 | 112.8 | 524909 ROOSEVELT 6 230 3WXFMR ABB LMM60042 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.21401 | 118.36 | 524909 ROOSEVELT 6 230 525531 TOLK 6 230 2
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 113.33 | 524923 PORTALES 2 69.0 524929 RO-PORT_MTR2 69.0 @1
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 113 | 525001 W_MULESHOE 2 69.0 525008 MULESH_CTY 2 69.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 113 | 525008 MULESH_CTY 2 69.0 525027 BAILEYCO 2 69.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 113.28 | 525023 BC-BAIL_MTR2 69.0 525027 BAILEYCO 2 69.0 @1
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20807 | 113.27 | 525056 BC-EARTH 3 115 525480 PLANT_X 3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 113.09 | 525191 KRESS_INT 2 69.0 525203 SW-KRESS 2 69.0 Z1
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 113.17 | 525192 KRESS_INT 3 115 3WXFMR ENRCO 136155 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.21005 | 113.6 | 525213 SWISHER 6 230 525461 NEWHART 6 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.73 | 525272 KISER 3 115 3WXFMR VON 13819/1 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 113.19 | 525326 COX 3 115 3WXFMR ELCO 13474-3 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 113.21 | 525414 LAMTON 3 115 3WXFMR ASEA MLL9204 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20825 | 113.03 | 525440 LC-S_OLTON+3 115 525446 RKYFORD_TP 3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20825 | 113.03 | 525446 RKYFORD_TP 3 115 525480 PLANT_X 3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.2232 | 116.34 | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20984 | 114.35 | 525481 PLANT_X 6 230 3WXFMR WH ALM20171 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.2166 | 118.3 | 525481 PLANT_X 6 230 526435 SUNDOWN 6 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.2201 | 117.38 | 525481 PLANT_X 6 230 760498 G17-146-TAP 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.21052 | 113.07 | 525481 PLANT_X 6 230 762174 G17-218TAP 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.21094 | 113.14 | 525481 PLANT_X 6 230 762174 G17-218TAP 230 2
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.21867 | 118.38 | 525531 TOLK 6 230 525586 NEEDMORE 6 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20963 | 114.61 | 525531 TOLK 6 230 525637 LAMB_CNTY 6 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.23641 | 118.52 | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.21218 | 113.33 | 525531 TOLK 6 230 762174 G17-218TAP 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.21254 | 113.39 | 525531 TOLK 6 230 762174 G17-218TAP 230 2
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.33791 | 149.08 | 525549 TOLK 7 345 3WXFMR ABBXNL844501 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.21867 | 118.36 | 525586 NEEDMORE 6 230 526935 YOAKUM 6 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 113.01 | 525599 LC-SANDHLL+2 69.0 525606 AMHERST 2 69.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 113.04 | 525606 AMHERST 2 69.0 525613 W_LITTLFLD 2 69.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 113.07 | 525613 W_LITTLFLD 2 69.0 525635 LAMB_CNTY 2 69.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 113.02 | 525635 LAMB_CNTY 2 69.0 525650 LC-LTTLFLD+2 69.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20963 | 114.61 | 525637 LAMB_CNTY 6 230 3WXFMR WH ALM20172 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.87 | 525828 TUCO_INT 3 115 3WXFMR DS F78800913 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20714 | 112.4 | 525830 TUCO_INT 6 230 3WXFMR ENRCO 136401 2
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 113.07 | 526086 SW_6786_N 2 69.0 526087 SW_6786_S 2 69.0 Z1
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 113.07 | 526086 SW_6786_N 2 69.0 526102 SP-HETTLER 2 69.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 113.14 | 526087 SW_6786_S 2 69.0 526284 PLANTERS 2 69.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.69 | 526160 CARLISLE 3 115 3WXFMR WH RLP38371 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 113.03 | 526195 QUINCY 3 115 526196 SP-MILWAUKEE 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.93 | 526268 LUBBCK_STH 3 115 3WXFMR NA 70454A 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 113.19 | 526284 PLANTERS 2 69.0 526297 LUBBCK_EST 2 69.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.207 | 112.63 | 526435 SUNDOWN 6 230 3WXFMR UPDATE LATER _12 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20729 | 115 | 526435 SUNDOWN 6 230 526460 AMOCO_SS 6 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20702 | 112.65 | 526525 WOLFFORTH 6 230 3WXFMR UPDATE LATER _13 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 113.07 | 526735 TERRY_CNTY 2 69.0 526747 LG-BROWNFLD2 69.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 113 | 526747 LG-BROWNFLD2 69.0 526754 BROWNFIELD 2 69.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20694 | 114.41 | 526935 YOAKUM 6 230 527028 INK_BASIN 6 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20683 | 113.76 | 527028 INK_BASIN 6 230 527894 HOBBS_INT 6 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20699 | 113 | 527130 DENVER_N 3 115 527286 HIGGEAST 3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.61 | 527149 MUSTANG 6 230 3WXFMR ENRCO 136161 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20719 | 110.49 | 527149 MUSTANG 6 230 527151 GS-MUSTANG 6 230 @1
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.86 | 527202 SEAGRAVES 3 115 3WXFMR ABB MLL92408 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.76 | 527212 DIAMONDBACK3 115 3WXFMR HOW 36773714 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.68 | 527261 SULPHUR 2 69.0 527271 LG-FOSTER +2 69.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20699 | 112.98 | 527286 HIGGEAST 3 115 527363 HIGG 3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20702 | 112.82 | 527322 GAINES 3 115 527325 OXY_WSEM_TP3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20702 | 112.74 | 527325 OXY_WSEM_TP3 115 527362 JOHNSON_DRW3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.73 | 527340 DOSS 3 115 3WXFMR ELCO 13566/1 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.71 | 527345 LEGACY 2 69.0 527350 XTO_ROBRTSN2 69.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.71 | 527346 LEGACY 3 115 3WXFMR VROL 13735-1 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.69 | 527350 XTO_ROBRTSN2 69.0 527355 BOARDMAN 2 69.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.63 | 527355 BOARDMAN 2 69.0 527365 FLANNAGAN 2 69.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.61 | 527360 MAPCO 3 115 527362 JOHNSON_DRW3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.65 | 527362 JOHNSON_DRW3 115 528775 LE-ERF 3 115 @1
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20707 | 112.39 | 527455 RSWL_SLRCOL3 115 527482 CHAVES_CNTY3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20707 | 112.41 | 527470 CHVS_SLRCOL3 115 527464 CHVS_SOLAR11 34.5 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20707 | 112.34 | 527470 CHVS_SLRCOL3 115 527482 CHAVES_CNTY3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20887 | 112.88 | 527483 CHAVES_CNTY6 230 527799 EDDY_NORTH 6 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.62 | 527508 PRICE 3 115 527509 PRICE_TAP 3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.62 | 527529 RIACBRSH_TP3 115 527533 SW4J795_E 3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.62 | 527533 SW4J795_E 3 115 527564 ROSWLL_INT 3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.62 | 527563 ROSWLL_INT 2 69.0 527575 SW_4702 2 69.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20722 | 112.67 | 527564 ROSWLL_INT 3 115 527597 TWEEDY 3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.62 | 527575 SW_4702 2 69.0 527589 CV-ORCHARD 2 69.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.207 | 112.78 | 527653 MILO_WIND 1 34.5 527655 RSVLT_CC_E 7 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20692 | 112.66 | 527654 RSVLT_CC_W 7 345 527655 RSVLT_CC_E 7 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20692 | 112.95 | 527654 RSVLT_CC_W 7 345 527666 RSVLT_COL1 7 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20687 | 112.86 | 527655 RSVLT_CC_E 7 345 527656 CROSSROADS 7 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20692 | 112.95 | 527666 RSVLT_COL1 7 345 3WXFMR RSVLT_COL1 7 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.36 | 527736 NAVAJO_5TP 3 115 527739 NAVAJO_4 3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20704 | 112.35 | 527864 CUNNINHAM 3 115 528348 BUCKEYE_TP 3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20704 | 112.63 | 527864 CUNNINHAM 3 115 528568 MONUMNT_TP 3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20688 | 112.91 | 527865 CUNNIGHM_N 6 230 527867 CUNNIGHM_S 6 230 *1
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20699 | 112.64 | 527865 CUNNIGHM_N 6 230 527963 POTASH_JCT 6 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20704 | 112.4 | 527867 CUNNIGHM_S 6 230 3WXFMR WH 7000266 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.207 | 112.86 | 527867 CUNNIGHM_S 6 230 527882 CUNINGHAM2 1 20.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20701 | 112.79 | 527894 HOBBS_INT 6 230 527903 HOBBS_PLT3 1 18.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20704 | 112.36 | 527965 KIOWA 7 345 528027 RDRUNNER 7 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.36 | 528015 PHANTOM 7 345 528027 RDRUNNER 7 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.41 | 528024 RR_SVC_HV 3 115 528021 RDRUNNR_SVC1 15.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.68 | 528025 RDRUNNER 3 115 587990 GEN-2016-121 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.42 | 528185 N_LOVING 7 345 3WXFMR HYO1063400-1 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20704 | 112.41 | 528185 N_LOVING 7 345 528223 CHINA_DRAW 7 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.36 | 528222 CHINA_DRAW 3 115 528225 CD_SVC_HV 3 115 Z1
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20703 | 112.34 | 528333 LE-WEST_SUB3 115 528334 LE-NRTH_INT3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20704 | 112.42 | 528341 LE-SANANDRS3 115 528627 LE-TXACO_TP3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20704 | 112.38 | 528348 BUCKEYE_TP 3 115 528627 LE-TXACO_TP3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20701 | 112.62 | 528394 QUAHADA 3 115 528396 XTO_BIGEDDY3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20704 | 112.33 | 528463 SANGER_SW 3 115 528575 OXYPERMIAN 3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20704 | 112.33 | 528463 SANGER_SW 3 115 762442 G18-004-TAP 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20704 | 112.63 | 528568 MONUMNT_TP 3 115 528581 BYRD_TP 3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20704 | 112.38 | 528574 OXY_NHU_RCF3 115 528575 OXYPERMIAN 3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.69 | 528617 LE-WAITS 2 69.0 528325 LE-WAITS 3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.61 | 528617 LE-WAITS 2 69.0 528714 LE-FORT_SW 2 69.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20704 | 112.42 | 528622 LE-SANANDRS2 69.0 528341 LE-SANANDRS3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.97 | 528626 LE-PLNSINT 2 69.0 526928 PLAINS_INT 3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.97 | 528626 LE-PLNSINT 2 69.0 528709 LE-PLNSGOAB2 69.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.63 | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.69 | 528669 LE-STKLDRTP2 69.0 528740 LE-PLANS_SW2 69.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.85 | 528709 LE-PLNSGOAB2 69.0 528740 LE-PLANS_SW2 69.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.63 | 528709 LE-PLNSGOAB2 69.0 528747 LE-ALLRED 2 69.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.61 | 528714 LE-FORT_SW 2 69.0 528718 LE-NEWTEX 2 69.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.69 | 528735 LE-PLAINSUB2 69.0 528740 LE-PLANS_SW2 69.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20694 | 112.41 | 530583 POSTROCK7 345 588654 G17-021-TAP 345 2
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.41 | 531213 SANTAFE3 115 531408 PIERCVL3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20674 | 112.33 | 531451 MINGO 7 345 531465 SETAB 7 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20703 | 112.62 | 531501 BUCKNER7 345 531502 CIMRRN 7 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20703 | 112.62 | 531502 CIMRRN 7 345 531503 CIMRRN 1 34.5 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20691 | 112.32 | 531510 HARBNGR3 115 3WXFMR HARBGR345 _1 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20703 | 112.64 | 532663 LEC U5 24.0 532854 LEC U5 6 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20703 | 112.64 | 532853 LAWHILL6 230 532854 LEC U5 6 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20704 | 112.69 | 542951 HAW G5 1 22.0 543665 HAWTHN5 161 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20703 | 112.74 | 542955 LAC G1 1 22.0 542981 LACYGNE7 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20703 | 112.72 | 542956 LAC G2 1 24.0 542981 LACYGNE7 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20702 | 112.76 | 542957 IAT G1 1 24.0 542982 IATAN 7 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20703 | 112.82 | 542962 IAT G2 1 24.5 542982 IATAN 7 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20704 | 112.61 | 542966 WGARDNR5 161 543105 BULLCRK5 161 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20959 | 112.16 | 560022 CRAWFISH_DR 345 762216 G17-151TAP 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20926 | 113.18 | 560022 CRAWFISH_DR 345 762467 G18-015-TAP 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 108.98 | 560022 CRAWFISH_DR 345 763087 GEN-2018-073 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.21041 | 113.55 | 560022 CRAWFISH_DR 345 763215 G18-092-TAP 345 2
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 113.05 | 560252 G10-14 345 560253 G10-14-1 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.78 | 560253 G10-14-1 115 560254 G10-14-SUB1 34.5 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.78 | 560253 G10-14-1 115 560255 G10-14-SUB2 34.5 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.63 | 560581 G06-44-2 34.5 523111 NOVUS1 3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.68 | 560582 G06-44-3 34.5 560577 G06-44 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.66 | 560583 G06-44-4 34.5 560577 G06-44 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.32 | 560757 ASGI13_02_1 69.0 560758 ASGI13_02_2 34.5 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.32 | 560757 ASGI13_02_1 69.0 562731 WHEATLAND 69.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.33 | 560763 ASGI13_03_1 115 560761 ASGI13_03_2 34.5 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.76 | 562015 FIREWHEEL1 34.5 523215 FREWHELCOL17 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.76 | 562016 FIREWHEEL2 34.5 523215 FREWHELCOL17 345 2
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.31 | 562323 AGI1202&1305 115 562324 AGI1202&1305 34.5 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.32 | 562727 LESBIA 115 562728 SANJONTAP 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.32 | 562728 SANJONTAP 115 562729 CAPROCKTAP1 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.32 | 562730 CAPROCKTAP2 69.0 562729 CAPROCKTAP1 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.32 | 562730 CAPROCKTAP2 69.0 562731 WHEATLAND 69.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.72 | 563171 G15082_2 34.5 563170 G15082_1 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.4 | P11:13.8:AEPW:COM1-1
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.41 | P11:13.8:AEPW:COM2-1
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.41 | P11:13.8:AEPW:COM3-1
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.42 | P11:18:AEPW:WELSH1-1
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.42 | P11:18:AEPW:WELSH3-1
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.42 | P11:24:AEPW:PIRKEY 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.39 | P11:24:AEPW:SWS3-1
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.39 | P11:24:AEPW:TURKCOAL
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20717 | 112.7 | P12:138:AEPW-OMPA:DUNCAN-4:OMDUNCN4
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20706 | 112.66 | P12:138:AEPW:112GORE4:SNYDER-4
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20706 | 112.66 | 5841_Dup1
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20714 | 111.96 | 584560 GEN-2015-014 115 584561 G15-014XFMR1 34.5 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20713 | 112.65 | P12:138:AEPW:SANTAFE:DUNCAN-4
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.68 | 587991 G16-121XFMR1 34.5 587990 GEN-2016-121 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.62 | 588480 A16-010_SUB 115 3WXFMR A16-010_SUB 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20717 | 112.7 | P12:138:AEPW:DUNCAN-4:L.E.S.-4
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.06 | 588761 G17-033XFMR1 34.5 588760 GEN-2017-033 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.06 | 588765 G17-033XFMR2 34.5 588760 GEN-2017-033 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.63 | 588861 G17-047XFMR1 34.5 588860 GEN-2017-047 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20667 | 112.2 | P12:138:AEPW:ELKCTY-4:CLINTJC4
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.64 | 589381 G17-100XFMR1 34.5 589380 GEN-2017-100 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20679 | 112.39 | P12:138:AEPW:HOB-JCT4:ELKCTY-4
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.64 | P12:138:AEPW:SHERID4:112GORE4
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20703 | 112.61 | P12:230:AEPW:SWEETWT6:BUFFCK6
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20702 | 112.66 | P12:230:AEPW:SWEETWT6:ROARK6
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20947 | 114.5 | P12:345:AEPW:L.E.S7:TERRYRD7
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20947 | 114.49 | P12:345:AEPW:L.E.S7:TERRYRD7
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20947 | 114.47 | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.2101 | 114.61 | P12:345:AEPW-OKGE:L.E.S.-7:GRACMNT7
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.2101 | 114.58 | P12:345:AEPW-OKGE:L.E.S.-7:GRACMNT7
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20701 | 112.4 | P12:345:AEPW-OKGE:PITTSB-7:SEMINOL7
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.21019 | 115.66 | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.66 | P22:345:AMMO::LABADIE:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.66 | P22:345:AMMO::LABADIE:2
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.66 | P22:345:AMMO::LABADIE:3
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.66 | P22:345:AMMO::LABADIE:4
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.65 | P22:345:AMMO::RUSHISLAND:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.64 | P22:345:AMMO::RUSHISLAND:2
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20706 | 112.41 | P13:138-13.8:AEPW:COMANC-4_#2
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.2053 | 111.28 | P13:138-230:AEPW:ELKCTY-4
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20707 | 112.4 | P13:138-24:AEPW:S.W.S.-4
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20706 | 112.39 | P13:138-24:AEPW:TURK 4
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20713 | 112.63 | P13:138-345:AEPW:L.E.S.-4_#1
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20722 | 112.75 | P13:138-345:AEPW:L.E.S.-4_#2
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20706 | 112.67 | P23:500:EES-EAI:KEO:B4941
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20706 | 112.66 | P23:500:EES-EAI:KEO:B4921
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.61 | P11:26:EES-EAI:INDEP2:1:D401
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.61 | P11:26:EES-EAI:INDEP2:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.61 | P13:500:EES-EAI:INDEP2:MT2
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.65 | P23:500:EES-EAI:INDEP2:B6126
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.64 | P23:500:EES-EAI:PD:INDEP2:LN:FK479
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20703 | 112.61 | P13:230-34.5:AEPW:BUFFCK6
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20702 | 112.67 | P13:230-34.5:AEPW:ROARK6
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.41 | P13:69-13.8:AEPW:COMANC-2
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.66 | P11:024:DPC:ALMA2:6
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.62 | P11:18:ITCM:EMERYGT1:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.63 | P11:18:ITCM:EMERYGT2:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.63 | P11:161:ITCM:MGS CT1:1C
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.63 | P11:161:ITCM:MGS CT2:2C
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20703 | 112.64 | 652537 WHITE 3 345 659286 DEERCREK-BE3 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20703 | 112.64 | 659286 DEERCREK-BE3 345 3WXFMR DEERCRK KU1A 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.63 | 672601 BD 4 230 672306 BD 6G 18.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.63 | 672610 POPLAR 4 230 672310 POPLAR 1G 18.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.63 | 672610 POPLAR 4 230 672311 POPLAR 2G 18.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.62 | 672621 SHAND 4 230 672321 SHAND 1G 18.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.61 | 672649 CODETTE 4 230 672650 NIPAWIN 4 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.62 | 672696 BRADA 4 230 672699 NBEC 4 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.69 | P23:345:MDU::COYOTE::5707-5712-5715::::
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.84 | P23:345:MEC:CBEC 905
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.81 | P23:345:MEC:CBEC 908
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.64 | P23:345:MEC:GDMEC 908
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.74 | P23:345:MEC:RAUN 0180
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.8 | P23:345:MEC:RAUN 0210
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.75 | P23:345:MEC:LOUISA 954
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.75 | P23:345:MEC:LOUISA 964
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.61 | P21:115:XEL:AUTO-SINGLE:CHEMOLT7:LSPOWER7:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.65 | P21:115:XEL:AUTO-SINGLE:COLVILL7:CANONFLSG7:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.61 | P21:115:XEL:AUTO-SINGLE:FARIBALTP7:FARIBALTGEN:Z
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.7 | P21:230:OTP:AUTO-SINGLE:SQBUTTE4:YNG24:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.69 | P23:345:OTP:CENTER 3:3215(1)
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.69 | P23:345:OTP:CENTER 3:3225(1)
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.63 | P12:230:UMZW:# 687 #: FT IN SD. FT-BG1 LINE FAULT
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.63 | P12:230:UMZW:# 3617 #: FT IN SD. FT-BG2 LINE FAULT
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 111.33 | 760494 GEN-2017-146 230 760498 G17-146-TAP 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 111.32 | 760495 G17-146-XFM1 34.5 760494 GEN-2017-146 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.05 | 761356 G17-239-XFMR 34.5 761355 GEN-2017-239 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.05 | 761359 G17-239-XFMR 34.5 761355 GEN-2017-239 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.23 | 761797 G17-187XFM1 34.5 761796 GEN-2017-187 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.23 | 761800 G17-187XFM2 34.5 761796 GEN-2017-187 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 107.16 | 762132 GEN-2017-158 230 763252 G18-099-XFM1 34.5 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 107.16 | 762132 GEN-2017-158 230 763255 G18-099-XFM2 34.5 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 107.74 | 762133 G17-158XFM1 34.5 762132 GEN-2017-158 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 107.74 | 762136 G17-158XFM2 34.5 762132 GEN-2017-158 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 109.9 | 762216 G17-151TAP 345 762217 GEN-2017-151 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20959 | 113.55 | 762216 G17-151TAP 345 762467 G18-015-TAP 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 111.85 | 762218 G17-151XFM1 34.5 762217 GEN-2017-151 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 111.85 | 762221 G17-151XFM2 34.5 762217 GEN-2017-151 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 111.85 | 762224 G17-151XFM3 34.5 762217 GEN-2017-151 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 111.85 | 762227 G17-151XFM4 34.5 762217 GEN-2017-151 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.36 | 762438 GEN-2018-004 115 762442 G18-004-TAP 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 110.89 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 111.7 | 762461 G18-015-XFM1 34.5 762460 GEN-2018-015 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 111.7 | 762464 G18-015-XFM2 34.5 762460 GEN-2018-015 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20843 | 113.07 | 762467 G18-015-TAP 345 763215 G18-092-TAP 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 110.18 | 763087 GEN-2018-073 345 763088 G18-073-XFM1 34.5 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 111.33 | 763087 GEN-2018-073 345 763091 G18-073-XFM2 34.5 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 107.16 | 763120 GEN-2018-081 230 763121 G18-081-XFM1 34.5 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 109.42 | 763120 GEN-2018-081 230 764011 G19-074-XFM1 34.5 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 109.44 | 763186 GEN-2018-089 230 763187 G18-089-XFM1 34.5 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 110.21 | 763208 GEN-2018-092 345 763215 G18-092-TAP 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 111.37 | 763208 GEN-2018-092 345 763220 G18-092-XFM1 34.5 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 111.37 | 763208 GEN-2018-092 345 763223 G18-092-XFM2 34.5 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 108.87 | 763241 GEN-2018-097 230 763242 G18-097-XFM1 34.5 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 109.78 | 763241 GEN-2018-097 230 763296 G18-111-XFM1 34.5 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 109.14 | 763241 GEN-2018-097 230 763307 G18-112-XFM1 34.5 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 109.14 | 763241 GEN-2018-097 230 763310 G18-112-XFM2 34.5 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 108.87 | 763241 GEN-2018-097 230 763395 G18-124-XFM1 34.5 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 108.87 | 763241 GEN-2018-097 230 763398 G18-124-XFM2 34.5 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.29 | 763318 GEN-2018-115 345 763319 G18-115-XFM1 34.5 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.75 | 763340 GEN-2018-117 230 763341 G18-117-XFM1 34.5 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 108.51 | 763483 GEN-2019-003 230 763484 G19-003-XFM1 34.5 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 111.19 | 763483 GEN-2019-003 230 763605 G19-021-XFM1 34.5 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 111.9 | 763516 GEN-2019-011 345 763517 G19-011-XFM1 34.5 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.26 | 763879 GEN-2019-056 115 763880 G19-056XFM1 34.5 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20655 | 112.68 | P42:345:OKGE:SB_BVTY7305
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20697 | 112.43 | P23:345:WERE:BUFF_345-534::
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20697 | 112.43 | P23:345:WERE:BUFF_345-543::
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20701 | 112.78 | P23:345:WERE:JEC_345-15::
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.207 | 112.75 | P23:345:WERE:JEC_345-16::
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20701 | 112.78 | P23:345:WERE:JEC_345-19::
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20701 | 112.78 | P23:345:WERE:JEC_345-20::
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.95 | P23:345:WERE:WOLF_345-50::
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.95 | P23:345:WERE:WOLF_345-60::
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20706 | 112.43 | P42:345:AEPW:WELSH CB 10620 NBTB+FAULT
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.21019 | 114.21 | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.21043 | 114.99 | P42:345:AEPW:LAWTON EASTSIDE CB 3413A NBTB+FAULT
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.21079 | 115.4 | P42:345:AEPW:LAWTON EASTSIDE CB 3425A NBTB+FAULT
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.21033 | 115.86 | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20719 | 112.31 | P42:345:AEPW:PITTSBURG CB 3441A NBTB+FAULT
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20701 | 112.4 | P42:345:AEPW:PITTSBURG CB 3445A NBTB+FAULT
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20947 | 114.49 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20947 | 114.49 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20947 | 114.47 | P42:345:AEPW:TERRYRD_CB_3421A_NBTB
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20703 | 112.75 | P23:345:KCPL:LACYGNE_R2-5::LACYGU2-LACYGNE-STILWELL
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20706 | 112.43 | P23:345:AEPW:WELSH CB 10620 NBTB
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.21019 | 114.54 | P23:345:AEPW:OKLAUNION CB 3401A NBTB
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.21043 | 114.99 | P23:345:AEPW:LAWTON EASTSIDE CB 3413A NBTB
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.21079 | 115.4 | P23:345:AEPW:LAWTON EASTSIDE CB 3425A NBTB
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.21033 | 115.86 | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20719 | 112.31 | P23:345:AEPW:PITTSBURG CB 3441A NBTB
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20701 | 112.4 | P23:345:AEPW:PITTSBURG CB 3445A NBTB
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20947 | 114.49 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20947 | 114.49 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20947 | 114.47 | P23:345:AEPW:TERRYRD_CB_3421A_NBTB
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20736 | 112.62 | P12:138:AEPW:S.W.S.-4:L.E.S.-4
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.65 | P11:115:SUNC:GARDENCITY_S2:97:531459(2)
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20966 | 114.72 | P23:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.21223 | 117.32 | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20966 | 114.72 | P42:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB+FAULT
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.21223 | 117.32 | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20674 | 112.33 | P23:345:SUNC:MO_BRK182
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20674 | 112.33 | P23:345:SUNC:MO_BRK382
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20702 | 112.42 | P21:345:UMZW:# 725 #: GI IN NE. GI-SWEET LINE FAULT
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.2086 | 112.8 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20706 | 112.41 | P12:138-13.8:AEPW:COMANC-4_#1
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.2053 | 111.26 | P12:230:AEPW:ELKCITY6:CHISHOLM6
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20849 | 113.54 | P12:230:AEPW:SWEETWT6:CHISHOLM6
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997715 ABBXNL844501 230 1 |  | 553 | 0.33791 | 150.96 | 525531 TOLK 6 230 3WXFMR TOLK 6 2
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20706 | 112.73 | P23:345:KCPL-WERE:237LACYGNE_R1-6::LACYGU1-LACYGNE-NEOSHO
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20703 | 112.64 | P11:230:WERE:LECU5_GEN::
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20704 | 112.63 | P11:161:GMO:DOGWOOD_COMBINED_CYCLE_UNIT_OUTAGE_1_1
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.2071 | 111.16 | P11:115:SPS:MUSTANG1&3:153MW::::
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20963 | 114.61 | P12:230:SPS:K37::1_TOLK_LAMB:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20723 | 112.61 | P12:230:SPS:K43::1_PRNGLE_HARR_E:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20707 | 112.37 | P12:230:SPS:K44::1_EPLNT_HARRW:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20718 | 112.79 | P12:115:SPS:T04::1_TRBLNC_CASTRO:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20704 | 112.19 | P12:115:SPS:T13::1_TAYLOR_WHOBBS:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20704 | 112.31 | P12:115:SPS:T14::1_MADDOX_TAYLOR:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 113.09 | P12:115:SPS:T21::1_GRSSLND_GRAHAM:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20704 | 112.41 | P12:115:SPS:T23::1_PCA_POTJCT:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.62 | P12:115:SPS:T24B::1_RSWLL_BRSHRF:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.64 | P12:115:SPS:T26::1_CHAVES_RSWLCTY:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20825 | 113.18 | P12:115:SPS:T28A::1_LAMTON_PLANTX:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20749 | 112.67 | P12:115:SPS:T29::1_LAMTON_HALECTR:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20876 | 113.96 | P12:115:SPS:T30::1_LAMB_HOCKLY:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20876 | 113.13 | P12:115:SPS:T31::1_HOCKLY_SUNDWN:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.207 | 112.63 | P12:115:SPS:T35::1_TERRY_YOAKUM:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 113.32 | P12:115:SPS:T45::1_NORRIS_OASIS:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20703 | 112.4 | P12:115:SPS:T57::1_MUSTG_SEGRVS:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20831 | 113.15 | P12:115:SPS:T59::1_CARGIL_CURRY:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.208 | 112.42 | P12:115:SPS:T66::1_RNDALL_HAPPY:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.208 | 112.9 | P12:115:SPS:T67::1_HAPPY_KRESS:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20709 | 112.39 | P12:115:SPS:T68::1_TUCO_FLOYD:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20699 | 113.2 | P12:115:SPS:T71::1_CRLSLE_YUMA:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20713 | 112.7 | P12:115:SPS:T81::1_COX_FLOYD:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20704 | 112.85 | P12:115:SPS:T83::1_SP-FKFD_ALLEN:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20699 | 113.01 | P12:115:SPS:T89::1_DC_N_HIGG:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.66 | P12:115:SPS:T91::1_HIGG_RUSSELL:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20727 | 112.62 | P12:115:SPS:V04::1_EPLANT_RNDALL:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20718 | 112.67 | P12:115:SPS:V07::1_COX_HALECTR:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20817 | 112.95 | P12:115:SPS:V09::1_HALECTR_PLANTX:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20703 | 112.83 | P12:115:SPS:V12::1_PLANTX_BAILEY:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20704 | 112.62 | P12:115:SPS:V15::1_TUCO_INDANA:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20667 | 112.67 | P12:115:SPS:V24::1_WOLFTH_TERRY:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20722 | 112.64 | P12:115:SPS:V26::1_RSWLL_EDDY_N:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.98 | P12:115:SPS:V33::1_LUBBS_LYNN:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20807 | 113.85 | P12:115:SPS:V37::1_CASTRO_PLANTX:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.75 | P12:115:SPS:V46::1_ALLEN_WHEELCK:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20706 | 113.09 | P12:115:SPS:V49::1_YOAKUM_SHLCO2:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20748 | 113.26 | P12:115:SPS:V55::1_SUNDWN_TERRY:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20718 | 113.09 | P12:115:SPS:V56::1_COCHRAN_SUNDWN:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20704 | 112.68 | P12:115:SPS:V62::1_CRLSLE_INDANA:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20706 | 112.62 | P12:115:SPS:V70::1_S_GORG_RNDALL:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20717 | 112.65 | P12:115:SPS:V78::2_CURRY_RSVLT:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20703 | 112.79 | P12:115:SPS:V81::1_LE-WAIT_LE-LVN:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.65 | P12:115:SPS:V95::1_DC_N_SHLCO2:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.61 | P12:115:SPS:W11::1_DC_S_SMINLE:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20704 | 112.61 | P12:115:SPS:W12::1_SMINLE_DOSS:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20704 | 112.68 | P12:115:SPS:W14::1_SMINLE_GAINES:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 113.14 | P12:115:SPS:W32::1_PRMTR_FE-CLSIN:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.61 | P12:115:SPS:W34::1_JNSDRW_MAPCO:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20702 | 112.85 | P12:115:SPS:W35::1_GAINES_JNSDRW:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20699 | 112.64 | P12:115:SPS:W36::1_TAYLOR_JNSDRW:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20895 | 113.15 | P12:115:SPS:W40::1_WCANYON_TRBLNC:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20732 | 112.71 | P12:115:SPS:W52::1_NEWHART_KRESS:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 113.2 | P12:115:SPS:W58::1_NORTON_LOPEZ:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.82 | P12:115:SPS:W59::1_LOPEZ_CMPBLL:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20706 | 113.15 | P12:115:SPS:W62::1_PLSTHL_CURRY:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20717 | 112.62 | P12:115:SPS:W63::1_PLSTHL_CURRY:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.96 | P12:115:SPS:W64::1_PLSTHL_FE-CLV:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20706 | 113.12 | P12:115:SPS:W65::1_PLSTHL_CURRY:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.81 | P12:115:SPS:W66::1_PORTA_GREYHUND:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20895 | 112.61 | P12:115:SPS:W77::1_RNDAL_WCANYON:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.64 | P12:115:SPS:W99::1_CAPITAN_CHAVES:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.207 | 113.08 | P12:115:SPS:U14::1_DC_STH_INKBSN:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20703 | 113.02 | P12:115:SPS:V15::1_INKBSN_LE-WAT:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20727 | 112.74 | P12:115:SPS:U16::1_BSHLND_OUTPST:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20727 | 112.73 | P12:115:SPS:U17::1_COLTR_OUTPST:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20711 | 112.8 | P12:115:SPS:U19::1_DEAN_PLAINS:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20727 | 112.67 | P12:115:SPS:U23::1_COLTR_HILSDE:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20704 | 112.62 | P11:18:HAST:::EGYCTR2G WEC2_LOSS OF WEC 2 GEN_:HV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20704 | 112.62 | P13:18-115:HAST:::EGYCNTR7 XFMR G2WEC 2 GSU_:HV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20704 | 112.63 | P11:161:GMO:DOGWOOD-COMBINED-CYCLE-UNIT-OUTA:::HV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20706 | 112.73 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20703 | 112.75 | P23:345:KCPL:LACYGNE-R2-5:::EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20701 | 112.78 | P11:230:WERE:JECU1-GEN:::HV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20703 | 112.64 | P11:230:WERE:LECU5-GEN:::HV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20701 | 112.78 | P11:345:WERE:JECU2-GEN:::EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20701 | 112.78 | P11:345:WERE:JECU3-GEN:::EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.95 | P11:345:WERE:WOLFU1-GEN:::EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20697 | 112.43 | P23:345:WERE:BUFF-345-534:::EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20697 | 112.43 | P23:345:WERE:BUFF-345-543:::EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20701 | 112.78 | P23:345:WERE:JEC-345-15:::EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.207 | 112.75 | P23:345:WERE:JEC-345-16:::EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20701 | 112.78 | P23:345:WERE:JEC-345-19:::EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20701 | 112.78 | P23:345:WERE:JEC-345-20:::EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.95 | P23:345:WERE:WOLF-345-50:::EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.95 | P23:345:WERE:WOLF-345-60:::EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.89 | P11:022:NPPD:COOPER1G:1:983:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.207 | 112.92 | P11:023:NPPD:GENTLM1G:1:757:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.207 | 112.94 | P11:024:NPPD:GENTLM2G:2:757:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20702 | 112.75 | P13:345:OPPD:NEBCTY1G:::EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.207 | 112.78 | P13:345:OPPD:NEBCTY2G:::EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.77 | P22:345:OPPD:S3458 NEBCTY1G:LT::EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20702 | 112.75 | P22:345:OPPD:S3458 NEBCTY1G:::EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.81 | P22:345:OPPD:S3458 NEBCTY2G:LT::EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.207 | 112.78 | P22:345:OPPD:S3458 NEBCTY2G:::EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.77 | P23:345:OPPD:S3458 NEBCTY1G:LT::EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20702 | 112.75 | P23:345:OPPD:S3458 NEBCTY1G:::EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.81 | P23:345:OPPD:S3458 NEBCTY2G:LT::EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.207 | 112.78 | P23:345:OPPD:S3458 NEBCTY2G:::EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.4 | P12:115:SUNC:PLYMELL-PIERCEVILLE:::HV::
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20703 | 112.64 | P11:018:UMZB:# 5 #:: DCS IN SD. DEERCREEK_MV::
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20704 | 112.61 | P11:022:UMZB:# 15 #:: LO IN ND. LELAND OLDS 1_MV::
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20703 | 112.65 | P11:020:UMZB:# 16 #:: LO IN ND. LELAND OLDS 2_MV::
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20702 | 112.7 | P11:023:UMZB:# 31 #:: AVS IN ND. ANTELOPE VALLEY 1_MV::
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20702 | 112.7 | P11:023:UMZB:# 32 #:: AVS IN ND. ANTELOPE VALLEY 2_MV::
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20699 | 112.9 | P11:024:UMZB:# 33 #:: LRS IN WY. LARAMIE RIVER STATION 1_MV::
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.63 | P12:230:UMZW:# 687 #:: FT IN SD. FT-BG1 BRANCH FAULT:HV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.63 | P12:230:UMZW:# 3617 #:: FT IN SD. FT-BG2 BRANCH FAULT:HV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.63 | P12:230:UMZW:# 4038 #:: BG-FT IN SD. FAULT FOR TRANSMISSION CIRCUIT (BG-FT).:HV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.63 | P12:230:UMZW:# 4039 #:: BG-FT IN SD. FAULT FOR TRANSMISSION CIRCUIT (BG-FT).:HV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.61 | P13:230:UMZW:# 5135 #:: OA IN SD. FAULT ON TRANSFORMER (2).:HV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.61 | P13:230:UMZW:# 5136 #:: OA IN SD. FAULT ON TRANSFORMER (3).:HV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20702 | 112.42 | P21:345:UMZW:# 725 #:: GI IN NE. GI-SWEET BRANCH FAULT:EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20702 | 112.42 | P23:345:UMZW:# 2430 #:: GI IN NE. GI 1492 BKR FAULT:EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20702 | 112.42 | P23:345:UMZW:# 2438 #:: GI IN NE. GI-SWEET BRANCH FAULT & GI 1492 STUCK BKR:EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20707 | 112.37 | P11:138:WFEC:HUGO1:465MW :::
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20701 | 112.4 | P12:345:OKGE-AEPW:BKRBKR20::::
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.2074 | 112.75 | P12:345:OKGE:BKRBKR21::::
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20759 | 112.95 | P12:345:OKGE:BKRBKR24::::
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20947 | 114.47 | P12:345:OKGE-AEPW:BKRBKR25::::
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20695 | 112.42 | P12:345:OKGE:BKRBKR336::::
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20695 | 112.41 | P12:345:OKGE:BKRBKR336_2::::
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.2101 | 114.61 | P12:345:OKGE-AEPW:BKRBKR366::::
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.2101 | 114.58 | P12:345:OKGE-AEPW:BKRBKR366::::
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.2076 | 112.87 | P12:345:OKGE:BKRBKR367::::
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20736 | 112.62 | P12:345:OKGE-WFEC:BKRBKR374::::
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20663 | 112.22 | P12:345:OKGE:BKRBKR4193::::
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20663 | 112.22 | P12:345:OKGE:BKRBKR4194::::
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20647 | 112.28 | P12:345:OKGE-SPS:BKRBKR4201::::
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20647 | 112.28 | P12:345:OKGE-SPS:BKRBKR4202::::
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20694 | 112.35 | P12:345:OKGE:BKRBKR443NEW::::
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20694 | 112.35 | P12:345:OKGE:BKRBKR443NEW2::::
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20698 | 112.88 | P12:345:OKGE:BKRBKR604::::
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20698 | 112.94 | P12:345:OKGE:BKRBKR604_2::::
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20656 | 112.62 | P42:345:OKGE:SB_ARIA7381::::
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.21489 | 116.05 | P42:345:OKGE:SB_BVTY7387::::
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.2074 | 112.68 | P42:345:OKGE:SB_SPCK7383::::
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20703 | 112.64 | P11:115:SUNC:GARDENCITY_S2:103:531459(2):HV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20703 | 112.64 | P11:115:SUNC:FORTDDODGE_4:157:539670(4):HV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.62 | P11:345:599:CIMARRON1WIND:200:531603(1):EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.92 | P13:115:SUNC:HOLCOMB_GSU:::HV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20703 | 112.64 | P13:115:SUNC:S2_GSU:::HV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20703 | 112.64 | P13:115:SUNC:FORTDODGE_GSU:::HV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20703 | 112.62 | P23:345:SUNC:BU_BRK682:::EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.71 | 300003 1THLG3 24.0 301503 7THOMHLGSU3 345 3
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.71 | 300049 7THOMHL 345 301503 7THOMHLGSU3 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.66 | P11:20:AMMO:1LAB�� G1:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.66 | P11:20:AMMO:1LAB�� G2:2
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.83 | P11:345:AMMO::CALLAWAY:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.66 | P11:345:AMMO::LABADIE:3
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.66 | P11:345:AMMO::LABADIE:4
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.66 | P11:345:AMMO::RUSHISLAND:U1
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.66 | P11:345:AMMO::RUSHISLAND:U2
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.64 | P11:138:AMMO::SIOUX:2
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.64 | P12:765:AEP:AEP ROCKP-AEP JEFF 765
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.61 | P11:HV:EES::1ISES U1:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.61 | P11:EHV:EES::1ISES U2:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.42 | P11:HV:EES::PIRKEY 1:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.42 | P11:EHV:EES::WELSH3-1:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.39 | P11:HV:EES::TURKCOAL:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.61 | P12:HV:EES::5ISES%:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.61 | P12:EHV:EES::8ISES%:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.82 | P12:EHV:EES::7CALAWY 1:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20706 | 112.39 | P12:HV:EES::TURK 4%:1(1)
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.64 | 344011 7HUGHES 345 344012 7HPW-N 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.66 | 344884 7LABADIE1 345 344894 1LAB G1 20.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.66 | 344885 7LABADIE2 345 344895 1LAB G2 20.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.66 | 344886 7LABADIE3 345 344896 1LAB G3 20.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.66 | 344887 7LABADIE4 345 344897 1LAB G4 20.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.65 | 345667 7RUSH 1 345 345670 1RUSH G1 18.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.65 | 345668 7RUSH 2 345 345671 1RUSH G2 18.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.64 | 345755 4SIOUX 1 138 345756 1SIOUX 1 18.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.64 | 345764 4SIOUX 2 138 345765 1SIOUX 2 18.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.69 | P12:345:MDU::CENTER:COYOTE:1::::
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.69 | P13:345:MDU:COYOTE GSU LOSS:COYOTE::1::::
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.61 | P11:345:MEC:GDMEC CT1
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.61 | P11:345:MEC:GDMEC CT2
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.71 | P11:345:MEC:GDMEC ST
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.9 | P11:345:MEC-NPPD:COOPER 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.8 | P11:24:XEL:AUTO-SINGLE:SHERC31G:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.8 | P11:24:XEL:AUTO-SINGLE:SHERC32G:2
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.87 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.73 | P11:20:XEL:AUTO-SINGLE:PRIS31G:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.73 | P11:20:XEL:AUTO-SINGLE:PRIS32G:2
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.76 | P11:22:XEL:AUTO-SINGLE:MNTCE31G:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.73 | P11:20:XEL:AUTO-SINGLE:KING31G:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.77 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.77 | P11:22:GRE:AUTO-SINGLE:GRE-COAL42G:2
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.71 | P11:24:OTP:AUTO-SINGLE:BIGSTN1G:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.71 | P11:20:OTP:AUTO-SINGLE:CENTER2G:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.63 | P11:22:OTP:AUTO-SINGLE:CENTER1G:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.7 | P11:24:OTP:AUTO-SINGLE:COYOTE1G:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.63 | P11:24:DPC:AUTO-SINGLE:GENOA53G:3
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.61 | P12:115:XEL:AUTO-SINGLE:CHEMOLT7:LSPOWER7:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.65 | P12:115:XEL:AUTO-SINGLE:COLVILL7:CANONFLSG7:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.61 | P12:115:XEL:AUTO-SINGLE:FARIBALTP7:FARIBALTGEN:Z
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.7 | P12:230:OTP:AUTO-SINGLE:SQBUTTE4:YNG24:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.78 | P13:24-345:XEL:AUTO-SINGLE:SHERC31G:SHERCO3:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.78 | P13:24-345:XEL:AUTO-SINGLE:SHERC32G:SHERCO3:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.85 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.73 | P13:20-345:XEL:AUTO-SINGLE:PRIS31G:PRISLD3:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.73 | P13:20-345:XEL:AUTO-SINGLE:PRIS32G:PRISLD3:2
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.76 | P13:22-345:XEL:AUTO-SINGLE:MNTCE31G:MNTCELO3:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.72 | P13:20-345:XEL:AUTO-SINGLE:KING31G:ASKING3:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.76 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL41G:GRE-COALCR4:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.75 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL42G:GRE-COALCR4:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.7 | P13:230-24:OTP:AUTO-SINGLE:BIGSTON4:BIGSTN1G:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.7 | P13:20-230:OTP:AUTO-SINGLE:CENTER2G:YNG24:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.62 | P13:22-230:OTP:AUTO-SINGLE:CENTER1G:CENTER4:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.69 | P13:24-345:OTP:AUTO-SINGLE:COYOTE1G:COYOTE3:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.63 | P13:24-161:DPC:AUTO-SINGLE:GENOA53G:GENOA5:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.64 | P13:24-161:DPC:AUTO-SINGLE:JPM:ALMA5:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.7 | P11:115:XEL:RIV COMBINE CYCLE
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.62 | P12:115:XEL:BDS #2 5
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.62 | P11:115:XEL:HBR #6
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.62 | P11:115:XEL:HBR #7
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.73 | P11:115:XEL:HBR #6 7 8
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.73 | P23:345:XEL:8H14 PRI
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.73 | P23:345:XEL:8H17 PRI AS
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.85 | P23:345:XEL:8N28 SHC
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.78 | P23:345:XEL:8N22 SHC
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.78 | P23:345:XEL:8N17 SHC
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.77 | P23:345:XEL:8N8 MNN
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.72 | P23:345:XEL:8P1 KING
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.72 | P23:345:XEL:8P2 KING
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.62 | P23:115:XEL:5P147 IVH AS
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.61 | P11:18:ALTW:AUTO-SINGLE:EMERYST1:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.61 | P11:22:ALTW:AUTO-SINGLE:LANS54G:4
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.74 | P11:22:ALTW:AUTO-SINGLE:ARNOLD1G:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.77 | P11:24:ALTW:AUTO-SINGLE:OTTUMW1G:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.61 | P13:18-161:ALTW:AUTO-SINGLE:EMERYST1:EMERY5:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.61 | P13:22-161:ALTW:AUTO-SINGLE:LANS54G:LANSINGL15:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.73 | P13:22-161:ALTW:AUTO-SINGLE:ARNOLD1G:ARNOLD5:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.76 | P13:24-161:ALTW:AUTO-SINGLE:OTTUMW1G:OTTUMWA5:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.82 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.88 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.75 | P11:22:MEC:AUTO-SINGLE:NEAL3G:3
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.81 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.76 | P11:24:MEC:AUTO-SINGLE:LOUIS31G:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.81 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.84 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.74 | P13:345-22:MEC:AUTO-SINGLE:RAUN3:NEAL3G:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.8 | P13:345-24:MEC:AUTO-SINGLE:RAUN3:NEAL4G:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.74 | P13:345-24:MEC:AUTO-SINGLE:LOUISA3:LOUIS31G:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20701 | 112.78 | P11:230:WERE:JECU1_GEN::
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20701 | 112.78 | P11:345:WERE:JECU2_GEN::
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20701 | 112.78 | P11:345:WERE:JECU3_GEN::
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.95 | P11:345:WERE:WOLFU1_GEN::
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20706 | 112.63 | 511435 SNYDER-4 138 588779 TAP_G17-036 138 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20679 | 112.38 | 511446 CL-AFTP4 138 511458 ELKCTY-4 138 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20679 | 112.4 | 511446 CL-AFTP4 138 511463 HOB-JCT4 138 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20713 | 112.63 | 511453 DUNCAN-4 138 511552 DUNCHERTP4 138 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20713 | 112.62 | 511455 D.E.S.-4 138 511552 DUNCHERTP4 138 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20713 | 112.62 | 511455 D.E.S.-4 138 529344 OMDUNE-4 138 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.63 | 511456 O.K.U.-7 345 511565 OKLAUN HVDC7 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 111.6 | 511456 O.K.U.-7 345 588760 GEN-2017-033 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.21019 | 114.54 | 511456 O.K.U.-7 345 763215 G18-092-TAP 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.21033 | 115.11 | 511468 L.E.S.-7 345 762467 G18-015-TAP 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20927 | 114.48 | 511468 L.E.S.-7 345 763215 G18-092-TAP 345 2
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.29 | 511468 L.E.S.-7 345 763318 GEN-2018-115 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20706 | 112.66 | 511488 112GORE4 138 511510 LAIRGST4 138 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20717 | 112.7 | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20706 | 112.65 | 511500 CACHE4 138 511510 LAIRGST4 138 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20706 | 112.64 | 511500 CACHE4 138 588779 TAP_G17-036 138 2
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.2086 | 112.8 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.75 | 511541 SWEETWT6 230 763340 GEN-2018-117 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20224 | 109.9 | 511553 CHISHOLM7 345 523961 POTTER_CO 7 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20224 | 109.9 | 511553 CHISHOLM7 345 523961 POTTER_CO 7 345 2
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.21489 | 116.03 | 515375 WWRDEHV7 345 515458 BORDER 7 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.21489 | 116.05 | 515458 BORDER 7 345 560022 CRAWFISH_DR 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20702 | 112.7 | 515618 BALKOW 7 345 3WXFMR BALKOW 7 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20702 | 112.7 | 515618 BALKOW 7 345 3WXFMR BALKOW 7 1_Dup1
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20698 | 112.95 | 515634 PALDR1W7 345 3WXFMR PALO2 _1 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.7 | 515677 BADGER 7 345 563170 G15082_1 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20698 | 112.61 | 520827 BINGERJ4 138 521017 ONEY 4 138 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20698 | 112.62 | 521017 ONEY 4 138 521089 WASHITA4 138 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.61 | 522800 MU-TULIA 3 115 525179 TULIA_TP 3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.75 | 522892 MU-BROWNFLD2 69.0 526761 BROWNFLD_TP2 69.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.64 | 523090 TEXAS_CNTY 3 115 589380 GEN-2017-100 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.207 | 112.78 | 523093 HITCHLAND 3 115 523174 GOODWELLWND3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.95 | 523097 HITCHLAND 7 345 523112 NOVUS1 7 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 113 | 523097 HITCHLAND 7 345 523215 FREWHELCOL17 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20478 | 111.48 | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 113.05 | 523097 HITCHLAND 7 345 560252 G10-14 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.62 | 523099 TC-DRYTRLS 3 115 588480 A16-010_SUB 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.82 | 523112 NOVUS1 7 345 3WXFMR NOVUS XF2 2
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.63 | 523112 NOVUS1 7 345 3WXFMR XIANA2011198 _1 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20703 | 112.61 | 523118 BUFF_DUNES 7 345 523853 FINNEY 7 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.63 | 523120 COLE 3 115 588860 GEN-2017-047 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20703 | 112.64 | 523172 GWELL_COLL11 34.5 523174 GOODWELLWND3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20703 | 112.65 | 523173 GWELL_COLL21 34.5 523174 GOODWELLWND3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20723 | 112.61 | 523267 PRINGLE 6 230 3WXFMR ENRCO13617-1 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20723 | 112.61 | 523267 PRINGLE 6 230 523979 HARRNG_EST 6 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20792 | 113.07 | 523771 GRAPEVINE 6 230 524044 NICHOLS 6 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.21511 | 113.75 | 523959 POTTER_CO 6 230 524267 BUSHLAND 6 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.21476 | 114.67 | 523959 POTTER_CO 6 230 525461 NEWHART 6 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20929 | 118.42 | 523961 POTTER_CO 7 345 3WXFMR WAUK 90343-A 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20703 | 112.4 | 523978 HARRNG_MID 6 230 523979 HARRNG_EST 6 230 @1
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20704 | 112.39 | 524010 ROLLHILLS 6 230 3WXFMR WAUK WT01104 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20727 | 112.74 | 524267 BUSHLAND 6 230 3WXFMR WH 7001795 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.22157 | 114.31 | 524267 BUSHLAND 6 230 524623 DEAFSMITH 6 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20691 | 113.07 | 524296 SPNSPUR_WND7 345 524299 SPNSPUR_COL7 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20691 | 113.07 | 524299 SPNSPUR_COL7 345 3WXFMR SPNSPUR_COL7 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.21086 | 113.32 | 524415 AMA_SOUTH 6 230 525213 SWISHER 6 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 113.2 | 524502 NORTON 3 115 524509 FE-TUCMCARI3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20895 | 113.01 | 524575 DS-#25+ 3 115 524597 PANDAHFD 3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20895 | 113.12 | 524575 DS-#25+ 3 115 524630 TIERABLANCA3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.7 | 524604 HEREFRD_SB 2 69.0 524608 HERFRD_STH 2 69.0 *1
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.2201 | 119.12 | 524623 DEAFSMITH 6 230 760498 G17-146-TAP 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 113.1 | 524721 DS-#15&#19+2 69.0 524745 CASTRO_CNTY2 69.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20711 | 112.61 | 524770 PLSNT_HILL 6 230 3WXFMR EFAE1100068A 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.21135 | 117.92 | 524875 OASIS 6 230 524885 SN_JUAN_TAP6 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20779 | 113.69 | 524875 OASIS 6 230 524909 ROOSEVELT 6 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.21126 | 118.38 | 524885 SN_JUAN_TAP6 230 527483 CHAVES_CNTY6 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20721 | 112.8 | 524909 ROOSEVELT 6 230 3WXFMR ABB LMM60042 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.21401 | 118.36 | 524909 ROOSEVELT 6 230 525531 TOLK 6 230 2
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 113.33 | 524923 PORTALES 2 69.0 524929 RO-PORT_MTR2 69.0 @1
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 113 | 525001 W_MULESHOE 2 69.0 525008 MULESH_CTY 2 69.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 113 | 525008 MULESH_CTY 2 69.0 525027 BAILEYCO 2 69.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 113.28 | 525023 BC-BAIL_MTR2 69.0 525027 BAILEYCO 2 69.0 @1
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20807 | 113.27 | 525056 BC-EARTH 3 115 525480 PLANT_X 3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 113.09 | 525191 KRESS_INT 2 69.0 525203 SW-KRESS 2 69.0 Z1
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 113.17 | 525192 KRESS_INT 3 115 3WXFMR ENRCO 136155 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.21005 | 113.6 | 525213 SWISHER 6 230 525461 NEWHART 6 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.73 | 525272 KISER 3 115 3WXFMR VON 13819/1 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 113.19 | 525326 COX 3 115 3WXFMR ELCO 13474-3 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 113.21 | 525414 LAMTON 3 115 3WXFMR ASEA MLL9204 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20825 | 113.03 | 525440 LC-S_OLTON+3 115 525446 RKYFORD_TP 3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20825 | 113.03 | 525446 RKYFORD_TP 3 115 525480 PLANT_X 3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.2232 | 116.34 | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20984 | 114.35 | 525481 PLANT_X 6 230 3WXFMR WH ALM20171 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.2166 | 118.3 | 525481 PLANT_X 6 230 526435 SUNDOWN 6 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.2201 | 117.38 | 525481 PLANT_X 6 230 760498 G17-146-TAP 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.21052 | 113.07 | 525481 PLANT_X 6 230 762174 G17-218TAP 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.21094 | 113.14 | 525481 PLANT_X 6 230 762174 G17-218TAP 230 2
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.21867 | 118.38 | 525531 TOLK 6 230 525586 NEEDMORE 6 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20963 | 114.61 | 525531 TOLK 6 230 525637 LAMB_CNTY 6 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.23641 | 118.52 | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.21218 | 113.33 | 525531 TOLK 6 230 762174 G17-218TAP 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.21254 | 113.39 | 525531 TOLK 6 230 762174 G17-218TAP 230 2
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.33791 | 149.08 | 525549 TOLK 7 345 3WXFMR ABBXNL844501 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.21867 | 118.36 | 525586 NEEDMORE 6 230 526935 YOAKUM 6 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 113.01 | 525599 LC-SANDHLL+2 69.0 525606 AMHERST 2 69.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 113.04 | 525606 AMHERST 2 69.0 525613 W_LITTLFLD 2 69.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 113.07 | 525613 W_LITTLFLD 2 69.0 525635 LAMB_CNTY 2 69.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 113.02 | 525635 LAMB_CNTY 2 69.0 525650 LC-LTTLFLD+2 69.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20963 | 114.61 | 525637 LAMB_CNTY 6 230 3WXFMR WH ALM20172 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.87 | 525828 TUCO_INT 3 115 3WXFMR DS F78800913 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20714 | 112.4 | 525830 TUCO_INT 6 230 3WXFMR ENRCO 136401 2
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 113.07 | 526086 SW_6786_N 2 69.0 526087 SW_6786_S 2 69.0 Z1
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 113.07 | 526086 SW_6786_N 2 69.0 526102 SP-HETTLER 2 69.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 113.14 | 526087 SW_6786_S 2 69.0 526284 PLANTERS 2 69.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.69 | 526160 CARLISLE 3 115 3WXFMR WH RLP38371 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 113.03 | 526195 QUINCY 3 115 526196 SP-MILWAUKEE 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.93 | 526268 LUBBCK_STH 3 115 3WXFMR NA 70454A 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 113.19 | 526284 PLANTERS 2 69.0 526297 LUBBCK_EST 2 69.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.207 | 112.63 | 526435 SUNDOWN 6 230 3WXFMR UPDATE LATER _12 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20729 | 115 | 526435 SUNDOWN 6 230 526460 AMOCO_SS 6 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20702 | 112.65 | 526525 WOLFFORTH 6 230 3WXFMR UPDATE LATER _13 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 113.07 | 526735 TERRY_CNTY 2 69.0 526747 LG-BROWNFLD2 69.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 113 | 526747 LG-BROWNFLD2 69.0 526754 BROWNFIELD 2 69.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20694 | 114.41 | 526935 YOAKUM 6 230 527028 INK_BASIN 6 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20683 | 113.76 | 527028 INK_BASIN 6 230 527894 HOBBS_INT 6 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20699 | 113 | 527130 DENVER_N 3 115 527286 HIGGEAST 3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.61 | 527149 MUSTANG 6 230 3WXFMR ENRCO 136161 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20719 | 110.49 | 527149 MUSTANG 6 230 527151 GS-MUSTANG 6 230 @1
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.86 | 527202 SEAGRAVES 3 115 3WXFMR ABB MLL92408 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.76 | 527212 DIAMONDBACK3 115 3WXFMR HOW 36773714 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.68 | 527261 SULPHUR 2 69.0 527271 LG-FOSTER +2 69.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20699 | 112.98 | 527286 HIGGEAST 3 115 527363 HIGG 3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20702 | 112.82 | 527322 GAINES 3 115 527325 OXY_WSEM_TP3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20702 | 112.74 | 527325 OXY_WSEM_TP3 115 527362 JOHNSON_DRW3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.73 | 527340 DOSS 3 115 3WXFMR ELCO 13566/1 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.71 | 527345 LEGACY 2 69.0 527350 XTO_ROBRTSN2 69.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.71 | 527346 LEGACY 3 115 3WXFMR VROL 13735-1 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.69 | 527350 XTO_ROBRTSN2 69.0 527355 BOARDMAN 2 69.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.63 | 527355 BOARDMAN 2 69.0 527365 FLANNAGAN 2 69.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.61 | 527360 MAPCO 3 115 527362 JOHNSON_DRW3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.65 | 527362 JOHNSON_DRW3 115 528775 LE-ERF 3 115 @1
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20707 | 112.39 | 527455 RSWL_SLRCOL3 115 527482 CHAVES_CNTY3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20707 | 112.41 | 527470 CHVS_SLRCOL3 115 527464 CHVS_SOLAR11 34.5 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20707 | 112.34 | 527470 CHVS_SLRCOL3 115 527482 CHAVES_CNTY3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20887 | 112.88 | 527483 CHAVES_CNTY6 230 527799 EDDY_NORTH 6 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.62 | 527508 PRICE 3 115 527509 PRICE_TAP 3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.62 | 527529 RIACBRSH_TP3 115 527533 SW4J795_E 3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.62 | 527533 SW4J795_E 3 115 527564 ROSWLL_INT 3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.62 | 527563 ROSWLL_INT 2 69.0 527575 SW_4702 2 69.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20722 | 112.67 | 527564 ROSWLL_INT 3 115 527597 TWEEDY 3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.62 | 527575 SW_4702 2 69.0 527589 CV-ORCHARD 2 69.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.207 | 112.78 | 527653 MILO_WIND 1 34.5 527655 RSVLT_CC_E 7 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20692 | 112.66 | 527654 RSVLT_CC_W 7 345 527655 RSVLT_CC_E 7 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20692 | 112.95 | 527654 RSVLT_CC_W 7 345 527666 RSVLT_COL1 7 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20687 | 112.86 | 527655 RSVLT_CC_E 7 345 527656 CROSSROADS 7 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20692 | 112.95 | 527666 RSVLT_COL1 7 345 3WXFMR RSVLT_COL1 7 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.36 | 527736 NAVAJO_5TP 3 115 527739 NAVAJO_4 3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20704 | 112.35 | 527864 CUNNINHAM 3 115 528348 BUCKEYE_TP 3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20704 | 112.63 | 527864 CUNNINHAM 3 115 528568 MONUMNT_TP 3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20688 | 112.91 | 527865 CUNNIGHM_N 6 230 527867 CUNNIGHM_S 6 230 *1
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20699 | 112.64 | 527865 CUNNIGHM_N 6 230 527963 POTASH_JCT 6 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20704 | 112.4 | 527867 CUNNIGHM_S 6 230 3WXFMR WH 7000266 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.207 | 112.86 | 527867 CUNNIGHM_S 6 230 527882 CUNINGHAM2 1 20.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20701 | 112.79 | 527894 HOBBS_INT 6 230 527903 HOBBS_PLT3 1 18.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20704 | 112.36 | 527965 KIOWA 7 345 528027 RDRUNNER 7 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.36 | 528015 PHANTOM 7 345 528027 RDRUNNER 7 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.41 | 528024 RR_SVC_HV 3 115 528021 RDRUNNR_SVC1 15.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.68 | 528025 RDRUNNER 3 115 587990 GEN-2016-121 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.42 | 528185 N_LOVING 7 345 3WXFMR HYO1063400-1 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20704 | 112.41 | 528185 N_LOVING 7 345 528223 CHINA_DRAW 7 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.36 | 528222 CHINA_DRAW 3 115 528225 CD_SVC_HV 3 115 Z1
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20703 | 112.34 | 528333 LE-WEST_SUB3 115 528334 LE-NRTH_INT3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20704 | 112.42 | 528341 LE-SANANDRS3 115 528627 LE-TXACO_TP3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20704 | 112.38 | 528348 BUCKEYE_TP 3 115 528627 LE-TXACO_TP3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20701 | 112.62 | 528394 QUAHADA 3 115 528396 XTO_BIGEDDY3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20704 | 112.33 | 528463 SANGER_SW 3 115 528575 OXYPERMIAN 3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20704 | 112.33 | 528463 SANGER_SW 3 115 762442 G18-004-TAP 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20704 | 112.63 | 528568 MONUMNT_TP 3 115 528581 BYRD_TP 3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20704 | 112.38 | 528574 OXY_NHU_RCF3 115 528575 OXYPERMIAN 3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.69 | 528617 LE-WAITS 2 69.0 528325 LE-WAITS 3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.61 | 528617 LE-WAITS 2 69.0 528714 LE-FORT_SW 2 69.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20704 | 112.42 | 528622 LE-SANANDRS2 69.0 528341 LE-SANANDRS3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.97 | 528626 LE-PLNSINT 2 69.0 526928 PLAINS_INT 3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.97 | 528626 LE-PLNSINT 2 69.0 528709 LE-PLNSGOAB2 69.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.63 | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.69 | 528669 LE-STKLDRTP2 69.0 528740 LE-PLANS_SW2 69.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.85 | 528709 LE-PLNSGOAB2 69.0 528740 LE-PLANS_SW2 69.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.63 | 528709 LE-PLNSGOAB2 69.0 528747 LE-ALLRED 2 69.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.61 | 528714 LE-FORT_SW 2 69.0 528718 LE-NEWTEX 2 69.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.69 | 528735 LE-PLAINSUB2 69.0 528740 LE-PLANS_SW2 69.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20694 | 112.41 | 530583 POSTROCK7 345 588654 G17-021-TAP 345 2
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.41 | 531213 SANTAFE3 115 531408 PIERCVL3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20674 | 112.33 | 531451 MINGO 7 345 531465 SETAB 7 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20703 | 112.62 | 531501 BUCKNER7 345 531502 CIMRRN 7 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20703 | 112.62 | 531502 CIMRRN 7 345 531503 CIMRRN 1 34.5 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20691 | 112.32 | 531510 HARBNGR3 115 3WXFMR HARBGR345 _1 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20703 | 112.64 | 532663 LEC U5 24.0 532854 LEC U5 6 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20703 | 112.64 | 532853 LAWHILL6 230 532854 LEC U5 6 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20704 | 112.69 | 542951 HAW G5 1 22.0 543665 HAWTHN5 161 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20703 | 112.74 | 542955 LAC G1 1 22.0 542981 LACYGNE7 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20703 | 112.72 | 542956 LAC G2 1 24.0 542981 LACYGNE7 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20702 | 112.76 | 542957 IAT G1 1 24.0 542982 IATAN 7 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20703 | 112.82 | 542962 IAT G2 1 24.5 542982 IATAN 7 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20704 | 112.61 | 542966 WGARDNR5 161 543105 BULLCRK5 161 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20959 | 112.16 | 560022 CRAWFISH_DR 345 762216 G17-151TAP 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20926 | 113.18 | 560022 CRAWFISH_DR 345 762467 G18-015-TAP 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 108.98 | 560022 CRAWFISH_DR 345 763087 GEN-2018-073 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.21041 | 113.55 | 560022 CRAWFISH_DR 345 763215 G18-092-TAP 345 2
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 113.05 | 560252 G10-14 345 560253 G10-14-1 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.78 | 560253 G10-14-1 115 560254 G10-14-SUB1 34.5 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.78 | 560253 G10-14-1 115 560255 G10-14-SUB2 34.5 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.63 | 560581 G06-44-2 34.5 523111 NOVUS1 3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.68 | 560582 G06-44-3 34.5 560577 G06-44 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.66 | 560583 G06-44-4 34.5 560577 G06-44 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.32 | 560757 ASGI13_02_1 69.0 560758 ASGI13_02_2 34.5 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.32 | 560757 ASGI13_02_1 69.0 562731 WHEATLAND 69.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.33 | 560763 ASGI13_03_1 115 560761 ASGI13_03_2 34.5 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.76 | 562015 FIREWHEEL1 34.5 523215 FREWHELCOL17 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.76 | 562016 FIREWHEEL2 34.5 523215 FREWHELCOL17 345 2
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.31 | 562323 AGI1202&1305 115 562324 AGI1202&1305 34.5 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.32 | 562727 LESBIA 115 562728 SANJONTAP 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.32 | 562728 SANJONTAP 115 562729 CAPROCKTAP1 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.32 | 562730 CAPROCKTAP2 69.0 562729 CAPROCKTAP1 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.32 | 562730 CAPROCKTAP2 69.0 562731 WHEATLAND 69.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.72 | 563171 G15082_2 34.5 563170 G15082_1 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.4 | P11:13.8:AEPW:COM1-1
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.41 | P11:13.8:AEPW:COM2-1
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.41 | P11:13.8:AEPW:COM3-1
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.42 | P11:18:AEPW:WELSH1-1
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.42 | P11:18:AEPW:WELSH3-1
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.42 | P11:24:AEPW:PIRKEY 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.39 | P11:24:AEPW:SWS3-1
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.39 | P11:24:AEPW:TURKCOAL
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20717 | 112.7 | P12:138:AEPW-OMPA:DUNCAN-4:OMDUNCN4
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20706 | 112.66 | P12:138:AEPW:112GORE4:SNYDER-4
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20706 | 112.66 | 5841_Dup1
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20714 | 111.96 | 584560 GEN-2015-014 115 584561 G15-014XFMR1 34.5 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20713 | 112.65 | P12:138:AEPW:SANTAFE:DUNCAN-4
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.68 | 587991 G16-121XFMR1 34.5 587990 GEN-2016-121 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.62 | 588480 A16-010_SUB 115 3WXFMR A16-010_SUB 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20717 | 112.7 | P12:138:AEPW:DUNCAN-4:L.E.S.-4
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.06 | 588761 G17-033XFMR1 34.5 588760 GEN-2017-033 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.06 | 588765 G17-033XFMR2 34.5 588760 GEN-2017-033 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.63 | 588861 G17-047XFMR1 34.5 588860 GEN-2017-047 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20667 | 112.2 | P12:138:AEPW:ELKCTY-4:CLINTJC4
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.64 | 589381 G17-100XFMR1 34.5 589380 GEN-2017-100 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20679 | 112.39 | P12:138:AEPW:HOB-JCT4:ELKCTY-4
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.64 | P12:138:AEPW:SHERID4:112GORE4
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20703 | 112.61 | P12:230:AEPW:SWEETWT6:BUFFCK6
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20702 | 112.66 | P12:230:AEPW:SWEETWT6:ROARK6
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20947 | 114.5 | P12:345:AEPW:L.E.S7:TERRYRD7
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20947 | 114.49 | P12:345:AEPW:L.E.S7:TERRYRD7
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20947 | 114.47 | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.2101 | 114.61 | P12:345:AEPW-OKGE:L.E.S.-7:GRACMNT7
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.2101 | 114.58 | P12:345:AEPW-OKGE:L.E.S.-7:GRACMNT7
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20701 | 112.4 | P12:345:AEPW-OKGE:PITTSB-7:SEMINOL7
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.21019 | 115.66 | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.66 | P22:345:AMMO::LABADIE:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.66 | P22:345:AMMO::LABADIE:2
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.66 | P22:345:AMMO::LABADIE:3
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.66 | P22:345:AMMO::LABADIE:4
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.65 | P22:345:AMMO::RUSHISLAND:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.64 | P22:345:AMMO::RUSHISLAND:2
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20706 | 112.41 | P13:138-13.8:AEPW:COMANC-4_#2
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.2053 | 111.28 | P13:138-230:AEPW:ELKCTY-4
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20707 | 112.4 | P13:138-24:AEPW:S.W.S.-4
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20706 | 112.39 | P13:138-24:AEPW:TURK 4
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20713 | 112.63 | P13:138-345:AEPW:L.E.S.-4_#1
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20722 | 112.75 | P13:138-345:AEPW:L.E.S.-4_#2
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20706 | 112.67 | P23:500:EES-EAI:KEO:B4941
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20706 | 112.66 | P23:500:EES-EAI:KEO:B4921
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.61 | P11:26:EES-EAI:INDEP2:1:D401
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.61 | P11:26:EES-EAI:INDEP2:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.61 | P13:500:EES-EAI:INDEP2:MT2
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.65 | P23:500:EES-EAI:INDEP2:B6126
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.64 | P23:500:EES-EAI:PD:INDEP2:LN:FK479
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20703 | 112.61 | P13:230-34.5:AEPW:BUFFCK6
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20702 | 112.67 | P13:230-34.5:AEPW:ROARK6
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.41 | P13:69-13.8:AEPW:COMANC-2
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.66 | P11:024:DPC:ALMA2:6
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.62 | P11:18:ITCM:EMERYGT1:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.63 | P11:18:ITCM:EMERYGT2:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.63 | P11:161:ITCM:MGS CT1:1C
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.63 | P11:161:ITCM:MGS CT2:2C
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20703 | 112.64 | 652537 WHITE 3 345 659286 DEERCREK-BE3 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20703 | 112.64 | 659286 DEERCREK-BE3 345 3WXFMR DEERCRK KU1A 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.63 | 672601 BD 4 230 672306 BD 6G 18.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.63 | 672610 POPLAR 4 230 672310 POPLAR 1G 18.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.63 | 672610 POPLAR 4 230 672311 POPLAR 2G 18.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.62 | 672621 SHAND 4 230 672321 SHAND 1G 18.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.61 | 672649 CODETTE 4 230 672650 NIPAWIN 4 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.62 | 672696 BRADA 4 230 672699 NBEC 4 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.69 | P23:345:MDU::COYOTE::5707-5712-5715::::
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.84 | P23:345:MEC:CBEC 905
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.81 | P23:345:MEC:CBEC 908
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.64 | P23:345:MEC:GDMEC 908
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.74 | P23:345:MEC:RAUN 0180
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.8 | P23:345:MEC:RAUN 0210
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.75 | P23:345:MEC:LOUISA 954
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.75 | P23:345:MEC:LOUISA 964
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.61 | P21:115:XEL:AUTO-SINGLE:CHEMOLT7:LSPOWER7:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.65 | P21:115:XEL:AUTO-SINGLE:COLVILL7:CANONFLSG7:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.61 | P21:115:XEL:AUTO-SINGLE:FARIBALTP7:FARIBALTGEN:Z
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.7 | P21:230:OTP:AUTO-SINGLE:SQBUTTE4:YNG24:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.69 | P23:345:OTP:CENTER 3:3215(1)
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.69 | P23:345:OTP:CENTER 3:3225(1)
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.63 | P12:230:UMZW:# 687 #: FT IN SD. FT-BG1 LINE FAULT
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.63 | P12:230:UMZW:# 3617 #: FT IN SD. FT-BG2 LINE FAULT
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 111.33 | 760494 GEN-2017-146 230 760498 G17-146-TAP 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 111.32 | 760495 G17-146-XFM1 34.5 760494 GEN-2017-146 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.05 | 761356 G17-239-XFMR 34.5 761355 GEN-2017-239 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.05 | 761359 G17-239-XFMR 34.5 761355 GEN-2017-239 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.23 | 761797 G17-187XFM1 34.5 761796 GEN-2017-187 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.23 | 761800 G17-187XFM2 34.5 761796 GEN-2017-187 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 107.16 | 762132 GEN-2017-158 230 763252 G18-099-XFM1 34.5 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 107.16 | 762132 GEN-2017-158 230 763255 G18-099-XFM2 34.5 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 107.74 | 762133 G17-158XFM1 34.5 762132 GEN-2017-158 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 107.74 | 762136 G17-158XFM2 34.5 762132 GEN-2017-158 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 109.9 | 762216 G17-151TAP 345 762217 GEN-2017-151 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20959 | 113.55 | 762216 G17-151TAP 345 762467 G18-015-TAP 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 111.85 | 762218 G17-151XFM1 34.5 762217 GEN-2017-151 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 111.85 | 762221 G17-151XFM2 34.5 762217 GEN-2017-151 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 111.85 | 762224 G17-151XFM3 34.5 762217 GEN-2017-151 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 111.85 | 762227 G17-151XFM4 34.5 762217 GEN-2017-151 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.36 | 762438 GEN-2018-004 115 762442 G18-004-TAP 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 110.89 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 111.7 | 762461 G18-015-XFM1 34.5 762460 GEN-2018-015 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 111.7 | 762464 G18-015-XFM2 34.5 762460 GEN-2018-015 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20843 | 113.07 | 762467 G18-015-TAP 345 763215 G18-092-TAP 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 110.18 | 763087 GEN-2018-073 345 763088 G18-073-XFM1 34.5 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 111.33 | 763087 GEN-2018-073 345 763091 G18-073-XFM2 34.5 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 107.16 | 763120 GEN-2018-081 230 763121 G18-081-XFM1 34.5 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 109.42 | 763120 GEN-2018-081 230 764011 G19-074-XFM1 34.5 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 109.44 | 763186 GEN-2018-089 230 763187 G18-089-XFM1 34.5 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 110.21 | 763208 GEN-2018-092 345 763215 G18-092-TAP 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 111.37 | 763208 GEN-2018-092 345 763220 G18-092-XFM1 34.5 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 111.37 | 763208 GEN-2018-092 345 763223 G18-092-XFM2 34.5 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 108.87 | 763241 GEN-2018-097 230 763242 G18-097-XFM1 34.5 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 109.78 | 763241 GEN-2018-097 230 763296 G18-111-XFM1 34.5 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 109.14 | 763241 GEN-2018-097 230 763307 G18-112-XFM1 34.5 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 109.14 | 763241 GEN-2018-097 230 763310 G18-112-XFM2 34.5 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 108.87 | 763241 GEN-2018-097 230 763395 G18-124-XFM1 34.5 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 108.87 | 763241 GEN-2018-097 230 763398 G18-124-XFM2 34.5 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.29 | 763318 GEN-2018-115 345 763319 G18-115-XFM1 34.5 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.75 | 763340 GEN-2018-117 230 763341 G18-117-XFM1 34.5 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 108.51 | 763483 GEN-2019-003 230 763484 G19-003-XFM1 34.5 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 111.19 | 763483 GEN-2019-003 230 763605 G19-021-XFM1 34.5 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 111.9 | 763516 GEN-2019-011 345 763517 G19-011-XFM1 34.5 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.26 | 763879 GEN-2019-056 115 763880 G19-056XFM1 34.5 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20655 | 112.68 | P42:345:OKGE:SB_BVTY7305
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20697 | 112.43 | P23:345:WERE:BUFF_345-534::
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20697 | 112.43 | P23:345:WERE:BUFF_345-543::
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20701 | 112.78 | P23:345:WERE:JEC_345-15::
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.207 | 112.75 | P23:345:WERE:JEC_345-16::
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20701 | 112.78 | P23:345:WERE:JEC_345-19::
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20701 | 112.78 | P23:345:WERE:JEC_345-20::
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.95 | P23:345:WERE:WOLF_345-50::
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.95 | P23:345:WERE:WOLF_345-60::
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20706 | 112.43 | P42:345:AEPW:WELSH CB 10620 NBTB+FAULT
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.21019 | 114.21 | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.21043 | 114.99 | P42:345:AEPW:LAWTON EASTSIDE CB 3413A NBTB+FAULT
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.21079 | 115.4 | P42:345:AEPW:LAWTON EASTSIDE CB 3425A NBTB+FAULT
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.21033 | 115.86 | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20719 | 112.31 | P42:345:AEPW:PITTSBURG CB 3441A NBTB+FAULT
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20701 | 112.4 | P42:345:AEPW:PITTSBURG CB 3445A NBTB+FAULT
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20947 | 114.49 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20947 | 114.49 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20947 | 114.47 | P42:345:AEPW:TERRYRD_CB_3421A_NBTB
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20703 | 112.75 | P23:345:KCPL:LACYGNE_R2-5::LACYGU2-LACYGNE-STILWELL
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20706 | 112.43 | P23:345:AEPW:WELSH CB 10620 NBTB
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.21019 | 114.54 | P23:345:AEPW:OKLAUNION CB 3401A NBTB
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.21043 | 114.99 | P23:345:AEPW:LAWTON EASTSIDE CB 3413A NBTB
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.21079 | 115.4 | P23:345:AEPW:LAWTON EASTSIDE CB 3425A NBTB
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.21033 | 115.86 | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20719 | 112.31 | P23:345:AEPW:PITTSBURG CB 3441A NBTB
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20701 | 112.4 | P23:345:AEPW:PITTSBURG CB 3445A NBTB
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20947 | 114.49 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20947 | 114.49 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20947 | 114.47 | P23:345:AEPW:TERRYRD_CB_3421A_NBTB
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20736 | 112.62 | P12:138:AEPW:S.W.S.-4:L.E.S.-4
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20705 | 112.65 | P11:115:SUNC:GARDENCITY_S2:97:531459(2)
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20966 | 114.72 | P23:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.21223 | 117.32 | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20966 | 114.72 | P42:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB+FAULT
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.21223 | 117.32 | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20674 | 112.33 | P23:345:SUNC:MO_BRK182
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20674 | 112.33 | P23:345:SUNC:MO_BRK382
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20702 | 112.42 | P21:345:UMZW:# 725 #: GI IN NE. GI-SWEET LINE FAULT
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.2086 | 112.8 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20706 | 112.41 | P12:138-13.8:AEPW:COMANC-4_#1
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.2053 | 111.26 | P12:230:AEPW:ELKCITY6:CHISHOLM6
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.20849 | 113.54 | P12:230:AEPW:SWEETWT6:CHISHOLM6
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997715 ABBXNL844501 230 1 |  | 553 | 0.24323 | 150.96 | 525531 TOLK 6 230 3WXFMR TOLK 6 2
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.24323 | 149.08 | 525549 TOLK 7 345 3WXFMR ABBXNL844501 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997715 ABBXNL844501 230 1 |  | 553 | 0.24323 | 150.96 | 525531 TOLK 6 230 3WXFMR TOLK 6 2
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.24323 | 149.08 | 525549 TOLK 7 345 3WXFMR ABBXNL844501 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997715 ABBXNL844501 230 1 |  | 553 | 0.28547 | 150.96 | 525531 TOLK 6 230 3WXFMR TOLK 6 2
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.28547 | 149.08 | 525549 TOLK 7 345 3WXFMR ABBXNL844501 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997713 ABBXNL844501 230 1 |  | 553 | 0.29039 | 157.44 | 525531 TOLK 6 230 3WXFMR TOLK 6 2
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.20007 | 119.68 | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.2016 | 120.42 | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.29039 | 155.48 | 525549 TOLK 7 345 3WXFMR ABBXNL844501 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997713 ABBXNL844501 230 1 |  | 553 | 0.34286 | 157.44 | 525531 TOLK 6 230 3WXFMR TOLK 6 2
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21029 | 116.18 | P23:345:KCPL-WERE:237LACYGNE_R1-6::LACYGU1-LACYGNE-NEOSHO
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21026 | 116.06 | P11:230:WERE:LECU5_GEN::
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.08 | P11:161:GMO:DOGWOOD_COMBINED_CYCLE_UNIT_OUTAGE_1_1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.02 | P11:20:KACY:NEARMAN N1::N1 OUT OF SERVICE:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21026 | 116.02 | P12:69:KACY:NMGEN-NMISOBUS::NEARMAN N1-NM ISOBUS OPEN:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21026 | 116.02 | P13:20-161:KACY:NEARMAN5-NMISOBUS:NAMEPLATE:NEARMAN N1 GSU:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21026 | 116.02 | P21:20:KACY:546702NMGENN1-546703NMISOBUSC1::::
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.23 | P11:115:SPS:HOBBS1&3:145MW::::
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21033 | 114.72 | P11:115:SPS:MUSTANG1&3:153MW::::
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21284 | 118.23 | P12:230:SPS:K37::1_TOLK_LAMB:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21048 | 116.06 | P12:230:SPS:K43::1_PRNGLE_HARR_E:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.2103 | 115.81 | P12:230:SPS:K44::1_EPLNT_HARRW:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21042 | 116.22 | P12:115:SPS:T04::1_TRBLNC_CASTRO:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21048 | 116.02 | P12:115:SPS:T06::1_SPRMN_PRNGLE:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.5 | P12:115:SPS:T21::1_GRSSLND_GRAHAM:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.05 | P12:115:SPS:T24B::1_RSWLL_BRSHRF:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21028 | 116.05 | P12:115:SPS:T26::1_CHAVES_RSWLCTY:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21149 | 116.45 | P12:115:SPS:T28A::1_LAMTON_PLANTX:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21073 | 116.02 | P12:115:SPS:T29::1_LAMTON_HALECTR:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21198 | 117.27 | P12:115:SPS:T30::1_LAMB_HOCKLY:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21198 | 116.37 | P12:115:SPS:T31::1_HOCKLY_SUNDWN:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21023 | 116.06 | P12:115:SPS:T35::1_TERRY_YOAKUM:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21028 | 116.78 | P12:115:SPS:T45::1_NORRIS_OASIS:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21026 | 115.82 | P12:115:SPS:T57::1_MUSTG_SEGRVS:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21154 | 116.03 | P12:115:SPS:T58::1_HERFRD_CARGIL:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21154 | 116.57 | P12:115:SPS:T59::1_CARGIL_CURRY:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.02 | P12:115:SPS:T64::1_RNDALL_PULLMN:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21124 | 116.38 | P12:115:SPS:T67::1_HAPPY_KRESS:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21032 | 115.77 | P12:115:SPS:T68::1_TUCO_FLOYD:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21028 | 115.81 | P12:115:SPS:T69::1_LUBBE_CROSBY:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.02 | P12:115:SPS:T70::1_COLTR_S_GORG:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21022 | 116.63 | P12:115:SPS:T71::1_CRLSLE_YUMA:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21036 | 116.1 | P12:115:SPS:T81::1_COX_FLOYD:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.26 | P12:115:SPS:T83::1_SP-FKFD_ALLEN:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21022 | 116.44 | P12:115:SPS:T89::1_DC_N_HIGG:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.07 | P12:115:SPS:T91::1_HIGG_RUSSELL:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21032 | 116.02 | P12:115:SPS:V01::1_MOOREW_RVRVIEW:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21049 | 116.07 | P12:115:SPS:V04::1_EPLANT_RNDALL:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21041 | 116.06 | P12:115:SPS:V07::1_COX_HALECTR:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21141 | 116.23 | P12:115:SPS:V09::1_HALECTR_PLANTX:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21026 | 116.21 | P12:115:SPS:V12::1_PLANTX_BAILEY:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.03 | P12:115:SPS:V15::1_TUCO_INDANA:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.20991 | 116.16 | P12:115:SPS:V24::1_WOLFTH_TERRY:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21045 | 116.07 | P12:115:SPS:V26::1_RSWLL_EDDY_N:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.4 | P12:115:SPS:V33::1_LUBBS_LYNN:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21132 | 117.14 | P12:115:SPS:V37::1_CASTRO_PLANTX:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21028 | 116.05 | P12:115:SPS:V44::1_COLTR_OWENS:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.16 | P12:115:SPS:V46::1_ALLEN_WHEELCK:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21029 | 116.5 | P12:115:SPS:V49::1_YOAKUM_SHLCO2:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.2107 | 116.68 | P12:115:SPS:V55::1_SUNDWN_TERRY:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.2104 | 116.59 | P12:115:SPS:V56::1_COCHRAN_SUNDWN:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.09 | P12:115:SPS:V62::1_CRLSLE_INDANA:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.2104 | 116.07 | P12:115:SPS:V78::2_CURRY_RSVLT:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21025 | 116.19 | P12:115:SPS:V81::1_LE-WAIT_LE-LVN:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21028 | 116.06 | P12:115:SPS:V95::1_DC_N_SHLCO2:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.02 | P12:115:SPS:W11::1_DC_S_SMINLE:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.03 | P12:115:SPS:W12::1_SMINLE_DOSS:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.1 | P12:115:SPS:W14::1_SMINLE_GAINES:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.03 | P12:115:SPS:W26::1_CUNGHM_OILCNTR:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.61 | P12:115:SPS:W32::1_PRMTR_FE-CLSIN:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21024 | 116.26 | P12:115:SPS:W35::1_GAINES_JNSDRW:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21219 | 116.59 | P12:115:SPS:W40::1_WCANYON_TRBLNC:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21055 | 116.11 | P12:115:SPS:W52::1_NEWHART_KRESS:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.67 | P12:115:SPS:W58::1_NORTON_LOPEZ:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.25 | P12:115:SPS:W59::1_LOPEZ_CMPBLL:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21028 | 116.55 | P12:115:SPS:W62::1_PLSTHL_CURRY:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.2104 | 116.07 | P12:115:SPS:W63::1_PLSTHL_CURRY:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.36 | P12:115:SPS:W64::1_PLSTHL_FE-CLV:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21029 | 116.57 | P12:115:SPS:W65::1_PLSTHL_CURRY:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.23 | P12:115:SPS:W66::1_PORTA_GREYHUND:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21024 | 116.02 | P12:115:SPS:W76::1_QUAHA_PCA:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21219 | 116.1 | P12:115:SPS:W77::1_RNDAL_WCANYON:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21028 | 116.07 | P12:115:SPS:W99::1_CAPITAN_CHAVES:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.05 | P12:115:SPS:U03::1_CARDNL_NEF:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21023 | 116.53 | P12:115:SPS:U14::1_DC_STH_INKBSN:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21025 | 116.47 | P12:115:SPS:V15::1_INKBSN_LE-WAT:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.2105 | 116.15 | P12:115:SPS:U16::1_BSHLND_OUTPST:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.2105 | 116.16 | P12:115:SPS:U17::1_COLTR_OUTPST:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21034 | 116.26 | P12:115:SPS:U19::1_DEAN_PLAINS:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.2105 | 116.07 | P12:115:SPS:U23::1_COLTR_HILSDE:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.20186 | 124.36 | P42:345:SPS:YOAKUM:J18####:SLG1:EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.20186 | 124.36 | P43:345:SPS:YOAKUM:TF#####:SLG:EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.20186 | 124.36 | P42:345:SPS:YOAKUM:J17####:SLG:EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.20186 | 124.36 | P42:345:SPS:YOAKUM:J18####:SLG2:EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21026 | 116.06 | P11:18:HAST:::EGYCTR2G WEC2_LOSS OF WEC 2 GEN_:HV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21026 | 116.06 | P13:18-115:HAST:::EGYCNTR7 XFMR G2WEC 2 GSU_:HV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.08 | P11:161:GMO:DOGWOOD-COMBINED-CYCLE-UNIT-OUTA:::HV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21029 | 116.18 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21026 | 116.18 | P23:345:KCPL:LACYGNE-R2-5:::EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21023 | 116.23 | P11:230:WERE:JECU1-GEN:::HV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21026 | 116.06 | P11:230:WERE:LECU5-GEN:::HV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21023 | 116.23 | P11:345:WERE:JECU2-GEN:::EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21023 | 116.22 | P11:345:WERE:JECU3-GEN:::EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.4 | P11:345:WERE:WOLFU1-GEN:::EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21013 | 115.77 | P12:345:PWT:BUFF-THIS-345-1:::EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21013 | 115.77 | P12:345:PWT:BUFF-THIS-345-2:::EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21011 | 115.75 | P23:345:WERE:BUFF-345-534:::EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21011 | 115.75 | P23:345:WERE:BUFF-345-543:::EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21023 | 116.23 | P23:345:WERE:JEC-345-15:::EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21022 | 116.18 | P23:345:WERE:JEC-345-16:::EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21023 | 116.22 | P23:345:WERE:JEC-345-19:::EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21023 | 116.22 | P23:345:WERE:JEC-345-20:::EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.39 | P23:345:WERE:WOLF-345-50:::EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.39 | P23:345:WERE:WOLF-345-60:::EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.34 | P11:022:NPPD:COOPER1G:1:983:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21022 | 116.33 | P11:023:NPPD:GENTLM1G:1:757:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21022 | 116.35 | P11:024:NPPD:GENTLM2G:2:757:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21026 | 116.01 | P11:161:OPPD:N OMA 5G:LT::HV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21026 | 116.01 | P11:161:OPPD:N OMA 5G:::HV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21023 | 116.2 | P13:345:OPPD:NEBCTY1G:::EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21022 | 116.22 | P13:345:OPPD:NEBCTY2G:::EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21026 | 116.01 | P13:161:OPPD:N OMA 5G:::HV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.22 | P22:345:OPPD:S3458 NEBCTY1G:LT::EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21023 | 116.2 | P22:345:OPPD:S3458 NEBCTY1G:::EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.25 | P22:345:OPPD:S3458 NEBCTY2G:LT::EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21022 | 116.22 | P22:345:OPPD:S3458 NEBCTY2G:::EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.22 | P23:345:OPPD:S3458 NEBCTY1G:LT::EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21023 | 116.2 | P23:345:OPPD:S3458 NEBCTY1G:::EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.25 | P23:345:OPPD:S3458 NEBCTY2G:LT::EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21022 | 116.22 | P23:345:OPPD:S3458 NEBCTY2G:::EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 115.8 | P12:115:SUNC:PLYMELL-PIERCEVILLE:::HV::
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21025 | 116.06 | P11:018:UMZB:# 5 #:: DCS IN SD. DEERCREEK_MV::
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21026 | 116.03 | P11:022:UMZB:# 15 #:: LO IN ND. LELAND OLDS 1_MV::
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21025 | 116.07 | P11:020:UMZB:# 16 #:: LO IN ND. LELAND OLDS 2_MV::
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21025 | 116.14 | P11:023:UMZB:# 31 #:: AVS IN ND. ANTELOPE VALLEY 1_MV::
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21025 | 116.14 | P11:023:UMZB:# 32 #:: AVS IN ND. ANTELOPE VALLEY 2_MV::
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21021 | 116.33 | P11:024:UMZB:# 33 #:: LRS IN WY. LARAMIE RIVER STATION 1_MV::
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.06 | P12:230:UMZW:# 687 #:: FT IN SD. FT-BG1 BRANCH FAULT:HV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.06 | P12:230:UMZW:# 3617 #:: FT IN SD. FT-BG2 BRANCH FAULT:HV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.06 | P12:230:UMZW:# 4038 #:: BG-FT IN SD. FAULT FOR TRANSMISSION CIRCUIT (BG-FT).:HV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.06 | P12:230:UMZW:# 4039 #:: BG-FT IN SD. FAULT FOR TRANSMISSION CIRCUIT (BG-FT).:HV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.03 | P13:230:UMZW:# 5135 #:: OA IN SD. FAULT ON TRANSFORMER (2).:HV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.03 | P13:230:UMZW:# 5136 #:: OA IN SD. FAULT ON TRANSFORMER (3).:HV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21026 | 115.82 | P23:345:UMZW:# 2423 #:: GI IN NE. GI 1596 BKR FAULT:EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21026 | 115.82 | P23:345:UMZW:# 2426 #:: GI IN NE. GI 1592 BKR FAULT:EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21026 | 115.82 | P23:345:UMZW:# 2432 #:: GI IN NE. GI 1092 BKR FAULT:EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21026 | 115.82 | P23:345:UMZW:# 2440 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1092 STUCK BKR:EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21026 | 115.82 | P23:345:UMZW:# 2444 #:: GI IN NE. GI-SWEET BRANCH FAULT & GI 1596 STUCK BKR:EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21026 | 115.82 | P23:345:UMZW:# 2446 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1196 STUCK BKR:EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21026 | 115.82 | P42:345:UMZW:# 2413 #:: FT2 IN SD. FT2-LO2 BRANCH FAULT & FT2 2992 STUCK BKR:EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21026 | 115.82 | P42:345:UMZW:# 2415 #:: FT2 IN SD. FT2-GI BRANCH FAULT & FT2 3392 STUCK BKR:EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21031 | 115.74 | P11:138:WFEC:HUGO1:465MW :::
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21026 | 116.02 | P11:138:WFEC:MORLND2:132MW:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21026 | 116.03 | P11:138:WFEC:MORLND3:149MW :::
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21036 | 116.06 | P12:138:WFEC:ANADRKO_CLVLND::::
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.2103 | 116.06 | P12:345:OKGE-AEPW:BKRBKR12::::
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21064 | 116.18 | P12:345:OKGE:BKRBKR21::::
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21083 | 116.26 | P12:345:OKGE:BKRBKR24::::
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21274 | 117.75 | P12:345:OKGE-AEPW:BKRBKR25::::
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.20996 | 115.72 | P12:345:OKGE:BKRBKR336::::
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.20996 | 115.72 | P12:345:OKGE:BKRBKR336_2::::
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21349 | 118.25 | P12:345:OKGE-AEPW:BKRBKR366::::
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21349 | 118.23 | P12:345:OKGE-AEPW:BKRBKR366::::
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21236 | 117.15 | P12:345:OKGE:BKRBKR367::::
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21001 | 115.72 | P12:345:OKGE:BKRBKR4193::::
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21001 | 115.72 | P12:345:OKGE:BKRBKR4194::::
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.02 | P12:345:OKGE:BKRBKR4195::::
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.2099 | 115.76 | P12:345:OKGE-SPS:BKRBKR4201::::
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.2099 | 115.76 | P12:345:OKGE-SPS:BKRBKR4202::::
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21037 | 116.03 | P12:345:OKGE:BKRBKR421::::
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.20994 | 115.6 | P12:345:OKGE:BKRBKR443NEW::::
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.20993 | 115.6 | P12:345:OKGE:BKRBKR443NEW2::::
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21011 | 115.79 | P12:345:OKGE-ITC:BKRBKR502::::
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21011 | 115.79 | P12:345:OKGE-ITC:BKRBKR503::::
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21014 | 115.83 | P12:345:OKGE-ITC:BKRBKR502_1::::
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21014 | 115.83 | P12:345:OKGE-ITC:BKRBKR503_1::::
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21021 | 116.33 | P12:345:OKGE:BKRBKR604::::
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.2102 | 116.37 | P12:345:OKGE:BKRBKR604_2::::
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21029 | 115.82 | P11:345:OKGE:BKRBKR_GSU07::::
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21029 | 115.81 | P11:345:OKGE:BKRBKR_GSU08::::
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21029 | 115.8 | P11:138:OKGE:BKRBKR_GSU21::::
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21025 | 115.83 | P12:138:OKGE:BKRBKR85_MOS1::::
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.20994 | 116.13 | P42:345:OKGE:SB_ARIA7381::::
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21722 | 120.17 | P42:345:OKGE:SB_BVTY7387::::
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21038 | 116.02 | P41:345:OKGE:SB_REUD7381::::
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21037 | 116.03 | P41:345:OKGE:SB_REUD7383::::
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21037 | 116.06 | P41:345:OKGE:SB_REUD7385::::
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.2104 | 116.06 | P42:345:OKGE:SB_REUD7389::::
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21025 | 116.05 | P11:115:SUNC:GARDENCITY_S2:103:531459(2):HV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21025 | 116.07 | P11:115:SUNC:FORTDDODGE_4:157:539670(4):HV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.04 | P11:345:599:CIMARRON1WIND:200:531603(1):EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.47 | P13:115:SUNC:HOLCOMB_GSU:::HV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21025 | 116.05 | P13:115:SUNC:S2_GSU:::HV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21025 | 116.07 | P13:115:SUNC:FORTDODGE_GSU:::HV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21025 | 116.04 | P23:345:SUNC:BU_BRK682:::EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.14 | 300003 1THLG3 24.0 301503 7THOMHLGSU3 345 3
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.01 | 300007 1NM G2 22.0 301537 7NEWMADGSU2 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.01 | 300046 7NEWMAD 345 301537 7NEWMADGSU2 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.14 | 300049 7THOMHL 345 301503 7THOMHLGSU3 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.08 | P11:20:AMMO:1LAB�� G1:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.08 | P11:20:AMMO:1LAB�� G2:2
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.27 | P11:345:AMMO::CALLAWAY:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.08 | P11:345:AMMO::LABADIE:3
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.08 | P11:345:AMMO::LABADIE:4
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.07 | P11:345:AMMO::RUSHISLAND:U1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.07 | P11:345:AMMO::RUSHISLAND:U2
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.06 | P11:138:AMMO::SIOUX:2
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 115.83 | P11:24:CLEC::G1DOLHIL:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.06 | P12:765:AEP:AEP ROCKP-AEP JEFF 765
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 115.78 | P11:HV:EES::PIRKEY 1:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 115.79 | P11:EHV:EES::WELSH3-1:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 115.74 | P11:HV:EES::TURKCOAL:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.25 | P12:EHV:EES::7CALAWY 1:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21028 | 116.02 | 338056 CHALKBLUFFPV 500 338162 8W.MEMPHIS% 500 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21029 | 115.75 | P12:HV:EES::TURK 4%:1(1)
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21029 | 115.79 | P12:EHV:EES::WELSH 7:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21029 | 115.79 | P12:EHV:EES::WELSH 7:1(1)
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21028 | 115.79 | P12:HV:EES::PIRKEY 4:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.2103 | 116.06 | P12:EHV:EES::CLARKSV7!:MUSKOGE7!:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.06 | 344011 7HUGHES 345 344012 7HPW-N 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.08 | 344884 7LABADIE1 345 344894 1LAB G1 20.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.08 | 344885 7LABADIE2 345 344895 1LAB G2 20.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.08 | 344886 7LABADIE3 345 344896 1LAB G3 20.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.08 | 344887 7LABADIE4 345 344897 1LAB G4 20.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.07 | 345667 7RUSH 1 345 345670 1RUSH G1 18.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.06 | 345668 7RUSH 2 345 345671 1RUSH G2 18.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.05 | 345755 4SIOUX 1 138 345756 1SIOUX 1 18.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.05 | 345764 4SIOUX 2 138 345765 1SIOUX 2 18.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.12 | P12:345:MDU::CENTER:COYOTE:1::::
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.12 | P13:345:MDU:COYOTE GSU LOSS:COYOTE::1::::
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.03 | P11:345:MEC:GDMEC CT1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.03 | P11:345:MEC:GDMEC CT2
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.14 | P11:345:MEC:GDMEC ST
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.35 | P11:345:MEC-NPPD:COOPER 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.24 | P11:24:XEL:AUTO-SINGLE:SHERC31G:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.24 | P11:24:XEL:AUTO-SINGLE:SHERC32G:2
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.33 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.16 | P11:20:XEL:AUTO-SINGLE:PRIS31G:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.16 | P11:20:XEL:AUTO-SINGLE:PRIS32G:2
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.2 | P11:22:XEL:AUTO-SINGLE:MNTCE31G:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.16 | P11:20:XEL:AUTO-SINGLE:KING31G:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.02 | P11:13:XEL:AUTO-SINGLE:HBRS73G:9
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.02 | P11:18:XEL:AUTO-SINGLE:BLKD76G:6
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.22 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.22 | P11:22:GRE:AUTO-SINGLE:GRE-COAL42G:2
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.14 | P11:24:OTP:AUTO-SINGLE:BIGSTN1G:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.15 | P11:20:OTP:AUTO-SINGLE:CENTER2G:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.05 | P11:22:OTP:AUTO-SINGLE:CENTER1G:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.13 | P11:24:OTP:AUTO-SINGLE:COYOTE1G:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.05 | P11:24:DPC:AUTO-SINGLE:GENOA53G:3
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.03 | P12:115:XEL:AUTO-SINGLE:CHEMOLT7:LSPOWER7:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.07 | P12:115:XEL:AUTO-SINGLE:COLVILL7:CANONFLSG7:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.03 | P12:115:XEL:AUTO-SINGLE:FARIBALTP7:FARIBALTGEN:Z
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.13 | P12:230:OTP:AUTO-SINGLE:SQBUTTE4:YNG24:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.22 | P13:24-345:XEL:AUTO-SINGLE:SHERC31G:SHERCO3:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.22 | P13:24-345:XEL:AUTO-SINGLE:SHERC32G:SHERCO3:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.3 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.16 | P13:20-345:XEL:AUTO-SINGLE:PRIS31G:PRISLD3:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.16 | P13:20-345:XEL:AUTO-SINGLE:PRIS32G:PRISLD3:2
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.2 | P13:22-345:XEL:AUTO-SINGLE:MNTCE31G:MNTCELO3:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.15 | P13:20-345:XEL:AUTO-SINGLE:KING31G:ASKING3:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.02 | P13:13-115:XEL:AUTO-SINGLE:HBRS73G:HIBRDGE7:9
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.2 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL41G:GRE-COALCR4:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.2 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL42G:GRE-COALCR4:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.13 | P13:230-24:OTP:AUTO-SINGLE:BIGSTON4:BIGSTN1G:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.13 | P13:20-230:OTP:AUTO-SINGLE:CENTER2G:YNG24:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.04 | P13:22-230:OTP:AUTO-SINGLE:CENTER1G:CENTER4:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.12 | P13:24-345:OTP:AUTO-SINGLE:COYOTE1G:COYOTE3:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.05 | P13:24-161:DPC:AUTO-SINGLE:GENOA53G:GENOA5:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.07 | P13:24-161:DPC:AUTO-SINGLE:JPM:ALMA5:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21028 | 116.02 | 38203 J1819 POI 500 337957 8KEO% 500 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21028 | 116.02 | 38203 J1819 POI 500 338056 CHALKBLUFFPV 500 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.13 | P11:115:XEL:RIV COMBINE CYCLE
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.04 | P12:115:XEL:BDS #2 5
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.04 | P11:115:XEL:HBR #6
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.04 | P11:115:XEL:HBR #7
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.16 | P11:115:XEL:HBR #6 7 8
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.16 | P23:345:XEL:8H14 PRI
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.16 | P23:345:XEL:8H17 PRI AS
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.3 | P23:345:XEL:8N28 SHC
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.22 | P23:345:XEL:8N22 SHC
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.22 | P23:345:XEL:8N17 SHC
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.21 | P23:345:XEL:8N8 MNN
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.15 | P23:345:XEL:8P1 KING
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.15 | P23:345:XEL:8P2 KING
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.04 | P23:115:XEL:5P147 IVH AS
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.03 | P11:18:ALTW:AUTO-SINGLE:EMERYST1:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.03 | P11:22:ALTW:AUTO-SINGLE:LANS54G:4
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.17 | P11:22:ALTW:AUTO-SINGLE:ARNOLD1G:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.2 | P11:24:ALTW:AUTO-SINGLE:OTTUMW1G:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.03 | P13:18-161:ALTW:AUTO-SINGLE:EMERYST1:EMERY5:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.03 | P13:22-161:ALTW:AUTO-SINGLE:LANS54G:LANSINGL15:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.16 | P13:22-161:ALTW:AUTO-SINGLE:ARNOLD1G:ARNOLD5:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.19 | P13:24-161:ALTW:AUTO-SINGLE:OTTUMW1G:OTTUMWA5:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.27 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.34 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.19 | P11:22:MEC:AUTO-SINGLE:NEAL3G:3
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.26 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.19 | P11:24:MEC:AUTO-SINGLE:LOUIS31G:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.25 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.3 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.17 | P13:345-22:MEC:AUTO-SINGLE:RAUN3:NEAL3G:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.24 | P13:345-24:MEC:AUTO-SINGLE:RAUN3:NEAL4G:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.18 | P13:345-24:MEC:AUTO-SINGLE:LOUISA3:LOUIS31G:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21023 | 116.23 | P11:230:WERE:JECU1_GEN::
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21023 | 116.23 | P11:345:WERE:JECU2_GEN::
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21023 | 116.22 | P11:345:WERE:JECU3_GEN::
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.4 | P11:345:WERE:WOLFU1_GEN::
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21029 | 116.03 | 511435 SNYDER-4 138 588779 TAP_G17-036 138 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21035 | 116.03 | 511453 DUNCAN-4 138 511552 DUNCHERTP4 138 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21035 | 116.03 | 511455 D.E.S.-4 138 511552 DUNCHERTP4 138 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21035 | 116.02 | 511455 D.E.S.-4 138 529344 OMDUNE-4 138 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 114.98 | 511456 O.K.U.-7 345 588760 GEN-2017-033 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21333 | 117.74 | 511456 O.K.U.-7 345 763215 G18-092-TAP 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21347 | 118.31 | 511468 L.E.S.-7 345 762467 G18-015-TAP 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21244 | 117.72 | 511468 L.E.S.-7 345 763215 G18-092-TAP 345 2
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 115.66 | 511468 L.E.S.-7 345 763318 GEN-2018-115 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21029 | 116.05 | 511488 112GORE4 138 511510 LAIRGST4 138 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.2104 | 116.11 | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21029 | 116.04 | 511500 CACHE4 138 511510 LAIRGST4 138 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21029 | 116.03 | 511500 CACHE4 138 588779 TAP_G17-036 138 2
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21146 | 116.06 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.20361 | 113.09 | 511553 CHISHOLM7 345 523961 POTTER_CO 7 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.20361 | 113.09 | 511553 CHISHOLM7 345 523961 POTTER_CO 7 345 2
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.20733 | 115.5 | 511553 CHISHOLM7 345 755000 WWDBORDT 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.14 | 511557 CHISHOLM6 230 3WXFMR CHISHOLM6 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21041 | 116.02 | 514801 MINCO 7 345 555234 NSUB345 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.20953 | 115.63 | 515375 WWRDEHV7 345 755000 WWDBORDT 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21722 | 120.2 | 515458 BORDER 7 345 560022 CRAWFISH_DR 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21722 | 120.15 | 515458 BORDER 7 345 755000 WWDBORDT 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21037 | 116.02 | 515543 RENFROW7 345 763421 G18-128-TAP 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21024 | 116.12 | 515618 BALKOW 7 345 3WXFMR BALKOW 7 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21024 | 116.13 | 515618 BALKOW 7 345 3WXFMR BALKOW 7 1_Dup1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21033 | 116.04 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.2102 | 116.39 | 515634 PALDR1W7 345 3WXFMR PALO2 _1 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.13 | 515677 BADGER 7 345 563170 G15082_1 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21023 | 116.01 | 521017 ONEY 4 138 521089 WASHITA4 138 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.02 | 522800 MU-TULIA 3 115 525179 TULIA_TP 3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.16 | 522892 MU-BROWNFLD2 69.0 526761 BROWNFLD_TP2 69.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.03 | 523090 TEXAS_CNTY 3 115 589380 GEN-2017-100 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21023 | 116.16 | 523093 HITCHLAND 3 115 523174 GOODWELLWND3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.34 | 523097 HITCHLAND 7 345 523112 NOVUS1 7 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.4 | 523097 HITCHLAND 7 345 523215 FREWHELCOL17 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.20824 | 114.83 | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.45 | 523097 HITCHLAND 7 345 560252 G10-14 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.01 | 523099 TC-DRYTRLS 3 115 588480 A16-010_SUB 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.23 | 523112 NOVUS1 7 345 3WXFMR NOVUS XF2 2
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.04 | 523112 NOVUS1 7 345 3WXFMR XIANA2011198 _1 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21026 | 116.02 | 523118 BUFF_DUNES 7 345 523853 FINNEY 7 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.02 | 523120 COLE 3 115 588860 GEN-2017-047 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21025 | 116.04 | 523172 GWELL_COLL11 34.5 523174 GOODWELLWND3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21025 | 116.04 | 523173 GWELL_COLL21 34.5 523174 GOODWELLWND3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21036 | 116.01 | 523221 XIT_INTG 6 230 3WXFMR SIEM_T126401 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21048 | 116.07 | 523267 PRINGLE 6 230 3WXFMR ENRCO13617-1 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21048 | 116.06 | 523267 PRINGLE 6 230 523979 HARRNG_EST 6 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.2109 | 116.2 | 523309 MOORE_CNTY 6 230 523323 MCDWL_CREEK6 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21062 | 116.12 | 523323 MCDWL_CREEK6 230 523959 POTTER_CO 6 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.20997 | 116.45 | 523959 POTTER_CO 6 230 524010 ROLLHILLS 6 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21843 | 117.19 | 523959 POTTER_CO 6 230 524267 BUSHLAND 6 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.2181 | 118.35 | 523959 POTTER_CO 6 230 525461 NEWHART 6 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.2139 | 121.11 | 523961 POTTER_CO 7 345 3WXFMR WAUK 90343-A 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21025 | 115.74 | 523978 HARRNG_MID 6 230 523979 HARRNG_EST 6 230 @1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.2105 | 116.16 | 524267 BUSHLAND 6 230 3WXFMR WH 7001795 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.22491 | 117.94 | 524267 BUSHLAND 6 230 524623 DEAFSMITH 6 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21015 | 116.44 | 524296 SPNSPUR_WND7 345 524299 SPNSPUR_COL7 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21015 | 116.44 | 524299 SPNSPUR_COL7 345 3WXFMR SPNSPUR_COL7 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21416 | 117.09 | 524415 AMA_SOUTH 6 230 525213 SWISHER 6 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.67 | 524502 NORTON 3 115 524509 FE-TUCMCARI3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21219 | 116.45 | 524575 DS-#25+ 3 115 524597 PANDAHFD 3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21219 | 116.55 | 524575 DS-#25+ 3 115 524630 TIERABLANCA3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.11 | 524604 HEREFRD_SB 2 69.0 524608 HERFRD_STH 2 69.0 *1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.2234 | 122.73 | 524623 DEAFSMITH 6 230 760498 G17-146-TAP 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.52 | 524721 DS-#15&#19+2 69.0 524745 CASTRO_CNTY2 69.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21033 | 116.03 | 524770 PLSNT_HILL 6 230 3WXFMR EFAE1100068A 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.2145 | 121.59 | 524875 OASIS 6 230 524885 SN_JUAN_TAP6 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21101 | 117.16 | 524875 OASIS 6 230 524909 ROOSEVELT 6 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21441 | 121.97 | 524885 SN_JUAN_TAP6 230 527483 CHAVES_CNTY6 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21044 | 116.22 | 524909 ROOSEVELT 6 230 3WXFMR ABB LMM60042 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21721 | 122.19 | 524909 ROOSEVELT 6 230 525531 TOLK 6 230 2
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.77 | 524923 PORTALES 2 69.0 524929 RO-PORT_MTR2 69.0 @1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.42 | 524923 PORTALES 2 69.0 524941 PORTALES#1 2 69.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.66 | 525023 BC-BAIL_MTR2 69.0 525027 BAILEYCO 2 69.0 @1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21132 | 116.55 | 525056 BC-EARTH 3 115 525480 PLANT_X 3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.51 | 525191 KRESS_INT 2 69.0 525203 SW-KRESS 2 69.0 Z1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.6 | 525192 KRESS_INT 3 115 3WXFMR ENRCO 136155 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21328 | 116.83 | 525213 SWISHER 6 230 525461 NEWHART 6 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.15 | 525272 KISER 3 115 3WXFMR VON 13819/1 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.61 | 525326 COX 3 115 3WXFMR ELCO 13474-3 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.61 | 525414 LAMTON 3 115 3WXFMR ASEA MLL9204 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.22646 | 119.68 | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21301 | 118.1 | 525481 PLANT_X 6 230 3WXFMR WH ALM20171 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21975 | 121 | 525481 PLANT_X 6 230 526435 SUNDOWN 6 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.2234 | 121.02 | 525481 PLANT_X 6 230 760498 G17-146-TAP 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21374 | 116.49 | 525481 PLANT_X 6 230 762174 G17-218TAP 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21416 | 116.56 | 525481 PLANT_X 6 230 762174 G17-218TAP 230 2
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.22176 | 121.7 | 525531 TOLK 6 230 525586 NEEDMORE 6 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21284 | 118.23 | 525531 TOLK 6 230 525637 LAMB_CNTY 6 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.23952 | 120.42 | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.2154 | 116.76 | 525531 TOLK 6 230 762174 G17-218TAP 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21576 | 116.82 | 525531 TOLK 6 230 762174 G17-218TAP 230 2
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.34286 | 155.48 | 525549 TOLK 7 345 3WXFMR ABBXNL844501 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.22176 | 121.69 | 525586 NEEDMORE 6 230 526935 YOAKUM 6 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.41 | 525599 LC-SANDHLL+2 69.0 525606 AMHERST 2 69.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.45 | 525606 AMHERST 2 69.0 525613 W_LITTLFLD 2 69.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.46 | 525613 W_LITTLFLD 2 69.0 525635 LAMB_CNTY 2 69.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.42 | 525635 LAMB_CNTY 2 69.0 525650 LC-LTTLFLD+2 69.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21284 | 118.23 | 525637 LAMB_CNTY 6 230 3WXFMR WH ALM20172 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.41 | 525779 FLOYD_CNTY 2 69.0 525790 FLOYDADA_TP2 69.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.29 | 525828 TUCO_INT 3 115 3WXFMR DS F78800913 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.20276 | 118.38 | 525832 TUCO_INT 7 345 526936 YOAKUM_345 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.49 | 526086 SW_6786_N 2 69.0 526087 SW_6786_S 2 69.0 Z1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.49 | 526086 SW_6786_N 2 69.0 526102 SP-HETTLER 2 69.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.56 | 526087 SW_6786_S 2 69.0 526284 PLANTERS 2 69.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.1 | 526160 CARLISLE 3 115 3WXFMR WH RLP38371 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.44 | 526195 QUINCY 3 115 526196 SP-MILWAUKEE 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.34 | 526268 LUBBCK_STH 3 115 3WXFMR NA 70454A 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.6 | 526284 PLANTERS 2 69.0 526297 LUBBCK_EST 2 69.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.2104 | 116.47 | 526424 PACIFIC 3 115 526434 SUNDOWN 3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21023 | 116.06 | 526435 SUNDOWN 6 230 3WXFMR UPDATE LATER _12 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21049 | 118.87 | 526435 SUNDOWN 6 230 526460 AMOCO_SS 6 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21049 | 116.5 | 526460 AMOCO_SS 6 230 526935 YOAKUM 6 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21025 | 116.08 | 526525 WOLFFORTH 6 230 3WXFMR UPDATE LATER _13 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.48 | 526735 TERRY_CNTY 2 69.0 526747 LG-BROWNFLD2 69.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21015 | 118.02 | 526935 YOAKUM 6 230 527028 INK_BASIN 6 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.2145 | 116.3 | 526936 YOAKUM_345 345 3WXFMR SPX WT04221 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.20267 | 126.57 | 526936 YOAKUM_345 345 527896 HOBBS_INT 7 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21004 | 117.39 | 527028 INK_BASIN 6 230 527894 HOBBS_INT 6 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21022 | 116.43 | 527130 DENVER_N 3 115 527286 HIGGEAST 3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21028 | 116.02 | 527149 MUSTANG 6 230 3WXFMR ENRCO 136161 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21043 | 114.01 | 527149 MUSTANG 6 230 527151 GS-MUSTANG 6 230 @1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.29 | 527202 SEAGRAVES 3 115 3WXFMR ABB MLL92408 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.17 | 527212 DIAMONDBACK3 115 3WXFMR HOW 36773714 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21022 | 116.41 | 527286 HIGGEAST 3 115 527363 HIGG 3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21024 | 116.16 | 527325 OXY_WSEM_TP3 115 527362 JOHNSON_DRW3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.15 | 527340 DOSS 3 115 3WXFMR ELCO 13566/1 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.14 | 527345 LEGACY 2 69.0 527350 XTO_ROBRTSN2 69.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.14 | 527346 LEGACY 3 115 3WXFMR VROL 13735-1 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.12 | 527350 XTO_ROBRTSN2 69.0 527355 BOARDMAN 2 69.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.05 | 527355 BOARDMAN 2 69.0 527365 FLANNAGAN 2 69.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.02 | 527360 MAPCO 3 115 527362 JOHNSON_DRW3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.08 | 527362 JOHNSON_DRW3 115 528775 LE-ERF 3 115 @1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.01 | 527370 TENNECO_TAP2 69.0 527371 TENNECO 2 69.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21205 | 116.35 | 527483 CHAVES_CNTY6 230 527799 EDDY_NORTH 6 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.05 | 527508 PRICE 3 115 527509 PRICE_TAP 3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.02 | 527514 CV-PINE 2 69.0 527563 ROSWLL_INT 2 69.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.05 | 527529 RIACBRSH_TP3 115 527533 SW4J795_E 3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.02 | 527529 RIACBRSH_TP3 115 527536 BRASHER 3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.05 | 527533 SW4J795_E 3 115 527564 ROSWLL_INT 3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.06 | 527563 ROSWLL_INT 2 69.0 527575 SW_4702 2 69.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21045 | 116.1 | 527564 ROSWLL_INT 3 115 527597 TWEEDY 3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.06 | 527575 SW_4702 2 69.0 527589 CV-ORCHARD 2 69.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.02 | 527589 CV-ORCHARD 2 69.0 527619 DEXTER_TP 2 69.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21023 | 116.18 | 527653 MILO_WIND 1 34.5 527655 RSVLT_CC_E 7 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21015 | 116.1 | 527654 RSVLT_CC_W 7 345 527655 RSVLT_CC_E 7 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21015 | 116.36 | 527654 RSVLT_CC_W 7 345 527666 RSVLT_COL1 7 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21011 | 116.3 | 527655 RSVLT_CC_E 7 345 527656 CROSSROADS 7 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21015 | 116.36 | 527666 RSVLT_COL1 7 345 3WXFMR RSVLT_COL1 7 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.15 | 527790 EDDY_SVC 1 8.50 527799 EDDY_NORTH 6 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.05 | 527864 CUNNINHAM 3 115 528568 MONUMNT_TP 3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21013 | 116.16 | 527865 CUNNIGHM_N 6 230 527867 CUNNIGHM_S 6 230 *1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.14 | 527865 CUNNIGHM_N 6 230 527883 CUNINGHAM3 1 13.8 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21023 | 116.08 | 527865 CUNNIGHM_N 6 230 527963 POTASH_JCT 6 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21023 | 116.02 | 527867 CUNNIGHM_S 6 230 527894 HOBBS_INT 6 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21025 | 116.35 | 527894 HOBBS_INT 6 230 527903 HOBBS_PLT3 1 18.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.2102 | 116.23 | 527896 HOBBS_INT 7 345 3WXFMR HICO 68759-1 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 115.8 | 527965 KIOWA 7 345 528027 RDRUNNER 7 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21028 | 115.81 | 528015 PHANTOM 7 345 528027 RDRUNNER 7 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.11 | 528024 RR_SVC_HV 3 115 528021 RDRUNNR_SVC1 15.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.25 | 528024 RR_SVC_HV 3 115 528025 RDRUNNER 3 115 Z1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 115.81 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.08 | 528025 RDRUNNER 3 115 587990 GEN-2016-121 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.14 | 528222 CHINA_DRAW 3 115 528225 CD_SVC_HV 3 115 Z1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 115.82 | 528341 LE-SANANDRS3 115 528627 LE-TXACO_TP3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21024 | 116.06 | 528394 QUAHADA 3 115 528396 XTO_BIGEDDY3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.01 | 528552 OIL_CENTER 3 115 528554 COOPER_RNCH3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.02 | 528554 COOPER_RNCH3 115 528581 BYRD_TP 3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.05 | 528568 MONUMNT_TP 3 115 528581 BYRD_TP 3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.04 | 528596 CARDINAL 3 115 528605 TARGA 3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.06 | 528603 NA_ENRICH 3 115 528605 TARGA 3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.11 | 528617 LE-WAITS 2 69.0 528325 LE-WAITS 3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.03 | 528617 LE-WAITS 2 69.0 528714 LE-FORT_SW 2 69.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21028 | 116.05 | 528618 LE-LOVINTON2 69.0 528334 LE-NRTH_INT3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.42 | 528626 LE-PLNSINT 2 69.0 526928 PLAINS_INT 3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.42 | 528626 LE-PLNSINT 2 69.0 528709 LE-PLNSGOAB2 69.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.05 | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.11 | 528669 LE-STKLDRTP2 69.0 528740 LE-PLANS_SW2 69.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.3 | 528709 LE-PLNSGOAB2 69.0 528740 LE-PLANS_SW2 69.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.05 | 528709 LE-PLNSGOAB2 69.0 528747 LE-ALLRED 2 69.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.03 | 528714 LE-FORT_SW 2 69.0 528718 LE-NEWTEX 2 69.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.11 | 528735 LE-PLAINSUB2 69.0 528740 LE-PLANS_SW2 69.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.03 | 528775 LE-ERF 3 115 528779 LE-TALLCOTN3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21016 | 115.79 | 530583 POSTROCK7 345 560082 G16-050-TAP 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 115.81 | 531213 SANTAFE3 115 531408 PIERCVL3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21025 | 116.04 | 531501 BUCKNER7 345 531502 CIMRRN 7 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21025 | 116.04 | 531502 CIMRRN 7 345 531503 CIMRRN 1 34.5 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21014 | 115.75 | 531510 HARBNGR3 115 3WXFMR HARBGR345 _1 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21026 | 116.06 | 532663 LEC U5 24.0 532854 LEC U5 6 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21033 | 116.04 | 532794 ROSEHIL7 345 560053 G15052_T 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21037 | 116.03 | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21026 | 116.06 | 532853 LAWHILL6 230 532854 LEC U5 6 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21025 | 116.01 | 539117 SPRVILL-EHVB 230 539695 SPEARVL6 230 Z1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21025 | 116.02 | 539803 IRONWOOD7 345 3WXFMR IRONWOOD MPT 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21026 | 116.13 | 542951 HAW G5 1 22.0 543665 HAWTHN5 161 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21026 | 116.17 | 542955 LAC G1 1 22.0 542981 LACYGNE7 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21025 | 116.15 | 542956 LAC G2 1 24.0 542981 LACYGNE7 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21024 | 116.2 | 542957 IAT G1 1 24.0 542982 IATAN 7 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21025 | 116.27 | 542962 IAT G2 1 24.5 542982 IATAN 7 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.03 | 542966 WGARDNR5 161 543105 BULLCRK5 161 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21274 | 115.57 | 560022 CRAWFISH_DR 345 762216 G17-151TAP 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21243 | 116.52 | 560022 CRAWFISH_DR 345 762467 G18-015-TAP 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 112.71 | 560022 CRAWFISH_DR 345 763087 GEN-2018-073 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21355 | 116.84 | 560022 CRAWFISH_DR 345 763215 G18-092-TAP 345 2
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21016 | 115.8 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.45 | 560252 G10-14 345 560253 G10-14-1 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.18 | 560253 G10-14-1 115 560254 G10-14-SUB1 34.5 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.19 | 560253 G10-14-1 115 560255 G10-14-SUB2 34.5 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.04 | 560581 G06-44-2 34.5 523111 NOVUS1 3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.08 | 560582 G06-44-3 34.5 560577 G06-44 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.07 | 560583 G06-44-4 34.5 560577 G06-44 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 115.72 | 560757 ASGI13_02_1 69.0 560758 ASGI13_02_2 34.5 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 115.72 | 560757 ASGI13_02_1 69.0 562731 WHEATLAND 69.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 115.73 | 560763 ASGI13_03_1 115 560761 ASGI13_03_2 34.5 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.16 | 562015 FIREWHEEL1 34.5 523215 FREWHELCOL17 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.16 | 562016 FIREWHEEL2 34.5 523215 FREWHELCOL17 345 2
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 115.71 | 562323 AGI1202&1305 115 562324 AGI1202&1305 34.5 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 115.73 | 562727 LESBIA 115 562728 SANJONTAP 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 115.72 | 562728 SANJONTAP 115 562729 CAPROCKTAP1 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 115.72 | 562730 CAPROCKTAP2 69.0 562729 CAPROCKTAP1 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 115.72 | 562730 CAPROCKTAP2 69.0 562731 WHEATLAND 69.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.15 | 563171 G15082_2 34.5 563170 G15082_1 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 115.78 | P11:13.8:AEPW:COM1-1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 115.79 | P11:13.8:AEPW:COM2-1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 115.79 | P11:13.8:AEPW:COM3-1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 115.78 | P11:18:AEPW:WELSH1-1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 115.79 | P11:18:AEPW:WELSH3-1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 115.78 | P11:24:AEPW:PIRKEY 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 115.68 | P11:24:AEPW:SWS3-1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 115.74 | P11:24:AEPW:TURKCOAL
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.2104 | 116.11 | P12:138:AEPW-OMPA:DUNCAN-4:OMDUNCN4
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.02 | P12:138:AEPW:112GORE4:L.E.S.-4
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21029 | 116.05 | P12:138:AEPW:112GORE4:SNYDER-4
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21029 | 116.05 | 5841_Dup1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21037 | 115.37 | 584560 GEN-2015-014 115 584561 G15-014XFMR1 34.5 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21035 | 116.08 | P12:138:AEPW:SANTAFE:DUNCAN-4
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.08 | 587991 G16-121XFMR1 34.5 587990 GEN-2016-121 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.01 | 588480 A16-010_SUB 115 3WXFMR A16-010_SUB 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.2104 | 116.1 | P12:138:AEPW:DUNCAN-4:L.E.S.-4
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 115.46 | 588761 G17-033XFMR1 34.5 588760 GEN-2017-033 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 115.46 | 588765 G17-033XFMR2 34.5 588760 GEN-2017-033 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.02 | 588861 G17-047XFMR1 34.5 588860 GEN-2017-047 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21013 | 115.79 | P12:138:AEPW:ELKCTY-4:CLINTJC4
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.03 | 589381 G17-100XFMR1 34.5 589380 GEN-2017-100 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21028 | 116.07 | P12:138:AEPW:SHERID4:112GORE4
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.2103 | 116.06 | P12:345:AEPW-OKGE:CLARKSV7:MUSKOGE7
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21275 | 117.78 | P12:345:AEPW:L.E.S7:TERRYRD7
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21275 | 117.77 | P12:345:AEPW:L.E.S7:TERRYRD7
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21274 | 117.75 | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21349 | 118.25 | P12:345:AEPW-OKGE:L.E.S.-7:GRACMNT7
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21349 | 118.23 | P12:345:AEPW-OKGE:L.E.S.-7:GRACMNT7
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21333 | 118.8 | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.08 | P22:345:AMMO::LABADIE:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.08 | P22:345:AMMO::LABADIE:2
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.09 | P22:345:AMMO::LABADIE:3
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.08 | P22:345:AMMO::LABADIE:4
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.07 | P22:345:AMMO::RUSHISLAND:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21028 | 116.06 | P22:345:AMMO::RUSHISLAND:2
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21029 | 115.79 | P13:138-13.8:AEPW:COMANC-4_#2
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 115.8 | P13:138-13.8:AEPW:S.W.S.-4
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.20968 | 115.47 | P13:138-230:AEPW:ELKCTY-4
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21028 | 115.79 | P13:138-24:AEPW:PIRKEY 4
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21032 | 115.69 | P13:138-24:AEPW:S.W.S.-4
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21029 | 115.75 | P13:138-24:AEPW:TURK 4
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21044 | 116.11 | P13:138-345:AEPW:L.E.S.-4_#2
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21028 | 116.02 | P12:500:EES-EAI:KEO:WMPEHV
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21029 | 116.14 | P23:500:EES-EAI:KEO:B4941
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21028 | 116.02 | P23:500:EES-EAI:KEO:B4931
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21029 | 116.13 | P23:500:EES-EAI:KEO:B4921
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21028 | 116.07 | P23:500:EES-EAI:INDEP2:B6126
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21028 | 116.06 | P23:500:EES-EAI:PD:INDEP2:LN:FK479
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21029 | 115.79 | P13:345-18:AEPW:WELSH 7_#1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21029 | 115.79 | P13:345-18:AEPW:WELSH 7_#3
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 115.79 | P13:69-13.8:AEPW:COMANC-2
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.08 | P11:024:DPC:ALMA2:6
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.04 | P11:18:ITCM:EMERYGT1:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.05 | P11:18:ITCM:EMERYGT2:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.05 | P11:161:ITCM:MGS CT1:1C
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.05 | P11:161:ITCM:MGS CT2:2C
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21025 | 116.06 | 652537 WHITE 3 345 659286 DEERCREK-BE3 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21026 | 116.02 | 652568 GROTONSOUTH7 115 659275 GROTON_G-BE7 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21025 | 116.06 | 659286 DEERCREK-BE3 345 3WXFMR DEERCRK KU1A 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.05 | 672601 BD 4 230 672306 BD 6G 18.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.05 | 672610 POPLAR 4 230 672310 POPLAR 1G 18.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.05 | 672610 POPLAR 4 230 672311 POPLAR 2G 18.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.04 | 672621 SHAND 4 230 672321 SHAND 1G 18.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.03 | 672649 CODETTE 4 230 672650 NIPAWIN 4 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.04 | 672696 BRADA 4 230 672699 NBEC 4 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.12 | P23:345:MDU::COYOTE::5707-5712-5715::::
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.3 | P23:345:MEC:CBEC 905
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.25 | P23:345:MEC:CBEC 908
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21028 | 116.04 | P23:345:MEC:GDMEC 901
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21028 | 116.04 | P23:345:MEC:GDMEC 902
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.06 | P23:345:MEC:GDMEC 908
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.17 | P23:345:MEC:RAUN 0180
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.24 | P23:345:MEC:RAUN 0210
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.18 | P23:345:MEC:LOUISA 954
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21028 | 116.19 | P23:345:MEC:LOUISA 964
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.03 | P21:115:XEL:AUTO-SINGLE:CHEMOLT7:LSPOWER7:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.07 | P21:115:XEL:AUTO-SINGLE:COLVILL7:CANONFLSG7:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.03 | P21:115:XEL:AUTO-SINGLE:FARIBALTP7:FARIBALTGEN:Z
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.13 | P21:230:OTP:AUTO-SINGLE:SQBUTTE4:YNG24:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.12 | P23:345:OTP:CENTER 3:3215(1)
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.12 | P23:345:OTP:CENTER 3:3225(1)
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.06 | P12:230:UMZW:# 687 #: FT IN SD. FT-BG1 LINE FAULT
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.06 | P12:230:UMZW:# 3617 #: FT IN SD. FT-BG2 LINE FAULT
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 114.69 | 760494 GEN-2017-146 230 760498 G17-146-TAP 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 114.68 | 760495 G17-146-XFM1 34.5 760494 GEN-2017-146 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 115.46 | 761356 G17-239-XFMR 34.5 761355 GEN-2017-239 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 115.46 | 761359 G17-239-XFMR 34.5 761355 GEN-2017-239 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 115.63 | 761797 G17-187XFM1 34.5 761796 GEN-2017-187 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 115.63 | 761800 G17-187XFM2 34.5 761796 GEN-2017-187 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 110.67 | 762132 GEN-2017-158 230 763252 G18-099-XFM1 34.5 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 110.67 | 762132 GEN-2017-158 230 763255 G18-099-XFM2 34.5 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 111.27 | 762133 G17-158XFM1 34.5 762132 GEN-2017-158 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 111.27 | 762136 G17-158XFM2 34.5 762132 GEN-2017-158 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 113.54 | 762216 G17-151TAP 345 762217 GEN-2017-151 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21274 | 116.85 | 762216 G17-151TAP 345 762467 G18-015-TAP 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 115.27 | 762218 G17-151XFM1 34.5 762217 GEN-2017-151 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 115.27 | 762221 G17-151XFM2 34.5 762217 GEN-2017-151 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 115.27 | 762224 G17-151XFM3 34.5 762217 GEN-2017-151 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 115.27 | 762227 G17-151XFM4 34.5 762217 GEN-2017-151 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 114.55 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 115.11 | 762461 G18-015-XFM1 34.5 762460 GEN-2018-015 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 115.11 | 762464 G18-015-XFM2 34.5 762460 GEN-2018-015 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21163 | 116.42 | 762467 G18-015-TAP 345 763215 G18-092-TAP 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 113.8 | 763087 GEN-2018-073 345 763088 G18-073-XFM1 34.5 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 114.78 | 763087 GEN-2018-073 345 763091 G18-073-XFM2 34.5 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 110.64 | 763120 GEN-2018-081 230 763121 G18-081-XFM1 34.5 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 112.78 | 763120 GEN-2018-081 230 764011 G19-074-XFM1 34.5 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 112.92 | 763186 GEN-2018-089 230 763187 G18-089-XFM1 34.5 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 113.84 | 763208 GEN-2018-092 345 763215 G18-092-TAP 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 114.77 | 763208 GEN-2018-092 345 763220 G18-092-XFM1 34.5 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 114.77 | 763208 GEN-2018-092 345 763223 G18-092-XFM2 34.5 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 113.15 | 763241 GEN-2018-097 230 763296 G18-111-XFM1 34.5 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 112.51 | 763241 GEN-2018-097 230 763307 G18-112-XFM1 34.5 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 112.51 | 763241 GEN-2018-097 230 763310 G18-112-XFM2 34.5 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 112.23 | 763241 GEN-2018-097 230 763395 G18-124-XFM1 34.5 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 112.23 | 763241 GEN-2018-097 230 763398 G18-124-XFM2 34.5 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 115.66 | 763318 GEN-2018-115 345 763319 G18-115-XFM1 34.5 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 112 | 763483 GEN-2019-003 230 763484 G19-003-XFM1 34.5 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 114.56 | 763483 GEN-2019-003 230 763605 G19-021-XFM1 34.5 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 115.46 | 763516 GEN-2019-011 345 763517 G19-011-XFM1 34.5 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 115.55 | 763879 GEN-2019-056 115 763880 G19-056XFM1 34.5 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.20993 | 116.19 | P42:345:OKGE:SB_BVTY7305
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21011 | 115.75 | P23:345:WERE:BUFF_345-534::
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21011 | 115.75 | P23:345:WERE:BUFF_345-543::
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21023 | 116.23 | P23:345:WERE:JEC_345-15::
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21022 | 116.18 | P23:345:WERE:JEC_345-16::
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21023 | 116.22 | P23:345:WERE:JEC_345-19::
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21023 | 116.22 | P23:345:WERE:JEC_345-20::
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.39 | P23:345:WERE:WOLF_345-50::
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.39 | P23:345:WERE:WOLF_345-60::
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21029 | 115.8 | P42:345:AEPW:WELSH CB 10620 NBTB+FAULT
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21028 | 115.79 | P41:345:AEPW:WELSH CB 10630 NBTB+FAULT
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 115.79 | P41:345:AEPW:WELSH CB 11670 NBTB+FAULT
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21039 | 115.78 | P41:345:AEPW:WELSH CB 11680 NBTB+FAULT
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 115.78 | P41:345:AEPW:WELSH CB 12540 NBTB+FAULT
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21333 | 117.33 | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21381 | 118.58 | P42:345:AEPW:LAWTON EASTSIDE CB 3413A NBTB+FAULT
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21416 | 118.94 | P42:345:AEPW:LAWTON EASTSIDE CB 3425A NBTB+FAULT
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21346 | 118.96 | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21275 | 117.77 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21275 | 117.77 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21275 | 117.74 | P42:345:AEPW:TERRYRD_CB_3421A_NBTB
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21026 | 116.18 | P23:345:KCPL:LACYGNE_R2-5::LACYGU2-LACYGNE-STILWELL
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21026 | 115.82 | P45:345:UMZW:# 1328 #: GI IN NE.
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21029 | 115.8 | P23:345:AEPW:WELSH CB 10620 NBTB
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21028 | 115.79 | P23:345:AEPW:WELSH CB 10630 NBTB
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 115.79 | P23:345:AEPW:WELSH CB 11670 NBTB
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21039 | 115.78 | P23:345:AEPW:WELSH CB 11680 NBTB
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 115.78 | P23:345:AEPW:WELSH CB 12540 NBTB
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21333 | 117.74 | P23:345:AEPW:OKLAUNION CB 3401A NBTB
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21381 | 118.58 | P23:345:AEPW:LAWTON EASTSIDE CB 3413A NBTB
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21416 | 118.94 | P23:345:AEPW:LAWTON EASTSIDE CB 3425A NBTB
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21346 | 118.96 | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21275 | 117.77 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21275 | 117.77 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21275 | 117.74 | P23:345:AEPW:TERRYRD_CB_3421A_NBTB
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.05 | P11:161:GMO:DOGWOOD_COMBINED_CYCLE_UNIT_OUTAGE
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.06 | P11:115:SUNC:GARDENCITY_S2:97:531459(2)
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21013 | 115.77 | P12:345:PWT:BUFF-THIS_345_1::
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21013 | 115.77 | P12:345:PWT:BUFF-THIS_345_2::
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21014 | 115.83 | P12:345:PWT:THIS-DGRS_345_1::FUTURE
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21014 | 115.83 | P12:345:PWT:THIS-DGRS_345_2::FUTURE
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21037 | 116.06 | P12:069:WFEC:ANADRKO_WATONGA
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21292 | 117.97 | P23:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21547 | 120.4 | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21292 | 117.97 | P42:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB+FAULT
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21547 | 120.4 | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.20561 | 114.13 | P42:345:OKGE:SB_BVTY7315_PRE19S
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.20996 | 115.62 | P23:345:SUNC:MO_BRK182
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.20996 | 115.62 | P23:345:SUNC:MO_BRK382
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.20992 | 115.79 | P23:345:SUNC:MO_BRK188
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21146 | 116.06 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21029 | 115.79 | P12:138-13.8:AEPW:COMANC-4_#1
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.20968 | 115.47 | P12:230:AEPW:ELKCITY6:CHISHOLM6
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.2114 | 116.62 | P12:230:AEPW:SWEETWT6:CHISHOLM6
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997713 ABBXNL844501 230 1 |  | 553 | 0.34286 | 157.44 | 525531 TOLK 6 230 3WXFMR TOLK 6 2
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21029 | 116.18 | P23:345:KCPL-WERE:237LACYGNE_R1-6::LACYGU1-LACYGNE-NEOSHO
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21026 | 116.06 | P11:230:WERE:LECU5_GEN::
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.08 | P11:161:GMO:DOGWOOD_COMBINED_CYCLE_UNIT_OUTAGE_1_1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.02 | P11:20:KACY:NEARMAN N1::N1 OUT OF SERVICE:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21026 | 116.02 | P12:69:KACY:NMGEN-NMISOBUS::NEARMAN N1-NM ISOBUS OPEN:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21026 | 116.02 | P13:20-161:KACY:NEARMAN5-NMISOBUS:NAMEPLATE:NEARMAN N1 GSU:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21026 | 116.02 | P21:20:KACY:546702NMGENN1-546703NMISOBUSC1::::
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.23 | P11:115:SPS:HOBBS1&3:145MW::::
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21033 | 114.72 | P11:115:SPS:MUSTANG1&3:153MW::::
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21284 | 118.23 | P12:230:SPS:K37::1_TOLK_LAMB:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21048 | 116.06 | P12:230:SPS:K43::1_PRNGLE_HARR_E:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.2103 | 115.81 | P12:230:SPS:K44::1_EPLNT_HARRW:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21042 | 116.22 | P12:115:SPS:T04::1_TRBLNC_CASTRO:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21048 | 116.02 | P12:115:SPS:T06::1_SPRMN_PRNGLE:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.5 | P12:115:SPS:T21::1_GRSSLND_GRAHAM:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.05 | P12:115:SPS:T24B::1_RSWLL_BRSHRF:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21028 | 116.05 | P12:115:SPS:T26::1_CHAVES_RSWLCTY:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21149 | 116.45 | P12:115:SPS:T28A::1_LAMTON_PLANTX:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21073 | 116.02 | P12:115:SPS:T29::1_LAMTON_HALECTR:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21198 | 117.27 | P12:115:SPS:T30::1_LAMB_HOCKLY:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21198 | 116.37 | P12:115:SPS:T31::1_HOCKLY_SUNDWN:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21023 | 116.06 | P12:115:SPS:T35::1_TERRY_YOAKUM:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21028 | 116.78 | P12:115:SPS:T45::1_NORRIS_OASIS:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21026 | 115.82 | P12:115:SPS:T57::1_MUSTG_SEGRVS:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21154 | 116.03 | P12:115:SPS:T58::1_HERFRD_CARGIL:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21154 | 116.57 | P12:115:SPS:T59::1_CARGIL_CURRY:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.02 | P12:115:SPS:T64::1_RNDALL_PULLMN:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21124 | 116.38 | P12:115:SPS:T67::1_HAPPY_KRESS:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21032 | 115.77 | P12:115:SPS:T68::1_TUCO_FLOYD:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21028 | 115.81 | P12:115:SPS:T69::1_LUBBE_CROSBY:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.02 | P12:115:SPS:T70::1_COLTR_S_GORG:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21022 | 116.63 | P12:115:SPS:T71::1_CRLSLE_YUMA:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21036 | 116.1 | P12:115:SPS:T81::1_COX_FLOYD:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.26 | P12:115:SPS:T83::1_SP-FKFD_ALLEN:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21022 | 116.44 | P12:115:SPS:T89::1_DC_N_HIGG:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.07 | P12:115:SPS:T91::1_HIGG_RUSSELL:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21032 | 116.02 | P12:115:SPS:V01::1_MOOREW_RVRVIEW:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21049 | 116.07 | P12:115:SPS:V04::1_EPLANT_RNDALL:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21041 | 116.06 | P12:115:SPS:V07::1_COX_HALECTR:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21141 | 116.23 | P12:115:SPS:V09::1_HALECTR_PLANTX:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21026 | 116.21 | P12:115:SPS:V12::1_PLANTX_BAILEY:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.03 | P12:115:SPS:V15::1_TUCO_INDANA:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.20991 | 116.16 | P12:115:SPS:V24::1_WOLFTH_TERRY:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21045 | 116.07 | P12:115:SPS:V26::1_RSWLL_EDDY_N:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.4 | P12:115:SPS:V33::1_LUBBS_LYNN:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21132 | 117.14 | P12:115:SPS:V37::1_CASTRO_PLANTX:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21028 | 116.05 | P12:115:SPS:V44::1_COLTR_OWENS:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.16 | P12:115:SPS:V46::1_ALLEN_WHEELCK:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21029 | 116.5 | P12:115:SPS:V49::1_YOAKUM_SHLCO2:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.2107 | 116.68 | P12:115:SPS:V55::1_SUNDWN_TERRY:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.2104 | 116.59 | P12:115:SPS:V56::1_COCHRAN_SUNDWN:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.09 | P12:115:SPS:V62::1_CRLSLE_INDANA:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.2104 | 116.07 | P12:115:SPS:V78::2_CURRY_RSVLT:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21025 | 116.19 | P12:115:SPS:V81::1_LE-WAIT_LE-LVN:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21028 | 116.06 | P12:115:SPS:V95::1_DC_N_SHLCO2:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.02 | P12:115:SPS:W11::1_DC_S_SMINLE:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.03 | P12:115:SPS:W12::1_SMINLE_DOSS:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.1 | P12:115:SPS:W14::1_SMINLE_GAINES:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.03 | P12:115:SPS:W26::1_CUNGHM_OILCNTR:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.61 | P12:115:SPS:W32::1_PRMTR_FE-CLSIN:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21024 | 116.26 | P12:115:SPS:W35::1_GAINES_JNSDRW:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21219 | 116.59 | P12:115:SPS:W40::1_WCANYON_TRBLNC:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21055 | 116.11 | P12:115:SPS:W52::1_NEWHART_KRESS:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.67 | P12:115:SPS:W58::1_NORTON_LOPEZ:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.25 | P12:115:SPS:W59::1_LOPEZ_CMPBLL:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21028 | 116.55 | P12:115:SPS:W62::1_PLSTHL_CURRY:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.2104 | 116.07 | P12:115:SPS:W63::1_PLSTHL_CURRY:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.36 | P12:115:SPS:W64::1_PLSTHL_FE-CLV:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21029 | 116.57 | P12:115:SPS:W65::1_PLSTHL_CURRY:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.23 | P12:115:SPS:W66::1_PORTA_GREYHUND:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21024 | 116.02 | P12:115:SPS:W76::1_QUAHA_PCA:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21219 | 116.1 | P12:115:SPS:W77::1_RNDAL_WCANYON:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21028 | 116.07 | P12:115:SPS:W99::1_CAPITAN_CHAVES:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.05 | P12:115:SPS:U03::1_CARDNL_NEF:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21023 | 116.53 | P12:115:SPS:U14::1_DC_STH_INKBSN:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21025 | 116.47 | P12:115:SPS:V15::1_INKBSN_LE-WAT:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.2105 | 116.15 | P12:115:SPS:U16::1_BSHLND_OUTPST:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.2105 | 116.16 | P12:115:SPS:U17::1_COLTR_OUTPST:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21034 | 116.26 | P12:115:SPS:U19::1_DEAN_PLAINS:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.2105 | 116.07 | P12:115:SPS:U23::1_COLTR_HILSDE:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.20186 | 124.36 | P42:345:SPS:YOAKUM:J18####:SLG1:EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.20186 | 124.36 | P43:345:SPS:YOAKUM:TF#####:SLG:EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.20186 | 124.36 | P42:345:SPS:YOAKUM:J17####:SLG:EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.20186 | 124.36 | P42:345:SPS:YOAKUM:J18####:SLG2:EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21026 | 116.06 | P11:18:HAST:::EGYCTR2G WEC2_LOSS OF WEC 2 GEN_:HV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21026 | 116.06 | P13:18-115:HAST:::EGYCNTR7 XFMR G2WEC 2 GSU_:HV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.08 | P11:161:GMO:DOGWOOD-COMBINED-CYCLE-UNIT-OUTA:::HV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21029 | 116.18 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21026 | 116.18 | P23:345:KCPL:LACYGNE-R2-5:::EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21023 | 116.23 | P11:230:WERE:JECU1-GEN:::HV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21026 | 116.06 | P11:230:WERE:LECU5-GEN:::HV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21023 | 116.23 | P11:345:WERE:JECU2-GEN:::EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21023 | 116.22 | P11:345:WERE:JECU3-GEN:::EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.4 | P11:345:WERE:WOLFU1-GEN:::EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21013 | 115.77 | P12:345:PWT:BUFF-THIS-345-1:::EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21013 | 115.77 | P12:345:PWT:BUFF-THIS-345-2:::EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21011 | 115.75 | P23:345:WERE:BUFF-345-534:::EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21011 | 115.75 | P23:345:WERE:BUFF-345-543:::EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21023 | 116.23 | P23:345:WERE:JEC-345-15:::EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21022 | 116.18 | P23:345:WERE:JEC-345-16:::EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21023 | 116.22 | P23:345:WERE:JEC-345-19:::EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21023 | 116.22 | P23:345:WERE:JEC-345-20:::EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.39 | P23:345:WERE:WOLF-345-50:::EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.39 | P23:345:WERE:WOLF-345-60:::EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.34 | P11:022:NPPD:COOPER1G:1:983:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21022 | 116.33 | P11:023:NPPD:GENTLM1G:1:757:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21022 | 116.35 | P11:024:NPPD:GENTLM2G:2:757:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21026 | 116.01 | P11:161:OPPD:N OMA 5G:LT::HV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21026 | 116.01 | P11:161:OPPD:N OMA 5G:::HV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21023 | 116.2 | P13:345:OPPD:NEBCTY1G:::EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21022 | 116.22 | P13:345:OPPD:NEBCTY2G:::EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21026 | 116.01 | P13:161:OPPD:N OMA 5G:::HV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.22 | P22:345:OPPD:S3458 NEBCTY1G:LT::EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21023 | 116.2 | P22:345:OPPD:S3458 NEBCTY1G:::EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.25 | P22:345:OPPD:S3458 NEBCTY2G:LT::EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21022 | 116.22 | P22:345:OPPD:S3458 NEBCTY2G:::EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.22 | P23:345:OPPD:S3458 NEBCTY1G:LT::EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21023 | 116.2 | P23:345:OPPD:S3458 NEBCTY1G:::EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.25 | P23:345:OPPD:S3458 NEBCTY2G:LT::EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21022 | 116.22 | P23:345:OPPD:S3458 NEBCTY2G:::EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 115.8 | P12:115:SUNC:PLYMELL-PIERCEVILLE:::HV::
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21025 | 116.06 | P11:018:UMZB:# 5 #:: DCS IN SD. DEERCREEK_MV::
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21026 | 116.03 | P11:022:UMZB:# 15 #:: LO IN ND. LELAND OLDS 1_MV::
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21025 | 116.07 | P11:020:UMZB:# 16 #:: LO IN ND. LELAND OLDS 2_MV::
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21025 | 116.14 | P11:023:UMZB:# 31 #:: AVS IN ND. ANTELOPE VALLEY 1_MV::
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21025 | 116.14 | P11:023:UMZB:# 32 #:: AVS IN ND. ANTELOPE VALLEY 2_MV::
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21021 | 116.33 | P11:024:UMZB:# 33 #:: LRS IN WY. LARAMIE RIVER STATION 1_MV::
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.06 | P12:230:UMZW:# 687 #:: FT IN SD. FT-BG1 BRANCH FAULT:HV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.06 | P12:230:UMZW:# 3617 #:: FT IN SD. FT-BG2 BRANCH FAULT:HV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.06 | P12:230:UMZW:# 4038 #:: BG-FT IN SD. FAULT FOR TRANSMISSION CIRCUIT (BG-FT).:HV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.06 | P12:230:UMZW:# 4039 #:: BG-FT IN SD. FAULT FOR TRANSMISSION CIRCUIT (BG-FT).:HV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.03 | P13:230:UMZW:# 5135 #:: OA IN SD. FAULT ON TRANSFORMER (2).:HV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.03 | P13:230:UMZW:# 5136 #:: OA IN SD. FAULT ON TRANSFORMER (3).:HV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21026 | 115.82 | P23:345:UMZW:# 2423 #:: GI IN NE. GI 1596 BKR FAULT:EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21026 | 115.82 | P23:345:UMZW:# 2426 #:: GI IN NE. GI 1592 BKR FAULT:EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21026 | 115.82 | P23:345:UMZW:# 2432 #:: GI IN NE. GI 1092 BKR FAULT:EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21026 | 115.82 | P23:345:UMZW:# 2440 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1092 STUCK BKR:EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21026 | 115.82 | P23:345:UMZW:# 2444 #:: GI IN NE. GI-SWEET BRANCH FAULT & GI 1596 STUCK BKR:EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21026 | 115.82 | P23:345:UMZW:# 2446 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1196 STUCK BKR:EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21026 | 115.82 | P42:345:UMZW:# 2413 #:: FT2 IN SD. FT2-LO2 BRANCH FAULT & FT2 2992 STUCK BKR:EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21026 | 115.82 | P42:345:UMZW:# 2415 #:: FT2 IN SD. FT2-GI BRANCH FAULT & FT2 3392 STUCK BKR:EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21031 | 115.74 | P11:138:WFEC:HUGO1:465MW :::
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21026 | 116.02 | P11:138:WFEC:MORLND2:132MW:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21026 | 116.03 | P11:138:WFEC:MORLND3:149MW :::
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21036 | 116.06 | P12:138:WFEC:ANADRKO_CLVLND::::
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.2103 | 116.06 | P12:345:OKGE-AEPW:BKRBKR12::::
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21064 | 116.18 | P12:345:OKGE:BKRBKR21::::
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21083 | 116.26 | P12:345:OKGE:BKRBKR24::::
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21274 | 117.75 | P12:345:OKGE-AEPW:BKRBKR25::::
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.20996 | 115.72 | P12:345:OKGE:BKRBKR336::::
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.20996 | 115.72 | P12:345:OKGE:BKRBKR336_2::::
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21349 | 118.25 | P12:345:OKGE-AEPW:BKRBKR366::::
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21349 | 118.23 | P12:345:OKGE-AEPW:BKRBKR366::::
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21236 | 117.15 | P12:345:OKGE:BKRBKR367::::
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21001 | 115.72 | P12:345:OKGE:BKRBKR4193::::
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21001 | 115.72 | P12:345:OKGE:BKRBKR4194::::
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.02 | P12:345:OKGE:BKRBKR4195::::
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.2099 | 115.76 | P12:345:OKGE-SPS:BKRBKR4201::::
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.2099 | 115.76 | P12:345:OKGE-SPS:BKRBKR4202::::
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21037 | 116.03 | P12:345:OKGE:BKRBKR421::::
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.20994 | 115.6 | P12:345:OKGE:BKRBKR443NEW::::
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.20993 | 115.6 | P12:345:OKGE:BKRBKR443NEW2::::
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21011 | 115.79 | P12:345:OKGE-ITC:BKRBKR502::::
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21011 | 115.79 | P12:345:OKGE-ITC:BKRBKR503::::
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21014 | 115.83 | P12:345:OKGE-ITC:BKRBKR502_1::::
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21014 | 115.83 | P12:345:OKGE-ITC:BKRBKR503_1::::
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21021 | 116.33 | P12:345:OKGE:BKRBKR604::::
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.2102 | 116.37 | P12:345:OKGE:BKRBKR604_2::::
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21029 | 115.82 | P11:345:OKGE:BKRBKR_GSU07::::
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21029 | 115.81 | P11:345:OKGE:BKRBKR_GSU08::::
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21029 | 115.8 | P11:138:OKGE:BKRBKR_GSU21::::
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21025 | 115.83 | P12:138:OKGE:BKRBKR85_MOS1::::
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.20994 | 116.13 | P42:345:OKGE:SB_ARIA7381::::
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21722 | 120.17 | P42:345:OKGE:SB_BVTY7387::::
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21038 | 116.02 | P41:345:OKGE:SB_REUD7381::::
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21037 | 116.03 | P41:345:OKGE:SB_REUD7383::::
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21037 | 116.06 | P41:345:OKGE:SB_REUD7385::::
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.2104 | 116.06 | P42:345:OKGE:SB_REUD7389::::
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21025 | 116.05 | P11:115:SUNC:GARDENCITY_S2:103:531459(2):HV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21025 | 116.07 | P11:115:SUNC:FORTDDODGE_4:157:539670(4):HV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.04 | P11:345:599:CIMARRON1WIND:200:531603(1):EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.47 | P13:115:SUNC:HOLCOMB_GSU:::HV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21025 | 116.05 | P13:115:SUNC:S2_GSU:::HV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21025 | 116.07 | P13:115:SUNC:FORTDODGE_GSU:::HV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21025 | 116.04 | P23:345:SUNC:BU_BRK682:::EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.14 | 300003 1THLG3 24.0 301503 7THOMHLGSU3 345 3
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.01 | 300007 1NM G2 22.0 301537 7NEWMADGSU2 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.01 | 300046 7NEWMAD 345 301537 7NEWMADGSU2 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.14 | 300049 7THOMHL 345 301503 7THOMHLGSU3 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.08 | P11:20:AMMO:1LAB�� G1:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.08 | P11:20:AMMO:1LAB�� G2:2
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.27 | P11:345:AMMO::CALLAWAY:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.08 | P11:345:AMMO::LABADIE:3
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.08 | P11:345:AMMO::LABADIE:4
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.07 | P11:345:AMMO::RUSHISLAND:U1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.07 | P11:345:AMMO::RUSHISLAND:U2
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.06 | P11:138:AMMO::SIOUX:2
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 115.83 | P11:24:CLEC::G1DOLHIL:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.06 | P12:765:AEP:AEP ROCKP-AEP JEFF 765
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 115.78 | P11:HV:EES::PIRKEY 1:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 115.79 | P11:EHV:EES::WELSH3-1:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 115.74 | P11:HV:EES::TURKCOAL:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.25 | P12:EHV:EES::7CALAWY 1:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21028 | 116.02 | 338056 CHALKBLUFFPV 500 338162 8W.MEMPHIS% 500 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21029 | 115.75 | P12:HV:EES::TURK 4%:1(1)
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21029 | 115.79 | P12:EHV:EES::WELSH 7:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21029 | 115.79 | P12:EHV:EES::WELSH 7:1(1)
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21028 | 115.79 | P12:HV:EES::PIRKEY 4:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.2103 | 116.06 | P12:EHV:EES::CLARKSV7!:MUSKOGE7!:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.06 | 344011 7HUGHES 345 344012 7HPW-N 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.08 | 344884 7LABADIE1 345 344894 1LAB G1 20.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.08 | 344885 7LABADIE2 345 344895 1LAB G2 20.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.08 | 344886 7LABADIE3 345 344896 1LAB G3 20.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.08 | 344887 7LABADIE4 345 344897 1LAB G4 20.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.07 | 345667 7RUSH 1 345 345670 1RUSH G1 18.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.06 | 345668 7RUSH 2 345 345671 1RUSH G2 18.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.05 | 345755 4SIOUX 1 138 345756 1SIOUX 1 18.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.05 | 345764 4SIOUX 2 138 345765 1SIOUX 2 18.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.12 | P12:345:MDU::CENTER:COYOTE:1::::
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.12 | P13:345:MDU:COYOTE GSU LOSS:COYOTE::1::::
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.03 | P11:345:MEC:GDMEC CT1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.03 | P11:345:MEC:GDMEC CT2
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.14 | P11:345:MEC:GDMEC ST
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.35 | P11:345:MEC-NPPD:COOPER 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.24 | P11:24:XEL:AUTO-SINGLE:SHERC31G:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.24 | P11:24:XEL:AUTO-SINGLE:SHERC32G:2
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.33 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.16 | P11:20:XEL:AUTO-SINGLE:PRIS31G:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.16 | P11:20:XEL:AUTO-SINGLE:PRIS32G:2
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.2 | P11:22:XEL:AUTO-SINGLE:MNTCE31G:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.16 | P11:20:XEL:AUTO-SINGLE:KING31G:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.02 | P11:13:XEL:AUTO-SINGLE:HBRS73G:9
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.02 | P11:18:XEL:AUTO-SINGLE:BLKD76G:6
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.22 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.22 | P11:22:GRE:AUTO-SINGLE:GRE-COAL42G:2
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.14 | P11:24:OTP:AUTO-SINGLE:BIGSTN1G:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.15 | P11:20:OTP:AUTO-SINGLE:CENTER2G:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.05 | P11:22:OTP:AUTO-SINGLE:CENTER1G:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.13 | P11:24:OTP:AUTO-SINGLE:COYOTE1G:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.05 | P11:24:DPC:AUTO-SINGLE:GENOA53G:3
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.03 | P12:115:XEL:AUTO-SINGLE:CHEMOLT7:LSPOWER7:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.07 | P12:115:XEL:AUTO-SINGLE:COLVILL7:CANONFLSG7:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.03 | P12:115:XEL:AUTO-SINGLE:FARIBALTP7:FARIBALTGEN:Z
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.13 | P12:230:OTP:AUTO-SINGLE:SQBUTTE4:YNG24:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.22 | P13:24-345:XEL:AUTO-SINGLE:SHERC31G:SHERCO3:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.22 | P13:24-345:XEL:AUTO-SINGLE:SHERC32G:SHERCO3:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.3 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.16 | P13:20-345:XEL:AUTO-SINGLE:PRIS31G:PRISLD3:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.16 | P13:20-345:XEL:AUTO-SINGLE:PRIS32G:PRISLD3:2
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.2 | P13:22-345:XEL:AUTO-SINGLE:MNTCE31G:MNTCELO3:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.15 | P13:20-345:XEL:AUTO-SINGLE:KING31G:ASKING3:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.02 | P13:13-115:XEL:AUTO-SINGLE:HBRS73G:HIBRDGE7:9
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.2 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL41G:GRE-COALCR4:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.2 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL42G:GRE-COALCR4:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.13 | P13:230-24:OTP:AUTO-SINGLE:BIGSTON4:BIGSTN1G:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.13 | P13:20-230:OTP:AUTO-SINGLE:CENTER2G:YNG24:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.04 | P13:22-230:OTP:AUTO-SINGLE:CENTER1G:CENTER4:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.12 | P13:24-345:OTP:AUTO-SINGLE:COYOTE1G:COYOTE3:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.05 | P13:24-161:DPC:AUTO-SINGLE:GENOA53G:GENOA5:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.07 | P13:24-161:DPC:AUTO-SINGLE:JPM:ALMA5:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21028 | 116.02 | 38203 J1819 POI 500 337957 8KEO% 500 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21028 | 116.02 | 38203 J1819 POI 500 338056 CHALKBLUFFPV 500 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.13 | P11:115:XEL:RIV COMBINE CYCLE
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.04 | P12:115:XEL:BDS #2 5
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.04 | P11:115:XEL:HBR #6
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.04 | P11:115:XEL:HBR #7
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.16 | P11:115:XEL:HBR #6 7 8
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.16 | P23:345:XEL:8H14 PRI
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.16 | P23:345:XEL:8H17 PRI AS
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.3 | P23:345:XEL:8N28 SHC
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.22 | P23:345:XEL:8N22 SHC
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.22 | P23:345:XEL:8N17 SHC
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.21 | P23:345:XEL:8N8 MNN
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.15 | P23:345:XEL:8P1 KING
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.15 | P23:345:XEL:8P2 KING
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.04 | P23:115:XEL:5P147 IVH AS
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.03 | P11:18:ALTW:AUTO-SINGLE:EMERYST1:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.03 | P11:22:ALTW:AUTO-SINGLE:LANS54G:4
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.17 | P11:22:ALTW:AUTO-SINGLE:ARNOLD1G:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.2 | P11:24:ALTW:AUTO-SINGLE:OTTUMW1G:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.03 | P13:18-161:ALTW:AUTO-SINGLE:EMERYST1:EMERY5:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.03 | P13:22-161:ALTW:AUTO-SINGLE:LANS54G:LANSINGL15:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.16 | P13:22-161:ALTW:AUTO-SINGLE:ARNOLD1G:ARNOLD5:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.19 | P13:24-161:ALTW:AUTO-SINGLE:OTTUMW1G:OTTUMWA5:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.27 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.34 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.19 | P11:22:MEC:AUTO-SINGLE:NEAL3G:3
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.26 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.19 | P11:24:MEC:AUTO-SINGLE:LOUIS31G:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.25 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.3 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.17 | P13:345-22:MEC:AUTO-SINGLE:RAUN3:NEAL3G:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.24 | P13:345-24:MEC:AUTO-SINGLE:RAUN3:NEAL4G:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.18 | P13:345-24:MEC:AUTO-SINGLE:LOUISA3:LOUIS31G:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21023 | 116.23 | P11:230:WERE:JECU1_GEN::
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21023 | 116.23 | P11:345:WERE:JECU2_GEN::
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21023 | 116.22 | P11:345:WERE:JECU3_GEN::
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.4 | P11:345:WERE:WOLFU1_GEN::
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21029 | 116.03 | 511435 SNYDER-4 138 588779 TAP_G17-036 138 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21035 | 116.03 | 511453 DUNCAN-4 138 511552 DUNCHERTP4 138 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21035 | 116.03 | 511455 D.E.S.-4 138 511552 DUNCHERTP4 138 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21035 | 116.02 | 511455 D.E.S.-4 138 529344 OMDUNE-4 138 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 114.98 | 511456 O.K.U.-7 345 588760 GEN-2017-033 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21333 | 117.74 | 511456 O.K.U.-7 345 763215 G18-092-TAP 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21347 | 118.31 | 511468 L.E.S.-7 345 762467 G18-015-TAP 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21244 | 117.72 | 511468 L.E.S.-7 345 763215 G18-092-TAP 345 2
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 115.66 | 511468 L.E.S.-7 345 763318 GEN-2018-115 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21029 | 116.05 | 511488 112GORE4 138 511510 LAIRGST4 138 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.2104 | 116.11 | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21029 | 116.04 | 511500 CACHE4 138 511510 LAIRGST4 138 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21029 | 116.03 | 511500 CACHE4 138 588779 TAP_G17-036 138 2
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21146 | 116.06 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.20361 | 113.09 | 511553 CHISHOLM7 345 523961 POTTER_CO 7 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.20361 | 113.09 | 511553 CHISHOLM7 345 523961 POTTER_CO 7 345 2
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.20733 | 115.5 | 511553 CHISHOLM7 345 755000 WWDBORDT 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.14 | 511557 CHISHOLM6 230 3WXFMR CHISHOLM6 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21041 | 116.02 | 514801 MINCO 7 345 555234 NSUB345 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.20953 | 115.63 | 515375 WWRDEHV7 345 755000 WWDBORDT 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21722 | 120.2 | 515458 BORDER 7 345 560022 CRAWFISH_DR 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21722 | 120.15 | 515458 BORDER 7 345 755000 WWDBORDT 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21037 | 116.02 | 515543 RENFROW7 345 763421 G18-128-TAP 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21024 | 116.12 | 515618 BALKOW 7 345 3WXFMR BALKOW 7 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21024 | 116.13 | 515618 BALKOW 7 345 3WXFMR BALKOW 7 1_Dup1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21033 | 116.04 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.2102 | 116.39 | 515634 PALDR1W7 345 3WXFMR PALO2 _1 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.13 | 515677 BADGER 7 345 563170 G15082_1 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21023 | 116.01 | 521017 ONEY 4 138 521089 WASHITA4 138 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.02 | 522800 MU-TULIA 3 115 525179 TULIA_TP 3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.16 | 522892 MU-BROWNFLD2 69.0 526761 BROWNFLD_TP2 69.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.03 | 523090 TEXAS_CNTY 3 115 589380 GEN-2017-100 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21023 | 116.16 | 523093 HITCHLAND 3 115 523174 GOODWELLWND3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.34 | 523097 HITCHLAND 7 345 523112 NOVUS1 7 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.4 | 523097 HITCHLAND 7 345 523215 FREWHELCOL17 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.20824 | 114.83 | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.45 | 523097 HITCHLAND 7 345 560252 G10-14 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.01 | 523099 TC-DRYTRLS 3 115 588480 A16-010_SUB 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.23 | 523112 NOVUS1 7 345 3WXFMR NOVUS XF2 2
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.04 | 523112 NOVUS1 7 345 3WXFMR XIANA2011198 _1 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21026 | 116.02 | 523118 BUFF_DUNES 7 345 523853 FINNEY 7 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.02 | 523120 COLE 3 115 588860 GEN-2017-047 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21025 | 116.04 | 523172 GWELL_COLL11 34.5 523174 GOODWELLWND3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21025 | 116.04 | 523173 GWELL_COLL21 34.5 523174 GOODWELLWND3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21036 | 116.01 | 523221 XIT_INTG 6 230 3WXFMR SIEM_T126401 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21048 | 116.07 | 523267 PRINGLE 6 230 3WXFMR ENRCO13617-1 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21048 | 116.06 | 523267 PRINGLE 6 230 523979 HARRNG_EST 6 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.2109 | 116.2 | 523309 MOORE_CNTY 6 230 523323 MCDWL_CREEK6 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21062 | 116.12 | 523323 MCDWL_CREEK6 230 523959 POTTER_CO 6 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.20997 | 116.45 | 523959 POTTER_CO 6 230 524010 ROLLHILLS 6 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21843 | 117.19 | 523959 POTTER_CO 6 230 524267 BUSHLAND 6 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.2181 | 118.35 | 523959 POTTER_CO 6 230 525461 NEWHART 6 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.2139 | 121.11 | 523961 POTTER_CO 7 345 3WXFMR WAUK 90343-A 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21025 | 115.74 | 523978 HARRNG_MID 6 230 523979 HARRNG_EST 6 230 @1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.2105 | 116.16 | 524267 BUSHLAND 6 230 3WXFMR WH 7001795 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.22491 | 117.94 | 524267 BUSHLAND 6 230 524623 DEAFSMITH 6 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21015 | 116.44 | 524296 SPNSPUR_WND7 345 524299 SPNSPUR_COL7 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21015 | 116.44 | 524299 SPNSPUR_COL7 345 3WXFMR SPNSPUR_COL7 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21416 | 117.09 | 524415 AMA_SOUTH 6 230 525213 SWISHER 6 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.67 | 524502 NORTON 3 115 524509 FE-TUCMCARI3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21219 | 116.45 | 524575 DS-#25+ 3 115 524597 PANDAHFD 3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21219 | 116.55 | 524575 DS-#25+ 3 115 524630 TIERABLANCA3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.11 | 524604 HEREFRD_SB 2 69.0 524608 HERFRD_STH 2 69.0 *1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.2234 | 122.73 | 524623 DEAFSMITH 6 230 760498 G17-146-TAP 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.52 | 524721 DS-#15&#19+2 69.0 524745 CASTRO_CNTY2 69.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21033 | 116.03 | 524770 PLSNT_HILL 6 230 3WXFMR EFAE1100068A 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.2145 | 121.59 | 524875 OASIS 6 230 524885 SN_JUAN_TAP6 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21101 | 117.16 | 524875 OASIS 6 230 524909 ROOSEVELT 6 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21441 | 121.97 | 524885 SN_JUAN_TAP6 230 527483 CHAVES_CNTY6 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21044 | 116.22 | 524909 ROOSEVELT 6 230 3WXFMR ABB LMM60042 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21721 | 122.19 | 524909 ROOSEVELT 6 230 525531 TOLK 6 230 2
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.77 | 524923 PORTALES 2 69.0 524929 RO-PORT_MTR2 69.0 @1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.42 | 524923 PORTALES 2 69.0 524941 PORTALES#1 2 69.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.66 | 525023 BC-BAIL_MTR2 69.0 525027 BAILEYCO 2 69.0 @1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21132 | 116.55 | 525056 BC-EARTH 3 115 525480 PLANT_X 3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.51 | 525191 KRESS_INT 2 69.0 525203 SW-KRESS 2 69.0 Z1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.6 | 525192 KRESS_INT 3 115 3WXFMR ENRCO 136155 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21328 | 116.83 | 525213 SWISHER 6 230 525461 NEWHART 6 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.15 | 525272 KISER 3 115 3WXFMR VON 13819/1 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.61 | 525326 COX 3 115 3WXFMR ELCO 13474-3 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.61 | 525414 LAMTON 3 115 3WXFMR ASEA MLL9204 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.22646 | 119.68 | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21301 | 118.1 | 525481 PLANT_X 6 230 3WXFMR WH ALM20171 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21975 | 121 | 525481 PLANT_X 6 230 526435 SUNDOWN 6 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.2234 | 121.02 | 525481 PLANT_X 6 230 760498 G17-146-TAP 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21374 | 116.49 | 525481 PLANT_X 6 230 762174 G17-218TAP 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21416 | 116.56 | 525481 PLANT_X 6 230 762174 G17-218TAP 230 2
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.22176 | 121.7 | 525531 TOLK 6 230 525586 NEEDMORE 6 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21284 | 118.23 | 525531 TOLK 6 230 525637 LAMB_CNTY 6 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.23952 | 120.42 | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.2154 | 116.76 | 525531 TOLK 6 230 762174 G17-218TAP 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21576 | 116.82 | 525531 TOLK 6 230 762174 G17-218TAP 230 2
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.34286 | 155.48 | 525549 TOLK 7 345 3WXFMR ABBXNL844501 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.22176 | 121.69 | 525586 NEEDMORE 6 230 526935 YOAKUM 6 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.41 | 525599 LC-SANDHLL+2 69.0 525606 AMHERST 2 69.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.45 | 525606 AMHERST 2 69.0 525613 W_LITTLFLD 2 69.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.46 | 525613 W_LITTLFLD 2 69.0 525635 LAMB_CNTY 2 69.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.42 | 525635 LAMB_CNTY 2 69.0 525650 LC-LTTLFLD+2 69.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21284 | 118.23 | 525637 LAMB_CNTY 6 230 3WXFMR WH ALM20172 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.41 | 525779 FLOYD_CNTY 2 69.0 525790 FLOYDADA_TP2 69.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.29 | 525828 TUCO_INT 3 115 3WXFMR DS F78800913 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.20276 | 118.38 | 525832 TUCO_INT 7 345 526936 YOAKUM_345 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.49 | 526086 SW_6786_N 2 69.0 526087 SW_6786_S 2 69.0 Z1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.49 | 526086 SW_6786_N 2 69.0 526102 SP-HETTLER 2 69.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.56 | 526087 SW_6786_S 2 69.0 526284 PLANTERS 2 69.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.1 | 526160 CARLISLE 3 115 3WXFMR WH RLP38371 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.44 | 526195 QUINCY 3 115 526196 SP-MILWAUKEE 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.34 | 526268 LUBBCK_STH 3 115 3WXFMR NA 70454A 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.6 | 526284 PLANTERS 2 69.0 526297 LUBBCK_EST 2 69.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.2104 | 116.47 | 526424 PACIFIC 3 115 526434 SUNDOWN 3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21023 | 116.06 | 526435 SUNDOWN 6 230 3WXFMR UPDATE LATER _12 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21049 | 118.87 | 526435 SUNDOWN 6 230 526460 AMOCO_SS 6 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21049 | 116.5 | 526460 AMOCO_SS 6 230 526935 YOAKUM 6 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21025 | 116.08 | 526525 WOLFFORTH 6 230 3WXFMR UPDATE LATER _13 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.48 | 526735 TERRY_CNTY 2 69.0 526747 LG-BROWNFLD2 69.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21015 | 118.02 | 526935 YOAKUM 6 230 527028 INK_BASIN 6 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.2145 | 116.3 | 526936 YOAKUM_345 345 3WXFMR SPX WT04221 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.20267 | 126.57 | 526936 YOAKUM_345 345 527896 HOBBS_INT 7 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21004 | 117.39 | 527028 INK_BASIN 6 230 527894 HOBBS_INT 6 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21022 | 116.43 | 527130 DENVER_N 3 115 527286 HIGGEAST 3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21028 | 116.02 | 527149 MUSTANG 6 230 3WXFMR ENRCO 136161 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21043 | 114.01 | 527149 MUSTANG 6 230 527151 GS-MUSTANG 6 230 @1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.29 | 527202 SEAGRAVES 3 115 3WXFMR ABB MLL92408 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.17 | 527212 DIAMONDBACK3 115 3WXFMR HOW 36773714 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21022 | 116.41 | 527286 HIGGEAST 3 115 527363 HIGG 3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21024 | 116.16 | 527325 OXY_WSEM_TP3 115 527362 JOHNSON_DRW3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.15 | 527340 DOSS 3 115 3WXFMR ELCO 13566/1 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.14 | 527345 LEGACY 2 69.0 527350 XTO_ROBRTSN2 69.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.14 | 527346 LEGACY 3 115 3WXFMR VROL 13735-1 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.12 | 527350 XTO_ROBRTSN2 69.0 527355 BOARDMAN 2 69.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.05 | 527355 BOARDMAN 2 69.0 527365 FLANNAGAN 2 69.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.02 | 527360 MAPCO 3 115 527362 JOHNSON_DRW3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.08 | 527362 JOHNSON_DRW3 115 528775 LE-ERF 3 115 @1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.01 | 527370 TENNECO_TAP2 69.0 527371 TENNECO 2 69.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21205 | 116.35 | 527483 CHAVES_CNTY6 230 527799 EDDY_NORTH 6 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.05 | 527508 PRICE 3 115 527509 PRICE_TAP 3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.02 | 527514 CV-PINE 2 69.0 527563 ROSWLL_INT 2 69.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.05 | 527529 RIACBRSH_TP3 115 527533 SW4J795_E 3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.02 | 527529 RIACBRSH_TP3 115 527536 BRASHER 3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.05 | 527533 SW4J795_E 3 115 527564 ROSWLL_INT 3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.06 | 527563 ROSWLL_INT 2 69.0 527575 SW_4702 2 69.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21045 | 116.1 | 527564 ROSWLL_INT 3 115 527597 TWEEDY 3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.06 | 527575 SW_4702 2 69.0 527589 CV-ORCHARD 2 69.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.02 | 527589 CV-ORCHARD 2 69.0 527619 DEXTER_TP 2 69.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21023 | 116.18 | 527653 MILO_WIND 1 34.5 527655 RSVLT_CC_E 7 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21015 | 116.1 | 527654 RSVLT_CC_W 7 345 527655 RSVLT_CC_E 7 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21015 | 116.36 | 527654 RSVLT_CC_W 7 345 527666 RSVLT_COL1 7 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21011 | 116.3 | 527655 RSVLT_CC_E 7 345 527656 CROSSROADS 7 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21015 | 116.36 | 527666 RSVLT_COL1 7 345 3WXFMR RSVLT_COL1 7 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.15 | 527790 EDDY_SVC 1 8.50 527799 EDDY_NORTH 6 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.05 | 527864 CUNNINHAM 3 115 528568 MONUMNT_TP 3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21013 | 116.16 | 527865 CUNNIGHM_N 6 230 527867 CUNNIGHM_S 6 230 *1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.14 | 527865 CUNNIGHM_N 6 230 527883 CUNINGHAM3 1 13.8 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21023 | 116.08 | 527865 CUNNIGHM_N 6 230 527963 POTASH_JCT 6 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21023 | 116.02 | 527867 CUNNIGHM_S 6 230 527894 HOBBS_INT 6 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21025 | 116.35 | 527894 HOBBS_INT 6 230 527903 HOBBS_PLT3 1 18.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.2102 | 116.23 | 527896 HOBBS_INT 7 345 3WXFMR HICO 68759-1 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 115.8 | 527965 KIOWA 7 345 528027 RDRUNNER 7 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21028 | 115.81 | 528015 PHANTOM 7 345 528027 RDRUNNER 7 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.11 | 528024 RR_SVC_HV 3 115 528021 RDRUNNR_SVC1 15.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.25 | 528024 RR_SVC_HV 3 115 528025 RDRUNNER 3 115 Z1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 115.81 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.08 | 528025 RDRUNNER 3 115 587990 GEN-2016-121 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.14 | 528222 CHINA_DRAW 3 115 528225 CD_SVC_HV 3 115 Z1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 115.82 | 528341 LE-SANANDRS3 115 528627 LE-TXACO_TP3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21024 | 116.06 | 528394 QUAHADA 3 115 528396 XTO_BIGEDDY3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.01 | 528552 OIL_CENTER 3 115 528554 COOPER_RNCH3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.02 | 528554 COOPER_RNCH3 115 528581 BYRD_TP 3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.05 | 528568 MONUMNT_TP 3 115 528581 BYRD_TP 3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.04 | 528596 CARDINAL 3 115 528605 TARGA 3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.06 | 528603 NA_ENRICH 3 115 528605 TARGA 3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.11 | 528617 LE-WAITS 2 69.0 528325 LE-WAITS 3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.03 | 528617 LE-WAITS 2 69.0 528714 LE-FORT_SW 2 69.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21028 | 116.05 | 528618 LE-LOVINTON2 69.0 528334 LE-NRTH_INT3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.42 | 528626 LE-PLNSINT 2 69.0 526928 PLAINS_INT 3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.42 | 528626 LE-PLNSINT 2 69.0 528709 LE-PLNSGOAB2 69.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.05 | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.11 | 528669 LE-STKLDRTP2 69.0 528740 LE-PLANS_SW2 69.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.3 | 528709 LE-PLNSGOAB2 69.0 528740 LE-PLANS_SW2 69.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.05 | 528709 LE-PLNSGOAB2 69.0 528747 LE-ALLRED 2 69.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.03 | 528714 LE-FORT_SW 2 69.0 528718 LE-NEWTEX 2 69.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.11 | 528735 LE-PLAINSUB2 69.0 528740 LE-PLANS_SW2 69.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.03 | 528775 LE-ERF 3 115 528779 LE-TALLCOTN3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21016 | 115.79 | 530583 POSTROCK7 345 560082 G16-050-TAP 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 115.81 | 531213 SANTAFE3 115 531408 PIERCVL3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21025 | 116.04 | 531501 BUCKNER7 345 531502 CIMRRN 7 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21025 | 116.04 | 531502 CIMRRN 7 345 531503 CIMRRN 1 34.5 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21014 | 115.75 | 531510 HARBNGR3 115 3WXFMR HARBGR345 _1 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21026 | 116.06 | 532663 LEC U5 24.0 532854 LEC U5 6 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21033 | 116.04 | 532794 ROSEHIL7 345 560053 G15052_T 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21037 | 116.03 | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21026 | 116.06 | 532853 LAWHILL6 230 532854 LEC U5 6 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21025 | 116.01 | 539117 SPRVILL-EHVB 230 539695 SPEARVL6 230 Z1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21025 | 116.02 | 539803 IRONWOOD7 345 3WXFMR IRONWOOD MPT 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21026 | 116.13 | 542951 HAW G5 1 22.0 543665 HAWTHN5 161 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21026 | 116.17 | 542955 LAC G1 1 22.0 542981 LACYGNE7 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21025 | 116.15 | 542956 LAC G2 1 24.0 542981 LACYGNE7 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21024 | 116.2 | 542957 IAT G1 1 24.0 542982 IATAN 7 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21025 | 116.27 | 542962 IAT G2 1 24.5 542982 IATAN 7 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.03 | 542966 WGARDNR5 161 543105 BULLCRK5 161 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21274 | 115.57 | 560022 CRAWFISH_DR 345 762216 G17-151TAP 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21243 | 116.52 | 560022 CRAWFISH_DR 345 762467 G18-015-TAP 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 112.71 | 560022 CRAWFISH_DR 345 763087 GEN-2018-073 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21355 | 116.84 | 560022 CRAWFISH_DR 345 763215 G18-092-TAP 345 2
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21016 | 115.8 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.45 | 560252 G10-14 345 560253 G10-14-1 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.18 | 560253 G10-14-1 115 560254 G10-14-SUB1 34.5 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.19 | 560253 G10-14-1 115 560255 G10-14-SUB2 34.5 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.04 | 560581 G06-44-2 34.5 523111 NOVUS1 3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.08 | 560582 G06-44-3 34.5 560577 G06-44 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.07 | 560583 G06-44-4 34.5 560577 G06-44 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 115.72 | 560757 ASGI13_02_1 69.0 560758 ASGI13_02_2 34.5 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 115.72 | 560757 ASGI13_02_1 69.0 562731 WHEATLAND 69.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 115.73 | 560763 ASGI13_03_1 115 560761 ASGI13_03_2 34.5 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.16 | 562015 FIREWHEEL1 34.5 523215 FREWHELCOL17 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.16 | 562016 FIREWHEEL2 34.5 523215 FREWHELCOL17 345 2
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 115.71 | 562323 AGI1202&1305 115 562324 AGI1202&1305 34.5 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 115.73 | 562727 LESBIA 115 562728 SANJONTAP 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 115.72 | 562728 SANJONTAP 115 562729 CAPROCKTAP1 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 115.72 | 562730 CAPROCKTAP2 69.0 562729 CAPROCKTAP1 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 115.72 | 562730 CAPROCKTAP2 69.0 562731 WHEATLAND 69.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.15 | 563171 G15082_2 34.5 563170 G15082_1 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 115.78 | P11:13.8:AEPW:COM1-1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 115.79 | P11:13.8:AEPW:COM2-1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 115.79 | P11:13.8:AEPW:COM3-1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 115.78 | P11:18:AEPW:WELSH1-1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 115.79 | P11:18:AEPW:WELSH3-1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 115.78 | P11:24:AEPW:PIRKEY 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 115.68 | P11:24:AEPW:SWS3-1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 115.74 | P11:24:AEPW:TURKCOAL
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.2104 | 116.11 | P12:138:AEPW-OMPA:DUNCAN-4:OMDUNCN4
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.02 | P12:138:AEPW:112GORE4:L.E.S.-4
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21029 | 116.05 | P12:138:AEPW:112GORE4:SNYDER-4
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21029 | 116.05 | 5841_Dup1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21037 | 115.37 | 584560 GEN-2015-014 115 584561 G15-014XFMR1 34.5 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21035 | 116.08 | P12:138:AEPW:SANTAFE:DUNCAN-4
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.08 | 587991 G16-121XFMR1 34.5 587990 GEN-2016-121 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.01 | 588480 A16-010_SUB 115 3WXFMR A16-010_SUB 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.2104 | 116.1 | P12:138:AEPW:DUNCAN-4:L.E.S.-4
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 115.46 | 588761 G17-033XFMR1 34.5 588760 GEN-2017-033 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 115.46 | 588765 G17-033XFMR2 34.5 588760 GEN-2017-033 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.02 | 588861 G17-047XFMR1 34.5 588860 GEN-2017-047 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21013 | 115.79 | P12:138:AEPW:ELKCTY-4:CLINTJC4
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.03 | 589381 G17-100XFMR1 34.5 589380 GEN-2017-100 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21028 | 116.07 | P12:138:AEPW:SHERID4:112GORE4
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.2103 | 116.06 | P12:345:AEPW-OKGE:CLARKSV7:MUSKOGE7
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21275 | 117.78 | P12:345:AEPW:L.E.S7:TERRYRD7
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21275 | 117.77 | P12:345:AEPW:L.E.S7:TERRYRD7
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21274 | 117.75 | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21349 | 118.25 | P12:345:AEPW-OKGE:L.E.S.-7:GRACMNT7
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21349 | 118.23 | P12:345:AEPW-OKGE:L.E.S.-7:GRACMNT7
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21333 | 118.8 | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.08 | P22:345:AMMO::LABADIE:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.08 | P22:345:AMMO::LABADIE:2
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.09 | P22:345:AMMO::LABADIE:3
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.08 | P22:345:AMMO::LABADIE:4
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.07 | P22:345:AMMO::RUSHISLAND:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21028 | 116.06 | P22:345:AMMO::RUSHISLAND:2
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21029 | 115.79 | P13:138-13.8:AEPW:COMANC-4_#2
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 115.8 | P13:138-13.8:AEPW:S.W.S.-4
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.20968 | 115.47 | P13:138-230:AEPW:ELKCTY-4
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21028 | 115.79 | P13:138-24:AEPW:PIRKEY 4
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21032 | 115.69 | P13:138-24:AEPW:S.W.S.-4
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21029 | 115.75 | P13:138-24:AEPW:TURK 4
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21044 | 116.11 | P13:138-345:AEPW:L.E.S.-4_#2
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21028 | 116.02 | P12:500:EES-EAI:KEO:WMPEHV
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21029 | 116.14 | P23:500:EES-EAI:KEO:B4941
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21028 | 116.02 | P23:500:EES-EAI:KEO:B4931
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21029 | 116.13 | P23:500:EES-EAI:KEO:B4921
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21028 | 116.07 | P23:500:EES-EAI:INDEP2:B6126
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21028 | 116.06 | P23:500:EES-EAI:PD:INDEP2:LN:FK479
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21029 | 115.79 | P13:345-18:AEPW:WELSH 7_#1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21029 | 115.79 | P13:345-18:AEPW:WELSH 7_#3
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 115.79 | P13:69-13.8:AEPW:COMANC-2
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.08 | P11:024:DPC:ALMA2:6
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.04 | P11:18:ITCM:EMERYGT1:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.05 | P11:18:ITCM:EMERYGT2:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.05 | P11:161:ITCM:MGS CT1:1C
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.05 | P11:161:ITCM:MGS CT2:2C
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21025 | 116.06 | 652537 WHITE 3 345 659286 DEERCREK-BE3 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21026 | 116.02 | 652568 GROTONSOUTH7 115 659275 GROTON_G-BE7 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21025 | 116.06 | 659286 DEERCREK-BE3 345 3WXFMR DEERCRK KU1A 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.05 | 672601 BD 4 230 672306 BD 6G 18.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.05 | 672610 POPLAR 4 230 672310 POPLAR 1G 18.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.05 | 672610 POPLAR 4 230 672311 POPLAR 2G 18.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.04 | 672621 SHAND 4 230 672321 SHAND 1G 18.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.03 | 672649 CODETTE 4 230 672650 NIPAWIN 4 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.04 | 672696 BRADA 4 230 672699 NBEC 4 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.12 | P23:345:MDU::COYOTE::5707-5712-5715::::
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.3 | P23:345:MEC:CBEC 905
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.25 | P23:345:MEC:CBEC 908
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21028 | 116.04 | P23:345:MEC:GDMEC 901
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21028 | 116.04 | P23:345:MEC:GDMEC 902
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.06 | P23:345:MEC:GDMEC 908
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.17 | P23:345:MEC:RAUN 0180
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.24 | P23:345:MEC:RAUN 0210
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.18 | P23:345:MEC:LOUISA 954
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21028 | 116.19 | P23:345:MEC:LOUISA 964
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.03 | P21:115:XEL:AUTO-SINGLE:CHEMOLT7:LSPOWER7:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.07 | P21:115:XEL:AUTO-SINGLE:COLVILL7:CANONFLSG7:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.03 | P21:115:XEL:AUTO-SINGLE:FARIBALTP7:FARIBALTGEN:Z
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.13 | P21:230:OTP:AUTO-SINGLE:SQBUTTE4:YNG24:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.12 | P23:345:OTP:CENTER 3:3215(1)
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.12 | P23:345:OTP:CENTER 3:3225(1)
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.06 | P12:230:UMZW:# 687 #: FT IN SD. FT-BG1 LINE FAULT
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.06 | P12:230:UMZW:# 3617 #: FT IN SD. FT-BG2 LINE FAULT
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 114.69 | 760494 GEN-2017-146 230 760498 G17-146-TAP 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 114.68 | 760495 G17-146-XFM1 34.5 760494 GEN-2017-146 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 115.46 | 761356 G17-239-XFMR 34.5 761355 GEN-2017-239 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 115.46 | 761359 G17-239-XFMR 34.5 761355 GEN-2017-239 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 115.63 | 761797 G17-187XFM1 34.5 761796 GEN-2017-187 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 115.63 | 761800 G17-187XFM2 34.5 761796 GEN-2017-187 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 110.67 | 762132 GEN-2017-158 230 763252 G18-099-XFM1 34.5 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 110.67 | 762132 GEN-2017-158 230 763255 G18-099-XFM2 34.5 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 111.27 | 762133 G17-158XFM1 34.5 762132 GEN-2017-158 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 111.27 | 762136 G17-158XFM2 34.5 762132 GEN-2017-158 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 113.54 | 762216 G17-151TAP 345 762217 GEN-2017-151 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21274 | 116.85 | 762216 G17-151TAP 345 762467 G18-015-TAP 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 115.27 | 762218 G17-151XFM1 34.5 762217 GEN-2017-151 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 115.27 | 762221 G17-151XFM2 34.5 762217 GEN-2017-151 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 115.27 | 762224 G17-151XFM3 34.5 762217 GEN-2017-151 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 115.27 | 762227 G17-151XFM4 34.5 762217 GEN-2017-151 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 114.55 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 115.11 | 762461 G18-015-XFM1 34.5 762460 GEN-2018-015 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 115.11 | 762464 G18-015-XFM2 34.5 762460 GEN-2018-015 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21163 | 116.42 | 762467 G18-015-TAP 345 763215 G18-092-TAP 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 113.8 | 763087 GEN-2018-073 345 763088 G18-073-XFM1 34.5 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 114.78 | 763087 GEN-2018-073 345 763091 G18-073-XFM2 34.5 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 110.64 | 763120 GEN-2018-081 230 763121 G18-081-XFM1 34.5 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 112.78 | 763120 GEN-2018-081 230 764011 G19-074-XFM1 34.5 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 112.92 | 763186 GEN-2018-089 230 763187 G18-089-XFM1 34.5 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 113.84 | 763208 GEN-2018-092 345 763215 G18-092-TAP 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 114.77 | 763208 GEN-2018-092 345 763220 G18-092-XFM1 34.5 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 114.77 | 763208 GEN-2018-092 345 763223 G18-092-XFM2 34.5 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 112.23 | 763241 GEN-2018-097 230 763242 G18-097-XFM1 34.5 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 113.15 | 763241 GEN-2018-097 230 763296 G18-111-XFM1 34.5 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 112.51 | 763241 GEN-2018-097 230 763307 G18-112-XFM1 34.5 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 112.51 | 763241 GEN-2018-097 230 763310 G18-112-XFM2 34.5 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 112.23 | 763241 GEN-2018-097 230 763395 G18-124-XFM1 34.5 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 112.23 | 763241 GEN-2018-097 230 763398 G18-124-XFM2 34.5 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 115.66 | 763318 GEN-2018-115 345 763319 G18-115-XFM1 34.5 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 112 | 763483 GEN-2019-003 230 763484 G19-003-XFM1 34.5 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 114.56 | 763483 GEN-2019-003 230 763605 G19-021-XFM1 34.5 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 115.46 | 763516 GEN-2019-011 345 763517 G19-011-XFM1 34.5 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 115.55 | 763879 GEN-2019-056 115 763880 G19-056XFM1 34.5 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.20993 | 116.19 | P42:345:OKGE:SB_BVTY7305
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21011 | 115.75 | P23:345:WERE:BUFF_345-534::
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21011 | 115.75 | P23:345:WERE:BUFF_345-543::
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21023 | 116.23 | P23:345:WERE:JEC_345-15::
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21022 | 116.18 | P23:345:WERE:JEC_345-16::
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21023 | 116.22 | P23:345:WERE:JEC_345-19::
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21023 | 116.22 | P23:345:WERE:JEC_345-20::
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.39 | P23:345:WERE:WOLF_345-50::
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.39 | P23:345:WERE:WOLF_345-60::
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21029 | 115.8 | P42:345:AEPW:WELSH CB 10620 NBTB+FAULT
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21028 | 115.79 | P41:345:AEPW:WELSH CB 10630 NBTB+FAULT
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 115.79 | P41:345:AEPW:WELSH CB 11670 NBTB+FAULT
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21039 | 115.78 | P41:345:AEPW:WELSH CB 11680 NBTB+FAULT
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 115.78 | P41:345:AEPW:WELSH CB 12540 NBTB+FAULT
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21333 | 117.33 | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21381 | 118.58 | P42:345:AEPW:LAWTON EASTSIDE CB 3413A NBTB+FAULT
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21416 | 118.94 | P42:345:AEPW:LAWTON EASTSIDE CB 3425A NBTB+FAULT
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21346 | 118.96 | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21275 | 117.77 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21275 | 117.77 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21275 | 117.74 | P42:345:AEPW:TERRYRD_CB_3421A_NBTB
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21026 | 116.18 | P23:345:KCPL:LACYGNE_R2-5::LACYGU2-LACYGNE-STILWELL
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21026 | 115.82 | P45:345:UMZW:# 1328 #: GI IN NE.
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21029 | 115.8 | P23:345:AEPW:WELSH CB 10620 NBTB
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21028 | 115.79 | P23:345:AEPW:WELSH CB 10630 NBTB
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 115.79 | P23:345:AEPW:WELSH CB 11670 NBTB
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21039 | 115.78 | P23:345:AEPW:WELSH CB 11680 NBTB
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 115.78 | P23:345:AEPW:WELSH CB 12540 NBTB
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21333 | 117.74 | P23:345:AEPW:OKLAUNION CB 3401A NBTB
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21381 | 118.58 | P23:345:AEPW:LAWTON EASTSIDE CB 3413A NBTB
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21416 | 118.94 | P23:345:AEPW:LAWTON EASTSIDE CB 3425A NBTB
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21346 | 118.96 | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21275 | 117.77 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21275 | 117.77 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21275 | 117.74 | P23:345:AEPW:TERRYRD_CB_3421A_NBTB
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.05 | P11:161:GMO:DOGWOOD_COMBINED_CYCLE_UNIT_OUTAGE
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.06 | P11:115:SUNC:GARDENCITY_S2:97:531459(2)
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21013 | 115.77 | P12:345:PWT:BUFF-THIS_345_1::
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21013 | 115.77 | P12:345:PWT:BUFF-THIS_345_2::
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21014 | 115.83 | P12:345:PWT:THIS-DGRS_345_1::FUTURE
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21014 | 115.83 | P12:345:PWT:THIS-DGRS_345_2::FUTURE
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21037 | 116.06 | P12:069:WFEC:ANADRKO_WATONGA
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21292 | 117.97 | P23:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21547 | 120.4 | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21292 | 117.97 | P42:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB+FAULT
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21547 | 120.4 | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.20561 | 114.13 | P42:345:OKGE:SB_BVTY7315_PRE19S
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.20996 | 115.62 | P23:345:SUNC:MO_BRK182
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.20996 | 115.62 | P23:345:SUNC:MO_BRK382
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.20992 | 115.79 | P23:345:SUNC:MO_BRK188
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21146 | 116.06 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21029 | 115.79 | P12:138-13.8:AEPW:COMANC-4_#1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.20968 | 115.47 | P12:230:AEPW:ELKCITY6:CHISHOLM6
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.2114 | 116.62 | P12:230:AEPW:SWEETWT6:CHISHOLM6
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997713 ABBXNL844501 230 1 |  | 553 | 0.34286 | 157.44 | 525531 TOLK 6 230 3WXFMR TOLK 6 2
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21029 | 116.18 | P23:345:KCPL-WERE:237LACYGNE_R1-6::LACYGU1-LACYGNE-NEOSHO
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21026 | 116.06 | P11:230:WERE:LECU5_GEN::
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.08 | P11:161:GMO:DOGWOOD_COMBINED_CYCLE_UNIT_OUTAGE_1_1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.02 | P11:20:KACY:NEARMAN N1::N1 OUT OF SERVICE:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21026 | 116.02 | P12:69:KACY:NMGEN-NMISOBUS::NEARMAN N1-NM ISOBUS OPEN:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21026 | 116.02 | P13:20-161:KACY:NEARMAN5-NMISOBUS:NAMEPLATE:NEARMAN N1 GSU:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21026 | 116.02 | P21:20:KACY:546702NMGENN1-546703NMISOBUSC1::::
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.23 | P11:115:SPS:HOBBS1&3:145MW::::
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21033 | 114.72 | P11:115:SPS:MUSTANG1&3:153MW::::
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21284 | 118.23 | P12:230:SPS:K37::1_TOLK_LAMB:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21048 | 116.06 | P12:230:SPS:K43::1_PRNGLE_HARR_E:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.2103 | 115.81 | P12:230:SPS:K44::1_EPLNT_HARRW:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21042 | 116.22 | P12:115:SPS:T04::1_TRBLNC_CASTRO:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21048 | 116.02 | P12:115:SPS:T06::1_SPRMN_PRNGLE:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.5 | P12:115:SPS:T21::1_GRSSLND_GRAHAM:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.05 | P12:115:SPS:T24B::1_RSWLL_BRSHRF:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21028 | 116.05 | P12:115:SPS:T26::1_CHAVES_RSWLCTY:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21149 | 116.45 | P12:115:SPS:T28A::1_LAMTON_PLANTX:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21073 | 116.02 | P12:115:SPS:T29::1_LAMTON_HALECTR:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21198 | 117.27 | P12:115:SPS:T30::1_LAMB_HOCKLY:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21198 | 116.37 | P12:115:SPS:T31::1_HOCKLY_SUNDWN:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21023 | 116.06 | P12:115:SPS:T35::1_TERRY_YOAKUM:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21028 | 116.78 | P12:115:SPS:T45::1_NORRIS_OASIS:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21026 | 115.82 | P12:115:SPS:T57::1_MUSTG_SEGRVS:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21154 | 116.03 | P12:115:SPS:T58::1_HERFRD_CARGIL:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21154 | 116.57 | P12:115:SPS:T59::1_CARGIL_CURRY:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.02 | P12:115:SPS:T64::1_RNDALL_PULLMN:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21124 | 116.38 | P12:115:SPS:T67::1_HAPPY_KRESS:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21032 | 115.77 | P12:115:SPS:T68::1_TUCO_FLOYD:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21028 | 115.81 | P12:115:SPS:T69::1_LUBBE_CROSBY:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.02 | P12:115:SPS:T70::1_COLTR_S_GORG:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21022 | 116.63 | P12:115:SPS:T71::1_CRLSLE_YUMA:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21036 | 116.1 | P12:115:SPS:T81::1_COX_FLOYD:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.26 | P12:115:SPS:T83::1_SP-FKFD_ALLEN:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21022 | 116.44 | P12:115:SPS:T89::1_DC_N_HIGG:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.07 | P12:115:SPS:T91::1_HIGG_RUSSELL:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21032 | 116.02 | P12:115:SPS:V01::1_MOOREW_RVRVIEW:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21049 | 116.07 | P12:115:SPS:V04::1_EPLANT_RNDALL:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21041 | 116.06 | P12:115:SPS:V07::1_COX_HALECTR:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21141 | 116.23 | P12:115:SPS:V09::1_HALECTR_PLANTX:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21026 | 116.21 | P12:115:SPS:V12::1_PLANTX_BAILEY:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.03 | P12:115:SPS:V15::1_TUCO_INDANA:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.20991 | 116.16 | P12:115:SPS:V24::1_WOLFTH_TERRY:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21045 | 116.07 | P12:115:SPS:V26::1_RSWLL_EDDY_N:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.4 | P12:115:SPS:V33::1_LUBBS_LYNN:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21132 | 117.14 | P12:115:SPS:V37::1_CASTRO_PLANTX:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21028 | 116.05 | P12:115:SPS:V44::1_COLTR_OWENS:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.16 | P12:115:SPS:V46::1_ALLEN_WHEELCK:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21029 | 116.5 | P12:115:SPS:V49::1_YOAKUM_SHLCO2:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.2107 | 116.68 | P12:115:SPS:V55::1_SUNDWN_TERRY:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.2104 | 116.59 | P12:115:SPS:V56::1_COCHRAN_SUNDWN:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.09 | P12:115:SPS:V62::1_CRLSLE_INDANA:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.2104 | 116.07 | P12:115:SPS:V78::2_CURRY_RSVLT:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21025 | 116.19 | P12:115:SPS:V81::1_LE-WAIT_LE-LVN:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21028 | 116.06 | P12:115:SPS:V95::1_DC_N_SHLCO2:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.02 | P12:115:SPS:W11::1_DC_S_SMINLE:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.03 | P12:115:SPS:W12::1_SMINLE_DOSS:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.1 | P12:115:SPS:W14::1_SMINLE_GAINES:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.03 | P12:115:SPS:W26::1_CUNGHM_OILCNTR:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.61 | P12:115:SPS:W32::1_PRMTR_FE-CLSIN:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21024 | 116.26 | P12:115:SPS:W35::1_GAINES_JNSDRW:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21219 | 116.59 | P12:115:SPS:W40::1_WCANYON_TRBLNC:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21055 | 116.11 | P12:115:SPS:W52::1_NEWHART_KRESS:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.67 | P12:115:SPS:W58::1_NORTON_LOPEZ:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.25 | P12:115:SPS:W59::1_LOPEZ_CMPBLL:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21028 | 116.55 | P12:115:SPS:W62::1_PLSTHL_CURRY:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.2104 | 116.07 | P12:115:SPS:W63::1_PLSTHL_CURRY:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.36 | P12:115:SPS:W64::1_PLSTHL_FE-CLV:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21029 | 116.57 | P12:115:SPS:W65::1_PLSTHL_CURRY:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.23 | P12:115:SPS:W66::1_PORTA_GREYHUND:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21024 | 116.02 | P12:115:SPS:W76::1_QUAHA_PCA:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21219 | 116.1 | P12:115:SPS:W77::1_RNDAL_WCANYON:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21028 | 116.07 | P12:115:SPS:W99::1_CAPITAN_CHAVES:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.05 | P12:115:SPS:U03::1_CARDNL_NEF:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21023 | 116.53 | P12:115:SPS:U14::1_DC_STH_INKBSN:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21025 | 116.47 | P12:115:SPS:V15::1_INKBSN_LE-WAT:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.2105 | 116.15 | P12:115:SPS:U16::1_BSHLND_OUTPST:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.2105 | 116.16 | P12:115:SPS:U17::1_COLTR_OUTPST:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21034 | 116.26 | P12:115:SPS:U19::1_DEAN_PLAINS:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.2105 | 116.07 | P12:115:SPS:U23::1_COLTR_HILSDE:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.20186 | 124.36 | P42:345:SPS:YOAKUM:J18####:SLG1:EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.20186 | 124.36 | P43:345:SPS:YOAKUM:TF#####:SLG:EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.20186 | 124.36 | P42:345:SPS:YOAKUM:J17####:SLG:EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.20186 | 124.36 | P42:345:SPS:YOAKUM:J18####:SLG2:EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21026 | 116.06 | P11:18:HAST:::EGYCTR2G WEC2_LOSS OF WEC 2 GEN_:HV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21026 | 116.06 | P13:18-115:HAST:::EGYCNTR7 XFMR G2WEC 2 GSU_:HV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.08 | P11:161:GMO:DOGWOOD-COMBINED-CYCLE-UNIT-OUTA:::HV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21029 | 116.18 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21026 | 116.18 | P23:345:KCPL:LACYGNE-R2-5:::EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21023 | 116.23 | P11:230:WERE:JECU1-GEN:::HV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21026 | 116.06 | P11:230:WERE:LECU5-GEN:::HV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21023 | 116.23 | P11:345:WERE:JECU2-GEN:::EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21023 | 116.22 | P11:345:WERE:JECU3-GEN:::EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.4 | P11:345:WERE:WOLFU1-GEN:::EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21013 | 115.77 | P12:345:PWT:BUFF-THIS-345-1:::EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21013 | 115.77 | P12:345:PWT:BUFF-THIS-345-2:::EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21011 | 115.75 | P23:345:WERE:BUFF-345-534:::EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21011 | 115.75 | P23:345:WERE:BUFF-345-543:::EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21023 | 116.23 | P23:345:WERE:JEC-345-15:::EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21022 | 116.18 | P23:345:WERE:JEC-345-16:::EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21023 | 116.22 | P23:345:WERE:JEC-345-19:::EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21023 | 116.22 | P23:345:WERE:JEC-345-20:::EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.39 | P23:345:WERE:WOLF-345-50:::EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.39 | P23:345:WERE:WOLF-345-60:::EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.34 | P11:022:NPPD:COOPER1G:1:983:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21022 | 116.33 | P11:023:NPPD:GENTLM1G:1:757:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21022 | 116.35 | P11:024:NPPD:GENTLM2G:2:757:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21026 | 116.01 | P11:161:OPPD:N OMA 5G:LT::HV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21026 | 116.01 | P11:161:OPPD:N OMA 5G:::HV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21023 | 116.2 | P13:345:OPPD:NEBCTY1G:::EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21022 | 116.22 | P13:345:OPPD:NEBCTY2G:::EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21026 | 116.01 | P13:161:OPPD:N OMA 5G:::HV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.22 | P22:345:OPPD:S3458 NEBCTY1G:LT::EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21023 | 116.2 | P22:345:OPPD:S3458 NEBCTY1G:::EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.25 | P22:345:OPPD:S3458 NEBCTY2G:LT::EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21022 | 116.22 | P22:345:OPPD:S3458 NEBCTY2G:::EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.22 | P23:345:OPPD:S3458 NEBCTY1G:LT::EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21023 | 116.2 | P23:345:OPPD:S3458 NEBCTY1G:::EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.25 | P23:345:OPPD:S3458 NEBCTY2G:LT::EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21022 | 116.22 | P23:345:OPPD:S3458 NEBCTY2G:::EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 115.8 | P12:115:SUNC:PLYMELL-PIERCEVILLE:::HV::
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21025 | 116.06 | P11:018:UMZB:# 5 #:: DCS IN SD. DEERCREEK_MV::
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21026 | 116.03 | P11:022:UMZB:# 15 #:: LO IN ND. LELAND OLDS 1_MV::
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21025 | 116.07 | P11:020:UMZB:# 16 #:: LO IN ND. LELAND OLDS 2_MV::
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21025 | 116.14 | P11:023:UMZB:# 31 #:: AVS IN ND. ANTELOPE VALLEY 1_MV::
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21025 | 116.14 | P11:023:UMZB:# 32 #:: AVS IN ND. ANTELOPE VALLEY 2_MV::
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21021 | 116.33 | P11:024:UMZB:# 33 #:: LRS IN WY. LARAMIE RIVER STATION 1_MV::
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.06 | P12:230:UMZW:# 687 #:: FT IN SD. FT-BG1 BRANCH FAULT:HV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.06 | P12:230:UMZW:# 3617 #:: FT IN SD. FT-BG2 BRANCH FAULT:HV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.06 | P12:230:UMZW:# 4038 #:: BG-FT IN SD. FAULT FOR TRANSMISSION CIRCUIT (BG-FT).:HV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.06 | P12:230:UMZW:# 4039 #:: BG-FT IN SD. FAULT FOR TRANSMISSION CIRCUIT (BG-FT).:HV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.03 | P13:230:UMZW:# 5135 #:: OA IN SD. FAULT ON TRANSFORMER (2).:HV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.03 | P13:230:UMZW:# 5136 #:: OA IN SD. FAULT ON TRANSFORMER (3).:HV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21026 | 115.82 | P23:345:UMZW:# 2423 #:: GI IN NE. GI 1596 BKR FAULT:EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21026 | 115.82 | P23:345:UMZW:# 2426 #:: GI IN NE. GI 1592 BKR FAULT:EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21026 | 115.82 | P23:345:UMZW:# 2432 #:: GI IN NE. GI 1092 BKR FAULT:EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21026 | 115.82 | P23:345:UMZW:# 2440 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1092 STUCK BKR:EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21026 | 115.82 | P23:345:UMZW:# 2444 #:: GI IN NE. GI-SWEET BRANCH FAULT & GI 1596 STUCK BKR:EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21026 | 115.82 | P23:345:UMZW:# 2446 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1196 STUCK BKR:EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21026 | 115.82 | P42:345:UMZW:# 2413 #:: FT2 IN SD. FT2-LO2 BRANCH FAULT & FT2 2992 STUCK BKR:EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21026 | 115.82 | P42:345:UMZW:# 2415 #:: FT2 IN SD. FT2-GI BRANCH FAULT & FT2 3392 STUCK BKR:EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21031 | 115.74 | P11:138:WFEC:HUGO1:465MW :::
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21026 | 116.02 | P11:138:WFEC:MORLND2:132MW:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21026 | 116.03 | P11:138:WFEC:MORLND3:149MW :::
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21036 | 116.06 | P12:138:WFEC:ANADRKO_CLVLND::::
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.2103 | 116.06 | P12:345:OKGE-AEPW:BKRBKR12::::
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21064 | 116.18 | P12:345:OKGE:BKRBKR21::::
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21083 | 116.26 | P12:345:OKGE:BKRBKR24::::
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21274 | 117.75 | P12:345:OKGE-AEPW:BKRBKR25::::
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.20996 | 115.72 | P12:345:OKGE:BKRBKR336::::
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.20996 | 115.72 | P12:345:OKGE:BKRBKR336_2::::
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21349 | 118.25 | P12:345:OKGE-AEPW:BKRBKR366::::
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21349 | 118.23 | P12:345:OKGE-AEPW:BKRBKR366::::
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21236 | 117.15 | P12:345:OKGE:BKRBKR367::::
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21001 | 115.72 | P12:345:OKGE:BKRBKR4193::::
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21001 | 115.72 | P12:345:OKGE:BKRBKR4194::::
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.02 | P12:345:OKGE:BKRBKR4195::::
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.2099 | 115.76 | P12:345:OKGE-SPS:BKRBKR4201::::
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.2099 | 115.76 | P12:345:OKGE-SPS:BKRBKR4202::::
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21037 | 116.03 | P12:345:OKGE:BKRBKR421::::
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.20994 | 115.6 | P12:345:OKGE:BKRBKR443NEW::::
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.20993 | 115.6 | P12:345:OKGE:BKRBKR443NEW2::::
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21011 | 115.79 | P12:345:OKGE-ITC:BKRBKR502::::
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21011 | 115.79 | P12:345:OKGE-ITC:BKRBKR503::::
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21014 | 115.83 | P12:345:OKGE-ITC:BKRBKR502_1::::
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21014 | 115.83 | P12:345:OKGE-ITC:BKRBKR503_1::::
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21021 | 116.33 | P12:345:OKGE:BKRBKR604::::
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.2102 | 116.37 | P12:345:OKGE:BKRBKR604_2::::
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21029 | 115.82 | P11:345:OKGE:BKRBKR_GSU07::::
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21029 | 115.81 | P11:345:OKGE:BKRBKR_GSU08::::
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21029 | 115.8 | P11:138:OKGE:BKRBKR_GSU21::::
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21025 | 115.83 | P12:138:OKGE:BKRBKR85_MOS1::::
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.20994 | 116.13 | P42:345:OKGE:SB_ARIA7381::::
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21722 | 120.17 | P42:345:OKGE:SB_BVTY7387::::
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21038 | 116.02 | P41:345:OKGE:SB_REUD7381::::
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21037 | 116.03 | P41:345:OKGE:SB_REUD7383::::
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21037 | 116.06 | P41:345:OKGE:SB_REUD7385::::
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.2104 | 116.06 | P42:345:OKGE:SB_REUD7389::::
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21025 | 116.05 | P11:115:SUNC:GARDENCITY_S2:103:531459(2):HV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21025 | 116.07 | P11:115:SUNC:FORTDDODGE_4:157:539670(4):HV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.04 | P11:345:599:CIMARRON1WIND:200:531603(1):EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.47 | P13:115:SUNC:HOLCOMB_GSU:::HV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21025 | 116.05 | P13:115:SUNC:S2_GSU:::HV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21025 | 116.07 | P13:115:SUNC:FORTDODGE_GSU:::HV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21025 | 116.04 | P23:345:SUNC:BU_BRK682:::EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.14 | 300003 1THLG3 24.0 301503 7THOMHLGSU3 345 3
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.01 | 300007 1NM G2 22.0 301537 7NEWMADGSU2 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.01 | 300046 7NEWMAD 345 301537 7NEWMADGSU2 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.14 | 300049 7THOMHL 345 301503 7THOMHLGSU3 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.08 | P11:20:AMMO:1LAB�� G1:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.08 | P11:20:AMMO:1LAB�� G2:2
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.27 | P11:345:AMMO::CALLAWAY:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.08 | P11:345:AMMO::LABADIE:3
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.08 | P11:345:AMMO::LABADIE:4
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.07 | P11:345:AMMO::RUSHISLAND:U1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.07 | P11:345:AMMO::RUSHISLAND:U2
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.06 | P11:138:AMMO::SIOUX:2
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 115.83 | P11:24:CLEC::G1DOLHIL:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.06 | P12:765:AEP:AEP ROCKP-AEP JEFF 765
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 115.78 | P11:HV:EES::PIRKEY 1:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 115.79 | P11:EHV:EES::WELSH3-1:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 115.74 | P11:HV:EES::TURKCOAL:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.25 | P12:EHV:EES::7CALAWY 1:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21028 | 116.02 | 338056 CHALKBLUFFPV 500 338162 8W.MEMPHIS% 500 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21029 | 115.75 | P12:HV:EES::TURK 4%:1(1)
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21029 | 115.79 | P12:EHV:EES::WELSH 7:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21029 | 115.79 | P12:EHV:EES::WELSH 7:1(1)
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21028 | 115.79 | P12:HV:EES::PIRKEY 4:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.2103 | 116.06 | P12:EHV:EES::CLARKSV7!:MUSKOGE7!:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.06 | 344011 7HUGHES 345 344012 7HPW-N 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.08 | 344884 7LABADIE1 345 344894 1LAB G1 20.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.08 | 344885 7LABADIE2 345 344895 1LAB G2 20.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.08 | 344886 7LABADIE3 345 344896 1LAB G3 20.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.08 | 344887 7LABADIE4 345 344897 1LAB G4 20.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.07 | 345667 7RUSH 1 345 345670 1RUSH G1 18.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.06 | 345668 7RUSH 2 345 345671 1RUSH G2 18.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.05 | 345755 4SIOUX 1 138 345756 1SIOUX 1 18.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.05 | 345764 4SIOUX 2 138 345765 1SIOUX 2 18.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.12 | P12:345:MDU::CENTER:COYOTE:1::::
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.12 | P13:345:MDU:COYOTE GSU LOSS:COYOTE::1::::
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.03 | P11:345:MEC:GDMEC CT1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.03 | P11:345:MEC:GDMEC CT2
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.14 | P11:345:MEC:GDMEC ST
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.35 | P11:345:MEC-NPPD:COOPER 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.24 | P11:24:XEL:AUTO-SINGLE:SHERC31G:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.24 | P11:24:XEL:AUTO-SINGLE:SHERC32G:2
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.33 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.16 | P11:20:XEL:AUTO-SINGLE:PRIS31G:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.16 | P11:20:XEL:AUTO-SINGLE:PRIS32G:2
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.2 | P11:22:XEL:AUTO-SINGLE:MNTCE31G:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.16 | P11:20:XEL:AUTO-SINGLE:KING31G:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.02 | P11:13:XEL:AUTO-SINGLE:HBRS73G:9
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.02 | P11:18:XEL:AUTO-SINGLE:BLKD76G:6
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.22 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.22 | P11:22:GRE:AUTO-SINGLE:GRE-COAL42G:2
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.14 | P11:24:OTP:AUTO-SINGLE:BIGSTN1G:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.15 | P11:20:OTP:AUTO-SINGLE:CENTER2G:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.05 | P11:22:OTP:AUTO-SINGLE:CENTER1G:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.13 | P11:24:OTP:AUTO-SINGLE:COYOTE1G:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.05 | P11:24:DPC:AUTO-SINGLE:GENOA53G:3
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.03 | P12:115:XEL:AUTO-SINGLE:CHEMOLT7:LSPOWER7:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.07 | P12:115:XEL:AUTO-SINGLE:COLVILL7:CANONFLSG7:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.03 | P12:115:XEL:AUTO-SINGLE:FARIBALTP7:FARIBALTGEN:Z
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.13 | P12:230:OTP:AUTO-SINGLE:SQBUTTE4:YNG24:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.22 | P13:24-345:XEL:AUTO-SINGLE:SHERC31G:SHERCO3:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.22 | P13:24-345:XEL:AUTO-SINGLE:SHERC32G:SHERCO3:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.3 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.16 | P13:20-345:XEL:AUTO-SINGLE:PRIS31G:PRISLD3:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.16 | P13:20-345:XEL:AUTO-SINGLE:PRIS32G:PRISLD3:2
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.2 | P13:22-345:XEL:AUTO-SINGLE:MNTCE31G:MNTCELO3:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.15 | P13:20-345:XEL:AUTO-SINGLE:KING31G:ASKING3:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.02 | P13:13-115:XEL:AUTO-SINGLE:HBRS73G:HIBRDGE7:9
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.2 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL41G:GRE-COALCR4:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.2 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL42G:GRE-COALCR4:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.13 | P13:230-24:OTP:AUTO-SINGLE:BIGSTON4:BIGSTN1G:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.13 | P13:20-230:OTP:AUTO-SINGLE:CENTER2G:YNG24:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.04 | P13:22-230:OTP:AUTO-SINGLE:CENTER1G:CENTER4:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.12 | P13:24-345:OTP:AUTO-SINGLE:COYOTE1G:COYOTE3:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.05 | P13:24-161:DPC:AUTO-SINGLE:GENOA53G:GENOA5:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.07 | P13:24-161:DPC:AUTO-SINGLE:JPM:ALMA5:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21028 | 116.02 | 38203 J1819 POI 500 337957 8KEO% 500 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21028 | 116.02 | 38203 J1819 POI 500 338056 CHALKBLUFFPV 500 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.13 | P11:115:XEL:RIV COMBINE CYCLE
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.04 | P12:115:XEL:BDS #2 5
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.04 | P11:115:XEL:HBR #6
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.04 | P11:115:XEL:HBR #7
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.16 | P11:115:XEL:HBR #6 7 8
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.16 | P23:345:XEL:8H14 PRI
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.16 | P23:345:XEL:8H17 PRI AS
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.3 | P23:345:XEL:8N28 SHC
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.22 | P23:345:XEL:8N22 SHC
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.22 | P23:345:XEL:8N17 SHC
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.21 | P23:345:XEL:8N8 MNN
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.15 | P23:345:XEL:8P1 KING
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.15 | P23:345:XEL:8P2 KING
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.04 | P23:115:XEL:5P147 IVH AS
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.03 | P11:18:ALTW:AUTO-SINGLE:EMERYST1:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.03 | P11:22:ALTW:AUTO-SINGLE:LANS54G:4
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.17 | P11:22:ALTW:AUTO-SINGLE:ARNOLD1G:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.2 | P11:24:ALTW:AUTO-SINGLE:OTTUMW1G:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.03 | P13:18-161:ALTW:AUTO-SINGLE:EMERYST1:EMERY5:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.03 | P13:22-161:ALTW:AUTO-SINGLE:LANS54G:LANSINGL15:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.16 | P13:22-161:ALTW:AUTO-SINGLE:ARNOLD1G:ARNOLD5:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.19 | P13:24-161:ALTW:AUTO-SINGLE:OTTUMW1G:OTTUMWA5:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.27 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.34 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.19 | P11:22:MEC:AUTO-SINGLE:NEAL3G:3
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.26 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.19 | P11:24:MEC:AUTO-SINGLE:LOUIS31G:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.25 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.3 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.17 | P13:345-22:MEC:AUTO-SINGLE:RAUN3:NEAL3G:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.24 | P13:345-24:MEC:AUTO-SINGLE:RAUN3:NEAL4G:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.18 | P13:345-24:MEC:AUTO-SINGLE:LOUISA3:LOUIS31G:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21023 | 116.23 | P11:230:WERE:JECU1_GEN::
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21023 | 116.23 | P11:345:WERE:JECU2_GEN::
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21023 | 116.22 | P11:345:WERE:JECU3_GEN::
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.4 | P11:345:WERE:WOLFU1_GEN::
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21029 | 116.03 | 511435 SNYDER-4 138 588779 TAP_G17-036 138 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21035 | 116.03 | 511453 DUNCAN-4 138 511552 DUNCHERTP4 138 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21035 | 116.03 | 511455 D.E.S.-4 138 511552 DUNCHERTP4 138 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21035 | 116.02 | 511455 D.E.S.-4 138 529344 OMDUNE-4 138 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 114.98 | 511456 O.K.U.-7 345 588760 GEN-2017-033 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21333 | 117.74 | 511456 O.K.U.-7 345 763215 G18-092-TAP 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21347 | 118.31 | 511468 L.E.S.-7 345 762467 G18-015-TAP 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21244 | 117.72 | 511468 L.E.S.-7 345 763215 G18-092-TAP 345 2
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 115.66 | 511468 L.E.S.-7 345 763318 GEN-2018-115 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21029 | 116.05 | 511488 112GORE4 138 511510 LAIRGST4 138 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.2104 | 116.11 | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21029 | 116.04 | 511500 CACHE4 138 511510 LAIRGST4 138 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21029 | 116.03 | 511500 CACHE4 138 588779 TAP_G17-036 138 2
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21146 | 116.06 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.20361 | 113.09 | 511553 CHISHOLM7 345 523961 POTTER_CO 7 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.20361 | 113.09 | 511553 CHISHOLM7 345 523961 POTTER_CO 7 345 2
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.20733 | 115.5 | 511553 CHISHOLM7 345 755000 WWDBORDT 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.14 | 511557 CHISHOLM6 230 3WXFMR CHISHOLM6 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21041 | 116.02 | 514801 MINCO 7 345 555234 NSUB345 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.20953 | 115.63 | 515375 WWRDEHV7 345 755000 WWDBORDT 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21722 | 120.2 | 515458 BORDER 7 345 560022 CRAWFISH_DR 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21722 | 120.15 | 515458 BORDER 7 345 755000 WWDBORDT 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21037 | 116.02 | 515543 RENFROW7 345 763421 G18-128-TAP 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21024 | 116.12 | 515618 BALKOW 7 345 3WXFMR BALKOW 7 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21024 | 116.13 | 515618 BALKOW 7 345 3WXFMR BALKOW 7 1_Dup1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21033 | 116.04 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.2102 | 116.39 | 515634 PALDR1W7 345 3WXFMR PALO2 _1 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.13 | 515677 BADGER 7 345 563170 G15082_1 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21023 | 116.01 | 521017 ONEY 4 138 521089 WASHITA4 138 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.02 | 522800 MU-TULIA 3 115 525179 TULIA_TP 3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.16 | 522892 MU-BROWNFLD2 69.0 526761 BROWNFLD_TP2 69.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.03 | 523090 TEXAS_CNTY 3 115 589380 GEN-2017-100 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21023 | 116.16 | 523093 HITCHLAND 3 115 523174 GOODWELLWND3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.34 | 523097 HITCHLAND 7 345 523112 NOVUS1 7 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.4 | 523097 HITCHLAND 7 345 523215 FREWHELCOL17 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.20824 | 114.83 | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.45 | 523097 HITCHLAND 7 345 560252 G10-14 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.01 | 523099 TC-DRYTRLS 3 115 588480 A16-010_SUB 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.23 | 523112 NOVUS1 7 345 3WXFMR NOVUS XF2 2
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.04 | 523112 NOVUS1 7 345 3WXFMR XIANA2011198 _1 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21026 | 116.02 | 523118 BUFF_DUNES 7 345 523853 FINNEY 7 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.02 | 523120 COLE 3 115 588860 GEN-2017-047 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21025 | 116.04 | 523172 GWELL_COLL11 34.5 523174 GOODWELLWND3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21025 | 116.04 | 523173 GWELL_COLL21 34.5 523174 GOODWELLWND3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21036 | 116.01 | 523221 XIT_INTG 6 230 3WXFMR SIEM_T126401 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21048 | 116.07 | 523267 PRINGLE 6 230 3WXFMR ENRCO13617-1 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21048 | 116.06 | 523267 PRINGLE 6 230 523979 HARRNG_EST 6 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.2109 | 116.2 | 523309 MOORE_CNTY 6 230 523323 MCDWL_CREEK6 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21062 | 116.12 | 523323 MCDWL_CREEK6 230 523959 POTTER_CO 6 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.20997 | 116.45 | 523959 POTTER_CO 6 230 524010 ROLLHILLS 6 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21843 | 117.19 | 523959 POTTER_CO 6 230 524267 BUSHLAND 6 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.2181 | 118.35 | 523959 POTTER_CO 6 230 525461 NEWHART 6 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.2139 | 121.11 | 523961 POTTER_CO 7 345 3WXFMR WAUK 90343-A 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21025 | 115.74 | 523978 HARRNG_MID 6 230 523979 HARRNG_EST 6 230 @1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.2105 | 116.16 | 524267 BUSHLAND 6 230 3WXFMR WH 7001795 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.22491 | 117.94 | 524267 BUSHLAND 6 230 524623 DEAFSMITH 6 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21015 | 116.44 | 524296 SPNSPUR_WND7 345 524299 SPNSPUR_COL7 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21015 | 116.44 | 524299 SPNSPUR_COL7 345 3WXFMR SPNSPUR_COL7 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21416 | 117.09 | 524415 AMA_SOUTH 6 230 525213 SWISHER 6 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.67 | 524502 NORTON 3 115 524509 FE-TUCMCARI3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21219 | 116.45 | 524575 DS-#25+ 3 115 524597 PANDAHFD 3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21219 | 116.55 | 524575 DS-#25+ 3 115 524630 TIERABLANCA3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.11 | 524604 HEREFRD_SB 2 69.0 524608 HERFRD_STH 2 69.0 *1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.2234 | 122.73 | 524623 DEAFSMITH 6 230 760498 G17-146-TAP 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.52 | 524721 DS-#15&#19+2 69.0 524745 CASTRO_CNTY2 69.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21033 | 116.03 | 524770 PLSNT_HILL 6 230 3WXFMR EFAE1100068A 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.2145 | 121.59 | 524875 OASIS 6 230 524885 SN_JUAN_TAP6 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21101 | 117.16 | 524875 OASIS 6 230 524909 ROOSEVELT 6 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21441 | 121.97 | 524885 SN_JUAN_TAP6 230 527483 CHAVES_CNTY6 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21044 | 116.22 | 524909 ROOSEVELT 6 230 3WXFMR ABB LMM60042 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21721 | 122.19 | 524909 ROOSEVELT 6 230 525531 TOLK 6 230 2
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.77 | 524923 PORTALES 2 69.0 524929 RO-PORT_MTR2 69.0 @1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.42 | 524923 PORTALES 2 69.0 524941 PORTALES#1 2 69.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.66 | 525023 BC-BAIL_MTR2 69.0 525027 BAILEYCO 2 69.0 @1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21132 | 116.55 | 525056 BC-EARTH 3 115 525480 PLANT_X 3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.51 | 525191 KRESS_INT 2 69.0 525203 SW-KRESS 2 69.0 Z1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.6 | 525192 KRESS_INT 3 115 3WXFMR ENRCO 136155 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21328 | 116.83 | 525213 SWISHER 6 230 525461 NEWHART 6 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.15 | 525272 KISER 3 115 3WXFMR VON 13819/1 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.61 | 525326 COX 3 115 3WXFMR ELCO 13474-3 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.61 | 525414 LAMTON 3 115 3WXFMR ASEA MLL9204 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.22646 | 119.68 | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21301 | 118.1 | 525481 PLANT_X 6 230 3WXFMR WH ALM20171 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21975 | 121 | 525481 PLANT_X 6 230 526435 SUNDOWN 6 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.2234 | 121.02 | 525481 PLANT_X 6 230 760498 G17-146-TAP 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21374 | 116.49 | 525481 PLANT_X 6 230 762174 G17-218TAP 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21416 | 116.56 | 525481 PLANT_X 6 230 762174 G17-218TAP 230 2
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.22176 | 121.7 | 525531 TOLK 6 230 525586 NEEDMORE 6 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21284 | 118.23 | 525531 TOLK 6 230 525637 LAMB_CNTY 6 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.23952 | 120.42 | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.2154 | 116.76 | 525531 TOLK 6 230 762174 G17-218TAP 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21576 | 116.82 | 525531 TOLK 6 230 762174 G17-218TAP 230 2
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.34286 | 155.48 | 525549 TOLK 7 345 3WXFMR ABBXNL844501 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.22176 | 121.69 | 525586 NEEDMORE 6 230 526935 YOAKUM 6 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.41 | 525599 LC-SANDHLL+2 69.0 525606 AMHERST 2 69.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.45 | 525606 AMHERST 2 69.0 525613 W_LITTLFLD 2 69.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.46 | 525613 W_LITTLFLD 2 69.0 525635 LAMB_CNTY 2 69.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.42 | 525635 LAMB_CNTY 2 69.0 525650 LC-LTTLFLD+2 69.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21284 | 118.23 | 525637 LAMB_CNTY 6 230 3WXFMR WH ALM20172 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.41 | 525779 FLOYD_CNTY 2 69.0 525790 FLOYDADA_TP2 69.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.29 | 525828 TUCO_INT 3 115 3WXFMR DS F78800913 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.20276 | 118.38 | 525832 TUCO_INT 7 345 526936 YOAKUM_345 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.49 | 526086 SW_6786_N 2 69.0 526087 SW_6786_S 2 69.0 Z1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.49 | 526086 SW_6786_N 2 69.0 526102 SP-HETTLER 2 69.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.56 | 526087 SW_6786_S 2 69.0 526284 PLANTERS 2 69.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.1 | 526160 CARLISLE 3 115 3WXFMR WH RLP38371 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.44 | 526195 QUINCY 3 115 526196 SP-MILWAUKEE 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.34 | 526268 LUBBCK_STH 3 115 3WXFMR NA 70454A 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.6 | 526284 PLANTERS 2 69.0 526297 LUBBCK_EST 2 69.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.2104 | 116.47 | 526424 PACIFIC 3 115 526434 SUNDOWN 3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21023 | 116.06 | 526435 SUNDOWN 6 230 3WXFMR UPDATE LATER _12 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21049 | 118.87 | 526435 SUNDOWN 6 230 526460 AMOCO_SS 6 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21049 | 116.5 | 526460 AMOCO_SS 6 230 526935 YOAKUM 6 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21025 | 116.08 | 526525 WOLFFORTH 6 230 3WXFMR UPDATE LATER _13 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.48 | 526735 TERRY_CNTY 2 69.0 526747 LG-BROWNFLD2 69.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21015 | 118.02 | 526935 YOAKUM 6 230 527028 INK_BASIN 6 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.2145 | 116.3 | 526936 YOAKUM_345 345 3WXFMR SPX WT04221 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.20267 | 126.57 | 526936 YOAKUM_345 345 527896 HOBBS_INT 7 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21004 | 117.39 | 527028 INK_BASIN 6 230 527894 HOBBS_INT 6 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21022 | 116.43 | 527130 DENVER_N 3 115 527286 HIGGEAST 3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21028 | 116.02 | 527149 MUSTANG 6 230 3WXFMR ENRCO 136161 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21043 | 114.01 | 527149 MUSTANG 6 230 527151 GS-MUSTANG 6 230 @1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.29 | 527202 SEAGRAVES 3 115 3WXFMR ABB MLL92408 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.17 | 527212 DIAMONDBACK3 115 3WXFMR HOW 36773714 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21022 | 116.41 | 527286 HIGGEAST 3 115 527363 HIGG 3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21024 | 116.16 | 527325 OXY_WSEM_TP3 115 527362 JOHNSON_DRW3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.15 | 527340 DOSS 3 115 3WXFMR ELCO 13566/1 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.14 | 527345 LEGACY 2 69.0 527350 XTO_ROBRTSN2 69.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.14 | 527346 LEGACY 3 115 3WXFMR VROL 13735-1 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.12 | 527350 XTO_ROBRTSN2 69.0 527355 BOARDMAN 2 69.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.05 | 527355 BOARDMAN 2 69.0 527365 FLANNAGAN 2 69.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.02 | 527360 MAPCO 3 115 527362 JOHNSON_DRW3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.08 | 527362 JOHNSON_DRW3 115 528775 LE-ERF 3 115 @1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.01 | 527370 TENNECO_TAP2 69.0 527371 TENNECO 2 69.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21205 | 116.35 | 527483 CHAVES_CNTY6 230 527799 EDDY_NORTH 6 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.05 | 527508 PRICE 3 115 527509 PRICE_TAP 3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.02 | 527514 CV-PINE 2 69.0 527563 ROSWLL_INT 2 69.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.05 | 527529 RIACBRSH_TP3 115 527533 SW4J795_E 3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.02 | 527529 RIACBRSH_TP3 115 527536 BRASHER 3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.05 | 527533 SW4J795_E 3 115 527564 ROSWLL_INT 3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.06 | 527563 ROSWLL_INT 2 69.0 527575 SW_4702 2 69.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21045 | 116.1 | 527564 ROSWLL_INT 3 115 527597 TWEEDY 3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.06 | 527575 SW_4702 2 69.0 527589 CV-ORCHARD 2 69.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.02 | 527589 CV-ORCHARD 2 69.0 527619 DEXTER_TP 2 69.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21023 | 116.18 | 527653 MILO_WIND 1 34.5 527655 RSVLT_CC_E 7 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21015 | 116.1 | 527654 RSVLT_CC_W 7 345 527655 RSVLT_CC_E 7 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21015 | 116.36 | 527654 RSVLT_CC_W 7 345 527666 RSVLT_COL1 7 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21011 | 116.3 | 527655 RSVLT_CC_E 7 345 527656 CROSSROADS 7 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21015 | 116.36 | 527666 RSVLT_COL1 7 345 3WXFMR RSVLT_COL1 7 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.15 | 527790 EDDY_SVC 1 8.50 527799 EDDY_NORTH 6 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.05 | 527864 CUNNINHAM 3 115 528568 MONUMNT_TP 3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21013 | 116.16 | 527865 CUNNIGHM_N 6 230 527867 CUNNIGHM_S 6 230 *1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.14 | 527865 CUNNIGHM_N 6 230 527883 CUNINGHAM3 1 13.8 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21023 | 116.08 | 527865 CUNNIGHM_N 6 230 527963 POTASH_JCT 6 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21023 | 116.02 | 527867 CUNNIGHM_S 6 230 527894 HOBBS_INT 6 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21025 | 116.35 | 527894 HOBBS_INT 6 230 527903 HOBBS_PLT3 1 18.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.2102 | 116.23 | 527896 HOBBS_INT 7 345 3WXFMR HICO 68759-1 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 115.8 | 527965 KIOWA 7 345 528027 RDRUNNER 7 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21028 | 115.81 | 528015 PHANTOM 7 345 528027 RDRUNNER 7 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.11 | 528024 RR_SVC_HV 3 115 528021 RDRUNNR_SVC1 15.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.25 | 528024 RR_SVC_HV 3 115 528025 RDRUNNER 3 115 Z1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 115.81 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.08 | 528025 RDRUNNER 3 115 587990 GEN-2016-121 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.14 | 528222 CHINA_DRAW 3 115 528225 CD_SVC_HV 3 115 Z1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 115.82 | 528341 LE-SANANDRS3 115 528627 LE-TXACO_TP3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21024 | 116.06 | 528394 QUAHADA 3 115 528396 XTO_BIGEDDY3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.01 | 528552 OIL_CENTER 3 115 528554 COOPER_RNCH3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.02 | 528554 COOPER_RNCH3 115 528581 BYRD_TP 3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.05 | 528568 MONUMNT_TP 3 115 528581 BYRD_TP 3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.04 | 528596 CARDINAL 3 115 528605 TARGA 3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.06 | 528603 NA_ENRICH 3 115 528605 TARGA 3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.11 | 528617 LE-WAITS 2 69.0 528325 LE-WAITS 3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.03 | 528617 LE-WAITS 2 69.0 528714 LE-FORT_SW 2 69.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21028 | 116.05 | 528618 LE-LOVINTON2 69.0 528334 LE-NRTH_INT3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.42 | 528626 LE-PLNSINT 2 69.0 526928 PLAINS_INT 3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.42 | 528626 LE-PLNSINT 2 69.0 528709 LE-PLNSGOAB2 69.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.05 | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.11 | 528669 LE-STKLDRTP2 69.0 528740 LE-PLANS_SW2 69.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.3 | 528709 LE-PLNSGOAB2 69.0 528740 LE-PLANS_SW2 69.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.05 | 528709 LE-PLNSGOAB2 69.0 528747 LE-ALLRED 2 69.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.03 | 528714 LE-FORT_SW 2 69.0 528718 LE-NEWTEX 2 69.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.11 | 528735 LE-PLAINSUB2 69.0 528740 LE-PLANS_SW2 69.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.03 | 528775 LE-ERF 3 115 528779 LE-TALLCOTN3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21016 | 115.79 | 530583 POSTROCK7 345 560082 G16-050-TAP 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 115.81 | 531213 SANTAFE3 115 531408 PIERCVL3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21025 | 116.04 | 531501 BUCKNER7 345 531502 CIMRRN 7 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21025 | 116.04 | 531502 CIMRRN 7 345 531503 CIMRRN 1 34.5 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21014 | 115.75 | 531510 HARBNGR3 115 3WXFMR HARBGR345 _1 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21026 | 116.06 | 532663 LEC U5 24.0 532854 LEC U5 6 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21033 | 116.04 | 532794 ROSEHIL7 345 560053 G15052_T 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21037 | 116.03 | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21026 | 116.06 | 532853 LAWHILL6 230 532854 LEC U5 6 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21025 | 116.01 | 539117 SPRVILL-EHVB 230 539695 SPEARVL6 230 Z1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21025 | 116.02 | 539803 IRONWOOD7 345 3WXFMR IRONWOOD MPT 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21026 | 116.13 | 542951 HAW G5 1 22.0 543665 HAWTHN5 161 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21026 | 116.17 | 542955 LAC G1 1 22.0 542981 LACYGNE7 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21025 | 116.15 | 542956 LAC G2 1 24.0 542981 LACYGNE7 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21024 | 116.2 | 542957 IAT G1 1 24.0 542982 IATAN 7 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21025 | 116.27 | 542962 IAT G2 1 24.5 542982 IATAN 7 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.03 | 542966 WGARDNR5 161 543105 BULLCRK5 161 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21274 | 115.57 | 560022 CRAWFISH_DR 345 762216 G17-151TAP 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21243 | 116.52 | 560022 CRAWFISH_DR 345 762467 G18-015-TAP 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 112.71 | 560022 CRAWFISH_DR 345 763087 GEN-2018-073 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21355 | 116.84 | 560022 CRAWFISH_DR 345 763215 G18-092-TAP 345 2
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21016 | 115.8 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.45 | 560252 G10-14 345 560253 G10-14-1 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.18 | 560253 G10-14-1 115 560254 G10-14-SUB1 34.5 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.19 | 560253 G10-14-1 115 560255 G10-14-SUB2 34.5 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.04 | 560581 G06-44-2 34.5 523111 NOVUS1 3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.08 | 560582 G06-44-3 34.5 560577 G06-44 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.07 | 560583 G06-44-4 34.5 560577 G06-44 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 115.72 | 560757 ASGI13_02_1 69.0 560758 ASGI13_02_2 34.5 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 115.72 | 560757 ASGI13_02_1 69.0 562731 WHEATLAND 69.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 115.73 | 560763 ASGI13_03_1 115 560761 ASGI13_03_2 34.5 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.16 | 562015 FIREWHEEL1 34.5 523215 FREWHELCOL17 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.16 | 562016 FIREWHEEL2 34.5 523215 FREWHELCOL17 345 2
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 115.71 | 562323 AGI1202&1305 115 562324 AGI1202&1305 34.5 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 115.73 | 562727 LESBIA 115 562728 SANJONTAP 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 115.72 | 562728 SANJONTAP 115 562729 CAPROCKTAP1 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 115.72 | 562730 CAPROCKTAP2 69.0 562729 CAPROCKTAP1 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 115.72 | 562730 CAPROCKTAP2 69.0 562731 WHEATLAND 69.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.15 | 563171 G15082_2 34.5 563170 G15082_1 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 115.78 | P11:13.8:AEPW:COM1-1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 115.79 | P11:13.8:AEPW:COM2-1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 115.79 | P11:13.8:AEPW:COM3-1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 115.78 | P11:18:AEPW:WELSH1-1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 115.79 | P11:18:AEPW:WELSH3-1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 115.78 | P11:24:AEPW:PIRKEY 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 115.68 | P11:24:AEPW:SWS3-1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 115.74 | P11:24:AEPW:TURKCOAL
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.2104 | 116.11 | P12:138:AEPW-OMPA:DUNCAN-4:OMDUNCN4
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.02 | P12:138:AEPW:112GORE4:L.E.S.-4
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21029 | 116.05 | P12:138:AEPW:112GORE4:SNYDER-4
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21029 | 116.05 | 5841_Dup1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21037 | 115.37 | 584560 GEN-2015-014 115 584561 G15-014XFMR1 34.5 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21035 | 116.08 | P12:138:AEPW:SANTAFE:DUNCAN-4
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.08 | 587991 G16-121XFMR1 34.5 587990 GEN-2016-121 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.01 | 588480 A16-010_SUB 115 3WXFMR A16-010_SUB 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.2104 | 116.1 | P12:138:AEPW:DUNCAN-4:L.E.S.-4
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 115.46 | 588761 G17-033XFMR1 34.5 588760 GEN-2017-033 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 115.46 | 588765 G17-033XFMR2 34.5 588760 GEN-2017-033 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.02 | 588861 G17-047XFMR1 34.5 588860 GEN-2017-047 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21013 | 115.79 | P12:138:AEPW:ELKCTY-4:CLINTJC4
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.03 | 589381 G17-100XFMR1 34.5 589380 GEN-2017-100 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21028 | 116.07 | P12:138:AEPW:SHERID4:112GORE4
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.2103 | 116.06 | P12:345:AEPW-OKGE:CLARKSV7:MUSKOGE7
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21275 | 117.78 | P12:345:AEPW:L.E.S7:TERRYRD7
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21275 | 117.77 | P12:345:AEPW:L.E.S7:TERRYRD7
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21274 | 117.75 | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21349 | 118.25 | P12:345:AEPW-OKGE:L.E.S.-7:GRACMNT7
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21349 | 118.23 | P12:345:AEPW-OKGE:L.E.S.-7:GRACMNT7
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21333 | 118.8 | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.08 | P22:345:AMMO::LABADIE:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.08 | P22:345:AMMO::LABADIE:2
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.09 | P22:345:AMMO::LABADIE:3
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.08 | P22:345:AMMO::LABADIE:4
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.07 | P22:345:AMMO::RUSHISLAND:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21028 | 116.06 | P22:345:AMMO::RUSHISLAND:2
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21029 | 115.79 | P13:138-13.8:AEPW:COMANC-4_#2
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 115.8 | P13:138-13.8:AEPW:S.W.S.-4
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.20968 | 115.47 | P13:138-230:AEPW:ELKCTY-4
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21028 | 115.79 | P13:138-24:AEPW:PIRKEY 4
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21032 | 115.69 | P13:138-24:AEPW:S.W.S.-4
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21029 | 115.75 | P13:138-24:AEPW:TURK 4
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21044 | 116.11 | P13:138-345:AEPW:L.E.S.-4_#2
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21028 | 116.02 | P12:500:EES-EAI:KEO:WMPEHV
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21029 | 116.14 | P23:500:EES-EAI:KEO:B4941
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21028 | 116.02 | P23:500:EES-EAI:KEO:B4931
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21029 | 116.13 | P23:500:EES-EAI:KEO:B4921
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21028 | 116.07 | P23:500:EES-EAI:INDEP2:B6126
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21028 | 116.06 | P23:500:EES-EAI:PD:INDEP2:LN:FK479
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21029 | 115.79 | P13:345-18:AEPW:WELSH 7_#1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21029 | 115.79 | P13:345-18:AEPW:WELSH 7_#3
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 115.79 | P13:69-13.8:AEPW:COMANC-2
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.08 | P11:024:DPC:ALMA2:6
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.04 | P11:18:ITCM:EMERYGT1:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.05 | P11:18:ITCM:EMERYGT2:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.05 | P11:161:ITCM:MGS CT1:1C
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.05 | P11:161:ITCM:MGS CT2:2C
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21025 | 116.06 | 652537 WHITE 3 345 659286 DEERCREK-BE3 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21026 | 116.02 | 652568 GROTONSOUTH7 115 659275 GROTON_G-BE7 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21025 | 116.06 | 659286 DEERCREK-BE3 345 3WXFMR DEERCRK KU1A 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.05 | 672601 BD 4 230 672306 BD 6G 18.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.05 | 672610 POPLAR 4 230 672310 POPLAR 1G 18.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.05 | 672610 POPLAR 4 230 672311 POPLAR 2G 18.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.04 | 672621 SHAND 4 230 672321 SHAND 1G 18.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.03 | 672649 CODETTE 4 230 672650 NIPAWIN 4 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.04 | 672696 BRADA 4 230 672699 NBEC 4 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.12 | P23:345:MDU::COYOTE::5707-5712-5715::::
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.3 | P23:345:MEC:CBEC 905
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.25 | P23:345:MEC:CBEC 908
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21028 | 116.04 | P23:345:MEC:GDMEC 901
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21028 | 116.04 | P23:345:MEC:GDMEC 902
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.06 | P23:345:MEC:GDMEC 908
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.17 | P23:345:MEC:RAUN 0180
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.24 | P23:345:MEC:RAUN 0210
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.18 | P23:345:MEC:LOUISA 954
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21028 | 116.19 | P23:345:MEC:LOUISA 964
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.03 | P21:115:XEL:AUTO-SINGLE:CHEMOLT7:LSPOWER7:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.07 | P21:115:XEL:AUTO-SINGLE:COLVILL7:CANONFLSG7:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.03 | P21:115:XEL:AUTO-SINGLE:FARIBALTP7:FARIBALTGEN:Z
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.13 | P21:230:OTP:AUTO-SINGLE:SQBUTTE4:YNG24:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.12 | P23:345:OTP:CENTER 3:3215(1)
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.12 | P23:345:OTP:CENTER 3:3225(1)
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.06 | P12:230:UMZW:# 687 #: FT IN SD. FT-BG1 LINE FAULT
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.06 | P12:230:UMZW:# 3617 #: FT IN SD. FT-BG2 LINE FAULT
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 114.69 | 760494 GEN-2017-146 230 760498 G17-146-TAP 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 114.68 | 760495 G17-146-XFM1 34.5 760494 GEN-2017-146 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 115.46 | 761356 G17-239-XFMR 34.5 761355 GEN-2017-239 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 115.46 | 761359 G17-239-XFMR 34.5 761355 GEN-2017-239 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 115.63 | 761797 G17-187XFM1 34.5 761796 GEN-2017-187 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 115.63 | 761800 G17-187XFM2 34.5 761796 GEN-2017-187 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 110.67 | 762132 GEN-2017-158 230 763252 G18-099-XFM1 34.5 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 110.67 | 762132 GEN-2017-158 230 763255 G18-099-XFM2 34.5 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 111.27 | 762133 G17-158XFM1 34.5 762132 GEN-2017-158 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 111.27 | 762136 G17-158XFM2 34.5 762132 GEN-2017-158 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 113.54 | 762216 G17-151TAP 345 762217 GEN-2017-151 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21274 | 116.85 | 762216 G17-151TAP 345 762467 G18-015-TAP 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 115.27 | 762218 G17-151XFM1 34.5 762217 GEN-2017-151 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 115.27 | 762221 G17-151XFM2 34.5 762217 GEN-2017-151 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 115.27 | 762224 G17-151XFM3 34.5 762217 GEN-2017-151 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 115.27 | 762227 G17-151XFM4 34.5 762217 GEN-2017-151 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 114.55 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 115.11 | 762461 G18-015-XFM1 34.5 762460 GEN-2018-015 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 115.11 | 762464 G18-015-XFM2 34.5 762460 GEN-2018-015 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21163 | 116.42 | 762467 G18-015-TAP 345 763215 G18-092-TAP 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 113.8 | 763087 GEN-2018-073 345 763088 G18-073-XFM1 34.5 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 114.78 | 763087 GEN-2018-073 345 763091 G18-073-XFM2 34.5 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 110.64 | 763120 GEN-2018-081 230 763121 G18-081-XFM1 34.5 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 112.78 | 763120 GEN-2018-081 230 764011 G19-074-XFM1 34.5 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 112.92 | 763186 GEN-2018-089 230 763187 G18-089-XFM1 34.5 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 113.84 | 763208 GEN-2018-092 345 763215 G18-092-TAP 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 114.77 | 763208 GEN-2018-092 345 763220 G18-092-XFM1 34.5 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 114.77 | 763208 GEN-2018-092 345 763223 G18-092-XFM2 34.5 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 112.23 | 763241 GEN-2018-097 230 763242 G18-097-XFM1 34.5 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 112.51 | 763241 GEN-2018-097 230 763307 G18-112-XFM1 34.5 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 112.51 | 763241 GEN-2018-097 230 763310 G18-112-XFM2 34.5 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 112.23 | 763241 GEN-2018-097 230 763395 G18-124-XFM1 34.5 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 112.23 | 763241 GEN-2018-097 230 763398 G18-124-XFM2 34.5 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 115.66 | 763318 GEN-2018-115 345 763319 G18-115-XFM1 34.5 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 112 | 763483 GEN-2019-003 230 763484 G19-003-XFM1 34.5 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 114.56 | 763483 GEN-2019-003 230 763605 G19-021-XFM1 34.5 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 115.46 | 763516 GEN-2019-011 345 763517 G19-011-XFM1 34.5 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 115.55 | 763879 GEN-2019-056 115 763880 G19-056XFM1 34.5 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.20993 | 116.19 | P42:345:OKGE:SB_BVTY7305
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21011 | 115.75 | P23:345:WERE:BUFF_345-534::
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21011 | 115.75 | P23:345:WERE:BUFF_345-543::
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21023 | 116.23 | P23:345:WERE:JEC_345-15::
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21022 | 116.18 | P23:345:WERE:JEC_345-16::
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21023 | 116.22 | P23:345:WERE:JEC_345-19::
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21023 | 116.22 | P23:345:WERE:JEC_345-20::
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.39 | P23:345:WERE:WOLF_345-50::
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.39 | P23:345:WERE:WOLF_345-60::
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21029 | 115.8 | P42:345:AEPW:WELSH CB 10620 NBTB+FAULT
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21028 | 115.79 | P41:345:AEPW:WELSH CB 10630 NBTB+FAULT
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 115.79 | P41:345:AEPW:WELSH CB 11670 NBTB+FAULT
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21039 | 115.78 | P41:345:AEPW:WELSH CB 11680 NBTB+FAULT
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 115.78 | P41:345:AEPW:WELSH CB 12540 NBTB+FAULT
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21333 | 117.33 | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21381 | 118.58 | P42:345:AEPW:LAWTON EASTSIDE CB 3413A NBTB+FAULT
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21416 | 118.94 | P42:345:AEPW:LAWTON EASTSIDE CB 3425A NBTB+FAULT
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21346 | 118.96 | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21275 | 117.77 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21275 | 117.77 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21275 | 117.74 | P42:345:AEPW:TERRYRD_CB_3421A_NBTB
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21026 | 116.18 | P23:345:KCPL:LACYGNE_R2-5::LACYGU2-LACYGNE-STILWELL
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21026 | 115.82 | P45:345:UMZW:# 1328 #: GI IN NE.
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21029 | 115.8 | P23:345:AEPW:WELSH CB 10620 NBTB
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21028 | 115.79 | P23:345:AEPW:WELSH CB 10630 NBTB
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 115.79 | P23:345:AEPW:WELSH CB 11670 NBTB
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21039 | 115.78 | P23:345:AEPW:WELSH CB 11680 NBTB
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 115.78 | P23:345:AEPW:WELSH CB 12540 NBTB
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21333 | 117.74 | P23:345:AEPW:OKLAUNION CB 3401A NBTB
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21381 | 118.58 | P23:345:AEPW:LAWTON EASTSIDE CB 3413A NBTB
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21416 | 118.94 | P23:345:AEPW:LAWTON EASTSIDE CB 3425A NBTB
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21346 | 118.96 | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21275 | 117.77 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21275 | 117.77 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21275 | 117.74 | P23:345:AEPW:TERRYRD_CB_3421A_NBTB
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.05 | P11:161:GMO:DOGWOOD_COMBINED_CYCLE_UNIT_OUTAGE
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.06 | P11:115:SUNC:GARDENCITY_S2:97:531459(2)
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21013 | 115.77 | P12:345:PWT:BUFF-THIS_345_1::
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21013 | 115.77 | P12:345:PWT:BUFF-THIS_345_2::
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21014 | 115.83 | P12:345:PWT:THIS-DGRS_345_1::FUTURE
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21014 | 115.83 | P12:345:PWT:THIS-DGRS_345_2::FUTURE
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21037 | 116.06 | P12:069:WFEC:ANADRKO_WATONGA
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21292 | 117.97 | P23:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21547 | 120.4 | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21292 | 117.97 | P42:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB+FAULT
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21547 | 120.4 | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.20561 | 114.13 | P42:345:OKGE:SB_BVTY7315_PRE19S
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.20996 | 115.62 | P23:345:SUNC:MO_BRK182
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.20996 | 115.62 | P23:345:SUNC:MO_BRK382
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.20992 | 115.79 | P23:345:SUNC:MO_BRK188
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21146 | 116.06 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21029 | 115.79 | P12:138-13.8:AEPW:COMANC-4_#1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.20968 | 115.47 | P12:230:AEPW:ELKCITY6:CHISHOLM6
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.2114 | 116.62 | P12:230:AEPW:SWEETWT6:CHISHOLM6
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997713 ABBXNL844501 230 1 |  | 553 | 0.34286 | 157.44 | 525531 TOLK 6 230 3WXFMR TOLK 6 2
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21029 | 116.18 | P23:345:KCPL-WERE:237LACYGNE_R1-6::LACYGU1-LACYGNE-NEOSHO
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21026 | 116.06 | P11:230:WERE:LECU5_GEN::
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.08 | P11:161:GMO:DOGWOOD_COMBINED_CYCLE_UNIT_OUTAGE_1_1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.02 | P11:20:KACY:NEARMAN N1::N1 OUT OF SERVICE:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21026 | 116.02 | P12:69:KACY:NMGEN-NMISOBUS::NEARMAN N1-NM ISOBUS OPEN:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21026 | 116.02 | P13:20-161:KACY:NEARMAN5-NMISOBUS:NAMEPLATE:NEARMAN N1 GSU:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21026 | 116.02 | P21:20:KACY:546702NMGENN1-546703NMISOBUSC1::::
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.23 | P11:115:SPS:HOBBS1&3:145MW::::
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21033 | 114.72 | P11:115:SPS:MUSTANG1&3:153MW::::
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21284 | 118.23 | P12:230:SPS:K37::1_TOLK_LAMB:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21048 | 116.06 | P12:230:SPS:K43::1_PRNGLE_HARR_E:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.2103 | 115.81 | P12:230:SPS:K44::1_EPLNT_HARRW:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21042 | 116.22 | P12:115:SPS:T04::1_TRBLNC_CASTRO:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21048 | 116.02 | P12:115:SPS:T06::1_SPRMN_PRNGLE:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.5 | P12:115:SPS:T21::1_GRSSLND_GRAHAM:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.05 | P12:115:SPS:T24B::1_RSWLL_BRSHRF:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21028 | 116.05 | P12:115:SPS:T26::1_CHAVES_RSWLCTY:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21149 | 116.45 | P12:115:SPS:T28A::1_LAMTON_PLANTX:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21073 | 116.02 | P12:115:SPS:T29::1_LAMTON_HALECTR:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21198 | 117.27 | P12:115:SPS:T30::1_LAMB_HOCKLY:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21198 | 116.37 | P12:115:SPS:T31::1_HOCKLY_SUNDWN:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21023 | 116.06 | P12:115:SPS:T35::1_TERRY_YOAKUM:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21028 | 116.78 | P12:115:SPS:T45::1_NORRIS_OASIS:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21026 | 115.82 | P12:115:SPS:T57::1_MUSTG_SEGRVS:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21154 | 116.03 | P12:115:SPS:T58::1_HERFRD_CARGIL:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21154 | 116.57 | P12:115:SPS:T59::1_CARGIL_CURRY:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.02 | P12:115:SPS:T64::1_RNDALL_PULLMN:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21124 | 116.38 | P12:115:SPS:T67::1_HAPPY_KRESS:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21032 | 115.77 | P12:115:SPS:T68::1_TUCO_FLOYD:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21028 | 115.81 | P12:115:SPS:T69::1_LUBBE_CROSBY:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.02 | P12:115:SPS:T70::1_COLTR_S_GORG:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21022 | 116.63 | P12:115:SPS:T71::1_CRLSLE_YUMA:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21036 | 116.1 | P12:115:SPS:T81::1_COX_FLOYD:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.26 | P12:115:SPS:T83::1_SP-FKFD_ALLEN:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21022 | 116.44 | P12:115:SPS:T89::1_DC_N_HIGG:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.07 | P12:115:SPS:T91::1_HIGG_RUSSELL:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21032 | 116.02 | P12:115:SPS:V01::1_MOOREW_RVRVIEW:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21049 | 116.07 | P12:115:SPS:V04::1_EPLANT_RNDALL:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21041 | 116.06 | P12:115:SPS:V07::1_COX_HALECTR:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21141 | 116.23 | P12:115:SPS:V09::1_HALECTR_PLANTX:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21026 | 116.21 | P12:115:SPS:V12::1_PLANTX_BAILEY:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.03 | P12:115:SPS:V15::1_TUCO_INDANA:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.20991 | 116.16 | P12:115:SPS:V24::1_WOLFTH_TERRY:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21045 | 116.07 | P12:115:SPS:V26::1_RSWLL_EDDY_N:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.4 | P12:115:SPS:V33::1_LUBBS_LYNN:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21132 | 117.14 | P12:115:SPS:V37::1_CASTRO_PLANTX:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21028 | 116.05 | P12:115:SPS:V44::1_COLTR_OWENS:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.16 | P12:115:SPS:V46::1_ALLEN_WHEELCK:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21029 | 116.5 | P12:115:SPS:V49::1_YOAKUM_SHLCO2:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.2107 | 116.68 | P12:115:SPS:V55::1_SUNDWN_TERRY:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.2104 | 116.59 | P12:115:SPS:V56::1_COCHRAN_SUNDWN:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.09 | P12:115:SPS:V62::1_CRLSLE_INDANA:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.2104 | 116.07 | P12:115:SPS:V78::2_CURRY_RSVLT:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21025 | 116.19 | P12:115:SPS:V81::1_LE-WAIT_LE-LVN:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21028 | 116.06 | P12:115:SPS:V95::1_DC_N_SHLCO2:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.02 | P12:115:SPS:W11::1_DC_S_SMINLE:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.03 | P12:115:SPS:W12::1_SMINLE_DOSS:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.1 | P12:115:SPS:W14::1_SMINLE_GAINES:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.03 | P12:115:SPS:W26::1_CUNGHM_OILCNTR:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.61 | P12:115:SPS:W32::1_PRMTR_FE-CLSIN:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21024 | 116.26 | P12:115:SPS:W35::1_GAINES_JNSDRW:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21219 | 116.59 | P12:115:SPS:W40::1_WCANYON_TRBLNC:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21055 | 116.11 | P12:115:SPS:W52::1_NEWHART_KRESS:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.67 | P12:115:SPS:W58::1_NORTON_LOPEZ:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.25 | P12:115:SPS:W59::1_LOPEZ_CMPBLL:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21028 | 116.55 | P12:115:SPS:W62::1_PLSTHL_CURRY:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.2104 | 116.07 | P12:115:SPS:W63::1_PLSTHL_CURRY:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.36 | P12:115:SPS:W64::1_PLSTHL_FE-CLV:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21029 | 116.57 | P12:115:SPS:W65::1_PLSTHL_CURRY:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.23 | P12:115:SPS:W66::1_PORTA_GREYHUND:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21024 | 116.02 | P12:115:SPS:W76::1_QUAHA_PCA:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21219 | 116.1 | P12:115:SPS:W77::1_RNDAL_WCANYON:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21028 | 116.07 | P12:115:SPS:W99::1_CAPITAN_CHAVES:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.05 | P12:115:SPS:U03::1_CARDNL_NEF:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21023 | 116.53 | P12:115:SPS:U14::1_DC_STH_INKBSN:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21025 | 116.47 | P12:115:SPS:V15::1_INKBSN_LE-WAT:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.2105 | 116.15 | P12:115:SPS:U16::1_BSHLND_OUTPST:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.2105 | 116.16 | P12:115:SPS:U17::1_COLTR_OUTPST:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21034 | 116.26 | P12:115:SPS:U19::1_DEAN_PLAINS:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.2105 | 116.07 | P12:115:SPS:U23::1_COLTR_HILSDE:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.20186 | 124.36 | P42:345:SPS:YOAKUM:J18####:SLG1:EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.20186 | 124.36 | P43:345:SPS:YOAKUM:TF#####:SLG:EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.20186 | 124.36 | P42:345:SPS:YOAKUM:J17####:SLG:EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.20186 | 124.36 | P42:345:SPS:YOAKUM:J18####:SLG2:EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21026 | 116.06 | P11:18:HAST:::EGYCTR2G WEC2_LOSS OF WEC 2 GEN_:HV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21026 | 116.06 | P13:18-115:HAST:::EGYCNTR7 XFMR G2WEC 2 GSU_:HV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.08 | P11:161:GMO:DOGWOOD-COMBINED-CYCLE-UNIT-OUTA:::HV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21029 | 116.18 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21026 | 116.18 | P23:345:KCPL:LACYGNE-R2-5:::EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21023 | 116.23 | P11:230:WERE:JECU1-GEN:::HV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21026 | 116.06 | P11:230:WERE:LECU5-GEN:::HV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21023 | 116.23 | P11:345:WERE:JECU2-GEN:::EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21023 | 116.22 | P11:345:WERE:JECU3-GEN:::EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.4 | P11:345:WERE:WOLFU1-GEN:::EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21013 | 115.77 | P12:345:PWT:BUFF-THIS-345-1:::EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21013 | 115.77 | P12:345:PWT:BUFF-THIS-345-2:::EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21011 | 115.75 | P23:345:WERE:BUFF-345-534:::EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21011 | 115.75 | P23:345:WERE:BUFF-345-543:::EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21023 | 116.23 | P23:345:WERE:JEC-345-15:::EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21022 | 116.18 | P23:345:WERE:JEC-345-16:::EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21023 | 116.22 | P23:345:WERE:JEC-345-19:::EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21023 | 116.22 | P23:345:WERE:JEC-345-20:::EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.39 | P23:345:WERE:WOLF-345-50:::EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.39 | P23:345:WERE:WOLF-345-60:::EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.34 | P11:022:NPPD:COOPER1G:1:983:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21022 | 116.33 | P11:023:NPPD:GENTLM1G:1:757:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21022 | 116.35 | P11:024:NPPD:GENTLM2G:2:757:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21026 | 116.01 | P11:161:OPPD:N OMA 5G:LT::HV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21026 | 116.01 | P11:161:OPPD:N OMA 5G:::HV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21023 | 116.2 | P13:345:OPPD:NEBCTY1G:::EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21022 | 116.22 | P13:345:OPPD:NEBCTY2G:::EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21026 | 116.01 | P13:161:OPPD:N OMA 5G:::HV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.22 | P22:345:OPPD:S3458 NEBCTY1G:LT::EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21023 | 116.2 | P22:345:OPPD:S3458 NEBCTY1G:::EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.25 | P22:345:OPPD:S3458 NEBCTY2G:LT::EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21022 | 116.22 | P22:345:OPPD:S3458 NEBCTY2G:::EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.22 | P23:345:OPPD:S3458 NEBCTY1G:LT::EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21023 | 116.2 | P23:345:OPPD:S3458 NEBCTY1G:::EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.25 | P23:345:OPPD:S3458 NEBCTY2G:LT::EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21022 | 116.22 | P23:345:OPPD:S3458 NEBCTY2G:::EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 115.8 | P12:115:SUNC:PLYMELL-PIERCEVILLE:::HV::
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21025 | 116.06 | P11:018:UMZB:# 5 #:: DCS IN SD. DEERCREEK_MV::
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21026 | 116.03 | P11:022:UMZB:# 15 #:: LO IN ND. LELAND OLDS 1_MV::
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21025 | 116.07 | P11:020:UMZB:# 16 #:: LO IN ND. LELAND OLDS 2_MV::
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21025 | 116.14 | P11:023:UMZB:# 31 #:: AVS IN ND. ANTELOPE VALLEY 1_MV::
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21025 | 116.14 | P11:023:UMZB:# 32 #:: AVS IN ND. ANTELOPE VALLEY 2_MV::
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21021 | 116.33 | P11:024:UMZB:# 33 #:: LRS IN WY. LARAMIE RIVER STATION 1_MV::
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.06 | P12:230:UMZW:# 687 #:: FT IN SD. FT-BG1 BRANCH FAULT:HV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.06 | P12:230:UMZW:# 3617 #:: FT IN SD. FT-BG2 BRANCH FAULT:HV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.06 | P12:230:UMZW:# 4038 #:: BG-FT IN SD. FAULT FOR TRANSMISSION CIRCUIT (BG-FT).:HV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.06 | P12:230:UMZW:# 4039 #:: BG-FT IN SD. FAULT FOR TRANSMISSION CIRCUIT (BG-FT).:HV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.03 | P13:230:UMZW:# 5135 #:: OA IN SD. FAULT ON TRANSFORMER (2).:HV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.03 | P13:230:UMZW:# 5136 #:: OA IN SD. FAULT ON TRANSFORMER (3).:HV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21026 | 115.82 | P23:345:UMZW:# 2423 #:: GI IN NE. GI 1596 BKR FAULT:EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21026 | 115.82 | P23:345:UMZW:# 2426 #:: GI IN NE. GI 1592 BKR FAULT:EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21026 | 115.82 | P23:345:UMZW:# 2432 #:: GI IN NE. GI 1092 BKR FAULT:EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21026 | 115.82 | P23:345:UMZW:# 2440 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1092 STUCK BKR:EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21026 | 115.82 | P23:345:UMZW:# 2444 #:: GI IN NE. GI-SWEET BRANCH FAULT & GI 1596 STUCK BKR:EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21026 | 115.82 | P23:345:UMZW:# 2446 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1196 STUCK BKR:EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21026 | 115.82 | P42:345:UMZW:# 2413 #:: FT2 IN SD. FT2-LO2 BRANCH FAULT & FT2 2992 STUCK BKR:EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21026 | 115.82 | P42:345:UMZW:# 2415 #:: FT2 IN SD. FT2-GI BRANCH FAULT & FT2 3392 STUCK BKR:EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21031 | 115.74 | P11:138:WFEC:HUGO1:465MW :::
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21026 | 116.02 | P11:138:WFEC:MORLND2:132MW:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21026 | 116.03 | P11:138:WFEC:MORLND3:149MW :::
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21036 | 116.06 | P12:138:WFEC:ANADRKO_CLVLND::::
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.2103 | 116.06 | P12:345:OKGE-AEPW:BKRBKR12::::
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21064 | 116.18 | P12:345:OKGE:BKRBKR21::::
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21083 | 116.26 | P12:345:OKGE:BKRBKR24::::
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21274 | 117.75 | P12:345:OKGE-AEPW:BKRBKR25::::
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.20996 | 115.72 | P12:345:OKGE:BKRBKR336::::
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.20996 | 115.72 | P12:345:OKGE:BKRBKR336_2::::
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21349 | 118.25 | P12:345:OKGE-AEPW:BKRBKR366::::
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21349 | 118.23 | P12:345:OKGE-AEPW:BKRBKR366::::
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21236 | 117.15 | P12:345:OKGE:BKRBKR367::::
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21001 | 115.72 | P12:345:OKGE:BKRBKR4193::::
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21001 | 115.72 | P12:345:OKGE:BKRBKR4194::::
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.02 | P12:345:OKGE:BKRBKR4195::::
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.2099 | 115.76 | P12:345:OKGE-SPS:BKRBKR4201::::
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.2099 | 115.76 | P12:345:OKGE-SPS:BKRBKR4202::::
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21037 | 116.03 | P12:345:OKGE:BKRBKR421::::
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.20994 | 115.6 | P12:345:OKGE:BKRBKR443NEW::::
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.20993 | 115.6 | P12:345:OKGE:BKRBKR443NEW2::::
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21011 | 115.79 | P12:345:OKGE-ITC:BKRBKR502::::
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21011 | 115.79 | P12:345:OKGE-ITC:BKRBKR503::::
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21014 | 115.83 | P12:345:OKGE-ITC:BKRBKR502_1::::
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21014 | 115.83 | P12:345:OKGE-ITC:BKRBKR503_1::::
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21021 | 116.33 | P12:345:OKGE:BKRBKR604::::
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.2102 | 116.37 | P12:345:OKGE:BKRBKR604_2::::
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21029 | 115.82 | P11:345:OKGE:BKRBKR_GSU07::::
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21029 | 115.81 | P11:345:OKGE:BKRBKR_GSU08::::
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21029 | 115.8 | P11:138:OKGE:BKRBKR_GSU21::::
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21025 | 115.83 | P12:138:OKGE:BKRBKR85_MOS1::::
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.20994 | 116.13 | P42:345:OKGE:SB_ARIA7381::::
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21722 | 120.17 | P42:345:OKGE:SB_BVTY7387::::
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21038 | 116.02 | P41:345:OKGE:SB_REUD7381::::
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21037 | 116.03 | P41:345:OKGE:SB_REUD7383::::
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21037 | 116.06 | P41:345:OKGE:SB_REUD7385::::
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.2104 | 116.06 | P42:345:OKGE:SB_REUD7389::::
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21025 | 116.05 | P11:115:SUNC:GARDENCITY_S2:103:531459(2):HV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21025 | 116.07 | P11:115:SUNC:FORTDDODGE_4:157:539670(4):HV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.04 | P11:345:599:CIMARRON1WIND:200:531603(1):EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.47 | P13:115:SUNC:HOLCOMB_GSU:::HV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21025 | 116.05 | P13:115:SUNC:S2_GSU:::HV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21025 | 116.07 | P13:115:SUNC:FORTDODGE_GSU:::HV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21025 | 116.04 | P23:345:SUNC:BU_BRK682:::EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.14 | 300003 1THLG3 24.0 301503 7THOMHLGSU3 345 3
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.01 | 300007 1NM G2 22.0 301537 7NEWMADGSU2 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.01 | 300046 7NEWMAD 345 301537 7NEWMADGSU2 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.14 | 300049 7THOMHL 345 301503 7THOMHLGSU3 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.08 | P11:20:AMMO:1LAB�� G1:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.08 | P11:20:AMMO:1LAB�� G2:2
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.27 | P11:345:AMMO::CALLAWAY:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.08 | P11:345:AMMO::LABADIE:3
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.08 | P11:345:AMMO::LABADIE:4
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.07 | P11:345:AMMO::RUSHISLAND:U1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.07 | P11:345:AMMO::RUSHISLAND:U2
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.06 | P11:138:AMMO::SIOUX:2
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 115.83 | P11:24:CLEC::G1DOLHIL:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.06 | P12:765:AEP:AEP ROCKP-AEP JEFF 765
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 115.78 | P11:HV:EES::PIRKEY 1:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 115.79 | P11:EHV:EES::WELSH3-1:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 115.74 | P11:HV:EES::TURKCOAL:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.25 | P12:EHV:EES::7CALAWY 1:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21028 | 116.02 | 338056 CHALKBLUFFPV 500 338162 8W.MEMPHIS% 500 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21029 | 115.75 | P12:HV:EES::TURK 4%:1(1)
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21029 | 115.79 | P12:EHV:EES::WELSH 7:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21029 | 115.79 | P12:EHV:EES::WELSH 7:1(1)
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21028 | 115.79 | P12:HV:EES::PIRKEY 4:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.2103 | 116.06 | P12:EHV:EES::CLARKSV7!:MUSKOGE7!:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.06 | 344011 7HUGHES 345 344012 7HPW-N 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.08 | 344884 7LABADIE1 345 344894 1LAB G1 20.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.08 | 344885 7LABADIE2 345 344895 1LAB G2 20.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.08 | 344886 7LABADIE3 345 344896 1LAB G3 20.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.08 | 344887 7LABADIE4 345 344897 1LAB G4 20.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.07 | 345667 7RUSH 1 345 345670 1RUSH G1 18.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.06 | 345668 7RUSH 2 345 345671 1RUSH G2 18.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.05 | 345755 4SIOUX 1 138 345756 1SIOUX 1 18.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.05 | 345764 4SIOUX 2 138 345765 1SIOUX 2 18.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.12 | P12:345:MDU::CENTER:COYOTE:1::::
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.12 | P13:345:MDU:COYOTE GSU LOSS:COYOTE::1::::
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.03 | P11:345:MEC:GDMEC CT1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.03 | P11:345:MEC:GDMEC CT2
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.14 | P11:345:MEC:GDMEC ST
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.35 | P11:345:MEC-NPPD:COOPER 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.24 | P11:24:XEL:AUTO-SINGLE:SHERC31G:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.24 | P11:24:XEL:AUTO-SINGLE:SHERC32G:2
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.33 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.16 | P11:20:XEL:AUTO-SINGLE:PRIS31G:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.16 | P11:20:XEL:AUTO-SINGLE:PRIS32G:2
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.2 | P11:22:XEL:AUTO-SINGLE:MNTCE31G:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.16 | P11:20:XEL:AUTO-SINGLE:KING31G:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.02 | P11:13:XEL:AUTO-SINGLE:HBRS73G:9
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.02 | P11:18:XEL:AUTO-SINGLE:BLKD76G:6
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.22 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.22 | P11:22:GRE:AUTO-SINGLE:GRE-COAL42G:2
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.14 | P11:24:OTP:AUTO-SINGLE:BIGSTN1G:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.15 | P11:20:OTP:AUTO-SINGLE:CENTER2G:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.05 | P11:22:OTP:AUTO-SINGLE:CENTER1G:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.13 | P11:24:OTP:AUTO-SINGLE:COYOTE1G:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.05 | P11:24:DPC:AUTO-SINGLE:GENOA53G:3
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.03 | P12:115:XEL:AUTO-SINGLE:CHEMOLT7:LSPOWER7:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.07 | P12:115:XEL:AUTO-SINGLE:COLVILL7:CANONFLSG7:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.03 | P12:115:XEL:AUTO-SINGLE:FARIBALTP7:FARIBALTGEN:Z
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.13 | P12:230:OTP:AUTO-SINGLE:SQBUTTE4:YNG24:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.22 | P13:24-345:XEL:AUTO-SINGLE:SHERC31G:SHERCO3:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.22 | P13:24-345:XEL:AUTO-SINGLE:SHERC32G:SHERCO3:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.3 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.16 | P13:20-345:XEL:AUTO-SINGLE:PRIS31G:PRISLD3:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.16 | P13:20-345:XEL:AUTO-SINGLE:PRIS32G:PRISLD3:2
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.2 | P13:22-345:XEL:AUTO-SINGLE:MNTCE31G:MNTCELO3:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.15 | P13:20-345:XEL:AUTO-SINGLE:KING31G:ASKING3:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.02 | P13:13-115:XEL:AUTO-SINGLE:HBRS73G:HIBRDGE7:9
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.2 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL41G:GRE-COALCR4:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.2 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL42G:GRE-COALCR4:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.13 | P13:230-24:OTP:AUTO-SINGLE:BIGSTON4:BIGSTN1G:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.13 | P13:20-230:OTP:AUTO-SINGLE:CENTER2G:YNG24:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.04 | P13:22-230:OTP:AUTO-SINGLE:CENTER1G:CENTER4:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.12 | P13:24-345:OTP:AUTO-SINGLE:COYOTE1G:COYOTE3:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.05 | P13:24-161:DPC:AUTO-SINGLE:GENOA53G:GENOA5:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.07 | P13:24-161:DPC:AUTO-SINGLE:JPM:ALMA5:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21028 | 116.02 | 38203 J1819 POI 500 337957 8KEO% 500 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21028 | 116.02 | 38203 J1819 POI 500 338056 CHALKBLUFFPV 500 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.13 | P11:115:XEL:RIV COMBINE CYCLE
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.04 | P12:115:XEL:BDS #2 5
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.04 | P11:115:XEL:HBR #6
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.04 | P11:115:XEL:HBR #7
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.16 | P11:115:XEL:HBR #6 7 8
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.16 | P23:345:XEL:8H14 PRI
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.16 | P23:345:XEL:8H17 PRI AS
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.3 | P23:345:XEL:8N28 SHC
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.22 | P23:345:XEL:8N22 SHC
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.22 | P23:345:XEL:8N17 SHC
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.21 | P23:345:XEL:8N8 MNN
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.15 | P23:345:XEL:8P1 KING
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.15 | P23:345:XEL:8P2 KING
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.04 | P23:115:XEL:5P147 IVH AS
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.03 | P11:18:ALTW:AUTO-SINGLE:EMERYST1:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.03 | P11:22:ALTW:AUTO-SINGLE:LANS54G:4
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.17 | P11:22:ALTW:AUTO-SINGLE:ARNOLD1G:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.2 | P11:24:ALTW:AUTO-SINGLE:OTTUMW1G:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.03 | P13:18-161:ALTW:AUTO-SINGLE:EMERYST1:EMERY5:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.03 | P13:22-161:ALTW:AUTO-SINGLE:LANS54G:LANSINGL15:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.16 | P13:22-161:ALTW:AUTO-SINGLE:ARNOLD1G:ARNOLD5:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.19 | P13:24-161:ALTW:AUTO-SINGLE:OTTUMW1G:OTTUMWA5:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.27 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.34 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.19 | P11:22:MEC:AUTO-SINGLE:NEAL3G:3
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.26 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.19 | P11:24:MEC:AUTO-SINGLE:LOUIS31G:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.25 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.3 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.17 | P13:345-22:MEC:AUTO-SINGLE:RAUN3:NEAL3G:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.24 | P13:345-24:MEC:AUTO-SINGLE:RAUN3:NEAL4G:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.18 | P13:345-24:MEC:AUTO-SINGLE:LOUISA3:LOUIS31G:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21023 | 116.23 | P11:230:WERE:JECU1_GEN::
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21023 | 116.23 | P11:345:WERE:JECU2_GEN::
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21023 | 116.22 | P11:345:WERE:JECU3_GEN::
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.4 | P11:345:WERE:WOLFU1_GEN::
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21029 | 116.03 | 511435 SNYDER-4 138 588779 TAP_G17-036 138 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21035 | 116.03 | 511453 DUNCAN-4 138 511552 DUNCHERTP4 138 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21035 | 116.03 | 511455 D.E.S.-4 138 511552 DUNCHERTP4 138 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21035 | 116.02 | 511455 D.E.S.-4 138 529344 OMDUNE-4 138 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 114.98 | 511456 O.K.U.-7 345 588760 GEN-2017-033 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21333 | 117.74 | 511456 O.K.U.-7 345 763215 G18-092-TAP 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21347 | 118.31 | 511468 L.E.S.-7 345 762467 G18-015-TAP 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21244 | 117.72 | 511468 L.E.S.-7 345 763215 G18-092-TAP 345 2
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 115.66 | 511468 L.E.S.-7 345 763318 GEN-2018-115 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21029 | 116.05 | 511488 112GORE4 138 511510 LAIRGST4 138 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.2104 | 116.11 | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21029 | 116.04 | 511500 CACHE4 138 511510 LAIRGST4 138 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21029 | 116.03 | 511500 CACHE4 138 588779 TAP_G17-036 138 2
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21146 | 116.06 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.20361 | 113.09 | 511553 CHISHOLM7 345 523961 POTTER_CO 7 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.20361 | 113.09 | 511553 CHISHOLM7 345 523961 POTTER_CO 7 345 2
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.20733 | 115.5 | 511553 CHISHOLM7 345 755000 WWDBORDT 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.14 | 511557 CHISHOLM6 230 3WXFMR CHISHOLM6 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21041 | 116.02 | 514801 MINCO 7 345 555234 NSUB345 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.20953 | 115.63 | 515375 WWRDEHV7 345 755000 WWDBORDT 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21722 | 120.2 | 515458 BORDER 7 345 560022 CRAWFISH_DR 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21722 | 120.15 | 515458 BORDER 7 345 755000 WWDBORDT 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21037 | 116.02 | 515543 RENFROW7 345 763421 G18-128-TAP 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21024 | 116.12 | 515618 BALKOW 7 345 3WXFMR BALKOW 7 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21024 | 116.13 | 515618 BALKOW 7 345 3WXFMR BALKOW 7 1_Dup1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21033 | 116.04 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.2102 | 116.39 | 515634 PALDR1W7 345 3WXFMR PALO2 _1 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.13 | 515677 BADGER 7 345 563170 G15082_1 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21023 | 116.01 | 521017 ONEY 4 138 521089 WASHITA4 138 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.02 | 522800 MU-TULIA 3 115 525179 TULIA_TP 3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.16 | 522892 MU-BROWNFLD2 69.0 526761 BROWNFLD_TP2 69.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.03 | 523090 TEXAS_CNTY 3 115 589380 GEN-2017-100 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21023 | 116.16 | 523093 HITCHLAND 3 115 523174 GOODWELLWND3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.34 | 523097 HITCHLAND 7 345 523112 NOVUS1 7 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.4 | 523097 HITCHLAND 7 345 523215 FREWHELCOL17 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.20824 | 114.83 | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.45 | 523097 HITCHLAND 7 345 560252 G10-14 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.01 | 523099 TC-DRYTRLS 3 115 588480 A16-010_SUB 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.23 | 523112 NOVUS1 7 345 3WXFMR NOVUS XF2 2
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.04 | 523112 NOVUS1 7 345 3WXFMR XIANA2011198 _1 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21026 | 116.02 | 523118 BUFF_DUNES 7 345 523853 FINNEY 7 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.02 | 523120 COLE 3 115 588860 GEN-2017-047 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21025 | 116.04 | 523172 GWELL_COLL11 34.5 523174 GOODWELLWND3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21025 | 116.04 | 523173 GWELL_COLL21 34.5 523174 GOODWELLWND3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21036 | 116.01 | 523221 XIT_INTG 6 230 3WXFMR SIEM_T126401 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21048 | 116.07 | 523267 PRINGLE 6 230 3WXFMR ENRCO13617-1 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21048 | 116.06 | 523267 PRINGLE 6 230 523979 HARRNG_EST 6 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.2109 | 116.2 | 523309 MOORE_CNTY 6 230 523323 MCDWL_CREEK6 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21062 | 116.12 | 523323 MCDWL_CREEK6 230 523959 POTTER_CO 6 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.20997 | 116.45 | 523959 POTTER_CO 6 230 524010 ROLLHILLS 6 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21843 | 117.19 | 523959 POTTER_CO 6 230 524267 BUSHLAND 6 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.2181 | 118.35 | 523959 POTTER_CO 6 230 525461 NEWHART 6 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.2139 | 121.11 | 523961 POTTER_CO 7 345 3WXFMR WAUK 90343-A 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21025 | 115.74 | 523978 HARRNG_MID 6 230 523979 HARRNG_EST 6 230 @1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.2105 | 116.16 | 524267 BUSHLAND 6 230 3WXFMR WH 7001795 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.22491 | 117.94 | 524267 BUSHLAND 6 230 524623 DEAFSMITH 6 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21015 | 116.44 | 524296 SPNSPUR_WND7 345 524299 SPNSPUR_COL7 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21015 | 116.44 | 524299 SPNSPUR_COL7 345 3WXFMR SPNSPUR_COL7 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21416 | 117.09 | 524415 AMA_SOUTH 6 230 525213 SWISHER 6 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.67 | 524502 NORTON 3 115 524509 FE-TUCMCARI3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21219 | 116.45 | 524575 DS-#25+ 3 115 524597 PANDAHFD 3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21219 | 116.55 | 524575 DS-#25+ 3 115 524630 TIERABLANCA3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.11 | 524604 HEREFRD_SB 2 69.0 524608 HERFRD_STH 2 69.0 *1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.2234 | 122.73 | 524623 DEAFSMITH 6 230 760498 G17-146-TAP 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.52 | 524721 DS-#15&#19+2 69.0 524745 CASTRO_CNTY2 69.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21033 | 116.03 | 524770 PLSNT_HILL 6 230 3WXFMR EFAE1100068A 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.2145 | 121.59 | 524875 OASIS 6 230 524885 SN_JUAN_TAP6 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21101 | 117.16 | 524875 OASIS 6 230 524909 ROOSEVELT 6 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21441 | 121.97 | 524885 SN_JUAN_TAP6 230 527483 CHAVES_CNTY6 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21044 | 116.22 | 524909 ROOSEVELT 6 230 3WXFMR ABB LMM60042 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21721 | 122.19 | 524909 ROOSEVELT 6 230 525531 TOLK 6 230 2
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.77 | 524923 PORTALES 2 69.0 524929 RO-PORT_MTR2 69.0 @1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.42 | 524923 PORTALES 2 69.0 524941 PORTALES#1 2 69.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.66 | 525023 BC-BAIL_MTR2 69.0 525027 BAILEYCO 2 69.0 @1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21132 | 116.55 | 525056 BC-EARTH 3 115 525480 PLANT_X 3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.51 | 525191 KRESS_INT 2 69.0 525203 SW-KRESS 2 69.0 Z1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.6 | 525192 KRESS_INT 3 115 3WXFMR ENRCO 136155 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21328 | 116.83 | 525213 SWISHER 6 230 525461 NEWHART 6 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.15 | 525272 KISER 3 115 3WXFMR VON 13819/1 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.61 | 525326 COX 3 115 3WXFMR ELCO 13474-3 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.61 | 525414 LAMTON 3 115 3WXFMR ASEA MLL9204 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.22646 | 119.68 | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21301 | 118.1 | 525481 PLANT_X 6 230 3WXFMR WH ALM20171 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21975 | 121 | 525481 PLANT_X 6 230 526435 SUNDOWN 6 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.2234 | 121.02 | 525481 PLANT_X 6 230 760498 G17-146-TAP 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21374 | 116.49 | 525481 PLANT_X 6 230 762174 G17-218TAP 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21416 | 116.56 | 525481 PLANT_X 6 230 762174 G17-218TAP 230 2
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.22176 | 121.7 | 525531 TOLK 6 230 525586 NEEDMORE 6 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21284 | 118.23 | 525531 TOLK 6 230 525637 LAMB_CNTY 6 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.23952 | 120.42 | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.2154 | 116.76 | 525531 TOLK 6 230 762174 G17-218TAP 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21576 | 116.82 | 525531 TOLK 6 230 762174 G17-218TAP 230 2
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.34286 | 155.48 | 525549 TOLK 7 345 3WXFMR ABBXNL844501 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.22176 | 121.69 | 525586 NEEDMORE 6 230 526935 YOAKUM 6 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.41 | 525599 LC-SANDHLL+2 69.0 525606 AMHERST 2 69.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.45 | 525606 AMHERST 2 69.0 525613 W_LITTLFLD 2 69.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.46 | 525613 W_LITTLFLD 2 69.0 525635 LAMB_CNTY 2 69.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.42 | 525635 LAMB_CNTY 2 69.0 525650 LC-LTTLFLD+2 69.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21284 | 118.23 | 525637 LAMB_CNTY 6 230 3WXFMR WH ALM20172 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.41 | 525779 FLOYD_CNTY 2 69.0 525790 FLOYDADA_TP2 69.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.29 | 525828 TUCO_INT 3 115 3WXFMR DS F78800913 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.20276 | 118.38 | 525832 TUCO_INT 7 345 526936 YOAKUM_345 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.49 | 526086 SW_6786_N 2 69.0 526087 SW_6786_S 2 69.0 Z1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.49 | 526086 SW_6786_N 2 69.0 526102 SP-HETTLER 2 69.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.56 | 526087 SW_6786_S 2 69.0 526284 PLANTERS 2 69.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.1 | 526160 CARLISLE 3 115 3WXFMR WH RLP38371 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.44 | 526195 QUINCY 3 115 526196 SP-MILWAUKEE 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.34 | 526268 LUBBCK_STH 3 115 3WXFMR NA 70454A 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.6 | 526284 PLANTERS 2 69.0 526297 LUBBCK_EST 2 69.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.2104 | 116.47 | 526424 PACIFIC 3 115 526434 SUNDOWN 3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21023 | 116.06 | 526435 SUNDOWN 6 230 3WXFMR UPDATE LATER _12 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21049 | 118.87 | 526435 SUNDOWN 6 230 526460 AMOCO_SS 6 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21049 | 116.5 | 526460 AMOCO_SS 6 230 526935 YOAKUM 6 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21025 | 116.08 | 526525 WOLFFORTH 6 230 3WXFMR UPDATE LATER _13 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.48 | 526735 TERRY_CNTY 2 69.0 526747 LG-BROWNFLD2 69.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21015 | 118.02 | 526935 YOAKUM 6 230 527028 INK_BASIN 6 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.2145 | 116.3 | 526936 YOAKUM_345 345 3WXFMR SPX WT04221 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.20267 | 126.57 | 526936 YOAKUM_345 345 527896 HOBBS_INT 7 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21004 | 117.39 | 527028 INK_BASIN 6 230 527894 HOBBS_INT 6 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21022 | 116.43 | 527130 DENVER_N 3 115 527286 HIGGEAST 3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21028 | 116.02 | 527149 MUSTANG 6 230 3WXFMR ENRCO 136161 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21043 | 114.01 | 527149 MUSTANG 6 230 527151 GS-MUSTANG 6 230 @1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.29 | 527202 SEAGRAVES 3 115 3WXFMR ABB MLL92408 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.17 | 527212 DIAMONDBACK3 115 3WXFMR HOW 36773714 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21022 | 116.41 | 527286 HIGGEAST 3 115 527363 HIGG 3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21024 | 116.16 | 527325 OXY_WSEM_TP3 115 527362 JOHNSON_DRW3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.15 | 527340 DOSS 3 115 3WXFMR ELCO 13566/1 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.14 | 527345 LEGACY 2 69.0 527350 XTO_ROBRTSN2 69.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.14 | 527346 LEGACY 3 115 3WXFMR VROL 13735-1 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.12 | 527350 XTO_ROBRTSN2 69.0 527355 BOARDMAN 2 69.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.05 | 527355 BOARDMAN 2 69.0 527365 FLANNAGAN 2 69.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.02 | 527360 MAPCO 3 115 527362 JOHNSON_DRW3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.08 | 527362 JOHNSON_DRW3 115 528775 LE-ERF 3 115 @1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.01 | 527370 TENNECO_TAP2 69.0 527371 TENNECO 2 69.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21205 | 116.35 | 527483 CHAVES_CNTY6 230 527799 EDDY_NORTH 6 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.05 | 527508 PRICE 3 115 527509 PRICE_TAP 3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.02 | 527514 CV-PINE 2 69.0 527563 ROSWLL_INT 2 69.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.05 | 527529 RIACBRSH_TP3 115 527533 SW4J795_E 3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.02 | 527529 RIACBRSH_TP3 115 527536 BRASHER 3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.05 | 527533 SW4J795_E 3 115 527564 ROSWLL_INT 3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.06 | 527563 ROSWLL_INT 2 69.0 527575 SW_4702 2 69.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21045 | 116.1 | 527564 ROSWLL_INT 3 115 527597 TWEEDY 3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.06 | 527575 SW_4702 2 69.0 527589 CV-ORCHARD 2 69.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.02 | 527589 CV-ORCHARD 2 69.0 527619 DEXTER_TP 2 69.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21023 | 116.18 | 527653 MILO_WIND 1 34.5 527655 RSVLT_CC_E 7 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21015 | 116.1 | 527654 RSVLT_CC_W 7 345 527655 RSVLT_CC_E 7 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21015 | 116.36 | 527654 RSVLT_CC_W 7 345 527666 RSVLT_COL1 7 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21011 | 116.3 | 527655 RSVLT_CC_E 7 345 527656 CROSSROADS 7 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21015 | 116.36 | 527666 RSVLT_COL1 7 345 3WXFMR RSVLT_COL1 7 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.15 | 527790 EDDY_SVC 1 8.50 527799 EDDY_NORTH 6 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.05 | 527864 CUNNINHAM 3 115 528568 MONUMNT_TP 3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21013 | 116.16 | 527865 CUNNIGHM_N 6 230 527867 CUNNIGHM_S 6 230 *1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.14 | 527865 CUNNIGHM_N 6 230 527883 CUNINGHAM3 1 13.8 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21023 | 116.08 | 527865 CUNNIGHM_N 6 230 527963 POTASH_JCT 6 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21023 | 116.02 | 527867 CUNNIGHM_S 6 230 527894 HOBBS_INT 6 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21025 | 116.35 | 527894 HOBBS_INT 6 230 527903 HOBBS_PLT3 1 18.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.2102 | 116.23 | 527896 HOBBS_INT 7 345 3WXFMR HICO 68759-1 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 115.8 | 527965 KIOWA 7 345 528027 RDRUNNER 7 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21028 | 115.81 | 528015 PHANTOM 7 345 528027 RDRUNNER 7 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.11 | 528024 RR_SVC_HV 3 115 528021 RDRUNNR_SVC1 15.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.25 | 528024 RR_SVC_HV 3 115 528025 RDRUNNER 3 115 Z1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 115.81 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.08 | 528025 RDRUNNER 3 115 587990 GEN-2016-121 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.14 | 528222 CHINA_DRAW 3 115 528225 CD_SVC_HV 3 115 Z1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 115.82 | 528341 LE-SANANDRS3 115 528627 LE-TXACO_TP3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21024 | 116.06 | 528394 QUAHADA 3 115 528396 XTO_BIGEDDY3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.01 | 528552 OIL_CENTER 3 115 528554 COOPER_RNCH3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.02 | 528554 COOPER_RNCH3 115 528581 BYRD_TP 3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.05 | 528568 MONUMNT_TP 3 115 528581 BYRD_TP 3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.04 | 528596 CARDINAL 3 115 528605 TARGA 3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.06 | 528603 NA_ENRICH 3 115 528605 TARGA 3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.11 | 528617 LE-WAITS 2 69.0 528325 LE-WAITS 3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.03 | 528617 LE-WAITS 2 69.0 528714 LE-FORT_SW 2 69.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21028 | 116.05 | 528618 LE-LOVINTON2 69.0 528334 LE-NRTH_INT3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.42 | 528626 LE-PLNSINT 2 69.0 526928 PLAINS_INT 3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.42 | 528626 LE-PLNSINT 2 69.0 528709 LE-PLNSGOAB2 69.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.05 | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.11 | 528669 LE-STKLDRTP2 69.0 528740 LE-PLANS_SW2 69.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.3 | 528709 LE-PLNSGOAB2 69.0 528740 LE-PLANS_SW2 69.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.05 | 528709 LE-PLNSGOAB2 69.0 528747 LE-ALLRED 2 69.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.03 | 528714 LE-FORT_SW 2 69.0 528718 LE-NEWTEX 2 69.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.11 | 528735 LE-PLAINSUB2 69.0 528740 LE-PLANS_SW2 69.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.03 | 528775 LE-ERF 3 115 528779 LE-TALLCOTN3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21016 | 115.79 | 530583 POSTROCK7 345 560082 G16-050-TAP 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 115.81 | 531213 SANTAFE3 115 531408 PIERCVL3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21025 | 116.04 | 531501 BUCKNER7 345 531502 CIMRRN 7 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21025 | 116.04 | 531502 CIMRRN 7 345 531503 CIMRRN 1 34.5 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21014 | 115.75 | 531510 HARBNGR3 115 3WXFMR HARBGR345 _1 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21026 | 116.06 | 532663 LEC U5 24.0 532854 LEC U5 6 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21033 | 116.04 | 532794 ROSEHIL7 345 560053 G15052_T 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21037 | 116.03 | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21026 | 116.06 | 532853 LAWHILL6 230 532854 LEC U5 6 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21025 | 116.01 | 539117 SPRVILL-EHVB 230 539695 SPEARVL6 230 Z1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21025 | 116.02 | 539803 IRONWOOD7 345 3WXFMR IRONWOOD MPT 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21026 | 116.13 | 542951 HAW G5 1 22.0 543665 HAWTHN5 161 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21026 | 116.17 | 542955 LAC G1 1 22.0 542981 LACYGNE7 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21025 | 116.15 | 542956 LAC G2 1 24.0 542981 LACYGNE7 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21024 | 116.2 | 542957 IAT G1 1 24.0 542982 IATAN 7 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21025 | 116.27 | 542962 IAT G2 1 24.5 542982 IATAN 7 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.03 | 542966 WGARDNR5 161 543105 BULLCRK5 161 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21274 | 115.57 | 560022 CRAWFISH_DR 345 762216 G17-151TAP 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21243 | 116.52 | 560022 CRAWFISH_DR 345 762467 G18-015-TAP 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 112.71 | 560022 CRAWFISH_DR 345 763087 GEN-2018-073 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21355 | 116.84 | 560022 CRAWFISH_DR 345 763215 G18-092-TAP 345 2
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21016 | 115.8 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.45 | 560252 G10-14 345 560253 G10-14-1 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.18 | 560253 G10-14-1 115 560254 G10-14-SUB1 34.5 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.19 | 560253 G10-14-1 115 560255 G10-14-SUB2 34.5 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.04 | 560581 G06-44-2 34.5 523111 NOVUS1 3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.08 | 560582 G06-44-3 34.5 560577 G06-44 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.07 | 560583 G06-44-4 34.5 560577 G06-44 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 115.72 | 560757 ASGI13_02_1 69.0 560758 ASGI13_02_2 34.5 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 115.72 | 560757 ASGI13_02_1 69.0 562731 WHEATLAND 69.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 115.73 | 560763 ASGI13_03_1 115 560761 ASGI13_03_2 34.5 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.16 | 562015 FIREWHEEL1 34.5 523215 FREWHELCOL17 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.16 | 562016 FIREWHEEL2 34.5 523215 FREWHELCOL17 345 2
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 115.71 | 562323 AGI1202&1305 115 562324 AGI1202&1305 34.5 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 115.73 | 562727 LESBIA 115 562728 SANJONTAP 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 115.72 | 562728 SANJONTAP 115 562729 CAPROCKTAP1 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 115.72 | 562730 CAPROCKTAP2 69.0 562729 CAPROCKTAP1 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 115.72 | 562730 CAPROCKTAP2 69.0 562731 WHEATLAND 69.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.15 | 563171 G15082_2 34.5 563170 G15082_1 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 115.78 | P11:13.8:AEPW:COM1-1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 115.79 | P11:13.8:AEPW:COM2-1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 115.79 | P11:13.8:AEPW:COM3-1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 115.78 | P11:18:AEPW:WELSH1-1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 115.79 | P11:18:AEPW:WELSH3-1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 115.78 | P11:24:AEPW:PIRKEY 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 115.68 | P11:24:AEPW:SWS3-1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 115.74 | P11:24:AEPW:TURKCOAL
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.2104 | 116.11 | P12:138:AEPW-OMPA:DUNCAN-4:OMDUNCN4
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.02 | P12:138:AEPW:112GORE4:L.E.S.-4
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21029 | 116.05 | P12:138:AEPW:112GORE4:SNYDER-4
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21029 | 116.05 | 5841_Dup1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21037 | 115.37 | 584560 GEN-2015-014 115 584561 G15-014XFMR1 34.5 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21035 | 116.08 | P12:138:AEPW:SANTAFE:DUNCAN-4
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.08 | 587991 G16-121XFMR1 34.5 587990 GEN-2016-121 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.01 | 588480 A16-010_SUB 115 3WXFMR A16-010_SUB 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.2104 | 116.1 | P12:138:AEPW:DUNCAN-4:L.E.S.-4
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 115.46 | 588761 G17-033XFMR1 34.5 588760 GEN-2017-033 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 115.46 | 588765 G17-033XFMR2 34.5 588760 GEN-2017-033 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.02 | 588861 G17-047XFMR1 34.5 588860 GEN-2017-047 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21013 | 115.79 | P12:138:AEPW:ELKCTY-4:CLINTJC4
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.03 | 589381 G17-100XFMR1 34.5 589380 GEN-2017-100 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21028 | 116.07 | P12:138:AEPW:SHERID4:112GORE4
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.2103 | 116.06 | P12:345:AEPW-OKGE:CLARKSV7:MUSKOGE7
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21275 | 117.78 | P12:345:AEPW:L.E.S7:TERRYRD7
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21275 | 117.77 | P12:345:AEPW:L.E.S7:TERRYRD7
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21274 | 117.75 | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21349 | 118.25 | P12:345:AEPW-OKGE:L.E.S.-7:GRACMNT7
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21349 | 118.23 | P12:345:AEPW-OKGE:L.E.S.-7:GRACMNT7
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21333 | 118.8 | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.08 | P22:345:AMMO::LABADIE:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.08 | P22:345:AMMO::LABADIE:2
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.09 | P22:345:AMMO::LABADIE:3
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.08 | P22:345:AMMO::LABADIE:4
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.07 | P22:345:AMMO::RUSHISLAND:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21028 | 116.06 | P22:345:AMMO::RUSHISLAND:2
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21029 | 115.79 | P13:138-13.8:AEPW:COMANC-4_#2
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 115.8 | P13:138-13.8:AEPW:S.W.S.-4
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.20968 | 115.47 | P13:138-230:AEPW:ELKCTY-4
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21028 | 115.79 | P13:138-24:AEPW:PIRKEY 4
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21032 | 115.69 | P13:138-24:AEPW:S.W.S.-4
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21029 | 115.75 | P13:138-24:AEPW:TURK 4
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21044 | 116.11 | P13:138-345:AEPW:L.E.S.-4_#2
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21028 | 116.02 | P12:500:EES-EAI:KEO:WMPEHV
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21029 | 116.14 | P23:500:EES-EAI:KEO:B4941
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21028 | 116.02 | P23:500:EES-EAI:KEO:B4931
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21029 | 116.13 | P23:500:EES-EAI:KEO:B4921
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21028 | 116.07 | P23:500:EES-EAI:INDEP2:B6126
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21028 | 116.06 | P23:500:EES-EAI:PD:INDEP2:LN:FK479
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21029 | 115.79 | P13:345-18:AEPW:WELSH 7_#1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21029 | 115.79 | P13:345-18:AEPW:WELSH 7_#3
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 115.79 | P13:69-13.8:AEPW:COMANC-2
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.08 | P11:024:DPC:ALMA2:6
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.04 | P11:18:ITCM:EMERYGT1:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.05 | P11:18:ITCM:EMERYGT2:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.05 | P11:161:ITCM:MGS CT1:1C
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.05 | P11:161:ITCM:MGS CT2:2C
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21025 | 116.06 | 652537 WHITE 3 345 659286 DEERCREK-BE3 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21026 | 116.02 | 652568 GROTONSOUTH7 115 659275 GROTON_G-BE7 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21025 | 116.06 | 659286 DEERCREK-BE3 345 3WXFMR DEERCRK KU1A 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.05 | 672601 BD 4 230 672306 BD 6G 18.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.05 | 672610 POPLAR 4 230 672310 POPLAR 1G 18.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.05 | 672610 POPLAR 4 230 672311 POPLAR 2G 18.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.04 | 672621 SHAND 4 230 672321 SHAND 1G 18.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.03 | 672649 CODETTE 4 230 672650 NIPAWIN 4 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.04 | 672696 BRADA 4 230 672699 NBEC 4 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.12 | P23:345:MDU::COYOTE::5707-5712-5715::::
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.3 | P23:345:MEC:CBEC 905
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.25 | P23:345:MEC:CBEC 908
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21028 | 116.04 | P23:345:MEC:GDMEC 901
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21028 | 116.04 | P23:345:MEC:GDMEC 902
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.06 | P23:345:MEC:GDMEC 908
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.17 | P23:345:MEC:RAUN 0180
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.24 | P23:345:MEC:RAUN 0210
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.18 | P23:345:MEC:LOUISA 954
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21028 | 116.19 | P23:345:MEC:LOUISA 964
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.03 | P21:115:XEL:AUTO-SINGLE:CHEMOLT7:LSPOWER7:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.07 | P21:115:XEL:AUTO-SINGLE:COLVILL7:CANONFLSG7:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.03 | P21:115:XEL:AUTO-SINGLE:FARIBALTP7:FARIBALTGEN:Z
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.13 | P21:230:OTP:AUTO-SINGLE:SQBUTTE4:YNG24:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.12 | P23:345:OTP:CENTER 3:3215(1)
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.12 | P23:345:OTP:CENTER 3:3225(1)
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.06 | P12:230:UMZW:# 687 #: FT IN SD. FT-BG1 LINE FAULT
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.06 | P12:230:UMZW:# 3617 #: FT IN SD. FT-BG2 LINE FAULT
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 114.69 | 760494 GEN-2017-146 230 760498 G17-146-TAP 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 114.68 | 760495 G17-146-XFM1 34.5 760494 GEN-2017-146 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 115.46 | 761356 G17-239-XFMR 34.5 761355 GEN-2017-239 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 115.46 | 761359 G17-239-XFMR 34.5 761355 GEN-2017-239 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 115.63 | 761797 G17-187XFM1 34.5 761796 GEN-2017-187 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 115.63 | 761800 G17-187XFM2 34.5 761796 GEN-2017-187 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 110.67 | 762132 GEN-2017-158 230 763252 G18-099-XFM1 34.5 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 110.67 | 762132 GEN-2017-158 230 763255 G18-099-XFM2 34.5 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 111.27 | 762133 G17-158XFM1 34.5 762132 GEN-2017-158 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 111.27 | 762136 G17-158XFM2 34.5 762132 GEN-2017-158 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 113.54 | 762216 G17-151TAP 345 762217 GEN-2017-151 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21274 | 116.85 | 762216 G17-151TAP 345 762467 G18-015-TAP 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 115.27 | 762218 G17-151XFM1 34.5 762217 GEN-2017-151 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 115.27 | 762221 G17-151XFM2 34.5 762217 GEN-2017-151 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 115.27 | 762224 G17-151XFM3 34.5 762217 GEN-2017-151 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 115.27 | 762227 G17-151XFM4 34.5 762217 GEN-2017-151 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 114.55 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 115.11 | 762461 G18-015-XFM1 34.5 762460 GEN-2018-015 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 115.11 | 762464 G18-015-XFM2 34.5 762460 GEN-2018-015 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21163 | 116.42 | 762467 G18-015-TAP 345 763215 G18-092-TAP 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 113.8 | 763087 GEN-2018-073 345 763088 G18-073-XFM1 34.5 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 114.78 | 763087 GEN-2018-073 345 763091 G18-073-XFM2 34.5 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 110.64 | 763120 GEN-2018-081 230 763121 G18-081-XFM1 34.5 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 112.78 | 763120 GEN-2018-081 230 764011 G19-074-XFM1 34.5 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 112.92 | 763186 GEN-2018-089 230 763187 G18-089-XFM1 34.5 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 113.84 | 763208 GEN-2018-092 345 763215 G18-092-TAP 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 114.77 | 763208 GEN-2018-092 345 763220 G18-092-XFM1 34.5 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 114.77 | 763208 GEN-2018-092 345 763223 G18-092-XFM2 34.5 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 112.23 | 763241 GEN-2018-097 230 763242 G18-097-XFM1 34.5 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 113.15 | 763241 GEN-2018-097 230 763296 G18-111-XFM1 34.5 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 112.51 | 763241 GEN-2018-097 230 763307 G18-112-XFM1 34.5 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 112.51 | 763241 GEN-2018-097 230 763310 G18-112-XFM2 34.5 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 112.23 | 763241 GEN-2018-097 230 763395 G18-124-XFM1 34.5 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 112.23 | 763241 GEN-2018-097 230 763398 G18-124-XFM2 34.5 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 115.66 | 763318 GEN-2018-115 345 763319 G18-115-XFM1 34.5 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 112 | 763483 GEN-2019-003 230 763484 G19-003-XFM1 34.5 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 114.56 | 763483 GEN-2019-003 230 763605 G19-021-XFM1 34.5 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 115.46 | 763516 GEN-2019-011 345 763517 G19-011-XFM1 34.5 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 115.55 | 763879 GEN-2019-056 115 763880 G19-056XFM1 34.5 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.20993 | 116.19 | P42:345:OKGE:SB_BVTY7305
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21011 | 115.75 | P23:345:WERE:BUFF_345-534::
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21011 | 115.75 | P23:345:WERE:BUFF_345-543::
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21023 | 116.23 | P23:345:WERE:JEC_345-15::
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21022 | 116.18 | P23:345:WERE:JEC_345-16::
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21023 | 116.22 | P23:345:WERE:JEC_345-19::
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21023 | 116.22 | P23:345:WERE:JEC_345-20::
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.39 | P23:345:WERE:WOLF_345-50::
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.39 | P23:345:WERE:WOLF_345-60::
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21029 | 115.8 | P42:345:AEPW:WELSH CB 10620 NBTB+FAULT
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21028 | 115.79 | P41:345:AEPW:WELSH CB 10630 NBTB+FAULT
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 115.79 | P41:345:AEPW:WELSH CB 11670 NBTB+FAULT
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21039 | 115.78 | P41:345:AEPW:WELSH CB 11680 NBTB+FAULT
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 115.78 | P41:345:AEPW:WELSH CB 12540 NBTB+FAULT
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21333 | 117.33 | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21381 | 118.58 | P42:345:AEPW:LAWTON EASTSIDE CB 3413A NBTB+FAULT
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21416 | 118.94 | P42:345:AEPW:LAWTON EASTSIDE CB 3425A NBTB+FAULT
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21346 | 118.96 | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21275 | 117.77 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21275 | 117.77 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21275 | 117.74 | P42:345:AEPW:TERRYRD_CB_3421A_NBTB
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21026 | 116.18 | P23:345:KCPL:LACYGNE_R2-5::LACYGU2-LACYGNE-STILWELL
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21026 | 115.82 | P45:345:UMZW:# 1328 #: GI IN NE.
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21029 | 115.8 | P23:345:AEPW:WELSH CB 10620 NBTB
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21028 | 115.79 | P23:345:AEPW:WELSH CB 10630 NBTB
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 115.79 | P23:345:AEPW:WELSH CB 11670 NBTB
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21039 | 115.78 | P23:345:AEPW:WELSH CB 11680 NBTB
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 115.78 | P23:345:AEPW:WELSH CB 12540 NBTB
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21333 | 117.74 | P23:345:AEPW:OKLAUNION CB 3401A NBTB
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21381 | 118.58 | P23:345:AEPW:LAWTON EASTSIDE CB 3413A NBTB
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21416 | 118.94 | P23:345:AEPW:LAWTON EASTSIDE CB 3425A NBTB
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21346 | 118.96 | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21275 | 117.77 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21275 | 117.77 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21275 | 117.74 | P23:345:AEPW:TERRYRD_CB_3421A_NBTB
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.05 | P11:161:GMO:DOGWOOD_COMBINED_CYCLE_UNIT_OUTAGE
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.06 | P11:115:SUNC:GARDENCITY_S2:97:531459(2)
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21013 | 115.77 | P12:345:PWT:BUFF-THIS_345_1::
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21013 | 115.77 | P12:345:PWT:BUFF-THIS_345_2::
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21014 | 115.83 | P12:345:PWT:THIS-DGRS_345_1::FUTURE
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21014 | 115.83 | P12:345:PWT:THIS-DGRS_345_2::FUTURE
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21037 | 116.06 | P12:069:WFEC:ANADRKO_WATONGA
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21292 | 117.97 | P23:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21547 | 120.4 | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21292 | 117.97 | P42:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB+FAULT
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21547 | 120.4 | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.20561 | 114.13 | P42:345:OKGE:SB_BVTY7315_PRE19S
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.20996 | 115.62 | P23:345:SUNC:MO_BRK182
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.20996 | 115.62 | P23:345:SUNC:MO_BRK382
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.20992 | 115.79 | P23:345:SUNC:MO_BRK188
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21146 | 116.06 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21029 | 115.79 | P12:138-13.8:AEPW:COMANC-4_#1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.20968 | 115.47 | P12:230:AEPW:ELKCITY6:CHISHOLM6
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.2114 | 116.62 | P12:230:AEPW:SWEETWT6:CHISHOLM6
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997713 ABBXNL844501 230 1 |  | 553 | 0.34286 | 157.44 | 525531 TOLK 6 230 3WXFMR TOLK 6 2
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21029 | 116.18 | P23:345:KCPL-WERE:237LACYGNE_R1-6::LACYGU1-LACYGNE-NEOSHO
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21026 | 116.06 | P11:230:WERE:LECU5_GEN::
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.08 | P11:161:GMO:DOGWOOD_COMBINED_CYCLE_UNIT_OUTAGE_1_1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.02 | P11:20:KACY:NEARMAN N1::N1 OUT OF SERVICE:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21026 | 116.02 | P12:69:KACY:NMGEN-NMISOBUS::NEARMAN N1-NM ISOBUS OPEN:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21026 | 116.02 | P13:20-161:KACY:NEARMAN5-NMISOBUS:NAMEPLATE:NEARMAN N1 GSU:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21026 | 116.02 | P21:20:KACY:546702NMGENN1-546703NMISOBUSC1::::
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.23 | P11:115:SPS:HOBBS1&3:145MW::::
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21033 | 114.72 | P11:115:SPS:MUSTANG1&3:153MW::::
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21284 | 118.23 | P12:230:SPS:K37::1_TOLK_LAMB:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21048 | 116.06 | P12:230:SPS:K43::1_PRNGLE_HARR_E:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.2103 | 115.81 | P12:230:SPS:K44::1_EPLNT_HARRW:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21042 | 116.22 | P12:115:SPS:T04::1_TRBLNC_CASTRO:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21048 | 116.02 | P12:115:SPS:T06::1_SPRMN_PRNGLE:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.5 | P12:115:SPS:T21::1_GRSSLND_GRAHAM:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.05 | P12:115:SPS:T24B::1_RSWLL_BRSHRF:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21028 | 116.05 | P12:115:SPS:T26::1_CHAVES_RSWLCTY:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21149 | 116.45 | P12:115:SPS:T28A::1_LAMTON_PLANTX:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21073 | 116.02 | P12:115:SPS:T29::1_LAMTON_HALECTR:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21198 | 117.27 | P12:115:SPS:T30::1_LAMB_HOCKLY:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21198 | 116.37 | P12:115:SPS:T31::1_HOCKLY_SUNDWN:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21023 | 116.06 | P12:115:SPS:T35::1_TERRY_YOAKUM:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21028 | 116.78 | P12:115:SPS:T45::1_NORRIS_OASIS:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21026 | 115.82 | P12:115:SPS:T57::1_MUSTG_SEGRVS:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21154 | 116.03 | P12:115:SPS:T58::1_HERFRD_CARGIL:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21154 | 116.57 | P12:115:SPS:T59::1_CARGIL_CURRY:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.02 | P12:115:SPS:T64::1_RNDALL_PULLMN:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21124 | 116.38 | P12:115:SPS:T67::1_HAPPY_KRESS:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21032 | 115.77 | P12:115:SPS:T68::1_TUCO_FLOYD:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21028 | 115.81 | P12:115:SPS:T69::1_LUBBE_CROSBY:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.02 | P12:115:SPS:T70::1_COLTR_S_GORG:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21022 | 116.63 | P12:115:SPS:T71::1_CRLSLE_YUMA:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21036 | 116.1 | P12:115:SPS:T81::1_COX_FLOYD:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.26 | P12:115:SPS:T83::1_SP-FKFD_ALLEN:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21022 | 116.44 | P12:115:SPS:T89::1_DC_N_HIGG:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.07 | P12:115:SPS:T91::1_HIGG_RUSSELL:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21032 | 116.02 | P12:115:SPS:V01::1_MOOREW_RVRVIEW:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21049 | 116.07 | P12:115:SPS:V04::1_EPLANT_RNDALL:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21041 | 116.06 | P12:115:SPS:V07::1_COX_HALECTR:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21141 | 116.23 | P12:115:SPS:V09::1_HALECTR_PLANTX:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21026 | 116.21 | P12:115:SPS:V12::1_PLANTX_BAILEY:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.03 | P12:115:SPS:V15::1_TUCO_INDANA:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.20991 | 116.16 | P12:115:SPS:V24::1_WOLFTH_TERRY:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21045 | 116.07 | P12:115:SPS:V26::1_RSWLL_EDDY_N:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.4 | P12:115:SPS:V33::1_LUBBS_LYNN:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21132 | 117.14 | P12:115:SPS:V37::1_CASTRO_PLANTX:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21028 | 116.05 | P12:115:SPS:V44::1_COLTR_OWENS:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.16 | P12:115:SPS:V46::1_ALLEN_WHEELCK:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21029 | 116.5 | P12:115:SPS:V49::1_YOAKUM_SHLCO2:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.2107 | 116.68 | P12:115:SPS:V55::1_SUNDWN_TERRY:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.2104 | 116.59 | P12:115:SPS:V56::1_COCHRAN_SUNDWN:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.09 | P12:115:SPS:V62::1_CRLSLE_INDANA:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.2104 | 116.07 | P12:115:SPS:V78::2_CURRY_RSVLT:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21025 | 116.19 | P12:115:SPS:V81::1_LE-WAIT_LE-LVN:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21028 | 116.06 | P12:115:SPS:V95::1_DC_N_SHLCO2:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.02 | P12:115:SPS:W11::1_DC_S_SMINLE:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.03 | P12:115:SPS:W12::1_SMINLE_DOSS:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.1 | P12:115:SPS:W14::1_SMINLE_GAINES:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.03 | P12:115:SPS:W26::1_CUNGHM_OILCNTR:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.61 | P12:115:SPS:W32::1_PRMTR_FE-CLSIN:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21024 | 116.26 | P12:115:SPS:W35::1_GAINES_JNSDRW:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21219 | 116.59 | P12:115:SPS:W40::1_WCANYON_TRBLNC:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21055 | 116.11 | P12:115:SPS:W52::1_NEWHART_KRESS:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.67 | P12:115:SPS:W58::1_NORTON_LOPEZ:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.25 | P12:115:SPS:W59::1_LOPEZ_CMPBLL:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21028 | 116.55 | P12:115:SPS:W62::1_PLSTHL_CURRY:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.2104 | 116.07 | P12:115:SPS:W63::1_PLSTHL_CURRY:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.36 | P12:115:SPS:W64::1_PLSTHL_FE-CLV:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21029 | 116.57 | P12:115:SPS:W65::1_PLSTHL_CURRY:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.23 | P12:115:SPS:W66::1_PORTA_GREYHUND:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21024 | 116.02 | P12:115:SPS:W76::1_QUAHA_PCA:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21219 | 116.1 | P12:115:SPS:W77::1_RNDAL_WCANYON:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21028 | 116.07 | P12:115:SPS:W99::1_CAPITAN_CHAVES:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.05 | P12:115:SPS:U03::1_CARDNL_NEF:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21023 | 116.53 | P12:115:SPS:U14::1_DC_STH_INKBSN:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21025 | 116.47 | P12:115:SPS:V15::1_INKBSN_LE-WAT:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.2105 | 116.15 | P12:115:SPS:U16::1_BSHLND_OUTPST:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.2105 | 116.16 | P12:115:SPS:U17::1_COLTR_OUTPST:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21034 | 116.26 | P12:115:SPS:U19::1_DEAN_PLAINS:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.2105 | 116.07 | P12:115:SPS:U23::1_COLTR_HILSDE:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.20186 | 124.36 | P42:345:SPS:YOAKUM:J18####:SLG1:EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.20186 | 124.36 | P43:345:SPS:YOAKUM:TF#####:SLG:EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.20186 | 124.36 | P42:345:SPS:YOAKUM:J17####:SLG:EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.20186 | 124.36 | P42:345:SPS:YOAKUM:J18####:SLG2:EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21026 | 116.06 | P11:18:HAST:::EGYCTR2G WEC2_LOSS OF WEC 2 GEN_:HV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21026 | 116.06 | P13:18-115:HAST:::EGYCNTR7 XFMR G2WEC 2 GSU_:HV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.08 | P11:161:GMO:DOGWOOD-COMBINED-CYCLE-UNIT-OUTA:::HV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21029 | 116.18 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21026 | 116.18 | P23:345:KCPL:LACYGNE-R2-5:::EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21023 | 116.23 | P11:230:WERE:JECU1-GEN:::HV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21026 | 116.06 | P11:230:WERE:LECU5-GEN:::HV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21023 | 116.23 | P11:345:WERE:JECU2-GEN:::EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21023 | 116.22 | P11:345:WERE:JECU3-GEN:::EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.4 | P11:345:WERE:WOLFU1-GEN:::EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21013 | 115.77 | P12:345:PWT:BUFF-THIS-345-1:::EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21013 | 115.77 | P12:345:PWT:BUFF-THIS-345-2:::EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21011 | 115.75 | P23:345:WERE:BUFF-345-534:::EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21011 | 115.75 | P23:345:WERE:BUFF-345-543:::EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21023 | 116.23 | P23:345:WERE:JEC-345-15:::EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21022 | 116.18 | P23:345:WERE:JEC-345-16:::EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21023 | 116.22 | P23:345:WERE:JEC-345-19:::EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21023 | 116.22 | P23:345:WERE:JEC-345-20:::EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.39 | P23:345:WERE:WOLF-345-50:::EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.39 | P23:345:WERE:WOLF-345-60:::EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.34 | P11:022:NPPD:COOPER1G:1:983:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21022 | 116.33 | P11:023:NPPD:GENTLM1G:1:757:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21022 | 116.35 | P11:024:NPPD:GENTLM2G:2:757:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21026 | 116.01 | P11:161:OPPD:N OMA 5G:LT::HV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21026 | 116.01 | P11:161:OPPD:N OMA 5G:::HV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21023 | 116.2 | P13:345:OPPD:NEBCTY1G:::EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21022 | 116.22 | P13:345:OPPD:NEBCTY2G:::EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21026 | 116.01 | P13:161:OPPD:N OMA 5G:::HV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.22 | P22:345:OPPD:S3458 NEBCTY1G:LT::EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21023 | 116.2 | P22:345:OPPD:S3458 NEBCTY1G:::EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.25 | P22:345:OPPD:S3458 NEBCTY2G:LT::EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21022 | 116.22 | P22:345:OPPD:S3458 NEBCTY2G:::EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.22 | P23:345:OPPD:S3458 NEBCTY1G:LT::EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21023 | 116.2 | P23:345:OPPD:S3458 NEBCTY1G:::EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.25 | P23:345:OPPD:S3458 NEBCTY2G:LT::EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21022 | 116.22 | P23:345:OPPD:S3458 NEBCTY2G:::EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 115.8 | P12:115:SUNC:PLYMELL-PIERCEVILLE:::HV::
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21025 | 116.06 | P11:018:UMZB:# 5 #:: DCS IN SD. DEERCREEK_MV::
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21026 | 116.03 | P11:022:UMZB:# 15 #:: LO IN ND. LELAND OLDS 1_MV::
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21025 | 116.07 | P11:020:UMZB:# 16 #:: LO IN ND. LELAND OLDS 2_MV::
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21025 | 116.14 | P11:023:UMZB:# 31 #:: AVS IN ND. ANTELOPE VALLEY 1_MV::
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21025 | 116.14 | P11:023:UMZB:# 32 #:: AVS IN ND. ANTELOPE VALLEY 2_MV::
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21021 | 116.33 | P11:024:UMZB:# 33 #:: LRS IN WY. LARAMIE RIVER STATION 1_MV::
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.06 | P12:230:UMZW:# 687 #:: FT IN SD. FT-BG1 BRANCH FAULT:HV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.06 | P12:230:UMZW:# 3617 #:: FT IN SD. FT-BG2 BRANCH FAULT:HV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.06 | P12:230:UMZW:# 4038 #:: BG-FT IN SD. FAULT FOR TRANSMISSION CIRCUIT (BG-FT).:HV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.06 | P12:230:UMZW:# 4039 #:: BG-FT IN SD. FAULT FOR TRANSMISSION CIRCUIT (BG-FT).:HV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.03 | P13:230:UMZW:# 5135 #:: OA IN SD. FAULT ON TRANSFORMER (2).:HV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.03 | P13:230:UMZW:# 5136 #:: OA IN SD. FAULT ON TRANSFORMER (3).:HV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21026 | 115.82 | P23:345:UMZW:# 2423 #:: GI IN NE. GI 1596 BKR FAULT:EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21026 | 115.82 | P23:345:UMZW:# 2426 #:: GI IN NE. GI 1592 BKR FAULT:EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21026 | 115.82 | P23:345:UMZW:# 2432 #:: GI IN NE. GI 1092 BKR FAULT:EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21026 | 115.82 | P23:345:UMZW:# 2440 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1092 STUCK BKR:EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21026 | 115.82 | P23:345:UMZW:# 2444 #:: GI IN NE. GI-SWEET BRANCH FAULT & GI 1596 STUCK BKR:EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21026 | 115.82 | P23:345:UMZW:# 2446 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1196 STUCK BKR:EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21026 | 115.82 | P42:345:UMZW:# 2413 #:: FT2 IN SD. FT2-LO2 BRANCH FAULT & FT2 2992 STUCK BKR:EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21026 | 115.82 | P42:345:UMZW:# 2415 #:: FT2 IN SD. FT2-GI BRANCH FAULT & FT2 3392 STUCK BKR:EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21031 | 115.74 | P11:138:WFEC:HUGO1:465MW :::
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21026 | 116.02 | P11:138:WFEC:MORLND2:132MW:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21026 | 116.03 | P11:138:WFEC:MORLND3:149MW :::
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21036 | 116.06 | P12:138:WFEC:ANADRKO_CLVLND::::
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.2103 | 116.06 | P12:345:OKGE-AEPW:BKRBKR12::::
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21064 | 116.18 | P12:345:OKGE:BKRBKR21::::
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21083 | 116.26 | P12:345:OKGE:BKRBKR24::::
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21274 | 117.75 | P12:345:OKGE-AEPW:BKRBKR25::::
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.20996 | 115.72 | P12:345:OKGE:BKRBKR336::::
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.20996 | 115.72 | P12:345:OKGE:BKRBKR336_2::::
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21349 | 118.25 | P12:345:OKGE-AEPW:BKRBKR366::::
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21349 | 118.23 | P12:345:OKGE-AEPW:BKRBKR366::::
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21236 | 117.15 | P12:345:OKGE:BKRBKR367::::
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21001 | 115.72 | P12:345:OKGE:BKRBKR4193::::
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21001 | 115.72 | P12:345:OKGE:BKRBKR4194::::
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.02 | P12:345:OKGE:BKRBKR4195::::
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.2099 | 115.76 | P12:345:OKGE-SPS:BKRBKR4201::::
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.2099 | 115.76 | P12:345:OKGE-SPS:BKRBKR4202::::
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21037 | 116.03 | P12:345:OKGE:BKRBKR421::::
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.20994 | 115.6 | P12:345:OKGE:BKRBKR443NEW::::
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.20993 | 115.6 | P12:345:OKGE:BKRBKR443NEW2::::
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21011 | 115.79 | P12:345:OKGE-ITC:BKRBKR502::::
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21011 | 115.79 | P12:345:OKGE-ITC:BKRBKR503::::
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21014 | 115.83 | P12:345:OKGE-ITC:BKRBKR502_1::::
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21014 | 115.83 | P12:345:OKGE-ITC:BKRBKR503_1::::
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21021 | 116.33 | P12:345:OKGE:BKRBKR604::::
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.2102 | 116.37 | P12:345:OKGE:BKRBKR604_2::::
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21029 | 115.82 | P11:345:OKGE:BKRBKR_GSU07::::
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21029 | 115.81 | P11:345:OKGE:BKRBKR_GSU08::::
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21029 | 115.8 | P11:138:OKGE:BKRBKR_GSU21::::
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21025 | 115.83 | P12:138:OKGE:BKRBKR85_MOS1::::
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.20994 | 116.13 | P42:345:OKGE:SB_ARIA7381::::
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21722 | 120.17 | P42:345:OKGE:SB_BVTY7387::::
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21038 | 116.02 | P41:345:OKGE:SB_REUD7381::::
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21037 | 116.03 | P41:345:OKGE:SB_REUD7383::::
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21037 | 116.06 | P41:345:OKGE:SB_REUD7385::::
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.2104 | 116.06 | P42:345:OKGE:SB_REUD7389::::
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21025 | 116.05 | P11:115:SUNC:GARDENCITY_S2:103:531459(2):HV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21025 | 116.07 | P11:115:SUNC:FORTDDODGE_4:157:539670(4):HV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.04 | P11:345:599:CIMARRON1WIND:200:531603(1):EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.47 | P13:115:SUNC:HOLCOMB_GSU:::HV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21025 | 116.05 | P13:115:SUNC:S2_GSU:::HV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21025 | 116.07 | P13:115:SUNC:FORTDODGE_GSU:::HV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21025 | 116.04 | P23:345:SUNC:BU_BRK682:::EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.14 | 300003 1THLG3 24.0 301503 7THOMHLGSU3 345 3
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.01 | 300007 1NM G2 22.0 301537 7NEWMADGSU2 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.01 | 300046 7NEWMAD 345 301537 7NEWMADGSU2 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.14 | 300049 7THOMHL 345 301503 7THOMHLGSU3 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.08 | P11:20:AMMO:1LAB�� G1:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.08 | P11:20:AMMO:1LAB�� G2:2
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.27 | P11:345:AMMO::CALLAWAY:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.08 | P11:345:AMMO::LABADIE:3
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.08 | P11:345:AMMO::LABADIE:4
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.07 | P11:345:AMMO::RUSHISLAND:U1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.07 | P11:345:AMMO::RUSHISLAND:U2
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.06 | P11:138:AMMO::SIOUX:2
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 115.83 | P11:24:CLEC::G1DOLHIL:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.06 | P12:765:AEP:AEP ROCKP-AEP JEFF 765
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 115.78 | P11:HV:EES::PIRKEY 1:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 115.79 | P11:EHV:EES::WELSH3-1:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 115.74 | P11:HV:EES::TURKCOAL:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.25 | P12:EHV:EES::7CALAWY 1:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21028 | 116.02 | 338056 CHALKBLUFFPV 500 338162 8W.MEMPHIS% 500 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21029 | 115.75 | P12:HV:EES::TURK 4%:1(1)
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21029 | 115.79 | P12:EHV:EES::WELSH 7:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21029 | 115.79 | P12:EHV:EES::WELSH 7:1(1)
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21028 | 115.79 | P12:HV:EES::PIRKEY 4:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.2103 | 116.06 | P12:EHV:EES::CLARKSV7!:MUSKOGE7!:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.06 | 344011 7HUGHES 345 344012 7HPW-N 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.08 | 344884 7LABADIE1 345 344894 1LAB G1 20.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.08 | 344885 7LABADIE2 345 344895 1LAB G2 20.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.08 | 344886 7LABADIE3 345 344896 1LAB G3 20.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.08 | 344887 7LABADIE4 345 344897 1LAB G4 20.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.07 | 345667 7RUSH 1 345 345670 1RUSH G1 18.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.06 | 345668 7RUSH 2 345 345671 1RUSH G2 18.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.05 | 345755 4SIOUX 1 138 345756 1SIOUX 1 18.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.05 | 345764 4SIOUX 2 138 345765 1SIOUX 2 18.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.12 | P12:345:MDU::CENTER:COYOTE:1::::
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.12 | P13:345:MDU:COYOTE GSU LOSS:COYOTE::1::::
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.03 | P11:345:MEC:GDMEC CT1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.03 | P11:345:MEC:GDMEC CT2
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.14 | P11:345:MEC:GDMEC ST
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.35 | P11:345:MEC-NPPD:COOPER 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.24 | P11:24:XEL:AUTO-SINGLE:SHERC31G:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.24 | P11:24:XEL:AUTO-SINGLE:SHERC32G:2
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.33 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.16 | P11:20:XEL:AUTO-SINGLE:PRIS31G:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.16 | P11:20:XEL:AUTO-SINGLE:PRIS32G:2
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.2 | P11:22:XEL:AUTO-SINGLE:MNTCE31G:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.16 | P11:20:XEL:AUTO-SINGLE:KING31G:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.02 | P11:13:XEL:AUTO-SINGLE:HBRS73G:9
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.02 | P11:18:XEL:AUTO-SINGLE:BLKD76G:6
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.22 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.22 | P11:22:GRE:AUTO-SINGLE:GRE-COAL42G:2
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.14 | P11:24:OTP:AUTO-SINGLE:BIGSTN1G:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.15 | P11:20:OTP:AUTO-SINGLE:CENTER2G:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.05 | P11:22:OTP:AUTO-SINGLE:CENTER1G:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.13 | P11:24:OTP:AUTO-SINGLE:COYOTE1G:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.05 | P11:24:DPC:AUTO-SINGLE:GENOA53G:3
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.03 | P12:115:XEL:AUTO-SINGLE:CHEMOLT7:LSPOWER7:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.07 | P12:115:XEL:AUTO-SINGLE:COLVILL7:CANONFLSG7:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.03 | P12:115:XEL:AUTO-SINGLE:FARIBALTP7:FARIBALTGEN:Z
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.13 | P12:230:OTP:AUTO-SINGLE:SQBUTTE4:YNG24:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.22 | P13:24-345:XEL:AUTO-SINGLE:SHERC31G:SHERCO3:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.22 | P13:24-345:XEL:AUTO-SINGLE:SHERC32G:SHERCO3:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.3 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.16 | P13:20-345:XEL:AUTO-SINGLE:PRIS31G:PRISLD3:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.16 | P13:20-345:XEL:AUTO-SINGLE:PRIS32G:PRISLD3:2
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.2 | P13:22-345:XEL:AUTO-SINGLE:MNTCE31G:MNTCELO3:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.15 | P13:20-345:XEL:AUTO-SINGLE:KING31G:ASKING3:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.02 | P13:13-115:XEL:AUTO-SINGLE:HBRS73G:HIBRDGE7:9
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.2 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL41G:GRE-COALCR4:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.2 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL42G:GRE-COALCR4:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.13 | P13:230-24:OTP:AUTO-SINGLE:BIGSTON4:BIGSTN1G:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.13 | P13:20-230:OTP:AUTO-SINGLE:CENTER2G:YNG24:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.04 | P13:22-230:OTP:AUTO-SINGLE:CENTER1G:CENTER4:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.12 | P13:24-345:OTP:AUTO-SINGLE:COYOTE1G:COYOTE3:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.05 | P13:24-161:DPC:AUTO-SINGLE:GENOA53G:GENOA5:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.07 | P13:24-161:DPC:AUTO-SINGLE:JPM:ALMA5:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21028 | 116.02 | 38203 J1819 POI 500 337957 8KEO% 500 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21028 | 116.02 | 38203 J1819 POI 500 338056 CHALKBLUFFPV 500 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.13 | P11:115:XEL:RIV COMBINE CYCLE
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.04 | P12:115:XEL:BDS #2 5
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.04 | P11:115:XEL:HBR #6
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.04 | P11:115:XEL:HBR #7
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.16 | P11:115:XEL:HBR #6 7 8
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.16 | P23:345:XEL:8H14 PRI
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.16 | P23:345:XEL:8H17 PRI AS
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.3 | P23:345:XEL:8N28 SHC
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.22 | P23:345:XEL:8N22 SHC
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.22 | P23:345:XEL:8N17 SHC
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.21 | P23:345:XEL:8N8 MNN
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.15 | P23:345:XEL:8P1 KING
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.15 | P23:345:XEL:8P2 KING
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.04 | P23:115:XEL:5P147 IVH AS
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.03 | P11:18:ALTW:AUTO-SINGLE:EMERYST1:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.03 | P11:22:ALTW:AUTO-SINGLE:LANS54G:4
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.17 | P11:22:ALTW:AUTO-SINGLE:ARNOLD1G:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.2 | P11:24:ALTW:AUTO-SINGLE:OTTUMW1G:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.03 | P13:18-161:ALTW:AUTO-SINGLE:EMERYST1:EMERY5:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.03 | P13:22-161:ALTW:AUTO-SINGLE:LANS54G:LANSINGL15:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.16 | P13:22-161:ALTW:AUTO-SINGLE:ARNOLD1G:ARNOLD5:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.19 | P13:24-161:ALTW:AUTO-SINGLE:OTTUMW1G:OTTUMWA5:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.27 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.34 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.19 | P11:22:MEC:AUTO-SINGLE:NEAL3G:3
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.26 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.19 | P11:24:MEC:AUTO-SINGLE:LOUIS31G:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.25 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.3 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.17 | P13:345-22:MEC:AUTO-SINGLE:RAUN3:NEAL3G:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.24 | P13:345-24:MEC:AUTO-SINGLE:RAUN3:NEAL4G:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.18 | P13:345-24:MEC:AUTO-SINGLE:LOUISA3:LOUIS31G:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21023 | 116.23 | P11:230:WERE:JECU1_GEN::
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21023 | 116.23 | P11:345:WERE:JECU2_GEN::
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21023 | 116.22 | P11:345:WERE:JECU3_GEN::
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.4 | P11:345:WERE:WOLFU1_GEN::
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21029 | 116.03 | 511435 SNYDER-4 138 588779 TAP_G17-036 138 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21035 | 116.03 | 511453 DUNCAN-4 138 511552 DUNCHERTP4 138 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21035 | 116.03 | 511455 D.E.S.-4 138 511552 DUNCHERTP4 138 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21035 | 116.02 | 511455 D.E.S.-4 138 529344 OMDUNE-4 138 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 114.98 | 511456 O.K.U.-7 345 588760 GEN-2017-033 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21333 | 117.74 | 511456 O.K.U.-7 345 763215 G18-092-TAP 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21347 | 118.31 | 511468 L.E.S.-7 345 762467 G18-015-TAP 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21244 | 117.72 | 511468 L.E.S.-7 345 763215 G18-092-TAP 345 2
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 115.66 | 511468 L.E.S.-7 345 763318 GEN-2018-115 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21029 | 116.05 | 511488 112GORE4 138 511510 LAIRGST4 138 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.2104 | 116.11 | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21029 | 116.04 | 511500 CACHE4 138 511510 LAIRGST4 138 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21029 | 116.03 | 511500 CACHE4 138 588779 TAP_G17-036 138 2
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21146 | 116.06 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.20361 | 113.09 | 511553 CHISHOLM7 345 523961 POTTER_CO 7 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.20361 | 113.09 | 511553 CHISHOLM7 345 523961 POTTER_CO 7 345 2
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.20733 | 115.5 | 511553 CHISHOLM7 345 755000 WWDBORDT 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.14 | 511557 CHISHOLM6 230 3WXFMR CHISHOLM6 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21041 | 116.02 | 514801 MINCO 7 345 555234 NSUB345 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.20953 | 115.63 | 515375 WWRDEHV7 345 755000 WWDBORDT 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21722 | 120.2 | 515458 BORDER 7 345 560022 CRAWFISH_DR 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21722 | 120.15 | 515458 BORDER 7 345 755000 WWDBORDT 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21037 | 116.02 | 515543 RENFROW7 345 763421 G18-128-TAP 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21024 | 116.12 | 515618 BALKOW 7 345 3WXFMR BALKOW 7 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21024 | 116.13 | 515618 BALKOW 7 345 3WXFMR BALKOW 7 1_Dup1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21033 | 116.04 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.2102 | 116.39 | 515634 PALDR1W7 345 3WXFMR PALO2 _1 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.13 | 515677 BADGER 7 345 563170 G15082_1 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21023 | 116.01 | 521017 ONEY 4 138 521089 WASHITA4 138 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.02 | 522800 MU-TULIA 3 115 525179 TULIA_TP 3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.16 | 522892 MU-BROWNFLD2 69.0 526761 BROWNFLD_TP2 69.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.03 | 523090 TEXAS_CNTY 3 115 589380 GEN-2017-100 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21023 | 116.16 | 523093 HITCHLAND 3 115 523174 GOODWELLWND3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.34 | 523097 HITCHLAND 7 345 523112 NOVUS1 7 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.4 | 523097 HITCHLAND 7 345 523215 FREWHELCOL17 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.20824 | 114.83 | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.45 | 523097 HITCHLAND 7 345 560252 G10-14 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.01 | 523099 TC-DRYTRLS 3 115 588480 A16-010_SUB 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.23 | 523112 NOVUS1 7 345 3WXFMR NOVUS XF2 2
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.04 | 523112 NOVUS1 7 345 3WXFMR XIANA2011198 _1 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21026 | 116.02 | 523118 BUFF_DUNES 7 345 523853 FINNEY 7 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.02 | 523120 COLE 3 115 588860 GEN-2017-047 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21025 | 116.04 | 523172 GWELL_COLL11 34.5 523174 GOODWELLWND3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21025 | 116.04 | 523173 GWELL_COLL21 34.5 523174 GOODWELLWND3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21036 | 116.01 | 523221 XIT_INTG 6 230 3WXFMR SIEM_T126401 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21048 | 116.07 | 523267 PRINGLE 6 230 3WXFMR ENRCO13617-1 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21048 | 116.06 | 523267 PRINGLE 6 230 523979 HARRNG_EST 6 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.2109 | 116.2 | 523309 MOORE_CNTY 6 230 523323 MCDWL_CREEK6 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21062 | 116.12 | 523323 MCDWL_CREEK6 230 523959 POTTER_CO 6 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.20997 | 116.45 | 523959 POTTER_CO 6 230 524010 ROLLHILLS 6 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21843 | 117.19 | 523959 POTTER_CO 6 230 524267 BUSHLAND 6 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.2181 | 118.35 | 523959 POTTER_CO 6 230 525461 NEWHART 6 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.2139 | 121.11 | 523961 POTTER_CO 7 345 3WXFMR WAUK 90343-A 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21025 | 115.74 | 523978 HARRNG_MID 6 230 523979 HARRNG_EST 6 230 @1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.2105 | 116.16 | 524267 BUSHLAND 6 230 3WXFMR WH 7001795 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.22491 | 117.94 | 524267 BUSHLAND 6 230 524623 DEAFSMITH 6 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21015 | 116.44 | 524296 SPNSPUR_WND7 345 524299 SPNSPUR_COL7 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21015 | 116.44 | 524299 SPNSPUR_COL7 345 3WXFMR SPNSPUR_COL7 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21416 | 117.09 | 524415 AMA_SOUTH 6 230 525213 SWISHER 6 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.67 | 524502 NORTON 3 115 524509 FE-TUCMCARI3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21219 | 116.45 | 524575 DS-#25+ 3 115 524597 PANDAHFD 3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21219 | 116.55 | 524575 DS-#25+ 3 115 524630 TIERABLANCA3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.11 | 524604 HEREFRD_SB 2 69.0 524608 HERFRD_STH 2 69.0 *1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.2234 | 122.73 | 524623 DEAFSMITH 6 230 760498 G17-146-TAP 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.52 | 524721 DS-#15&#19+2 69.0 524745 CASTRO_CNTY2 69.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21033 | 116.03 | 524770 PLSNT_HILL 6 230 3WXFMR EFAE1100068A 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.2145 | 121.59 | 524875 OASIS 6 230 524885 SN_JUAN_TAP6 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21101 | 117.16 | 524875 OASIS 6 230 524909 ROOSEVELT 6 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21441 | 121.97 | 524885 SN_JUAN_TAP6 230 527483 CHAVES_CNTY6 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21044 | 116.22 | 524909 ROOSEVELT 6 230 3WXFMR ABB LMM60042 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21721 | 122.19 | 524909 ROOSEVELT 6 230 525531 TOLK 6 230 2
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.77 | 524923 PORTALES 2 69.0 524929 RO-PORT_MTR2 69.0 @1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.42 | 524923 PORTALES 2 69.0 524941 PORTALES#1 2 69.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.66 | 525023 BC-BAIL_MTR2 69.0 525027 BAILEYCO 2 69.0 @1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21132 | 116.55 | 525056 BC-EARTH 3 115 525480 PLANT_X 3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.51 | 525191 KRESS_INT 2 69.0 525203 SW-KRESS 2 69.0 Z1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.6 | 525192 KRESS_INT 3 115 3WXFMR ENRCO 136155 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21328 | 116.83 | 525213 SWISHER 6 230 525461 NEWHART 6 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.15 | 525272 KISER 3 115 3WXFMR VON 13819/1 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.61 | 525326 COX 3 115 3WXFMR ELCO 13474-3 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.61 | 525414 LAMTON 3 115 3WXFMR ASEA MLL9204 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.22646 | 119.68 | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21301 | 118.1 | 525481 PLANT_X 6 230 3WXFMR WH ALM20171 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21975 | 121 | 525481 PLANT_X 6 230 526435 SUNDOWN 6 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.2234 | 121.02 | 525481 PLANT_X 6 230 760498 G17-146-TAP 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21374 | 116.49 | 525481 PLANT_X 6 230 762174 G17-218TAP 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21416 | 116.56 | 525481 PLANT_X 6 230 762174 G17-218TAP 230 2
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.22176 | 121.7 | 525531 TOLK 6 230 525586 NEEDMORE 6 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21284 | 118.23 | 525531 TOLK 6 230 525637 LAMB_CNTY 6 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.23952 | 120.42 | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.2154 | 116.76 | 525531 TOLK 6 230 762174 G17-218TAP 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21576 | 116.82 | 525531 TOLK 6 230 762174 G17-218TAP 230 2
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.34286 | 155.48 | 525549 TOLK 7 345 3WXFMR ABBXNL844501 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.22176 | 121.69 | 525586 NEEDMORE 6 230 526935 YOAKUM 6 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.41 | 525599 LC-SANDHLL+2 69.0 525606 AMHERST 2 69.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.45 | 525606 AMHERST 2 69.0 525613 W_LITTLFLD 2 69.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.46 | 525613 W_LITTLFLD 2 69.0 525635 LAMB_CNTY 2 69.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.42 | 525635 LAMB_CNTY 2 69.0 525650 LC-LTTLFLD+2 69.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21284 | 118.23 | 525637 LAMB_CNTY 6 230 3WXFMR WH ALM20172 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.41 | 525779 FLOYD_CNTY 2 69.0 525790 FLOYDADA_TP2 69.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.29 | 525828 TUCO_INT 3 115 3WXFMR DS F78800913 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.20276 | 118.38 | 525832 TUCO_INT 7 345 526936 YOAKUM_345 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.49 | 526086 SW_6786_N 2 69.0 526087 SW_6786_S 2 69.0 Z1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.49 | 526086 SW_6786_N 2 69.0 526102 SP-HETTLER 2 69.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.56 | 526087 SW_6786_S 2 69.0 526284 PLANTERS 2 69.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.1 | 526160 CARLISLE 3 115 3WXFMR WH RLP38371 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.44 | 526195 QUINCY 3 115 526196 SP-MILWAUKEE 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.34 | 526268 LUBBCK_STH 3 115 3WXFMR NA 70454A 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.6 | 526284 PLANTERS 2 69.0 526297 LUBBCK_EST 2 69.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.2104 | 116.47 | 526424 PACIFIC 3 115 526434 SUNDOWN 3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21023 | 116.06 | 526435 SUNDOWN 6 230 3WXFMR UPDATE LATER _12 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21049 | 118.87 | 526435 SUNDOWN 6 230 526460 AMOCO_SS 6 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21049 | 116.5 | 526460 AMOCO_SS 6 230 526935 YOAKUM 6 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21025 | 116.08 | 526525 WOLFFORTH 6 230 3WXFMR UPDATE LATER _13 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.48 | 526735 TERRY_CNTY 2 69.0 526747 LG-BROWNFLD2 69.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21015 | 118.02 | 526935 YOAKUM 6 230 527028 INK_BASIN 6 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.2145 | 116.3 | 526936 YOAKUM_345 345 3WXFMR SPX WT04221 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.20267 | 126.57 | 526936 YOAKUM_345 345 527896 HOBBS_INT 7 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21004 | 117.39 | 527028 INK_BASIN 6 230 527894 HOBBS_INT 6 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21022 | 116.43 | 527130 DENVER_N 3 115 527286 HIGGEAST 3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21028 | 116.02 | 527149 MUSTANG 6 230 3WXFMR ENRCO 136161 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21043 | 114.01 | 527149 MUSTANG 6 230 527151 GS-MUSTANG 6 230 @1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.29 | 527202 SEAGRAVES 3 115 3WXFMR ABB MLL92408 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.17 | 527212 DIAMONDBACK3 115 3WXFMR HOW 36773714 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21022 | 116.41 | 527286 HIGGEAST 3 115 527363 HIGG 3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21024 | 116.16 | 527325 OXY_WSEM_TP3 115 527362 JOHNSON_DRW3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.15 | 527340 DOSS 3 115 3WXFMR ELCO 13566/1 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.14 | 527345 LEGACY 2 69.0 527350 XTO_ROBRTSN2 69.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.14 | 527346 LEGACY 3 115 3WXFMR VROL 13735-1 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.12 | 527350 XTO_ROBRTSN2 69.0 527355 BOARDMAN 2 69.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.05 | 527355 BOARDMAN 2 69.0 527365 FLANNAGAN 2 69.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.02 | 527360 MAPCO 3 115 527362 JOHNSON_DRW3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.08 | 527362 JOHNSON_DRW3 115 528775 LE-ERF 3 115 @1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.01 | 527370 TENNECO_TAP2 69.0 527371 TENNECO 2 69.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21205 | 116.35 | 527483 CHAVES_CNTY6 230 527799 EDDY_NORTH 6 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.05 | 527508 PRICE 3 115 527509 PRICE_TAP 3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.02 | 527514 CV-PINE 2 69.0 527563 ROSWLL_INT 2 69.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.05 | 527529 RIACBRSH_TP3 115 527533 SW4J795_E 3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.02 | 527529 RIACBRSH_TP3 115 527536 BRASHER 3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.05 | 527533 SW4J795_E 3 115 527564 ROSWLL_INT 3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.06 | 527563 ROSWLL_INT 2 69.0 527575 SW_4702 2 69.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21045 | 116.1 | 527564 ROSWLL_INT 3 115 527597 TWEEDY 3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.06 | 527575 SW_4702 2 69.0 527589 CV-ORCHARD 2 69.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.02 | 527589 CV-ORCHARD 2 69.0 527619 DEXTER_TP 2 69.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21023 | 116.18 | 527653 MILO_WIND 1 34.5 527655 RSVLT_CC_E 7 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21015 | 116.1 | 527654 RSVLT_CC_W 7 345 527655 RSVLT_CC_E 7 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21015 | 116.36 | 527654 RSVLT_CC_W 7 345 527666 RSVLT_COL1 7 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21011 | 116.3 | 527655 RSVLT_CC_E 7 345 527656 CROSSROADS 7 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21015 | 116.36 | 527666 RSVLT_COL1 7 345 3WXFMR RSVLT_COL1 7 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.15 | 527790 EDDY_SVC 1 8.50 527799 EDDY_NORTH 6 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.05 | 527864 CUNNINHAM 3 115 528568 MONUMNT_TP 3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21013 | 116.16 | 527865 CUNNIGHM_N 6 230 527867 CUNNIGHM_S 6 230 *1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.14 | 527865 CUNNIGHM_N 6 230 527883 CUNINGHAM3 1 13.8 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21023 | 116.08 | 527865 CUNNIGHM_N 6 230 527963 POTASH_JCT 6 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21023 | 116.02 | 527867 CUNNIGHM_S 6 230 527894 HOBBS_INT 6 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21025 | 116.35 | 527894 HOBBS_INT 6 230 527903 HOBBS_PLT3 1 18.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.2102 | 116.23 | 527896 HOBBS_INT 7 345 3WXFMR HICO 68759-1 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 115.8 | 527965 KIOWA 7 345 528027 RDRUNNER 7 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21028 | 115.81 | 528015 PHANTOM 7 345 528027 RDRUNNER 7 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.11 | 528024 RR_SVC_HV 3 115 528021 RDRUNNR_SVC1 15.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.25 | 528024 RR_SVC_HV 3 115 528025 RDRUNNER 3 115 Z1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 115.81 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.08 | 528025 RDRUNNER 3 115 587990 GEN-2016-121 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.14 | 528222 CHINA_DRAW 3 115 528225 CD_SVC_HV 3 115 Z1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 115.82 | 528341 LE-SANANDRS3 115 528627 LE-TXACO_TP3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21024 | 116.06 | 528394 QUAHADA 3 115 528396 XTO_BIGEDDY3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.01 | 528552 OIL_CENTER 3 115 528554 COOPER_RNCH3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.02 | 528554 COOPER_RNCH3 115 528581 BYRD_TP 3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.05 | 528568 MONUMNT_TP 3 115 528581 BYRD_TP 3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.04 | 528596 CARDINAL 3 115 528605 TARGA 3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.06 | 528603 NA_ENRICH 3 115 528605 TARGA 3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.11 | 528617 LE-WAITS 2 69.0 528325 LE-WAITS 3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.03 | 528617 LE-WAITS 2 69.0 528714 LE-FORT_SW 2 69.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21028 | 116.05 | 528618 LE-LOVINTON2 69.0 528334 LE-NRTH_INT3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.42 | 528626 LE-PLNSINT 2 69.0 526928 PLAINS_INT 3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.42 | 528626 LE-PLNSINT 2 69.0 528709 LE-PLNSGOAB2 69.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.05 | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.11 | 528669 LE-STKLDRTP2 69.0 528740 LE-PLANS_SW2 69.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.3 | 528709 LE-PLNSGOAB2 69.0 528740 LE-PLANS_SW2 69.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.05 | 528709 LE-PLNSGOAB2 69.0 528747 LE-ALLRED 2 69.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.03 | 528714 LE-FORT_SW 2 69.0 528718 LE-NEWTEX 2 69.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.11 | 528735 LE-PLAINSUB2 69.0 528740 LE-PLANS_SW2 69.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.03 | 528775 LE-ERF 3 115 528779 LE-TALLCOTN3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21016 | 115.79 | 530583 POSTROCK7 345 560082 G16-050-TAP 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 115.81 | 531213 SANTAFE3 115 531408 PIERCVL3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21025 | 116.04 | 531501 BUCKNER7 345 531502 CIMRRN 7 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21025 | 116.04 | 531502 CIMRRN 7 345 531503 CIMRRN 1 34.5 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21014 | 115.75 | 531510 HARBNGR3 115 3WXFMR HARBGR345 _1 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21026 | 116.06 | 532663 LEC U5 24.0 532854 LEC U5 6 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21033 | 116.04 | 532794 ROSEHIL7 345 560053 G15052_T 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21037 | 116.03 | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21026 | 116.06 | 532853 LAWHILL6 230 532854 LEC U5 6 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21025 | 116.01 | 539117 SPRVILL-EHVB 230 539695 SPEARVL6 230 Z1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21025 | 116.02 | 539803 IRONWOOD7 345 3WXFMR IRONWOOD MPT 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21026 | 116.13 | 542951 HAW G5 1 22.0 543665 HAWTHN5 161 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21026 | 116.17 | 542955 LAC G1 1 22.0 542981 LACYGNE7 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21025 | 116.15 | 542956 LAC G2 1 24.0 542981 LACYGNE7 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21024 | 116.2 | 542957 IAT G1 1 24.0 542982 IATAN 7 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21025 | 116.27 | 542962 IAT G2 1 24.5 542982 IATAN 7 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.03 | 542966 WGARDNR5 161 543105 BULLCRK5 161 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21274 | 115.57 | 560022 CRAWFISH_DR 345 762216 G17-151TAP 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21243 | 116.52 | 560022 CRAWFISH_DR 345 762467 G18-015-TAP 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 112.71 | 560022 CRAWFISH_DR 345 763087 GEN-2018-073 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21355 | 116.84 | 560022 CRAWFISH_DR 345 763215 G18-092-TAP 345 2
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21016 | 115.8 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.45 | 560252 G10-14 345 560253 G10-14-1 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.18 | 560253 G10-14-1 115 560254 G10-14-SUB1 34.5 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.19 | 560253 G10-14-1 115 560255 G10-14-SUB2 34.5 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.04 | 560581 G06-44-2 34.5 523111 NOVUS1 3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.08 | 560582 G06-44-3 34.5 560577 G06-44 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.07 | 560583 G06-44-4 34.5 560577 G06-44 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 115.72 | 560757 ASGI13_02_1 69.0 560758 ASGI13_02_2 34.5 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 115.72 | 560757 ASGI13_02_1 69.0 562731 WHEATLAND 69.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 115.73 | 560763 ASGI13_03_1 115 560761 ASGI13_03_2 34.5 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.16 | 562015 FIREWHEEL1 34.5 523215 FREWHELCOL17 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.16 | 562016 FIREWHEEL2 34.5 523215 FREWHELCOL17 345 2
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 115.71 | 562323 AGI1202&1305 115 562324 AGI1202&1305 34.5 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 115.73 | 562727 LESBIA 115 562728 SANJONTAP 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 115.72 | 562728 SANJONTAP 115 562729 CAPROCKTAP1 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 115.72 | 562730 CAPROCKTAP2 69.0 562729 CAPROCKTAP1 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 115.72 | 562730 CAPROCKTAP2 69.0 562731 WHEATLAND 69.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.15 | 563171 G15082_2 34.5 563170 G15082_1 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 115.78 | P11:13.8:AEPW:COM1-1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 115.79 | P11:13.8:AEPW:COM2-1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 115.79 | P11:13.8:AEPW:COM3-1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 115.78 | P11:18:AEPW:WELSH1-1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 115.79 | P11:18:AEPW:WELSH3-1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 115.78 | P11:24:AEPW:PIRKEY 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 115.68 | P11:24:AEPW:SWS3-1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 115.74 | P11:24:AEPW:TURKCOAL
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.2104 | 116.11 | P12:138:AEPW-OMPA:DUNCAN-4:OMDUNCN4
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.02 | P12:138:AEPW:112GORE4:L.E.S.-4
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21029 | 116.05 | P12:138:AEPW:112GORE4:SNYDER-4
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21029 | 116.05 | 5841_Dup1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21037 | 115.37 | 584560 GEN-2015-014 115 584561 G15-014XFMR1 34.5 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21035 | 116.08 | P12:138:AEPW:SANTAFE:DUNCAN-4
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.08 | 587991 G16-121XFMR1 34.5 587990 GEN-2016-121 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.01 | 588480 A16-010_SUB 115 3WXFMR A16-010_SUB 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.2104 | 116.1 | P12:138:AEPW:DUNCAN-4:L.E.S.-4
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 115.46 | 588761 G17-033XFMR1 34.5 588760 GEN-2017-033 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 115.46 | 588765 G17-033XFMR2 34.5 588760 GEN-2017-033 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.02 | 588861 G17-047XFMR1 34.5 588860 GEN-2017-047 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21013 | 115.79 | P12:138:AEPW:ELKCTY-4:CLINTJC4
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.03 | 589381 G17-100XFMR1 34.5 589380 GEN-2017-100 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21028 | 116.07 | P12:138:AEPW:SHERID4:112GORE4
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.2103 | 116.06 | P12:345:AEPW-OKGE:CLARKSV7:MUSKOGE7
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21275 | 117.78 | P12:345:AEPW:L.E.S7:TERRYRD7
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21275 | 117.77 | P12:345:AEPW:L.E.S7:TERRYRD7
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21274 | 117.75 | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21349 | 118.25 | P12:345:AEPW-OKGE:L.E.S.-7:GRACMNT7
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21349 | 118.23 | P12:345:AEPW-OKGE:L.E.S.-7:GRACMNT7
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21333 | 118.8 | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.08 | P22:345:AMMO::LABADIE:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.08 | P22:345:AMMO::LABADIE:2
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.09 | P22:345:AMMO::LABADIE:3
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.08 | P22:345:AMMO::LABADIE:4
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.07 | P22:345:AMMO::RUSHISLAND:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21028 | 116.06 | P22:345:AMMO::RUSHISLAND:2
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21029 | 115.79 | P13:138-13.8:AEPW:COMANC-4_#2
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 115.8 | P13:138-13.8:AEPW:S.W.S.-4
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.20968 | 115.47 | P13:138-230:AEPW:ELKCTY-4
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21028 | 115.79 | P13:138-24:AEPW:PIRKEY 4
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21032 | 115.69 | P13:138-24:AEPW:S.W.S.-4
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21029 | 115.75 | P13:138-24:AEPW:TURK 4
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21044 | 116.11 | P13:138-345:AEPW:L.E.S.-4_#2
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21028 | 116.02 | P12:500:EES-EAI:KEO:WMPEHV
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21029 | 116.14 | P23:500:EES-EAI:KEO:B4941
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21028 | 116.02 | P23:500:EES-EAI:KEO:B4931
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21029 | 116.13 | P23:500:EES-EAI:KEO:B4921
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21028 | 116.07 | P23:500:EES-EAI:INDEP2:B6126
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21028 | 116.06 | P23:500:EES-EAI:PD:INDEP2:LN:FK479
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21029 | 115.79 | P13:345-18:AEPW:WELSH 7_#1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21029 | 115.79 | P13:345-18:AEPW:WELSH 7_#3
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 115.79 | P13:69-13.8:AEPW:COMANC-2
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.08 | P11:024:DPC:ALMA2:6
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.04 | P11:18:ITCM:EMERYGT1:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.05 | P11:18:ITCM:EMERYGT2:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.05 | P11:161:ITCM:MGS CT1:1C
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.05 | P11:161:ITCM:MGS CT2:2C
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21025 | 116.06 | 652537 WHITE 3 345 659286 DEERCREK-BE3 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21026 | 116.02 | 652568 GROTONSOUTH7 115 659275 GROTON_G-BE7 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21025 | 116.06 | 659286 DEERCREK-BE3 345 3WXFMR DEERCRK KU1A 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.05 | 672601 BD 4 230 672306 BD 6G 18.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.05 | 672610 POPLAR 4 230 672310 POPLAR 1G 18.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.05 | 672610 POPLAR 4 230 672311 POPLAR 2G 18.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.04 | 672621 SHAND 4 230 672321 SHAND 1G 18.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.03 | 672649 CODETTE 4 230 672650 NIPAWIN 4 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.04 | 672696 BRADA 4 230 672699 NBEC 4 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.12 | P23:345:MDU::COYOTE::5707-5712-5715::::
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.3 | P23:345:MEC:CBEC 905
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.25 | P23:345:MEC:CBEC 908
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21028 | 116.04 | P23:345:MEC:GDMEC 901
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21028 | 116.04 | P23:345:MEC:GDMEC 902
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.06 | P23:345:MEC:GDMEC 908
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.17 | P23:345:MEC:RAUN 0180
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.24 | P23:345:MEC:RAUN 0210
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.18 | P23:345:MEC:LOUISA 954
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21028 | 116.19 | P23:345:MEC:LOUISA 964
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.03 | P21:115:XEL:AUTO-SINGLE:CHEMOLT7:LSPOWER7:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.07 | P21:115:XEL:AUTO-SINGLE:COLVILL7:CANONFLSG7:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.03 | P21:115:XEL:AUTO-SINGLE:FARIBALTP7:FARIBALTGEN:Z
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.13 | P21:230:OTP:AUTO-SINGLE:SQBUTTE4:YNG24:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.12 | P23:345:OTP:CENTER 3:3215(1)
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.12 | P23:345:OTP:CENTER 3:3225(1)
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.06 | P12:230:UMZW:# 687 #: FT IN SD. FT-BG1 LINE FAULT
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.06 | P12:230:UMZW:# 3617 #: FT IN SD. FT-BG2 LINE FAULT
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 114.69 | 760494 GEN-2017-146 230 760498 G17-146-TAP 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 114.68 | 760495 G17-146-XFM1 34.5 760494 GEN-2017-146 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 115.46 | 761356 G17-239-XFMR 34.5 761355 GEN-2017-239 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 115.46 | 761359 G17-239-XFMR 34.5 761355 GEN-2017-239 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 115.63 | 761797 G17-187XFM1 34.5 761796 GEN-2017-187 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 115.63 | 761800 G17-187XFM2 34.5 761796 GEN-2017-187 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 110.67 | 762132 GEN-2017-158 230 763252 G18-099-XFM1 34.5 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 110.67 | 762132 GEN-2017-158 230 763255 G18-099-XFM2 34.5 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 111.27 | 762133 G17-158XFM1 34.5 762132 GEN-2017-158 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 111.27 | 762136 G17-158XFM2 34.5 762132 GEN-2017-158 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 113.54 | 762216 G17-151TAP 345 762217 GEN-2017-151 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21274 | 116.85 | 762216 G17-151TAP 345 762467 G18-015-TAP 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 115.27 | 762218 G17-151XFM1 34.5 762217 GEN-2017-151 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 115.27 | 762221 G17-151XFM2 34.5 762217 GEN-2017-151 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 115.27 | 762224 G17-151XFM3 34.5 762217 GEN-2017-151 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 115.27 | 762227 G17-151XFM4 34.5 762217 GEN-2017-151 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 114.55 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 115.11 | 762461 G18-015-XFM1 34.5 762460 GEN-2018-015 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 115.11 | 762464 G18-015-XFM2 34.5 762460 GEN-2018-015 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21163 | 116.42 | 762467 G18-015-TAP 345 763215 G18-092-TAP 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 113.8 | 763087 GEN-2018-073 345 763088 G18-073-XFM1 34.5 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 114.78 | 763087 GEN-2018-073 345 763091 G18-073-XFM2 34.5 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 110.64 | 763120 GEN-2018-081 230 763121 G18-081-XFM1 34.5 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 112.78 | 763120 GEN-2018-081 230 764011 G19-074-XFM1 34.5 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 112.92 | 763186 GEN-2018-089 230 763187 G18-089-XFM1 34.5 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 113.84 | 763208 GEN-2018-092 345 763215 G18-092-TAP 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 114.77 | 763208 GEN-2018-092 345 763220 G18-092-XFM1 34.5 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 114.77 | 763208 GEN-2018-092 345 763223 G18-092-XFM2 34.5 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 112.23 | 763241 GEN-2018-097 230 763242 G18-097-XFM1 34.5 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 113.15 | 763241 GEN-2018-097 230 763296 G18-111-XFM1 34.5 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 112.51 | 763241 GEN-2018-097 230 763307 G18-112-XFM1 34.5 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 112.51 | 763241 GEN-2018-097 230 763310 G18-112-XFM2 34.5 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 112.23 | 763241 GEN-2018-097 230 763395 G18-124-XFM1 34.5 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 112.23 | 763241 GEN-2018-097 230 763398 G18-124-XFM2 34.5 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 115.66 | 763318 GEN-2018-115 345 763319 G18-115-XFM1 34.5 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 112 | 763483 GEN-2019-003 230 763484 G19-003-XFM1 34.5 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 114.56 | 763483 GEN-2019-003 230 763605 G19-021-XFM1 34.5 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 115.46 | 763516 GEN-2019-011 345 763517 G19-011-XFM1 34.5 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 115.55 | 763879 GEN-2019-056 115 763880 G19-056XFM1 34.5 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.20993 | 116.19 | P42:345:OKGE:SB_BVTY7305
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21011 | 115.75 | P23:345:WERE:BUFF_345-534::
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21011 | 115.75 | P23:345:WERE:BUFF_345-543::
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21023 | 116.23 | P23:345:WERE:JEC_345-15::
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21022 | 116.18 | P23:345:WERE:JEC_345-16::
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21023 | 116.22 | P23:345:WERE:JEC_345-19::
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21023 | 116.22 | P23:345:WERE:JEC_345-20::
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.39 | P23:345:WERE:WOLF_345-50::
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.39 | P23:345:WERE:WOLF_345-60::
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21029 | 115.8 | P42:345:AEPW:WELSH CB 10620 NBTB+FAULT
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21028 | 115.79 | P41:345:AEPW:WELSH CB 10630 NBTB+FAULT
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 115.79 | P41:345:AEPW:WELSH CB 11670 NBTB+FAULT
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21039 | 115.78 | P41:345:AEPW:WELSH CB 11680 NBTB+FAULT
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 115.78 | P41:345:AEPW:WELSH CB 12540 NBTB+FAULT
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21333 | 117.33 | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21381 | 118.58 | P42:345:AEPW:LAWTON EASTSIDE CB 3413A NBTB+FAULT
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21416 | 118.94 | P42:345:AEPW:LAWTON EASTSIDE CB 3425A NBTB+FAULT
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21346 | 118.96 | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21275 | 117.77 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21275 | 117.77 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21275 | 117.74 | P42:345:AEPW:TERRYRD_CB_3421A_NBTB
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21026 | 116.18 | P23:345:KCPL:LACYGNE_R2-5::LACYGU2-LACYGNE-STILWELL
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21026 | 115.82 | P45:345:UMZW:# 1328 #: GI IN NE.
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21029 | 115.8 | P23:345:AEPW:WELSH CB 10620 NBTB
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21028 | 115.79 | P23:345:AEPW:WELSH CB 10630 NBTB
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 115.79 | P23:345:AEPW:WELSH CB 11670 NBTB
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21039 | 115.78 | P23:345:AEPW:WELSH CB 11680 NBTB
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 115.78 | P23:345:AEPW:WELSH CB 12540 NBTB
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21333 | 117.74 | P23:345:AEPW:OKLAUNION CB 3401A NBTB
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21381 | 118.58 | P23:345:AEPW:LAWTON EASTSIDE CB 3413A NBTB
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21416 | 118.94 | P23:345:AEPW:LAWTON EASTSIDE CB 3425A NBTB
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21346 | 118.96 | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21275 | 117.77 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21275 | 117.77 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21275 | 117.74 | P23:345:AEPW:TERRYRD_CB_3421A_NBTB
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.05 | P11:161:GMO:DOGWOOD_COMBINED_CYCLE_UNIT_OUTAGE
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21027 | 116.06 | P11:115:SUNC:GARDENCITY_S2:97:531459(2)
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21013 | 115.77 | P12:345:PWT:BUFF-THIS_345_1::
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21013 | 115.77 | P12:345:PWT:BUFF-THIS_345_2::
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21014 | 115.83 | P12:345:PWT:THIS-DGRS_345_1::FUTURE
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21014 | 115.83 | P12:345:PWT:THIS-DGRS_345_2::FUTURE
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21037 | 116.06 | P12:069:WFEC:ANADRKO_WATONGA
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21292 | 117.97 | P23:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21547 | 120.4 | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21292 | 117.97 | P42:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB+FAULT
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21547 | 120.4 | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.20561 | 114.13 | P42:345:OKGE:SB_BVTY7315_PRE19S
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.20996 | 115.62 | P23:345:SUNC:MO_BRK182
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.20996 | 115.62 | P23:345:SUNC:MO_BRK382
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.20992 | 115.79 | P23:345:SUNC:MO_BRK188
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21146 | 116.06 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.21029 | 115.79 | P12:138-13.8:AEPW:COMANC-4_#1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.20968 | 115.47 | P12:230:AEPW:ELKCITY6:CHISHOLM6
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.2114 | 116.62 | P12:230:AEPW:SWEETWT6:CHISHOLM6
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997713 ABBXNL844501 230 1 |  | 553 | 0.24819 | 157.44 | 525531 TOLK 6 230 3WXFMR TOLK 6 2
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.24819 | 155.48 | 525549 TOLK 7 345 3WXFMR ABBXNL844501 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997713 ABBXNL844501 230 1 |  | 553 | 0.24819 | 157.44 | 525531 TOLK 6 230 3WXFMR TOLK 6 2
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.24819 | 155.48 | 525549 TOLK 7 345 3WXFMR ABBXNL844501 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997713 ABBXNL844501 230 1 |  | 553 | 0.29039 | 157.44 | 525531 TOLK 6 230 3WXFMR TOLK 6 2
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.20007 | 119.68 | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.2016 | 120.42 | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.29039 | 155.48 | 525549 TOLK 7 345 3WXFMR ABBXNL844501 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997711 ABBXNL844501 230 1 |  | 552.5 | 0.28873 | 164.23 | 525531 TOLK 6 230 3WXFMR TOLK 6 2
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20024 | 127.4 | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.28873 | 162.04 | 525549 TOLK 7 345 3WXFMR ABBXNL844501 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997711 ABBXNL844501 230 1 |  | 552.5 | 0.3412 | 164.23 | 525531 TOLK 6 230 3WXFMR TOLK 6 2
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20928 | 120.49 | P12:345:AEPW-AEPW:CHAMPSP-CLARKSV
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20927 | 120.61 | P23:345:KCPL-WERE:237LACYGNE_R1-6::LACYGU1-LACYGNE-NEOSHO
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20925 | 120.5 | P11:161:GMO:DOGWOOD_COMBINED_CYCLE_UNIT_OUTAGE_1_1
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20933 | 118.96 | P11:115:SPS:MUSTANG1&3:153MW::::
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21179 | 122.27 | P12:230:SPS:K37::1_TOLK_LAMB:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20946 | 120.48 | P12:230:SPS:K43::1_PRNGLE_HARR_E:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20929 | 120.26 | P12:230:SPS:K44::1_EPLNT_HARRW:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.2094 | 120.61 | P12:115:SPS:T04::1_TRBLNC_CASTRO:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20925 | 120.48 | P12:115:SPS:T13::1_TAYLOR_WHOBBS:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20925 | 120.26 | P12:115:SPS:T14::1_MADDOX_TAYLOR:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.73 | P12:115:SPS:T21::1_GRSSLND_GRAHAM:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20925 | 120.29 | P12:115:SPS:T23::1_PCA_POTJCT:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20927 | 120.52 | P12:115:SPS:T26::1_CHAVES_RSWLCTY:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21046 | 120.8 | P12:115:SPS:T28A::1_LAMTON_PLANTX:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.2097 | 120.54 | P12:115:SPS:T29::1_LAMTON_HALECTR:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21093 | 121.92 | P12:115:SPS:T30::1_LAMB_HOCKLY:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21093 | 121.43 | P12:115:SPS:T31::1_HOCKLY_SUNDWN:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20921 | 120.59 | P12:115:SPS:T35::1_TERRY_YOAKUM:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 121.24 | P12:115:SPS:T45::1_NORRIS_OASIS:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21052 | 120.73 | P12:115:SPS:T59::1_CARGIL_CURRY:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21023 | 120.66 | P12:115:SPS:T67::1_HAPPY_KRESS:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20921 | 120.96 | P12:115:SPS:T71::1_CRLSLE_YUMA:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20934 | 120.57 | P12:115:SPS:T81::1_COX_FLOYD:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20925 | 120.57 | P12:115:SPS:T83::1_SP-FKFD_ALLEN:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20921 | 120.91 | P12:115:SPS:T89::1_DC_N_HIGG:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.54 | P12:115:SPS:T91::1_HIGG_RUSSELL:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20948 | 120.51 | P12:115:SPS:V04::1_EPLANT_RNDALL:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20939 | 120.5 | P12:115:SPS:V07::1_COX_HALECTR:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21038 | 120.71 | P12:115:SPS:V09::1_HALECTR_PLANTX:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20925 | 120.56 | P12:115:SPS:V12::1_PLANTX_BAILEY:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.5 | P12:115:SPS:V15::1_TUCO_INDANA:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20917 | 120.51 | P12:115:SPS:V16::1_TERRY_DC_N:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.2089 | 120.62 | P12:115:SPS:V24::1_WOLFTH_TERRY:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20943 | 120.6 | P12:115:SPS:V26::1_RSWLL_EDDY_N:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.58 | P12:115:SPS:V33::1_LUBBS_LYNN:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.2103 | 121.13 | P12:115:SPS:V37::1_CASTRO_PLANTX:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.63 | P12:115:SPS:V46::1_ALLEN_WHEELCK:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20927 | 120.95 | P12:115:SPS:V49::1_YOAKUM_SHLCO2:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20968 | 121.15 | P12:115:SPS:V55::1_SUNDWN_TERRY:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20936 | 120.98 | P12:115:SPS:V56::1_COCHRAN_SUNDWN:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20939 | 120.5 | P12:115:SPS:V78::2_CURRY_RSVLT:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20924 | 120.67 | P12:115:SPS:V81::1_LE-WAIT_LE-LVN:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.54 | P12:115:SPS:V95::1_DC_N_SHLCO2:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.5 | P12:115:SPS:W11::1_DC_S_SMINLE:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20925 | 120.54 | P12:115:SPS:W14::1_SMINLE_GAINES:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20925 | 120.5 | P12:115:SPS:W26::1_CUNGHM_OILCNTR:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 121.13 | P12:115:SPS:W32::1_PRMTR_FE-CLSIN:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.5 | P12:115:SPS:W34::1_JNSDRW_MAPCO:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20923 | 120.73 | P12:115:SPS:W35::1_GAINES_JNSDRW:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.2092 | 120.52 | P12:115:SPS:W36::1_TAYLOR_JNSDRW:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21116 | 120.93 | P12:115:SPS:W40::1_WCANYON_TRBLNC:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20936 | 120.29 | P12:115:SPS:W46::1_RHILLS_NWEST:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20953 | 120.55 | P12:115:SPS:W52::1_NEWHART_KRESS:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 121.01 | P12:115:SPS:W58::1_NORTON_LOPEZ:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.69 | P12:115:SPS:W59::1_LOPEZ_CMPBLL:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20927 | 120.96 | P12:115:SPS:W62::1_PLSTHL_CURRY:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.84 | P12:115:SPS:W64::1_PLSTHL_FE-CLV:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20927 | 120.81 | P12:115:SPS:W65::1_PLSTHL_CURRY:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.68 | P12:115:SPS:W66::1_PORTA_GREYHUND:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21116 | 120.53 | P12:115:SPS:W77::1_RNDAL_WCANYON:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.51 | P12:115:SPS:W99::1_CAPITAN_CHAVES:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20925 | 120.51 | P12:115:SPS:U03::1_CARDNL_NEF:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20922 | 121.04 | P12:115:SPS:U14::1_DC_STH_INKBSN:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20924 | 120.92 | P12:115:SPS:V15::1_INKBSN_LE-WAT:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20948 | 120.55 | P12:115:SPS:U16::1_BSHLND_OUTPST:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20948 | 120.54 | P12:115:SPS:U17::1_COLTR_OUTPST:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20933 | 120.76 | P12:115:SPS:U19::1_DEAN_PLAINS:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20948 | 120.49 | P12:115:SPS:U23::1_COLTR_HILSDE:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.201 | 127.42 | P42:345:SPS:YOAKUM:J18####:SLG1:EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.201 | 127.42 | P43:345:SPS:YOAKUM:TF#####:SLG:EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.201 | 127.42 | P42:345:SPS:YOAKUM:J17####:SLG:EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20181 | 122.69 | P43:345:SPS:TUCO:SLG::EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.201 | 127.42 | P42:345:SPS:YOAKUM:J18####:SLG2:EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20928 | 120.49 | P12:345:AEPW-AEPW:CHAMPSP-CLARKSV:::EHV::
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20925 | 120.52 | P11:18:HAST:::EGYCTR2G WEC2_LOSS OF WEC 2 GEN_:HV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20925 | 120.52 | P13:18-115:HAST:::EGYCNTR7 XFMR G2WEC 2 GSU_:HV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20925 | 120.5 | P11:161:GMO:DOGWOOD-COMBINED-CYCLE-UNIT-OUTA:::HV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20927 | 120.61 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20924 | 120.65 | P23:345:KCPL:LACYGNE-R2-5:::EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20922 | 120.66 | P11:230:WERE:JECU1-GEN:::HV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20922 | 120.66 | P11:345:WERE:JECU2-GEN:::EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20922 | 120.66 | P11:345:WERE:JECU3-GEN:::EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.88 | P11:345:WERE:WOLFU1-GEN:::EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20912 | 120.25 | P12:345:PWT:BUFF-THIS-345-1:::EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20912 | 120.25 | P12:345:PWT:BUFF-THIS-345-2:::EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.2091 | 120.23 | P23:345:WERE:BUFF-345-534:::EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.2091 | 120.23 | P23:345:WERE:BUFF-345-543:::EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20922 | 120.66 | P23:345:WERE:JEC-345-15:::EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.2092 | 120.62 | P23:345:WERE:JEC-345-16:::EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20922 | 120.66 | P23:345:WERE:JEC-345-19:::EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20922 | 120.66 | P23:345:WERE:JEC-345-20:::EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.2092 | 120.29 | P23:345:WERE:WICH-345-50:::EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20925 | 120.87 | P23:345:WERE:WOLF-345-50:::EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.87 | P23:345:WERE:WOLF-345-60:::EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.81 | P11:022:NPPD:COOPER1G:1:983:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.2092 | 120.83 | P11:023:NPPD:GENTLM1G:1:757:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20924 | 120.68 | P11:024:NPPD:GENTLM2G:2:757:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20921 | 120.68 | P13:345:OPPD:NEBCTY1G:::EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.2092 | 120.69 | P13:345:OPPD:NEBCTY2G:::EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.69 | P22:345:OPPD:S3458 NEBCTY1G:LT::EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20921 | 120.68 | P22:345:OPPD:S3458 NEBCTY1G:::EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.72 | P22:345:OPPD:S3458 NEBCTY2G:LT::EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.2092 | 120.69 | P22:345:OPPD:S3458 NEBCTY2G:::EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.69 | P23:345:OPPD:S3458 NEBCTY1G:LT::EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20921 | 120.68 | P23:345:OPPD:S3458 NEBCTY1G:::EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.72 | P23:345:OPPD:S3458 NEBCTY2G:LT::EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.2092 | 120.69 | P23:345:OPPD:S3458 NEBCTY2G:::EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.29 | P12:115:SUNC:PLYMELL-PIERCEVILLE:::HV::
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20923 | 120.53 | P11:018:UMZB:# 5 #:: DCS IN SD. DEERCREEK_MV::
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20924 | 120.5 | P11:022:UMZB:# 15 #:: LO IN ND. LELAND OLDS 1_MV::
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20925 | 120.5 | P11:020:UMZB:# 16 #:: LO IN ND. LELAND OLDS 2_MV::
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20923 | 120.61 | P11:023:UMZB:# 31 #:: AVS IN ND. ANTELOPE VALLEY 1_MV::
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20923 | 120.61 | P11:023:UMZB:# 32 #:: AVS IN ND. ANTELOPE VALLEY 2_MV::
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20919 | 120.82 | P11:024:UMZB:# 33 #:: LRS IN WY. LARAMIE RIVER STATION 1_MV::
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.49 | P13:230:UMZW:# 5135 #:: OA IN SD. FAULT ON TRANSFORMER (2).:HV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.49 | P13:230:UMZW:# 5136 #:: OA IN SD. FAULT ON TRANSFORMER (3).:HV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.5 | P13:230:UMZW:# 5137 #:: OA IN SD. FAULT ON TRANSFORMER (4).:HV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20924 | 120.28 | P23:345:UMZW:# 2423 #:: GI IN NE. GI 1596 BKR FAULT:EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20924 | 120.28 | P23:345:UMZW:# 2426 #:: GI IN NE. GI 1592 BKR FAULT:EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20924 | 120.28 | P23:345:UMZW:# 2432 #:: GI IN NE. GI 1092 BKR FAULT:EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20924 | 120.28 | P23:345:UMZW:# 2440 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1092 STUCK BKR:EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20924 | 120.28 | P23:345:UMZW:# 2444 #:: GI IN NE. GI-SWEET BRANCH FAULT & GI 1596 STUCK BKR:EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20924 | 120.28 | P23:345:UMZW:# 2446 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1196 STUCK BKR:EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20924 | 120.28 | P42:345:UMZW:# 2413 #:: FT2 IN SD. FT2-LO2 BRANCH FAULT & FT2 2992 STUCK BKR:EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20924 | 120.28 | P42:345:UMZW:# 2415 #:: FT2 IN SD. FT2-GI BRANCH FAULT & FT2 3392 STUCK BKR:EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.2093 | 120.2 | P11:138:WFEC:HUGO1:465MW :::
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20924 | 120.49 | P11:138:WFEC:MORLND2:132MW:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20924 | 120.5 | P11:138:WFEC:MORLND3:149MW :::
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20934 | 120.52 | P12:138:WFEC:ANADRKO_CLVLND::::
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.2092 | 120.25 | P12:345:OKGE-AEPW:BKRBKR20::::
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20961 | 120.7 | P12:345:OKGE:BKRBKR21::::
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20981 | 120.7 | P12:345:OKGE:BKRBKR24::::
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21172 | 122.65 | P12:345:OKGE-AEPW:BKRBKR25::::
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20895 | 120.12 | P12:345:OKGE:BKRBKR336::::
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20894 | 120.11 | P12:345:OKGE:BKRBKR336_2::::
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.2096 | 120.48 | P12:345:OKGE-AEPW:BKRBKR343::::
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21247 | 122.27 | P12:345:OKGE-AEPW:BKRBKR366::::
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21247 | 122.24 | P12:345:OKGE-AEPW:BKRBKR366::::
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21132 | 121.66 | P12:345:OKGE:BKRBKR367::::
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20962 | 120.59 | P12:345:OKGE-WFEC:BKRBKR374::::
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20962 | 120.56 | P12:345:OKGE-WFEC:BKRBKR374::::
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20899 | 120.16 | P12:345:OKGE:BKRBKR4193::::
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20899 | 120.16 | P12:345:OKGE:BKRBKR4194::::
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20889 | 120.16 | P12:345:OKGE-SPS:BKRBKR4201::::
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20889 | 120.16 | P12:345:OKGE-SPS:BKRBKR4202::::
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20893 | 119.95 | P12:345:OKGE:BKRBKR443NEW::::
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20893 | 119.95 | P12:345:OKGE:BKRBKR443NEW2::::
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20909 | 120.27 | P12:345:OKGE-ITC:BKRBKR502::::
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20909 | 120.27 | P12:345:OKGE-ITC:BKRBKR503::::
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20921 | 120.61 | P12:345:OKGE:BKRBKR604::::
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20919 | 120.72 | P12:345:OKGE:BKRBKR604_2::::
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21627 | 123.72 | P42:345:OKGE:SB_BVTY7387::::
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20966 | 120.63 | P42:345:OKGE:SB_SPCK7383::::
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20923 | 120.53 | P11:115:SUNC:GARDENCITY_S2:103:531459(2):HV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20923 | 120.54 | P11:115:SUNC:FORTDDODGE_4:157:539670(4):HV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20888 | 120.5 | P12:345:SUNC-NPPD:MINGO-REDWILLOW::531451-640325(1):EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.61 | P13:115:SUNC:HOLCOMB_GSU:::HV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20923 | 120.53 | P13:115:SUNC:S2_GSU:::HV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20923 | 120.54 | P13:115:SUNC:FORTDODGE_GSU:::HV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.48 | 300002 1THLG2 22.0 301505 5THOMHLGSU2 161 2
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.62 | 300003 1THLG3 24.0 301503 7THOMHLGSU3 345 3
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.48 | 300006 1NM G1 22.0 301536 5NEWMADGSU1 161 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.48 | 300007 1NM G2 22.0 301537 7NEWMADGSU2 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.48 | 300046 7NEWMAD 345 301537 7NEWMADGSU2 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.62 | 300049 7THOMHL 345 301503 7THOMHLGSU3 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.48 | 300103 5NEWMAD 161 301536 5NEWMADGSU1 161 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.48 | 300132 5THMHLB2 161 301505 5THOMHLGSU2 161 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20925 | 120.29 | 300739 7BLACKBERRY 345 532797 WOLFCRK7 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.56 | P11:20:AMMO:1LAB�� G1:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.54 | P11:20:AMMO:1LAB�� G2:2
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.75 | P11:345:AMMO::CALLAWAY:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.56 | P11:345:AMMO::LABADIE:3
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.56 | P11:345:AMMO::LABADIE:4
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.55 | P11:345:AMMO::RUSHISLAND:U1
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.54 | P11:345:AMMO::RUSHISLAND:U2
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.53 | P11:138:AMMO::SIOUX:2
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.49 | P13:345-230:CLEC::DOLHILL7:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.29 | P11:345-24:CLEC::DOLHILL7:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.29 | P11:24:CLEC::G1DOLHIL:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.53 | P12:765:AEP:AEP ROCKP-AEP JEFF 765
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.48 | P11:HV:EES::1ISES U1:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.25 | P11:HV:EES::PIRKEY 1:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.26 | P11:EHV:EES::WELSH3-1:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.2 | P11:HV:EES::TURKCOAL:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.48 | P12:HV:EES::5ISES%:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.74 | P12:EHV:EES::7CALAWY 1:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20928 | 120.49 | P12:EHV:EES::CHAMSPR7!:CLARKSV7!:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20927 | 120.21 | P12:HV:EES::TURK 4%:1(1)
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20928 | 120.26 | P12:EHV:EES::WELSH 7:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20928 | 120.26 | P12:EHV:EES::WELSH 7:1(1)
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20927 | 120.26 | P12:HV:EES::PIRKEY 4:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.53 | 344011 7HUGHES 345 344012 7HPW-N 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.55 | 344884 7LABADIE1 345 344894 1LAB G1 20.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.53 | 344885 7LABADIE2 345 344895 1LAB G2 20.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.55 | 344886 7LABADIE3 345 344896 1LAB G3 20.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.55 | 344887 7LABADIE4 345 344897 1LAB G4 20.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.54 | 345667 7RUSH 1 345 345670 1RUSH G1 18.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.53 | 345668 7RUSH 2 345 345671 1RUSH G2 18.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.52 | 345755 4SIOUX 1 138 345756 1SIOUX 1 18.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.52 | 345764 4SIOUX 2 138 345765 1SIOUX 2 18.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.6 | P12:345:MDU::CENTER:COYOTE:1::::
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.6 | P13:345:MDU:COYOTE GSU LOSS:COYOTE::1::::
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.82 | P11:345:MEC-NPPD:COOPER 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.72 | P11:24:XEL:AUTO-SINGLE:SHERC31G:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.72 | P11:24:XEL:AUTO-SINGLE:SHERC32G:2
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.81 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.64 | P11:20:XEL:AUTO-SINGLE:PRIS31G:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.63 | P11:20:XEL:AUTO-SINGLE:PRIS32G:2
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.68 | P11:22:XEL:AUTO-SINGLE:MNTCE31G:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.64 | P11:20:XEL:AUTO-SINGLE:KING31G:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.48 | P11:18:XEL:AUTO-SINGLE:BLKD76G:6
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.69 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.69 | P11:22:GRE:AUTO-SINGLE:GRE-COAL42G:2
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.61 | P11:24:OTP:AUTO-SINGLE:BIGSTN1G:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.63 | P11:20:OTP:AUTO-SINGLE:CENTER2G:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.52 | P11:22:OTP:AUTO-SINGLE:CENTER1G:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.61 | P11:24:OTP:AUTO-SINGLE:COYOTE1G:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.51 | P11:24:DPC:AUTO-SINGLE:GENOA53G:3
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.5 | P12:115:XEL:AUTO-SINGLE:CHEMOLT7:LSPOWER7:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.49 | P12:115:XEL:AUTO-SINGLE:FARIBALTP7:FARIBALTGEN:Z
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.61 | P12:230:OTP:AUTO-SINGLE:SQBUTTE4:YNG24:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.69 | P13:24-345:XEL:AUTO-SINGLE:SHERC31G:SHERCO3:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.69 | P13:24-345:XEL:AUTO-SINGLE:SHERC32G:SHERCO3:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.78 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.64 | P13:20-345:XEL:AUTO-SINGLE:PRIS31G:PRISLD3:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.64 | P13:20-345:XEL:AUTO-SINGLE:PRIS32G:PRISLD3:2
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.68 | P13:22-345:XEL:AUTO-SINGLE:MNTCE31G:MNTCELO3:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.62 | P13:20-345:XEL:AUTO-SINGLE:KING31G:ASKING3:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.48 | P13:18-115:XEL:AUTO-SINGLE:BLKD76G:BLKDG27:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.67 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL41G:GRE-COALCR4:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.67 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL42G:GRE-COALCR4:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.6 | P13:230-24:OTP:AUTO-SINGLE:BIGSTON4:BIGSTN1G:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.61 | P13:20-230:OTP:AUTO-SINGLE:CENTER2G:YNG24:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.51 | P13:22-230:OTP:AUTO-SINGLE:CENTER1G:CENTER4:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.6 | P13:24-345:OTP:AUTO-SINGLE:COYOTE1G:COYOTE3:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.5 | P13:24-161:DPC:AUTO-SINGLE:GENOA53G:GENOA5:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.55 | P13:24-161:DPC:AUTO-SINGLE:JPM:ALMA5:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.6 | P11:115:XEL:RIV COMBINE CYCLE
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.51 | P12:115:XEL:BDS #2 5
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.49 | P11:115:XEL:HBR #6 7 8
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.63 | P23:345:XEL:8H14 PRI
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.64 | P23:345:XEL:8H17 PRI AS
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.78 | P23:345:XEL:8N28 SHC
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.7 | P23:345:XEL:8N22 SHC
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.69 | P23:345:XEL:8N17 SHC
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.68 | P23:345:XEL:8N8 MNN
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.63 | P23:345:XEL:8P1 KING
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.63 | P23:345:XEL:8P2 KING
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.5 | P11:22:ALTW:AUTO-SINGLE:LANS54G:4
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.64 | P11:22:ALTW:AUTO-SINGLE:ARNOLD1G:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.67 | P11:24:ALTW:AUTO-SINGLE:OTTUMW1G:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.49 | P13:22-161:ALTW:AUTO-SINGLE:LANS54G:LANSINGL15:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.63 | P13:22-161:ALTW:AUTO-SINGLE:ARNOLD1G:ARNOLD5:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.66 | P13:24-161:ALTW:AUTO-SINGLE:OTTUMW1G:OTTUMWA5:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.74 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.8 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.65 | P11:22:MEC:AUTO-SINGLE:NEAL3G:3
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.73 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.66 | P11:24:MEC:AUTO-SINGLE:LOUIS31G:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.72 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.76 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.64 | P13:345-22:MEC:AUTO-SINGLE:RAUN3:NEAL3G:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.71 | P13:345-24:MEC:AUTO-SINGLE:RAUN3:NEAL4G:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.64 | P13:345-24:MEC:AUTO-SINGLE:LOUISA3:LOUIS31G:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20922 | 120.66 | P11:230:WERE:JECU1_GEN::
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20922 | 120.66 | P11:345:WERE:JECU2_GEN::
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20922 | 120.66 | P11:345:WERE:JECU3_GEN::
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.88 | P11:345:WERE:WOLFU1_GEN::
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20933 | 120.48 | 511453 DUNCAN-4 138 511552 DUNCHERTP4 138 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20933 | 120.48 | 511455 D.E.S.-4 138 511552 DUNCHERTP4 138 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.48 | 511456 O.K.U.-7 345 511565 OKLAUN HVDC7 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 119.42 | 511456 O.K.U.-7 345 588760 GEN-2017-033 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21233 | 122.19 | 511456 O.K.U.-7 345 763215 G18-092-TAP 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21246 | 122.76 | 511468 L.E.S.-7 345 762467 G18-015-TAP 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21143 | 122.19 | 511468 L.E.S.-7 345 763215 G18-092-TAP 345 2
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20938 | 120.56 | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21045 | 120.68 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20262 | 117.21 | 511553 CHISHOLM7 345 523961 POTTER_CO 7 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20262 | 117.21 | 511553 CHISHOLM7 345 523961 POTTER_CO 7 345 2
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20633 | 119.86 | 511553 CHISHOLM7 345 755000 WWDBORDT 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20924 | 120.5 | 511557 CHISHOLM6 230 3WXFMR CHISHOLM6 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20939 | 120.51 | 514801 MINCO 7 345 555234 NSUB345 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20852 | 120.15 | 515375 WWRDEHV7 345 755000 WWDBORDT 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21627 | 123.76 | 515458 BORDER 7 345 560022 CRAWFISH_DR 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21627 | 123.7 | 515458 BORDER 7 345 755000 WWDBORDT 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20924 | 120.51 | 515618 BALKOW 7 345 3WXFMR BALKOW 7 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20924 | 120.5 | 515618 BALKOW 7 345 3WXFMR BALKOW 7 1_Dup1
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20919 | 120.73 | 515634 PALDR1W7 345 3WXFMR PALO2 _1 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.63 | 515677 BADGER 7 345 563170 G15082_1 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.49 | 522800 MU-TULIA 3 115 525179 TULIA_TP 3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.63 | 522892 MU-BROWNFLD2 69.0 526761 BROWNFLD_TP2 69.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20923 | 120.52 | 523093 HITCHLAND 3 115 523174 GOODWELLWND3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21053 | 120.53 | 523095 HITCHLAND 6 230 523309 MOORE_CNTY 6 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.88 | 523097 HITCHLAND 7 345 523112 NOVUS1 7 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.93 | 523097 HITCHLAND 7 345 523215 FREWHELCOL17 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20717 | 119.43 | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.99 | 523097 HITCHLAND 7 345 560252 G10-14 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.5 | 523099 TC-DRYTRLS 3 115 588480 A16-010_SUB 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.74 | 523112 NOVUS1 7 345 3WXFMR NOVUS XF2 2
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.52 | 523112 NOVUS1 7 345 3WXFMR XIANA2011198 _1 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20923 | 120.5 | 523118 BUFF_DUNES 7 345 523853 FINNEY 7 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.51 | 523120 COLE 3 115 588860 GEN-2017-047 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20935 | 120.48 | 523221 XIT_INTG 6 230 3WXFMR SIEM_T126401 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20946 | 120.48 | 523267 PRINGLE 6 230 3WXFMR ENRCO13617-1 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20946 | 120.48 | 523267 PRINGLE 6 230 523979 HARRNG_EST 6 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20988 | 120.61 | 523309 MOORE_CNTY 6 230 523323 MCDWL_CREEK6 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.2096 | 120.53 | 523323 MCDWL_CREEK6 230 523959 POTTER_CO 6 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20896 | 120.85 | 523959 POTTER_CO 6 230 523979 HARRNG_EST 6 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21737 | 121.98 | 523959 POTTER_CO 6 230 524267 BUSHLAND 6 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.2171 | 122.4 | 523959 POTTER_CO 6 230 525461 NEWHART 6 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21287 | 129.34 | 523961 POTTER_CO 7 345 3WXFMR WAUK 90343-A 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20912 | 120.79 | 523961 POTTER_CO 7 345 524296 SPNSPUR_WND7 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20928 | 120.27 | 523977 HARRNG_WST 6 230 523971 HARRNGTON1 1 24.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20905 | 120.79 | 523977 HARRNG_WST 6 230 524010 ROLLHILLS 6 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20925 | 120.22 | 523978 HARRNG_MID 6 230 523979 HARRNG_EST 6 230 @1
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20925 | 120.29 | 524010 ROLLHILLS 6 230 3WXFMR WAUK WT01104 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20948 | 120.55 | 524267 BUSHLAND 6 230 3WXFMR WH 7001795 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.22387 | 122.23 | 524267 BUSHLAND 6 230 524623 DEAFSMITH 6 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20912 | 120.89 | 524296 SPNSPUR_WND7 345 524299 SPNSPUR_COL7 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20912 | 120.89 | 524299 SPNSPUR_COL7 345 3WXFMR SPNSPUR_COL7 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21317 | 120.9 | 524415 AMA_SOUTH 6 230 525213 SWISHER 6 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 121.01 | 524502 NORTON 3 115 524509 FE-TUCMCARI3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21116 | 120.82 | 524575 DS-#25+ 3 115 524597 PANDAHFD 3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21116 | 120.9 | 524575 DS-#25+ 3 115 524630 TIERABLANCA3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.5 | 524604 HEREFRD_SB 2 69.0 524608 HERFRD_STH 2 69.0 *1
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.22236 | 125.98 | 524623 DEAFSMITH 6 230 760498 G17-146-TAP 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.78 | 524721 DS-#15&#19+2 69.0 524745 CASTRO_CNTY2 69.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.84 | 524764 NORRIS_TP 3 115 524801 NORRIS 3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20932 | 120.49 | 524770 PLSNT_HILL 6 230 3WXFMR EFAE1100068A 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.84 | 524776 N_CLOVIS_TP3 115 524777 N_CLOVIS 3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.78 | 524790 CANNON_TP 3 115 524794 CANNONAFB 3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21343 | 127.03 | 524875 OASIS 6 230 524885 SN_JUAN_TAP6 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20999 | 121.66 | 524875 OASIS 6 230 524909 ROOSEVELT 6 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21325 | 127.79 | 524885 SN_JUAN_TAP6 230 527483 CHAVES_CNTY6 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20942 | 120.65 | 524909 ROOSEVELT 6 230 3WXFMR ABB LMM60042 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21617 | 125.82 | 524909 ROOSEVELT 6 230 525531 TOLK 6 230 2
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 121.25 | 524923 PORTALES 2 69.0 524929 RO-PORT_MTR2 69.0 @1
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.88 | 524923 PORTALES 2 69.0 524941 PORTALES#1 2 69.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.84 | 525023 BC-BAIL_MTR2 69.0 525027 BAILEYCO 2 69.0 @1
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.2103 | 120.8 | 525056 BC-EARTH 3 115 525480 PLANT_X 3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.57 | 525192 KRESS_INT 3 115 3WXFMR ENRCO 136155 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20937 | 120.29 | 525213 SWISHER 6 230 3WXFMR SIEM_T127101 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21223 | 121.59 | 525213 SWISHER 6 230 525461 NEWHART 6 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.54 | 525272 KISER 3 115 3WXFMR VON 13819/1 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.81 | 525326 COX 3 115 3WXFMR ELCO 13474-3 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.81 | 525414 LAMTON 3 115 3WXFMR ASEA MLL9204 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.22535 | 123.54 | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21198 | 122.16 | 525481 PLANT_X 6 230 3WXFMR WH ALM20171 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21856 | 127.05 | 525481 PLANT_X 6 230 526435 SUNDOWN 6 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.22236 | 124.03 | 525481 PLANT_X 6 230 760498 G17-146-TAP 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21271 | 120.86 | 525481 PLANT_X 6 230 762174 G17-218TAP 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21313 | 120.92 | 525481 PLANT_X 6 230 762174 G17-218TAP 230 2
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.22055 | 128.41 | 525531 TOLK 6 230 525586 NEEDMORE 6 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21179 | 122.27 | 525531 TOLK 6 230 525637 LAMB_CNTY 6 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.23816 | 127.4 | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21436 | 121.08 | 525531 TOLK 6 230 762174 G17-218TAP 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21471 | 121.13 | 525531 TOLK 6 230 762174 G17-218TAP 230 2
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.3412 | 162.04 | 525549 TOLK 7 345 3WXFMR ABBXNL844501 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.22055 | 128.41 | 525586 NEEDMORE 6 230 526935 YOAKUM 6 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21179 | 122.27 | 525637 LAMB_CNTY 6 230 3WXFMR WH ALM20172 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.54 | 525828 TUCO_INT 3 115 3WXFMR DS F78800913 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21357 | 120.96 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21476 | 121.11 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _9 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20181 | 122.69 | 525832 TUCO_INT 7 345 526936 YOAKUM_345 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21093 | 121.33 | 526020 HOCKLEY 3 115 526036 LC-OPDYKE 3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21093 | 121.18 | 526036 LC-OPDYKE 3 115 526434 SUNDOWN 3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.57 | 526160 CARLISLE 3 115 3WXFMR WH RLP38371 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.79 | 526162 LP-DOUD_TP 3 115 526176 LP-DOUD 3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.82 | 526268 LUBBCK_STH 3 115 3WXFMR NA 70454A 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20936 | 120.81 | 526361 COCHRAN 3 115 526424 PACIFIC 3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20936 | 120.9 | 526424 PACIFIC 3 115 526434 SUNDOWN 3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20968 | 120.94 | 526434 SUNDOWN 3 115 526445 AMOCO_TP 3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20921 | 120.51 | 526435 SUNDOWN 6 230 3WXFMR UPDATE LATER _12 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20944 | 124.22 | 526435 SUNDOWN 6 230 526460 AMOCO_SS 6 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20968 | 120.8 | 526445 AMOCO_TP 3 115 526484 LG-LEVELAND3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20944 | 121.88 | 526460 AMOCO_SS 6 230 526935 YOAKUM 6 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20968 | 120.79 | 526484 LG-LEVELAND3 115 526491 LG-CLAUENE 3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20923 | 120.51 | 526525 WOLFFORTH 6 230 3WXFMR UPDATE LATER _13 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20916 | 122.38 | 526935 YOAKUM 6 230 527028 INK_BASIN 6 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20181 | 129.67 | 526936 YOAKUM_345 345 527896 HOBBS_INT 7 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20905 | 121.79 | 527028 INK_BASIN 6 230 527894 HOBBS_INT 6 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20921 | 120.9 | 527130 DENVER_N 3 115 527286 HIGGEAST 3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20928 | 119.59 | 527149 MUSTANG 6 230 527151 GS-MUSTANG 6 230 @1
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.62 | 527202 SEAGRAVES 3 115 3WXFMR ABB MLL92408 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.59 | 527212 DIAMONDBACK3 115 3WXFMR HOW 36773714 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20921 | 120.88 | 527286 HIGGEAST 3 115 527363 HIGG 3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20923 | 120.62 | 527325 OXY_WSEM_TP3 115 527362 JOHNSON_DRW3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.59 | 527340 DOSS 3 115 3WXFMR ELCO 13566/1 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.58 | 527345 LEGACY 2 69.0 527350 XTO_ROBRTSN2 69.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.58 | 527346 LEGACY 3 115 3WXFMR VROL 13735-1 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.56 | 527350 XTO_ROBRTSN2 69.0 527355 BOARDMAN 2 69.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.51 | 527355 BOARDMAN 2 69.0 527365 FLANNAGAN 2 69.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.5 | 527360 MAPCO 3 115 527362 JOHNSON_DRW3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.58 | 527362 JOHNSON_DRW3 115 528775 LE-ERF 3 115 @1
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.48 | 527370 TENNECO_TAP2 69.0 527371 TENNECO 2 69.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20928 | 120.29 | 527470 CHVS_SLRCOL3 115 527482 CHAVES_CNTY3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21101 | 121.58 | 527483 CHAVES_CNTY6 230 527799 EDDY_NORTH 6 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.49 | 527508 PRICE 3 115 527509 PRICE_TAP 3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.5 | 527514 CV-PINE 2 69.0 527563 ROSWLL_INT 2 69.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.52 | 527563 ROSWLL_INT 2 69.0 527575 SW_4702 2 69.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20943 | 120.61 | 527564 ROSWLL_INT 3 115 527597 TWEEDY 3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.52 | 527575 SW_4702 2 69.0 527589 CV-ORCHARD 2 69.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.48 | 527589 CV-ORCHARD 2 69.0 527619 DEXTER_TP 2 69.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20919 | 120.69 | 527653 MILO_WIND 1 34.5 527655 RSVLT_CC_E 7 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20909 | 120.67 | 527654 RSVLT_CC_W 7 345 527655 RSVLT_CC_E 7 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20909 | 120.92 | 527654 RSVLT_CC_W 7 345 527666 RSVLT_COL1 7 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20902 | 120.92 | 527655 RSVLT_CC_E 7 345 527656 CROSSROADS 7 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20909 | 120.92 | 527666 RSVLT_COL1 7 345 3WXFMR RSVLT_COL1 7 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.63 | 527790 EDDY_SVC 1 8.50 527799 EDDY_NORTH 6 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20925 | 120.22 | 527864 CUNNINHAM 3 115 528348 BUCKEYE_TP 3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20925 | 120.52 | 527864 CUNNINHAM 3 115 528568 MONUMNT_TP 3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20911 | 120.69 | 527865 CUNNIGHM_N 6 230 527867 CUNNIGHM_S 6 230 *1
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20921 | 120.51 | 527865 CUNNIGHM_N 6 230 527963 POTASH_JCT 6 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20921 | 120.51 | 527867 CUNNIGHM_S 6 230 527894 HOBBS_INT 6 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20925 | 120.3 | 527894 HOBBS_INT 6 230 3WXFMR ME C0482951 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20923 | 120.57 | 527894 HOBBS_INT 6 230 527903 HOBBS_PLT3 1 18.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.23 | 527896 HOBBS_INT 7 345 527965 KIOWA 7 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.2 | 527896 HOBBS_INT 7 345 528027 RDRUNNER 7 345 UC
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.2 | 527896 HOBBS_INT 7 345 528027 RDRUNNER 7 345 XA
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20925 | 120.29 | 527965 KIOWA 7 345 528027 RDRUNNER 7 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.55 | 528024 RR_SVC_HV 3 115 528021 RDRUNNR_SVC1 15.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.64 | 528024 RR_SVC_HV 3 115 528025 RDRUNNER 3 115 Z1
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.25 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.5 | 528182 NORTH_LOVNG3 115 528193 BLACKRIVER 3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.63 | 528222 CHINA_DRAW 3 115 528225 CD_SVC_HV 3 115 Z1
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20924 | 120.22 | 528333 LE-WEST_SUB3 115 528334 LE-NRTH_INT3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20925 | 120.29 | 528341 LE-SANANDRS3 115 528627 LE-TXACO_TP3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20925 | 120.25 | 528348 BUCKEYE_TP 3 115 528627 LE-TXACO_TP3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20925 | 120.24 | 528463 SANGER_SW 3 115 528575 OXYPERMIAN 3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20925 | 120.24 | 528463 SANGER_SW 3 115 762442 G18-004-TAP 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20925 | 120.52 | 528568 MONUMNT_TP 3 115 528581 BYRD_TP 3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20925 | 120.28 | 528574 OXY_NHU_RCF3 115 528575 OXYPERMIAN 3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20925 | 120.5 | 528596 CARDINAL 3 115 528605 TARGA 3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20925 | 120.53 | 528603 NA_ENRICH 3 115 528605 TARGA 3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.61 | 528617 LE-WAITS 2 69.0 528325 LE-WAITS 3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.51 | 528617 LE-WAITS 2 69.0 528714 LE-FORT_SW 2 69.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.49 | 528617 LE-WAITS 2 69.0 528759 LE-TP51 2 69.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20925 | 120.29 | 528622 LE-SANANDRS2 69.0 528341 LE-SANANDRS3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.92 | 528626 LE-PLNSINT 2 69.0 526928 PLAINS_INT 3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.92 | 528626 LE-PLNSINT 2 69.0 528709 LE-PLNSGOAB2 69.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.52 | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.59 | 528669 LE-STKLDRTP2 69.0 528740 LE-PLANS_SW2 69.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.79 | 528709 LE-PLNSGOAB2 69.0 528740 LE-PLANS_SW2 69.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.52 | 528709 LE-PLNSGOAB2 69.0 528747 LE-ALLRED 2 69.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.51 | 528714 LE-FORT_SW 2 69.0 528718 LE-NEWTEX 2 69.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.59 | 528735 LE-PLAINSUB2 69.0 528740 LE-PLANS_SW2 69.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.52 | 528775 LE-ERF 3 115 528779 LE-TALLCOTN3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.3 | 531213 SANTAFE3 115 531408 PIERCVL3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20924 | 120.48 | 531501 BUCKNER7 345 531502 CIMRRN 7 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20924 | 120.48 | 531502 CIMRRN 7 345 531503 CIMRRN 1 34.5 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20912 | 120.24 | 531510 HARBNGR3 115 3WXFMR HARBGR345 _1 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20923 | 120.5 | 539803 IRONWOOD7 345 3WXFMR IRONWOOD MPT 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20925 | 120.59 | 542951 HAW G5 1 22.0 543665 HAWTHN5 161 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20924 | 120.63 | 542955 LAC G1 1 22.0 542981 LACYGNE7 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20923 | 120.62 | 542956 LAC G2 1 24.0 542981 LACYGNE7 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20922 | 120.67 | 542957 IAT G1 1 24.0 542982 IATAN 7 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20923 | 120.74 | 542962 IAT G2 1 24.5 542982 IATAN 7 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21174 | 119.99 | 560022 CRAWFISH_DR 345 762216 G17-151TAP 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21142 | 120.98 | 560022 CRAWFISH_DR 345 762467 G18-015-TAP 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 116.89 | 560022 CRAWFISH_DR 345 763087 GEN-2018-073 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21254 | 121.28 | 560022 CRAWFISH_DR 345 763215 G18-092-TAP 345 2
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.99 | 560252 G10-14 345 560253 G10-14-1 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.69 | 560253 G10-14-1 115 560254 G10-14-SUB1 34.5 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.69 | 560253 G10-14-1 115 560255 G10-14-SUB2 34.5 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.52 | 560581 G06-44-2 34.5 523111 NOVUS1 3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.57 | 560582 G06-44-3 34.5 560577 G06-44 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.56 | 560583 G06-44-4 34.5 560577 G06-44 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.17 | 560757 ASGI13_02_1 69.0 560758 ASGI13_02_2 34.5 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.17 | 560757 ASGI13_02_1 69.0 562731 WHEATLAND 69.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.17 | 560763 ASGI13_03_1 115 560761 ASGI13_03_2 34.5 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.66 | 562015 FIREWHEEL1 34.5 523215 FREWHELCOL17 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.66 | 562016 FIREWHEEL2 34.5 523215 FREWHELCOL17 345 2
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.16 | 562323 AGI1202&1305 115 562324 AGI1202&1305 34.5 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.17 | 562727 LESBIA 115 562728 SANJONTAP 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.17 | 562728 SANJONTAP 115 562729 CAPROCKTAP1 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.17 | 562730 CAPROCKTAP2 69.0 562729 CAPROCKTAP1 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.17 | 562730 CAPROCKTAP2 69.0 562731 WHEATLAND 69.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.65 | 563171 G15082_2 34.5 563170 G15082_1 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.23 | P11:13.8:AEPW:COM1-1
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.24 | P11:13.8:AEPW:COM2-1
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.25 | P11:13.8:AEPW:COM3-1
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.26 | P11:18:AEPW:WELSH1-1
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.26 | P11:18:AEPW:WELSH3-1
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.25 | P11:24:AEPW:PIRKEY 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.13 | P11:24:AEPW:SWS3-1
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.2 | P11:24:AEPW:TURKCOAL
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20938 | 120.56 | P12:138:AEPW-OMPA:DUNCAN-4:OMDUNCN4
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20931 | 120.09 | 584560 GEN-2015-014 115 584561 G15-014XFMR1 34.5 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20927 | 120.29 | P12:138:AEPW:ARSHILL4:STLGENS4
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20933 | 120.51 | P12:138:AEPW:SANTAFE:DUNCAN-4
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.5 | 588480 A16-010_SUB 115 3WXFMR A16-010_SUB 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20938 | 120.55 | P12:138:AEPW:DUNCAN-4:L.E.S.-4
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 119.91 | 588761 G17-033XFMR1 34.5 588760 GEN-2017-033 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 119.91 | 588765 G17-033XFMR2 34.5 588760 GEN-2017-033 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.51 | 588861 G17-047XFMR1 34.5 588860 GEN-2017-047 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20911 | 120.25 | P12:138:AEPW:ELKCTY-4:CLINTJC4
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.49 | P12:138:AEPW:SHERID4:112GORE4
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21173 | 122.68 | P12:345:AEPW:L.E.S7:TERRYRD7
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21173 | 122.67 | P12:345:AEPW:L.E.S7:TERRYRD7
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21172 | 122.65 | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21247 | 122.27 | P12:345:AEPW-OKGE:L.E.S.-7:GRACMNT7
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21247 | 122.24 | P12:345:AEPW-OKGE:L.E.S.-7:GRACMNT7
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.2096 | 120.48 | P12:345:AEPW-OKGE:PITTSB-7:JOHNCO7
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.2092 | 120.25 | P12:345:AEPW-OKGE:PITTSB-7:SEMINOL7
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20941 | 120.52 | P12:345:AEPW-WFEC:VALIANT7:HUGO7
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21233 | 123.25 | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.55 | P22:345:AMMO::LABADIE:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.53 | P22:345:AMMO::LABADIE:2
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.55 | P22:345:AMMO::LABADIE:3
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.55 | P22:345:AMMO::LABADIE:4
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.54 | P22:345:AMMO::RUSHISLAND:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.51 | P22:345:AMMO::RUSHISLAND:2
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20927 | 120.24 | P13:138-13.8:AEPW:COMANC-4_#2
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20867 | 119.94 | P13:138-230:AEPW:ELKCTY-4
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20927 | 120.26 | P13:138-24:AEPW:PIRKEY 4
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20931 | 120.15 | P13:138-24:AEPW:S.W.S.-4
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20927 | 120.21 | P13:138-24:AEPW:TURK 4
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20943 | 120.54 | P13:138-345:AEPW:L.E.S.-4_#2
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20928 | 120.55 | P23:500:EES-EAI:KEO:B4941
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20928 | 120.53 | P23:500:EES-EAI:KEO:B4921
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20909 | 120.51 | 640183 GENTLMN3 345 640325 REDWILO3 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.48 | P11:26:EES-EAI:INDEP2:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20927 | 120.51 | P23:500:EES-EAI:INDEP2:B6126
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.51 | P23:500:EES-EAI:PD:INDEP2:LN:FK479
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20928 | 120.26 | P13:345-18:AEPW:WELSH 7_#1
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20928 | 120.26 | P13:345-18:AEPW:WELSH 7_#3
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.25 | P13:69-13.8:AEPW:COMANC-2
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20923 | 120.5 | 648513 GRPR1 3 345 652532 GR PRAIRIE 3 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.56 | P11:024:DPC:ALMA2:6
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20923 | 120.53 | 652537 WHITE 3 345 659286 DEERCREK-BE3 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20924 | 120.48 | 652568 GROTONSOUTH7 115 659275 GROTON_G-BE7 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20923 | 120.53 | 659286 DEERCREK-BE3 345 3WXFMR DEERCRK KU1A 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.49 | 672540 QE 6 138 672541 CORY 6 138 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.53 | 672601 BD 4 230 672306 BD 6G 18.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.53 | 672610 POPLAR 4 230 672310 POPLAR 1G 18.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.53 | 672610 POPLAR 4 230 672311 POPLAR 2G 18.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.53 | 672621 SHAND 4 230 672321 SHAND 1G 18.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.51 | 672649 CODETTE 4 230 672650 NIPAWIN 4 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.5 | 672685 SWIFTCU 4 230 672389 CHINOOK 1G 18.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.5 | 672688 PASQUA 4 230 673390 FUT-PQ1X 18.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.55 | 672696 BRADA 4 230 672699 NBEC 4 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.48 | 672699 NBEC 4 230 672392 NBEC GT 1G 18.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.49 | P13:345-230:CLEC:DOLET:5092
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.6 | P23:345:MDU::COYOTE::5707-5712-5715::::
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.76 | P23:345:MEC:CBEC 905
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.72 | P23:345:MEC:CBEC 908
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.64 | P23:345:MEC:RAUN 0180
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.71 | P23:345:MEC:RAUN 0210
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.64 | P23:345:MEC:LOUISA 954
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.64 | P23:345:MEC:LOUISA 964
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.5 | P21:115:XEL:AUTO-SINGLE:CHEMOLT7:LSPOWER7:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.49 | P21:115:XEL:AUTO-SINGLE:FARIBALTP7:FARIBALTGEN:Z
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.61 | P21:230:OTP:AUTO-SINGLE:SQBUTTE4:YNG24:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.59 | P23:345:OTP:CENTER 3:3215(1)
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.59 | P23:345:OTP:CENTER 3:3225(1)
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 119 | 760494 GEN-2017-146 230 760498 G17-146-TAP 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 119 | 760495 G17-146-XFM1 34.5 760494 GEN-2017-146 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.26 | 761356 G17-239-XFMR 34.5 761355 GEN-2017-239 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.26 | 761359 G17-239-XFMR 34.5 761355 GEN-2017-239 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 114.95 | 762132 GEN-2017-158 230 763252 G18-099-XFM1 34.5 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 114.95 | 762132 GEN-2017-158 230 763255 G18-099-XFM2 34.5 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 115.52 | 762133 G17-158XFM1 34.5 762132 GEN-2017-158 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 115.52 | 762136 G17-158XFM2 34.5 762132 GEN-2017-158 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 117.81 | 762216 G17-151TAP 345 762217 GEN-2017-151 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21174 | 121.31 | 762216 G17-151TAP 345 762467 G18-015-TAP 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 119.71 | 762218 G17-151XFM1 34.5 762217 GEN-2017-151 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 119.71 | 762221 G17-151XFM2 34.5 762217 GEN-2017-151 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 119.71 | 762224 G17-151XFM3 34.5 762217 GEN-2017-151 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 119.71 | 762227 G17-151XFM4 34.5 762217 GEN-2017-151 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.26 | 762438 GEN-2018-004 115 762442 G18-004-TAP 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 118.8 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 119.55 | 762461 G18-015-XFM1 34.5 762460 GEN-2018-015 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 119.55 | 762464 G18-015-XFM2 34.5 762460 GEN-2018-015 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21061 | 120.87 | 762467 G18-015-TAP 345 763215 G18-092-TAP 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 118.04 | 763087 GEN-2018-073 345 763088 G18-073-XFM1 34.5 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 119.21 | 763087 GEN-2018-073 345 763091 G18-073-XFM2 34.5 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 114.92 | 763120 GEN-2018-081 230 763121 G18-081-XFM1 34.5 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 117.23 | 763120 GEN-2018-081 230 764011 G19-074-XFM1 34.5 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 117.2 | 763186 GEN-2018-089 230 763187 G18-089-XFM1 34.5 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 118.06 | 763208 GEN-2018-092 345 763215 G18-092-TAP 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 119.2 | 763208 GEN-2018-092 345 763220 G18-092-XFM1 34.5 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 119.2 | 763208 GEN-2018-092 345 763223 G18-092-XFM2 34.5 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 117.6 | 763241 GEN-2018-097 230 763296 G18-111-XFM1 34.5 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 116.95 | 763241 GEN-2018-097 230 763307 G18-112-XFM1 34.5 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 116.95 | 763241 GEN-2018-097 230 763310 G18-112-XFM2 34.5 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 116.67 | 763241 GEN-2018-097 230 763395 G18-124-XFM1 34.5 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 116.67 | 763241 GEN-2018-097 230 763398 G18-124-XFM2 34.5 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 116.31 | 763483 GEN-2019-003 230 763484 G19-003-XFM1 34.5 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 119.03 | 763483 GEN-2019-003 230 763605 G19-021-XFM1 34.5 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 119.65 | 763516 GEN-2019-011 345 763517 G19-011-XFM1 34.5 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.06 | 763879 GEN-2019-056 115 763880 G19-056XFM1 34.5 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.49 | P13:345,230:CLEC::DOLHILL::1
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.29 | P13:345,24:CLEC::G1DOLHILL::1
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20892 | 120.51 | P42:345:OKGE:SB_BVTY7305
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.2091 | 120.23 | P23:345:WERE:BUFF_345-534::
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.2091 | 120.23 | P23:345:WERE:BUFF_345-543::
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20922 | 120.66 | P23:345:WERE:JEC_345-15::
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.2092 | 120.62 | P23:345:WERE:JEC_345-16::
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20922 | 120.66 | P23:345:WERE:JEC_345-19::
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20922 | 120.66 | P23:345:WERE:JEC_345-20::
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.2092 | 120.29 | P23:345:WERE:WICH_345-50::
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20925 | 120.87 | P23:345:WERE:WOLF_345-50::
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.87 | P23:345:WERE:WOLF_345-60::
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20927 | 120.28 | P42:345:AEPW:WELSH CB 10620 NBTB+FAULT
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.27 | P41:345:AEPW:WELSH CB 10630 NBTB+FAULT
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.26 | P41:345:AEPW:WELSH CB 11670 NBTB+FAULT
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20929 | 120.53 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.26 | P41:345:AEPW:WELSH CB 12540 NBTB+FAULT
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20928 | 120.49 | P43:345:AEPW:CHAMBERS SPRING CB 12720 NBTB+FAULT
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20928 | 120.49 | P42:345:AEPW:CHAMBERS SPRING CB 13720 NBTB+FAULT
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20928 | 120.49 | P42:345:AEPW:CHAMBERS SPRING CB 13850 NBTB+FAULT
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21233 | 121.76 | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.2128 | 122.49 | P42:345:AEPW:LAWTON EASTSIDE CB 3413A NBTB+FAULT
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21314 | 122.73 | P42:345:AEPW:LAWTON EASTSIDE CB 3425A NBTB+FAULT
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21246 | 123.34 | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.2096 | 120.48 | P42:345:AEPW:PITTSBURG CB 3433A NBTB+FAULT
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20936 | 120.18 | P42:345:AEPW:PITTSBURG CB 3441A NBTB+FAULT
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.2092 | 120.25 | P42:345:AEPW:PITTSBURG CB 3445A NBTB+FAULT
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21173 | 122.67 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21173 | 122.67 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21173 | 122.65 | P42:345:AEPW:TERRYRD_CB_3421A_NBTB
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20924 | 120.65 | P23:345:KCPL:LACYGNE_R2-5::LACYGU2-LACYGNE-STILWELL
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20924 | 120.28 | P45:345:UMZW:# 1328 #: GI IN NE.
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20927 | 120.28 | P23:345:AEPW:WELSH CB 10620 NBTB
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.27 | P23:345:AEPW:WELSH CB 10630 NBTB
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.26 | P23:345:AEPW:WELSH CB 11670 NBTB
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20929 | 120.53 | P23:345:AEPW:WELSH CB 11990 NBTB
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.26 | P23:345:AEPW:WELSH CB 12540 NBTB
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20928 | 120.49 | P23:345:AEPW:CHAMBERS SPRING CB 12720 NBTB
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20928 | 120.49 | P23:345:AEPW:CHAMBERS SPRING CB 13720 NBTB
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20928 | 120.49 | P23:345:AEPW:CHAMBERS SPRING CB 13850 NBTB
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21233 | 122.19 | P23:345:AEPW:OKLAUNION CB 3401A NBTB
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.2128 | 122.49 | P23:345:AEPW:LAWTON EASTSIDE CB 3413A NBTB
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21314 | 122.73 | P23:345:AEPW:LAWTON EASTSIDE CB 3425A NBTB
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21246 | 123.34 | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.2096 | 120.48 | P23:345:AEPW:PITTSBURG CB 3433A NBTB
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20936 | 120.18 | P23:345:AEPW:PITTSBURG CB 3441A NBTB
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.2092 | 120.25 | P23:345:AEPW:PITTSBURG CB 3445A NBTB
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21173 | 122.67 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21173 | 122.67 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21173 | 122.65 | P23:345:AEPW:TERRYRD_CB_3421A_NBTB
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20956 | 120.48 | P12:138:AEPW:S.W.S.-4:L.E.S.-4
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20925 | 120.54 | P11:161:GMO:DOGWOOD_COMBINED_CYCLE_UNIT_OUTAGE
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.54 | P11:115:SUNC:GARDENCITY_S2:97:531459(2)
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20912 | 120.25 | P12:345:PWT:BUFF-THIS_345_1::
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20912 | 120.25 | P12:345:PWT:BUFF-THIS_345_2::
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20935 | 120.52 | P12:069:WFEC:ANADRKO_WATONGA
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20944 | 120.54 | P23:345:AEPW:VALLIANT CB 3413A NBTB
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.2095 | 120.56 | P23:345:AEPW:VALLIANT CB 3417A NBTB
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.2119 | 122.82 | P23:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21446 | 125.21 | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20944 | 120.54 | P42:345:AEPW:VALLIANT CB 3413A NBTB+FAULT
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.2095 | 120.56 | P42:345:AEPW:VALLIANT CB 3417A NBTB+FAULT
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.2119 | 122.82 | P42:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB+FAULT
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21446 | 125.21 | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20466 | 117.77 | P42:345:OKGE:SB_BVTY7315_PRE19S
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20888 | 120.52 | P23:345:SUNC:MO_BRK188
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21045 | 120.68 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20927 | 120.23 | P12:138-13.8:AEPW:COMANC-4_#1
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20867 | 119.93 | P12:230:AEPW:ELKCITY6:CHISHOLM6
Thermal | 05ALL | 1 | 26WP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21036 | 121.03 | P12:230:AEPW:SWEETWT6:CHISHOLM6
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997711 ABBXNL844501 230 1 |  | 552.5 | 0.3412 | 164.23 | 525531 TOLK 6 230 3WXFMR TOLK 6 2
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20928 | 120.49 | P12:345:AEPW-AEPW:CHAMPSP-CLARKSV
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20927 | 120.61 | P23:345:KCPL-WERE:237LACYGNE_R1-6::LACYGU1-LACYGNE-NEOSHO
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20925 | 120.5 | P11:161:GMO:DOGWOOD_COMBINED_CYCLE_UNIT_OUTAGE_1_1
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20933 | 118.96 | P11:115:SPS:MUSTANG1&3:153MW::::
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21179 | 122.27 | P12:230:SPS:K37::1_TOLK_LAMB:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20946 | 120.48 | P12:230:SPS:K43::1_PRNGLE_HARR_E:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20929 | 120.26 | P12:230:SPS:K44::1_EPLNT_HARRW:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.2094 | 120.61 | P12:115:SPS:T04::1_TRBLNC_CASTRO:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20925 | 120.48 | P12:115:SPS:T13::1_TAYLOR_WHOBBS:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20925 | 120.26 | P12:115:SPS:T14::1_MADDOX_TAYLOR:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.73 | P12:115:SPS:T21::1_GRSSLND_GRAHAM:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20925 | 120.29 | P12:115:SPS:T23::1_PCA_POTJCT:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20927 | 120.52 | P12:115:SPS:T26::1_CHAVES_RSWLCTY:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21046 | 120.8 | P12:115:SPS:T28A::1_LAMTON_PLANTX:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.2097 | 120.54 | P12:115:SPS:T29::1_LAMTON_HALECTR:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21093 | 121.92 | P12:115:SPS:T30::1_LAMB_HOCKLY:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21093 | 121.43 | P12:115:SPS:T31::1_HOCKLY_SUNDWN:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20921 | 120.59 | P12:115:SPS:T35::1_TERRY_YOAKUM:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 121.24 | P12:115:SPS:T45::1_NORRIS_OASIS:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21052 | 120.73 | P12:115:SPS:T59::1_CARGIL_CURRY:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21023 | 120.66 | P12:115:SPS:T67::1_HAPPY_KRESS:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20921 | 120.96 | P12:115:SPS:T71::1_CRLSLE_YUMA:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20934 | 120.57 | P12:115:SPS:T81::1_COX_FLOYD:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20925 | 120.57 | P12:115:SPS:T83::1_SP-FKFD_ALLEN:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20921 | 120.91 | P12:115:SPS:T89::1_DC_N_HIGG:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.54 | P12:115:SPS:T91::1_HIGG_RUSSELL:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20948 | 120.51 | P12:115:SPS:V04::1_EPLANT_RNDALL:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20939 | 120.5 | P12:115:SPS:V07::1_COX_HALECTR:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21038 | 120.71 | P12:115:SPS:V09::1_HALECTR_PLANTX:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20925 | 120.56 | P12:115:SPS:V12::1_PLANTX_BAILEY:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.5 | P12:115:SPS:V15::1_TUCO_INDANA:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20917 | 120.51 | P12:115:SPS:V16::1_TERRY_DC_N:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.2089 | 120.62 | P12:115:SPS:V24::1_WOLFTH_TERRY:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20943 | 120.6 | P12:115:SPS:V26::1_RSWLL_EDDY_N:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.58 | P12:115:SPS:V33::1_LUBBS_LYNN:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.2103 | 121.13 | P12:115:SPS:V37::1_CASTRO_PLANTX:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.63 | P12:115:SPS:V46::1_ALLEN_WHEELCK:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20927 | 120.95 | P12:115:SPS:V49::1_YOAKUM_SHLCO2:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20968 | 121.15 | P12:115:SPS:V55::1_SUNDWN_TERRY:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20936 | 120.98 | P12:115:SPS:V56::1_COCHRAN_SUNDWN:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20939 | 120.5 | P12:115:SPS:V78::2_CURRY_RSVLT:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20924 | 120.67 | P12:115:SPS:V81::1_LE-WAIT_LE-LVN:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.54 | P12:115:SPS:V95::1_DC_N_SHLCO2:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.5 | P12:115:SPS:W11::1_DC_S_SMINLE:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20925 | 120.54 | P12:115:SPS:W14::1_SMINLE_GAINES:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20925 | 120.5 | P12:115:SPS:W26::1_CUNGHM_OILCNTR:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 121.13 | P12:115:SPS:W32::1_PRMTR_FE-CLSIN:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.5 | P12:115:SPS:W34::1_JNSDRW_MAPCO:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20923 | 120.73 | P12:115:SPS:W35::1_GAINES_JNSDRW:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.2092 | 120.52 | P12:115:SPS:W36::1_TAYLOR_JNSDRW:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21116 | 120.93 | P12:115:SPS:W40::1_WCANYON_TRBLNC:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20936 | 120.29 | P12:115:SPS:W46::1_RHILLS_NWEST:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20953 | 120.55 | P12:115:SPS:W52::1_NEWHART_KRESS:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 121.01 | P12:115:SPS:W58::1_NORTON_LOPEZ:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.69 | P12:115:SPS:W59::1_LOPEZ_CMPBLL:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20927 | 120.96 | P12:115:SPS:W62::1_PLSTHL_CURRY:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.84 | P12:115:SPS:W64::1_PLSTHL_FE-CLV:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20927 | 120.81 | P12:115:SPS:W65::1_PLSTHL_CURRY:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.68 | P12:115:SPS:W66::1_PORTA_GREYHUND:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21116 | 120.53 | P12:115:SPS:W77::1_RNDAL_WCANYON:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.51 | P12:115:SPS:W99::1_CAPITAN_CHAVES:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20925 | 120.51 | P12:115:SPS:U03::1_CARDNL_NEF:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20922 | 121.04 | P12:115:SPS:U14::1_DC_STH_INKBSN:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20924 | 120.92 | P12:115:SPS:V15::1_INKBSN_LE-WAT:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20948 | 120.55 | P12:115:SPS:U16::1_BSHLND_OUTPST:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20948 | 120.54 | P12:115:SPS:U17::1_COLTR_OUTPST:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20933 | 120.76 | P12:115:SPS:U19::1_DEAN_PLAINS:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20948 | 120.49 | P12:115:SPS:U23::1_COLTR_HILSDE:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.201 | 127.42 | P42:345:SPS:YOAKUM:J18####:SLG1:EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.201 | 127.42 | P43:345:SPS:YOAKUM:TF#####:SLG:EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.201 | 127.42 | P42:345:SPS:YOAKUM:J17####:SLG:EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20181 | 122.69 | P43:345:SPS:TUCO:SLG::EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.201 | 127.42 | P42:345:SPS:YOAKUM:J18####:SLG2:EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20928 | 120.49 | P12:345:AEPW-AEPW:CHAMPSP-CLARKSV:::EHV::
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20925 | 120.52 | P11:18:HAST:::EGYCTR2G WEC2_LOSS OF WEC 2 GEN_:HV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20925 | 120.52 | P13:18-115:HAST:::EGYCNTR7 XFMR G2WEC 2 GSU_:HV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20925 | 120.5 | P11:161:GMO:DOGWOOD-COMBINED-CYCLE-UNIT-OUTA:::HV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20927 | 120.61 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20924 | 120.65 | P23:345:KCPL:LACYGNE-R2-5:::EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20922 | 120.66 | P11:230:WERE:JECU1-GEN:::HV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20922 | 120.66 | P11:345:WERE:JECU2-GEN:::EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20922 | 120.66 | P11:345:WERE:JECU3-GEN:::EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.88 | P11:345:WERE:WOLFU1-GEN:::EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20912 | 120.25 | P12:345:PWT:BUFF-THIS-345-1:::EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20912 | 120.25 | P12:345:PWT:BUFF-THIS-345-2:::EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.2091 | 120.23 | P23:345:WERE:BUFF-345-534:::EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.2091 | 120.23 | P23:345:WERE:BUFF-345-543:::EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20922 | 120.66 | P23:345:WERE:JEC-345-15:::EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.2092 | 120.62 | P23:345:WERE:JEC-345-16:::EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20922 | 120.66 | P23:345:WERE:JEC-345-19:::EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20922 | 120.66 | P23:345:WERE:JEC-345-20:::EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.2092 | 120.29 | P23:345:WERE:WICH-345-50:::EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20925 | 120.87 | P23:345:WERE:WOLF-345-50:::EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.87 | P23:345:WERE:WOLF-345-60:::EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.81 | P11:022:NPPD:COOPER1G:1:983:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.2092 | 120.83 | P11:023:NPPD:GENTLM1G:1:757:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20924 | 120.68 | P11:024:NPPD:GENTLM2G:2:757:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20921 | 120.68 | P13:345:OPPD:NEBCTY1G:::EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.2092 | 120.69 | P13:345:OPPD:NEBCTY2G:::EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.69 | P22:345:OPPD:S3458 NEBCTY1G:LT::EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20921 | 120.68 | P22:345:OPPD:S3458 NEBCTY1G:::EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.72 | P22:345:OPPD:S3458 NEBCTY2G:LT::EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.2092 | 120.69 | P22:345:OPPD:S3458 NEBCTY2G:::EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.69 | P23:345:OPPD:S3458 NEBCTY1G:LT::EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20921 | 120.68 | P23:345:OPPD:S3458 NEBCTY1G:::EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.72 | P23:345:OPPD:S3458 NEBCTY2G:LT::EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.2092 | 120.69 | P23:345:OPPD:S3458 NEBCTY2G:::EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.29 | P12:115:SUNC:PLYMELL-PIERCEVILLE:::HV::
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20923 | 120.53 | P11:018:UMZB:# 5 #:: DCS IN SD. DEERCREEK_MV::
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20924 | 120.5 | P11:022:UMZB:# 15 #:: LO IN ND. LELAND OLDS 1_MV::
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20925 | 120.5 | P11:020:UMZB:# 16 #:: LO IN ND. LELAND OLDS 2_MV::
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20923 | 120.61 | P11:023:UMZB:# 31 #:: AVS IN ND. ANTELOPE VALLEY 1_MV::
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20923 | 120.61 | P11:023:UMZB:# 32 #:: AVS IN ND. ANTELOPE VALLEY 2_MV::
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20919 | 120.82 | P11:024:UMZB:# 33 #:: LRS IN WY. LARAMIE RIVER STATION 1_MV::
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.49 | P13:230:UMZW:# 5135 #:: OA IN SD. FAULT ON TRANSFORMER (2).:HV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.49 | P13:230:UMZW:# 5136 #:: OA IN SD. FAULT ON TRANSFORMER (3).:HV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.5 | P13:230:UMZW:# 5137 #:: OA IN SD. FAULT ON TRANSFORMER (4).:HV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20924 | 120.28 | P23:345:UMZW:# 2423 #:: GI IN NE. GI 1596 BKR FAULT:EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20924 | 120.28 | P23:345:UMZW:# 2426 #:: GI IN NE. GI 1592 BKR FAULT:EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20924 | 120.28 | P23:345:UMZW:# 2432 #:: GI IN NE. GI 1092 BKR FAULT:EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20924 | 120.28 | P23:345:UMZW:# 2440 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1092 STUCK BKR:EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20924 | 120.28 | P23:345:UMZW:# 2444 #:: GI IN NE. GI-SWEET BRANCH FAULT & GI 1596 STUCK BKR:EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20924 | 120.28 | P23:345:UMZW:# 2446 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1196 STUCK BKR:EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20924 | 120.28 | P42:345:UMZW:# 2413 #:: FT2 IN SD. FT2-LO2 BRANCH FAULT & FT2 2992 STUCK BKR:EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20924 | 120.28 | P42:345:UMZW:# 2415 #:: FT2 IN SD. FT2-GI BRANCH FAULT & FT2 3392 STUCK BKR:EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.2093 | 120.2 | P11:138:WFEC:HUGO1:465MW :::
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20924 | 120.49 | P11:138:WFEC:MORLND2:132MW:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20924 | 120.5 | P11:138:WFEC:MORLND3:149MW :::
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20934 | 120.52 | P12:138:WFEC:ANADRKO_CLVLND::::
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.2092 | 120.25 | P12:345:OKGE-AEPW:BKRBKR20::::
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20961 | 120.7 | P12:345:OKGE:BKRBKR21::::
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20981 | 120.7 | P12:345:OKGE:BKRBKR24::::
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21172 | 122.65 | P12:345:OKGE-AEPW:BKRBKR25::::
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20895 | 120.12 | P12:345:OKGE:BKRBKR336::::
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20894 | 120.11 | P12:345:OKGE:BKRBKR336_2::::
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.2096 | 120.48 | P12:345:OKGE-AEPW:BKRBKR343::::
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21247 | 122.27 | P12:345:OKGE-AEPW:BKRBKR366::::
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21247 | 122.24 | P12:345:OKGE-AEPW:BKRBKR366::::
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21132 | 121.66 | P12:345:OKGE:BKRBKR367::::
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20962 | 120.59 | P12:345:OKGE-WFEC:BKRBKR374::::
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20962 | 120.56 | P12:345:OKGE-WFEC:BKRBKR374::::
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20899 | 120.16 | P12:345:OKGE:BKRBKR4193::::
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20899 | 120.16 | P12:345:OKGE:BKRBKR4194::::
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20889 | 120.16 | P12:345:OKGE-SPS:BKRBKR4201::::
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20889 | 120.16 | P12:345:OKGE-SPS:BKRBKR4202::::
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20893 | 119.95 | P12:345:OKGE:BKRBKR443NEW::::
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20893 | 119.95 | P12:345:OKGE:BKRBKR443NEW2::::
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20909 | 120.27 | P12:345:OKGE-ITC:BKRBKR502::::
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20909 | 120.27 | P12:345:OKGE-ITC:BKRBKR503::::
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20921 | 120.61 | P12:345:OKGE:BKRBKR604::::
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20919 | 120.72 | P12:345:OKGE:BKRBKR604_2::::
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21627 | 123.72 | P42:345:OKGE:SB_BVTY7387::::
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20966 | 120.63 | P42:345:OKGE:SB_SPCK7383::::
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20923 | 120.53 | P11:115:SUNC:GARDENCITY_S2:103:531459(2):HV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20923 | 120.54 | P11:115:SUNC:FORTDDODGE_4:157:539670(4):HV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20888 | 120.5 | P12:345:SUNC-NPPD:MINGO-REDWILLOW::531451-640325(1):EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.61 | P13:115:SUNC:HOLCOMB_GSU:::HV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20923 | 120.53 | P13:115:SUNC:S2_GSU:::HV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20923 | 120.54 | P13:115:SUNC:FORTDODGE_GSU:::HV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.48 | 300002 1THLG2 22.0 301505 5THOMHLGSU2 161 2
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.62 | 300003 1THLG3 24.0 301503 7THOMHLGSU3 345 3
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.48 | 300006 1NM G1 22.0 301536 5NEWMADGSU1 161 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.48 | 300007 1NM G2 22.0 301537 7NEWMADGSU2 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.48 | 300046 7NEWMAD 345 301537 7NEWMADGSU2 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.62 | 300049 7THOMHL 345 301503 7THOMHLGSU3 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.48 | 300103 5NEWMAD 161 301536 5NEWMADGSU1 161 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.48 | 300132 5THMHLB2 161 301505 5THOMHLGSU2 161 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20925 | 120.29 | 300739 7BLACKBERRY 345 532797 WOLFCRK7 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.56 | P11:20:AMMO:1LAB�� G1:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.54 | P11:20:AMMO:1LAB�� G2:2
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.75 | P11:345:AMMO::CALLAWAY:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.56 | P11:345:AMMO::LABADIE:3
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.56 | P11:345:AMMO::LABADIE:4
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.55 | P11:345:AMMO::RUSHISLAND:U1
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.54 | P11:345:AMMO::RUSHISLAND:U2
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.53 | P11:138:AMMO::SIOUX:2
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.49 | P13:345-230:CLEC::DOLHILL7:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.29 | P11:345-24:CLEC::DOLHILL7:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.29 | P11:24:CLEC::G1DOLHIL:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.53 | P12:765:AEP:AEP ROCKP-AEP JEFF 765
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.48 | P11:HV:EES::1ISES U1:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.25 | P11:HV:EES::PIRKEY 1:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.26 | P11:EHV:EES::WELSH3-1:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.2 | P11:HV:EES::TURKCOAL:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.48 | P12:HV:EES::5ISES%:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.74 | P12:EHV:EES::7CALAWY 1:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20928 | 120.49 | P12:EHV:EES::CHAMSPR7!:CLARKSV7!:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20927 | 120.21 | P12:HV:EES::TURK 4%:1(1)
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20928 | 120.26 | P12:EHV:EES::WELSH 7:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20928 | 120.26 | P12:EHV:EES::WELSH 7:1(1)
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20927 | 120.26 | P12:HV:EES::PIRKEY 4:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.53 | 344011 7HUGHES 345 344012 7HPW-N 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.55 | 344884 7LABADIE1 345 344894 1LAB G1 20.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.53 | 344885 7LABADIE2 345 344895 1LAB G2 20.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.55 | 344886 7LABADIE3 345 344896 1LAB G3 20.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.55 | 344887 7LABADIE4 345 344897 1LAB G4 20.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.54 | 345667 7RUSH 1 345 345670 1RUSH G1 18.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.53 | 345668 7RUSH 2 345 345671 1RUSH G2 18.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.52 | 345755 4SIOUX 1 138 345756 1SIOUX 1 18.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.52 | 345764 4SIOUX 2 138 345765 1SIOUX 2 18.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.6 | P12:345:MDU::CENTER:COYOTE:1::::
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.6 | P13:345:MDU:COYOTE GSU LOSS:COYOTE::1::::
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.82 | P11:345:MEC-NPPD:COOPER 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.72 | P11:24:XEL:AUTO-SINGLE:SHERC31G:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.72 | P11:24:XEL:AUTO-SINGLE:SHERC32G:2
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.81 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.64 | P11:20:XEL:AUTO-SINGLE:PRIS31G:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.63 | P11:20:XEL:AUTO-SINGLE:PRIS32G:2
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.68 | P11:22:XEL:AUTO-SINGLE:MNTCE31G:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.64 | P11:20:XEL:AUTO-SINGLE:KING31G:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.48 | P11:18:XEL:AUTO-SINGLE:BLKD76G:6
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.69 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.69 | P11:22:GRE:AUTO-SINGLE:GRE-COAL42G:2
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.61 | P11:24:OTP:AUTO-SINGLE:BIGSTN1G:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.63 | P11:20:OTP:AUTO-SINGLE:CENTER2G:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.52 | P11:22:OTP:AUTO-SINGLE:CENTER1G:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.61 | P11:24:OTP:AUTO-SINGLE:COYOTE1G:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.51 | P11:24:DPC:AUTO-SINGLE:GENOA53G:3
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.5 | P12:115:XEL:AUTO-SINGLE:CHEMOLT7:LSPOWER7:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.49 | P12:115:XEL:AUTO-SINGLE:FARIBALTP7:FARIBALTGEN:Z
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.61 | P12:230:OTP:AUTO-SINGLE:SQBUTTE4:YNG24:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.69 | P13:24-345:XEL:AUTO-SINGLE:SHERC31G:SHERCO3:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.69 | P13:24-345:XEL:AUTO-SINGLE:SHERC32G:SHERCO3:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.78 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.64 | P13:20-345:XEL:AUTO-SINGLE:PRIS31G:PRISLD3:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.64 | P13:20-345:XEL:AUTO-SINGLE:PRIS32G:PRISLD3:2
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.68 | P13:22-345:XEL:AUTO-SINGLE:MNTCE31G:MNTCELO3:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.62 | P13:20-345:XEL:AUTO-SINGLE:KING31G:ASKING3:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.48 | P13:18-115:XEL:AUTO-SINGLE:BLKD76G:BLKDG27:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.67 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL41G:GRE-COALCR4:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.67 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL42G:GRE-COALCR4:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.6 | P13:230-24:OTP:AUTO-SINGLE:BIGSTON4:BIGSTN1G:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.61 | P13:20-230:OTP:AUTO-SINGLE:CENTER2G:YNG24:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.51 | P13:22-230:OTP:AUTO-SINGLE:CENTER1G:CENTER4:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.6 | P13:24-345:OTP:AUTO-SINGLE:COYOTE1G:COYOTE3:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.5 | P13:24-161:DPC:AUTO-SINGLE:GENOA53G:GENOA5:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.55 | P13:24-161:DPC:AUTO-SINGLE:JPM:ALMA5:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.6 | P11:115:XEL:RIV COMBINE CYCLE
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.51 | P12:115:XEL:BDS #2 5
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.49 | P11:115:XEL:HBR #6 7 8
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.63 | P23:345:XEL:8H14 PRI
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.64 | P23:345:XEL:8H17 PRI AS
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.78 | P23:345:XEL:8N28 SHC
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.7 | P23:345:XEL:8N22 SHC
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.69 | P23:345:XEL:8N17 SHC
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.68 | P23:345:XEL:8N8 MNN
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.63 | P23:345:XEL:8P1 KING
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.63 | P23:345:XEL:8P2 KING
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.5 | P11:22:ALTW:AUTO-SINGLE:LANS54G:4
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.64 | P11:22:ALTW:AUTO-SINGLE:ARNOLD1G:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.67 | P11:24:ALTW:AUTO-SINGLE:OTTUMW1G:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.49 | P13:22-161:ALTW:AUTO-SINGLE:LANS54G:LANSINGL15:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.63 | P13:22-161:ALTW:AUTO-SINGLE:ARNOLD1G:ARNOLD5:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.66 | P13:24-161:ALTW:AUTO-SINGLE:OTTUMW1G:OTTUMWA5:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.74 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.8 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.65 | P11:22:MEC:AUTO-SINGLE:NEAL3G:3
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.73 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.66 | P11:24:MEC:AUTO-SINGLE:LOUIS31G:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.72 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.76 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.64 | P13:345-22:MEC:AUTO-SINGLE:RAUN3:NEAL3G:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.71 | P13:345-24:MEC:AUTO-SINGLE:RAUN3:NEAL4G:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.64 | P13:345-24:MEC:AUTO-SINGLE:LOUISA3:LOUIS31G:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20922 | 120.66 | P11:230:WERE:JECU1_GEN::
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20922 | 120.66 | P11:345:WERE:JECU2_GEN::
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20922 | 120.66 | P11:345:WERE:JECU3_GEN::
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.88 | P11:345:WERE:WOLFU1_GEN::
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20933 | 120.48 | 511453 DUNCAN-4 138 511552 DUNCHERTP4 138 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20933 | 120.48 | 511455 D.E.S.-4 138 511552 DUNCHERTP4 138 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.48 | 511456 O.K.U.-7 345 511565 OKLAUN HVDC7 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 119.42 | 511456 O.K.U.-7 345 588760 GEN-2017-033 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21233 | 122.19 | 511456 O.K.U.-7 345 763215 G18-092-TAP 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21246 | 122.76 | 511468 L.E.S.-7 345 762467 G18-015-TAP 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21143 | 122.19 | 511468 L.E.S.-7 345 763215 G18-092-TAP 345 2
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20938 | 120.56 | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21045 | 120.68 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20262 | 117.21 | 511553 CHISHOLM7 345 523961 POTTER_CO 7 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20262 | 117.21 | 511553 CHISHOLM7 345 523961 POTTER_CO 7 345 2
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20633 | 119.86 | 511553 CHISHOLM7 345 755000 WWDBORDT 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20924 | 120.5 | 511557 CHISHOLM6 230 3WXFMR CHISHOLM6 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20939 | 120.51 | 514801 MINCO 7 345 555234 NSUB345 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20852 | 120.15 | 515375 WWRDEHV7 345 755000 WWDBORDT 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21627 | 123.76 | 515458 BORDER 7 345 560022 CRAWFISH_DR 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21627 | 123.7 | 515458 BORDER 7 345 755000 WWDBORDT 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20924 | 120.51 | 515618 BALKOW 7 345 3WXFMR BALKOW 7 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20924 | 120.5 | 515618 BALKOW 7 345 3WXFMR BALKOW 7 1_Dup1
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20919 | 120.73 | 515634 PALDR1W7 345 3WXFMR PALO2 _1 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.63 | 515677 BADGER 7 345 563170 G15082_1 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.49 | 522800 MU-TULIA 3 115 525179 TULIA_TP 3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.63 | 522892 MU-BROWNFLD2 69.0 526761 BROWNFLD_TP2 69.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20923 | 120.52 | 523093 HITCHLAND 3 115 523174 GOODWELLWND3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21053 | 120.53 | 523095 HITCHLAND 6 230 523309 MOORE_CNTY 6 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.88 | 523097 HITCHLAND 7 345 523112 NOVUS1 7 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.93 | 523097 HITCHLAND 7 345 523215 FREWHELCOL17 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20717 | 119.43 | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.99 | 523097 HITCHLAND 7 345 560252 G10-14 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.5 | 523099 TC-DRYTRLS 3 115 588480 A16-010_SUB 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.74 | 523112 NOVUS1 7 345 3WXFMR NOVUS XF2 2
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.52 | 523112 NOVUS1 7 345 3WXFMR XIANA2011198 _1 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20923 | 120.5 | 523118 BUFF_DUNES 7 345 523853 FINNEY 7 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.51 | 523120 COLE 3 115 588860 GEN-2017-047 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20935 | 120.48 | 523221 XIT_INTG 6 230 3WXFMR SIEM_T126401 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20946 | 120.48 | 523267 PRINGLE 6 230 3WXFMR ENRCO13617-1 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20946 | 120.48 | 523267 PRINGLE 6 230 523979 HARRNG_EST 6 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20988 | 120.61 | 523309 MOORE_CNTY 6 230 523323 MCDWL_CREEK6 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.2096 | 120.53 | 523323 MCDWL_CREEK6 230 523959 POTTER_CO 6 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20896 | 120.85 | 523959 POTTER_CO 6 230 523979 HARRNG_EST 6 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21737 | 121.98 | 523959 POTTER_CO 6 230 524267 BUSHLAND 6 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.2171 | 122.4 | 523959 POTTER_CO 6 230 525461 NEWHART 6 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21287 | 129.34 | 523961 POTTER_CO 7 345 3WXFMR WAUK 90343-A 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20912 | 120.79 | 523961 POTTER_CO 7 345 524296 SPNSPUR_WND7 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20928 | 120.27 | 523977 HARRNG_WST 6 230 523971 HARRNGTON1 1 24.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20905 | 120.79 | 523977 HARRNG_WST 6 230 524010 ROLLHILLS 6 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20925 | 120.22 | 523978 HARRNG_MID 6 230 523979 HARRNG_EST 6 230 @1
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20925 | 120.29 | 524010 ROLLHILLS 6 230 3WXFMR WAUK WT01104 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20948 | 120.55 | 524267 BUSHLAND 6 230 3WXFMR WH 7001795 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.22387 | 122.23 | 524267 BUSHLAND 6 230 524623 DEAFSMITH 6 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20912 | 120.89 | 524296 SPNSPUR_WND7 345 524299 SPNSPUR_COL7 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20912 | 120.89 | 524299 SPNSPUR_COL7 345 3WXFMR SPNSPUR_COL7 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21317 | 120.9 | 524415 AMA_SOUTH 6 230 525213 SWISHER 6 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 121.01 | 524502 NORTON 3 115 524509 FE-TUCMCARI3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21116 | 120.82 | 524575 DS-#25+ 3 115 524597 PANDAHFD 3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21116 | 120.9 | 524575 DS-#25+ 3 115 524630 TIERABLANCA3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.5 | 524604 HEREFRD_SB 2 69.0 524608 HERFRD_STH 2 69.0 *1
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.22236 | 125.98 | 524623 DEAFSMITH 6 230 760498 G17-146-TAP 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.78 | 524721 DS-#15&#19+2 69.0 524745 CASTRO_CNTY2 69.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.84 | 524764 NORRIS_TP 3 115 524801 NORRIS 3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20932 | 120.49 | 524770 PLSNT_HILL 6 230 3WXFMR EFAE1100068A 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.84 | 524776 N_CLOVIS_TP3 115 524777 N_CLOVIS 3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.78 | 524790 CANNON_TP 3 115 524794 CANNONAFB 3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21343 | 127.03 | 524875 OASIS 6 230 524885 SN_JUAN_TAP6 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20999 | 121.66 | 524875 OASIS 6 230 524909 ROOSEVELT 6 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21325 | 127.79 | 524885 SN_JUAN_TAP6 230 527483 CHAVES_CNTY6 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20942 | 120.65 | 524909 ROOSEVELT 6 230 3WXFMR ABB LMM60042 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21617 | 125.82 | 524909 ROOSEVELT 6 230 525531 TOLK 6 230 2
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 121.25 | 524923 PORTALES 2 69.0 524929 RO-PORT_MTR2 69.0 @1
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.88 | 524923 PORTALES 2 69.0 524941 PORTALES#1 2 69.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.84 | 525023 BC-BAIL_MTR2 69.0 525027 BAILEYCO 2 69.0 @1
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.2103 | 120.8 | 525056 BC-EARTH 3 115 525480 PLANT_X 3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.57 | 525192 KRESS_INT 3 115 3WXFMR ENRCO 136155 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20937 | 120.29 | 525213 SWISHER 6 230 3WXFMR SIEM_T127101 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21223 | 121.59 | 525213 SWISHER 6 230 525461 NEWHART 6 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.54 | 525272 KISER 3 115 3WXFMR VON 13819/1 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.81 | 525326 COX 3 115 3WXFMR ELCO 13474-3 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.81 | 525414 LAMTON 3 115 3WXFMR ASEA MLL9204 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.22535 | 123.54 | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21198 | 122.16 | 525481 PLANT_X 6 230 3WXFMR WH ALM20171 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21856 | 127.05 | 525481 PLANT_X 6 230 526435 SUNDOWN 6 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.22236 | 124.03 | 525481 PLANT_X 6 230 760498 G17-146-TAP 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21271 | 120.86 | 525481 PLANT_X 6 230 762174 G17-218TAP 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21313 | 120.92 | 525481 PLANT_X 6 230 762174 G17-218TAP 230 2
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.22055 | 128.41 | 525531 TOLK 6 230 525586 NEEDMORE 6 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21179 | 122.27 | 525531 TOLK 6 230 525637 LAMB_CNTY 6 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.23816 | 127.4 | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21436 | 121.08 | 525531 TOLK 6 230 762174 G17-218TAP 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21471 | 121.13 | 525531 TOLK 6 230 762174 G17-218TAP 230 2
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.3412 | 162.04 | 525549 TOLK 7 345 3WXFMR ABBXNL844501 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.22055 | 128.41 | 525586 NEEDMORE 6 230 526935 YOAKUM 6 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21179 | 122.27 | 525637 LAMB_CNTY 6 230 3WXFMR WH ALM20172 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.54 | 525828 TUCO_INT 3 115 3WXFMR DS F78800913 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21357 | 120.96 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21476 | 121.11 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _9 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20181 | 122.69 | 525832 TUCO_INT 7 345 526936 YOAKUM_345 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21093 | 121.33 | 526020 HOCKLEY 3 115 526036 LC-OPDYKE 3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21093 | 121.18 | 526036 LC-OPDYKE 3 115 526434 SUNDOWN 3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.57 | 526160 CARLISLE 3 115 3WXFMR WH RLP38371 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.79 | 526162 LP-DOUD_TP 3 115 526176 LP-DOUD 3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.82 | 526268 LUBBCK_STH 3 115 3WXFMR NA 70454A 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20936 | 120.81 | 526361 COCHRAN 3 115 526424 PACIFIC 3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20936 | 120.9 | 526424 PACIFIC 3 115 526434 SUNDOWN 3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20968 | 120.94 | 526434 SUNDOWN 3 115 526445 AMOCO_TP 3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20921 | 120.51 | 526435 SUNDOWN 6 230 3WXFMR UPDATE LATER _12 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20944 | 124.22 | 526435 SUNDOWN 6 230 526460 AMOCO_SS 6 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20968 | 120.8 | 526445 AMOCO_TP 3 115 526484 LG-LEVELAND3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20944 | 121.88 | 526460 AMOCO_SS 6 230 526935 YOAKUM 6 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20968 | 120.79 | 526484 LG-LEVELAND3 115 526491 LG-CLAUENE 3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20923 | 120.51 | 526525 WOLFFORTH 6 230 3WXFMR UPDATE LATER _13 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20916 | 122.38 | 526935 YOAKUM 6 230 527028 INK_BASIN 6 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20181 | 129.67 | 526936 YOAKUM_345 345 527896 HOBBS_INT 7 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20905 | 121.79 | 527028 INK_BASIN 6 230 527894 HOBBS_INT 6 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20921 | 120.9 | 527130 DENVER_N 3 115 527286 HIGGEAST 3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20928 | 119.59 | 527149 MUSTANG 6 230 527151 GS-MUSTANG 6 230 @1
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.62 | 527202 SEAGRAVES 3 115 3WXFMR ABB MLL92408 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.59 | 527212 DIAMONDBACK3 115 3WXFMR HOW 36773714 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20921 | 120.88 | 527286 HIGGEAST 3 115 527363 HIGG 3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20923 | 120.62 | 527325 OXY_WSEM_TP3 115 527362 JOHNSON_DRW3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.59 | 527340 DOSS 3 115 3WXFMR ELCO 13566/1 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.58 | 527345 LEGACY 2 69.0 527350 XTO_ROBRTSN2 69.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.58 | 527346 LEGACY 3 115 3WXFMR VROL 13735-1 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.56 | 527350 XTO_ROBRTSN2 69.0 527355 BOARDMAN 2 69.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.51 | 527355 BOARDMAN 2 69.0 527365 FLANNAGAN 2 69.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.5 | 527360 MAPCO 3 115 527362 JOHNSON_DRW3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.58 | 527362 JOHNSON_DRW3 115 528775 LE-ERF 3 115 @1
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.48 | 527370 TENNECO_TAP2 69.0 527371 TENNECO 2 69.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20928 | 120.29 | 527470 CHVS_SLRCOL3 115 527482 CHAVES_CNTY3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21101 | 121.58 | 527483 CHAVES_CNTY6 230 527799 EDDY_NORTH 6 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.49 | 527508 PRICE 3 115 527509 PRICE_TAP 3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.5 | 527514 CV-PINE 2 69.0 527563 ROSWLL_INT 2 69.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.52 | 527563 ROSWLL_INT 2 69.0 527575 SW_4702 2 69.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20943 | 120.61 | 527564 ROSWLL_INT 3 115 527597 TWEEDY 3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.52 | 527575 SW_4702 2 69.0 527589 CV-ORCHARD 2 69.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.48 | 527589 CV-ORCHARD 2 69.0 527619 DEXTER_TP 2 69.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20919 | 120.69 | 527653 MILO_WIND 1 34.5 527655 RSVLT_CC_E 7 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20909 | 120.67 | 527654 RSVLT_CC_W 7 345 527655 RSVLT_CC_E 7 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20909 | 120.92 | 527654 RSVLT_CC_W 7 345 527666 RSVLT_COL1 7 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20902 | 120.92 | 527655 RSVLT_CC_E 7 345 527656 CROSSROADS 7 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20909 | 120.92 | 527666 RSVLT_COL1 7 345 3WXFMR RSVLT_COL1 7 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.63 | 527790 EDDY_SVC 1 8.50 527799 EDDY_NORTH 6 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20925 | 120.22 | 527864 CUNNINHAM 3 115 528348 BUCKEYE_TP 3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20925 | 120.52 | 527864 CUNNINHAM 3 115 528568 MONUMNT_TP 3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20911 | 120.69 | 527865 CUNNIGHM_N 6 230 527867 CUNNIGHM_S 6 230 *1
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20921 | 120.51 | 527865 CUNNIGHM_N 6 230 527963 POTASH_JCT 6 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20921 | 120.51 | 527867 CUNNIGHM_S 6 230 527894 HOBBS_INT 6 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20925 | 120.3 | 527894 HOBBS_INT 6 230 3WXFMR ME C0482951 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20923 | 120.57 | 527894 HOBBS_INT 6 230 527903 HOBBS_PLT3 1 18.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.23 | 527896 HOBBS_INT 7 345 527965 KIOWA 7 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.2 | 527896 HOBBS_INT 7 345 528027 RDRUNNER 7 345 UC
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.2 | 527896 HOBBS_INT 7 345 528027 RDRUNNER 7 345 XA
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20925 | 120.29 | 527965 KIOWA 7 345 528027 RDRUNNER 7 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.55 | 528024 RR_SVC_HV 3 115 528021 RDRUNNR_SVC1 15.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.64 | 528024 RR_SVC_HV 3 115 528025 RDRUNNER 3 115 Z1
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.25 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.5 | 528182 NORTH_LOVNG3 115 528193 BLACKRIVER 3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.63 | 528222 CHINA_DRAW 3 115 528225 CD_SVC_HV 3 115 Z1
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20924 | 120.22 | 528333 LE-WEST_SUB3 115 528334 LE-NRTH_INT3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20925 | 120.29 | 528341 LE-SANANDRS3 115 528627 LE-TXACO_TP3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20925 | 120.25 | 528348 BUCKEYE_TP 3 115 528627 LE-TXACO_TP3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20925 | 120.24 | 528463 SANGER_SW 3 115 528575 OXYPERMIAN 3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20925 | 120.24 | 528463 SANGER_SW 3 115 762442 G18-004-TAP 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20925 | 120.52 | 528568 MONUMNT_TP 3 115 528581 BYRD_TP 3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20925 | 120.28 | 528574 OXY_NHU_RCF3 115 528575 OXYPERMIAN 3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20925 | 120.5 | 528596 CARDINAL 3 115 528605 TARGA 3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20925 | 120.53 | 528603 NA_ENRICH 3 115 528605 TARGA 3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.61 | 528617 LE-WAITS 2 69.0 528325 LE-WAITS 3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.51 | 528617 LE-WAITS 2 69.0 528714 LE-FORT_SW 2 69.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.49 | 528617 LE-WAITS 2 69.0 528759 LE-TP51 2 69.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20925 | 120.29 | 528622 LE-SANANDRS2 69.0 528341 LE-SANANDRS3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.92 | 528626 LE-PLNSINT 2 69.0 526928 PLAINS_INT 3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.92 | 528626 LE-PLNSINT 2 69.0 528709 LE-PLNSGOAB2 69.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.52 | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.59 | 528669 LE-STKLDRTP2 69.0 528740 LE-PLANS_SW2 69.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.79 | 528709 LE-PLNSGOAB2 69.0 528740 LE-PLANS_SW2 69.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.52 | 528709 LE-PLNSGOAB2 69.0 528747 LE-ALLRED 2 69.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.51 | 528714 LE-FORT_SW 2 69.0 528718 LE-NEWTEX 2 69.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.59 | 528735 LE-PLAINSUB2 69.0 528740 LE-PLANS_SW2 69.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.52 | 528775 LE-ERF 3 115 528779 LE-TALLCOTN3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.3 | 531213 SANTAFE3 115 531408 PIERCVL3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20924 | 120.48 | 531501 BUCKNER7 345 531502 CIMRRN 7 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20924 | 120.48 | 531502 CIMRRN 7 345 531503 CIMRRN 1 34.5 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20912 | 120.24 | 531510 HARBNGR3 115 3WXFMR HARBGR345 _1 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20923 | 120.5 | 539803 IRONWOOD7 345 3WXFMR IRONWOOD MPT 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20925 | 120.59 | 542951 HAW G5 1 22.0 543665 HAWTHN5 161 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20924 | 120.63 | 542955 LAC G1 1 22.0 542981 LACYGNE7 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20923 | 120.62 | 542956 LAC G2 1 24.0 542981 LACYGNE7 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20922 | 120.67 | 542957 IAT G1 1 24.0 542982 IATAN 7 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20923 | 120.74 | 542962 IAT G2 1 24.5 542982 IATAN 7 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21174 | 119.99 | 560022 CRAWFISH_DR 345 762216 G17-151TAP 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21142 | 120.98 | 560022 CRAWFISH_DR 345 762467 G18-015-TAP 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 116.89 | 560022 CRAWFISH_DR 345 763087 GEN-2018-073 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21254 | 121.28 | 560022 CRAWFISH_DR 345 763215 G18-092-TAP 345 2
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.99 | 560252 G10-14 345 560253 G10-14-1 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.69 | 560253 G10-14-1 115 560254 G10-14-SUB1 34.5 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.69 | 560253 G10-14-1 115 560255 G10-14-SUB2 34.5 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.52 | 560581 G06-44-2 34.5 523111 NOVUS1 3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.57 | 560582 G06-44-3 34.5 560577 G06-44 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.56 | 560583 G06-44-4 34.5 560577 G06-44 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.17 | 560757 ASGI13_02_1 69.0 560758 ASGI13_02_2 34.5 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.17 | 560757 ASGI13_02_1 69.0 562731 WHEATLAND 69.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.17 | 560763 ASGI13_03_1 115 560761 ASGI13_03_2 34.5 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.66 | 562015 FIREWHEEL1 34.5 523215 FREWHELCOL17 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.66 | 562016 FIREWHEEL2 34.5 523215 FREWHELCOL17 345 2
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.16 | 562323 AGI1202&1305 115 562324 AGI1202&1305 34.5 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.17 | 562727 LESBIA 115 562728 SANJONTAP 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.17 | 562728 SANJONTAP 115 562729 CAPROCKTAP1 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.17 | 562730 CAPROCKTAP2 69.0 562729 CAPROCKTAP1 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.17 | 562730 CAPROCKTAP2 69.0 562731 WHEATLAND 69.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.65 | 563171 G15082_2 34.5 563170 G15082_1 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.23 | P11:13.8:AEPW:COM1-1
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.24 | P11:13.8:AEPW:COM2-1
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.25 | P11:13.8:AEPW:COM3-1
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.26 | P11:18:AEPW:WELSH1-1
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.26 | P11:18:AEPW:WELSH3-1
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.25 | P11:24:AEPW:PIRKEY 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.13 | P11:24:AEPW:SWS3-1
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.2 | P11:24:AEPW:TURKCOAL
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20938 | 120.56 | P12:138:AEPW-OMPA:DUNCAN-4:OMDUNCN4
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20931 | 120.09 | 584560 GEN-2015-014 115 584561 G15-014XFMR1 34.5 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20927 | 120.29 | P12:138:AEPW:ARSHILL4:STLGENS4
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20933 | 120.51 | P12:138:AEPW:SANTAFE:DUNCAN-4
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.5 | 588480 A16-010_SUB 115 3WXFMR A16-010_SUB 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20938 | 120.55 | P12:138:AEPW:DUNCAN-4:L.E.S.-4
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 119.91 | 588761 G17-033XFMR1 34.5 588760 GEN-2017-033 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 119.91 | 588765 G17-033XFMR2 34.5 588760 GEN-2017-033 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.51 | 588861 G17-047XFMR1 34.5 588860 GEN-2017-047 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20911 | 120.25 | P12:138:AEPW:ELKCTY-4:CLINTJC4
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.49 | P12:138:AEPW:SHERID4:112GORE4
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21173 | 122.68 | P12:345:AEPW:L.E.S7:TERRYRD7
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21173 | 122.67 | P12:345:AEPW:L.E.S7:TERRYRD7
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21172 | 122.65 | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21247 | 122.27 | P12:345:AEPW-OKGE:L.E.S.-7:GRACMNT7
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21247 | 122.24 | P12:345:AEPW-OKGE:L.E.S.-7:GRACMNT7
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.2096 | 120.48 | P12:345:AEPW-OKGE:PITTSB-7:JOHNCO7
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.2092 | 120.25 | P12:345:AEPW-OKGE:PITTSB-7:SEMINOL7
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20941 | 120.52 | P12:345:AEPW-WFEC:VALIANT7:HUGO7
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21233 | 123.25 | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.55 | P22:345:AMMO::LABADIE:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.53 | P22:345:AMMO::LABADIE:2
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.55 | P22:345:AMMO::LABADIE:3
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.55 | P22:345:AMMO::LABADIE:4
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.54 | P22:345:AMMO::RUSHISLAND:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.51 | P22:345:AMMO::RUSHISLAND:2
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20927 | 120.24 | P13:138-13.8:AEPW:COMANC-4_#2
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20867 | 119.94 | P13:138-230:AEPW:ELKCTY-4
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20927 | 120.26 | P13:138-24:AEPW:PIRKEY 4
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20931 | 120.15 | P13:138-24:AEPW:S.W.S.-4
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20927 | 120.21 | P13:138-24:AEPW:TURK 4
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20943 | 120.54 | P13:138-345:AEPW:L.E.S.-4_#2
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20928 | 120.55 | P23:500:EES-EAI:KEO:B4941
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20928 | 120.53 | P23:500:EES-EAI:KEO:B4921
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20909 | 120.51 | 640183 GENTLMN3 345 640325 REDWILO3 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.48 | P11:26:EES-EAI:INDEP2:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20927 | 120.51 | P23:500:EES-EAI:INDEP2:B6126
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.51 | P23:500:EES-EAI:PD:INDEP2:LN:FK479
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20928 | 120.26 | P13:345-18:AEPW:WELSH 7_#1
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20928 | 120.26 | P13:345-18:AEPW:WELSH 7_#3
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.25 | P13:69-13.8:AEPW:COMANC-2
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20923 | 120.5 | 648513 GRPR1 3 345 652532 GR PRAIRIE 3 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.56 | P11:024:DPC:ALMA2:6
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20923 | 120.53 | 652537 WHITE 3 345 659286 DEERCREK-BE3 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20924 | 120.48 | 652568 GROTONSOUTH7 115 659275 GROTON_G-BE7 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20923 | 120.53 | 659286 DEERCREK-BE3 345 3WXFMR DEERCRK KU1A 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.49 | 672540 QE 6 138 672541 CORY 6 138 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.53 | 672601 BD 4 230 672306 BD 6G 18.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.53 | 672610 POPLAR 4 230 672310 POPLAR 1G 18.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.53 | 672610 POPLAR 4 230 672311 POPLAR 2G 18.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.53 | 672621 SHAND 4 230 672321 SHAND 1G 18.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.51 | 672649 CODETTE 4 230 672650 NIPAWIN 4 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.5 | 672685 SWIFTCU 4 230 672389 CHINOOK 1G 18.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.5 | 672688 PASQUA 4 230 673390 FUT-PQ1X 18.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.55 | 672696 BRADA 4 230 672699 NBEC 4 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.48 | 672699 NBEC 4 230 672392 NBEC GT 1G 18.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.49 | P13:345-230:CLEC:DOLET:5092
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.6 | P23:345:MDU::COYOTE::5707-5712-5715::::
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.76 | P23:345:MEC:CBEC 905
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.72 | P23:345:MEC:CBEC 908
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.64 | P23:345:MEC:RAUN 0180
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.71 | P23:345:MEC:RAUN 0210
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.64 | P23:345:MEC:LOUISA 954
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.64 | P23:345:MEC:LOUISA 964
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.5 | P21:115:XEL:AUTO-SINGLE:CHEMOLT7:LSPOWER7:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.49 | P21:115:XEL:AUTO-SINGLE:FARIBALTP7:FARIBALTGEN:Z
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.61 | P21:230:OTP:AUTO-SINGLE:SQBUTTE4:YNG24:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.59 | P23:345:OTP:CENTER 3:3215(1)
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.59 | P23:345:OTP:CENTER 3:3225(1)
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 119 | 760494 GEN-2017-146 230 760498 G17-146-TAP 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 119 | 760495 G17-146-XFM1 34.5 760494 GEN-2017-146 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.26 | 761356 G17-239-XFMR 34.5 761355 GEN-2017-239 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.26 | 761359 G17-239-XFMR 34.5 761355 GEN-2017-239 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 114.95 | 762132 GEN-2017-158 230 763252 G18-099-XFM1 34.5 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 114.95 | 762132 GEN-2017-158 230 763255 G18-099-XFM2 34.5 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 115.52 | 762133 G17-158XFM1 34.5 762132 GEN-2017-158 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 115.52 | 762136 G17-158XFM2 34.5 762132 GEN-2017-158 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 117.81 | 762216 G17-151TAP 345 762217 GEN-2017-151 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21174 | 121.31 | 762216 G17-151TAP 345 762467 G18-015-TAP 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 119.71 | 762218 G17-151XFM1 34.5 762217 GEN-2017-151 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 119.71 | 762221 G17-151XFM2 34.5 762217 GEN-2017-151 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 119.71 | 762224 G17-151XFM3 34.5 762217 GEN-2017-151 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 119.71 | 762227 G17-151XFM4 34.5 762217 GEN-2017-151 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.26 | 762438 GEN-2018-004 115 762442 G18-004-TAP 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 118.8 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 119.55 | 762461 G18-015-XFM1 34.5 762460 GEN-2018-015 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 119.55 | 762464 G18-015-XFM2 34.5 762460 GEN-2018-015 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21061 | 120.87 | 762467 G18-015-TAP 345 763215 G18-092-TAP 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 118.04 | 763087 GEN-2018-073 345 763088 G18-073-XFM1 34.5 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 119.21 | 763087 GEN-2018-073 345 763091 G18-073-XFM2 34.5 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 114.92 | 763120 GEN-2018-081 230 763121 G18-081-XFM1 34.5 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 117.23 | 763120 GEN-2018-081 230 764011 G19-074-XFM1 34.5 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 117.2 | 763186 GEN-2018-089 230 763187 G18-089-XFM1 34.5 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 118.06 | 763208 GEN-2018-092 345 763215 G18-092-TAP 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 119.2 | 763208 GEN-2018-092 345 763220 G18-092-XFM1 34.5 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 119.2 | 763208 GEN-2018-092 345 763223 G18-092-XFM2 34.5 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 116.67 | 763241 GEN-2018-097 230 763242 G18-097-XFM1 34.5 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 117.6 | 763241 GEN-2018-097 230 763296 G18-111-XFM1 34.5 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 116.95 | 763241 GEN-2018-097 230 763307 G18-112-XFM1 34.5 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 116.95 | 763241 GEN-2018-097 230 763310 G18-112-XFM2 34.5 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 116.67 | 763241 GEN-2018-097 230 763395 G18-124-XFM1 34.5 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 116.67 | 763241 GEN-2018-097 230 763398 G18-124-XFM2 34.5 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 116.31 | 763483 GEN-2019-003 230 763484 G19-003-XFM1 34.5 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 119.03 | 763483 GEN-2019-003 230 763605 G19-021-XFM1 34.5 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 119.65 | 763516 GEN-2019-011 345 763517 G19-011-XFM1 34.5 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.06 | 763879 GEN-2019-056 115 763880 G19-056XFM1 34.5 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.49 | P13:345,230:CLEC::DOLHILL::1
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.29 | P13:345,24:CLEC::G1DOLHILL::1
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20892 | 120.51 | P42:345:OKGE:SB_BVTY7305
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.2091 | 120.23 | P23:345:WERE:BUFF_345-534::
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.2091 | 120.23 | P23:345:WERE:BUFF_345-543::
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20922 | 120.66 | P23:345:WERE:JEC_345-15::
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.2092 | 120.62 | P23:345:WERE:JEC_345-16::
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20922 | 120.66 | P23:345:WERE:JEC_345-19::
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20922 | 120.66 | P23:345:WERE:JEC_345-20::
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.2092 | 120.29 | P23:345:WERE:WICH_345-50::
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20925 | 120.87 | P23:345:WERE:WOLF_345-50::
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.87 | P23:345:WERE:WOLF_345-60::
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20927 | 120.28 | P42:345:AEPW:WELSH CB 10620 NBTB+FAULT
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.27 | P41:345:AEPW:WELSH CB 10630 NBTB+FAULT
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.26 | P41:345:AEPW:WELSH CB 11670 NBTB+FAULT
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20929 | 120.53 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.26 | P41:345:AEPW:WELSH CB 12540 NBTB+FAULT
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20928 | 120.49 | P43:345:AEPW:CHAMBERS SPRING CB 12720 NBTB+FAULT
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20928 | 120.49 | P42:345:AEPW:CHAMBERS SPRING CB 13720 NBTB+FAULT
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20928 | 120.49 | P42:345:AEPW:CHAMBERS SPRING CB 13850 NBTB+FAULT
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21233 | 121.76 | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.2128 | 122.49 | P42:345:AEPW:LAWTON EASTSIDE CB 3413A NBTB+FAULT
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21314 | 122.73 | P42:345:AEPW:LAWTON EASTSIDE CB 3425A NBTB+FAULT
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21246 | 123.34 | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.2096 | 120.48 | P42:345:AEPW:PITTSBURG CB 3433A NBTB+FAULT
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20936 | 120.18 | P42:345:AEPW:PITTSBURG CB 3441A NBTB+FAULT
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.2092 | 120.25 | P42:345:AEPW:PITTSBURG CB 3445A NBTB+FAULT
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21173 | 122.67 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21173 | 122.67 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21173 | 122.65 | P42:345:AEPW:TERRYRD_CB_3421A_NBTB
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20924 | 120.65 | P23:345:KCPL:LACYGNE_R2-5::LACYGU2-LACYGNE-STILWELL
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20924 | 120.28 | P45:345:UMZW:# 1328 #: GI IN NE.
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20927 | 120.28 | P23:345:AEPW:WELSH CB 10620 NBTB
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.27 | P23:345:AEPW:WELSH CB 10630 NBTB
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.26 | P23:345:AEPW:WELSH CB 11670 NBTB
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20929 | 120.53 | P23:345:AEPW:WELSH CB 11990 NBTB
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.26 | P23:345:AEPW:WELSH CB 12540 NBTB
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20928 | 120.49 | P23:345:AEPW:CHAMBERS SPRING CB 12720 NBTB
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20928 | 120.49 | P23:345:AEPW:CHAMBERS SPRING CB 13720 NBTB
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20928 | 120.49 | P23:345:AEPW:CHAMBERS SPRING CB 13850 NBTB
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21233 | 122.19 | P23:345:AEPW:OKLAUNION CB 3401A NBTB
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.2128 | 122.49 | P23:345:AEPW:LAWTON EASTSIDE CB 3413A NBTB
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21314 | 122.73 | P23:345:AEPW:LAWTON EASTSIDE CB 3425A NBTB
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21246 | 123.34 | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.2096 | 120.48 | P23:345:AEPW:PITTSBURG CB 3433A NBTB
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20936 | 120.18 | P23:345:AEPW:PITTSBURG CB 3441A NBTB
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.2092 | 120.25 | P23:345:AEPW:PITTSBURG CB 3445A NBTB
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21173 | 122.67 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21173 | 122.67 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21173 | 122.65 | P23:345:AEPW:TERRYRD_CB_3421A_NBTB
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20956 | 120.48 | P12:138:AEPW:S.W.S.-4:L.E.S.-4
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20925 | 120.54 | P11:161:GMO:DOGWOOD_COMBINED_CYCLE_UNIT_OUTAGE
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.54 | P11:115:SUNC:GARDENCITY_S2:97:531459(2)
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20912 | 120.25 | P12:345:PWT:BUFF-THIS_345_1::
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20912 | 120.25 | P12:345:PWT:BUFF-THIS_345_2::
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20935 | 120.52 | P12:069:WFEC:ANADRKO_WATONGA
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20944 | 120.54 | P23:345:AEPW:VALLIANT CB 3413A NBTB
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.2095 | 120.56 | P23:345:AEPW:VALLIANT CB 3417A NBTB
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.2119 | 122.82 | P23:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21446 | 125.21 | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20944 | 120.54 | P42:345:AEPW:VALLIANT CB 3413A NBTB+FAULT
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.2095 | 120.56 | P42:345:AEPW:VALLIANT CB 3417A NBTB+FAULT
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.2119 | 122.82 | P42:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB+FAULT
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21446 | 125.21 | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20466 | 117.77 | P42:345:OKGE:SB_BVTY7315_PRE19S
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20888 | 120.52 | P23:345:SUNC:MO_BRK188
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21045 | 120.68 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20927 | 120.23 | P12:138-13.8:AEPW:COMANC-4_#1
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20867 | 119.93 | P12:230:AEPW:ELKCITY6:CHISHOLM6
Thermal | 05ALL | 1 | 26WP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21036 | 121.03 | P12:230:AEPW:SWEETWT6:CHISHOLM6
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997711 ABBXNL844501 230 1 |  | 552.5 | 0.3412 | 164.23 | 525531 TOLK 6 230 3WXFMR TOLK 6 2
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20928 | 120.49 | P12:345:AEPW-AEPW:CHAMPSP-CLARKSV
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20927 | 120.61 | P23:345:KCPL-WERE:237LACYGNE_R1-6::LACYGU1-LACYGNE-NEOSHO
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20925 | 120.5 | P11:161:GMO:DOGWOOD_COMBINED_CYCLE_UNIT_OUTAGE_1_1
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20933 | 118.96 | P11:115:SPS:MUSTANG1&3:153MW::::
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21179 | 122.27 | P12:230:SPS:K37::1_TOLK_LAMB:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20946 | 120.48 | P12:230:SPS:K43::1_PRNGLE_HARR_E:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20929 | 120.26 | P12:230:SPS:K44::1_EPLNT_HARRW:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.2094 | 120.61 | P12:115:SPS:T04::1_TRBLNC_CASTRO:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20925 | 120.48 | P12:115:SPS:T13::1_TAYLOR_WHOBBS:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20925 | 120.26 | P12:115:SPS:T14::1_MADDOX_TAYLOR:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.73 | P12:115:SPS:T21::1_GRSSLND_GRAHAM:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20925 | 120.29 | P12:115:SPS:T23::1_PCA_POTJCT:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20927 | 120.52 | P12:115:SPS:T26::1_CHAVES_RSWLCTY:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21046 | 120.8 | P12:115:SPS:T28A::1_LAMTON_PLANTX:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.2097 | 120.54 | P12:115:SPS:T29::1_LAMTON_HALECTR:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21093 | 121.92 | P12:115:SPS:T30::1_LAMB_HOCKLY:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21093 | 121.43 | P12:115:SPS:T31::1_HOCKLY_SUNDWN:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20921 | 120.59 | P12:115:SPS:T35::1_TERRY_YOAKUM:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 121.24 | P12:115:SPS:T45::1_NORRIS_OASIS:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21052 | 120.73 | P12:115:SPS:T59::1_CARGIL_CURRY:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21023 | 120.66 | P12:115:SPS:T67::1_HAPPY_KRESS:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20921 | 120.96 | P12:115:SPS:T71::1_CRLSLE_YUMA:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20934 | 120.57 | P12:115:SPS:T81::1_COX_FLOYD:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20925 | 120.57 | P12:115:SPS:T83::1_SP-FKFD_ALLEN:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20921 | 120.91 | P12:115:SPS:T89::1_DC_N_HIGG:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.54 | P12:115:SPS:T91::1_HIGG_RUSSELL:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20948 | 120.51 | P12:115:SPS:V04::1_EPLANT_RNDALL:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20939 | 120.5 | P12:115:SPS:V07::1_COX_HALECTR:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21038 | 120.71 | P12:115:SPS:V09::1_HALECTR_PLANTX:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20925 | 120.56 | P12:115:SPS:V12::1_PLANTX_BAILEY:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.5 | P12:115:SPS:V15::1_TUCO_INDANA:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20917 | 120.51 | P12:115:SPS:V16::1_TERRY_DC_N:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.2089 | 120.62 | P12:115:SPS:V24::1_WOLFTH_TERRY:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20943 | 120.6 | P12:115:SPS:V26::1_RSWLL_EDDY_N:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.58 | P12:115:SPS:V33::1_LUBBS_LYNN:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.2103 | 121.13 | P12:115:SPS:V37::1_CASTRO_PLANTX:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.63 | P12:115:SPS:V46::1_ALLEN_WHEELCK:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20927 | 120.95 | P12:115:SPS:V49::1_YOAKUM_SHLCO2:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20968 | 121.15 | P12:115:SPS:V55::1_SUNDWN_TERRY:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20936 | 120.98 | P12:115:SPS:V56::1_COCHRAN_SUNDWN:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20939 | 120.5 | P12:115:SPS:V78::2_CURRY_RSVLT:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20924 | 120.67 | P12:115:SPS:V81::1_LE-WAIT_LE-LVN:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.54 | P12:115:SPS:V95::1_DC_N_SHLCO2:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.5 | P12:115:SPS:W11::1_DC_S_SMINLE:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20925 | 120.54 | P12:115:SPS:W14::1_SMINLE_GAINES:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20925 | 120.5 | P12:115:SPS:W26::1_CUNGHM_OILCNTR:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 121.13 | P12:115:SPS:W32::1_PRMTR_FE-CLSIN:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.5 | P12:115:SPS:W34::1_JNSDRW_MAPCO:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20923 | 120.73 | P12:115:SPS:W35::1_GAINES_JNSDRW:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.2092 | 120.52 | P12:115:SPS:W36::1_TAYLOR_JNSDRW:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21116 | 120.93 | P12:115:SPS:W40::1_WCANYON_TRBLNC:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20936 | 120.29 | P12:115:SPS:W46::1_RHILLS_NWEST:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20953 | 120.55 | P12:115:SPS:W52::1_NEWHART_KRESS:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 121.01 | P12:115:SPS:W58::1_NORTON_LOPEZ:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.69 | P12:115:SPS:W59::1_LOPEZ_CMPBLL:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20927 | 120.96 | P12:115:SPS:W62::1_PLSTHL_CURRY:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.84 | P12:115:SPS:W64::1_PLSTHL_FE-CLV:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20927 | 120.81 | P12:115:SPS:W65::1_PLSTHL_CURRY:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.68 | P12:115:SPS:W66::1_PORTA_GREYHUND:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21116 | 120.53 | P12:115:SPS:W77::1_RNDAL_WCANYON:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.51 | P12:115:SPS:W99::1_CAPITAN_CHAVES:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20925 | 120.51 | P12:115:SPS:U03::1_CARDNL_NEF:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20922 | 121.04 | P12:115:SPS:U14::1_DC_STH_INKBSN:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20924 | 120.92 | P12:115:SPS:V15::1_INKBSN_LE-WAT:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20948 | 120.55 | P12:115:SPS:U16::1_BSHLND_OUTPST:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20948 | 120.54 | P12:115:SPS:U17::1_COLTR_OUTPST:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20933 | 120.76 | P12:115:SPS:U19::1_DEAN_PLAINS:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20948 | 120.49 | P12:115:SPS:U23::1_COLTR_HILSDE:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.201 | 127.42 | P42:345:SPS:YOAKUM:J18####:SLG1:EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.201 | 127.42 | P43:345:SPS:YOAKUM:TF#####:SLG:EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.201 | 127.42 | P42:345:SPS:YOAKUM:J17####:SLG:EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20181 | 122.69 | P43:345:SPS:TUCO:SLG::EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.201 | 127.42 | P42:345:SPS:YOAKUM:J18####:SLG2:EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20928 | 120.49 | P12:345:AEPW-AEPW:CHAMPSP-CLARKSV:::EHV::
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20925 | 120.52 | P11:18:HAST:::EGYCTR2G WEC2_LOSS OF WEC 2 GEN_:HV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20925 | 120.52 | P13:18-115:HAST:::EGYCNTR7 XFMR G2WEC 2 GSU_:HV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20925 | 120.5 | P11:161:GMO:DOGWOOD-COMBINED-CYCLE-UNIT-OUTA:::HV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20927 | 120.61 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20924 | 120.65 | P23:345:KCPL:LACYGNE-R2-5:::EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20922 | 120.66 | P11:230:WERE:JECU1-GEN:::HV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20922 | 120.66 | P11:345:WERE:JECU2-GEN:::EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20922 | 120.66 | P11:345:WERE:JECU3-GEN:::EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.88 | P11:345:WERE:WOLFU1-GEN:::EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20912 | 120.25 | P12:345:PWT:BUFF-THIS-345-1:::EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20912 | 120.25 | P12:345:PWT:BUFF-THIS-345-2:::EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.2091 | 120.23 | P23:345:WERE:BUFF-345-534:::EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.2091 | 120.23 | P23:345:WERE:BUFF-345-543:::EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20922 | 120.66 | P23:345:WERE:JEC-345-15:::EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.2092 | 120.62 | P23:345:WERE:JEC-345-16:::EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20922 | 120.66 | P23:345:WERE:JEC-345-19:::EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20922 | 120.66 | P23:345:WERE:JEC-345-20:::EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.2092 | 120.29 | P23:345:WERE:WICH-345-50:::EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20925 | 120.87 | P23:345:WERE:WOLF-345-50:::EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.87 | P23:345:WERE:WOLF-345-60:::EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.81 | P11:022:NPPD:COOPER1G:1:983:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.2092 | 120.83 | P11:023:NPPD:GENTLM1G:1:757:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20924 | 120.68 | P11:024:NPPD:GENTLM2G:2:757:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20921 | 120.68 | P13:345:OPPD:NEBCTY1G:::EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.2092 | 120.69 | P13:345:OPPD:NEBCTY2G:::EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.69 | P22:345:OPPD:S3458 NEBCTY1G:LT::EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20921 | 120.68 | P22:345:OPPD:S3458 NEBCTY1G:::EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.72 | P22:345:OPPD:S3458 NEBCTY2G:LT::EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.2092 | 120.69 | P22:345:OPPD:S3458 NEBCTY2G:::EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.69 | P23:345:OPPD:S3458 NEBCTY1G:LT::EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20921 | 120.68 | P23:345:OPPD:S3458 NEBCTY1G:::EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.72 | P23:345:OPPD:S3458 NEBCTY2G:LT::EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.2092 | 120.69 | P23:345:OPPD:S3458 NEBCTY2G:::EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.29 | P12:115:SUNC:PLYMELL-PIERCEVILLE:::HV::
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20923 | 120.53 | P11:018:UMZB:# 5 #:: DCS IN SD. DEERCREEK_MV::
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20924 | 120.5 | P11:022:UMZB:# 15 #:: LO IN ND. LELAND OLDS 1_MV::
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20925 | 120.5 | P11:020:UMZB:# 16 #:: LO IN ND. LELAND OLDS 2_MV::
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20923 | 120.61 | P11:023:UMZB:# 31 #:: AVS IN ND. ANTELOPE VALLEY 1_MV::
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20923 | 120.61 | P11:023:UMZB:# 32 #:: AVS IN ND. ANTELOPE VALLEY 2_MV::
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20919 | 120.82 | P11:024:UMZB:# 33 #:: LRS IN WY. LARAMIE RIVER STATION 1_MV::
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.49 | P13:230:UMZW:# 5135 #:: OA IN SD. FAULT ON TRANSFORMER (2).:HV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.49 | P13:230:UMZW:# 5136 #:: OA IN SD. FAULT ON TRANSFORMER (3).:HV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.5 | P13:230:UMZW:# 5137 #:: OA IN SD. FAULT ON TRANSFORMER (4).:HV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20924 | 120.28 | P23:345:UMZW:# 2423 #:: GI IN NE. GI 1596 BKR FAULT:EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20924 | 120.28 | P23:345:UMZW:# 2426 #:: GI IN NE. GI 1592 BKR FAULT:EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20924 | 120.28 | P23:345:UMZW:# 2432 #:: GI IN NE. GI 1092 BKR FAULT:EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20924 | 120.28 | P23:345:UMZW:# 2440 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1092 STUCK BKR:EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20924 | 120.28 | P23:345:UMZW:# 2444 #:: GI IN NE. GI-SWEET BRANCH FAULT & GI 1596 STUCK BKR:EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20924 | 120.28 | P23:345:UMZW:# 2446 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1196 STUCK BKR:EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20924 | 120.28 | P42:345:UMZW:# 2413 #:: FT2 IN SD. FT2-LO2 BRANCH FAULT & FT2 2992 STUCK BKR:EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20924 | 120.28 | P42:345:UMZW:# 2415 #:: FT2 IN SD. FT2-GI BRANCH FAULT & FT2 3392 STUCK BKR:EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.2093 | 120.2 | P11:138:WFEC:HUGO1:465MW :::
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20924 | 120.49 | P11:138:WFEC:MORLND2:132MW:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20924 | 120.5 | P11:138:WFEC:MORLND3:149MW :::
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20934 | 120.52 | P12:138:WFEC:ANADRKO_CLVLND::::
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.2092 | 120.25 | P12:345:OKGE-AEPW:BKRBKR20::::
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20961 | 120.7 | P12:345:OKGE:BKRBKR21::::
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20981 | 120.7 | P12:345:OKGE:BKRBKR24::::
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21172 | 122.65 | P12:345:OKGE-AEPW:BKRBKR25::::
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20895 | 120.12 | P12:345:OKGE:BKRBKR336::::
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20894 | 120.11 | P12:345:OKGE:BKRBKR336_2::::
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.2096 | 120.48 | P12:345:OKGE-AEPW:BKRBKR343::::
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21247 | 122.27 | P12:345:OKGE-AEPW:BKRBKR366::::
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21247 | 122.24 | P12:345:OKGE-AEPW:BKRBKR366::::
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21132 | 121.66 | P12:345:OKGE:BKRBKR367::::
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20962 | 120.59 | P12:345:OKGE-WFEC:BKRBKR374::::
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20962 | 120.56 | P12:345:OKGE-WFEC:BKRBKR374::::
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20899 | 120.16 | P12:345:OKGE:BKRBKR4193::::
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20899 | 120.16 | P12:345:OKGE:BKRBKR4194::::
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20889 | 120.16 | P12:345:OKGE-SPS:BKRBKR4201::::
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20889 | 120.16 | P12:345:OKGE-SPS:BKRBKR4202::::
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20893 | 119.95 | P12:345:OKGE:BKRBKR443NEW::::
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20893 | 119.95 | P12:345:OKGE:BKRBKR443NEW2::::
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20909 | 120.27 | P12:345:OKGE-ITC:BKRBKR502::::
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20909 | 120.27 | P12:345:OKGE-ITC:BKRBKR503::::
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20921 | 120.61 | P12:345:OKGE:BKRBKR604::::
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20919 | 120.72 | P12:345:OKGE:BKRBKR604_2::::
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21627 | 123.72 | P42:345:OKGE:SB_BVTY7387::::
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20966 | 120.63 | P42:345:OKGE:SB_SPCK7383::::
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20923 | 120.53 | P11:115:SUNC:GARDENCITY_S2:103:531459(2):HV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20923 | 120.54 | P11:115:SUNC:FORTDDODGE_4:157:539670(4):HV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20888 | 120.5 | P12:345:SUNC-NPPD:MINGO-REDWILLOW::531451-640325(1):EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.61 | P13:115:SUNC:HOLCOMB_GSU:::HV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20923 | 120.53 | P13:115:SUNC:S2_GSU:::HV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20923 | 120.54 | P13:115:SUNC:FORTDODGE_GSU:::HV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.48 | 300002 1THLG2 22.0 301505 5THOMHLGSU2 161 2
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.62 | 300003 1THLG3 24.0 301503 7THOMHLGSU3 345 3
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.48 | 300006 1NM G1 22.0 301536 5NEWMADGSU1 161 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.48 | 300007 1NM G2 22.0 301537 7NEWMADGSU2 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.48 | 300046 7NEWMAD 345 301537 7NEWMADGSU2 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.62 | 300049 7THOMHL 345 301503 7THOMHLGSU3 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.48 | 300103 5NEWMAD 161 301536 5NEWMADGSU1 161 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.48 | 300132 5THMHLB2 161 301505 5THOMHLGSU2 161 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20925 | 120.29 | 300739 7BLACKBERRY 345 532797 WOLFCRK7 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.56 | P11:20:AMMO:1LAB�� G1:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.54 | P11:20:AMMO:1LAB�� G2:2
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.75 | P11:345:AMMO::CALLAWAY:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.56 | P11:345:AMMO::LABADIE:3
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.56 | P11:345:AMMO::LABADIE:4
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.55 | P11:345:AMMO::RUSHISLAND:U1
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.54 | P11:345:AMMO::RUSHISLAND:U2
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.53 | P11:138:AMMO::SIOUX:2
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.49 | P13:345-230:CLEC::DOLHILL7:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.29 | P11:345-24:CLEC::DOLHILL7:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.29 | P11:24:CLEC::G1DOLHIL:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.53 | P12:765:AEP:AEP ROCKP-AEP JEFF 765
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.48 | P11:HV:EES::1ISES U1:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.25 | P11:HV:EES::PIRKEY 1:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.26 | P11:EHV:EES::WELSH3-1:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.2 | P11:HV:EES::TURKCOAL:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.48 | P12:HV:EES::5ISES%:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.74 | P12:EHV:EES::7CALAWY 1:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20928 | 120.49 | P12:EHV:EES::CHAMSPR7!:CLARKSV7!:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20927 | 120.21 | P12:HV:EES::TURK 4%:1(1)
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20928 | 120.26 | P12:EHV:EES::WELSH 7:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20928 | 120.26 | P12:EHV:EES::WELSH 7:1(1)
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20927 | 120.26 | P12:HV:EES::PIRKEY 4:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.53 | 344011 7HUGHES 345 344012 7HPW-N 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.55 | 344884 7LABADIE1 345 344894 1LAB G1 20.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.53 | 344885 7LABADIE2 345 344895 1LAB G2 20.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.55 | 344886 7LABADIE3 345 344896 1LAB G3 20.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.55 | 344887 7LABADIE4 345 344897 1LAB G4 20.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.54 | 345667 7RUSH 1 345 345670 1RUSH G1 18.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.53 | 345668 7RUSH 2 345 345671 1RUSH G2 18.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.52 | 345755 4SIOUX 1 138 345756 1SIOUX 1 18.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.52 | 345764 4SIOUX 2 138 345765 1SIOUX 2 18.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.6 | P12:345:MDU::CENTER:COYOTE:1::::
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.6 | P13:345:MDU:COYOTE GSU LOSS:COYOTE::1::::
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.82 | P11:345:MEC-NPPD:COOPER 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.72 | P11:24:XEL:AUTO-SINGLE:SHERC31G:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.72 | P11:24:XEL:AUTO-SINGLE:SHERC32G:2
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.81 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.64 | P11:20:XEL:AUTO-SINGLE:PRIS31G:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.63 | P11:20:XEL:AUTO-SINGLE:PRIS32G:2
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.68 | P11:22:XEL:AUTO-SINGLE:MNTCE31G:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.64 | P11:20:XEL:AUTO-SINGLE:KING31G:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.48 | P11:18:XEL:AUTO-SINGLE:BLKD76G:6
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.69 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.69 | P11:22:GRE:AUTO-SINGLE:GRE-COAL42G:2
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.61 | P11:24:OTP:AUTO-SINGLE:BIGSTN1G:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.63 | P11:20:OTP:AUTO-SINGLE:CENTER2G:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.52 | P11:22:OTP:AUTO-SINGLE:CENTER1G:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.61 | P11:24:OTP:AUTO-SINGLE:COYOTE1G:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.51 | P11:24:DPC:AUTO-SINGLE:GENOA53G:3
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.5 | P12:115:XEL:AUTO-SINGLE:CHEMOLT7:LSPOWER7:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.49 | P12:115:XEL:AUTO-SINGLE:FARIBALTP7:FARIBALTGEN:Z
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.61 | P12:230:OTP:AUTO-SINGLE:SQBUTTE4:YNG24:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.69 | P13:24-345:XEL:AUTO-SINGLE:SHERC31G:SHERCO3:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.69 | P13:24-345:XEL:AUTO-SINGLE:SHERC32G:SHERCO3:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.78 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.64 | P13:20-345:XEL:AUTO-SINGLE:PRIS31G:PRISLD3:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.64 | P13:20-345:XEL:AUTO-SINGLE:PRIS32G:PRISLD3:2
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.68 | P13:22-345:XEL:AUTO-SINGLE:MNTCE31G:MNTCELO3:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.62 | P13:20-345:XEL:AUTO-SINGLE:KING31G:ASKING3:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.48 | P13:18-115:XEL:AUTO-SINGLE:BLKD76G:BLKDG27:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.67 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL41G:GRE-COALCR4:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.67 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL42G:GRE-COALCR4:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.6 | P13:230-24:OTP:AUTO-SINGLE:BIGSTON4:BIGSTN1G:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.61 | P13:20-230:OTP:AUTO-SINGLE:CENTER2G:YNG24:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.51 | P13:22-230:OTP:AUTO-SINGLE:CENTER1G:CENTER4:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.6 | P13:24-345:OTP:AUTO-SINGLE:COYOTE1G:COYOTE3:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.5 | P13:24-161:DPC:AUTO-SINGLE:GENOA53G:GENOA5:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.55 | P13:24-161:DPC:AUTO-SINGLE:JPM:ALMA5:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.6 | P11:115:XEL:RIV COMBINE CYCLE
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.51 | P12:115:XEL:BDS #2 5
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.49 | P11:115:XEL:HBR #6 7 8
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.63 | P23:345:XEL:8H14 PRI
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.64 | P23:345:XEL:8H17 PRI AS
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.78 | P23:345:XEL:8N28 SHC
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.7 | P23:345:XEL:8N22 SHC
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.69 | P23:345:XEL:8N17 SHC
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.68 | P23:345:XEL:8N8 MNN
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.63 | P23:345:XEL:8P1 KING
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.63 | P23:345:XEL:8P2 KING
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.5 | P11:22:ALTW:AUTO-SINGLE:LANS54G:4
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.64 | P11:22:ALTW:AUTO-SINGLE:ARNOLD1G:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.67 | P11:24:ALTW:AUTO-SINGLE:OTTUMW1G:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.49 | P13:22-161:ALTW:AUTO-SINGLE:LANS54G:LANSINGL15:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.63 | P13:22-161:ALTW:AUTO-SINGLE:ARNOLD1G:ARNOLD5:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.66 | P13:24-161:ALTW:AUTO-SINGLE:OTTUMW1G:OTTUMWA5:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.74 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.8 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.65 | P11:22:MEC:AUTO-SINGLE:NEAL3G:3
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.73 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.66 | P11:24:MEC:AUTO-SINGLE:LOUIS31G:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.72 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.76 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.64 | P13:345-22:MEC:AUTO-SINGLE:RAUN3:NEAL3G:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.71 | P13:345-24:MEC:AUTO-SINGLE:RAUN3:NEAL4G:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.64 | P13:345-24:MEC:AUTO-SINGLE:LOUISA3:LOUIS31G:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20922 | 120.66 | P11:230:WERE:JECU1_GEN::
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20922 | 120.66 | P11:345:WERE:JECU2_GEN::
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20922 | 120.66 | P11:345:WERE:JECU3_GEN::
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.88 | P11:345:WERE:WOLFU1_GEN::
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20933 | 120.48 | 511453 DUNCAN-4 138 511552 DUNCHERTP4 138 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20933 | 120.48 | 511455 D.E.S.-4 138 511552 DUNCHERTP4 138 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.48 | 511456 O.K.U.-7 345 511565 OKLAUN HVDC7 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 119.42 | 511456 O.K.U.-7 345 588760 GEN-2017-033 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21233 | 122.19 | 511456 O.K.U.-7 345 763215 G18-092-TAP 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21246 | 122.76 | 511468 L.E.S.-7 345 762467 G18-015-TAP 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21143 | 122.19 | 511468 L.E.S.-7 345 763215 G18-092-TAP 345 2
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20938 | 120.56 | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21045 | 120.68 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20262 | 117.21 | 511553 CHISHOLM7 345 523961 POTTER_CO 7 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20262 | 117.21 | 511553 CHISHOLM7 345 523961 POTTER_CO 7 345 2
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20633 | 119.86 | 511553 CHISHOLM7 345 755000 WWDBORDT 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20924 | 120.5 | 511557 CHISHOLM6 230 3WXFMR CHISHOLM6 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20939 | 120.51 | 514801 MINCO 7 345 555234 NSUB345 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20852 | 120.15 | 515375 WWRDEHV7 345 755000 WWDBORDT 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21627 | 123.76 | 515458 BORDER 7 345 560022 CRAWFISH_DR 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21627 | 123.7 | 515458 BORDER 7 345 755000 WWDBORDT 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20924 | 120.51 | 515618 BALKOW 7 345 3WXFMR BALKOW 7 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20924 | 120.5 | 515618 BALKOW 7 345 3WXFMR BALKOW 7 1_Dup1
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20919 | 120.73 | 515634 PALDR1W7 345 3WXFMR PALO2 _1 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.63 | 515677 BADGER 7 345 563170 G15082_1 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.49 | 522800 MU-TULIA 3 115 525179 TULIA_TP 3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.63 | 522892 MU-BROWNFLD2 69.0 526761 BROWNFLD_TP2 69.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20923 | 120.52 | 523093 HITCHLAND 3 115 523174 GOODWELLWND3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21053 | 120.53 | 523095 HITCHLAND 6 230 523309 MOORE_CNTY 6 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.88 | 523097 HITCHLAND 7 345 523112 NOVUS1 7 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.93 | 523097 HITCHLAND 7 345 523215 FREWHELCOL17 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20717 | 119.43 | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.99 | 523097 HITCHLAND 7 345 560252 G10-14 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.5 | 523099 TC-DRYTRLS 3 115 588480 A16-010_SUB 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.74 | 523112 NOVUS1 7 345 3WXFMR NOVUS XF2 2
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.52 | 523112 NOVUS1 7 345 3WXFMR XIANA2011198 _1 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20923 | 120.5 | 523118 BUFF_DUNES 7 345 523853 FINNEY 7 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.51 | 523120 COLE 3 115 588860 GEN-2017-047 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20935 | 120.48 | 523221 XIT_INTG 6 230 3WXFMR SIEM_T126401 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20946 | 120.48 | 523267 PRINGLE 6 230 3WXFMR ENRCO13617-1 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20946 | 120.48 | 523267 PRINGLE 6 230 523979 HARRNG_EST 6 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20988 | 120.61 | 523309 MOORE_CNTY 6 230 523323 MCDWL_CREEK6 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.2096 | 120.53 | 523323 MCDWL_CREEK6 230 523959 POTTER_CO 6 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20896 | 120.85 | 523959 POTTER_CO 6 230 523979 HARRNG_EST 6 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21737 | 121.98 | 523959 POTTER_CO 6 230 524267 BUSHLAND 6 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.2171 | 122.4 | 523959 POTTER_CO 6 230 525461 NEWHART 6 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21287 | 129.34 | 523961 POTTER_CO 7 345 3WXFMR WAUK 90343-A 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20912 | 120.79 | 523961 POTTER_CO 7 345 524296 SPNSPUR_WND7 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20928 | 120.27 | 523977 HARRNG_WST 6 230 523971 HARRNGTON1 1 24.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20905 | 120.79 | 523977 HARRNG_WST 6 230 524010 ROLLHILLS 6 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20925 | 120.22 | 523978 HARRNG_MID 6 230 523979 HARRNG_EST 6 230 @1
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20925 | 120.29 | 524010 ROLLHILLS 6 230 3WXFMR WAUK WT01104 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20948 | 120.55 | 524267 BUSHLAND 6 230 3WXFMR WH 7001795 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.22387 | 122.23 | 524267 BUSHLAND 6 230 524623 DEAFSMITH 6 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20912 | 120.89 | 524296 SPNSPUR_WND7 345 524299 SPNSPUR_COL7 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20912 | 120.89 | 524299 SPNSPUR_COL7 345 3WXFMR SPNSPUR_COL7 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21317 | 120.9 | 524415 AMA_SOUTH 6 230 525213 SWISHER 6 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 121.01 | 524502 NORTON 3 115 524509 FE-TUCMCARI3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21116 | 120.82 | 524575 DS-#25+ 3 115 524597 PANDAHFD 3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21116 | 120.9 | 524575 DS-#25+ 3 115 524630 TIERABLANCA3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.5 | 524604 HEREFRD_SB 2 69.0 524608 HERFRD_STH 2 69.0 *1
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.22236 | 125.98 | 524623 DEAFSMITH 6 230 760498 G17-146-TAP 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.78 | 524721 DS-#15&#19+2 69.0 524745 CASTRO_CNTY2 69.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.84 | 524764 NORRIS_TP 3 115 524801 NORRIS 3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20932 | 120.49 | 524770 PLSNT_HILL 6 230 3WXFMR EFAE1100068A 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.84 | 524776 N_CLOVIS_TP3 115 524777 N_CLOVIS 3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.78 | 524790 CANNON_TP 3 115 524794 CANNONAFB 3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21343 | 127.03 | 524875 OASIS 6 230 524885 SN_JUAN_TAP6 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20999 | 121.66 | 524875 OASIS 6 230 524909 ROOSEVELT 6 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21325 | 127.79 | 524885 SN_JUAN_TAP6 230 527483 CHAVES_CNTY6 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20942 | 120.65 | 524909 ROOSEVELT 6 230 3WXFMR ABB LMM60042 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21617 | 125.82 | 524909 ROOSEVELT 6 230 525531 TOLK 6 230 2
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 121.25 | 524923 PORTALES 2 69.0 524929 RO-PORT_MTR2 69.0 @1
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.88 | 524923 PORTALES 2 69.0 524941 PORTALES#1 2 69.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.84 | 525023 BC-BAIL_MTR2 69.0 525027 BAILEYCO 2 69.0 @1
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.2103 | 120.8 | 525056 BC-EARTH 3 115 525480 PLANT_X 3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.57 | 525192 KRESS_INT 3 115 3WXFMR ENRCO 136155 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20937 | 120.29 | 525213 SWISHER 6 230 3WXFMR SIEM_T127101 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21223 | 121.59 | 525213 SWISHER 6 230 525461 NEWHART 6 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.54 | 525272 KISER 3 115 3WXFMR VON 13819/1 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.81 | 525326 COX 3 115 3WXFMR ELCO 13474-3 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.81 | 525414 LAMTON 3 115 3WXFMR ASEA MLL9204 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.22535 | 123.54 | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21198 | 122.16 | 525481 PLANT_X 6 230 3WXFMR WH ALM20171 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21856 | 127.05 | 525481 PLANT_X 6 230 526435 SUNDOWN 6 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.22236 | 124.03 | 525481 PLANT_X 6 230 760498 G17-146-TAP 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21271 | 120.86 | 525481 PLANT_X 6 230 762174 G17-218TAP 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21313 | 120.92 | 525481 PLANT_X 6 230 762174 G17-218TAP 230 2
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.22055 | 128.41 | 525531 TOLK 6 230 525586 NEEDMORE 6 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21179 | 122.27 | 525531 TOLK 6 230 525637 LAMB_CNTY 6 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.23816 | 127.4 | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21436 | 121.08 | 525531 TOLK 6 230 762174 G17-218TAP 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21471 | 121.13 | 525531 TOLK 6 230 762174 G17-218TAP 230 2
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.3412 | 162.04 | 525549 TOLK 7 345 3WXFMR ABBXNL844501 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.22055 | 128.41 | 525586 NEEDMORE 6 230 526935 YOAKUM 6 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21179 | 122.27 | 525637 LAMB_CNTY 6 230 3WXFMR WH ALM20172 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.54 | 525828 TUCO_INT 3 115 3WXFMR DS F78800913 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21357 | 120.96 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21476 | 121.11 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _9 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20181 | 122.69 | 525832 TUCO_INT 7 345 526936 YOAKUM_345 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21093 | 121.33 | 526020 HOCKLEY 3 115 526036 LC-OPDYKE 3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21093 | 121.18 | 526036 LC-OPDYKE 3 115 526434 SUNDOWN 3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.57 | 526160 CARLISLE 3 115 3WXFMR WH RLP38371 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.79 | 526162 LP-DOUD_TP 3 115 526176 LP-DOUD 3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.82 | 526268 LUBBCK_STH 3 115 3WXFMR NA 70454A 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20936 | 120.81 | 526361 COCHRAN 3 115 526424 PACIFIC 3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20936 | 120.9 | 526424 PACIFIC 3 115 526434 SUNDOWN 3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20968 | 120.94 | 526434 SUNDOWN 3 115 526445 AMOCO_TP 3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20921 | 120.51 | 526435 SUNDOWN 6 230 3WXFMR UPDATE LATER _12 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20944 | 124.22 | 526435 SUNDOWN 6 230 526460 AMOCO_SS 6 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20968 | 120.8 | 526445 AMOCO_TP 3 115 526484 LG-LEVELAND3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20944 | 121.88 | 526460 AMOCO_SS 6 230 526935 YOAKUM 6 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20968 | 120.79 | 526484 LG-LEVELAND3 115 526491 LG-CLAUENE 3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20923 | 120.51 | 526525 WOLFFORTH 6 230 3WXFMR UPDATE LATER _13 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20916 | 122.38 | 526935 YOAKUM 6 230 527028 INK_BASIN 6 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20181 | 129.67 | 526936 YOAKUM_345 345 527896 HOBBS_INT 7 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20905 | 121.79 | 527028 INK_BASIN 6 230 527894 HOBBS_INT 6 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20921 | 120.9 | 527130 DENVER_N 3 115 527286 HIGGEAST 3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20928 | 119.59 | 527149 MUSTANG 6 230 527151 GS-MUSTANG 6 230 @1
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.62 | 527202 SEAGRAVES 3 115 3WXFMR ABB MLL92408 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.59 | 527212 DIAMONDBACK3 115 3WXFMR HOW 36773714 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20921 | 120.88 | 527286 HIGGEAST 3 115 527363 HIGG 3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20923 | 120.62 | 527325 OXY_WSEM_TP3 115 527362 JOHNSON_DRW3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.59 | 527340 DOSS 3 115 3WXFMR ELCO 13566/1 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.58 | 527345 LEGACY 2 69.0 527350 XTO_ROBRTSN2 69.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.58 | 527346 LEGACY 3 115 3WXFMR VROL 13735-1 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.56 | 527350 XTO_ROBRTSN2 69.0 527355 BOARDMAN 2 69.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.51 | 527355 BOARDMAN 2 69.0 527365 FLANNAGAN 2 69.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.5 | 527360 MAPCO 3 115 527362 JOHNSON_DRW3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.58 | 527362 JOHNSON_DRW3 115 528775 LE-ERF 3 115 @1
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.48 | 527370 TENNECO_TAP2 69.0 527371 TENNECO 2 69.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20928 | 120.29 | 527470 CHVS_SLRCOL3 115 527482 CHAVES_CNTY3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21101 | 121.58 | 527483 CHAVES_CNTY6 230 527799 EDDY_NORTH 6 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.49 | 527508 PRICE 3 115 527509 PRICE_TAP 3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.5 | 527514 CV-PINE 2 69.0 527563 ROSWLL_INT 2 69.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.52 | 527563 ROSWLL_INT 2 69.0 527575 SW_4702 2 69.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20943 | 120.61 | 527564 ROSWLL_INT 3 115 527597 TWEEDY 3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.52 | 527575 SW_4702 2 69.0 527589 CV-ORCHARD 2 69.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.48 | 527589 CV-ORCHARD 2 69.0 527619 DEXTER_TP 2 69.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20919 | 120.69 | 527653 MILO_WIND 1 34.5 527655 RSVLT_CC_E 7 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20909 | 120.67 | 527654 RSVLT_CC_W 7 345 527655 RSVLT_CC_E 7 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20909 | 120.92 | 527654 RSVLT_CC_W 7 345 527666 RSVLT_COL1 7 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20902 | 120.92 | 527655 RSVLT_CC_E 7 345 527656 CROSSROADS 7 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20909 | 120.92 | 527666 RSVLT_COL1 7 345 3WXFMR RSVLT_COL1 7 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.63 | 527790 EDDY_SVC 1 8.50 527799 EDDY_NORTH 6 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20925 | 120.22 | 527864 CUNNINHAM 3 115 528348 BUCKEYE_TP 3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20925 | 120.52 | 527864 CUNNINHAM 3 115 528568 MONUMNT_TP 3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20911 | 120.69 | 527865 CUNNIGHM_N 6 230 527867 CUNNIGHM_S 6 230 *1
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20921 | 120.51 | 527865 CUNNIGHM_N 6 230 527963 POTASH_JCT 6 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20921 | 120.51 | 527867 CUNNIGHM_S 6 230 527894 HOBBS_INT 6 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20925 | 120.3 | 527894 HOBBS_INT 6 230 3WXFMR ME C0482951 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20923 | 120.57 | 527894 HOBBS_INT 6 230 527903 HOBBS_PLT3 1 18.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.23 | 527896 HOBBS_INT 7 345 527965 KIOWA 7 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.2 | 527896 HOBBS_INT 7 345 528027 RDRUNNER 7 345 UC
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.2 | 527896 HOBBS_INT 7 345 528027 RDRUNNER 7 345 XA
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20925 | 120.29 | 527965 KIOWA 7 345 528027 RDRUNNER 7 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.55 | 528024 RR_SVC_HV 3 115 528021 RDRUNNR_SVC1 15.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.64 | 528024 RR_SVC_HV 3 115 528025 RDRUNNER 3 115 Z1
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.25 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.5 | 528182 NORTH_LOVNG3 115 528193 BLACKRIVER 3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.63 | 528222 CHINA_DRAW 3 115 528225 CD_SVC_HV 3 115 Z1
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20924 | 120.22 | 528333 LE-WEST_SUB3 115 528334 LE-NRTH_INT3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20925 | 120.29 | 528341 LE-SANANDRS3 115 528627 LE-TXACO_TP3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20925 | 120.25 | 528348 BUCKEYE_TP 3 115 528627 LE-TXACO_TP3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20925 | 120.24 | 528463 SANGER_SW 3 115 528575 OXYPERMIAN 3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20925 | 120.24 | 528463 SANGER_SW 3 115 762442 G18-004-TAP 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20925 | 120.52 | 528568 MONUMNT_TP 3 115 528581 BYRD_TP 3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20925 | 120.28 | 528574 OXY_NHU_RCF3 115 528575 OXYPERMIAN 3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20925 | 120.5 | 528596 CARDINAL 3 115 528605 TARGA 3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20925 | 120.53 | 528603 NA_ENRICH 3 115 528605 TARGA 3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.61 | 528617 LE-WAITS 2 69.0 528325 LE-WAITS 3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.51 | 528617 LE-WAITS 2 69.0 528714 LE-FORT_SW 2 69.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.49 | 528617 LE-WAITS 2 69.0 528759 LE-TP51 2 69.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20925 | 120.29 | 528622 LE-SANANDRS2 69.0 528341 LE-SANANDRS3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.92 | 528626 LE-PLNSINT 2 69.0 526928 PLAINS_INT 3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.92 | 528626 LE-PLNSINT 2 69.0 528709 LE-PLNSGOAB2 69.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.52 | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.59 | 528669 LE-STKLDRTP2 69.0 528740 LE-PLANS_SW2 69.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.79 | 528709 LE-PLNSGOAB2 69.0 528740 LE-PLANS_SW2 69.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.52 | 528709 LE-PLNSGOAB2 69.0 528747 LE-ALLRED 2 69.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.51 | 528714 LE-FORT_SW 2 69.0 528718 LE-NEWTEX 2 69.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.59 | 528735 LE-PLAINSUB2 69.0 528740 LE-PLANS_SW2 69.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.52 | 528775 LE-ERF 3 115 528779 LE-TALLCOTN3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.3 | 531213 SANTAFE3 115 531408 PIERCVL3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20924 | 120.48 | 531501 BUCKNER7 345 531502 CIMRRN 7 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20924 | 120.48 | 531502 CIMRRN 7 345 531503 CIMRRN 1 34.5 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20912 | 120.24 | 531510 HARBNGR3 115 3WXFMR HARBGR345 _1 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20923 | 120.5 | 539803 IRONWOOD7 345 3WXFMR IRONWOOD MPT 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20925 | 120.59 | 542951 HAW G5 1 22.0 543665 HAWTHN5 161 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20924 | 120.63 | 542955 LAC G1 1 22.0 542981 LACYGNE7 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20923 | 120.62 | 542956 LAC G2 1 24.0 542981 LACYGNE7 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20922 | 120.67 | 542957 IAT G1 1 24.0 542982 IATAN 7 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20923 | 120.74 | 542962 IAT G2 1 24.5 542982 IATAN 7 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21174 | 119.99 | 560022 CRAWFISH_DR 345 762216 G17-151TAP 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21142 | 120.98 | 560022 CRAWFISH_DR 345 762467 G18-015-TAP 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 116.89 | 560022 CRAWFISH_DR 345 763087 GEN-2018-073 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21254 | 121.28 | 560022 CRAWFISH_DR 345 763215 G18-092-TAP 345 2
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.99 | 560252 G10-14 345 560253 G10-14-1 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.69 | 560253 G10-14-1 115 560254 G10-14-SUB1 34.5 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.69 | 560253 G10-14-1 115 560255 G10-14-SUB2 34.5 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.52 | 560581 G06-44-2 34.5 523111 NOVUS1 3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.57 | 560582 G06-44-3 34.5 560577 G06-44 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.56 | 560583 G06-44-4 34.5 560577 G06-44 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.17 | 560757 ASGI13_02_1 69.0 560758 ASGI13_02_2 34.5 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.17 | 560757 ASGI13_02_1 69.0 562731 WHEATLAND 69.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.17 | 560763 ASGI13_03_1 115 560761 ASGI13_03_2 34.5 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.66 | 562015 FIREWHEEL1 34.5 523215 FREWHELCOL17 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.66 | 562016 FIREWHEEL2 34.5 523215 FREWHELCOL17 345 2
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.16 | 562323 AGI1202&1305 115 562324 AGI1202&1305 34.5 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.17 | 562727 LESBIA 115 562728 SANJONTAP 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.17 | 562728 SANJONTAP 115 562729 CAPROCKTAP1 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.17 | 562730 CAPROCKTAP2 69.0 562729 CAPROCKTAP1 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.17 | 562730 CAPROCKTAP2 69.0 562731 WHEATLAND 69.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.65 | 563171 G15082_2 34.5 563170 G15082_1 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.23 | P11:13.8:AEPW:COM1-1
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.24 | P11:13.8:AEPW:COM2-1
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.25 | P11:13.8:AEPW:COM3-1
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.26 | P11:18:AEPW:WELSH1-1
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.26 | P11:18:AEPW:WELSH3-1
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.25 | P11:24:AEPW:PIRKEY 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.13 | P11:24:AEPW:SWS3-1
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.2 | P11:24:AEPW:TURKCOAL
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20938 | 120.56 | P12:138:AEPW-OMPA:DUNCAN-4:OMDUNCN4
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20931 | 120.09 | 584560 GEN-2015-014 115 584561 G15-014XFMR1 34.5 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20927 | 120.29 | P12:138:AEPW:ARSHILL4:STLGENS4
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20933 | 120.51 | P12:138:AEPW:SANTAFE:DUNCAN-4
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.5 | 588480 A16-010_SUB 115 3WXFMR A16-010_SUB 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20938 | 120.55 | P12:138:AEPW:DUNCAN-4:L.E.S.-4
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 119.91 | 588761 G17-033XFMR1 34.5 588760 GEN-2017-033 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 119.91 | 588765 G17-033XFMR2 34.5 588760 GEN-2017-033 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.51 | 588861 G17-047XFMR1 34.5 588860 GEN-2017-047 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20911 | 120.25 | P12:138:AEPW:ELKCTY-4:CLINTJC4
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.49 | P12:138:AEPW:SHERID4:112GORE4
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21173 | 122.68 | P12:345:AEPW:L.E.S7:TERRYRD7
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21173 | 122.67 | P12:345:AEPW:L.E.S7:TERRYRD7
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21172 | 122.65 | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21247 | 122.27 | P12:345:AEPW-OKGE:L.E.S.-7:GRACMNT7
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21247 | 122.24 | P12:345:AEPW-OKGE:L.E.S.-7:GRACMNT7
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.2096 | 120.48 | P12:345:AEPW-OKGE:PITTSB-7:JOHNCO7
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.2092 | 120.25 | P12:345:AEPW-OKGE:PITTSB-7:SEMINOL7
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20941 | 120.52 | P12:345:AEPW-WFEC:VALIANT7:HUGO7
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21233 | 123.25 | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.55 | P22:345:AMMO::LABADIE:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.53 | P22:345:AMMO::LABADIE:2
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.55 | P22:345:AMMO::LABADIE:3
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.55 | P22:345:AMMO::LABADIE:4
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.54 | P22:345:AMMO::RUSHISLAND:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.51 | P22:345:AMMO::RUSHISLAND:2
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20927 | 120.24 | P13:138-13.8:AEPW:COMANC-4_#2
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20867 | 119.94 | P13:138-230:AEPW:ELKCTY-4
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20927 | 120.26 | P13:138-24:AEPW:PIRKEY 4
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20931 | 120.15 | P13:138-24:AEPW:S.W.S.-4
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20927 | 120.21 | P13:138-24:AEPW:TURK 4
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20943 | 120.54 | P13:138-345:AEPW:L.E.S.-4_#2
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20928 | 120.55 | P23:500:EES-EAI:KEO:B4941
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20928 | 120.53 | P23:500:EES-EAI:KEO:B4921
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20909 | 120.51 | 640183 GENTLMN3 345 640325 REDWILO3 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.48 | P11:26:EES-EAI:INDEP2:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20927 | 120.51 | P23:500:EES-EAI:INDEP2:B6126
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.51 | P23:500:EES-EAI:PD:INDEP2:LN:FK479
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20928 | 120.26 | P13:345-18:AEPW:WELSH 7_#1
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20928 | 120.26 | P13:345-18:AEPW:WELSH 7_#3
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.25 | P13:69-13.8:AEPW:COMANC-2
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20923 | 120.5 | 648513 GRPR1 3 345 652532 GR PRAIRIE 3 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.56 | P11:024:DPC:ALMA2:6
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20923 | 120.53 | 652537 WHITE 3 345 659286 DEERCREK-BE3 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20924 | 120.48 | 652568 GROTONSOUTH7 115 659275 GROTON_G-BE7 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20923 | 120.53 | 659286 DEERCREK-BE3 345 3WXFMR DEERCRK KU1A 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.49 | 672540 QE 6 138 672541 CORY 6 138 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.53 | 672601 BD 4 230 672306 BD 6G 18.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.53 | 672610 POPLAR 4 230 672310 POPLAR 1G 18.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.53 | 672610 POPLAR 4 230 672311 POPLAR 2G 18.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.53 | 672621 SHAND 4 230 672321 SHAND 1G 18.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.51 | 672649 CODETTE 4 230 672650 NIPAWIN 4 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.5 | 672685 SWIFTCU 4 230 672389 CHINOOK 1G 18.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.5 | 672688 PASQUA 4 230 673390 FUT-PQ1X 18.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.55 | 672696 BRADA 4 230 672699 NBEC 4 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.48 | 672699 NBEC 4 230 672392 NBEC GT 1G 18.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.49 | P13:345-230:CLEC:DOLET:5092
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.6 | P23:345:MDU::COYOTE::5707-5712-5715::::
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.76 | P23:345:MEC:CBEC 905
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.72 | P23:345:MEC:CBEC 908
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.64 | P23:345:MEC:RAUN 0180
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.71 | P23:345:MEC:RAUN 0210
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.64 | P23:345:MEC:LOUISA 954
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.64 | P23:345:MEC:LOUISA 964
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.5 | P21:115:XEL:AUTO-SINGLE:CHEMOLT7:LSPOWER7:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.49 | P21:115:XEL:AUTO-SINGLE:FARIBALTP7:FARIBALTGEN:Z
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.61 | P21:230:OTP:AUTO-SINGLE:SQBUTTE4:YNG24:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.59 | P23:345:OTP:CENTER 3:3215(1)
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.59 | P23:345:OTP:CENTER 3:3225(1)
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 119 | 760494 GEN-2017-146 230 760498 G17-146-TAP 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 119 | 760495 G17-146-XFM1 34.5 760494 GEN-2017-146 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.26 | 761356 G17-239-XFMR 34.5 761355 GEN-2017-239 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.26 | 761359 G17-239-XFMR 34.5 761355 GEN-2017-239 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 114.95 | 762132 GEN-2017-158 230 763252 G18-099-XFM1 34.5 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 114.95 | 762132 GEN-2017-158 230 763255 G18-099-XFM2 34.5 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 115.52 | 762133 G17-158XFM1 34.5 762132 GEN-2017-158 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 115.52 | 762136 G17-158XFM2 34.5 762132 GEN-2017-158 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 117.81 | 762216 G17-151TAP 345 762217 GEN-2017-151 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21174 | 121.31 | 762216 G17-151TAP 345 762467 G18-015-TAP 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 119.71 | 762218 G17-151XFM1 34.5 762217 GEN-2017-151 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 119.71 | 762221 G17-151XFM2 34.5 762217 GEN-2017-151 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 119.71 | 762224 G17-151XFM3 34.5 762217 GEN-2017-151 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 119.71 | 762227 G17-151XFM4 34.5 762217 GEN-2017-151 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.26 | 762438 GEN-2018-004 115 762442 G18-004-TAP 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 118.8 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 119.55 | 762461 G18-015-XFM1 34.5 762460 GEN-2018-015 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 119.55 | 762464 G18-015-XFM2 34.5 762460 GEN-2018-015 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21061 | 120.87 | 762467 G18-015-TAP 345 763215 G18-092-TAP 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 118.04 | 763087 GEN-2018-073 345 763088 G18-073-XFM1 34.5 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 119.21 | 763087 GEN-2018-073 345 763091 G18-073-XFM2 34.5 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 114.92 | 763120 GEN-2018-081 230 763121 G18-081-XFM1 34.5 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 117.23 | 763120 GEN-2018-081 230 764011 G19-074-XFM1 34.5 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 117.2 | 763186 GEN-2018-089 230 763187 G18-089-XFM1 34.5 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 118.06 | 763208 GEN-2018-092 345 763215 G18-092-TAP 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 119.2 | 763208 GEN-2018-092 345 763220 G18-092-XFM1 34.5 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 119.2 | 763208 GEN-2018-092 345 763223 G18-092-XFM2 34.5 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 116.67 | 763241 GEN-2018-097 230 763242 G18-097-XFM1 34.5 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 116.95 | 763241 GEN-2018-097 230 763307 G18-112-XFM1 34.5 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 116.95 | 763241 GEN-2018-097 230 763310 G18-112-XFM2 34.5 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 116.67 | 763241 GEN-2018-097 230 763395 G18-124-XFM1 34.5 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 116.67 | 763241 GEN-2018-097 230 763398 G18-124-XFM2 34.5 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 116.31 | 763483 GEN-2019-003 230 763484 G19-003-XFM1 34.5 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 119.03 | 763483 GEN-2019-003 230 763605 G19-021-XFM1 34.5 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 119.65 | 763516 GEN-2019-011 345 763517 G19-011-XFM1 34.5 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.06 | 763879 GEN-2019-056 115 763880 G19-056XFM1 34.5 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.49 | P13:345,230:CLEC::DOLHILL::1
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.29 | P13:345,24:CLEC::G1DOLHILL::1
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20892 | 120.51 | P42:345:OKGE:SB_BVTY7305
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.2091 | 120.23 | P23:345:WERE:BUFF_345-534::
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.2091 | 120.23 | P23:345:WERE:BUFF_345-543::
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20922 | 120.66 | P23:345:WERE:JEC_345-15::
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.2092 | 120.62 | P23:345:WERE:JEC_345-16::
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20922 | 120.66 | P23:345:WERE:JEC_345-19::
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20922 | 120.66 | P23:345:WERE:JEC_345-20::
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.2092 | 120.29 | P23:345:WERE:WICH_345-50::
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20925 | 120.87 | P23:345:WERE:WOLF_345-50::
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.87 | P23:345:WERE:WOLF_345-60::
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20927 | 120.28 | P42:345:AEPW:WELSH CB 10620 NBTB+FAULT
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.27 | P41:345:AEPW:WELSH CB 10630 NBTB+FAULT
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.26 | P41:345:AEPW:WELSH CB 11670 NBTB+FAULT
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20929 | 120.53 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.26 | P41:345:AEPW:WELSH CB 12540 NBTB+FAULT
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20928 | 120.49 | P43:345:AEPW:CHAMBERS SPRING CB 12720 NBTB+FAULT
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20928 | 120.49 | P42:345:AEPW:CHAMBERS SPRING CB 13720 NBTB+FAULT
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20928 | 120.49 | P42:345:AEPW:CHAMBERS SPRING CB 13850 NBTB+FAULT
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21233 | 121.76 | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.2128 | 122.49 | P42:345:AEPW:LAWTON EASTSIDE CB 3413A NBTB+FAULT
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21314 | 122.73 | P42:345:AEPW:LAWTON EASTSIDE CB 3425A NBTB+FAULT
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21246 | 123.34 | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.2096 | 120.48 | P42:345:AEPW:PITTSBURG CB 3433A NBTB+FAULT
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20936 | 120.18 | P42:345:AEPW:PITTSBURG CB 3441A NBTB+FAULT
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.2092 | 120.25 | P42:345:AEPW:PITTSBURG CB 3445A NBTB+FAULT
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21173 | 122.67 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21173 | 122.67 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21173 | 122.65 | P42:345:AEPW:TERRYRD_CB_3421A_NBTB
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20924 | 120.65 | P23:345:KCPL:LACYGNE_R2-5::LACYGU2-LACYGNE-STILWELL
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20924 | 120.28 | P45:345:UMZW:# 1328 #: GI IN NE.
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20927 | 120.28 | P23:345:AEPW:WELSH CB 10620 NBTB
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.27 | P23:345:AEPW:WELSH CB 10630 NBTB
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.26 | P23:345:AEPW:WELSH CB 11670 NBTB
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20929 | 120.53 | P23:345:AEPW:WELSH CB 11990 NBTB
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.26 | P23:345:AEPW:WELSH CB 12540 NBTB
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20928 | 120.49 | P23:345:AEPW:CHAMBERS SPRING CB 12720 NBTB
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20928 | 120.49 | P23:345:AEPW:CHAMBERS SPRING CB 13720 NBTB
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20928 | 120.49 | P23:345:AEPW:CHAMBERS SPRING CB 13850 NBTB
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21233 | 122.19 | P23:345:AEPW:OKLAUNION CB 3401A NBTB
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.2128 | 122.49 | P23:345:AEPW:LAWTON EASTSIDE CB 3413A NBTB
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21314 | 122.73 | P23:345:AEPW:LAWTON EASTSIDE CB 3425A NBTB
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21246 | 123.34 | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.2096 | 120.48 | P23:345:AEPW:PITTSBURG CB 3433A NBTB
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20936 | 120.18 | P23:345:AEPW:PITTSBURG CB 3441A NBTB
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.2092 | 120.25 | P23:345:AEPW:PITTSBURG CB 3445A NBTB
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21173 | 122.67 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21173 | 122.67 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21173 | 122.65 | P23:345:AEPW:TERRYRD_CB_3421A_NBTB
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20956 | 120.48 | P12:138:AEPW:S.W.S.-4:L.E.S.-4
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20925 | 120.54 | P11:161:GMO:DOGWOOD_COMBINED_CYCLE_UNIT_OUTAGE
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.54 | P11:115:SUNC:GARDENCITY_S2:97:531459(2)
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20912 | 120.25 | P12:345:PWT:BUFF-THIS_345_1::
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20912 | 120.25 | P12:345:PWT:BUFF-THIS_345_2::
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20935 | 120.52 | P12:069:WFEC:ANADRKO_WATONGA
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20944 | 120.54 | P23:345:AEPW:VALLIANT CB 3413A NBTB
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.2095 | 120.56 | P23:345:AEPW:VALLIANT CB 3417A NBTB
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.2119 | 122.82 | P23:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21446 | 125.21 | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20944 | 120.54 | P42:345:AEPW:VALLIANT CB 3413A NBTB+FAULT
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.2095 | 120.56 | P42:345:AEPW:VALLIANT CB 3417A NBTB+FAULT
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.2119 | 122.82 | P42:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB+FAULT
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21446 | 125.21 | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20466 | 117.77 | P42:345:OKGE:SB_BVTY7315_PRE19S
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20888 | 120.52 | P23:345:SUNC:MO_BRK188
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21045 | 120.68 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20927 | 120.23 | P12:138-13.8:AEPW:COMANC-4_#1
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20867 | 119.93 | P12:230:AEPW:ELKCITY6:CHISHOLM6
Thermal | 05ALL | 1 | 26WP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21036 | 121.03 | P12:230:AEPW:SWEETWT6:CHISHOLM6
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997711 ABBXNL844501 230 1 |  | 552.5 | 0.3412 | 164.23 | 525531 TOLK 6 230 3WXFMR TOLK 6 2
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20928 | 120.49 | P12:345:AEPW-AEPW:CHAMPSP-CLARKSV
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20927 | 120.61 | P23:345:KCPL-WERE:237LACYGNE_R1-6::LACYGU1-LACYGNE-NEOSHO
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20925 | 120.5 | P11:161:GMO:DOGWOOD_COMBINED_CYCLE_UNIT_OUTAGE_1_1
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20933 | 118.96 | P11:115:SPS:MUSTANG1&3:153MW::::
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21179 | 122.27 | P12:230:SPS:K37::1_TOLK_LAMB:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20946 | 120.48 | P12:230:SPS:K43::1_PRNGLE_HARR_E:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20929 | 120.26 | P12:230:SPS:K44::1_EPLNT_HARRW:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.2094 | 120.61 | P12:115:SPS:T04::1_TRBLNC_CASTRO:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20925 | 120.48 | P12:115:SPS:T13::1_TAYLOR_WHOBBS:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20925 | 120.26 | P12:115:SPS:T14::1_MADDOX_TAYLOR:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.73 | P12:115:SPS:T21::1_GRSSLND_GRAHAM:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20925 | 120.29 | P12:115:SPS:T23::1_PCA_POTJCT:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20927 | 120.52 | P12:115:SPS:T26::1_CHAVES_RSWLCTY:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21046 | 120.8 | P12:115:SPS:T28A::1_LAMTON_PLANTX:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.2097 | 120.54 | P12:115:SPS:T29::1_LAMTON_HALECTR:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21093 | 121.92 | P12:115:SPS:T30::1_LAMB_HOCKLY:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21093 | 121.43 | P12:115:SPS:T31::1_HOCKLY_SUNDWN:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20921 | 120.59 | P12:115:SPS:T35::1_TERRY_YOAKUM:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 121.24 | P12:115:SPS:T45::1_NORRIS_OASIS:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21052 | 120.73 | P12:115:SPS:T59::1_CARGIL_CURRY:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21023 | 120.66 | P12:115:SPS:T67::1_HAPPY_KRESS:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20921 | 120.96 | P12:115:SPS:T71::1_CRLSLE_YUMA:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20934 | 120.57 | P12:115:SPS:T81::1_COX_FLOYD:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20925 | 120.57 | P12:115:SPS:T83::1_SP-FKFD_ALLEN:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20921 | 120.91 | P12:115:SPS:T89::1_DC_N_HIGG:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.54 | P12:115:SPS:T91::1_HIGG_RUSSELL:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20948 | 120.51 | P12:115:SPS:V04::1_EPLANT_RNDALL:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20939 | 120.5 | P12:115:SPS:V07::1_COX_HALECTR:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21038 | 120.71 | P12:115:SPS:V09::1_HALECTR_PLANTX:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20925 | 120.56 | P12:115:SPS:V12::1_PLANTX_BAILEY:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.5 | P12:115:SPS:V15::1_TUCO_INDANA:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20917 | 120.51 | P12:115:SPS:V16::1_TERRY_DC_N:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.2089 | 120.62 | P12:115:SPS:V24::1_WOLFTH_TERRY:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20943 | 120.6 | P12:115:SPS:V26::1_RSWLL_EDDY_N:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.58 | P12:115:SPS:V33::1_LUBBS_LYNN:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.2103 | 121.13 | P12:115:SPS:V37::1_CASTRO_PLANTX:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.63 | P12:115:SPS:V46::1_ALLEN_WHEELCK:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20927 | 120.95 | P12:115:SPS:V49::1_YOAKUM_SHLCO2:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20968 | 121.15 | P12:115:SPS:V55::1_SUNDWN_TERRY:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20936 | 120.98 | P12:115:SPS:V56::1_COCHRAN_SUNDWN:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20939 | 120.5 | P12:115:SPS:V78::2_CURRY_RSVLT:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20924 | 120.67 | P12:115:SPS:V81::1_LE-WAIT_LE-LVN:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.54 | P12:115:SPS:V95::1_DC_N_SHLCO2:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.5 | P12:115:SPS:W11::1_DC_S_SMINLE:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20925 | 120.54 | P12:115:SPS:W14::1_SMINLE_GAINES:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20925 | 120.5 | P12:115:SPS:W26::1_CUNGHM_OILCNTR:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 121.13 | P12:115:SPS:W32::1_PRMTR_FE-CLSIN:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.5 | P12:115:SPS:W34::1_JNSDRW_MAPCO:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20923 | 120.73 | P12:115:SPS:W35::1_GAINES_JNSDRW:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.2092 | 120.52 | P12:115:SPS:W36::1_TAYLOR_JNSDRW:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21116 | 120.93 | P12:115:SPS:W40::1_WCANYON_TRBLNC:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20936 | 120.29 | P12:115:SPS:W46::1_RHILLS_NWEST:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20953 | 120.55 | P12:115:SPS:W52::1_NEWHART_KRESS:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 121.01 | P12:115:SPS:W58::1_NORTON_LOPEZ:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.69 | P12:115:SPS:W59::1_LOPEZ_CMPBLL:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20927 | 120.96 | P12:115:SPS:W62::1_PLSTHL_CURRY:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.84 | P12:115:SPS:W64::1_PLSTHL_FE-CLV:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20927 | 120.81 | P12:115:SPS:W65::1_PLSTHL_CURRY:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.68 | P12:115:SPS:W66::1_PORTA_GREYHUND:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21116 | 120.53 | P12:115:SPS:W77::1_RNDAL_WCANYON:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.51 | P12:115:SPS:W99::1_CAPITAN_CHAVES:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20925 | 120.51 | P12:115:SPS:U03::1_CARDNL_NEF:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20922 | 121.04 | P12:115:SPS:U14::1_DC_STH_INKBSN:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20924 | 120.92 | P12:115:SPS:V15::1_INKBSN_LE-WAT:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20948 | 120.55 | P12:115:SPS:U16::1_BSHLND_OUTPST:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20948 | 120.54 | P12:115:SPS:U17::1_COLTR_OUTPST:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20933 | 120.76 | P12:115:SPS:U19::1_DEAN_PLAINS:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20948 | 120.49 | P12:115:SPS:U23::1_COLTR_HILSDE:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.201 | 127.42 | P42:345:SPS:YOAKUM:J18####:SLG1:EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.201 | 127.42 | P43:345:SPS:YOAKUM:TF#####:SLG:EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.201 | 127.42 | P42:345:SPS:YOAKUM:J17####:SLG:EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20181 | 122.69 | P43:345:SPS:TUCO:SLG::EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.201 | 127.42 | P42:345:SPS:YOAKUM:J18####:SLG2:EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20928 | 120.49 | P12:345:AEPW-AEPW:CHAMPSP-CLARKSV:::EHV::
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20925 | 120.52 | P11:18:HAST:::EGYCTR2G WEC2_LOSS OF WEC 2 GEN_:HV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20925 | 120.52 | P13:18-115:HAST:::EGYCNTR7 XFMR G2WEC 2 GSU_:HV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20925 | 120.5 | P11:161:GMO:DOGWOOD-COMBINED-CYCLE-UNIT-OUTA:::HV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20927 | 120.61 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20924 | 120.65 | P23:345:KCPL:LACYGNE-R2-5:::EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20922 | 120.66 | P11:230:WERE:JECU1-GEN:::HV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20922 | 120.66 | P11:345:WERE:JECU2-GEN:::EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20922 | 120.66 | P11:345:WERE:JECU3-GEN:::EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.88 | P11:345:WERE:WOLFU1-GEN:::EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20912 | 120.25 | P12:345:PWT:BUFF-THIS-345-1:::EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20912 | 120.25 | P12:345:PWT:BUFF-THIS-345-2:::EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.2091 | 120.23 | P23:345:WERE:BUFF-345-534:::EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.2091 | 120.23 | P23:345:WERE:BUFF-345-543:::EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20922 | 120.66 | P23:345:WERE:JEC-345-15:::EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.2092 | 120.62 | P23:345:WERE:JEC-345-16:::EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20922 | 120.66 | P23:345:WERE:JEC-345-19:::EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20922 | 120.66 | P23:345:WERE:JEC-345-20:::EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.2092 | 120.29 | P23:345:WERE:WICH-345-50:::EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20925 | 120.87 | P23:345:WERE:WOLF-345-50:::EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.87 | P23:345:WERE:WOLF-345-60:::EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.81 | P11:022:NPPD:COOPER1G:1:983:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.2092 | 120.83 | P11:023:NPPD:GENTLM1G:1:757:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20924 | 120.68 | P11:024:NPPD:GENTLM2G:2:757:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20921 | 120.68 | P13:345:OPPD:NEBCTY1G:::EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.2092 | 120.69 | P13:345:OPPD:NEBCTY2G:::EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.69 | P22:345:OPPD:S3458 NEBCTY1G:LT::EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20921 | 120.68 | P22:345:OPPD:S3458 NEBCTY1G:::EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.72 | P22:345:OPPD:S3458 NEBCTY2G:LT::EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.2092 | 120.69 | P22:345:OPPD:S3458 NEBCTY2G:::EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.69 | P23:345:OPPD:S3458 NEBCTY1G:LT::EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20921 | 120.68 | P23:345:OPPD:S3458 NEBCTY1G:::EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.72 | P23:345:OPPD:S3458 NEBCTY2G:LT::EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.2092 | 120.69 | P23:345:OPPD:S3458 NEBCTY2G:::EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.29 | P12:115:SUNC:PLYMELL-PIERCEVILLE:::HV::
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20923 | 120.53 | P11:018:UMZB:# 5 #:: DCS IN SD. DEERCREEK_MV::
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20924 | 120.5 | P11:022:UMZB:# 15 #:: LO IN ND. LELAND OLDS 1_MV::
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20925 | 120.5 | P11:020:UMZB:# 16 #:: LO IN ND. LELAND OLDS 2_MV::
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20923 | 120.61 | P11:023:UMZB:# 31 #:: AVS IN ND. ANTELOPE VALLEY 1_MV::
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20923 | 120.61 | P11:023:UMZB:# 32 #:: AVS IN ND. ANTELOPE VALLEY 2_MV::
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20919 | 120.82 | P11:024:UMZB:# 33 #:: LRS IN WY. LARAMIE RIVER STATION 1_MV::
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.49 | P13:230:UMZW:# 5135 #:: OA IN SD. FAULT ON TRANSFORMER (2).:HV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.49 | P13:230:UMZW:# 5136 #:: OA IN SD. FAULT ON TRANSFORMER (3).:HV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.5 | P13:230:UMZW:# 5137 #:: OA IN SD. FAULT ON TRANSFORMER (4).:HV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20924 | 120.28 | P23:345:UMZW:# 2423 #:: GI IN NE. GI 1596 BKR FAULT:EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20924 | 120.28 | P23:345:UMZW:# 2426 #:: GI IN NE. GI 1592 BKR FAULT:EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20924 | 120.28 | P23:345:UMZW:# 2432 #:: GI IN NE. GI 1092 BKR FAULT:EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20924 | 120.28 | P23:345:UMZW:# 2440 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1092 STUCK BKR:EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20924 | 120.28 | P23:345:UMZW:# 2444 #:: GI IN NE. GI-SWEET BRANCH FAULT & GI 1596 STUCK BKR:EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20924 | 120.28 | P23:345:UMZW:# 2446 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1196 STUCK BKR:EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20924 | 120.28 | P42:345:UMZW:# 2413 #:: FT2 IN SD. FT2-LO2 BRANCH FAULT & FT2 2992 STUCK BKR:EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20924 | 120.28 | P42:345:UMZW:# 2415 #:: FT2 IN SD. FT2-GI BRANCH FAULT & FT2 3392 STUCK BKR:EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.2093 | 120.2 | P11:138:WFEC:HUGO1:465MW :::
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20924 | 120.49 | P11:138:WFEC:MORLND2:132MW:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20924 | 120.5 | P11:138:WFEC:MORLND3:149MW :::
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20934 | 120.52 | P12:138:WFEC:ANADRKO_CLVLND::::
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.2092 | 120.25 | P12:345:OKGE-AEPW:BKRBKR20::::
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20961 | 120.7 | P12:345:OKGE:BKRBKR21::::
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20981 | 120.7 | P12:345:OKGE:BKRBKR24::::
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21172 | 122.65 | P12:345:OKGE-AEPW:BKRBKR25::::
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20895 | 120.12 | P12:345:OKGE:BKRBKR336::::
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20894 | 120.11 | P12:345:OKGE:BKRBKR336_2::::
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.2096 | 120.48 | P12:345:OKGE-AEPW:BKRBKR343::::
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21247 | 122.27 | P12:345:OKGE-AEPW:BKRBKR366::::
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21247 | 122.24 | P12:345:OKGE-AEPW:BKRBKR366::::
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21132 | 121.66 | P12:345:OKGE:BKRBKR367::::
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20962 | 120.59 | P12:345:OKGE-WFEC:BKRBKR374::::
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20962 | 120.56 | P12:345:OKGE-WFEC:BKRBKR374::::
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20899 | 120.16 | P12:345:OKGE:BKRBKR4193::::
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20899 | 120.16 | P12:345:OKGE:BKRBKR4194::::
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20889 | 120.16 | P12:345:OKGE-SPS:BKRBKR4201::::
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20889 | 120.16 | P12:345:OKGE-SPS:BKRBKR4202::::
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20893 | 119.95 | P12:345:OKGE:BKRBKR443NEW::::
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20893 | 119.95 | P12:345:OKGE:BKRBKR443NEW2::::
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20909 | 120.27 | P12:345:OKGE-ITC:BKRBKR502::::
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20909 | 120.27 | P12:345:OKGE-ITC:BKRBKR503::::
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20921 | 120.61 | P12:345:OKGE:BKRBKR604::::
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20919 | 120.72 | P12:345:OKGE:BKRBKR604_2::::
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21627 | 123.72 | P42:345:OKGE:SB_BVTY7387::::
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20966 | 120.63 | P42:345:OKGE:SB_SPCK7383::::
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20923 | 120.53 | P11:115:SUNC:GARDENCITY_S2:103:531459(2):HV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20923 | 120.54 | P11:115:SUNC:FORTDDODGE_4:157:539670(4):HV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20888 | 120.5 | P12:345:SUNC-NPPD:MINGO-REDWILLOW::531451-640325(1):EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.61 | P13:115:SUNC:HOLCOMB_GSU:::HV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20923 | 120.53 | P13:115:SUNC:S2_GSU:::HV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20923 | 120.54 | P13:115:SUNC:FORTDODGE_GSU:::HV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.48 | 300002 1THLG2 22.0 301505 5THOMHLGSU2 161 2
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.62 | 300003 1THLG3 24.0 301503 7THOMHLGSU3 345 3
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.48 | 300006 1NM G1 22.0 301536 5NEWMADGSU1 161 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.48 | 300007 1NM G2 22.0 301537 7NEWMADGSU2 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.48 | 300046 7NEWMAD 345 301537 7NEWMADGSU2 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.62 | 300049 7THOMHL 345 301503 7THOMHLGSU3 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.48 | 300103 5NEWMAD 161 301536 5NEWMADGSU1 161 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.48 | 300132 5THMHLB2 161 301505 5THOMHLGSU2 161 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20925 | 120.29 | 300739 7BLACKBERRY 345 532797 WOLFCRK7 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.56 | P11:20:AMMO:1LAB�� G1:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.54 | P11:20:AMMO:1LAB�� G2:2
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.75 | P11:345:AMMO::CALLAWAY:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.56 | P11:345:AMMO::LABADIE:3
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.56 | P11:345:AMMO::LABADIE:4
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.55 | P11:345:AMMO::RUSHISLAND:U1
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.54 | P11:345:AMMO::RUSHISLAND:U2
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.53 | P11:138:AMMO::SIOUX:2
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.49 | P13:345-230:CLEC::DOLHILL7:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.29 | P11:345-24:CLEC::DOLHILL7:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.29 | P11:24:CLEC::G1DOLHIL:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.53 | P12:765:AEP:AEP ROCKP-AEP JEFF 765
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.48 | P11:HV:EES::1ISES U1:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.25 | P11:HV:EES::PIRKEY 1:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.26 | P11:EHV:EES::WELSH3-1:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.2 | P11:HV:EES::TURKCOAL:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.48 | P12:HV:EES::5ISES%:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.74 | P12:EHV:EES::7CALAWY 1:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20928 | 120.49 | P12:EHV:EES::CHAMSPR7!:CLARKSV7!:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20927 | 120.21 | P12:HV:EES::TURK 4%:1(1)
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20928 | 120.26 | P12:EHV:EES::WELSH 7:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20928 | 120.26 | P12:EHV:EES::WELSH 7:1(1)
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20927 | 120.26 | P12:HV:EES::PIRKEY 4:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.53 | 344011 7HUGHES 345 344012 7HPW-N 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.55 | 344884 7LABADIE1 345 344894 1LAB G1 20.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.53 | 344885 7LABADIE2 345 344895 1LAB G2 20.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.55 | 344886 7LABADIE3 345 344896 1LAB G3 20.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.55 | 344887 7LABADIE4 345 344897 1LAB G4 20.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.54 | 345667 7RUSH 1 345 345670 1RUSH G1 18.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.53 | 345668 7RUSH 2 345 345671 1RUSH G2 18.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.52 | 345755 4SIOUX 1 138 345756 1SIOUX 1 18.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.52 | 345764 4SIOUX 2 138 345765 1SIOUX 2 18.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.6 | P12:345:MDU::CENTER:COYOTE:1::::
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.6 | P13:345:MDU:COYOTE GSU LOSS:COYOTE::1::::
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.82 | P11:345:MEC-NPPD:COOPER 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.72 | P11:24:XEL:AUTO-SINGLE:SHERC31G:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.72 | P11:24:XEL:AUTO-SINGLE:SHERC32G:2
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.81 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.64 | P11:20:XEL:AUTO-SINGLE:PRIS31G:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.63 | P11:20:XEL:AUTO-SINGLE:PRIS32G:2
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.68 | P11:22:XEL:AUTO-SINGLE:MNTCE31G:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.64 | P11:20:XEL:AUTO-SINGLE:KING31G:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.48 | P11:18:XEL:AUTO-SINGLE:BLKD76G:6
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.69 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.69 | P11:22:GRE:AUTO-SINGLE:GRE-COAL42G:2
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.61 | P11:24:OTP:AUTO-SINGLE:BIGSTN1G:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.63 | P11:20:OTP:AUTO-SINGLE:CENTER2G:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.52 | P11:22:OTP:AUTO-SINGLE:CENTER1G:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.61 | P11:24:OTP:AUTO-SINGLE:COYOTE1G:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.51 | P11:24:DPC:AUTO-SINGLE:GENOA53G:3
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.5 | P12:115:XEL:AUTO-SINGLE:CHEMOLT7:LSPOWER7:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.49 | P12:115:XEL:AUTO-SINGLE:FARIBALTP7:FARIBALTGEN:Z
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.61 | P12:230:OTP:AUTO-SINGLE:SQBUTTE4:YNG24:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.69 | P13:24-345:XEL:AUTO-SINGLE:SHERC31G:SHERCO3:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.69 | P13:24-345:XEL:AUTO-SINGLE:SHERC32G:SHERCO3:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.78 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.64 | P13:20-345:XEL:AUTO-SINGLE:PRIS31G:PRISLD3:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.64 | P13:20-345:XEL:AUTO-SINGLE:PRIS32G:PRISLD3:2
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.68 | P13:22-345:XEL:AUTO-SINGLE:MNTCE31G:MNTCELO3:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.62 | P13:20-345:XEL:AUTO-SINGLE:KING31G:ASKING3:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.48 | P13:18-115:XEL:AUTO-SINGLE:BLKD76G:BLKDG27:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.67 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL41G:GRE-COALCR4:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.67 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL42G:GRE-COALCR4:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.6 | P13:230-24:OTP:AUTO-SINGLE:BIGSTON4:BIGSTN1G:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.61 | P13:20-230:OTP:AUTO-SINGLE:CENTER2G:YNG24:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.51 | P13:22-230:OTP:AUTO-SINGLE:CENTER1G:CENTER4:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.6 | P13:24-345:OTP:AUTO-SINGLE:COYOTE1G:COYOTE3:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.5 | P13:24-161:DPC:AUTO-SINGLE:GENOA53G:GENOA5:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.55 | P13:24-161:DPC:AUTO-SINGLE:JPM:ALMA5:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.6 | P11:115:XEL:RIV COMBINE CYCLE
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.51 | P12:115:XEL:BDS #2 5
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.49 | P11:115:XEL:HBR #6 7 8
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.63 | P23:345:XEL:8H14 PRI
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.64 | P23:345:XEL:8H17 PRI AS
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.78 | P23:345:XEL:8N28 SHC
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.7 | P23:345:XEL:8N22 SHC
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.69 | P23:345:XEL:8N17 SHC
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.68 | P23:345:XEL:8N8 MNN
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.63 | P23:345:XEL:8P1 KING
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.63 | P23:345:XEL:8P2 KING
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.5 | P11:22:ALTW:AUTO-SINGLE:LANS54G:4
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.64 | P11:22:ALTW:AUTO-SINGLE:ARNOLD1G:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.67 | P11:24:ALTW:AUTO-SINGLE:OTTUMW1G:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.49 | P13:22-161:ALTW:AUTO-SINGLE:LANS54G:LANSINGL15:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.63 | P13:22-161:ALTW:AUTO-SINGLE:ARNOLD1G:ARNOLD5:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.66 | P13:24-161:ALTW:AUTO-SINGLE:OTTUMW1G:OTTUMWA5:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.74 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.8 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.65 | P11:22:MEC:AUTO-SINGLE:NEAL3G:3
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.73 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.66 | P11:24:MEC:AUTO-SINGLE:LOUIS31G:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.72 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.76 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.64 | P13:345-22:MEC:AUTO-SINGLE:RAUN3:NEAL3G:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.71 | P13:345-24:MEC:AUTO-SINGLE:RAUN3:NEAL4G:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.64 | P13:345-24:MEC:AUTO-SINGLE:LOUISA3:LOUIS31G:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20922 | 120.66 | P11:230:WERE:JECU1_GEN::
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20922 | 120.66 | P11:345:WERE:JECU2_GEN::
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20922 | 120.66 | P11:345:WERE:JECU3_GEN::
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.88 | P11:345:WERE:WOLFU1_GEN::
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20933 | 120.48 | 511453 DUNCAN-4 138 511552 DUNCHERTP4 138 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20933 | 120.48 | 511455 D.E.S.-4 138 511552 DUNCHERTP4 138 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.48 | 511456 O.K.U.-7 345 511565 OKLAUN HVDC7 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 119.42 | 511456 O.K.U.-7 345 588760 GEN-2017-033 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21233 | 122.19 | 511456 O.K.U.-7 345 763215 G18-092-TAP 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21246 | 122.76 | 511468 L.E.S.-7 345 762467 G18-015-TAP 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21143 | 122.19 | 511468 L.E.S.-7 345 763215 G18-092-TAP 345 2
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20938 | 120.56 | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21045 | 120.68 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20262 | 117.21 | 511553 CHISHOLM7 345 523961 POTTER_CO 7 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20262 | 117.21 | 511553 CHISHOLM7 345 523961 POTTER_CO 7 345 2
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20633 | 119.86 | 511553 CHISHOLM7 345 755000 WWDBORDT 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20924 | 120.5 | 511557 CHISHOLM6 230 3WXFMR CHISHOLM6 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20939 | 120.51 | 514801 MINCO 7 345 555234 NSUB345 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20852 | 120.15 | 515375 WWRDEHV7 345 755000 WWDBORDT 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21627 | 123.76 | 515458 BORDER 7 345 560022 CRAWFISH_DR 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21627 | 123.7 | 515458 BORDER 7 345 755000 WWDBORDT 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20924 | 120.51 | 515618 BALKOW 7 345 3WXFMR BALKOW 7 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20924 | 120.5 | 515618 BALKOW 7 345 3WXFMR BALKOW 7 1_Dup1
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20919 | 120.73 | 515634 PALDR1W7 345 3WXFMR PALO2 _1 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.63 | 515677 BADGER 7 345 563170 G15082_1 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.49 | 522800 MU-TULIA 3 115 525179 TULIA_TP 3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.63 | 522892 MU-BROWNFLD2 69.0 526761 BROWNFLD_TP2 69.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20923 | 120.52 | 523093 HITCHLAND 3 115 523174 GOODWELLWND3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21053 | 120.53 | 523095 HITCHLAND 6 230 523309 MOORE_CNTY 6 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.88 | 523097 HITCHLAND 7 345 523112 NOVUS1 7 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.93 | 523097 HITCHLAND 7 345 523215 FREWHELCOL17 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20717 | 119.43 | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.99 | 523097 HITCHLAND 7 345 560252 G10-14 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.5 | 523099 TC-DRYTRLS 3 115 588480 A16-010_SUB 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.74 | 523112 NOVUS1 7 345 3WXFMR NOVUS XF2 2
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.52 | 523112 NOVUS1 7 345 3WXFMR XIANA2011198 _1 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20923 | 120.5 | 523118 BUFF_DUNES 7 345 523853 FINNEY 7 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.51 | 523120 COLE 3 115 588860 GEN-2017-047 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20935 | 120.48 | 523221 XIT_INTG 6 230 3WXFMR SIEM_T126401 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20946 | 120.48 | 523267 PRINGLE 6 230 3WXFMR ENRCO13617-1 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20946 | 120.48 | 523267 PRINGLE 6 230 523979 HARRNG_EST 6 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20988 | 120.61 | 523309 MOORE_CNTY 6 230 523323 MCDWL_CREEK6 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.2096 | 120.53 | 523323 MCDWL_CREEK6 230 523959 POTTER_CO 6 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20896 | 120.85 | 523959 POTTER_CO 6 230 523979 HARRNG_EST 6 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21737 | 121.98 | 523959 POTTER_CO 6 230 524267 BUSHLAND 6 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.2171 | 122.4 | 523959 POTTER_CO 6 230 525461 NEWHART 6 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21287 | 129.34 | 523961 POTTER_CO 7 345 3WXFMR WAUK 90343-A 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20912 | 120.79 | 523961 POTTER_CO 7 345 524296 SPNSPUR_WND7 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20928 | 120.27 | 523977 HARRNG_WST 6 230 523971 HARRNGTON1 1 24.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20905 | 120.79 | 523977 HARRNG_WST 6 230 524010 ROLLHILLS 6 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20925 | 120.22 | 523978 HARRNG_MID 6 230 523979 HARRNG_EST 6 230 @1
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20925 | 120.29 | 524010 ROLLHILLS 6 230 3WXFMR WAUK WT01104 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20948 | 120.55 | 524267 BUSHLAND 6 230 3WXFMR WH 7001795 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.22387 | 122.23 | 524267 BUSHLAND 6 230 524623 DEAFSMITH 6 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20912 | 120.89 | 524296 SPNSPUR_WND7 345 524299 SPNSPUR_COL7 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20912 | 120.89 | 524299 SPNSPUR_COL7 345 3WXFMR SPNSPUR_COL7 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21317 | 120.9 | 524415 AMA_SOUTH 6 230 525213 SWISHER 6 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 121.01 | 524502 NORTON 3 115 524509 FE-TUCMCARI3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21116 | 120.82 | 524575 DS-#25+ 3 115 524597 PANDAHFD 3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21116 | 120.9 | 524575 DS-#25+ 3 115 524630 TIERABLANCA3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.5 | 524604 HEREFRD_SB 2 69.0 524608 HERFRD_STH 2 69.0 *1
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.22236 | 125.98 | 524623 DEAFSMITH 6 230 760498 G17-146-TAP 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.78 | 524721 DS-#15&#19+2 69.0 524745 CASTRO_CNTY2 69.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.84 | 524764 NORRIS_TP 3 115 524801 NORRIS 3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20932 | 120.49 | 524770 PLSNT_HILL 6 230 3WXFMR EFAE1100068A 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.84 | 524776 N_CLOVIS_TP3 115 524777 N_CLOVIS 3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.78 | 524790 CANNON_TP 3 115 524794 CANNONAFB 3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21343 | 127.03 | 524875 OASIS 6 230 524885 SN_JUAN_TAP6 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20999 | 121.66 | 524875 OASIS 6 230 524909 ROOSEVELT 6 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21325 | 127.79 | 524885 SN_JUAN_TAP6 230 527483 CHAVES_CNTY6 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20942 | 120.65 | 524909 ROOSEVELT 6 230 3WXFMR ABB LMM60042 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21617 | 125.82 | 524909 ROOSEVELT 6 230 525531 TOLK 6 230 2
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 121.25 | 524923 PORTALES 2 69.0 524929 RO-PORT_MTR2 69.0 @1
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.88 | 524923 PORTALES 2 69.0 524941 PORTALES#1 2 69.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.84 | 525023 BC-BAIL_MTR2 69.0 525027 BAILEYCO 2 69.0 @1
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.2103 | 120.8 | 525056 BC-EARTH 3 115 525480 PLANT_X 3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.57 | 525192 KRESS_INT 3 115 3WXFMR ENRCO 136155 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20937 | 120.29 | 525213 SWISHER 6 230 3WXFMR SIEM_T127101 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21223 | 121.59 | 525213 SWISHER 6 230 525461 NEWHART 6 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.54 | 525272 KISER 3 115 3WXFMR VON 13819/1 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.81 | 525326 COX 3 115 3WXFMR ELCO 13474-3 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.81 | 525414 LAMTON 3 115 3WXFMR ASEA MLL9204 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.22535 | 123.54 | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21198 | 122.16 | 525481 PLANT_X 6 230 3WXFMR WH ALM20171 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21856 | 127.05 | 525481 PLANT_X 6 230 526435 SUNDOWN 6 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.22236 | 124.03 | 525481 PLANT_X 6 230 760498 G17-146-TAP 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21271 | 120.86 | 525481 PLANT_X 6 230 762174 G17-218TAP 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21313 | 120.92 | 525481 PLANT_X 6 230 762174 G17-218TAP 230 2
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.22055 | 128.41 | 525531 TOLK 6 230 525586 NEEDMORE 6 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21179 | 122.27 | 525531 TOLK 6 230 525637 LAMB_CNTY 6 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.23816 | 127.4 | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21436 | 121.08 | 525531 TOLK 6 230 762174 G17-218TAP 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21471 | 121.13 | 525531 TOLK 6 230 762174 G17-218TAP 230 2
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.3412 | 162.04 | 525549 TOLK 7 345 3WXFMR ABBXNL844501 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.22055 | 128.41 | 525586 NEEDMORE 6 230 526935 YOAKUM 6 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21179 | 122.27 | 525637 LAMB_CNTY 6 230 3WXFMR WH ALM20172 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.54 | 525828 TUCO_INT 3 115 3WXFMR DS F78800913 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21357 | 120.96 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21476 | 121.11 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _9 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20181 | 122.69 | 525832 TUCO_INT 7 345 526936 YOAKUM_345 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21093 | 121.33 | 526020 HOCKLEY 3 115 526036 LC-OPDYKE 3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21093 | 121.18 | 526036 LC-OPDYKE 3 115 526434 SUNDOWN 3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.57 | 526160 CARLISLE 3 115 3WXFMR WH RLP38371 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.79 | 526162 LP-DOUD_TP 3 115 526176 LP-DOUD 3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.82 | 526268 LUBBCK_STH 3 115 3WXFMR NA 70454A 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20936 | 120.81 | 526361 COCHRAN 3 115 526424 PACIFIC 3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20936 | 120.9 | 526424 PACIFIC 3 115 526434 SUNDOWN 3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20968 | 120.94 | 526434 SUNDOWN 3 115 526445 AMOCO_TP 3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20921 | 120.51 | 526435 SUNDOWN 6 230 3WXFMR UPDATE LATER _12 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20944 | 124.22 | 526435 SUNDOWN 6 230 526460 AMOCO_SS 6 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20968 | 120.8 | 526445 AMOCO_TP 3 115 526484 LG-LEVELAND3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20944 | 121.88 | 526460 AMOCO_SS 6 230 526935 YOAKUM 6 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20968 | 120.79 | 526484 LG-LEVELAND3 115 526491 LG-CLAUENE 3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20923 | 120.51 | 526525 WOLFFORTH 6 230 3WXFMR UPDATE LATER _13 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20916 | 122.38 | 526935 YOAKUM 6 230 527028 INK_BASIN 6 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20181 | 129.67 | 526936 YOAKUM_345 345 527896 HOBBS_INT 7 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20905 | 121.79 | 527028 INK_BASIN 6 230 527894 HOBBS_INT 6 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20921 | 120.9 | 527130 DENVER_N 3 115 527286 HIGGEAST 3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20928 | 119.59 | 527149 MUSTANG 6 230 527151 GS-MUSTANG 6 230 @1
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.62 | 527202 SEAGRAVES 3 115 3WXFMR ABB MLL92408 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.59 | 527212 DIAMONDBACK3 115 3WXFMR HOW 36773714 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20921 | 120.88 | 527286 HIGGEAST 3 115 527363 HIGG 3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20923 | 120.62 | 527325 OXY_WSEM_TP3 115 527362 JOHNSON_DRW3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.59 | 527340 DOSS 3 115 3WXFMR ELCO 13566/1 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.58 | 527345 LEGACY 2 69.0 527350 XTO_ROBRTSN2 69.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.58 | 527346 LEGACY 3 115 3WXFMR VROL 13735-1 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.56 | 527350 XTO_ROBRTSN2 69.0 527355 BOARDMAN 2 69.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.51 | 527355 BOARDMAN 2 69.0 527365 FLANNAGAN 2 69.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.5 | 527360 MAPCO 3 115 527362 JOHNSON_DRW3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.58 | 527362 JOHNSON_DRW3 115 528775 LE-ERF 3 115 @1
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.48 | 527370 TENNECO_TAP2 69.0 527371 TENNECO 2 69.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20928 | 120.29 | 527470 CHVS_SLRCOL3 115 527482 CHAVES_CNTY3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21101 | 121.58 | 527483 CHAVES_CNTY6 230 527799 EDDY_NORTH 6 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.49 | 527508 PRICE 3 115 527509 PRICE_TAP 3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.5 | 527514 CV-PINE 2 69.0 527563 ROSWLL_INT 2 69.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.52 | 527563 ROSWLL_INT 2 69.0 527575 SW_4702 2 69.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20943 | 120.61 | 527564 ROSWLL_INT 3 115 527597 TWEEDY 3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.52 | 527575 SW_4702 2 69.0 527589 CV-ORCHARD 2 69.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.48 | 527589 CV-ORCHARD 2 69.0 527619 DEXTER_TP 2 69.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20919 | 120.69 | 527653 MILO_WIND 1 34.5 527655 RSVLT_CC_E 7 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20909 | 120.67 | 527654 RSVLT_CC_W 7 345 527655 RSVLT_CC_E 7 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20909 | 120.92 | 527654 RSVLT_CC_W 7 345 527666 RSVLT_COL1 7 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20902 | 120.92 | 527655 RSVLT_CC_E 7 345 527656 CROSSROADS 7 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20909 | 120.92 | 527666 RSVLT_COL1 7 345 3WXFMR RSVLT_COL1 7 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.63 | 527790 EDDY_SVC 1 8.50 527799 EDDY_NORTH 6 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20925 | 120.22 | 527864 CUNNINHAM 3 115 528348 BUCKEYE_TP 3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20925 | 120.52 | 527864 CUNNINHAM 3 115 528568 MONUMNT_TP 3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20911 | 120.69 | 527865 CUNNIGHM_N 6 230 527867 CUNNIGHM_S 6 230 *1
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20921 | 120.51 | 527865 CUNNIGHM_N 6 230 527963 POTASH_JCT 6 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20921 | 120.51 | 527867 CUNNIGHM_S 6 230 527894 HOBBS_INT 6 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20925 | 120.3 | 527894 HOBBS_INT 6 230 3WXFMR ME C0482951 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20923 | 120.57 | 527894 HOBBS_INT 6 230 527903 HOBBS_PLT3 1 18.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.23 | 527896 HOBBS_INT 7 345 527965 KIOWA 7 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.2 | 527896 HOBBS_INT 7 345 528027 RDRUNNER 7 345 UC
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.2 | 527896 HOBBS_INT 7 345 528027 RDRUNNER 7 345 XA
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20925 | 120.29 | 527965 KIOWA 7 345 528027 RDRUNNER 7 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.55 | 528024 RR_SVC_HV 3 115 528021 RDRUNNR_SVC1 15.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.64 | 528024 RR_SVC_HV 3 115 528025 RDRUNNER 3 115 Z1
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.25 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.5 | 528182 NORTH_LOVNG3 115 528193 BLACKRIVER 3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.63 | 528222 CHINA_DRAW 3 115 528225 CD_SVC_HV 3 115 Z1
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20924 | 120.22 | 528333 LE-WEST_SUB3 115 528334 LE-NRTH_INT3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20925 | 120.29 | 528341 LE-SANANDRS3 115 528627 LE-TXACO_TP3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20925 | 120.25 | 528348 BUCKEYE_TP 3 115 528627 LE-TXACO_TP3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20925 | 120.24 | 528463 SANGER_SW 3 115 528575 OXYPERMIAN 3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20925 | 120.24 | 528463 SANGER_SW 3 115 762442 G18-004-TAP 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20925 | 120.52 | 528568 MONUMNT_TP 3 115 528581 BYRD_TP 3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20925 | 120.28 | 528574 OXY_NHU_RCF3 115 528575 OXYPERMIAN 3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20925 | 120.5 | 528596 CARDINAL 3 115 528605 TARGA 3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20925 | 120.53 | 528603 NA_ENRICH 3 115 528605 TARGA 3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.61 | 528617 LE-WAITS 2 69.0 528325 LE-WAITS 3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.51 | 528617 LE-WAITS 2 69.0 528714 LE-FORT_SW 2 69.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.49 | 528617 LE-WAITS 2 69.0 528759 LE-TP51 2 69.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20925 | 120.29 | 528622 LE-SANANDRS2 69.0 528341 LE-SANANDRS3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.92 | 528626 LE-PLNSINT 2 69.0 526928 PLAINS_INT 3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.92 | 528626 LE-PLNSINT 2 69.0 528709 LE-PLNSGOAB2 69.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.52 | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.59 | 528669 LE-STKLDRTP2 69.0 528740 LE-PLANS_SW2 69.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.79 | 528709 LE-PLNSGOAB2 69.0 528740 LE-PLANS_SW2 69.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.52 | 528709 LE-PLNSGOAB2 69.0 528747 LE-ALLRED 2 69.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.51 | 528714 LE-FORT_SW 2 69.0 528718 LE-NEWTEX 2 69.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.59 | 528735 LE-PLAINSUB2 69.0 528740 LE-PLANS_SW2 69.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.52 | 528775 LE-ERF 3 115 528779 LE-TALLCOTN3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.3 | 531213 SANTAFE3 115 531408 PIERCVL3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20924 | 120.48 | 531501 BUCKNER7 345 531502 CIMRRN 7 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20924 | 120.48 | 531502 CIMRRN 7 345 531503 CIMRRN 1 34.5 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20912 | 120.24 | 531510 HARBNGR3 115 3WXFMR HARBGR345 _1 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20923 | 120.5 | 539803 IRONWOOD7 345 3WXFMR IRONWOOD MPT 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20925 | 120.59 | 542951 HAW G5 1 22.0 543665 HAWTHN5 161 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20924 | 120.63 | 542955 LAC G1 1 22.0 542981 LACYGNE7 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20923 | 120.62 | 542956 LAC G2 1 24.0 542981 LACYGNE7 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20922 | 120.67 | 542957 IAT G1 1 24.0 542982 IATAN 7 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20923 | 120.74 | 542962 IAT G2 1 24.5 542982 IATAN 7 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21174 | 119.99 | 560022 CRAWFISH_DR 345 762216 G17-151TAP 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21142 | 120.98 | 560022 CRAWFISH_DR 345 762467 G18-015-TAP 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 116.89 | 560022 CRAWFISH_DR 345 763087 GEN-2018-073 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21254 | 121.28 | 560022 CRAWFISH_DR 345 763215 G18-092-TAP 345 2
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.99 | 560252 G10-14 345 560253 G10-14-1 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.69 | 560253 G10-14-1 115 560254 G10-14-SUB1 34.5 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.69 | 560253 G10-14-1 115 560255 G10-14-SUB2 34.5 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.52 | 560581 G06-44-2 34.5 523111 NOVUS1 3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.57 | 560582 G06-44-3 34.5 560577 G06-44 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.56 | 560583 G06-44-4 34.5 560577 G06-44 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.17 | 560757 ASGI13_02_1 69.0 560758 ASGI13_02_2 34.5 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.17 | 560757 ASGI13_02_1 69.0 562731 WHEATLAND 69.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.17 | 560763 ASGI13_03_1 115 560761 ASGI13_03_2 34.5 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.66 | 562015 FIREWHEEL1 34.5 523215 FREWHELCOL17 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.66 | 562016 FIREWHEEL2 34.5 523215 FREWHELCOL17 345 2
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.16 | 562323 AGI1202&1305 115 562324 AGI1202&1305 34.5 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.17 | 562727 LESBIA 115 562728 SANJONTAP 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.17 | 562728 SANJONTAP 115 562729 CAPROCKTAP1 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.17 | 562730 CAPROCKTAP2 69.0 562729 CAPROCKTAP1 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.17 | 562730 CAPROCKTAP2 69.0 562731 WHEATLAND 69.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.65 | 563171 G15082_2 34.5 563170 G15082_1 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.23 | P11:13.8:AEPW:COM1-1
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.24 | P11:13.8:AEPW:COM2-1
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.25 | P11:13.8:AEPW:COM3-1
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.26 | P11:18:AEPW:WELSH1-1
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.26 | P11:18:AEPW:WELSH3-1
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.25 | P11:24:AEPW:PIRKEY 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.13 | P11:24:AEPW:SWS3-1
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.2 | P11:24:AEPW:TURKCOAL
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20938 | 120.56 | P12:138:AEPW-OMPA:DUNCAN-4:OMDUNCN4
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20931 | 120.09 | 584560 GEN-2015-014 115 584561 G15-014XFMR1 34.5 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20927 | 120.29 | P12:138:AEPW:ARSHILL4:STLGENS4
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20933 | 120.51 | P12:138:AEPW:SANTAFE:DUNCAN-4
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.5 | 588480 A16-010_SUB 115 3WXFMR A16-010_SUB 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20938 | 120.55 | P12:138:AEPW:DUNCAN-4:L.E.S.-4
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 119.91 | 588761 G17-033XFMR1 34.5 588760 GEN-2017-033 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 119.91 | 588765 G17-033XFMR2 34.5 588760 GEN-2017-033 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.51 | 588861 G17-047XFMR1 34.5 588860 GEN-2017-047 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20911 | 120.25 | P12:138:AEPW:ELKCTY-4:CLINTJC4
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.49 | P12:138:AEPW:SHERID4:112GORE4
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21173 | 122.68 | P12:345:AEPW:L.E.S7:TERRYRD7
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21173 | 122.67 | P12:345:AEPW:L.E.S7:TERRYRD7
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21172 | 122.65 | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21247 | 122.27 | P12:345:AEPW-OKGE:L.E.S.-7:GRACMNT7
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21247 | 122.24 | P12:345:AEPW-OKGE:L.E.S.-7:GRACMNT7
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.2096 | 120.48 | P12:345:AEPW-OKGE:PITTSB-7:JOHNCO7
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.2092 | 120.25 | P12:345:AEPW-OKGE:PITTSB-7:SEMINOL7
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20941 | 120.52 | P12:345:AEPW-WFEC:VALIANT7:HUGO7
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21233 | 123.25 | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.55 | P22:345:AMMO::LABADIE:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.53 | P22:345:AMMO::LABADIE:2
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.55 | P22:345:AMMO::LABADIE:3
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.55 | P22:345:AMMO::LABADIE:4
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.54 | P22:345:AMMO::RUSHISLAND:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.51 | P22:345:AMMO::RUSHISLAND:2
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20927 | 120.24 | P13:138-13.8:AEPW:COMANC-4_#2
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20867 | 119.94 | P13:138-230:AEPW:ELKCTY-4
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20927 | 120.26 | P13:138-24:AEPW:PIRKEY 4
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20931 | 120.15 | P13:138-24:AEPW:S.W.S.-4
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20927 | 120.21 | P13:138-24:AEPW:TURK 4
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20943 | 120.54 | P13:138-345:AEPW:L.E.S.-4_#2
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20928 | 120.55 | P23:500:EES-EAI:KEO:B4941
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20928 | 120.53 | P23:500:EES-EAI:KEO:B4921
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20909 | 120.51 | 640183 GENTLMN3 345 640325 REDWILO3 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.48 | P11:26:EES-EAI:INDEP2:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20927 | 120.51 | P23:500:EES-EAI:INDEP2:B6126
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.51 | P23:500:EES-EAI:PD:INDEP2:LN:FK479
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20928 | 120.26 | P13:345-18:AEPW:WELSH 7_#1
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20928 | 120.26 | P13:345-18:AEPW:WELSH 7_#3
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.25 | P13:69-13.8:AEPW:COMANC-2
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20923 | 120.5 | 648513 GRPR1 3 345 652532 GR PRAIRIE 3 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.56 | P11:024:DPC:ALMA2:6
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20923 | 120.53 | 652537 WHITE 3 345 659286 DEERCREK-BE3 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20924 | 120.48 | 652568 GROTONSOUTH7 115 659275 GROTON_G-BE7 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20923 | 120.53 | 659286 DEERCREK-BE3 345 3WXFMR DEERCRK KU1A 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.49 | 672540 QE 6 138 672541 CORY 6 138 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.53 | 672601 BD 4 230 672306 BD 6G 18.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.53 | 672610 POPLAR 4 230 672310 POPLAR 1G 18.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.53 | 672610 POPLAR 4 230 672311 POPLAR 2G 18.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.53 | 672621 SHAND 4 230 672321 SHAND 1G 18.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.51 | 672649 CODETTE 4 230 672650 NIPAWIN 4 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.5 | 672685 SWIFTCU 4 230 672389 CHINOOK 1G 18.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.5 | 672688 PASQUA 4 230 673390 FUT-PQ1X 18.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.55 | 672696 BRADA 4 230 672699 NBEC 4 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.48 | 672699 NBEC 4 230 672392 NBEC GT 1G 18.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.49 | P13:345-230:CLEC:DOLET:5092
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.6 | P23:345:MDU::COYOTE::5707-5712-5715::::
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.76 | P23:345:MEC:CBEC 905
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.72 | P23:345:MEC:CBEC 908
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.64 | P23:345:MEC:RAUN 0180
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.71 | P23:345:MEC:RAUN 0210
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.64 | P23:345:MEC:LOUISA 954
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.64 | P23:345:MEC:LOUISA 964
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.5 | P21:115:XEL:AUTO-SINGLE:CHEMOLT7:LSPOWER7:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.49 | P21:115:XEL:AUTO-SINGLE:FARIBALTP7:FARIBALTGEN:Z
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.61 | P21:230:OTP:AUTO-SINGLE:SQBUTTE4:YNG24:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.59 | P23:345:OTP:CENTER 3:3215(1)
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.59 | P23:345:OTP:CENTER 3:3225(1)
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 119 | 760494 GEN-2017-146 230 760498 G17-146-TAP 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 119 | 760495 G17-146-XFM1 34.5 760494 GEN-2017-146 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.26 | 761356 G17-239-XFMR 34.5 761355 GEN-2017-239 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.26 | 761359 G17-239-XFMR 34.5 761355 GEN-2017-239 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 114.95 | 762132 GEN-2017-158 230 763252 G18-099-XFM1 34.5 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 114.95 | 762132 GEN-2017-158 230 763255 G18-099-XFM2 34.5 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 115.52 | 762133 G17-158XFM1 34.5 762132 GEN-2017-158 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 115.52 | 762136 G17-158XFM2 34.5 762132 GEN-2017-158 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 117.81 | 762216 G17-151TAP 345 762217 GEN-2017-151 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21174 | 121.31 | 762216 G17-151TAP 345 762467 G18-015-TAP 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 119.71 | 762218 G17-151XFM1 34.5 762217 GEN-2017-151 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 119.71 | 762221 G17-151XFM2 34.5 762217 GEN-2017-151 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 119.71 | 762224 G17-151XFM3 34.5 762217 GEN-2017-151 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 119.71 | 762227 G17-151XFM4 34.5 762217 GEN-2017-151 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.26 | 762438 GEN-2018-004 115 762442 G18-004-TAP 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 118.8 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 119.55 | 762461 G18-015-XFM1 34.5 762460 GEN-2018-015 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 119.55 | 762464 G18-015-XFM2 34.5 762460 GEN-2018-015 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21061 | 120.87 | 762467 G18-015-TAP 345 763215 G18-092-TAP 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 118.04 | 763087 GEN-2018-073 345 763088 G18-073-XFM1 34.5 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 119.21 | 763087 GEN-2018-073 345 763091 G18-073-XFM2 34.5 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 114.92 | 763120 GEN-2018-081 230 763121 G18-081-XFM1 34.5 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 117.23 | 763120 GEN-2018-081 230 764011 G19-074-XFM1 34.5 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 117.2 | 763186 GEN-2018-089 230 763187 G18-089-XFM1 34.5 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 118.06 | 763208 GEN-2018-092 345 763215 G18-092-TAP 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 119.2 | 763208 GEN-2018-092 345 763220 G18-092-XFM1 34.5 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 119.2 | 763208 GEN-2018-092 345 763223 G18-092-XFM2 34.5 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 116.67 | 763241 GEN-2018-097 230 763242 G18-097-XFM1 34.5 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 117.6 | 763241 GEN-2018-097 230 763296 G18-111-XFM1 34.5 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 116.95 | 763241 GEN-2018-097 230 763307 G18-112-XFM1 34.5 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 116.95 | 763241 GEN-2018-097 230 763310 G18-112-XFM2 34.5 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 116.67 | 763241 GEN-2018-097 230 763395 G18-124-XFM1 34.5 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 116.67 | 763241 GEN-2018-097 230 763398 G18-124-XFM2 34.5 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 116.31 | 763483 GEN-2019-003 230 763484 G19-003-XFM1 34.5 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 119.03 | 763483 GEN-2019-003 230 763605 G19-021-XFM1 34.5 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 119.65 | 763516 GEN-2019-011 345 763517 G19-011-XFM1 34.5 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.06 | 763879 GEN-2019-056 115 763880 G19-056XFM1 34.5 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.49 | P13:345,230:CLEC::DOLHILL::1
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.29 | P13:345,24:CLEC::G1DOLHILL::1
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20892 | 120.51 | P42:345:OKGE:SB_BVTY7305
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.2091 | 120.23 | P23:345:WERE:BUFF_345-534::
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.2091 | 120.23 | P23:345:WERE:BUFF_345-543::
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20922 | 120.66 | P23:345:WERE:JEC_345-15::
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.2092 | 120.62 | P23:345:WERE:JEC_345-16::
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20922 | 120.66 | P23:345:WERE:JEC_345-19::
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20922 | 120.66 | P23:345:WERE:JEC_345-20::
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.2092 | 120.29 | P23:345:WERE:WICH_345-50::
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20925 | 120.87 | P23:345:WERE:WOLF_345-50::
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.87 | P23:345:WERE:WOLF_345-60::
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20927 | 120.28 | P42:345:AEPW:WELSH CB 10620 NBTB+FAULT
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.27 | P41:345:AEPW:WELSH CB 10630 NBTB+FAULT
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.26 | P41:345:AEPW:WELSH CB 11670 NBTB+FAULT
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20929 | 120.53 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.26 | P41:345:AEPW:WELSH CB 12540 NBTB+FAULT
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20928 | 120.49 | P43:345:AEPW:CHAMBERS SPRING CB 12720 NBTB+FAULT
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20928 | 120.49 | P42:345:AEPW:CHAMBERS SPRING CB 13720 NBTB+FAULT
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20928 | 120.49 | P42:345:AEPW:CHAMBERS SPRING CB 13850 NBTB+FAULT
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21233 | 121.76 | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.2128 | 122.49 | P42:345:AEPW:LAWTON EASTSIDE CB 3413A NBTB+FAULT
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21314 | 122.73 | P42:345:AEPW:LAWTON EASTSIDE CB 3425A NBTB+FAULT
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21246 | 123.34 | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.2096 | 120.48 | P42:345:AEPW:PITTSBURG CB 3433A NBTB+FAULT
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20936 | 120.18 | P42:345:AEPW:PITTSBURG CB 3441A NBTB+FAULT
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.2092 | 120.25 | P42:345:AEPW:PITTSBURG CB 3445A NBTB+FAULT
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21173 | 122.67 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21173 | 122.67 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21173 | 122.65 | P42:345:AEPW:TERRYRD_CB_3421A_NBTB
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20924 | 120.65 | P23:345:KCPL:LACYGNE_R2-5::LACYGU2-LACYGNE-STILWELL
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20924 | 120.28 | P45:345:UMZW:# 1328 #: GI IN NE.
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20927 | 120.28 | P23:345:AEPW:WELSH CB 10620 NBTB
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.27 | P23:345:AEPW:WELSH CB 10630 NBTB
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.26 | P23:345:AEPW:WELSH CB 11670 NBTB
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20929 | 120.53 | P23:345:AEPW:WELSH CB 11990 NBTB
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.26 | P23:345:AEPW:WELSH CB 12540 NBTB
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20928 | 120.49 | P23:345:AEPW:CHAMBERS SPRING CB 12720 NBTB
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20928 | 120.49 | P23:345:AEPW:CHAMBERS SPRING CB 13720 NBTB
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20928 | 120.49 | P23:345:AEPW:CHAMBERS SPRING CB 13850 NBTB
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21233 | 122.19 | P23:345:AEPW:OKLAUNION CB 3401A NBTB
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.2128 | 122.49 | P23:345:AEPW:LAWTON EASTSIDE CB 3413A NBTB
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21314 | 122.73 | P23:345:AEPW:LAWTON EASTSIDE CB 3425A NBTB
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21246 | 123.34 | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.2096 | 120.48 | P23:345:AEPW:PITTSBURG CB 3433A NBTB
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20936 | 120.18 | P23:345:AEPW:PITTSBURG CB 3441A NBTB
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.2092 | 120.25 | P23:345:AEPW:PITTSBURG CB 3445A NBTB
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21173 | 122.67 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21173 | 122.67 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21173 | 122.65 | P23:345:AEPW:TERRYRD_CB_3421A_NBTB
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20956 | 120.48 | P12:138:AEPW:S.W.S.-4:L.E.S.-4
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20925 | 120.54 | P11:161:GMO:DOGWOOD_COMBINED_CYCLE_UNIT_OUTAGE
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.54 | P11:115:SUNC:GARDENCITY_S2:97:531459(2)
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20912 | 120.25 | P12:345:PWT:BUFF-THIS_345_1::
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20912 | 120.25 | P12:345:PWT:BUFF-THIS_345_2::
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20935 | 120.52 | P12:069:WFEC:ANADRKO_WATONGA
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20944 | 120.54 | P23:345:AEPW:VALLIANT CB 3413A NBTB
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.2095 | 120.56 | P23:345:AEPW:VALLIANT CB 3417A NBTB
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.2119 | 122.82 | P23:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21446 | 125.21 | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20944 | 120.54 | P42:345:AEPW:VALLIANT CB 3413A NBTB+FAULT
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.2095 | 120.56 | P42:345:AEPW:VALLIANT CB 3417A NBTB+FAULT
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.2119 | 122.82 | P42:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB+FAULT
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21446 | 125.21 | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20466 | 117.77 | P42:345:OKGE:SB_BVTY7315_PRE19S
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20888 | 120.52 | P23:345:SUNC:MO_BRK188
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21045 | 120.68 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20927 | 120.23 | P12:138-13.8:AEPW:COMANC-4_#1
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20867 | 119.93 | P12:230:AEPW:ELKCITY6:CHISHOLM6
Thermal | 05ALL | 1 | 26WP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21036 | 121.03 | P12:230:AEPW:SWEETWT6:CHISHOLM6
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997711 ABBXNL844501 230 1 |  | 552.5 | 0.3412 | 164.23 | 525531 TOLK 6 230 3WXFMR TOLK 6 2
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20928 | 120.49 | P12:345:AEPW-AEPW:CHAMPSP-CLARKSV
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20927 | 120.61 | P23:345:KCPL-WERE:237LACYGNE_R1-6::LACYGU1-LACYGNE-NEOSHO
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20925 | 120.5 | P11:161:GMO:DOGWOOD_COMBINED_CYCLE_UNIT_OUTAGE_1_1
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20933 | 118.96 | P11:115:SPS:MUSTANG1&3:153MW::::
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21179 | 122.27 | P12:230:SPS:K37::1_TOLK_LAMB:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20946 | 120.48 | P12:230:SPS:K43::1_PRNGLE_HARR_E:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20929 | 120.26 | P12:230:SPS:K44::1_EPLNT_HARRW:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.2094 | 120.61 | P12:115:SPS:T04::1_TRBLNC_CASTRO:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20925 | 120.48 | P12:115:SPS:T13::1_TAYLOR_WHOBBS:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20925 | 120.26 | P12:115:SPS:T14::1_MADDOX_TAYLOR:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.73 | P12:115:SPS:T21::1_GRSSLND_GRAHAM:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20925 | 120.29 | P12:115:SPS:T23::1_PCA_POTJCT:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20927 | 120.52 | P12:115:SPS:T26::1_CHAVES_RSWLCTY:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21046 | 120.8 | P12:115:SPS:T28A::1_LAMTON_PLANTX:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.2097 | 120.54 | P12:115:SPS:T29::1_LAMTON_HALECTR:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21093 | 121.92 | P12:115:SPS:T30::1_LAMB_HOCKLY:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21093 | 121.43 | P12:115:SPS:T31::1_HOCKLY_SUNDWN:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20921 | 120.59 | P12:115:SPS:T35::1_TERRY_YOAKUM:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 121.24 | P12:115:SPS:T45::1_NORRIS_OASIS:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21052 | 120.73 | P12:115:SPS:T59::1_CARGIL_CURRY:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21023 | 120.66 | P12:115:SPS:T67::1_HAPPY_KRESS:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20921 | 120.96 | P12:115:SPS:T71::1_CRLSLE_YUMA:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20934 | 120.57 | P12:115:SPS:T81::1_COX_FLOYD:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20925 | 120.57 | P12:115:SPS:T83::1_SP-FKFD_ALLEN:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20921 | 120.91 | P12:115:SPS:T89::1_DC_N_HIGG:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.54 | P12:115:SPS:T91::1_HIGG_RUSSELL:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20948 | 120.51 | P12:115:SPS:V04::1_EPLANT_RNDALL:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20939 | 120.5 | P12:115:SPS:V07::1_COX_HALECTR:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21038 | 120.71 | P12:115:SPS:V09::1_HALECTR_PLANTX:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20925 | 120.56 | P12:115:SPS:V12::1_PLANTX_BAILEY:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.5 | P12:115:SPS:V15::1_TUCO_INDANA:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20917 | 120.51 | P12:115:SPS:V16::1_TERRY_DC_N:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.2089 | 120.62 | P12:115:SPS:V24::1_WOLFTH_TERRY:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20943 | 120.6 | P12:115:SPS:V26::1_RSWLL_EDDY_N:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.58 | P12:115:SPS:V33::1_LUBBS_LYNN:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.2103 | 121.13 | P12:115:SPS:V37::1_CASTRO_PLANTX:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.63 | P12:115:SPS:V46::1_ALLEN_WHEELCK:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20927 | 120.95 | P12:115:SPS:V49::1_YOAKUM_SHLCO2:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20968 | 121.15 | P12:115:SPS:V55::1_SUNDWN_TERRY:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20936 | 120.98 | P12:115:SPS:V56::1_COCHRAN_SUNDWN:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20939 | 120.5 | P12:115:SPS:V78::2_CURRY_RSVLT:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20924 | 120.67 | P12:115:SPS:V81::1_LE-WAIT_LE-LVN:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.54 | P12:115:SPS:V95::1_DC_N_SHLCO2:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.5 | P12:115:SPS:W11::1_DC_S_SMINLE:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20925 | 120.54 | P12:115:SPS:W14::1_SMINLE_GAINES:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20925 | 120.5 | P12:115:SPS:W26::1_CUNGHM_OILCNTR:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 121.13 | P12:115:SPS:W32::1_PRMTR_FE-CLSIN:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.5 | P12:115:SPS:W34::1_JNSDRW_MAPCO:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20923 | 120.73 | P12:115:SPS:W35::1_GAINES_JNSDRW:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.2092 | 120.52 | P12:115:SPS:W36::1_TAYLOR_JNSDRW:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21116 | 120.93 | P12:115:SPS:W40::1_WCANYON_TRBLNC:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20936 | 120.29 | P12:115:SPS:W46::1_RHILLS_NWEST:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20953 | 120.55 | P12:115:SPS:W52::1_NEWHART_KRESS:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 121.01 | P12:115:SPS:W58::1_NORTON_LOPEZ:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.69 | P12:115:SPS:W59::1_LOPEZ_CMPBLL:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20927 | 120.96 | P12:115:SPS:W62::1_PLSTHL_CURRY:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.84 | P12:115:SPS:W64::1_PLSTHL_FE-CLV:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20927 | 120.81 | P12:115:SPS:W65::1_PLSTHL_CURRY:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.68 | P12:115:SPS:W66::1_PORTA_GREYHUND:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21116 | 120.53 | P12:115:SPS:W77::1_RNDAL_WCANYON:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.51 | P12:115:SPS:W99::1_CAPITAN_CHAVES:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20925 | 120.51 | P12:115:SPS:U03::1_CARDNL_NEF:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20922 | 121.04 | P12:115:SPS:U14::1_DC_STH_INKBSN:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20924 | 120.92 | P12:115:SPS:V15::1_INKBSN_LE-WAT:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20948 | 120.55 | P12:115:SPS:U16::1_BSHLND_OUTPST:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20948 | 120.54 | P12:115:SPS:U17::1_COLTR_OUTPST:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20933 | 120.76 | P12:115:SPS:U19::1_DEAN_PLAINS:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20948 | 120.49 | P12:115:SPS:U23::1_COLTR_HILSDE:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.201 | 127.42 | P42:345:SPS:YOAKUM:J18####:SLG1:EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.201 | 127.42 | P43:345:SPS:YOAKUM:TF#####:SLG:EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.201 | 127.42 | P42:345:SPS:YOAKUM:J17####:SLG:EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20181 | 122.69 | P43:345:SPS:TUCO:SLG::EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.201 | 127.42 | P42:345:SPS:YOAKUM:J18####:SLG2:EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20928 | 120.49 | P12:345:AEPW-AEPW:CHAMPSP-CLARKSV:::EHV::
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20925 | 120.52 | P11:18:HAST:::EGYCTR2G WEC2_LOSS OF WEC 2 GEN_:HV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20925 | 120.52 | P13:18-115:HAST:::EGYCNTR7 XFMR G2WEC 2 GSU_:HV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20925 | 120.5 | P11:161:GMO:DOGWOOD-COMBINED-CYCLE-UNIT-OUTA:::HV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20927 | 120.61 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20924 | 120.65 | P23:345:KCPL:LACYGNE-R2-5:::EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20922 | 120.66 | P11:230:WERE:JECU1-GEN:::HV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20922 | 120.66 | P11:345:WERE:JECU2-GEN:::EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20922 | 120.66 | P11:345:WERE:JECU3-GEN:::EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.88 | P11:345:WERE:WOLFU1-GEN:::EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20912 | 120.25 | P12:345:PWT:BUFF-THIS-345-1:::EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20912 | 120.25 | P12:345:PWT:BUFF-THIS-345-2:::EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.2091 | 120.23 | P23:345:WERE:BUFF-345-534:::EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.2091 | 120.23 | P23:345:WERE:BUFF-345-543:::EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20922 | 120.66 | P23:345:WERE:JEC-345-15:::EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.2092 | 120.62 | P23:345:WERE:JEC-345-16:::EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20922 | 120.66 | P23:345:WERE:JEC-345-19:::EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20922 | 120.66 | P23:345:WERE:JEC-345-20:::EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.2092 | 120.29 | P23:345:WERE:WICH-345-50:::EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20925 | 120.87 | P23:345:WERE:WOLF-345-50:::EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.87 | P23:345:WERE:WOLF-345-60:::EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.81 | P11:022:NPPD:COOPER1G:1:983:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.2092 | 120.83 | P11:023:NPPD:GENTLM1G:1:757:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20924 | 120.68 | P11:024:NPPD:GENTLM2G:2:757:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20921 | 120.68 | P13:345:OPPD:NEBCTY1G:::EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.2092 | 120.69 | P13:345:OPPD:NEBCTY2G:::EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.69 | P22:345:OPPD:S3458 NEBCTY1G:LT::EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20921 | 120.68 | P22:345:OPPD:S3458 NEBCTY1G:::EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.72 | P22:345:OPPD:S3458 NEBCTY2G:LT::EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.2092 | 120.69 | P22:345:OPPD:S3458 NEBCTY2G:::EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.69 | P23:345:OPPD:S3458 NEBCTY1G:LT::EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20921 | 120.68 | P23:345:OPPD:S3458 NEBCTY1G:::EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.72 | P23:345:OPPD:S3458 NEBCTY2G:LT::EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.2092 | 120.69 | P23:345:OPPD:S3458 NEBCTY2G:::EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.29 | P12:115:SUNC:PLYMELL-PIERCEVILLE:::HV::
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20923 | 120.53 | P11:018:UMZB:# 5 #:: DCS IN SD. DEERCREEK_MV::
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20924 | 120.5 | P11:022:UMZB:# 15 #:: LO IN ND. LELAND OLDS 1_MV::
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20925 | 120.5 | P11:020:UMZB:# 16 #:: LO IN ND. LELAND OLDS 2_MV::
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20923 | 120.61 | P11:023:UMZB:# 31 #:: AVS IN ND. ANTELOPE VALLEY 1_MV::
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20923 | 120.61 | P11:023:UMZB:# 32 #:: AVS IN ND. ANTELOPE VALLEY 2_MV::
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20919 | 120.82 | P11:024:UMZB:# 33 #:: LRS IN WY. LARAMIE RIVER STATION 1_MV::
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.49 | P13:230:UMZW:# 5135 #:: OA IN SD. FAULT ON TRANSFORMER (2).:HV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.49 | P13:230:UMZW:# 5136 #:: OA IN SD. FAULT ON TRANSFORMER (3).:HV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.5 | P13:230:UMZW:# 5137 #:: OA IN SD. FAULT ON TRANSFORMER (4).:HV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20924 | 120.28 | P23:345:UMZW:# 2423 #:: GI IN NE. GI 1596 BKR FAULT:EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20924 | 120.28 | P23:345:UMZW:# 2426 #:: GI IN NE. GI 1592 BKR FAULT:EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20924 | 120.28 | P23:345:UMZW:# 2432 #:: GI IN NE. GI 1092 BKR FAULT:EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20924 | 120.28 | P23:345:UMZW:# 2440 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1092 STUCK BKR:EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20924 | 120.28 | P23:345:UMZW:# 2444 #:: GI IN NE. GI-SWEET BRANCH FAULT & GI 1596 STUCK BKR:EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20924 | 120.28 | P23:345:UMZW:# 2446 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1196 STUCK BKR:EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20924 | 120.28 | P42:345:UMZW:# 2413 #:: FT2 IN SD. FT2-LO2 BRANCH FAULT & FT2 2992 STUCK BKR:EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20924 | 120.28 | P42:345:UMZW:# 2415 #:: FT2 IN SD. FT2-GI BRANCH FAULT & FT2 3392 STUCK BKR:EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.2093 | 120.2 | P11:138:WFEC:HUGO1:465MW :::
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20924 | 120.49 | P11:138:WFEC:MORLND2:132MW:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20924 | 120.5 | P11:138:WFEC:MORLND3:149MW :::
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20934 | 120.52 | P12:138:WFEC:ANADRKO_CLVLND::::
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.2092 | 120.25 | P12:345:OKGE-AEPW:BKRBKR20::::
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20961 | 120.7 | P12:345:OKGE:BKRBKR21::::
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20981 | 120.7 | P12:345:OKGE:BKRBKR24::::
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21172 | 122.65 | P12:345:OKGE-AEPW:BKRBKR25::::
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20895 | 120.12 | P12:345:OKGE:BKRBKR336::::
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20894 | 120.11 | P12:345:OKGE:BKRBKR336_2::::
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.2096 | 120.48 | P12:345:OKGE-AEPW:BKRBKR343::::
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21247 | 122.27 | P12:345:OKGE-AEPW:BKRBKR366::::
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21247 | 122.24 | P12:345:OKGE-AEPW:BKRBKR366::::
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21132 | 121.66 | P12:345:OKGE:BKRBKR367::::
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20962 | 120.59 | P12:345:OKGE-WFEC:BKRBKR374::::
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20962 | 120.56 | P12:345:OKGE-WFEC:BKRBKR374::::
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20899 | 120.16 | P12:345:OKGE:BKRBKR4193::::
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20899 | 120.16 | P12:345:OKGE:BKRBKR4194::::
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20889 | 120.16 | P12:345:OKGE-SPS:BKRBKR4201::::
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20889 | 120.16 | P12:345:OKGE-SPS:BKRBKR4202::::
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20893 | 119.95 | P12:345:OKGE:BKRBKR443NEW::::
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20893 | 119.95 | P12:345:OKGE:BKRBKR443NEW2::::
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20909 | 120.27 | P12:345:OKGE-ITC:BKRBKR502::::
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20909 | 120.27 | P12:345:OKGE-ITC:BKRBKR503::::
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20921 | 120.61 | P12:345:OKGE:BKRBKR604::::
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20919 | 120.72 | P12:345:OKGE:BKRBKR604_2::::
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21627 | 123.72 | P42:345:OKGE:SB_BVTY7387::::
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20966 | 120.63 | P42:345:OKGE:SB_SPCK7383::::
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20923 | 120.53 | P11:115:SUNC:GARDENCITY_S2:103:531459(2):HV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20923 | 120.54 | P11:115:SUNC:FORTDDODGE_4:157:539670(4):HV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20888 | 120.5 | P12:345:SUNC-NPPD:MINGO-REDWILLOW::531451-640325(1):EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.61 | P13:115:SUNC:HOLCOMB_GSU:::HV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20923 | 120.53 | P13:115:SUNC:S2_GSU:::HV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20923 | 120.54 | P13:115:SUNC:FORTDODGE_GSU:::HV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.48 | 300002 1THLG2 22.0 301505 5THOMHLGSU2 161 2
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.62 | 300003 1THLG3 24.0 301503 7THOMHLGSU3 345 3
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.48 | 300006 1NM G1 22.0 301536 5NEWMADGSU1 161 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.48 | 300007 1NM G2 22.0 301537 7NEWMADGSU2 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.48 | 300046 7NEWMAD 345 301537 7NEWMADGSU2 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.62 | 300049 7THOMHL 345 301503 7THOMHLGSU3 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.48 | 300103 5NEWMAD 161 301536 5NEWMADGSU1 161 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.48 | 300132 5THMHLB2 161 301505 5THOMHLGSU2 161 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20925 | 120.29 | 300739 7BLACKBERRY 345 532797 WOLFCRK7 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.56 | P11:20:AMMO:1LAB�� G1:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.54 | P11:20:AMMO:1LAB�� G2:2
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.75 | P11:345:AMMO::CALLAWAY:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.56 | P11:345:AMMO::LABADIE:3
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.56 | P11:345:AMMO::LABADIE:4
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.55 | P11:345:AMMO::RUSHISLAND:U1
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.54 | P11:345:AMMO::RUSHISLAND:U2
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.53 | P11:138:AMMO::SIOUX:2
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.49 | P13:345-230:CLEC::DOLHILL7:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.29 | P11:345-24:CLEC::DOLHILL7:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.29 | P11:24:CLEC::G1DOLHIL:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.53 | P12:765:AEP:AEP ROCKP-AEP JEFF 765
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.48 | P11:HV:EES::1ISES U1:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.25 | P11:HV:EES::PIRKEY 1:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.26 | P11:EHV:EES::WELSH3-1:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.2 | P11:HV:EES::TURKCOAL:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.48 | P12:HV:EES::5ISES%:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.74 | P12:EHV:EES::7CALAWY 1:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20928 | 120.49 | P12:EHV:EES::CHAMSPR7!:CLARKSV7!:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20927 | 120.21 | P12:HV:EES::TURK 4%:1(1)
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20928 | 120.26 | P12:EHV:EES::WELSH 7:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20928 | 120.26 | P12:EHV:EES::WELSH 7:1(1)
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20927 | 120.26 | P12:HV:EES::PIRKEY 4:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.53 | 344011 7HUGHES 345 344012 7HPW-N 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.55 | 344884 7LABADIE1 345 344894 1LAB G1 20.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.53 | 344885 7LABADIE2 345 344895 1LAB G2 20.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.55 | 344886 7LABADIE3 345 344896 1LAB G3 20.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.55 | 344887 7LABADIE4 345 344897 1LAB G4 20.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.54 | 345667 7RUSH 1 345 345670 1RUSH G1 18.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.53 | 345668 7RUSH 2 345 345671 1RUSH G2 18.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.52 | 345755 4SIOUX 1 138 345756 1SIOUX 1 18.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.52 | 345764 4SIOUX 2 138 345765 1SIOUX 2 18.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.6 | P12:345:MDU::CENTER:COYOTE:1::::
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.6 | P13:345:MDU:COYOTE GSU LOSS:COYOTE::1::::
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.82 | P11:345:MEC-NPPD:COOPER 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.72 | P11:24:XEL:AUTO-SINGLE:SHERC31G:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.72 | P11:24:XEL:AUTO-SINGLE:SHERC32G:2
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.81 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.64 | P11:20:XEL:AUTO-SINGLE:PRIS31G:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.63 | P11:20:XEL:AUTO-SINGLE:PRIS32G:2
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.68 | P11:22:XEL:AUTO-SINGLE:MNTCE31G:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.64 | P11:20:XEL:AUTO-SINGLE:KING31G:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.48 | P11:18:XEL:AUTO-SINGLE:BLKD76G:6
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.69 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.69 | P11:22:GRE:AUTO-SINGLE:GRE-COAL42G:2
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.61 | P11:24:OTP:AUTO-SINGLE:BIGSTN1G:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.63 | P11:20:OTP:AUTO-SINGLE:CENTER2G:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.52 | P11:22:OTP:AUTO-SINGLE:CENTER1G:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.61 | P11:24:OTP:AUTO-SINGLE:COYOTE1G:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.51 | P11:24:DPC:AUTO-SINGLE:GENOA53G:3
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.5 | P12:115:XEL:AUTO-SINGLE:CHEMOLT7:LSPOWER7:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.49 | P12:115:XEL:AUTO-SINGLE:FARIBALTP7:FARIBALTGEN:Z
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.61 | P12:230:OTP:AUTO-SINGLE:SQBUTTE4:YNG24:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.69 | P13:24-345:XEL:AUTO-SINGLE:SHERC31G:SHERCO3:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.69 | P13:24-345:XEL:AUTO-SINGLE:SHERC32G:SHERCO3:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.78 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.64 | P13:20-345:XEL:AUTO-SINGLE:PRIS31G:PRISLD3:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.64 | P13:20-345:XEL:AUTO-SINGLE:PRIS32G:PRISLD3:2
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.68 | P13:22-345:XEL:AUTO-SINGLE:MNTCE31G:MNTCELO3:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.62 | P13:20-345:XEL:AUTO-SINGLE:KING31G:ASKING3:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.48 | P13:18-115:XEL:AUTO-SINGLE:BLKD76G:BLKDG27:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.67 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL41G:GRE-COALCR4:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.67 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL42G:GRE-COALCR4:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.6 | P13:230-24:OTP:AUTO-SINGLE:BIGSTON4:BIGSTN1G:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.61 | P13:20-230:OTP:AUTO-SINGLE:CENTER2G:YNG24:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.51 | P13:22-230:OTP:AUTO-SINGLE:CENTER1G:CENTER4:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.6 | P13:24-345:OTP:AUTO-SINGLE:COYOTE1G:COYOTE3:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.5 | P13:24-161:DPC:AUTO-SINGLE:GENOA53G:GENOA5:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.55 | P13:24-161:DPC:AUTO-SINGLE:JPM:ALMA5:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.6 | P11:115:XEL:RIV COMBINE CYCLE
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.51 | P12:115:XEL:BDS #2 5
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.49 | P11:115:XEL:HBR #6 7 8
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.63 | P23:345:XEL:8H14 PRI
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.64 | P23:345:XEL:8H17 PRI AS
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.78 | P23:345:XEL:8N28 SHC
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.7 | P23:345:XEL:8N22 SHC
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.69 | P23:345:XEL:8N17 SHC
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.68 | P23:345:XEL:8N8 MNN
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.63 | P23:345:XEL:8P1 KING
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.63 | P23:345:XEL:8P2 KING
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.5 | P11:22:ALTW:AUTO-SINGLE:LANS54G:4
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.64 | P11:22:ALTW:AUTO-SINGLE:ARNOLD1G:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.67 | P11:24:ALTW:AUTO-SINGLE:OTTUMW1G:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.49 | P13:22-161:ALTW:AUTO-SINGLE:LANS54G:LANSINGL15:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.63 | P13:22-161:ALTW:AUTO-SINGLE:ARNOLD1G:ARNOLD5:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.66 | P13:24-161:ALTW:AUTO-SINGLE:OTTUMW1G:OTTUMWA5:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.74 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.8 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.65 | P11:22:MEC:AUTO-SINGLE:NEAL3G:3
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.73 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.66 | P11:24:MEC:AUTO-SINGLE:LOUIS31G:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.72 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.76 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.64 | P13:345-22:MEC:AUTO-SINGLE:RAUN3:NEAL3G:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.71 | P13:345-24:MEC:AUTO-SINGLE:RAUN3:NEAL4G:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.64 | P13:345-24:MEC:AUTO-SINGLE:LOUISA3:LOUIS31G:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20922 | 120.66 | P11:230:WERE:JECU1_GEN::
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20922 | 120.66 | P11:345:WERE:JECU2_GEN::
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20922 | 120.66 | P11:345:WERE:JECU3_GEN::
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.88 | P11:345:WERE:WOLFU1_GEN::
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20933 | 120.48 | 511453 DUNCAN-4 138 511552 DUNCHERTP4 138 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20933 | 120.48 | 511455 D.E.S.-4 138 511552 DUNCHERTP4 138 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.48 | 511456 O.K.U.-7 345 511565 OKLAUN HVDC7 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 119.42 | 511456 O.K.U.-7 345 588760 GEN-2017-033 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21233 | 122.19 | 511456 O.K.U.-7 345 763215 G18-092-TAP 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21246 | 122.76 | 511468 L.E.S.-7 345 762467 G18-015-TAP 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21143 | 122.19 | 511468 L.E.S.-7 345 763215 G18-092-TAP 345 2
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20938 | 120.56 | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21045 | 120.68 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20262 | 117.21 | 511553 CHISHOLM7 345 523961 POTTER_CO 7 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20262 | 117.21 | 511553 CHISHOLM7 345 523961 POTTER_CO 7 345 2
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20633 | 119.86 | 511553 CHISHOLM7 345 755000 WWDBORDT 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20924 | 120.5 | 511557 CHISHOLM6 230 3WXFMR CHISHOLM6 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20939 | 120.51 | 514801 MINCO 7 345 555234 NSUB345 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20852 | 120.15 | 515375 WWRDEHV7 345 755000 WWDBORDT 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21627 | 123.76 | 515458 BORDER 7 345 560022 CRAWFISH_DR 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21627 | 123.7 | 515458 BORDER 7 345 755000 WWDBORDT 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20924 | 120.51 | 515618 BALKOW 7 345 3WXFMR BALKOW 7 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20924 | 120.5 | 515618 BALKOW 7 345 3WXFMR BALKOW 7 1_Dup1
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20919 | 120.73 | 515634 PALDR1W7 345 3WXFMR PALO2 _1 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.63 | 515677 BADGER 7 345 563170 G15082_1 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.49 | 522800 MU-TULIA 3 115 525179 TULIA_TP 3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.63 | 522892 MU-BROWNFLD2 69.0 526761 BROWNFLD_TP2 69.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20923 | 120.52 | 523093 HITCHLAND 3 115 523174 GOODWELLWND3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21053 | 120.53 | 523095 HITCHLAND 6 230 523309 MOORE_CNTY 6 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.88 | 523097 HITCHLAND 7 345 523112 NOVUS1 7 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.93 | 523097 HITCHLAND 7 345 523215 FREWHELCOL17 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20717 | 119.43 | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.99 | 523097 HITCHLAND 7 345 560252 G10-14 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.5 | 523099 TC-DRYTRLS 3 115 588480 A16-010_SUB 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.74 | 523112 NOVUS1 7 345 3WXFMR NOVUS XF2 2
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.52 | 523112 NOVUS1 7 345 3WXFMR XIANA2011198 _1 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20923 | 120.5 | 523118 BUFF_DUNES 7 345 523853 FINNEY 7 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.51 | 523120 COLE 3 115 588860 GEN-2017-047 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20935 | 120.48 | 523221 XIT_INTG 6 230 3WXFMR SIEM_T126401 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20946 | 120.48 | 523267 PRINGLE 6 230 3WXFMR ENRCO13617-1 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20946 | 120.48 | 523267 PRINGLE 6 230 523979 HARRNG_EST 6 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20988 | 120.61 | 523309 MOORE_CNTY 6 230 523323 MCDWL_CREEK6 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.2096 | 120.53 | 523323 MCDWL_CREEK6 230 523959 POTTER_CO 6 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20896 | 120.85 | 523959 POTTER_CO 6 230 523979 HARRNG_EST 6 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21737 | 121.98 | 523959 POTTER_CO 6 230 524267 BUSHLAND 6 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.2171 | 122.4 | 523959 POTTER_CO 6 230 525461 NEWHART 6 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21287 | 129.34 | 523961 POTTER_CO 7 345 3WXFMR WAUK 90343-A 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20912 | 120.79 | 523961 POTTER_CO 7 345 524296 SPNSPUR_WND7 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20928 | 120.27 | 523977 HARRNG_WST 6 230 523971 HARRNGTON1 1 24.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20905 | 120.79 | 523977 HARRNG_WST 6 230 524010 ROLLHILLS 6 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20925 | 120.22 | 523978 HARRNG_MID 6 230 523979 HARRNG_EST 6 230 @1
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20925 | 120.29 | 524010 ROLLHILLS 6 230 3WXFMR WAUK WT01104 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20948 | 120.55 | 524267 BUSHLAND 6 230 3WXFMR WH 7001795 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.22387 | 122.23 | 524267 BUSHLAND 6 230 524623 DEAFSMITH 6 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20912 | 120.89 | 524296 SPNSPUR_WND7 345 524299 SPNSPUR_COL7 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20912 | 120.89 | 524299 SPNSPUR_COL7 345 3WXFMR SPNSPUR_COL7 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21317 | 120.9 | 524415 AMA_SOUTH 6 230 525213 SWISHER 6 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 121.01 | 524502 NORTON 3 115 524509 FE-TUCMCARI3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21116 | 120.82 | 524575 DS-#25+ 3 115 524597 PANDAHFD 3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21116 | 120.9 | 524575 DS-#25+ 3 115 524630 TIERABLANCA3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.5 | 524604 HEREFRD_SB 2 69.0 524608 HERFRD_STH 2 69.0 *1
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.22236 | 125.98 | 524623 DEAFSMITH 6 230 760498 G17-146-TAP 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.78 | 524721 DS-#15&#19+2 69.0 524745 CASTRO_CNTY2 69.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.84 | 524764 NORRIS_TP 3 115 524801 NORRIS 3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20932 | 120.49 | 524770 PLSNT_HILL 6 230 3WXFMR EFAE1100068A 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.84 | 524776 N_CLOVIS_TP3 115 524777 N_CLOVIS 3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.78 | 524790 CANNON_TP 3 115 524794 CANNONAFB 3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21343 | 127.03 | 524875 OASIS 6 230 524885 SN_JUAN_TAP6 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20999 | 121.66 | 524875 OASIS 6 230 524909 ROOSEVELT 6 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21325 | 127.79 | 524885 SN_JUAN_TAP6 230 527483 CHAVES_CNTY6 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20942 | 120.65 | 524909 ROOSEVELT 6 230 3WXFMR ABB LMM60042 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21617 | 125.82 | 524909 ROOSEVELT 6 230 525531 TOLK 6 230 2
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 121.25 | 524923 PORTALES 2 69.0 524929 RO-PORT_MTR2 69.0 @1
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.88 | 524923 PORTALES 2 69.0 524941 PORTALES#1 2 69.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.84 | 525023 BC-BAIL_MTR2 69.0 525027 BAILEYCO 2 69.0 @1
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.2103 | 120.8 | 525056 BC-EARTH 3 115 525480 PLANT_X 3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.57 | 525192 KRESS_INT 3 115 3WXFMR ENRCO 136155 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20937 | 120.29 | 525213 SWISHER 6 230 3WXFMR SIEM_T127101 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21223 | 121.59 | 525213 SWISHER 6 230 525461 NEWHART 6 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.54 | 525272 KISER 3 115 3WXFMR VON 13819/1 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.81 | 525326 COX 3 115 3WXFMR ELCO 13474-3 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.81 | 525414 LAMTON 3 115 3WXFMR ASEA MLL9204 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.22535 | 123.54 | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21198 | 122.16 | 525481 PLANT_X 6 230 3WXFMR WH ALM20171 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21856 | 127.05 | 525481 PLANT_X 6 230 526435 SUNDOWN 6 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.22236 | 124.03 | 525481 PLANT_X 6 230 760498 G17-146-TAP 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21271 | 120.86 | 525481 PLANT_X 6 230 762174 G17-218TAP 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21313 | 120.92 | 525481 PLANT_X 6 230 762174 G17-218TAP 230 2
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.22055 | 128.41 | 525531 TOLK 6 230 525586 NEEDMORE 6 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21179 | 122.27 | 525531 TOLK 6 230 525637 LAMB_CNTY 6 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.23816 | 127.4 | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21436 | 121.08 | 525531 TOLK 6 230 762174 G17-218TAP 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21471 | 121.13 | 525531 TOLK 6 230 762174 G17-218TAP 230 2
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.3412 | 162.04 | 525549 TOLK 7 345 3WXFMR ABBXNL844501 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.22055 | 128.41 | 525586 NEEDMORE 6 230 526935 YOAKUM 6 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21179 | 122.27 | 525637 LAMB_CNTY 6 230 3WXFMR WH ALM20172 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.54 | 525828 TUCO_INT 3 115 3WXFMR DS F78800913 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21357 | 120.96 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21476 | 121.11 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _9 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20181 | 122.69 | 525832 TUCO_INT 7 345 526936 YOAKUM_345 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21093 | 121.33 | 526020 HOCKLEY 3 115 526036 LC-OPDYKE 3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21093 | 121.18 | 526036 LC-OPDYKE 3 115 526434 SUNDOWN 3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.57 | 526160 CARLISLE 3 115 3WXFMR WH RLP38371 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.79 | 526162 LP-DOUD_TP 3 115 526176 LP-DOUD 3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.82 | 526268 LUBBCK_STH 3 115 3WXFMR NA 70454A 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20936 | 120.81 | 526361 COCHRAN 3 115 526424 PACIFIC 3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20936 | 120.9 | 526424 PACIFIC 3 115 526434 SUNDOWN 3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20968 | 120.94 | 526434 SUNDOWN 3 115 526445 AMOCO_TP 3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20921 | 120.51 | 526435 SUNDOWN 6 230 3WXFMR UPDATE LATER _12 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20944 | 124.22 | 526435 SUNDOWN 6 230 526460 AMOCO_SS 6 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20968 | 120.8 | 526445 AMOCO_TP 3 115 526484 LG-LEVELAND3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20944 | 121.88 | 526460 AMOCO_SS 6 230 526935 YOAKUM 6 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20968 | 120.79 | 526484 LG-LEVELAND3 115 526491 LG-CLAUENE 3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20923 | 120.51 | 526525 WOLFFORTH 6 230 3WXFMR UPDATE LATER _13 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20916 | 122.38 | 526935 YOAKUM 6 230 527028 INK_BASIN 6 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20181 | 129.67 | 526936 YOAKUM_345 345 527896 HOBBS_INT 7 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20905 | 121.79 | 527028 INK_BASIN 6 230 527894 HOBBS_INT 6 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20921 | 120.9 | 527130 DENVER_N 3 115 527286 HIGGEAST 3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20928 | 119.59 | 527149 MUSTANG 6 230 527151 GS-MUSTANG 6 230 @1
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.62 | 527202 SEAGRAVES 3 115 3WXFMR ABB MLL92408 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.59 | 527212 DIAMONDBACK3 115 3WXFMR HOW 36773714 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20921 | 120.88 | 527286 HIGGEAST 3 115 527363 HIGG 3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20923 | 120.62 | 527325 OXY_WSEM_TP3 115 527362 JOHNSON_DRW3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.59 | 527340 DOSS 3 115 3WXFMR ELCO 13566/1 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.58 | 527345 LEGACY 2 69.0 527350 XTO_ROBRTSN2 69.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.58 | 527346 LEGACY 3 115 3WXFMR VROL 13735-1 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.56 | 527350 XTO_ROBRTSN2 69.0 527355 BOARDMAN 2 69.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.51 | 527355 BOARDMAN 2 69.0 527365 FLANNAGAN 2 69.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.5 | 527360 MAPCO 3 115 527362 JOHNSON_DRW3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.58 | 527362 JOHNSON_DRW3 115 528775 LE-ERF 3 115 @1
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.48 | 527370 TENNECO_TAP2 69.0 527371 TENNECO 2 69.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20928 | 120.29 | 527470 CHVS_SLRCOL3 115 527482 CHAVES_CNTY3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21101 | 121.58 | 527483 CHAVES_CNTY6 230 527799 EDDY_NORTH 6 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.49 | 527508 PRICE 3 115 527509 PRICE_TAP 3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.5 | 527514 CV-PINE 2 69.0 527563 ROSWLL_INT 2 69.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.52 | 527563 ROSWLL_INT 2 69.0 527575 SW_4702 2 69.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20943 | 120.61 | 527564 ROSWLL_INT 3 115 527597 TWEEDY 3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.52 | 527575 SW_4702 2 69.0 527589 CV-ORCHARD 2 69.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.48 | 527589 CV-ORCHARD 2 69.0 527619 DEXTER_TP 2 69.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20919 | 120.69 | 527653 MILO_WIND 1 34.5 527655 RSVLT_CC_E 7 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20909 | 120.67 | 527654 RSVLT_CC_W 7 345 527655 RSVLT_CC_E 7 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20909 | 120.92 | 527654 RSVLT_CC_W 7 345 527666 RSVLT_COL1 7 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20902 | 120.92 | 527655 RSVLT_CC_E 7 345 527656 CROSSROADS 7 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20909 | 120.92 | 527666 RSVLT_COL1 7 345 3WXFMR RSVLT_COL1 7 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.63 | 527790 EDDY_SVC 1 8.50 527799 EDDY_NORTH 6 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20925 | 120.22 | 527864 CUNNINHAM 3 115 528348 BUCKEYE_TP 3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20925 | 120.52 | 527864 CUNNINHAM 3 115 528568 MONUMNT_TP 3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20911 | 120.69 | 527865 CUNNIGHM_N 6 230 527867 CUNNIGHM_S 6 230 *1
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20921 | 120.51 | 527865 CUNNIGHM_N 6 230 527963 POTASH_JCT 6 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20921 | 120.51 | 527867 CUNNIGHM_S 6 230 527894 HOBBS_INT 6 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20925 | 120.3 | 527894 HOBBS_INT 6 230 3WXFMR ME C0482951 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20923 | 120.57 | 527894 HOBBS_INT 6 230 527903 HOBBS_PLT3 1 18.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.23 | 527896 HOBBS_INT 7 345 527965 KIOWA 7 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.2 | 527896 HOBBS_INT 7 345 528027 RDRUNNER 7 345 UC
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.2 | 527896 HOBBS_INT 7 345 528027 RDRUNNER 7 345 XA
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20925 | 120.29 | 527965 KIOWA 7 345 528027 RDRUNNER 7 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.55 | 528024 RR_SVC_HV 3 115 528021 RDRUNNR_SVC1 15.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.64 | 528024 RR_SVC_HV 3 115 528025 RDRUNNER 3 115 Z1
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.25 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.5 | 528182 NORTH_LOVNG3 115 528193 BLACKRIVER 3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.63 | 528222 CHINA_DRAW 3 115 528225 CD_SVC_HV 3 115 Z1
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20924 | 120.22 | 528333 LE-WEST_SUB3 115 528334 LE-NRTH_INT3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20925 | 120.29 | 528341 LE-SANANDRS3 115 528627 LE-TXACO_TP3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20925 | 120.25 | 528348 BUCKEYE_TP 3 115 528627 LE-TXACO_TP3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20925 | 120.24 | 528463 SANGER_SW 3 115 528575 OXYPERMIAN 3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20925 | 120.24 | 528463 SANGER_SW 3 115 762442 G18-004-TAP 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20925 | 120.52 | 528568 MONUMNT_TP 3 115 528581 BYRD_TP 3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20925 | 120.28 | 528574 OXY_NHU_RCF3 115 528575 OXYPERMIAN 3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20925 | 120.5 | 528596 CARDINAL 3 115 528605 TARGA 3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20925 | 120.53 | 528603 NA_ENRICH 3 115 528605 TARGA 3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.61 | 528617 LE-WAITS 2 69.0 528325 LE-WAITS 3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.51 | 528617 LE-WAITS 2 69.0 528714 LE-FORT_SW 2 69.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.49 | 528617 LE-WAITS 2 69.0 528759 LE-TP51 2 69.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20925 | 120.29 | 528622 LE-SANANDRS2 69.0 528341 LE-SANANDRS3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.92 | 528626 LE-PLNSINT 2 69.0 526928 PLAINS_INT 3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.92 | 528626 LE-PLNSINT 2 69.0 528709 LE-PLNSGOAB2 69.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.52 | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.59 | 528669 LE-STKLDRTP2 69.0 528740 LE-PLANS_SW2 69.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.79 | 528709 LE-PLNSGOAB2 69.0 528740 LE-PLANS_SW2 69.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.52 | 528709 LE-PLNSGOAB2 69.0 528747 LE-ALLRED 2 69.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.51 | 528714 LE-FORT_SW 2 69.0 528718 LE-NEWTEX 2 69.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.59 | 528735 LE-PLAINSUB2 69.0 528740 LE-PLANS_SW2 69.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.52 | 528775 LE-ERF 3 115 528779 LE-TALLCOTN3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.3 | 531213 SANTAFE3 115 531408 PIERCVL3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20924 | 120.48 | 531501 BUCKNER7 345 531502 CIMRRN 7 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20924 | 120.48 | 531502 CIMRRN 7 345 531503 CIMRRN 1 34.5 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20912 | 120.24 | 531510 HARBNGR3 115 3WXFMR HARBGR345 _1 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20923 | 120.5 | 539803 IRONWOOD7 345 3WXFMR IRONWOOD MPT 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20925 | 120.59 | 542951 HAW G5 1 22.0 543665 HAWTHN5 161 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20924 | 120.63 | 542955 LAC G1 1 22.0 542981 LACYGNE7 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20923 | 120.62 | 542956 LAC G2 1 24.0 542981 LACYGNE7 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20922 | 120.67 | 542957 IAT G1 1 24.0 542982 IATAN 7 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20923 | 120.74 | 542962 IAT G2 1 24.5 542982 IATAN 7 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21174 | 119.99 | 560022 CRAWFISH_DR 345 762216 G17-151TAP 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21142 | 120.98 | 560022 CRAWFISH_DR 345 762467 G18-015-TAP 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 116.89 | 560022 CRAWFISH_DR 345 763087 GEN-2018-073 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21254 | 121.28 | 560022 CRAWFISH_DR 345 763215 G18-092-TAP 345 2
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.99 | 560252 G10-14 345 560253 G10-14-1 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.69 | 560253 G10-14-1 115 560254 G10-14-SUB1 34.5 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.69 | 560253 G10-14-1 115 560255 G10-14-SUB2 34.5 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.52 | 560581 G06-44-2 34.5 523111 NOVUS1 3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.57 | 560582 G06-44-3 34.5 560577 G06-44 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.56 | 560583 G06-44-4 34.5 560577 G06-44 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.17 | 560757 ASGI13_02_1 69.0 560758 ASGI13_02_2 34.5 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.17 | 560757 ASGI13_02_1 69.0 562731 WHEATLAND 69.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.17 | 560763 ASGI13_03_1 115 560761 ASGI13_03_2 34.5 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.66 | 562015 FIREWHEEL1 34.5 523215 FREWHELCOL17 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.66 | 562016 FIREWHEEL2 34.5 523215 FREWHELCOL17 345 2
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.16 | 562323 AGI1202&1305 115 562324 AGI1202&1305 34.5 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.17 | 562727 LESBIA 115 562728 SANJONTAP 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.17 | 562728 SANJONTAP 115 562729 CAPROCKTAP1 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.17 | 562730 CAPROCKTAP2 69.0 562729 CAPROCKTAP1 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.17 | 562730 CAPROCKTAP2 69.0 562731 WHEATLAND 69.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.65 | 563171 G15082_2 34.5 563170 G15082_1 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.23 | P11:13.8:AEPW:COM1-1
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.24 | P11:13.8:AEPW:COM2-1
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.25 | P11:13.8:AEPW:COM3-1
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.26 | P11:18:AEPW:WELSH1-1
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.26 | P11:18:AEPW:WELSH3-1
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.25 | P11:24:AEPW:PIRKEY 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.13 | P11:24:AEPW:SWS3-1
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.2 | P11:24:AEPW:TURKCOAL
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20938 | 120.56 | P12:138:AEPW-OMPA:DUNCAN-4:OMDUNCN4
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20931 | 120.09 | 584560 GEN-2015-014 115 584561 G15-014XFMR1 34.5 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20927 | 120.29 | P12:138:AEPW:ARSHILL4:STLGENS4
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20933 | 120.51 | P12:138:AEPW:SANTAFE:DUNCAN-4
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.5 | 588480 A16-010_SUB 115 3WXFMR A16-010_SUB 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20938 | 120.55 | P12:138:AEPW:DUNCAN-4:L.E.S.-4
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 119.91 | 588761 G17-033XFMR1 34.5 588760 GEN-2017-033 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 119.91 | 588765 G17-033XFMR2 34.5 588760 GEN-2017-033 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.51 | 588861 G17-047XFMR1 34.5 588860 GEN-2017-047 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20911 | 120.25 | P12:138:AEPW:ELKCTY-4:CLINTJC4
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.49 | P12:138:AEPW:SHERID4:112GORE4
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21173 | 122.68 | P12:345:AEPW:L.E.S7:TERRYRD7
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21173 | 122.67 | P12:345:AEPW:L.E.S7:TERRYRD7
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21172 | 122.65 | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21247 | 122.27 | P12:345:AEPW-OKGE:L.E.S.-7:GRACMNT7
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21247 | 122.24 | P12:345:AEPW-OKGE:L.E.S.-7:GRACMNT7
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.2096 | 120.48 | P12:345:AEPW-OKGE:PITTSB-7:JOHNCO7
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.2092 | 120.25 | P12:345:AEPW-OKGE:PITTSB-7:SEMINOL7
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20941 | 120.52 | P12:345:AEPW-WFEC:VALIANT7:HUGO7
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21233 | 123.25 | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.55 | P22:345:AMMO::LABADIE:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.53 | P22:345:AMMO::LABADIE:2
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.55 | P22:345:AMMO::LABADIE:3
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.55 | P22:345:AMMO::LABADIE:4
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.54 | P22:345:AMMO::RUSHISLAND:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.51 | P22:345:AMMO::RUSHISLAND:2
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20927 | 120.24 | P13:138-13.8:AEPW:COMANC-4_#2
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20867 | 119.94 | P13:138-230:AEPW:ELKCTY-4
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20927 | 120.26 | P13:138-24:AEPW:PIRKEY 4
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20931 | 120.15 | P13:138-24:AEPW:S.W.S.-4
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20927 | 120.21 | P13:138-24:AEPW:TURK 4
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20943 | 120.54 | P13:138-345:AEPW:L.E.S.-4_#2
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20928 | 120.55 | P23:500:EES-EAI:KEO:B4941
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20928 | 120.53 | P23:500:EES-EAI:KEO:B4921
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20909 | 120.51 | 640183 GENTLMN3 345 640325 REDWILO3 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.48 | P11:26:EES-EAI:INDEP2:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20927 | 120.51 | P23:500:EES-EAI:INDEP2:B6126
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.51 | P23:500:EES-EAI:PD:INDEP2:LN:FK479
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20928 | 120.26 | P13:345-18:AEPW:WELSH 7_#1
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20928 | 120.26 | P13:345-18:AEPW:WELSH 7_#3
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.25 | P13:69-13.8:AEPW:COMANC-2
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20923 | 120.5 | 648513 GRPR1 3 345 652532 GR PRAIRIE 3 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.56 | P11:024:DPC:ALMA2:6
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20923 | 120.53 | 652537 WHITE 3 345 659286 DEERCREK-BE3 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20924 | 120.48 | 652568 GROTONSOUTH7 115 659275 GROTON_G-BE7 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20923 | 120.53 | 659286 DEERCREK-BE3 345 3WXFMR DEERCRK KU1A 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.49 | 672540 QE 6 138 672541 CORY 6 138 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.53 | 672601 BD 4 230 672306 BD 6G 18.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.53 | 672610 POPLAR 4 230 672310 POPLAR 1G 18.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.53 | 672610 POPLAR 4 230 672311 POPLAR 2G 18.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.53 | 672621 SHAND 4 230 672321 SHAND 1G 18.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.51 | 672649 CODETTE 4 230 672650 NIPAWIN 4 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.5 | 672685 SWIFTCU 4 230 672389 CHINOOK 1G 18.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.5 | 672688 PASQUA 4 230 673390 FUT-PQ1X 18.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.55 | 672696 BRADA 4 230 672699 NBEC 4 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.48 | 672699 NBEC 4 230 672392 NBEC GT 1G 18.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.49 | P13:345-230:CLEC:DOLET:5092
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.6 | P23:345:MDU::COYOTE::5707-5712-5715::::
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.76 | P23:345:MEC:CBEC 905
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.72 | P23:345:MEC:CBEC 908
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.64 | P23:345:MEC:RAUN 0180
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.71 | P23:345:MEC:RAUN 0210
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.64 | P23:345:MEC:LOUISA 954
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.64 | P23:345:MEC:LOUISA 964
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.5 | P21:115:XEL:AUTO-SINGLE:CHEMOLT7:LSPOWER7:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.49 | P21:115:XEL:AUTO-SINGLE:FARIBALTP7:FARIBALTGEN:Z
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.61 | P21:230:OTP:AUTO-SINGLE:SQBUTTE4:YNG24:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.59 | P23:345:OTP:CENTER 3:3215(1)
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.59 | P23:345:OTP:CENTER 3:3225(1)
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 119 | 760494 GEN-2017-146 230 760498 G17-146-TAP 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 119 | 760495 G17-146-XFM1 34.5 760494 GEN-2017-146 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.26 | 761356 G17-239-XFMR 34.5 761355 GEN-2017-239 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.26 | 761359 G17-239-XFMR 34.5 761355 GEN-2017-239 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 114.95 | 762132 GEN-2017-158 230 763252 G18-099-XFM1 34.5 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 114.95 | 762132 GEN-2017-158 230 763255 G18-099-XFM2 34.5 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 115.52 | 762133 G17-158XFM1 34.5 762132 GEN-2017-158 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 115.52 | 762136 G17-158XFM2 34.5 762132 GEN-2017-158 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 117.81 | 762216 G17-151TAP 345 762217 GEN-2017-151 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21174 | 121.31 | 762216 G17-151TAP 345 762467 G18-015-TAP 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 119.71 | 762218 G17-151XFM1 34.5 762217 GEN-2017-151 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 119.71 | 762221 G17-151XFM2 34.5 762217 GEN-2017-151 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 119.71 | 762224 G17-151XFM3 34.5 762217 GEN-2017-151 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 119.71 | 762227 G17-151XFM4 34.5 762217 GEN-2017-151 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.26 | 762438 GEN-2018-004 115 762442 G18-004-TAP 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 118.8 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 119.55 | 762461 G18-015-XFM1 34.5 762460 GEN-2018-015 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 119.55 | 762464 G18-015-XFM2 34.5 762460 GEN-2018-015 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21061 | 120.87 | 762467 G18-015-TAP 345 763215 G18-092-TAP 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 118.04 | 763087 GEN-2018-073 345 763088 G18-073-XFM1 34.5 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 119.21 | 763087 GEN-2018-073 345 763091 G18-073-XFM2 34.5 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 114.92 | 763120 GEN-2018-081 230 763121 G18-081-XFM1 34.5 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 117.23 | 763120 GEN-2018-081 230 764011 G19-074-XFM1 34.5 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 117.2 | 763186 GEN-2018-089 230 763187 G18-089-XFM1 34.5 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 118.06 | 763208 GEN-2018-092 345 763215 G18-092-TAP 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 119.2 | 763208 GEN-2018-092 345 763220 G18-092-XFM1 34.5 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 119.2 | 763208 GEN-2018-092 345 763223 G18-092-XFM2 34.5 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 116.67 | 763241 GEN-2018-097 230 763242 G18-097-XFM1 34.5 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 117.6 | 763241 GEN-2018-097 230 763296 G18-111-XFM1 34.5 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 116.95 | 763241 GEN-2018-097 230 763307 G18-112-XFM1 34.5 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 116.95 | 763241 GEN-2018-097 230 763310 G18-112-XFM2 34.5 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 116.67 | 763241 GEN-2018-097 230 763395 G18-124-XFM1 34.5 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 116.67 | 763241 GEN-2018-097 230 763398 G18-124-XFM2 34.5 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 116.31 | 763483 GEN-2019-003 230 763484 G19-003-XFM1 34.5 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 119.03 | 763483 GEN-2019-003 230 763605 G19-021-XFM1 34.5 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 119.65 | 763516 GEN-2019-011 345 763517 G19-011-XFM1 34.5 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.06 | 763879 GEN-2019-056 115 763880 G19-056XFM1 34.5 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.49 | P13:345,230:CLEC::DOLHILL::1
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.29 | P13:345,24:CLEC::G1DOLHILL::1
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20892 | 120.51 | P42:345:OKGE:SB_BVTY7305
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.2091 | 120.23 | P23:345:WERE:BUFF_345-534::
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.2091 | 120.23 | P23:345:WERE:BUFF_345-543::
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20922 | 120.66 | P23:345:WERE:JEC_345-15::
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.2092 | 120.62 | P23:345:WERE:JEC_345-16::
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20922 | 120.66 | P23:345:WERE:JEC_345-19::
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20922 | 120.66 | P23:345:WERE:JEC_345-20::
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.2092 | 120.29 | P23:345:WERE:WICH_345-50::
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20925 | 120.87 | P23:345:WERE:WOLF_345-50::
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.87 | P23:345:WERE:WOLF_345-60::
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20927 | 120.28 | P42:345:AEPW:WELSH CB 10620 NBTB+FAULT
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.27 | P41:345:AEPW:WELSH CB 10630 NBTB+FAULT
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.26 | P41:345:AEPW:WELSH CB 11670 NBTB+FAULT
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20929 | 120.53 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.26 | P41:345:AEPW:WELSH CB 12540 NBTB+FAULT
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20928 | 120.49 | P43:345:AEPW:CHAMBERS SPRING CB 12720 NBTB+FAULT
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20928 | 120.49 | P42:345:AEPW:CHAMBERS SPRING CB 13720 NBTB+FAULT
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20928 | 120.49 | P42:345:AEPW:CHAMBERS SPRING CB 13850 NBTB+FAULT
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21233 | 121.76 | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.2128 | 122.49 | P42:345:AEPW:LAWTON EASTSIDE CB 3413A NBTB+FAULT
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21314 | 122.73 | P42:345:AEPW:LAWTON EASTSIDE CB 3425A NBTB+FAULT
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21246 | 123.34 | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.2096 | 120.48 | P42:345:AEPW:PITTSBURG CB 3433A NBTB+FAULT
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20936 | 120.18 | P42:345:AEPW:PITTSBURG CB 3441A NBTB+FAULT
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.2092 | 120.25 | P42:345:AEPW:PITTSBURG CB 3445A NBTB+FAULT
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21173 | 122.67 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21173 | 122.67 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21173 | 122.65 | P42:345:AEPW:TERRYRD_CB_3421A_NBTB
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20924 | 120.65 | P23:345:KCPL:LACYGNE_R2-5::LACYGU2-LACYGNE-STILWELL
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20924 | 120.28 | P45:345:UMZW:# 1328 #: GI IN NE.
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20927 | 120.28 | P23:345:AEPW:WELSH CB 10620 NBTB
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.27 | P23:345:AEPW:WELSH CB 10630 NBTB
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.26 | P23:345:AEPW:WELSH CB 11670 NBTB
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20929 | 120.53 | P23:345:AEPW:WELSH CB 11990 NBTB
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.26 | P23:345:AEPW:WELSH CB 12540 NBTB
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20928 | 120.49 | P23:345:AEPW:CHAMBERS SPRING CB 12720 NBTB
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20928 | 120.49 | P23:345:AEPW:CHAMBERS SPRING CB 13720 NBTB
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20928 | 120.49 | P23:345:AEPW:CHAMBERS SPRING CB 13850 NBTB
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21233 | 122.19 | P23:345:AEPW:OKLAUNION CB 3401A NBTB
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.2128 | 122.49 | P23:345:AEPW:LAWTON EASTSIDE CB 3413A NBTB
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21314 | 122.73 | P23:345:AEPW:LAWTON EASTSIDE CB 3425A NBTB
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21246 | 123.34 | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.2096 | 120.48 | P23:345:AEPW:PITTSBURG CB 3433A NBTB
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20936 | 120.18 | P23:345:AEPW:PITTSBURG CB 3441A NBTB
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.2092 | 120.25 | P23:345:AEPW:PITTSBURG CB 3445A NBTB
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21173 | 122.67 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21173 | 122.67 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21173 | 122.65 | P23:345:AEPW:TERRYRD_CB_3421A_NBTB
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20956 | 120.48 | P12:138:AEPW:S.W.S.-4:L.E.S.-4
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20925 | 120.54 | P11:161:GMO:DOGWOOD_COMBINED_CYCLE_UNIT_OUTAGE
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20926 | 120.54 | P11:115:SUNC:GARDENCITY_S2:97:531459(2)
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20912 | 120.25 | P12:345:PWT:BUFF-THIS_345_1::
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20912 | 120.25 | P12:345:PWT:BUFF-THIS_345_2::
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20935 | 120.52 | P12:069:WFEC:ANADRKO_WATONGA
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20944 | 120.54 | P23:345:AEPW:VALLIANT CB 3413A NBTB
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.2095 | 120.56 | P23:345:AEPW:VALLIANT CB 3417A NBTB
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.2119 | 122.82 | P23:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21446 | 125.21 | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20944 | 120.54 | P42:345:AEPW:VALLIANT CB 3413A NBTB+FAULT
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.2095 | 120.56 | P42:345:AEPW:VALLIANT CB 3417A NBTB+FAULT
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.2119 | 122.82 | P42:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB+FAULT
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21446 | 125.21 | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20466 | 117.77 | P42:345:OKGE:SB_BVTY7315_PRE19S
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20888 | 120.52 | P23:345:SUNC:MO_BRK188
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21045 | 120.68 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20927 | 120.23 | P12:138-13.8:AEPW:COMANC-4_#1
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20867 | 119.93 | P12:230:AEPW:ELKCITY6:CHISHOLM6
Thermal | 05ALL | 1 | 26WP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.21036 | 121.03 | P12:230:AEPW:SWEETWT6:CHISHOLM6
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997711 ABBXNL844501 230 1 |  | 552.5 | 0.24653 | 164.23 | 525531 TOLK 6 230 3WXFMR TOLK 6 2
Thermal | 05ALL | 1 | 26WP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.24653 | 162.04 | 525549 TOLK 7 345 3WXFMR ABBXNL844501 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997711 ABBXNL844501 230 1 |  | 552.5 | 0.24653 | 164.23 | 525531 TOLK 6 230 3WXFMR TOLK 6 2
Thermal | 05ALL | 1 | 26WP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.24653 | 162.04 | 525549 TOLK 7 345 3WXFMR ABBXNL844501 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997711 ABBXNL844501 230 1 |  | 552.5 | 0.28873 | 164.23 | 525531 TOLK 6 230 3WXFMR TOLK 6 2
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.20024 | 127.4 | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.28873 | 162.04 | 525549 TOLK 7 345 3WXFMR ABBXNL844501 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 511458 ELKCTY-4 138 998036 ELKCTY-6 _1 138 1 |  | 330 | 0.05505 | 112.44 | P12:345:OKGE-AEPW:BKRBKR371::::
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 511458 ELKCTY-4 138 998036 ELKCTY-6 _1 138 1 |  | 330 | 0.05505 | 112.78 | P12:345:OKGE-AEPW:BKRBKR371::::
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.05505 | 108.04 | P12:345:OKGE-AEPW:BKRBKR371::::
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.05505 | 108.6 | P12:345:OKGE-AEPW:BKRBKR371::::
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 511490 ELKCITY6 230 998036 ELKCTY-6 _1 138 1 |  | 330 | 0.05505 | 112.79 | P12:345:OKGE-AEPW:BKRBKR371::::
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 511490 ELKCITY6 230 998036 ELKCTY-6 _1 138 1 |  | 330 | 0.05505 | 113.27 | P12:345:OKGE-AEPW:BKRBKR371::::
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997715 ABBXNL844501 230 1 |  | 553 | 0.08313 | 150.96 | 525531 TOLK 6 230 3WXFMR TOLK 6 2
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05095 | 112.73 | P23:345:KCPL-WERE:237LACYGNE_R1-6::LACYGU1-LACYGNE-NEOSHO
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05092 | 112.64 | P11:230:WERE:LECU5_GEN::
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05093 | 112.63 | P11:161:GMO:DOGWOOD_COMBINED_CYCLE_UNIT_OUTAGE_1_1
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.051 | 111.16 | P11:115:SPS:MUSTANG1&3:153MW::::
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.0504 | 114.61 | P12:230:SPS:K37::1_TOLK_LAMB:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05106 | 112.61 | P12:230:SPS:K43::1_PRNGLE_HARR_E:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05097 | 112.37 | P12:230:SPS:K44::1_EPLNT_HARRW:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05123 | 112.79 | P12:115:SPS:T04::1_TRBLNC_CASTRO:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05095 | 112.19 | P12:115:SPS:T13::1_TAYLOR_WHOBBS:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05095 | 112.31 | P12:115:SPS:T14::1_MADDOX_TAYLOR:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05094 | 113.09 | P12:115:SPS:T21::1_GRSSLND_GRAHAM:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05094 | 112.41 | P12:115:SPS:T23::1_PCA_POTJCT:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05094 | 112.62 | P12:115:SPS:T24B::1_RSWLL_BRSHRF:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05094 | 112.64 | P12:115:SPS:T26::1_CHAVES_RSWLCTY:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05069 | 113.18 | P12:115:SPS:T28A::1_LAMTON_PLANTX:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05061 | 112.67 | P12:115:SPS:T29::1_LAMTON_HALECTR:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05006 | 113.96 | P12:115:SPS:T30::1_LAMB_HOCKLY:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05006 | 113.13 | P12:115:SPS:T31::1_HOCKLY_SUNDWN:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05099 | 112.63 | P12:115:SPS:T35::1_TERRY_YOAKUM:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05094 | 113.32 | P12:115:SPS:T45::1_NORRIS_OASIS:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05098 | 112.4 | P12:115:SPS:T57::1_MUSTG_SEGRVS:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05142 | 113.15 | P12:115:SPS:T59::1_CARGIL_CURRY:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05221 | 112.42 | P12:115:SPS:T66::1_RNDALL_HAPPY:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05221 | 112.9 | P12:115:SPS:T67::1_HAPPY_KRESS:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05086 | 112.39 | P12:115:SPS:T68::1_TUCO_FLOYD:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05098 | 113.2 | P12:115:SPS:T71::1_CRLSLE_YUMA:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05077 | 112.7 | P12:115:SPS:T81::1_COX_FLOYD:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05094 | 112.85 | P12:115:SPS:T83::1_SP-FKFD_ALLEN:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05105 | 113.01 | P12:115:SPS:T89::1_DC_N_HIGG:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05094 | 112.66 | P12:115:SPS:T91::1_HIGG_RUSSELL:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05113 | 112.62 | P12:115:SPS:V04::1_EPLANT_RNDALL:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05086 | 112.67 | P12:115:SPS:V07::1_COX_HALECTR:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05048 | 112.95 | P12:115:SPS:V09::1_HALECTR_PLANTX:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05094 | 112.83 | P12:115:SPS:V12::1_PLANTX_BAILEY:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05094 | 112.62 | P12:115:SPS:V15::1_TUCO_INDANA:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05125 | 112.67 | P12:115:SPS:V24::1_WOLFTH_TERRY:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05084 | 112.64 | P12:115:SPS:V26::1_RSWLL_EDDY_N:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05094 | 112.98 | P12:115:SPS:V33::1_LUBBS_LYNN:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05129 | 113.85 | P12:115:SPS:V37::1_CASTRO_PLANTX:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05094 | 112.75 | P12:115:SPS:V46::1_ALLEN_WHEELCK:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05097 | 113.09 | P12:115:SPS:V49::1_YOAKUM_SHLCO2:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05073 | 113.26 | P12:115:SPS:V55::1_SUNDWN_TERRY:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05097 | 113.09 | P12:115:SPS:V56::1_COCHRAN_SUNDWN:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05094 | 112.68 | P12:115:SPS:V62::1_CRLSLE_INDANA:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05096 | 112.62 | P12:115:SPS:V70::1_S_GORG_RNDALL:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05097 | 112.65 | P12:115:SPS:V78::2_CURRY_RSVLT:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05103 | 112.79 | P12:115:SPS:V81::1_LE-WAIT_LE-LVN:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05095 | 112.65 | P12:115:SPS:V95::1_DC_N_SHLCO2:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05094 | 112.61 | P12:115:SPS:W11::1_DC_S_SMINLE:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05095 | 112.61 | P12:115:SPS:W12::1_SMINLE_DOSS:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05096 | 112.68 | P12:115:SPS:W14::1_SMINLE_GAINES:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05094 | 113.14 | P12:115:SPS:W32::1_PRMTR_FE-CLSIN:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05094 | 112.61 | P12:115:SPS:W34::1_JNSDRW_MAPCO:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05102 | 112.85 | P12:115:SPS:W35::1_GAINES_JNSDRW:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05108 | 112.64 | P12:115:SPS:W36::1_TAYLOR_JNSDRW:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05174 | 113.15 | P12:115:SPS:W40::1_WCANYON_TRBLNC:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05079 | 112.71 | P12:115:SPS:W52::1_NEWHART_KRESS:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05094 | 113.2 | P12:115:SPS:W58::1_NORTON_LOPEZ:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05094 | 112.82 | P12:115:SPS:W59::1_LOPEZ_CMPBLL:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05094 | 113.15 | P12:115:SPS:W62::1_PLSTHL_CURRY:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05106 | 112.62 | P12:115:SPS:W63::1_PLSTHL_CURRY:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05094 | 112.96 | P12:115:SPS:W64::1_PLSTHL_FE-CLV:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05094 | 113.12 | P12:115:SPS:W65::1_PLSTHL_CURRY:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05094 | 112.81 | P12:115:SPS:W66::1_PORTA_GREYHUND:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05174 | 112.61 | P12:115:SPS:W77::1_RNDAL_WCANYON:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05094 | 112.64 | P12:115:SPS:W99::1_CAPITAN_CHAVES:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05099 | 113.08 | P12:115:SPS:U14::1_DC_STH_INKBSN:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05103 | 113.02 | P12:115:SPS:V15::1_INKBSN_LE-WAT:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.051 | 112.74 | P12:115:SPS:U16::1_BSHLND_OUTPST:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.051 | 112.73 | P12:115:SPS:U17::1_COLTR_OUTPST:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05091 | 112.8 | P12:115:SPS:U19::1_DEAN_PLAINS:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.051 | 112.67 | P12:115:SPS:U23::1_COLTR_HILSDE:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.06131 | 119.61 | P42:345:SPS:YOAKUM:J18####:SLG1:EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.06131 | 119.61 | P43:345:SPS:YOAKUM:TF#####:SLG:EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.06131 | 119.61 | P42:345:SPS:YOAKUM:J17####:SLG:EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.06131 | 119.61 | P42:345:SPS:YOAKUM:J18####:SLG2:EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05093 | 112.62 | P11:18:HAST:::EGYCTR2G WEC2_LOSS OF WEC 2 GEN_:HV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05093 | 112.62 | P13:18-115:HAST:::EGYCNTR7 XFMR G2WEC 2 GSU_:HV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05093 | 112.63 | P11:161:GMO:DOGWOOD-COMBINED-CYCLE-UNIT-OUTA:::HV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05095 | 112.73 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05092 | 112.75 | P23:345:KCPL:LACYGNE-R2-5:::EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.0509 | 112.78 | P11:230:WERE:JECU1-GEN:::HV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05092 | 112.64 | P11:230:WERE:LECU5-GEN:::HV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.0509 | 112.78 | P11:345:WERE:JECU2-GEN:::EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05091 | 112.78 | P11:345:WERE:JECU3-GEN:::EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05094 | 112.95 | P11:345:WERE:WOLFU1-GEN:::EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05087 | 112.43 | P23:345:WERE:BUFF-345-534:::EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05087 | 112.43 | P23:345:WERE:BUFF-345-543:::EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05091 | 112.78 | P23:345:WERE:JEC-345-15:::EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.0509 | 112.75 | P23:345:WERE:JEC-345-16:::EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05091 | 112.78 | P23:345:WERE:JEC-345-19:::EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05091 | 112.78 | P23:345:WERE:JEC-345-20:::EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05094 | 112.95 | P23:345:WERE:WOLF-345-50:::EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05094 | 112.95 | P23:345:WERE:WOLF-345-60:::EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05094 | 112.89 | P11:022:NPPD:COOPER1G:1:983:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05089 | 112.92 | P11:023:NPPD:GENTLM1G:1:757:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05089 | 112.94 | P11:024:NPPD:GENTLM2G:2:757:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05091 | 112.75 | P13:345:OPPD:NEBCTY1G:::EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05089 | 112.78 | P13:345:OPPD:NEBCTY2G:::EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05094 | 112.77 | P22:345:OPPD:S3458 NEBCTY1G:LT::EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05091 | 112.75 | P22:345:OPPD:S3458 NEBCTY1G:::EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05094 | 112.81 | P22:345:OPPD:S3458 NEBCTY2G:LT::EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05089 | 112.78 | P22:345:OPPD:S3458 NEBCTY2G:::EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05094 | 112.77 | P23:345:OPPD:S3458 NEBCTY1G:LT::EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05091 | 112.75 | P23:345:OPPD:S3458 NEBCTY1G:::EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05094 | 112.81 | P23:345:OPPD:S3458 NEBCTY2G:LT::EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05089 | 112.78 | P23:345:OPPD:S3458 NEBCTY2G:::EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05094 | 112.4 | P12:115:SUNC:PLYMELL-PIERCEVILLE:::HV::
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05092 | 112.64 | P11:018:UMZB:# 5 #:: DCS IN SD. DEERCREEK_MV::
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05093 | 112.61 | P11:022:UMZB:# 15 #:: LO IN ND. LELAND OLDS 1_MV::
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05092 | 112.65 | P11:020:UMZB:# 16 #:: LO IN ND. LELAND OLDS 2_MV::
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05092 | 112.7 | P11:023:UMZB:# 31 #:: AVS IN ND. ANTELOPE VALLEY 1_MV::
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05092 | 112.7 | P11:023:UMZB:# 32 #:: AVS IN ND. ANTELOPE VALLEY 2_MV::
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05088 | 112.9 | P11:024:UMZB:# 33 #:: LRS IN WY. LARAMIE RIVER STATION 1_MV::
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05094 | 112.63 | P12:230:UMZW:# 687 #:: FT IN SD. FT-BG1 BRANCH FAULT:HV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05094 | 112.63 | P12:230:UMZW:# 3617 #:: FT IN SD. FT-BG2 BRANCH FAULT:HV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05094 | 112.63 | P12:230:UMZW:# 4038 #:: BG-FT IN SD. FAULT FOR TRANSMISSION CIRCUIT (BG-FT).:HV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05094 | 112.63 | P12:230:UMZW:# 4039 #:: BG-FT IN SD. FAULT FOR TRANSMISSION CIRCUIT (BG-FT).:HV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05094 | 112.61 | P13:230:UMZW:# 5135 #:: OA IN SD. FAULT ON TRANSFORMER (2).:HV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05094 | 112.61 | P13:230:UMZW:# 5136 #:: OA IN SD. FAULT ON TRANSFORMER (3).:HV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05092 | 112.42 | P21:345:UMZW:# 725 #:: GI IN NE. GI-SWEET BRANCH FAULT:EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05092 | 112.42 | P23:345:UMZW:# 2430 #:: GI IN NE. GI 1492 BKR FAULT:EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05092 | 112.42 | P23:345:UMZW:# 2438 #:: GI IN NE. GI-SWEET BRANCH FAULT & GI 1492 STUCK BKR:EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05096 | 112.37 | P11:138:WFEC:HUGO1:465MW :::
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05092 | 112.4 | P12:345:OKGE-AEPW:BKRBKR20::::
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05138 | 112.75 | P12:345:OKGE:BKRBKR21::::
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05152 | 112.95 | P12:345:OKGE:BKRBKR24::::
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.0539 | 114.47 | P12:345:OKGE-AEPW:BKRBKR25::::
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05086 | 112.42 | P12:345:OKGE:BKRBKR336::::
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05086 | 112.41 | P12:345:OKGE:BKRBKR336_2::::
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05737 | 114.61 | P12:345:OKGE-AEPW:BKRBKR366::::
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05737 | 114.58 | P12:345:OKGE-AEPW:BKRBKR366::::
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05153 | 112.87 | P12:345:OKGE:BKRBKR367::::
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.0513 | 112.62 | P12:345:OKGE-WFEC:BKRBKR374::::
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05073 | 112.22 | P12:345:OKGE:BKRBKR4193::::
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05073 | 112.22 | P12:345:OKGE:BKRBKR4194::::
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05063 | 112.28 | P12:345:OKGE-SPS:BKRBKR4201::::
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05063 | 112.28 | P12:345:OKGE-SPS:BKRBKR4202::::
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05086 | 112.35 | P12:345:OKGE:BKRBKR443NEW::::
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05086 | 112.35 | P12:345:OKGE:BKRBKR443NEW2::::
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05088 | 112.88 | P12:345:OKGE:BKRBKR604::::
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05087 | 112.94 | P12:345:OKGE:BKRBKR604_2::::
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05066 | 112.62 | P42:345:OKGE:SB_ARIA7381::::
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.06362 | 116.05 | P42:345:OKGE:SB_BVTY7387::::
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05134 | 112.68 | P42:345:OKGE:SB_SPCK7383::::
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05092 | 112.64 | P11:115:SUNC:GARDENCITY_S2:103:531459(2):HV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05092 | 112.64 | P11:115:SUNC:FORTDDODGE_4:157:539670(4):HV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05094 | 112.62 | P11:345:599:CIMARRON1WIND:200:531603(1):EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05094 | 112.92 | P13:115:SUNC:HOLCOMB_GSU:::HV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05092 | 112.64 | P13:115:SUNC:S2_GSU:::HV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05092 | 112.64 | P13:115:SUNC:FORTDODGE_GSU:::HV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05092 | 112.62 | P23:345:SUNC:BU_BRK682:::EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05094 | 112.71 | 300003 1THLG3 24.0 301503 7THOMHLGSU3 345 3
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05094 | 112.71 | 300049 7THOMHL 345 301503 7THOMHLGSU3 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05094 | 112.66 | P11:20:AMMO:1LAB�� G1:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05094 | 112.66 | P11:20:AMMO:1LAB�� G2:2
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05094 | 112.83 | P11:345:AMMO::CALLAWAY:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05094 | 112.66 | P11:345:AMMO::LABADIE:3
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05094 | 112.66 | P11:345:AMMO::LABADIE:4
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05094 | 112.66 | P11:345:AMMO::RUSHISLAND:U1
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05094 | 112.66 | P11:345:AMMO::RUSHISLAND:U2
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05094 | 112.64 | P11:138:AMMO::SIOUX:2
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05094 | 112.64 | P12:765:AEP:AEP ROCKP-AEP JEFF 765
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05094 | 112.61 | P11:HV:EES::1ISES U1:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05094 | 112.61 | P11:EHV:EES::1ISES U2:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05094 | 112.42 | P11:HV:EES::PIRKEY 1:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05094 | 112.42 | P11:EHV:EES::WELSH3-1:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05094 | 112.39 | P11:HV:EES::TURKCOAL:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05094 | 112.61 | P12:HV:EES::5ISES%:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05094 | 112.61 | P12:EHV:EES::8ISES%:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05094 | 112.82 | P12:EHV:EES::7CALAWY 1:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05095 | 112.39 | P12:HV:EES::TURK 4%:1(1)
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05094 | 112.64 | 344011 7HUGHES 345 344012 7HPW-N 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05094 | 112.66 | 344884 7LABADIE1 345 344894 1LAB G1 20.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05094 | 112.66 | 344885 7LABADIE2 345 344895 1LAB G2 20.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05094 | 112.66 | 344886 7LABADIE3 345 344896 1LAB G3 20.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05094 | 112.66 | 344887 7LABADIE4 345 344897 1LAB G4 20.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05094 | 112.65 | 345667 7RUSH 1 345 345670 1RUSH G1 18.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05094 | 112.65 | 345668 7RUSH 2 345 345671 1RUSH G2 18.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05094 | 112.64 | 345755 4SIOUX 1 138 345756 1SIOUX 1 18.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05094 | 112.64 | 345764 4SIOUX 2 138 345765 1SIOUX 2 18.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05094 | 112.69 | P12:345:MDU::CENTER:COYOTE:1::::
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05094 | 112.69 | P13:345:MDU:COYOTE GSU LOSS:COYOTE::1::::
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05094 | 112.61 | P11:345:MEC:GDMEC CT1
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05094 | 112.61 | P11:345:MEC:GDMEC CT2
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05094 | 112.71 | P11:345:MEC:GDMEC ST
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05094 | 112.9 | P11:345:MEC-NPPD:COOPER 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05094 | 112.8 | P11:24:XEL:AUTO-SINGLE:SHERC31G:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05094 | 112.8 | P11:24:XEL:AUTO-SINGLE:SHERC32G:2
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05094 | 112.87 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05094 | 112.73 | P11:20:XEL:AUTO-SINGLE:PRIS31G:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05094 | 112.73 | P11:20:XEL:AUTO-SINGLE:PRIS32G:2
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05094 | 112.76 | P11:22:XEL:AUTO-SINGLE:MNTCE31G:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05094 | 112.73 | P11:20:XEL:AUTO-SINGLE:KING31G:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05094 | 112.77 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05094 | 112.77 | P11:22:GRE:AUTO-SINGLE:GRE-COAL42G:2
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05094 | 112.71 | P11:24:OTP:AUTO-SINGLE:BIGSTN1G:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05094 | 112.71 | P11:20:OTP:AUTO-SINGLE:CENTER2G:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05094 | 112.63 | P11:22:OTP:AUTO-SINGLE:CENTER1G:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05094 | 112.7 | P11:24:OTP:AUTO-SINGLE:COYOTE1G:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05094 | 112.63 | P11:24:DPC:AUTO-SINGLE:GENOA53G:3
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05094 | 112.61 | P12:115:XEL:AUTO-SINGLE:CHEMOLT7:LSPOWER7:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05094 | 112.65 | P12:115:XEL:AUTO-SINGLE:COLVILL7:CANONFLSG7:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05094 | 112.61 | P12:115:XEL:AUTO-SINGLE:FARIBALTP7:FARIBALTGEN:Z
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05094 | 112.7 | P12:230:OTP:AUTO-SINGLE:SQBUTTE4:YNG24:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05094 | 112.78 | P13:24-345:XEL:AUTO-SINGLE:SHERC31G:SHERCO3:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05094 | 112.78 | P13:24-345:XEL:AUTO-SINGLE:SHERC32G:SHERCO3:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05094 | 112.85 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05094 | 112.73 | P13:20-345:XEL:AUTO-SINGLE:PRIS31G:PRISLD3:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05094 | 112.73 | P13:20-345:XEL:AUTO-SINGLE:PRIS32G:PRISLD3:2
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05094 | 112.76 | P13:22-345:XEL:AUTO-SINGLE:MNTCE31G:MNTCELO3:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05094 | 112.72 | P13:20-345:XEL:AUTO-SINGLE:KING31G:ASKING3:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05094 | 112.76 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL41G:GRE-COALCR4:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05094 | 112.75 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL42G:GRE-COALCR4:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05094 | 112.7 | P13:230-24:OTP:AUTO-SINGLE:BIGSTON4:BIGSTN1G:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05094 | 112.7 | P13:20-230:OTP:AUTO-SINGLE:CENTER2G:YNG24:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05094 | 112.62 | P13:22-230:OTP:AUTO-SINGLE:CENTER1G:CENTER4:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05094 | 112.69 | P13:24-345:OTP:AUTO-SINGLE:COYOTE1G:COYOTE3:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05094 | 112.63 | P13:24-161:DPC:AUTO-SINGLE:GENOA53G:GENOA5:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05094 | 112.64 | P13:24-161:DPC:AUTO-SINGLE:JPM:ALMA5:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05094 | 112.7 | P11:115:XEL:RIV COMBINE CYCLE
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05094 | 112.62 | P12:115:XEL:BDS #2 5
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05094 | 112.62 | P11:115:XEL:HBR #6
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05094 | 112.62 | P11:115:XEL:HBR #7
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05094 | 112.73 | P11:115:XEL:HBR #6 7 8
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05094 | 112.73 | P23:345:XEL:8H14 PRI
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05094 | 112.73 | P23:345:XEL:8H17 PRI AS
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05094 | 112.85 | P23:345:XEL:8N28 SHC
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05094 | 112.78 | P23:345:XEL:8N22 SHC
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05094 | 112.78 | P23:345:XEL:8N17 SHC
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05094 | 112.77 | P23:345:XEL:8N8 MNN
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05094 | 112.72 | P23:345:XEL:8P1 KING
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05094 | 112.72 | P23:345:XEL:8P2 KING
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05094 | 112.62 | P23:115:XEL:5P147 IVH AS
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05094 | 112.61 | P11:18:ALTW:AUTO-SINGLE:EMERYST1:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05094 | 112.61 | P11:22:ALTW:AUTO-SINGLE:LANS54G:4
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05094 | 112.74 | P11:22:ALTW:AUTO-SINGLE:ARNOLD1G:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05094 | 112.77 | P11:24:ALTW:AUTO-SINGLE:OTTUMW1G:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05094 | 112.61 | P13:18-161:ALTW:AUTO-SINGLE:EMERYST1:EMERY5:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05094 | 112.61 | P13:22-161:ALTW:AUTO-SINGLE:LANS54G:LANSINGL15:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05094 | 112.73 | P13:22-161:ALTW:AUTO-SINGLE:ARNOLD1G:ARNOLD5:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05094 | 112.76 | P13:24-161:ALTW:AUTO-SINGLE:OTTUMW1G:OTTUMWA5:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05094 | 112.82 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05094 | 112.88 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05094 | 112.75 | P11:22:MEC:AUTO-SINGLE:NEAL3G:3
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05094 | 112.81 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05094 | 112.76 | P11:24:MEC:AUTO-SINGLE:LOUIS31G:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05094 | 112.81 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05094 | 112.84 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05094 | 112.74 | P13:345-22:MEC:AUTO-SINGLE:RAUN3:NEAL3G:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05094 | 112.8 | P13:345-24:MEC:AUTO-SINGLE:RAUN3:NEAL4G:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05094 | 112.74 | P13:345-24:MEC:AUTO-SINGLE:LOUISA3:LOUIS31G:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.0509 | 112.78 | P11:230:WERE:JECU1_GEN::
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.0509 | 112.78 | P11:345:WERE:JECU2_GEN::
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05091 | 112.78 | P11:345:WERE:JECU3_GEN::
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05094 | 112.95 | P11:345:WERE:WOLFU1_GEN::
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05106 | 112.63 | 511435 SNYDER-4 138 588779 TAP_G17-036 138 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05087 | 112.38 | 511446 CL-AFTP4 138 511458 ELKCTY-4 138 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05087 | 112.4 | 511446 CL-AFTP4 138 511463 HOB-JCT4 138 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05105 | 112.63 | 511453 DUNCAN-4 138 511552 DUNCHERTP4 138 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05105 | 112.62 | 511455 D.E.S.-4 138 511552 DUNCHERTP4 138 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05105 | 112.62 | 511455 D.E.S.-4 138 529344 OMDUNE-4 138 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05094 | 112.63 | 511456 O.K.U.-7 345 511565 OKLAUN HVDC7 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05094 | 111.6 | 511456 O.K.U.-7 345 588760 GEN-2017-033 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05591 | 114.54 | 511456 O.K.U.-7 345 763215 G18-092-TAP 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05613 | 115.11 | 511468 L.E.S.-7 345 762467 G18-015-TAP 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05446 | 114.48 | 511468 L.E.S.-7 345 763215 G18-092-TAP 345 2
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05094 | 112.29 | 511468 L.E.S.-7 345 763318 GEN-2018-115 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05106 | 112.66 | 511488 112GORE4 138 511510 LAIRGST4 138 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05111 | 112.7 | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05106 | 112.65 | 511500 CACHE4 138 511510 LAIRGST4 138 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05106 | 112.64 | 511500 CACHE4 138 588779 TAP_G17-036 138 2
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05184 | 112.8 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05094 | 112.75 | 511541 SWEETWT6 230 763340 GEN-2018-117 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.06362 | 116.03 | 515375 WWRDEHV7 345 515458 BORDER 7 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.06362 | 116.05 | 515458 BORDER 7 345 560022 CRAWFISH_DR 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05091 | 112.7 | 515618 BALKOW 7 345 3WXFMR BALKOW 7 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05091 | 112.7 | 515618 BALKOW 7 345 3WXFMR BALKOW 7 1_Dup1
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05087 | 112.95 | 515634 PALDR1W7 345 3WXFMR PALO2 _1 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05094 | 112.7 | 515677 BADGER 7 345 563170 G15082_1 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05093 | 112.61 | 520827 BINGERJ4 138 521017 ONEY 4 138 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05093 | 112.62 | 521017 ONEY 4 138 521089 WASHITA4 138 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05094 | 112.61 | 522800 MU-TULIA 3 115 525179 TULIA_TP 3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05094 | 112.75 | 522892 MU-BROWNFLD2 69.0 526761 BROWNFLD_TP2 69.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05094 | 112.64 | 523090 TEXAS_CNTY 3 115 589380 GEN-2017-100 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.0509 | 112.78 | 523093 HITCHLAND 3 115 523174 GOODWELLWND3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05094 | 112.95 | 523097 HITCHLAND 7 345 523112 NOVUS1 7 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05094 | 113 | 523097 HITCHLAND 7 345 523215 FREWHELCOL17 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05094 | 113.05 | 523097 HITCHLAND 7 345 560252 G10-14 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05094 | 112.62 | 523099 TC-DRYTRLS 3 115 588480 A16-010_SUB 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05094 | 112.82 | 523112 NOVUS1 7 345 3WXFMR NOVUS XF2 2
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05094 | 112.63 | 523112 NOVUS1 7 345 3WXFMR XIANA2011198 _1 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05092 | 112.61 | 523118 BUFF_DUNES 7 345 523853 FINNEY 7 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05094 | 112.63 | 523120 COLE 3 115 588860 GEN-2017-047 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05092 | 112.64 | 523172 GWELL_COLL11 34.5 523174 GOODWELLWND3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05092 | 112.65 | 523173 GWELL_COLL21 34.5 523174 GOODWELLWND3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05106 | 112.61 | 523267 PRINGLE 6 230 3WXFMR ENRCO13617-1 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05106 | 112.61 | 523267 PRINGLE 6 230 523979 HARRNG_EST 6 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05144 | 113.07 | 523771 GRAPEVINE 6 230 524044 NICHOLS 6 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05484 | 113.75 | 523959 POTTER_CO 6 230 524267 BUSHLAND 6 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05765 | 114.67 | 523959 POTTER_CO 6 230 525461 NEWHART 6 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05716 | 118.42 | 523961 POTTER_CO 7 345 3WXFMR WAUK 90343-A 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05111 | 112.4 | 523978 HARRNG_MID 6 230 523979 HARRNG_EST 6 230 @1
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05095 | 112.39 | 524010 ROLLHILLS 6 230 3WXFMR WAUK WT01104 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.051 | 112.74 | 524267 BUSHLAND 6 230 3WXFMR WH 7001795 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05773 | 114.31 | 524267 BUSHLAND 6 230 524623 DEAFSMITH 6 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05081 | 113.07 | 524296 SPNSPUR_WND7 345 524299 SPNSPUR_COL7 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05081 | 113.07 | 524299 SPNSPUR_COL7 345 3WXFMR SPNSPUR_COL7 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05665 | 113.32 | 524415 AMA_SOUTH 6 230 525213 SWISHER 6 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05094 | 113.2 | 524502 NORTON 3 115 524509 FE-TUCMCARI3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05174 | 113.01 | 524575 DS-#25+ 3 115 524597 PANDAHFD 3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05174 | 113.12 | 524575 DS-#25+ 3 115 524630 TIERABLANCA3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05094 | 112.7 | 524604 HEREFRD_SB 2 69.0 524608 HERFRD_STH 2 69.0 *1
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.0559 | 119.12 | 524623 DEAFSMITH 6 230 760498 G17-146-TAP 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05094 | 113.1 | 524721 DS-#15&#19+2 69.0 524745 CASTRO_CNTY2 69.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05096 | 112.61 | 524770 PLSNT_HILL 6 230 3WXFMR EFAE1100068A 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05085 | 113.69 | 524875 OASIS 6 230 524909 ROOSEVELT 6 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05097 | 112.8 | 524909 ROOSEVELT 6 230 3WXFMR ABB LMM60042 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05099 | 118.36 | 524909 ROOSEVELT 6 230 525531 TOLK 6 230 2
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05094 | 113.33 | 524923 PORTALES 2 69.0 524929 RO-PORT_MTR2 69.0 @1
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05094 | 113 | 525001 W_MULESHOE 2 69.0 525008 MULESH_CTY 2 69.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05094 | 113 | 525008 MULESH_CTY 2 69.0 525027 BAILEYCO 2 69.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05094 | 113.28 | 525023 BC-BAIL_MTR2 69.0 525027 BAILEYCO 2 69.0 @1
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05129 | 113.27 | 525056 BC-EARTH 3 115 525480 PLANT_X 3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05094 | 113.09 | 525191 KRESS_INT 2 69.0 525203 SW-KRESS 2 69.0 Z1
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05094 | 113.17 | 525192 KRESS_INT 3 115 3WXFMR ENRCO 136155 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05094 | 112.73 | 525272 KISER 3 115 3WXFMR VON 13819/1 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05094 | 113.19 | 525326 COX 3 115 3WXFMR ELCO 13474-3 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05094 | 113.21 | 525414 LAMTON 3 115 3WXFMR ASEA MLL9204 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05069 | 113.03 | 525440 LC-S_OLTON+3 115 525446 RKYFORD_TP 3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05069 | 113.03 | 525446 RKYFORD_TP 3 115 525480 PLANT_X 3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.0516 | 116.34 | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05062 | 114.35 | 525481 PLANT_X 6 230 3WXFMR WH ALM20171 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.0559 | 117.38 | 525481 PLANT_X 6 230 760498 G17-146-TAP 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05088 | 113.07 | 525481 PLANT_X 6 230 762174 G17-218TAP 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05087 | 113.14 | 525481 PLANT_X 6 230 762174 G17-218TAP 230 2
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.0504 | 114.61 | 525531 TOLK 6 230 525637 LAMB_CNTY 6 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05085 | 113.33 | 525531 TOLK 6 230 762174 G17-218TAP 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05085 | 113.39 | 525531 TOLK 6 230 762174 G17-218TAP 230 2
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08313 | 149.08 | 525549 TOLK 7 345 3WXFMR ABBXNL844501 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05094 | 113.01 | 525599 LC-SANDHLL+2 69.0 525606 AMHERST 2 69.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05094 | 113.04 | 525606 AMHERST 2 69.0 525613 W_LITTLFLD 2 69.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05094 | 113.07 | 525613 W_LITTLFLD 2 69.0 525635 LAMB_CNTY 2 69.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05094 | 113.02 | 525635 LAMB_CNTY 2 69.0 525650 LC-LTTLFLD+2 69.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.0504 | 114.61 | 525637 LAMB_CNTY 6 230 3WXFMR WH ALM20172 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05094 | 112.87 | 525828 TUCO_INT 3 115 3WXFMR DS F78800913 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05081 | 112.4 | 525830 TUCO_INT 6 230 3WXFMR ENRCO 136401 2
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05884 | 114.37 | 525832 TUCO_INT 7 345 526936 YOAKUM_345 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05094 | 113.07 | 526086 SW_6786_N 2 69.0 526087 SW_6786_S 2 69.0 Z1
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05094 | 113.07 | 526086 SW_6786_N 2 69.0 526102 SP-HETTLER 2 69.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05094 | 113.14 | 526087 SW_6786_S 2 69.0 526284 PLANTERS 2 69.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05094 | 112.69 | 526160 CARLISLE 3 115 3WXFMR WH RLP38371 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05094 | 113.03 | 526195 QUINCY 3 115 526196 SP-MILWAUKEE 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05094 | 112.93 | 526268 LUBBCK_STH 3 115 3WXFMR NA 70454A 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05094 | 113.19 | 526284 PLANTERS 2 69.0 526297 LUBBCK_EST 2 69.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05099 | 112.63 | 526435 SUNDOWN 6 230 3WXFMR UPDATE LATER _12 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05129 | 115 | 526435 SUNDOWN 6 230 526460 AMOCO_SS 6 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05096 | 112.65 | 526525 WOLFFORTH 6 230 3WXFMR UPDATE LATER _13 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05094 | 113.07 | 526735 TERRY_CNTY 2 69.0 526747 LG-BROWNFLD2 69.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05094 | 113 | 526747 LG-BROWNFLD2 69.0 526754 BROWNFIELD 2 69.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05162 | 114.41 | 526935 YOAKUM 6 230 527028 INK_BASIN 6 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.06019 | 121.79 | 526936 YOAKUM_345 345 527896 HOBBS_INT 7 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05173 | 113.76 | 527028 INK_BASIN 6 230 527894 HOBBS_INT 6 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05105 | 113 | 527130 DENVER_N 3 115 527286 HIGGEAST 3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05095 | 112.61 | 527149 MUSTANG 6 230 3WXFMR ENRCO 136161 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05108 | 110.49 | 527149 MUSTANG 6 230 527151 GS-MUSTANG 6 230 @1
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05094 | 112.86 | 527202 SEAGRAVES 3 115 3WXFMR ABB MLL92408 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05094 | 112.76 | 527212 DIAMONDBACK3 115 3WXFMR HOW 36773714 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05094 | 112.68 | 527261 SULPHUR 2 69.0 527271 LG-FOSTER +2 69.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05105 | 112.98 | 527286 HIGGEAST 3 115 527363 HIGG 3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05102 | 112.82 | 527322 GAINES 3 115 527325 OXY_WSEM_TP3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05102 | 112.74 | 527325 OXY_WSEM_TP3 115 527362 JOHNSON_DRW3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05094 | 112.73 | 527340 DOSS 3 115 3WXFMR ELCO 13566/1 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05094 | 112.71 | 527345 LEGACY 2 69.0 527350 XTO_ROBRTSN2 69.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05094 | 112.71 | 527346 LEGACY 3 115 3WXFMR VROL 13735-1 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05094 | 112.69 | 527350 XTO_ROBRTSN2 69.0 527355 BOARDMAN 2 69.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05094 | 112.63 | 527355 BOARDMAN 2 69.0 527365 FLANNAGAN 2 69.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05094 | 112.61 | 527360 MAPCO 3 115 527362 JOHNSON_DRW3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05094 | 112.65 | 527362 JOHNSON_DRW3 115 528775 LE-ERF 3 115 @1
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05096 | 112.39 | 527455 RSWL_SLRCOL3 115 527482 CHAVES_CNTY3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05096 | 112.41 | 527470 CHVS_SLRCOL3 115 527464 CHVS_SOLAR11 34.5 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05096 | 112.34 | 527470 CHVS_SLRCOL3 115 527482 CHAVES_CNTY3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05007 | 112.88 | 527483 CHAVES_CNTY6 230 527799 EDDY_NORTH 6 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05094 | 112.62 | 527508 PRICE 3 115 527509 PRICE_TAP 3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05094 | 112.62 | 527529 RIACBRSH_TP3 115 527533 SW4J795_E 3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05094 | 112.62 | 527533 SW4J795_E 3 115 527564 ROSWLL_INT 3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05094 | 112.62 | 527563 ROSWLL_INT 2 69.0 527575 SW_4702 2 69.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05084 | 112.67 | 527564 ROSWLL_INT 3 115 527597 TWEEDY 3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05094 | 112.62 | 527575 SW_4702 2 69.0 527589 CV-ORCHARD 2 69.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05089 | 112.78 | 527653 MILO_WIND 1 34.5 527655 RSVLT_CC_E 7 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05081 | 112.66 | 527654 RSVLT_CC_W 7 345 527655 RSVLT_CC_E 7 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05081 | 112.95 | 527654 RSVLT_CC_W 7 345 527666 RSVLT_COL1 7 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05077 | 112.86 | 527655 RSVLT_CC_E 7 345 527656 CROSSROADS 7 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05081 | 112.95 | 527666 RSVLT_COL1 7 345 3WXFMR RSVLT_COL1 7 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05094 | 112.36 | 527736 NAVAJO_5TP 3 115 527739 NAVAJO_4 3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05094 | 112.35 | 527864 CUNNINHAM 3 115 528348 BUCKEYE_TP 3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05095 | 112.63 | 527864 CUNNINHAM 3 115 528568 MONUMNT_TP 3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05104 | 112.91 | 527865 CUNNIGHM_N 6 230 527867 CUNNIGHM_S 6 230 *1
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05097 | 112.64 | 527865 CUNNIGHM_N 6 230 527963 POTASH_JCT 6 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05095 | 112.4 | 527867 CUNNIGHM_S 6 230 3WXFMR WH 7000266 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.0509 | 112.86 | 527867 CUNNIGHM_S 6 230 527882 CUNINGHAM2 1 20.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.0509 | 112.79 | 527894 HOBBS_INT 6 230 527903 HOBBS_PLT3 1 18.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05095 | 112.36 | 527965 KIOWA 7 345 528027 RDRUNNER 7 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05094 | 112.36 | 528015 PHANTOM 7 345 528027 RDRUNNER 7 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05094 | 112.41 | 528024 RR_SVC_HV 3 115 528021 RDRUNNR_SVC1 15.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05094 | 112.68 | 528025 RDRUNNER 3 115 587990 GEN-2016-121 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05094 | 112.42 | 528185 N_LOVING 7 345 3WXFMR HYO1063400-1 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05094 | 112.41 | 528185 N_LOVING 7 345 528223 CHINA_DRAW 7 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05094 | 112.36 | 528222 CHINA_DRAW 3 115 528225 CD_SVC_HV 3 115 Z1
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05099 | 112.34 | 528333 LE-WEST_SUB3 115 528334 LE-NRTH_INT3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05094 | 112.42 | 528341 LE-SANANDRS3 115 528627 LE-TXACO_TP3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05094 | 112.38 | 528348 BUCKEYE_TP 3 115 528627 LE-TXACO_TP3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05097 | 112.62 | 528394 QUAHADA 3 115 528396 XTO_BIGEDDY3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05095 | 112.33 | 528463 SANGER_SW 3 115 528575 OXYPERMIAN 3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05095 | 112.33 | 528463 SANGER_SW 3 115 762442 G18-004-TAP 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05095 | 112.63 | 528568 MONUMNT_TP 3 115 528581 BYRD_TP 3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05095 | 112.38 | 528574 OXY_NHU_RCF3 115 528575 OXYPERMIAN 3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05094 | 112.69 | 528617 LE-WAITS 2 69.0 528325 LE-WAITS 3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05094 | 112.61 | 528617 LE-WAITS 2 69.0 528714 LE-FORT_SW 2 69.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05094 | 112.42 | 528622 LE-SANANDRS2 69.0 528341 LE-SANANDRS3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05094 | 112.97 | 528626 LE-PLNSINT 2 69.0 526928 PLAINS_INT 3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05094 | 112.97 | 528626 LE-PLNSINT 2 69.0 528709 LE-PLNSGOAB2 69.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05094 | 112.63 | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05094 | 112.69 | 528669 LE-STKLDRTP2 69.0 528740 LE-PLANS_SW2 69.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05094 | 112.85 | 528709 LE-PLNSGOAB2 69.0 528740 LE-PLANS_SW2 69.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05094 | 112.63 | 528709 LE-PLNSGOAB2 69.0 528747 LE-ALLRED 2 69.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05094 | 112.61 | 528714 LE-FORT_SW 2 69.0 528718 LE-NEWTEX 2 69.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05094 | 112.69 | 528735 LE-PLAINSUB2 69.0 528740 LE-PLANS_SW2 69.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05084 | 112.41 | 530583 POSTROCK7 345 588654 G17-021-TAP 345 2
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05094 | 112.41 | 531213 SANTAFE3 115 531408 PIERCVL3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05067 | 112.33 | 531451 MINGO 7 345 531465 SETAB 7 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05092 | 112.62 | 531501 BUCKNER7 345 531502 CIMRRN 7 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05092 | 112.62 | 531502 CIMRRN 7 345 531503 CIMRRN 1 34.5 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05083 | 112.32 | 531510 HARBNGR3 115 3WXFMR HARBGR345 _1 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05092 | 112.64 | 532663 LEC U5 24.0 532854 LEC U5 6 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05092 | 112.64 | 532853 LAWHILL6 230 532854 LEC U5 6 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05093 | 112.69 | 542951 HAW G5 1 22.0 543665 HAWTHN5 161 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05092 | 112.74 | 542955 LAC G1 1 22.0 542981 LACYGNE7 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05092 | 112.72 | 542956 LAC G2 1 24.0 542981 LACYGNE7 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05091 | 112.76 | 542957 IAT G1 1 24.0 542982 IATAN 7 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05092 | 112.82 | 542962 IAT G2 1 24.5 542982 IATAN 7 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05093 | 112.61 | 542966 WGARDNR5 161 543105 BULLCRK5 161 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05495 | 112.16 | 560022 CRAWFISH_DR 345 762216 G17-151TAP 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05443 | 113.18 | 560022 CRAWFISH_DR 345 762467 G18-015-TAP 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05626 | 113.55 | 560022 CRAWFISH_DR 345 763215 G18-092-TAP 345 2
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05094 | 113.05 | 560252 G10-14 345 560253 G10-14-1 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05094 | 112.78 | 560253 G10-14-1 115 560254 G10-14-SUB1 34.5 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05094 | 112.78 | 560253 G10-14-1 115 560255 G10-14-SUB2 34.5 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05094 | 112.63 | 560581 G06-44-2 34.5 523111 NOVUS1 3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05094 | 112.68 | 560582 G06-44-3 34.5 560577 G06-44 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05094 | 112.66 | 560583 G06-44-4 34.5 560577 G06-44 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05094 | 112.32 | 560757 ASGI13_02_1 69.0 560758 ASGI13_02_2 34.5 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05094 | 112.32 | 560757 ASGI13_02_1 69.0 562731 WHEATLAND 69.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05094 | 112.33 | 560763 ASGI13_03_1 115 560761 ASGI13_03_2 34.5 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05094 | 112.76 | 562015 FIREWHEEL1 34.5 523215 FREWHELCOL17 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05094 | 112.76 | 562016 FIREWHEEL2 34.5 523215 FREWHELCOL17 345 2
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05094 | 112.31 | 562323 AGI1202&1305 115 562324 AGI1202&1305 34.5 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05094 | 112.32 | 562727 LESBIA 115 562728 SANJONTAP 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05094 | 112.32 | 562728 SANJONTAP 115 562729 CAPROCKTAP1 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05094 | 112.32 | 562730 CAPROCKTAP2 69.0 562729 CAPROCKTAP1 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05094 | 112.32 | 562730 CAPROCKTAP2 69.0 562731 WHEATLAND 69.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05094 | 112.72 | 563171 G15082_2 34.5 563170 G15082_1 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05094 | 112.4 | P11:13.8:AEPW:COM1-1
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05094 | 112.41 | P11:13.8:AEPW:COM2-1
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05094 | 112.41 | P11:13.8:AEPW:COM3-1
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05094 | 112.42 | P11:18:AEPW:WELSH1-1
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05094 | 112.42 | P11:18:AEPW:WELSH3-1
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05094 | 112.42 | P11:24:AEPW:PIRKEY 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05094 | 112.39 | P11:24:AEPW:SWS3-1
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05094 | 112.39 | P11:24:AEPW:TURKCOAL
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05111 | 112.7 | P12:138:AEPW-OMPA:DUNCAN-4:OMDUNCN4
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05106 | 112.66 | P12:138:AEPW:112GORE4:SNYDER-4
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05106 | 112.66 | 5841_Dup1
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05103 | 111.96 | 584560 GEN-2015-014 115 584561 G15-014XFMR1 34.5 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05105 | 112.65 | P12:138:AEPW:SANTAFE:DUNCAN-4
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05094 | 112.68 | 587991 G16-121XFMR1 34.5 587990 GEN-2016-121 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05094 | 112.62 | 588480 A16-010_SUB 115 3WXFMR A16-010_SUB 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05111 | 112.7 | P12:138:AEPW:DUNCAN-4:L.E.S.-4
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05094 | 112.06 | 588761 G17-033XFMR1 34.5 588760 GEN-2017-033 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05094 | 112.06 | 588765 G17-033XFMR2 34.5 588760 GEN-2017-033 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05094 | 112.63 | 588861 G17-047XFMR1 34.5 588860 GEN-2017-047 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05071 | 112.2 | P12:138:AEPW:ELKCTY-4:CLINTJC4
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05094 | 112.64 | 589381 G17-100XFMR1 34.5 589380 GEN-2017-100 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05087 | 112.39 | P12:138:AEPW:HOB-JCT4:ELKCTY-4
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05095 | 112.64 | P12:138:AEPW:SHERID4:112GORE4
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05092 | 112.61 | P12:230:AEPW:SWEETWT6:BUFFCK6
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05091 | 112.66 | P12:230:AEPW:SWEETWT6:ROARK6
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.0539 | 114.5 | P12:345:AEPW:L.E.S7:TERRYRD7
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.0539 | 114.49 | P12:345:AEPW:L.E.S7:TERRYRD7
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.0539 | 114.47 | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05737 | 114.61 | P12:345:AEPW-OKGE:L.E.S.-7:GRACMNT7
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05737 | 114.58 | P12:345:AEPW-OKGE:L.E.S.-7:GRACMNT7
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05092 | 112.4 | P12:345:AEPW-OKGE:PITTSB-7:SEMINOL7
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05591 | 115.66 | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05094 | 112.66 | P22:345:AMMO::LABADIE:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05094 | 112.66 | P22:345:AMMO::LABADIE:2
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05094 | 112.66 | P22:345:AMMO::LABADIE:3
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05094 | 112.66 | P22:345:AMMO::LABADIE:4
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05094 | 112.65 | P22:345:AMMO::RUSHISLAND:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05094 | 112.64 | P22:345:AMMO::RUSHISLAND:2
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05095 | 112.41 | P13:138-13.8:AEPW:COMANC-4_#2
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05096 | 112.4 | P13:138-24:AEPW:S.W.S.-4
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05095 | 112.39 | P13:138-24:AEPW:TURK 4
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05109 | 112.63 | P13:138-345:AEPW:L.E.S.-4_#1
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05123 | 112.75 | P13:138-345:AEPW:L.E.S.-4_#2
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05096 | 112.67 | P23:500:EES-EAI:KEO:B4941
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05096 | 112.66 | P23:500:EES-EAI:KEO:B4921
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05094 | 112.61 | P11:26:EES-EAI:INDEP2:1:D401
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05094 | 112.61 | P11:26:EES-EAI:INDEP2:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05094 | 112.61 | P13:500:EES-EAI:INDEP2:MT2
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05095 | 112.65 | P23:500:EES-EAI:INDEP2:B6126
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05094 | 112.64 | P23:500:EES-EAI:PD:INDEP2:LN:FK479
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05092 | 112.61 | P13:230-34.5:AEPW:BUFFCK6
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05091 | 112.67 | P13:230-34.5:AEPW:ROARK6
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05094 | 112.41 | P13:69-13.8:AEPW:COMANC-2
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05094 | 112.66 | P11:024:DPC:ALMA2:6
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05094 | 112.62 | P11:18:ITCM:EMERYGT1:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05094 | 112.63 | P11:18:ITCM:EMERYGT2:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05094 | 112.63 | P11:161:ITCM:MGS CT1:1C
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05094 | 112.63 | P11:161:ITCM:MGS CT2:2C
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05092 | 112.64 | 652537 WHITE 3 345 659286 DEERCREK-BE3 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05092 | 112.64 | 659286 DEERCREK-BE3 345 3WXFMR DEERCRK KU1A 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05094 | 112.63 | 672601 BD 4 230 672306 BD 6G 18.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05094 | 112.63 | 672610 POPLAR 4 230 672310 POPLAR 1G 18.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05094 | 112.63 | 672610 POPLAR 4 230 672311 POPLAR 2G 18.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05094 | 112.62 | 672621 SHAND 4 230 672321 SHAND 1G 18.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05094 | 112.61 | 672649 CODETTE 4 230 672650 NIPAWIN 4 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05094 | 112.62 | 672696 BRADA 4 230 672699 NBEC 4 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05094 | 112.69 | P23:345:MDU::COYOTE::5707-5712-5715::::
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05094 | 112.84 | P23:345:MEC:CBEC 905
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05094 | 112.81 | P23:345:MEC:CBEC 908
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05094 | 112.64 | P23:345:MEC:GDMEC 908
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05094 | 112.74 | P23:345:MEC:RAUN 0180
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05094 | 112.8 | P23:345:MEC:RAUN 0210
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05094 | 112.75 | P23:345:MEC:LOUISA 954
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05094 | 112.75 | P23:345:MEC:LOUISA 964
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05094 | 112.61 | P21:115:XEL:AUTO-SINGLE:CHEMOLT7:LSPOWER7:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05094 | 112.65 | P21:115:XEL:AUTO-SINGLE:COLVILL7:CANONFLSG7:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05094 | 112.61 | P21:115:XEL:AUTO-SINGLE:FARIBALTP7:FARIBALTGEN:Z
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05094 | 112.7 | P21:230:OTP:AUTO-SINGLE:SQBUTTE4:YNG24:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05094 | 112.69 | P23:345:OTP:CENTER 3:3215(1)
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05094 | 112.69 | P23:345:OTP:CENTER 3:3225(1)
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05094 | 112.63 | P12:230:UMZW:# 687 #: FT IN SD. FT-BG1 LINE FAULT
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05094 | 112.63 | P12:230:UMZW:# 3617 #: FT IN SD. FT-BG2 LINE FAULT
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05094 | 111.33 | 760494 GEN-2017-146 230 760498 G17-146-TAP 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05094 | 111.32 | 760495 G17-146-XFM1 34.5 760494 GEN-2017-146 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05094 | 112.05 | 761356 G17-239-XFMR 34.5 761355 GEN-2017-239 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05094 | 112.05 | 761359 G17-239-XFMR 34.5 761355 GEN-2017-239 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05094 | 112.23 | 761797 G17-187XFM1 34.5 761796 GEN-2017-187 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05094 | 112.23 | 761800 G17-187XFM2 34.5 761796 GEN-2017-187 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05094 | 107.16 | 762132 GEN-2017-158 230 763252 G18-099-XFM1 34.5 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05094 | 107.16 | 762132 GEN-2017-158 230 763255 G18-099-XFM2 34.5 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05094 | 107.74 | 762133 G17-158XFM1 34.5 762132 GEN-2017-158 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05094 | 107.74 | 762136 G17-158XFM2 34.5 762132 GEN-2017-158 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05094 | 109.9 | 762216 G17-151TAP 345 762217 GEN-2017-151 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05495 | 113.55 | 762216 G17-151TAP 345 762467 G18-015-TAP 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05094 | 111.85 | 762218 G17-151XFM1 34.5 762217 GEN-2017-151 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05094 | 111.85 | 762221 G17-151XFM2 34.5 762217 GEN-2017-151 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05094 | 111.85 | 762224 G17-151XFM3 34.5 762217 GEN-2017-151 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05094 | 111.85 | 762227 G17-151XFM4 34.5 762217 GEN-2017-151 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05094 | 112.36 | 762438 GEN-2018-004 115 762442 G18-004-TAP 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05094 | 110.89 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05094 | 111.7 | 762461 G18-015-XFM1 34.5 762460 GEN-2018-015 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05094 | 111.7 | 762464 G18-015-XFM2 34.5 762460 GEN-2018-015 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05313 | 113.07 | 762467 G18-015-TAP 345 763215 G18-092-TAP 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05094 | 110.18 | 763087 GEN-2018-073 345 763088 G18-073-XFM1 34.5 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05094 | 111.33 | 763087 GEN-2018-073 345 763091 G18-073-XFM2 34.5 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05094 | 107.16 | 763120 GEN-2018-081 230 763121 G18-081-XFM1 34.5 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05094 | 109.42 | 763120 GEN-2018-081 230 764011 G19-074-XFM1 34.5 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05094 | 109.44 | 763186 GEN-2018-089 230 763187 G18-089-XFM1 34.5 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05094 | 110.21 | 763208 GEN-2018-092 345 763215 G18-092-TAP 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05094 | 111.37 | 763208 GEN-2018-092 345 763220 G18-092-XFM1 34.5 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05094 | 111.37 | 763208 GEN-2018-092 345 763223 G18-092-XFM2 34.5 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05094 | 108.87 | 763241 GEN-2018-097 230 763242 G18-097-XFM1 34.5 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05094 | 109.78 | 763241 GEN-2018-097 230 763296 G18-111-XFM1 34.5 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05094 | 109.14 | 763241 GEN-2018-097 230 763307 G18-112-XFM1 34.5 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05094 | 109.14 | 763241 GEN-2018-097 230 763310 G18-112-XFM2 34.5 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05094 | 108.87 | 763241 GEN-2018-097 230 763395 G18-124-XFM1 34.5 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05094 | 108.87 | 763241 GEN-2018-097 230 763398 G18-124-XFM2 34.5 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05094 | 112.29 | 763318 GEN-2018-115 345 763319 G18-115-XFM1 34.5 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05094 | 112.75 | 763340 GEN-2018-117 230 763341 G18-117-XFM1 34.5 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05094 | 108.51 | 763483 GEN-2019-003 230 763484 G19-003-XFM1 34.5 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05094 | 111.19 | 763483 GEN-2019-003 230 763605 G19-021-XFM1 34.5 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05094 | 111.9 | 763516 GEN-2019-011 345 763517 G19-011-XFM1 34.5 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05094 | 112.26 | 763879 GEN-2019-056 115 763880 G19-056XFM1 34.5 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05065 | 112.68 | P42:345:OKGE:SB_BVTY7305
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05087 | 112.43 | P23:345:WERE:BUFF_345-534::
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05087 | 112.43 | P23:345:WERE:BUFF_345-543::
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05091 | 112.78 | P23:345:WERE:JEC_345-15::
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.0509 | 112.75 | P23:345:WERE:JEC_345-16::
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05091 | 112.78 | P23:345:WERE:JEC_345-19::
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05091 | 112.78 | P23:345:WERE:JEC_345-20::
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05094 | 112.95 | P23:345:WERE:WOLF_345-50::
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05094 | 112.95 | P23:345:WERE:WOLF_345-60::
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05095 | 112.43 | P42:345:AEPW:WELSH CB 10620 NBTB+FAULT
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05591 | 114.21 | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05799 | 114.99 | P42:345:AEPW:LAWTON EASTSIDE CB 3413A NBTB+FAULT
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05864 | 115.4 | P42:345:AEPW:LAWTON EASTSIDE CB 3425A NBTB+FAULT
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05614 | 115.86 | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05115 | 112.31 | P42:345:AEPW:PITTSBURG CB 3441A NBTB+FAULT
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05092 | 112.4 | P42:345:AEPW:PITTSBURG CB 3445A NBTB+FAULT
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.0539 | 114.49 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.0539 | 114.49 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.0539 | 114.47 | P42:345:AEPW:TERRYRD_CB_3421A_NBTB
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05092 | 112.75 | P23:345:KCPL:LACYGNE_R2-5::LACYGU2-LACYGNE-STILWELL
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05095 | 112.43 | P23:345:AEPW:WELSH CB 10620 NBTB
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05591 | 114.54 | P23:345:AEPW:OKLAUNION CB 3401A NBTB
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05799 | 114.99 | P23:345:AEPW:LAWTON EASTSIDE CB 3413A NBTB
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05864 | 115.4 | P23:345:AEPW:LAWTON EASTSIDE CB 3425A NBTB
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05614 | 115.86 | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05115 | 112.31 | P23:345:AEPW:PITTSBURG CB 3441A NBTB
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05092 | 112.4 | P23:345:AEPW:PITTSBURG CB 3445A NBTB
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.0539 | 114.49 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.0539 | 114.49 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.0539 | 114.47 | P23:345:AEPW:TERRYRD_CB_3421A_NBTB
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05144 | 112.62 | P12:138:AEPW:S.W.S.-4:L.E.S.-4
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05094 | 112.65 | P11:115:SUNC:GARDENCITY_S2:97:531459(2)
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05417 | 114.72 | P23:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05837 | 117.32 | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05417 | 114.72 | P42:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB+FAULT
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05837 | 117.32 | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05067 | 112.33 | P23:345:SUNC:MO_BRK182
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05067 | 112.33 | P23:345:SUNC:MO_BRK382
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05092 | 112.42 | P21:345:UMZW:# 725 #: GI IN NE. GI-SWEET LINE FAULT
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05184 | 112.8 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05095 | 112.41 | P12:138-13.8:AEPW:COMANC-4_#1
Thermal | 05ALL | 1 | 23SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05174 | 113.54 | P12:230:AEPW:SWEETWT6:CHISHOLM6
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 511458 ELKCTY-4 138 998036 ELKCTY-6 _1 138 1 |  | 330 | 0.10462 | 112.44 | P12:345:OKGE-AEPW:BKRBKR371::::
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 511458 ELKCTY-4 138 998036 ELKCTY-6 _1 138 1 |  | 330 | 0.10462 | 112.78 | P12:345:OKGE-AEPW:BKRBKR371::::
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.10462 | 108.04 | P12:345:OKGE-AEPW:BKRBKR371::::
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.10462 | 108.6 | P12:345:OKGE-AEPW:BKRBKR371::::
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 511490 ELKCITY6 230 998036 ELKCTY-6 _1 138 1 |  | 330 | 0.10462 | 112.79 | P12:345:OKGE-AEPW:BKRBKR371::::
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 511490 ELKCITY6 230 998036 ELKCTY-6 _1 138 1 |  | 330 | 0.10462 | 113.27 | P12:345:OKGE-AEPW:BKRBKR371::::
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17493 | 112.73 | P23:345:KCPL-WERE:237LACYGNE_R1-6::LACYGU1-LACYGNE-NEOSHO
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.1749 | 112.64 | P11:230:WERE:LECU5_GEN::
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17491 | 112.63 | P11:161:GMO:DOGWOOD_COMBINED_CYCLE_UNIT_OUTAGE_1_1
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17498 | 111.16 | P11:115:SPS:MUSTANG1&3:153MW::::
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17572 | 114.61 | P12:230:SPS:K37::1_TOLK_LAMB:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17511 | 112.61 | P12:230:SPS:K43::1_PRNGLE_HARR_E:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17495 | 112.37 | P12:230:SPS:K44::1_EPLNT_HARRW:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17509 | 112.79 | P12:115:SPS:T04::1_TRBLNC_CASTRO:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.19 | P12:115:SPS:T13::1_TAYLOR_WHOBBS:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.31 | P12:115:SPS:T14::1_MADDOX_TAYLOR:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 113.09 | P12:115:SPS:T21::1_GRSSLND_GRAHAM:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.41 | P12:115:SPS:T23::1_PCA_POTJCT:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.62 | P12:115:SPS:T24B::1_RSWLL_BRSHRF:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17493 | 112.64 | P12:115:SPS:T26::1_CHAVES_RSWLCTY:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17632 | 113.18 | P12:115:SPS:T28A::1_LAMTON_PLANTX:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17549 | 112.67 | P12:115:SPS:T29::1_LAMTON_HALECTR:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17634 | 113.96 | P12:115:SPS:T30::1_LAMB_HOCKLY:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17634 | 113.13 | P12:115:SPS:T31::1_HOCKLY_SUNDWN:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.1749 | 112.63 | P12:115:SPS:T35::1_TERRY_YOAKUM:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 113.32 | P12:115:SPS:T45::1_NORRIS_OASIS:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17493 | 112.4 | P12:115:SPS:T57::1_MUSTG_SEGRVS:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17557 | 113.15 | P12:115:SPS:T59::1_CARGIL_CURRY:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.176 | 112.42 | P12:115:SPS:T66::1_RNDALL_HAPPY:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.176 | 112.9 | P12:115:SPS:T67::1_HAPPY_KRESS:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17497 | 112.39 | P12:115:SPS:T68::1_TUCO_FLOYD:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17486 | 113.2 | P12:115:SPS:T71::1_CRLSLE_YUMA:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17504 | 112.7 | P12:115:SPS:T81::1_COX_FLOYD:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17491 | 112.85 | P12:115:SPS:T83::1_SP-FKFD_ALLEN:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 113.01 | P12:115:SPS:T89::1_DC_N_HIGG:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.66 | P12:115:SPS:T91::1_HIGG_RUSSELL:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17517 | 112.62 | P12:115:SPS:V04::1_EPLANT_RNDALL:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17508 | 112.67 | P12:115:SPS:V07::1_COX_HALECTR:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17628 | 112.95 | P12:115:SPS:V09::1_HALECTR_PLANTX:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17493 | 112.83 | P12:115:SPS:V12::1_PLANTX_BAILEY:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17491 | 112.62 | P12:115:SPS:V15::1_TUCO_INDANA:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17459 | 112.67 | P12:115:SPS:V24::1_WOLFTH_TERRY:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17508 | 112.64 | P12:115:SPS:V26::1_RSWLL_EDDY_N:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.98 | P12:115:SPS:V33::1_LUBBS_LYNN:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17607 | 113.85 | P12:115:SPS:V37::1_CASTRO_PLANTX:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.75 | P12:115:SPS:V46::1_ALLEN_WHEELCK:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17494 | 113.09 | P12:115:SPS:V49::1_YOAKUM_SHLCO2:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17551 | 113.26 | P12:115:SPS:V55::1_SUNDWN_TERRY:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17517 | 113.09 | P12:115:SPS:V56::1_COCHRAN_SUNDWN:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17491 | 112.68 | P12:115:SPS:V62::1_CRLSLE_INDANA:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17493 | 112.62 | P12:115:SPS:V70::1_S_GORG_RNDALL:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17496 | 112.65 | P12:115:SPS:V78::2_CURRY_RSVLT:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17494 | 112.79 | P12:115:SPS:V81::1_LE-WAIT_LE-LVN:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.65 | P12:115:SPS:V95::1_DC_N_SHLCO2:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.61 | P12:115:SPS:W11::1_DC_S_SMINLE:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.61 | P12:115:SPS:W12::1_SMINLE_DOSS:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.68 | P12:115:SPS:W14::1_SMINLE_GAINES:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 113.14 | P12:115:SPS:W32::1_PRMTR_FE-CLSIN:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.61 | P12:115:SPS:W34::1_JNSDRW_MAPCO:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17493 | 112.85 | P12:115:SPS:W35::1_GAINES_JNSDRW:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17493 | 112.64 | P12:115:SPS:W36::1_TAYLOR_JNSDRW:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17714 | 113.15 | P12:115:SPS:W40::1_WCANYON_TRBLNC:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17529 | 112.71 | P12:115:SPS:W52::1_NEWHART_KRESS:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 113.2 | P12:115:SPS:W58::1_NORTON_LOPEZ:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.82 | P12:115:SPS:W59::1_LOPEZ_CMPBLL:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 113.15 | P12:115:SPS:W62::1_PLSTHL_CURRY:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17504 | 112.62 | P12:115:SPS:W63::1_PLSTHL_CURRY:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.96 | P12:115:SPS:W64::1_PLSTHL_FE-CLV:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 113.12 | P12:115:SPS:W65::1_PLSTHL_CURRY:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.81 | P12:115:SPS:W66::1_PORTA_GREYHUND:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17714 | 112.61 | P12:115:SPS:W77::1_RNDAL_WCANYON:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.64 | P12:115:SPS:W99::1_CAPITAN_CHAVES:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17491 | 113.08 | P12:115:SPS:U14::1_DC_STH_INKBSN:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17494 | 113.02 | P12:115:SPS:V15::1_INKBSN_LE-WAT:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17519 | 112.74 | P12:115:SPS:U16::1_BSHLND_OUTPST:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17519 | 112.73 | P12:115:SPS:U17::1_COLTR_OUTPST:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.1751 | 112.8 | P12:115:SPS:U19::1_DEAN_PLAINS:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17519 | 112.67 | P12:115:SPS:U23::1_COLTR_HILSDE:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.16753 | 119.61 | P42:345:SPS:YOAKUM:J18####:SLG1:EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.16753 | 119.61 | P43:345:SPS:YOAKUM:TF#####:SLG:EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.16753 | 119.61 | P42:345:SPS:YOAKUM:J17####:SLG:EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.16753 | 119.61 | P42:345:SPS:YOAKUM:J18####:SLG2:EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17491 | 112.62 | P11:18:HAST:::EGYCTR2G WEC2_LOSS OF WEC 2 GEN_:HV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17491 | 112.62 | P13:18-115:HAST:::EGYCNTR7 XFMR G2WEC 2 GSU_:HV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17491 | 112.63 | P11:161:GMO:DOGWOOD-COMBINED-CYCLE-UNIT-OUTA:::HV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17493 | 112.73 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.1749 | 112.75 | P23:345:KCPL:LACYGNE-R2-5:::EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17488 | 112.78 | P11:230:WERE:JECU1-GEN:::HV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.1749 | 112.64 | P11:230:WERE:LECU5-GEN:::HV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17488 | 112.78 | P11:345:WERE:JECU2-GEN:::EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17488 | 112.78 | P11:345:WERE:JECU3-GEN:::EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.95 | P11:345:WERE:WOLFU1-GEN:::EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17484 | 112.43 | P23:345:WERE:BUFF-345-534:::EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17484 | 112.43 | P23:345:WERE:BUFF-345-543:::EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17488 | 112.78 | P23:345:WERE:JEC-345-15:::EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17487 | 112.75 | P23:345:WERE:JEC-345-16:::EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17488 | 112.78 | P23:345:WERE:JEC-345-19:::EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17488 | 112.78 | P23:345:WERE:JEC-345-20:::EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.95 | P23:345:WERE:WOLF-345-50:::EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.95 | P23:345:WERE:WOLF-345-60:::EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.89 | P11:022:NPPD:COOPER1G:1:983:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17487 | 112.92 | P11:023:NPPD:GENTLM1G:1:757:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17487 | 112.94 | P11:024:NPPD:GENTLM2G:2:757:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17489 | 112.75 | P13:345:OPPD:NEBCTY1G:::EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17487 | 112.78 | P13:345:OPPD:NEBCTY2G:::EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.77 | P22:345:OPPD:S3458 NEBCTY1G:LT::EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17489 | 112.75 | P22:345:OPPD:S3458 NEBCTY1G:::EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.81 | P22:345:OPPD:S3458 NEBCTY2G:LT::EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17487 | 112.78 | P22:345:OPPD:S3458 NEBCTY2G:::EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.77 | P23:345:OPPD:S3458 NEBCTY1G:LT::EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17489 | 112.75 | P23:345:OPPD:S3458 NEBCTY1G:::EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.81 | P23:345:OPPD:S3458 NEBCTY2G:LT::EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17487 | 112.78 | P23:345:OPPD:S3458 NEBCTY2G:::EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.4 | P12:115:SUNC:PLYMELL-PIERCEVILLE:::HV::
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.1749 | 112.64 | P11:018:UMZB:# 5 #:: DCS IN SD. DEERCREEK_MV::
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17491 | 112.61 | P11:022:UMZB:# 15 #:: LO IN ND. LELAND OLDS 1_MV::
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.1749 | 112.65 | P11:020:UMZB:# 16 #:: LO IN ND. LELAND OLDS 2_MV::
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.1749 | 112.7 | P11:023:UMZB:# 31 #:: AVS IN ND. ANTELOPE VALLEY 1_MV::
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.1749 | 112.7 | P11:023:UMZB:# 32 #:: AVS IN ND. ANTELOPE VALLEY 2_MV::
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17486 | 112.9 | P11:024:UMZB:# 33 #:: LRS IN WY. LARAMIE RIVER STATION 1_MV::
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.63 | P12:230:UMZW:# 687 #:: FT IN SD. FT-BG1 BRANCH FAULT:HV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.63 | P12:230:UMZW:# 3617 #:: FT IN SD. FT-BG2 BRANCH FAULT:HV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.63 | P12:230:UMZW:# 4038 #:: BG-FT IN SD. FAULT FOR TRANSMISSION CIRCUIT (BG-FT).:HV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.63 | P12:230:UMZW:# 4039 #:: BG-FT IN SD. FAULT FOR TRANSMISSION CIRCUIT (BG-FT).:HV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.61 | P13:230:UMZW:# 5135 #:: OA IN SD. FAULT ON TRANSFORMER (2).:HV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.61 | P13:230:UMZW:# 5136 #:: OA IN SD. FAULT ON TRANSFORMER (3).:HV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17489 | 112.42 | P21:345:UMZW:# 725 #:: GI IN NE. GI-SWEET BRANCH FAULT:EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17489 | 112.42 | P23:345:UMZW:# 2430 #:: GI IN NE. GI 1492 BKR FAULT:EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17489 | 112.42 | P23:345:UMZW:# 2438 #:: GI IN NE. GI-SWEET BRANCH FAULT & GI 1492 STUCK BKR:EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17494 | 112.37 | P11:138:WFEC:HUGO1:465MW :::
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17488 | 112.4 | P12:345:OKGE-AEPW:BKRBKR20::::
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17528 | 112.75 | P12:345:OKGE:BKRBKR21::::
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17546 | 112.95 | P12:345:OKGE:BKRBKR24::::
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17734 | 114.47 | P12:345:OKGE-AEPW:BKRBKR25::::
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17482 | 112.42 | P12:345:OKGE:BKRBKR336::::
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17482 | 112.41 | P12:345:OKGE:BKRBKR336_2::::
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17799 | 114.61 | P12:345:OKGE-AEPW:BKRBKR366::::
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17799 | 114.58 | P12:345:OKGE-AEPW:BKRBKR366::::
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17547 | 112.87 | P12:345:OKGE:BKRBKR367::::
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17523 | 112.62 | P12:345:OKGE-WFEC:BKRBKR374::::
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.1745 | 112.22 | P12:345:OKGE:BKRBKR4193::::
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.1745 | 112.22 | P12:345:OKGE:BKRBKR4194::::
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17434 | 112.28 | P12:345:OKGE-SPS:BKRBKR4201::::
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17434 | 112.28 | P12:345:OKGE-SPS:BKRBKR4202::::
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17481 | 112.35 | P12:345:OKGE:BKRBKR443NEW::::
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17481 | 112.35 | P12:345:OKGE:BKRBKR443NEW2::::
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17486 | 112.88 | P12:345:OKGE:BKRBKR604::::
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17485 | 112.94 | P12:345:OKGE:BKRBKR604_2::::
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17443 | 112.62 | P42:345:OKGE:SB_ARIA7381::::
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.18278 | 116.05 | P42:345:OKGE:SB_BVTY7387::::
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17527 | 112.68 | P42:345:OKGE:SB_SPCK7383::::
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.1749 | 112.64 | P11:115:SUNC:GARDENCITY_S2:103:531459(2):HV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.1749 | 112.64 | P11:115:SUNC:FORTDDODGE_4:157:539670(4):HV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.62 | P11:345:599:CIMARRON1WIND:200:531603(1):EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.92 | P13:115:SUNC:HOLCOMB_GSU:::HV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.1749 | 112.64 | P13:115:SUNC:S2_GSU:::HV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.1749 | 112.64 | P13:115:SUNC:FORTDODGE_GSU:::HV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.1749 | 112.62 | P23:345:SUNC:BU_BRK682:::EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.71 | 300003 1THLG3 24.0 301503 7THOMHLGSU3 345 3
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.71 | 300049 7THOMHL 345 301503 7THOMHLGSU3 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.66 | P11:20:AMMO:1LAB�� G1:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.66 | P11:20:AMMO:1LAB�� G2:2
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.83 | P11:345:AMMO::CALLAWAY:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.66 | P11:345:AMMO::LABADIE:3
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.66 | P11:345:AMMO::LABADIE:4
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.66 | P11:345:AMMO::RUSHISLAND:U1
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.66 | P11:345:AMMO::RUSHISLAND:U2
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.64 | P11:138:AMMO::SIOUX:2
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.64 | P12:765:AEP:AEP ROCKP-AEP JEFF 765
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.61 | P11:HV:EES::1ISES U1:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.61 | P11:EHV:EES::1ISES U2:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.42 | P11:HV:EES::PIRKEY 1:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.42 | P11:EHV:EES::WELSH3-1:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.39 | P11:HV:EES::TURKCOAL:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.61 | P12:HV:EES::5ISES%:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.61 | P12:EHV:EES::8ISES%:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.82 | P12:EHV:EES::7CALAWY 1:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17493 | 112.39 | P12:HV:EES::TURK 4%:1(1)
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.64 | 344011 7HUGHES 345 344012 7HPW-N 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.66 | 344884 7LABADIE1 345 344894 1LAB G1 20.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.66 | 344885 7LABADIE2 345 344895 1LAB G2 20.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.66 | 344886 7LABADIE3 345 344896 1LAB G3 20.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.66 | 344887 7LABADIE4 345 344897 1LAB G4 20.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.65 | 345667 7RUSH 1 345 345670 1RUSH G1 18.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.65 | 345668 7RUSH 2 345 345671 1RUSH G2 18.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.64 | 345755 4SIOUX 1 138 345756 1SIOUX 1 18.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.64 | 345764 4SIOUX 2 138 345765 1SIOUX 2 18.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.69 | P12:345:MDU::CENTER:COYOTE:1::::
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.69 | P13:345:MDU:COYOTE GSU LOSS:COYOTE::1::::
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.61 | P11:345:MEC:GDMEC CT1
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.61 | P11:345:MEC:GDMEC CT2
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.71 | P11:345:MEC:GDMEC ST
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.9 | P11:345:MEC-NPPD:COOPER 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.8 | P11:24:XEL:AUTO-SINGLE:SHERC31G:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.8 | P11:24:XEL:AUTO-SINGLE:SHERC32G:2
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.87 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.73 | P11:20:XEL:AUTO-SINGLE:PRIS31G:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.73 | P11:20:XEL:AUTO-SINGLE:PRIS32G:2
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.76 | P11:22:XEL:AUTO-SINGLE:MNTCE31G:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.73 | P11:20:XEL:AUTO-SINGLE:KING31G:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.77 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.77 | P11:22:GRE:AUTO-SINGLE:GRE-COAL42G:2
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.71 | P11:24:OTP:AUTO-SINGLE:BIGSTN1G:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.71 | P11:20:OTP:AUTO-SINGLE:CENTER2G:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.63 | P11:22:OTP:AUTO-SINGLE:CENTER1G:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.7 | P11:24:OTP:AUTO-SINGLE:COYOTE1G:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.63 | P11:24:DPC:AUTO-SINGLE:GENOA53G:3
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.61 | P12:115:XEL:AUTO-SINGLE:CHEMOLT7:LSPOWER7:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.65 | P12:115:XEL:AUTO-SINGLE:COLVILL7:CANONFLSG7:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.61 | P12:115:XEL:AUTO-SINGLE:FARIBALTP7:FARIBALTGEN:Z
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.7 | P12:230:OTP:AUTO-SINGLE:SQBUTTE4:YNG24:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.78 | P13:24-345:XEL:AUTO-SINGLE:SHERC31G:SHERCO3:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.78 | P13:24-345:XEL:AUTO-SINGLE:SHERC32G:SHERCO3:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.85 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.73 | P13:20-345:XEL:AUTO-SINGLE:PRIS31G:PRISLD3:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.73 | P13:20-345:XEL:AUTO-SINGLE:PRIS32G:PRISLD3:2
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.76 | P13:22-345:XEL:AUTO-SINGLE:MNTCE31G:MNTCELO3:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.72 | P13:20-345:XEL:AUTO-SINGLE:KING31G:ASKING3:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.76 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL41G:GRE-COALCR4:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.75 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL42G:GRE-COALCR4:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.7 | P13:230-24:OTP:AUTO-SINGLE:BIGSTON4:BIGSTN1G:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.7 | P13:20-230:OTP:AUTO-SINGLE:CENTER2G:YNG24:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.62 | P13:22-230:OTP:AUTO-SINGLE:CENTER1G:CENTER4:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.69 | P13:24-345:OTP:AUTO-SINGLE:COYOTE1G:COYOTE3:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.63 | P13:24-161:DPC:AUTO-SINGLE:GENOA53G:GENOA5:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.64 | P13:24-161:DPC:AUTO-SINGLE:JPM:ALMA5:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.7 | P11:115:XEL:RIV COMBINE CYCLE
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.62 | P12:115:XEL:BDS #2 5
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.62 | P11:115:XEL:HBR #6
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.62 | P11:115:XEL:HBR #7
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.73 | P11:115:XEL:HBR #6 7 8
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.73 | P23:345:XEL:8H14 PRI
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.73 | P23:345:XEL:8H17 PRI AS
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.85 | P23:345:XEL:8N28 SHC
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.78 | P23:345:XEL:8N22 SHC
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.78 | P23:345:XEL:8N17 SHC
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.77 | P23:345:XEL:8N8 MNN
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.72 | P23:345:XEL:8P1 KING
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.72 | P23:345:XEL:8P2 KING
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.62 | P23:115:XEL:5P147 IVH AS
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.61 | P11:18:ALTW:AUTO-SINGLE:EMERYST1:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.61 | P11:22:ALTW:AUTO-SINGLE:LANS54G:4
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.74 | P11:22:ALTW:AUTO-SINGLE:ARNOLD1G:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.77 | P11:24:ALTW:AUTO-SINGLE:OTTUMW1G:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.61 | P13:18-161:ALTW:AUTO-SINGLE:EMERYST1:EMERY5:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.61 | P13:22-161:ALTW:AUTO-SINGLE:LANS54G:LANSINGL15:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.73 | P13:22-161:ALTW:AUTO-SINGLE:ARNOLD1G:ARNOLD5:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.76 | P13:24-161:ALTW:AUTO-SINGLE:OTTUMW1G:OTTUMWA5:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.82 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.88 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.75 | P11:22:MEC:AUTO-SINGLE:NEAL3G:3
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.81 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.76 | P11:24:MEC:AUTO-SINGLE:LOUIS31G:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.81 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.84 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.74 | P13:345-22:MEC:AUTO-SINGLE:RAUN3:NEAL3G:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.8 | P13:345-24:MEC:AUTO-SINGLE:RAUN3:NEAL4G:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.74 | P13:345-24:MEC:AUTO-SINGLE:LOUISA3:LOUIS31G:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17488 | 112.78 | P11:230:WERE:JECU1_GEN::
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17488 | 112.78 | P11:345:WERE:JECU2_GEN::
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17488 | 112.78 | P11:345:WERE:JECU3_GEN::
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.95 | P11:345:WERE:WOLFU1_GEN::
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17493 | 112.63 | 511435 SNYDER-4 138 588779 TAP_G17-036 138 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17466 | 112.38 | 511446 CL-AFTP4 138 511458 ELKCTY-4 138 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17466 | 112.4 | 511446 CL-AFTP4 138 511463 HOB-JCT4 138 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.175 | 112.63 | 511453 DUNCAN-4 138 511552 DUNCHERTP4 138 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.175 | 112.62 | 511455 D.E.S.-4 138 511552 DUNCHERTP4 138 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.175 | 112.62 | 511455 D.E.S.-4 138 529344 OMDUNE-4 138 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.63 | 511456 O.K.U.-7 345 511565 OKLAUN HVDC7 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 111.6 | 511456 O.K.U.-7 345 588760 GEN-2017-033 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17807 | 114.54 | 511456 O.K.U.-7 345 763215 G18-092-TAP 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17821 | 115.11 | 511468 L.E.S.-7 345 762467 G18-015-TAP 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17715 | 114.48 | 511468 L.E.S.-7 345 763215 G18-092-TAP 345 2
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.29 | 511468 L.E.S.-7 345 763318 GEN-2018-115 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17493 | 112.66 | 511488 112GORE4 138 511510 LAIRGST4 138 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17504 | 112.7 | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17493 | 112.65 | 511500 CACHE4 138 511510 LAIRGST4 138 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17493 | 112.64 | 511500 CACHE4 138 588779 TAP_G17-036 138 2
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17659 | 112.8 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.75 | 511541 SWEETWT6 230 763340 GEN-2018-117 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17025 | 109.9 | 511553 CHISHOLM7 345 523961 POTTER_CO 7 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17025 | 109.9 | 511553 CHISHOLM7 345 523961 POTTER_CO 7 345 2
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.18278 | 116.03 | 515375 WWRDEHV7 345 515458 BORDER 7 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.18278 | 116.05 | 515458 BORDER 7 345 560022 CRAWFISH_DR 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17489 | 112.7 | 515618 BALKOW 7 345 3WXFMR BALKOW 7 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17489 | 112.7 | 515618 BALKOW 7 345 3WXFMR BALKOW 7 1_Dup1
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17485 | 112.95 | 515634 PALDR1W7 345 3WXFMR PALO2 _1 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.7 | 515677 BADGER 7 345 563170 G15082_1 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17485 | 112.61 | 520827 BINGERJ4 138 521017 ONEY 4 138 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17485 | 112.62 | 521017 ONEY 4 138 521089 WASHITA4 138 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.61 | 522800 MU-TULIA 3 115 525179 TULIA_TP 3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.75 | 522892 MU-BROWNFLD2 69.0 526761 BROWNFLD_TP2 69.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.64 | 523090 TEXAS_CNTY 3 115 589380 GEN-2017-100 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17487 | 112.78 | 523093 HITCHLAND 3 115 523174 GOODWELLWND3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.95 | 523097 HITCHLAND 7 345 523112 NOVUS1 7 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 113 | 523097 HITCHLAND 7 345 523215 FREWHELCOL17 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17264 | 111.48 | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.15856 | 109.07 | 523097 HITCHLAND 7 345 523961 POTTER_CO 7 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 113.05 | 523097 HITCHLAND 7 345 560252 G10-14 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.62 | 523099 TC-DRYTRLS 3 115 588480 A16-010_SUB 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.82 | 523112 NOVUS1 7 345 3WXFMR NOVUS XF2 2
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.63 | 523112 NOVUS1 7 345 3WXFMR XIANA2011198 _1 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.1749 | 112.61 | 523118 BUFF_DUNES 7 345 523853 FINNEY 7 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.63 | 523120 COLE 3 115 588860 GEN-2017-047 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.1749 | 112.64 | 523172 GWELL_COLL11 34.5 523174 GOODWELLWND3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.1749 | 112.65 | 523173 GWELL_COLL21 34.5 523174 GOODWELLWND3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17511 | 112.61 | 523267 PRINGLE 6 230 3WXFMR ENRCO13617-1 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17511 | 112.61 | 523267 PRINGLE 6 230 523979 HARRNG_EST 6 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17585 | 113.07 | 523771 GRAPEVINE 6 230 524044 NICHOLS 6 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.18497 | 113.75 | 523959 POTTER_CO 6 230 524267 BUSHLAND 6 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.18447 | 114.67 | 523959 POTTER_CO 6 230 525461 NEWHART 6 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.18369 | 118.42 | 523961 POTTER_CO 7 345 3WXFMR WAUK 90343-A 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17495 | 112.4 | 523978 HARRNG_MID 6 230 523979 HARRNG_EST 6 230 @1
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.39 | 524010 ROLLHILLS 6 230 3WXFMR WAUK WT01104 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17519 | 112.74 | 524267 BUSHLAND 6 230 3WXFMR WH 7001795 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.19279 | 114.31 | 524267 BUSHLAND 6 230 524623 DEAFSMITH 6 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17479 | 113.07 | 524296 SPNSPUR_WND7 345 524299 SPNSPUR_COL7 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17479 | 113.07 | 524299 SPNSPUR_COL7 345 3WXFMR SPNSPUR_COL7 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17927 | 113.32 | 524415 AMA_SOUTH 6 230 525213 SWISHER 6 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 113.2 | 524502 NORTON 3 115 524509 FE-TUCMCARI3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17714 | 113.01 | 524575 DS-#25+ 3 115 524597 PANDAHFD 3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17714 | 113.12 | 524575 DS-#25+ 3 115 524630 TIERABLANCA3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.7 | 524604 HEREFRD_SB 2 69.0 524608 HERFRD_STH 2 69.0 *1
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.19287 | 119.12 | 524623 DEAFSMITH 6 230 760498 G17-146-TAP 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 113.1 | 524721 DS-#15&#19+2 69.0 524745 CASTRO_CNTY2 69.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17494 | 112.61 | 524770 PLSNT_HILL 6 230 3WXFMR EFAE1100068A 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17893 | 117.92 | 524875 OASIS 6 230 524885 SN_JUAN_TAP6 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17544 | 113.69 | 524875 OASIS 6 230 524909 ROOSEVELT 6 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17884 | 118.38 | 524885 SN_JUAN_TAP6 230 527483 CHAVES_CNTY6 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17497 | 112.8 | 524909 ROOSEVELT 6 230 3WXFMR ABB LMM60042 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17876 | 118.36 | 524909 ROOSEVELT 6 230 525531 TOLK 6 230 2
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 113.33 | 524923 PORTALES 2 69.0 524929 RO-PORT_MTR2 69.0 @1
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 113 | 525001 W_MULESHOE 2 69.0 525008 MULESH_CTY 2 69.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 113 | 525008 MULESH_CTY 2 69.0 525027 BAILEYCO 2 69.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 113.28 | 525023 BC-BAIL_MTR2 69.0 525027 BAILEYCO 2 69.0 @1
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17607 | 113.27 | 525056 BC-EARTH 3 115 525480 PLANT_X 3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 113.09 | 525191 KRESS_INT 2 69.0 525203 SW-KRESS 2 69.0 Z1
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 113.17 | 525192 KRESS_INT 3 115 3WXFMR ENRCO 136155 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17903 | 113.6 | 525213 SWISHER 6 230 525461 NEWHART 6 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.73 | 525272 KISER 3 115 3WXFMR VON 13819/1 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 113.19 | 525326 COX 3 115 3WXFMR ELCO 13474-3 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 113.21 | 525414 LAMTON 3 115 3WXFMR ASEA MLL9204 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17632 | 113.03 | 525440 LC-S_OLTON+3 115 525446 RKYFORD_TP 3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17632 | 113.03 | 525446 RKYFORD_TP 3 115 525480 PLANT_X 3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.19686 | 116.34 | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.18 | 114.35 | 525481 PLANT_X 6 230 3WXFMR WH ALM20171 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.19039 | 118.3 | 525481 PLANT_X 6 230 526435 SUNDOWN 6 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.19287 | 117.38 | 525481 PLANT_X 6 230 760498 G17-146-TAP 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.16851 | 113.07 | 525481 PLANT_X 6 230 762174 G17-218TAP 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.16772 | 113.14 | 525481 PLANT_X 6 230 762174 G17-218TAP 230 2
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.18345 | 118.38 | 525531 TOLK 6 230 525586 NEEDMORE 6 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17572 | 114.61 | 525531 TOLK 6 230 525637 LAMB_CNTY 6 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.1986 | 118.52 | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.16543 | 113.33 | 525531 TOLK 6 230 762174 G17-218TAP 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.16478 | 113.39 | 525531 TOLK 6 230 762174 G17-218TAP 230 2
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.18345 | 118.36 | 525586 NEEDMORE 6 230 526935 YOAKUM 6 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 113.01 | 525599 LC-SANDHLL+2 69.0 525606 AMHERST 2 69.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 113.04 | 525606 AMHERST 2 69.0 525613 W_LITTLFLD 2 69.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 113.07 | 525613 W_LITTLFLD 2 69.0 525635 LAMB_CNTY 2 69.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 113.02 | 525635 LAMB_CNTY 2 69.0 525650 LC-LTTLFLD+2 69.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17572 | 114.61 | 525637 LAMB_CNTY 6 230 3WXFMR WH ALM20172 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.87 | 525828 TUCO_INT 3 115 3WXFMR DS F78800913 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17504 | 112.4 | 525830 TUCO_INT 6 230 3WXFMR ENRCO 136401 2
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.16731 | 114.37 | 525832 TUCO_INT 7 345 526936 YOAKUM_345 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 113.07 | 526086 SW_6786_N 2 69.0 526087 SW_6786_S 2 69.0 Z1
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 113.07 | 526086 SW_6786_N 2 69.0 526102 SP-HETTLER 2 69.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 113.14 | 526087 SW_6786_S 2 69.0 526284 PLANTERS 2 69.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.69 | 526160 CARLISLE 3 115 3WXFMR WH RLP38371 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 113.03 | 526195 QUINCY 3 115 526196 SP-MILWAUKEE 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.93 | 526268 LUBBCK_STH 3 115 3WXFMR NA 70454A 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 113.19 | 526284 PLANTERS 2 69.0 526297 LUBBCK_EST 2 69.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17495 | 112.63 | 526435 SUNDOWN 6 230 3WXFMR UPDATE LATER _12 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17703 | 115 | 526435 SUNDOWN 6 230 526460 AMOCO_SS 6 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17491 | 112.65 | 526525 WOLFFORTH 6 230 3WXFMR UPDATE LATER _13 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 113.07 | 526735 TERRY_CNTY 2 69.0 526747 LG-BROWNFLD2 69.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 113 | 526747 LG-BROWNFLD2 69.0 526754 BROWNFIELD 2 69.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17506 | 114.41 | 526935 YOAKUM 6 230 527028 INK_BASIN 6 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.16868 | 121.79 | 526936 YOAKUM_345 345 527896 HOBBS_INT 7 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17504 | 113.76 | 527028 INK_BASIN 6 230 527894 HOBBS_INT 6 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 113 | 527130 DENVER_N 3 115 527286 HIGGEAST 3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.61 | 527149 MUSTANG 6 230 3WXFMR ENRCO 136161 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17506 | 110.49 | 527149 MUSTANG 6 230 527151 GS-MUSTANG 6 230 @1
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.86 | 527202 SEAGRAVES 3 115 3WXFMR ABB MLL92408 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.76 | 527212 DIAMONDBACK3 115 3WXFMR HOW 36773714 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.68 | 527261 SULPHUR 2 69.0 527271 LG-FOSTER +2 69.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.98 | 527286 HIGGEAST 3 115 527363 HIGG 3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17493 | 112.82 | 527322 GAINES 3 115 527325 OXY_WSEM_TP3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17493 | 112.74 | 527325 OXY_WSEM_TP3 115 527362 JOHNSON_DRW3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.73 | 527340 DOSS 3 115 3WXFMR ELCO 13566/1 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.71 | 527345 LEGACY 2 69.0 527350 XTO_ROBRTSN2 69.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.71 | 527346 LEGACY 3 115 3WXFMR VROL 13735-1 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.69 | 527350 XTO_ROBRTSN2 69.0 527355 BOARDMAN 2 69.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.63 | 527355 BOARDMAN 2 69.0 527365 FLANNAGAN 2 69.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.61 | 527360 MAPCO 3 115 527362 JOHNSON_DRW3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.65 | 527362 JOHNSON_DRW3 115 528775 LE-ERF 3 115 @1
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17494 | 112.39 | 527455 RSWL_SLRCOL3 115 527482 CHAVES_CNTY3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17494 | 112.41 | 527470 CHVS_SLRCOL3 115 527464 CHVS_SOLAR11 34.5 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17494 | 112.34 | 527470 CHVS_SLRCOL3 115 527482 CHAVES_CNTY3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17661 | 112.88 | 527483 CHAVES_CNTY6 230 527799 EDDY_NORTH 6 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.62 | 527508 PRICE 3 115 527509 PRICE_TAP 3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.62 | 527529 RIACBRSH_TP3 115 527533 SW4J795_E 3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.62 | 527533 SW4J795_E 3 115 527564 ROSWLL_INT 3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.62 | 527563 ROSWLL_INT 2 69.0 527575 SW_4702 2 69.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17508 | 112.67 | 527564 ROSWLL_INT 3 115 527597 TWEEDY 3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.62 | 527575 SW_4702 2 69.0 527589 CV-ORCHARD 2 69.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17487 | 112.78 | 527653 MILO_WIND 1 34.5 527655 RSVLT_CC_E 7 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17479 | 112.66 | 527654 RSVLT_CC_W 7 345 527655 RSVLT_CC_E 7 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17479 | 112.95 | 527654 RSVLT_CC_W 7 345 527666 RSVLT_COL1 7 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17475 | 112.86 | 527655 RSVLT_CC_E 7 345 527656 CROSSROADS 7 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17479 | 112.95 | 527666 RSVLT_COL1 7 345 3WXFMR RSVLT_COL1 7 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.36 | 527736 NAVAJO_5TP 3 115 527739 NAVAJO_4 3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.35 | 527864 CUNNINHAM 3 115 528348 BUCKEYE_TP 3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.63 | 527864 CUNNINHAM 3 115 528568 MONUMNT_TP 3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17479 | 112.91 | 527865 CUNNIGHM_N 6 230 527867 CUNNIGHM_S 6 230 *1
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17488 | 112.64 | 527865 CUNNIGHM_N 6 230 527963 POTASH_JCT 6 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17491 | 112.4 | 527867 CUNNIGHM_S 6 230 3WXFMR WH 7000266 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17487 | 112.86 | 527867 CUNNIGHM_S 6 230 527882 CUNINGHAM2 1 20.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17488 | 112.79 | 527894 HOBBS_INT 6 230 527903 HOBBS_PLT3 1 18.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17491 | 112.36 | 527965 KIOWA 7 345 528027 RDRUNNER 7 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.36 | 528015 PHANTOM 7 345 528027 RDRUNNER 7 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.41 | 528024 RR_SVC_HV 3 115 528021 RDRUNNR_SVC1 15.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.68 | 528025 RDRUNNER 3 115 587990 GEN-2016-121 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.42 | 528185 N_LOVING 7 345 3WXFMR HYO1063400-1 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.41 | 528185 N_LOVING 7 345 528223 CHINA_DRAW 7 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.36 | 528222 CHINA_DRAW 3 115 528225 CD_SVC_HV 3 115 Z1
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.34 | 528333 LE-WEST_SUB3 115 528334 LE-NRTH_INT3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.42 | 528341 LE-SANANDRS3 115 528627 LE-TXACO_TP3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.38 | 528348 BUCKEYE_TP 3 115 528627 LE-TXACO_TP3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17489 | 112.62 | 528394 QUAHADA 3 115 528396 XTO_BIGEDDY3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.33 | 528463 SANGER_SW 3 115 528575 OXYPERMIAN 3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.33 | 528463 SANGER_SW 3 115 762442 G18-004-TAP 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.63 | 528568 MONUMNT_TP 3 115 528581 BYRD_TP 3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.38 | 528574 OXY_NHU_RCF3 115 528575 OXYPERMIAN 3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.69 | 528617 LE-WAITS 2 69.0 528325 LE-WAITS 3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.61 | 528617 LE-WAITS 2 69.0 528714 LE-FORT_SW 2 69.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.42 | 528622 LE-SANANDRS2 69.0 528341 LE-SANANDRS3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.97 | 528626 LE-PLNSINT 2 69.0 526928 PLAINS_INT 3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.97 | 528626 LE-PLNSINT 2 69.0 528709 LE-PLNSGOAB2 69.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.63 | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.69 | 528669 LE-STKLDRTP2 69.0 528740 LE-PLANS_SW2 69.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.85 | 528709 LE-PLNSGOAB2 69.0 528740 LE-PLANS_SW2 69.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.63 | 528709 LE-PLNSGOAB2 69.0 528747 LE-ALLRED 2 69.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.61 | 528714 LE-FORT_SW 2 69.0 528718 LE-NEWTEX 2 69.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.69 | 528735 LE-PLAINSUB2 69.0 528740 LE-PLANS_SW2 69.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17481 | 112.41 | 530583 POSTROCK7 345 588654 G17-021-TAP 345 2
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.41 | 531213 SANTAFE3 115 531408 PIERCVL3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17461 | 112.33 | 531451 MINGO 7 345 531465 SETAB 7 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.1749 | 112.62 | 531501 BUCKNER7 345 531502 CIMRRN 7 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.1749 | 112.62 | 531502 CIMRRN 7 345 531503 CIMRRN 1 34.5 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17478 | 112.32 | 531510 HARBNGR3 115 3WXFMR HARBGR345 _1 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.1749 | 112.64 | 532663 LEC U5 24.0 532854 LEC U5 6 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.1749 | 112.64 | 532853 LAWHILL6 230 532854 LEC U5 6 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17491 | 112.69 | 542951 HAW G5 1 22.0 543665 HAWTHN5 161 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.1749 | 112.74 | 542955 LAC G1 1 22.0 542981 LACYGNE7 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.1749 | 112.72 | 542956 LAC G2 1 24.0 542981 LACYGNE7 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17489 | 112.76 | 542957 IAT G1 1 24.0 542982 IATAN 7 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.1749 | 112.82 | 542962 IAT G2 1 24.5 542982 IATAN 7 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17491 | 112.61 | 542966 WGARDNR5 161 543105 BULLCRK5 161 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17746 | 112.16 | 560022 CRAWFISH_DR 345 762216 G17-151TAP 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17714 | 113.18 | 560022 CRAWFISH_DR 345 762467 G18-015-TAP 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 108.98 | 560022 CRAWFISH_DR 345 763087 GEN-2018-073 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17829 | 113.55 | 560022 CRAWFISH_DR 345 763215 G18-092-TAP 345 2
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 113.05 | 560252 G10-14 345 560253 G10-14-1 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.78 | 560253 G10-14-1 115 560254 G10-14-SUB1 34.5 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.78 | 560253 G10-14-1 115 560255 G10-14-SUB2 34.5 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.63 | 560581 G06-44-2 34.5 523111 NOVUS1 3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.68 | 560582 G06-44-3 34.5 560577 G06-44 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.66 | 560583 G06-44-4 34.5 560577 G06-44 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.32 | 560757 ASGI13_02_1 69.0 560758 ASGI13_02_2 34.5 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.32 | 560757 ASGI13_02_1 69.0 562731 WHEATLAND 69.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.33 | 560763 ASGI13_03_1 115 560761 ASGI13_03_2 34.5 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.76 | 562015 FIREWHEEL1 34.5 523215 FREWHELCOL17 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.76 | 562016 FIREWHEEL2 34.5 523215 FREWHELCOL17 345 2
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.31 | 562323 AGI1202&1305 115 562324 AGI1202&1305 34.5 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.32 | 562727 LESBIA 115 562728 SANJONTAP 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.32 | 562728 SANJONTAP 115 562729 CAPROCKTAP1 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.32 | 562730 CAPROCKTAP2 69.0 562729 CAPROCKTAP1 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.32 | 562730 CAPROCKTAP2 69.0 562731 WHEATLAND 69.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.72 | 563171 G15082_2 34.5 563170 G15082_1 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.4 | P11:13.8:AEPW:COM1-1
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.41 | P11:13.8:AEPW:COM2-1
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.41 | P11:13.8:AEPW:COM3-1
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.42 | P11:18:AEPW:WELSH1-1
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.42 | P11:18:AEPW:WELSH3-1
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.42 | P11:24:AEPW:PIRKEY 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.39 | P11:24:AEPW:SWS3-1
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.39 | P11:24:AEPW:TURKCOAL
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17504 | 112.7 | P12:138:AEPW-OMPA:DUNCAN-4:OMDUNCN4
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17493 | 112.66 | P12:138:AEPW:112GORE4:SNYDER-4
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17493 | 112.66 | 5841_Dup1
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17501 | 111.96 | 584560 GEN-2015-014 115 584561 G15-014XFMR1 34.5 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.175 | 112.65 | P12:138:AEPW:SANTAFE:DUNCAN-4
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.68 | 587991 G16-121XFMR1 34.5 587990 GEN-2016-121 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.62 | 588480 A16-010_SUB 115 3WXFMR A16-010_SUB 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17504 | 112.7 | P12:138:AEPW:DUNCAN-4:L.E.S.-4
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.06 | 588761 G17-033XFMR1 34.5 588760 GEN-2017-033 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.06 | 588765 G17-033XFMR2 34.5 588760 GEN-2017-033 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.63 | 588861 G17-047XFMR1 34.5 588860 GEN-2017-047 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17454 | 112.2 | P12:138:AEPW:ELKCTY-4:CLINTJC4
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.64 | 589381 G17-100XFMR1 34.5 589380 GEN-2017-100 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17466 | 112.39 | P12:138:AEPW:HOB-JCT4:ELKCTY-4
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.64 | P12:138:AEPW:SHERID4:112GORE4
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.1749 | 112.61 | P12:230:AEPW:SWEETWT6:BUFFCK6
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17489 | 112.66 | P12:230:AEPW:SWEETWT6:ROARK6
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17734 | 114.5 | P12:345:AEPW:L.E.S7:TERRYRD7
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17734 | 114.49 | P12:345:AEPW:L.E.S7:TERRYRD7
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17734 | 114.47 | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17799 | 114.61 | P12:345:AEPW-OKGE:L.E.S.-7:GRACMNT7
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17799 | 114.58 | P12:345:AEPW-OKGE:L.E.S.-7:GRACMNT7
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17488 | 112.4 | P12:345:AEPW-OKGE:PITTSB-7:SEMINOL7
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17807 | 115.66 | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.66 | P22:345:AMMO::LABADIE:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.66 | P22:345:AMMO::LABADIE:2
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.66 | P22:345:AMMO::LABADIE:3
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.66 | P22:345:AMMO::LABADIE:4
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.65 | P22:345:AMMO::RUSHISLAND:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.64 | P22:345:AMMO::RUSHISLAND:2
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17493 | 112.41 | P13:138-13.8:AEPW:COMANC-4_#2
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17317 | 111.28 | P13:138-230:AEPW:ELKCTY-4
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17494 | 112.4 | P13:138-24:AEPW:S.W.S.-4
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17493 | 112.39 | P13:138-24:AEPW:TURK 4
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17501 | 112.63 | P13:138-345:AEPW:L.E.S.-4_#1
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.1751 | 112.75 | P13:138-345:AEPW:L.E.S.-4_#2
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17493 | 112.67 | P23:500:EES-EAI:KEO:B4941
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17493 | 112.66 | P23:500:EES-EAI:KEO:B4921
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.61 | P11:26:EES-EAI:INDEP2:1:D401
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.61 | P11:26:EES-EAI:INDEP2:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.61 | P13:500:EES-EAI:INDEP2:MT2
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17493 | 112.65 | P23:500:EES-EAI:INDEP2:B6126
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.64 | P23:500:EES-EAI:PD:INDEP2:LN:FK479
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.1749 | 112.61 | P13:230-34.5:AEPW:BUFFCK6
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17489 | 112.67 | P13:230-34.5:AEPW:ROARK6
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.41 | P13:69-13.8:AEPW:COMANC-2
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.66 | P11:024:DPC:ALMA2:6
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.62 | P11:18:ITCM:EMERYGT1:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.63 | P11:18:ITCM:EMERYGT2:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.63 | P11:161:ITCM:MGS CT1:1C
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.63 | P11:161:ITCM:MGS CT2:2C
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.1749 | 112.64 | 652537 WHITE 3 345 659286 DEERCREK-BE3 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.1749 | 112.64 | 659286 DEERCREK-BE3 345 3WXFMR DEERCRK KU1A 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.63 | 672601 BD 4 230 672306 BD 6G 18.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.63 | 672610 POPLAR 4 230 672310 POPLAR 1G 18.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.63 | 672610 POPLAR 4 230 672311 POPLAR 2G 18.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.62 | 672621 SHAND 4 230 672321 SHAND 1G 18.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.61 | 672649 CODETTE 4 230 672650 NIPAWIN 4 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.62 | 672696 BRADA 4 230 672699 NBEC 4 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.69 | P23:345:MDU::COYOTE::5707-5712-5715::::
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.84 | P23:345:MEC:CBEC 905
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.81 | P23:345:MEC:CBEC 908
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.64 | P23:345:MEC:GDMEC 908
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.74 | P23:345:MEC:RAUN 0180
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.8 | P23:345:MEC:RAUN 0210
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.75 | P23:345:MEC:LOUISA 954
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.75 | P23:345:MEC:LOUISA 964
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.61 | P21:115:XEL:AUTO-SINGLE:CHEMOLT7:LSPOWER7:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.65 | P21:115:XEL:AUTO-SINGLE:COLVILL7:CANONFLSG7:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.61 | P21:115:XEL:AUTO-SINGLE:FARIBALTP7:FARIBALTGEN:Z
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.7 | P21:230:OTP:AUTO-SINGLE:SQBUTTE4:YNG24:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.69 | P23:345:OTP:CENTER 3:3215(1)
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.69 | P23:345:OTP:CENTER 3:3225(1)
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.63 | P12:230:UMZW:# 687 #: FT IN SD. FT-BG1 LINE FAULT
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.63 | P12:230:UMZW:# 3617 #: FT IN SD. FT-BG2 LINE FAULT
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 111.33 | 760494 GEN-2017-146 230 760498 G17-146-TAP 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 111.32 | 760495 G17-146-XFM1 34.5 760494 GEN-2017-146 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.05 | 761356 G17-239-XFMR 34.5 761355 GEN-2017-239 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.05 | 761359 G17-239-XFMR 34.5 761355 GEN-2017-239 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.23 | 761797 G17-187XFM1 34.5 761796 GEN-2017-187 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.23 | 761800 G17-187XFM2 34.5 761796 GEN-2017-187 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 107.16 | 762132 GEN-2017-158 230 763252 G18-099-XFM1 34.5 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 107.16 | 762132 GEN-2017-158 230 763255 G18-099-XFM2 34.5 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 107.74 | 762133 G17-158XFM1 34.5 762132 GEN-2017-158 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 107.74 | 762136 G17-158XFM2 34.5 762132 GEN-2017-158 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 109.9 | 762216 G17-151TAP 345 762217 GEN-2017-151 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17746 | 113.55 | 762216 G17-151TAP 345 762467 G18-015-TAP 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 111.85 | 762218 G17-151XFM1 34.5 762217 GEN-2017-151 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 111.85 | 762221 G17-151XFM2 34.5 762217 GEN-2017-151 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 111.85 | 762224 G17-151XFM3 34.5 762217 GEN-2017-151 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 111.85 | 762227 G17-151XFM4 34.5 762217 GEN-2017-151 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.36 | 762438 GEN-2018-004 115 762442 G18-004-TAP 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 110.89 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 111.7 | 762461 G18-015-XFM1 34.5 762460 GEN-2018-015 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 111.7 | 762464 G18-015-XFM2 34.5 762460 GEN-2018-015 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17631 | 113.07 | 762467 G18-015-TAP 345 763215 G18-092-TAP 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 110.18 | 763087 GEN-2018-073 345 763088 G18-073-XFM1 34.5 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 111.33 | 763087 GEN-2018-073 345 763091 G18-073-XFM2 34.5 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 109.42 | 763120 GEN-2018-081 230 764011 G19-074-XFM1 34.5 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 109.44 | 763186 GEN-2018-089 230 763187 G18-089-XFM1 34.5 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 110.21 | 763208 GEN-2018-092 345 763215 G18-092-TAP 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 111.37 | 763208 GEN-2018-092 345 763220 G18-092-XFM1 34.5 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 111.37 | 763208 GEN-2018-092 345 763223 G18-092-XFM2 34.5 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 108.87 | 763241 GEN-2018-097 230 763242 G18-097-XFM1 34.5 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 109.78 | 763241 GEN-2018-097 230 763296 G18-111-XFM1 34.5 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 109.14 | 763241 GEN-2018-097 230 763307 G18-112-XFM1 34.5 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 109.14 | 763241 GEN-2018-097 230 763310 G18-112-XFM2 34.5 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 108.87 | 763241 GEN-2018-097 230 763395 G18-124-XFM1 34.5 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 108.87 | 763241 GEN-2018-097 230 763398 G18-124-XFM2 34.5 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.29 | 763318 GEN-2018-115 345 763319 G18-115-XFM1 34.5 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.75 | 763340 GEN-2018-117 230 763341 G18-117-XFM1 34.5 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 108.51 | 763483 GEN-2019-003 230 763484 G19-003-XFM1 34.5 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 111.19 | 763483 GEN-2019-003 230 763605 G19-021-XFM1 34.5 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 111.9 | 763516 GEN-2019-011 345 763517 G19-011-XFM1 34.5 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.26 | 763879 GEN-2019-056 115 763880 G19-056XFM1 34.5 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17442 | 112.68 | P42:345:OKGE:SB_BVTY7305
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17484 | 112.43 | P23:345:WERE:BUFF_345-534::
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17484 | 112.43 | P23:345:WERE:BUFF_345-543::
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17488 | 112.78 | P23:345:WERE:JEC_345-15::
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17487 | 112.75 | P23:345:WERE:JEC_345-16::
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17488 | 112.78 | P23:345:WERE:JEC_345-19::
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17488 | 112.78 | P23:345:WERE:JEC_345-20::
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.95 | P23:345:WERE:WOLF_345-50::
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.95 | P23:345:WERE:WOLF_345-60::
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17493 | 112.43 | P42:345:AEPW:WELSH CB 10620 NBTB+FAULT
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17807 | 114.21 | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17833 | 114.99 | P42:345:AEPW:LAWTON EASTSIDE CB 3413A NBTB+FAULT
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17868 | 115.4 | P42:345:AEPW:LAWTON EASTSIDE CB 3425A NBTB+FAULT
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17821 | 115.86 | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17506 | 112.31 | P42:345:AEPW:PITTSBURG CB 3441A NBTB+FAULT
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17488 | 112.4 | P42:345:AEPW:PITTSBURG CB 3445A NBTB+FAULT
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17734 | 114.49 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17734 | 114.49 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17734 | 114.47 | P42:345:AEPW:TERRYRD_CB_3421A_NBTB
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.1749 | 112.75 | P23:345:KCPL:LACYGNE_R2-5::LACYGU2-LACYGNE-STILWELL
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17493 | 112.43 | P23:345:AEPW:WELSH CB 10620 NBTB
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17807 | 114.54 | P23:345:AEPW:OKLAUNION CB 3401A NBTB
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17833 | 114.99 | P23:345:AEPW:LAWTON EASTSIDE CB 3413A NBTB
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17868 | 115.4 | P23:345:AEPW:LAWTON EASTSIDE CB 3425A NBTB
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17821 | 115.86 | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17506 | 112.31 | P23:345:AEPW:PITTSBURG CB 3441A NBTB
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17488 | 112.4 | P23:345:AEPW:PITTSBURG CB 3445A NBTB
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17734 | 114.49 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17734 | 114.49 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17734 | 114.47 | P23:345:AEPW:TERRYRD_CB_3421A_NBTB
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17523 | 112.62 | P12:138:AEPW:S.W.S.-4:L.E.S.-4
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.65 | P11:115:SUNC:GARDENCITY_S2:97:531459(2)
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17753 | 114.72 | P23:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.18011 | 117.32 | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17753 | 114.72 | P42:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB+FAULT
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.18011 | 117.32 | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.16716 | 109.51 | P42:345:OKGE:SB_BVTY7315_PRE19S
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17461 | 112.33 | P23:345:SUNC:MO_BRK182
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17461 | 112.33 | P23:345:SUNC:MO_BRK382
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17489 | 112.42 | P21:345:UMZW:# 725 #: GI IN NE. GI-SWEET LINE FAULT
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17659 | 112.8 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17493 | 112.41 | P12:138-13.8:AEPW:COMANC-4_#1
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17317 | 111.26 | P12:230:AEPW:ELKCITY6:CHISHOLM6
Thermal | 05ALL | 1 | 23SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17649 | 113.54 | P12:230:AEPW:SWEETWT6:CHISHOLM6
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 511458 ELKCTY-4 138 998036 ELKCTY-6 _1 138 1 |  | 330 | 0.10594 | 112.44 | P12:345:OKGE-AEPW:BKRBKR371::::
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 511458 ELKCTY-4 138 998036 ELKCTY-6 _1 138 1 |  | 330 | 0.10594 | 112.78 | P12:345:OKGE-AEPW:BKRBKR371::::
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.10594 | 108.04 | P12:345:OKGE-AEPW:BKRBKR371::::
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.10594 | 108.6 | P12:345:OKGE-AEPW:BKRBKR371::::
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 511490 ELKCITY6 230 998036 ELKCTY-6 _1 138 1 |  | 330 | 0.10594 | 112.79 | P12:345:OKGE-AEPW:BKRBKR371::::
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 511490 ELKCITY6 230 998036 ELKCTY-6 _1 138 1 |  | 330 | 0.10594 | 113.27 | P12:345:OKGE-AEPW:BKRBKR371::::
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997715 ABBXNL844501 230 1 |  | 553 | 0.14654 | 150.96 | 525531 TOLK 6 230 3WXFMR TOLK 6 2
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.0898 | 112.73 | P23:345:KCPL-WERE:237LACYGNE_R1-6::LACYGU1-LACYGNE-NEOSHO
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08978 | 112.64 | P11:230:WERE:LECU5_GEN::
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08978 | 112.63 | P11:161:GMO:DOGWOOD_COMBINED_CYCLE_UNIT_OUTAGE_1_1
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08985 | 111.16 | P11:115:SPS:MUSTANG1&3:153MW::::
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08905 | 114.61 | P12:230:SPS:K37::1_TOLK_LAMB:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.09002 | 112.61 | P12:230:SPS:K43::1_PRNGLE_HARR_E:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08983 | 112.37 | P12:230:SPS:K44::1_EPLNT_HARRW:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.091 | 112.79 | P12:115:SPS:T04::1_TRBLNC_CASTRO:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08979 | 112.19 | P12:115:SPS:T13::1_TAYLOR_WHOBBS:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.0898 | 112.31 | P12:115:SPS:T14::1_MADDOX_TAYLOR:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08979 | 113.09 | P12:115:SPS:T21::1_GRSSLND_GRAHAM:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08979 | 112.41 | P12:115:SPS:T23::1_PCA_POTJCT:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08979 | 112.62 | P12:115:SPS:T24B::1_RSWLL_BRSHRF:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.0898 | 112.64 | P12:115:SPS:T26::1_CHAVES_RSWLCTY:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08828 | 113.18 | P12:115:SPS:T28A::1_LAMTON_PLANTX:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.09053 | 112.67 | P12:115:SPS:T29::1_LAMTON_HALECTR:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.09083 | 113.96 | P12:115:SPS:T30::1_LAMB_HOCKLY:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.09083 | 113.13 | P12:115:SPS:T31::1_HOCKLY_SUNDWN:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08982 | 112.63 | P12:115:SPS:T35::1_TERRY_YOAKUM:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08979 | 113.32 | P12:115:SPS:T45::1_NORRIS_OASIS:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08982 | 112.4 | P12:115:SPS:T57::1_MUSTG_SEGRVS:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08952 | 113.15 | P12:115:SPS:T59::1_CARGIL_CURRY:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.092 | 112.42 | P12:115:SPS:T66::1_RNDALL_HAPPY:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.092 | 112.9 | P12:115:SPS:T67::1_HAPPY_KRESS:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08991 | 112.39 | P12:115:SPS:T68::1_TUCO_FLOYD:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08979 | 113.2 | P12:115:SPS:T71::1_CRLSLE_YUMA:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.09012 | 112.7 | P12:115:SPS:T81::1_COX_FLOYD:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08979 | 112.85 | P12:115:SPS:T83::1_SP-FKFD_ALLEN:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08982 | 113.01 | P12:115:SPS:T89::1_DC_N_HIGG:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08979 | 112.66 | P12:115:SPS:T91::1_HIGG_RUSSELL:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.09011 | 112.62 | P12:115:SPS:V04::1_EPLANT_RNDALL:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08989 | 112.67 | P12:115:SPS:V07::1_COX_HALECTR:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08959 | 112.95 | P12:115:SPS:V09::1_HALECTR_PLANTX:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08982 | 112.83 | P12:115:SPS:V12::1_PLANTX_BAILEY:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08979 | 112.62 | P12:115:SPS:V15::1_TUCO_INDANA:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08976 | 112.67 | P12:115:SPS:V24::1_WOLFTH_TERRY:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.0899 | 112.64 | P12:115:SPS:V26::1_RSWLL_EDDY_N:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08979 | 112.98 | P12:115:SPS:V33::1_LUBBS_LYNN:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08827 | 113.85 | P12:115:SPS:V37::1_CASTRO_PLANTX:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08979 | 112.75 | P12:115:SPS:V46::1_ALLEN_WHEELCK:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08981 | 113.09 | P12:115:SPS:V49::1_YOAKUM_SHLCO2:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.09011 | 113.26 | P12:115:SPS:V55::1_SUNDWN_TERRY:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.09001 | 113.09 | P12:115:SPS:V56::1_COCHRAN_SUNDWN:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08979 | 112.68 | P12:115:SPS:V62::1_CRLSLE_INDANA:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08983 | 112.62 | P12:115:SPS:V70::1_S_GORG_RNDALL:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08973 | 112.65 | P12:115:SPS:V78::2_CURRY_RSVLT:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08982 | 112.79 | P12:115:SPS:V81::1_LE-WAIT_LE-LVN:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08979 | 112.65 | P12:115:SPS:V95::1_DC_N_SHLCO2:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08979 | 112.61 | P12:115:SPS:W11::1_DC_S_SMINLE:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08979 | 112.61 | P12:115:SPS:W12::1_SMINLE_DOSS:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.0898 | 112.68 | P12:115:SPS:W14::1_SMINLE_GAINES:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08979 | 113.14 | P12:115:SPS:W32::1_PRMTR_FE-CLSIN:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08979 | 112.61 | P12:115:SPS:W34::1_JNSDRW_MAPCO:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08981 | 112.85 | P12:115:SPS:W35::1_GAINES_JNSDRW:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08983 | 112.64 | P12:115:SPS:W36::1_TAYLOR_JNSDRW:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.09077 | 113.15 | P12:115:SPS:W40::1_WCANYON_TRBLNC:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.09113 | 112.71 | P12:115:SPS:W52::1_NEWHART_KRESS:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08979 | 113.2 | P12:115:SPS:W58::1_NORTON_LOPEZ:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08979 | 112.82 | P12:115:SPS:W59::1_LOPEZ_CMPBLL:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08979 | 113.15 | P12:115:SPS:W62::1_PLSTHL_CURRY:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08991 | 112.62 | P12:115:SPS:W63::1_PLSTHL_CURRY:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08979 | 112.96 | P12:115:SPS:W64::1_PLSTHL_FE-CLV:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08978 | 113.12 | P12:115:SPS:W65::1_PLSTHL_CURRY:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08979 | 112.81 | P12:115:SPS:W66::1_PORTA_GREYHUND:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.09077 | 112.61 | P12:115:SPS:W77::1_RNDAL_WCANYON:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08979 | 112.64 | P12:115:SPS:W99::1_CAPITAN_CHAVES:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.0898 | 113.08 | P12:115:SPS:U14::1_DC_STH_INKBSN:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08982 | 113.02 | P12:115:SPS:V15::1_INKBSN_LE-WAT:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08984 | 112.74 | P12:115:SPS:U16::1_BSHLND_OUTPST:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08984 | 112.73 | P12:115:SPS:U17::1_COLTR_OUTPST:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08994 | 112.8 | P12:115:SPS:U19::1_DEAN_PLAINS:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08984 | 112.67 | P12:115:SPS:U23::1_COLTR_HILSDE:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08625 | 119.61 | P42:345:SPS:YOAKUM:J18####:SLG1:EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08625 | 119.61 | P43:345:SPS:YOAKUM:TF#####:SLG:EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08625 | 119.61 | P42:345:SPS:YOAKUM:J17####:SLG:EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08625 | 119.61 | P42:345:SPS:YOAKUM:J18####:SLG2:EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08978 | 112.62 | P11:18:HAST:::EGYCTR2G WEC2_LOSS OF WEC 2 GEN_:HV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08978 | 112.62 | P13:18-115:HAST:::EGYCNTR7 XFMR G2WEC 2 GSU_:HV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08978 | 112.63 | P11:161:GMO:DOGWOOD-COMBINED-CYCLE-UNIT-OUTA:::HV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.0898 | 112.73 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08978 | 112.75 | P23:345:KCPL:LACYGNE-R2-5:::EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08976 | 112.78 | P11:230:WERE:JECU1-GEN:::HV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08978 | 112.64 | P11:230:WERE:LECU5-GEN:::HV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08976 | 112.78 | P11:345:WERE:JECU2-GEN:::EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08976 | 112.78 | P11:345:WERE:JECU3-GEN:::EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08979 | 112.95 | P11:345:WERE:WOLFU1-GEN:::EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08971 | 112.43 | P23:345:WERE:BUFF-345-534:::EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08971 | 112.43 | P23:345:WERE:BUFF-345-543:::EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08976 | 112.78 | P23:345:WERE:JEC-345-15:::EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08975 | 112.75 | P23:345:WERE:JEC-345-16:::EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08976 | 112.78 | P23:345:WERE:JEC-345-19:::EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08976 | 112.78 | P23:345:WERE:JEC-345-20:::EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08979 | 112.95 | P23:345:WERE:WOLF-345-50:::EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08979 | 112.95 | P23:345:WERE:WOLF-345-60:::EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08979 | 112.89 | P11:022:NPPD:COOPER1G:1:983:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08974 | 112.92 | P11:023:NPPD:GENTLM1G:1:757:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08974 | 112.94 | P11:024:NPPD:GENTLM2G:2:757:::
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08976 | 112.75 | P13:345:OPPD:NEBCTY1G:::EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08975 | 112.78 | P13:345:OPPD:NEBCTY2G:::EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08979 | 112.77 | P22:345:OPPD:S3458 NEBCTY1G:LT::EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08976 | 112.75 | P22:345:OPPD:S3458 NEBCTY1G:::EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08979 | 112.81 | P22:345:OPPD:S3458 NEBCTY2G:LT::EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08975 | 112.78 | P22:345:OPPD:S3458 NEBCTY2G:::EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08979 | 112.77 | P23:345:OPPD:S3458 NEBCTY1G:LT::EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08976 | 112.75 | P23:345:OPPD:S3458 NEBCTY1G:::EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08979 | 112.81 | P23:345:OPPD:S3458 NEBCTY2G:LT::EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08975 | 112.78 | P23:345:OPPD:S3458 NEBCTY2G:::EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08979 | 112.4 | P12:115:SUNC:PLYMELL-PIERCEVILLE:::HV::
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08977 | 112.64 | P11:018:UMZB:# 5 #:: DCS IN SD. DEERCREEK_MV::
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08978 | 112.61 | P11:022:UMZB:# 15 #:: LO IN ND. LELAND OLDS 1_MV::
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08977 | 112.65 | P11:020:UMZB:# 16 #:: LO IN ND. LELAND OLDS 2_MV::
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08977 | 112.7 | P11:023:UMZB:# 31 #:: AVS IN ND. ANTELOPE VALLEY 1_MV::
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08977 | 112.7 | P11:023:UMZB:# 32 #:: AVS IN ND. ANTELOPE VALLEY 2_MV::
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08974 | 112.9 | P11:024:UMZB:# 33 #:: LRS IN WY. LARAMIE RIVER STATION 1_MV::
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08979 | 112.63 | P12:230:UMZW:# 687 #:: FT IN SD. FT-BG1 BRANCH FAULT:HV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08979 | 112.63 | P12:230:UMZW:# 3617 #:: FT IN SD. FT-BG2 BRANCH FAULT:HV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08979 | 112.63 | P12:230:UMZW:# 4038 #:: BG-FT IN SD. FAULT FOR TRANSMISSION CIRCUIT (BG-FT).:HV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08979 | 112.63 | P12:230:UMZW:# 4039 #:: BG-FT IN SD. FAULT FOR TRANSMISSION CIRCUIT (BG-FT).:HV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08979 | 112.61 | P13:230:UMZW:# 5135 #:: OA IN SD. FAULT ON TRANSFORMER (2).:HV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08979 | 112.61 | P13:230:UMZW:# 5136 #:: OA IN SD. FAULT ON TRANSFORMER (3).:HV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08977 | 112.42 | P21:345:UMZW:# 725 #:: GI IN NE. GI-SWEET BRANCH FAULT:EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08977 | 112.42 | P23:345:UMZW:# 2430 #:: GI IN NE. GI 1492 BKR FAULT:EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08977 | 112.42 | P23:345:UMZW:# 2438 #:: GI IN NE. GI-SWEET BRANCH FAULT & GI 1492 STUCK BKR:EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08981 | 112.37 | P11:138:WFEC:HUGO1:465MW :::
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08975 | 112.4 | P12:345:OKGE-AEPW:BKRBKR20::::
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.09014 | 112.75 | P12:345:OKGE:BKRBKR21::::
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.09033 | 112.95 | P12:345:OKGE:BKRBKR24::::
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.09218 | 114.47 | P12:345:OKGE-AEPW:BKRBKR25::::
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08969 | 112.42 | P12:345:OKGE:BKRBKR336::::
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08969 | 112.41 | P12:345:OKGE:BKRBKR336_2::::
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.09273 | 114.61 | P12:345:OKGE-AEPW:BKRBKR366::::
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.09273 | 114.58 | P12:345:OKGE-AEPW:BKRBKR366::::
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.09034 | 112.87 | P12:345:OKGE:BKRBKR367::::
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.0901 | 112.62 | P12:345:OKGE-WFEC:BKRBKR374::::
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08936 | 112.22 | P12:345:OKGE:BKRBKR4193::::
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08936 | 112.22 | P12:345:OKGE:BKRBKR4194::::
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.0892 | 112.28 | P12:345:OKGE-SPS:BKRBKR4201::::
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.0892 | 112.28 | P12:345:OKGE-SPS:BKRBKR4202::::
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08968 | 112.35 | P12:345:OKGE:BKRBKR443NEW::::
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08968 | 112.35 | P12:345:OKGE:BKRBKR443NEW2::::
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08973 | 112.88 | P12:345:OKGE:BKRBKR604::::
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08972 | 112.94 | P12:345:OKGE:BKRBKR604_2::::
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08929 | 112.62 | P42:345:OKGE:SB_ARIA7381::::
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.09739 | 116.05 | P42:345:OKGE:SB_BVTY7387::::
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.09014 | 112.68 | P42:345:OKGE:SB_SPCK7383::::
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08977 | 112.64 | P11:115:SUNC:GARDENCITY_S2:103:531459(2):HV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08977 | 112.64 | P11:115:SUNC:FORTDDODGE_4:157:539670(4):HV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08979 | 112.62 | P11:345:599:CIMARRON1WIND:200:531603(1):EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08979 | 112.92 | P13:115:SUNC:HOLCOMB_GSU:::HV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08977 | 112.64 | P13:115:SUNC:S2_GSU:::HV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08977 | 112.64 | P13:115:SUNC:FORTDODGE_GSU:::HV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08977 | 112.62 | P23:345:SUNC:BU_BRK682:::EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08979 | 112.71 | 300003 1THLG3 24.0 301503 7THOMHLGSU3 345 3
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08979 | 112.71 | 300049 7THOMHL 345 301503 7THOMHLGSU3 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08979 | 112.66 | P11:20:AMMO:1LAB�� G1:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08979 | 112.66 | P11:20:AMMO:1LAB�� G2:2
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08979 | 112.83 | P11:345:AMMO::CALLAWAY:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08979 | 112.66 | P11:345:AMMO::LABADIE:3
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08979 | 112.66 | P11:345:AMMO::LABADIE:4
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08979 | 112.66 | P11:345:AMMO::RUSHISLAND:U1
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08979 | 112.66 | P11:345:AMMO::RUSHISLAND:U2
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08979 | 112.64 | P11:138:AMMO::SIOUX:2
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08979 | 112.64 | P12:765:AEP:AEP ROCKP-AEP JEFF 765
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08979 | 112.61 | P11:HV:EES::1ISES U1:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08979 | 112.61 | P11:EHV:EES::1ISES U2:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08979 | 112.42 | P11:HV:EES::PIRKEY 1:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08979 | 112.42 | P11:EHV:EES::WELSH3-1:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08979 | 112.39 | P11:HV:EES::TURKCOAL:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08979 | 112.61 | P12:HV:EES::5ISES%:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08979 | 112.61 | P12:EHV:EES::8ISES%:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08979 | 112.82 | P12:EHV:EES::7CALAWY 1:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.0898 | 112.39 | P12:HV:EES::TURK 4%:1(1)
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08979 | 112.64 | 344011 7HUGHES 345 344012 7HPW-N 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08979 | 112.66 | 344884 7LABADIE1 345 344894 1LAB G1 20.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08979 | 112.66 | 344885 7LABADIE2 345 344895 1LAB G2 20.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08979 | 112.66 | 344886 7LABADIE3 345 344896 1LAB G3 20.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08979 | 112.66 | 344887 7LABADIE4 345 344897 1LAB G4 20.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08979 | 112.65 | 345667 7RUSH 1 345 345670 1RUSH G1 18.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08979 | 112.65 | 345668 7RUSH 2 345 345671 1RUSH G2 18.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08979 | 112.64 | 345755 4SIOUX 1 138 345756 1SIOUX 1 18.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08979 | 112.64 | 345764 4SIOUX 2 138 345765 1SIOUX 2 18.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08979 | 112.69 | P12:345:MDU::CENTER:COYOTE:1::::
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08979 | 112.69 | P13:345:MDU:COYOTE GSU LOSS:COYOTE::1::::
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08979 | 112.61 | P11:345:MEC:GDMEC CT1
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08979 | 112.61 | P11:345:MEC:GDMEC CT2
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08979 | 112.71 | P11:345:MEC:GDMEC ST
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08979 | 112.9 | P11:345:MEC-NPPD:COOPER 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08979 | 112.8 | P11:24:XEL:AUTO-SINGLE:SHERC31G:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08979 | 112.8 | P11:24:XEL:AUTO-SINGLE:SHERC32G:2
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08979 | 112.87 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08979 | 112.73 | P11:20:XEL:AUTO-SINGLE:PRIS31G:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08979 | 112.73 | P11:20:XEL:AUTO-SINGLE:PRIS32G:2
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08979 | 112.76 | P11:22:XEL:AUTO-SINGLE:MNTCE31G:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08979 | 112.73 | P11:20:XEL:AUTO-SINGLE:KING31G:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08979 | 112.77 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08979 | 112.77 | P11:22:GRE:AUTO-SINGLE:GRE-COAL42G:2
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08979 | 112.71 | P11:24:OTP:AUTO-SINGLE:BIGSTN1G:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08979 | 112.71 | P11:20:OTP:AUTO-SINGLE:CENTER2G:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08979 | 112.63 | P11:22:OTP:AUTO-SINGLE:CENTER1G:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08979 | 112.7 | P11:24:OTP:AUTO-SINGLE:COYOTE1G:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08979 | 112.63 | P11:24:DPC:AUTO-SINGLE:GENOA53G:3
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08979 | 112.61 | P12:115:XEL:AUTO-SINGLE:CHEMOLT7:LSPOWER7:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08979 | 112.65 | P12:115:XEL:AUTO-SINGLE:COLVILL7:CANONFLSG7:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08979 | 112.61 | P12:115:XEL:AUTO-SINGLE:FARIBALTP7:FARIBALTGEN:Z
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08979 | 112.7 | P12:230:OTP:AUTO-SINGLE:SQBUTTE4:YNG24:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08979 | 112.78 | P13:24-345:XEL:AUTO-SINGLE:SHERC31G:SHERCO3:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08979 | 112.78 | P13:24-345:XEL:AUTO-SINGLE:SHERC32G:SHERCO3:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08979 | 112.85 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08979 | 112.73 | P13:20-345:XEL:AUTO-SINGLE:PRIS31G:PRISLD3:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08979 | 112.73 | P13:20-345:XEL:AUTO-SINGLE:PRIS32G:PRISLD3:2
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08979 | 112.76 | P13:22-345:XEL:AUTO-SINGLE:MNTCE31G:MNTCELO3:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08979 | 112.72 | P13:20-345:XEL:AUTO-SINGLE:KING31G:ASKING3:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08979 | 112.76 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL41G:GRE-COALCR4:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08979 | 112.75 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL42G:GRE-COALCR4:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08979 | 112.7 | P13:230-24:OTP:AUTO-SINGLE:BIGSTON4:BIGSTN1G:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08979 | 112.7 | P13:20-230:OTP:AUTO-SINGLE:CENTER2G:YNG24:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08979 | 112.62 | P13:22-230:OTP:AUTO-SINGLE:CENTER1G:CENTER4:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08979 | 112.69 | P13:24-345:OTP:AUTO-SINGLE:COYOTE1G:COYOTE3:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08979 | 112.63 | P13:24-161:DPC:AUTO-SINGLE:GENOA53G:GENOA5:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08979 | 112.64 | P13:24-161:DPC:AUTO-SINGLE:JPM:ALMA5:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08979 | 112.7 | P11:115:XEL:RIV COMBINE CYCLE
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08979 | 112.62 | P12:115:XEL:BDS #2 5
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08979 | 112.62 | P11:115:XEL:HBR #6
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08979 | 112.62 | P11:115:XEL:HBR #7
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08979 | 112.73 | P11:115:XEL:HBR #6 7 8
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08979 | 112.73 | P23:345:XEL:8H14 PRI
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08979 | 112.73 | P23:345:XEL:8H17 PRI AS
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08979 | 112.85 | P23:345:XEL:8N28 SHC
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08979 | 112.78 | P23:345:XEL:8N22 SHC
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08979 | 112.78 | P23:345:XEL:8N17 SHC
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08979 | 112.77 | P23:345:XEL:8N8 MNN
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08979 | 112.72 | P23:345:XEL:8P1 KING
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08979 | 112.72 | P23:345:XEL:8P2 KING
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08979 | 112.62 | P23:115:XEL:5P147 IVH AS
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08979 | 112.61 | P11:18:ALTW:AUTO-SINGLE:EMERYST1:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08979 | 112.61 | P11:22:ALTW:AUTO-SINGLE:LANS54G:4
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08979 | 112.74 | P11:22:ALTW:AUTO-SINGLE:ARNOLD1G:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08979 | 112.77 | P11:24:ALTW:AUTO-SINGLE:OTTUMW1G:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08979 | 112.61 | P13:18-161:ALTW:AUTO-SINGLE:EMERYST1:EMERY5:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08979 | 112.61 | P13:22-161:ALTW:AUTO-SINGLE:LANS54G:LANSINGL15:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08979 | 112.73 | P13:22-161:ALTW:AUTO-SINGLE:ARNOLD1G:ARNOLD5:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08979 | 112.76 | P13:24-161:ALTW:AUTO-SINGLE:OTTUMW1G:OTTUMWA5:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08979 | 112.82 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08979 | 112.88 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08979 | 112.75 | P11:22:MEC:AUTO-SINGLE:NEAL3G:3
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08979 | 112.81 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08979 | 112.76 | P11:24:MEC:AUTO-SINGLE:LOUIS31G:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08979 | 112.81 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08979 | 112.84 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08979 | 112.74 | P13:345-22:MEC:AUTO-SINGLE:RAUN3:NEAL3G:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08979 | 112.8 | P13:345-24:MEC:AUTO-SINGLE:RAUN3:NEAL4G:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08979 | 112.74 | P13:345-24:MEC:AUTO-SINGLE:LOUISA3:LOUIS31G:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08976 | 112.78 | P11:230:WERE:JECU1_GEN::
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08976 | 112.78 | P11:345:WERE:JECU2_GEN::
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08976 | 112.78 | P11:345:WERE:JECU3_GEN::
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08979 | 112.95 | P11:345:WERE:WOLFU1_GEN::
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08979 | 112.63 | 511435 SNYDER-4 138 588779 TAP_G17-036 138 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08953 | 112.38 | 511446 CL-AFTP4 138 511458 ELKCTY-4 138 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08953 | 112.4 | 511446 CL-AFTP4 138 511463 HOB-JCT4 138 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08987 | 112.63 | 511453 DUNCAN-4 138 511552 DUNCHERTP4 138 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08987 | 112.62 | 511455 D.E.S.-4 138 511552 DUNCHERTP4 138 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08987 | 112.62 | 511455 D.E.S.-4 138 529344 OMDUNE-4 138 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08979 | 112.63 | 511456 O.K.U.-7 345 511565 OKLAUN HVDC7 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08979 | 111.6 | 511456 O.K.U.-7 345 588760 GEN-2017-033 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.09286 | 114.54 | 511456 O.K.U.-7 345 763215 G18-092-TAP 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.09299 | 115.11 | 511468 L.E.S.-7 345 762467 G18-015-TAP 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.09196 | 114.48 | 511468 L.E.S.-7 345 763215 G18-092-TAP 345 2
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08979 | 112.29 | 511468 L.E.S.-7 345 763318 GEN-2018-115 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08979 | 112.66 | 511488 112GORE4 138 511510 LAIRGST4 138 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08992 | 112.7 | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08979 | 112.65 | 511500 CACHE4 138 511510 LAIRGST4 138 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08979 | 112.64 | 511500 CACHE4 138 588779 TAP_G17-036 138 2
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.09195 | 112.8 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08979 | 112.75 | 511541 SWEETWT6 230 763340 GEN-2018-117 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08547 | 109.9 | 511553 CHISHOLM7 345 523961 POTTER_CO 7 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08547 | 109.9 | 511553 CHISHOLM7 345 523961 POTTER_CO 7 345 2
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.09739 | 116.03 | 515375 WWRDEHV7 345 515458 BORDER 7 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.09739 | 116.05 | 515458 BORDER 7 345 560022 CRAWFISH_DR 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08976 | 112.7 | 515618 BALKOW 7 345 3WXFMR BALKOW 7 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08976 | 112.7 | 515618 BALKOW 7 345 3WXFMR BALKOW 7 1_Dup1
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08972 | 112.95 | 515634 PALDR1W7 345 3WXFMR PALO2 _1 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08979 | 112.7 | 515677 BADGER 7 345 563170 G15082_1 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08972 | 112.61 | 520827 BINGERJ4 138 521017 ONEY 4 138 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08972 | 112.62 | 521017 ONEY 4 138 521089 WASHITA4 138 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08979 | 112.61 | 522800 MU-TULIA 3 115 525179 TULIA_TP 3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08979 | 112.75 | 522892 MU-BROWNFLD2 69.0 526761 BROWNFLD_TP2 69.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08979 | 112.64 | 523090 TEXAS_CNTY 3 115 589380 GEN-2017-100 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08975 | 112.78 | 523093 HITCHLAND 3 115 523174 GOODWELLWND3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08979 | 112.95 | 523097 HITCHLAND 7 345 523112 NOVUS1 7 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08979 | 113 | 523097 HITCHLAND 7 345 523215 FREWHELCOL17 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08748 | 111.48 | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.0747 | 109.07 | 523097 HITCHLAND 7 345 523961 POTTER_CO 7 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08979 | 113.05 | 523097 HITCHLAND 7 345 560252 G10-14 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08979 | 112.62 | 523099 TC-DRYTRLS 3 115 588480 A16-010_SUB 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08979 | 112.82 | 523112 NOVUS1 7 345 3WXFMR NOVUS XF2 2
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08979 | 112.63 | 523112 NOVUS1 7 345 3WXFMR XIANA2011198 _1 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08977 | 112.61 | 523118 BUFF_DUNES 7 345 523853 FINNEY 7 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08979 | 112.63 | 523120 COLE 3 115 588860 GEN-2017-047 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08977 | 112.64 | 523172 GWELL_COLL11 34.5 523174 GOODWELLWND3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08977 | 112.65 | 523173 GWELL_COLL21 34.5 523174 GOODWELLWND3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.09002 | 112.61 | 523267 PRINGLE 6 230 3WXFMR ENRCO13617-1 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.09002 | 112.61 | 523267 PRINGLE 6 230 523979 HARRNG_EST 6 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.09098 | 113.07 | 523771 GRAPEVINE 6 230 524044 NICHOLS 6 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.09442 | 113.75 | 523959 POTTER_CO 6 230 524267 BUSHLAND 6 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.11957 | 114.67 | 523959 POTTER_CO 6 230 525461 NEWHART 6 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.12153 | 118.42 | 523961 POTTER_CO 7 345 3WXFMR WAUK 90343-A 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.09006 | 112.4 | 523978 HARRNG_MID 6 230 523979 HARRNG_EST 6 230 @1
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.0898 | 112.39 | 524010 ROLLHILLS 6 230 3WXFMR WAUK WT01104 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08984 | 112.74 | 524267 BUSHLAND 6 230 3WXFMR WH 7001795 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.09754 | 114.31 | 524267 BUSHLAND 6 230 524623 DEAFSMITH 6 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08966 | 113.07 | 524296 SPNSPUR_WND7 345 524299 SPNSPUR_COL7 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08966 | 113.07 | 524299 SPNSPUR_COL7 345 3WXFMR SPNSPUR_COL7 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.10059 | 113.32 | 524415 AMA_SOUTH 6 230 525213 SWISHER 6 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08979 | 113.2 | 524502 NORTON 3 115 524509 FE-TUCMCARI3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.09077 | 113.01 | 524575 DS-#25+ 3 115 524597 PANDAHFD 3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.09077 | 113.12 | 524575 DS-#25+ 3 115 524630 TIERABLANCA3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08979 | 112.7 | 524604 HEREFRD_SB 2 69.0 524608 HERFRD_STH 2 69.0 *1
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.09256 | 119.12 | 524623 DEAFSMITH 6 230 760498 G17-146-TAP 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08979 | 113.1 | 524721 DS-#15&#19+2 69.0 524745 CASTRO_CNTY2 69.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08976 | 112.61 | 524770 PLSNT_HILL 6 230 3WXFMR EFAE1100068A 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.09265 | 117.92 | 524875 OASIS 6 230 524885 SN_JUAN_TAP6 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08998 | 113.69 | 524875 OASIS 6 230 524909 ROOSEVELT 6 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.09256 | 118.38 | 524885 SN_JUAN_TAP6 230 527483 CHAVES_CNTY6 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08973 | 112.8 | 524909 ROOSEVELT 6 230 3WXFMR ABB LMM60042 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08972 | 118.36 | 524909 ROOSEVELT 6 230 525531 TOLK 6 230 2
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08979 | 113.33 | 524923 PORTALES 2 69.0 524929 RO-PORT_MTR2 69.0 @1
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08979 | 113 | 525001 W_MULESHOE 2 69.0 525008 MULESH_CTY 2 69.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08979 | 113 | 525008 MULESH_CTY 2 69.0 525027 BAILEYCO 2 69.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08979 | 113.28 | 525023 BC-BAIL_MTR2 69.0 525027 BAILEYCO 2 69.0 @1
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08827 | 113.27 | 525056 BC-EARTH 3 115 525480 PLANT_X 3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08979 | 113.09 | 525191 KRESS_INT 2 69.0 525203 SW-KRESS 2 69.0 Z1
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08979 | 113.17 | 525192 KRESS_INT 3 115 3WXFMR ENRCO 136155 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.10664 | 113.6 | 525213 SWISHER 6 230 525461 NEWHART 6 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08979 | 112.73 | 525272 KISER 3 115 3WXFMR VON 13819/1 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08979 | 113.19 | 525326 COX 3 115 3WXFMR ELCO 13474-3 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08979 | 113.21 | 525414 LAMTON 3 115 3WXFMR ASEA MLL9204 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08828 | 113.03 | 525440 LC-S_OLTON+3 115 525446 RKYFORD_TP 3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08828 | 113.03 | 525446 RKYFORD_TP 3 115 525480 PLANT_X 3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08809 | 114.35 | 525481 PLANT_X 6 230 3WXFMR WH ALM20171 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.09597 | 118.3 | 525481 PLANT_X 6 230 526435 SUNDOWN 6 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.09256 | 117.38 | 525481 PLANT_X 6 230 760498 G17-146-TAP 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08695 | 113.07 | 525481 PLANT_X 6 230 762174 G17-218TAP 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.0866 | 113.14 | 525481 PLANT_X 6 230 762174 G17-218TAP 230 2
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.09384 | 118.38 | 525531 TOLK 6 230 525586 NEEDMORE 6 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08905 | 114.61 | 525531 TOLK 6 230 525637 LAMB_CNTY 6 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.0978 | 118.52 | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08559 | 113.33 | 525531 TOLK 6 230 762174 G17-218TAP 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.0853 | 113.39 | 525531 TOLK 6 230 762174 G17-218TAP 230 2
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14654 | 149.08 | 525549 TOLK 7 345 3WXFMR ABBXNL844501 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.09384 | 118.36 | 525586 NEEDMORE 6 230 526935 YOAKUM 6 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08979 | 113.01 | 525599 LC-SANDHLL+2 69.0 525606 AMHERST 2 69.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08979 | 113.04 | 525606 AMHERST 2 69.0 525613 W_LITTLFLD 2 69.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08979 | 113.07 | 525613 W_LITTLFLD 2 69.0 525635 LAMB_CNTY 2 69.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08979 | 113.02 | 525635 LAMB_CNTY 2 69.0 525650 LC-LTTLFLD+2 69.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08905 | 114.61 | 525637 LAMB_CNTY 6 230 3WXFMR WH ALM20172 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08979 | 112.87 | 525828 TUCO_INT 3 115 3WXFMR DS F78800913 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08995 | 112.4 | 525830 TUCO_INT 6 230 3WXFMR ENRCO 136401 2
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.0858 | 114.37 | 525832 TUCO_INT 7 345 526936 YOAKUM_345 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08979 | 113.07 | 526086 SW_6786_N 2 69.0 526087 SW_6786_S 2 69.0 Z1
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08979 | 113.07 | 526086 SW_6786_N 2 69.0 526102 SP-HETTLER 2 69.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08979 | 113.14 | 526087 SW_6786_S 2 69.0 526284 PLANTERS 2 69.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08979 | 112.69 | 526160 CARLISLE 3 115 3WXFMR WH RLP38371 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08979 | 113.03 | 526195 QUINCY 3 115 526196 SP-MILWAUKEE 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08979 | 112.93 | 526268 LUBBCK_STH 3 115 3WXFMR NA 70454A 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08979 | 113.19 | 526284 PLANTERS 2 69.0 526297 LUBBCK_EST 2 69.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.0898 | 112.63 | 526435 SUNDOWN 6 230 3WXFMR UPDATE LATER _12 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.09145 | 115 | 526435 SUNDOWN 6 230 526460 AMOCO_SS 6 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08979 | 112.65 | 526525 WOLFFORTH 6 230 3WXFMR UPDATE LATER _13 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08979 | 113.07 | 526735 TERRY_CNTY 2 69.0 526747 LG-BROWNFLD2 69.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08979 | 113 | 526747 LG-BROWNFLD2 69.0 526754 BROWNFIELD 2 69.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08997 | 114.41 | 526935 YOAKUM 6 230 527028 INK_BASIN 6 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08687 | 121.79 | 526936 YOAKUM_345 345 527896 HOBBS_INT 7 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08999 | 113.76 | 527028 INK_BASIN 6 230 527894 HOBBS_INT 6 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08982 | 113 | 527130 DENVER_N 3 115 527286 HIGGEAST 3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08979 | 112.61 | 527149 MUSTANG 6 230 3WXFMR ENRCO 136161 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08994 | 110.49 | 527149 MUSTANG 6 230 527151 GS-MUSTANG 6 230 @1
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08979 | 112.86 | 527202 SEAGRAVES 3 115 3WXFMR ABB MLL92408 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08979 | 112.76 | 527212 DIAMONDBACK3 115 3WXFMR HOW 36773714 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08979 | 112.68 | 527261 SULPHUR 2 69.0 527271 LG-FOSTER +2 69.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08982 | 112.98 | 527286 HIGGEAST 3 115 527363 HIGG 3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08981 | 112.82 | 527322 GAINES 3 115 527325 OXY_WSEM_TP3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08981 | 112.74 | 527325 OXY_WSEM_TP3 115 527362 JOHNSON_DRW3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08979 | 112.73 | 527340 DOSS 3 115 3WXFMR ELCO 13566/1 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08979 | 112.71 | 527345 LEGACY 2 69.0 527350 XTO_ROBRTSN2 69.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08979 | 112.71 | 527346 LEGACY 3 115 3WXFMR VROL 13735-1 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08979 | 112.69 | 527350 XTO_ROBRTSN2 69.0 527355 BOARDMAN 2 69.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08979 | 112.63 | 527355 BOARDMAN 2 69.0 527365 FLANNAGAN 2 69.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08979 | 112.61 | 527360 MAPCO 3 115 527362 JOHNSON_DRW3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08979 | 112.65 | 527362 JOHNSON_DRW3 115 528775 LE-ERF 3 115 @1
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08982 | 112.39 | 527455 RSWL_SLRCOL3 115 527482 CHAVES_CNTY3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08981 | 112.41 | 527470 CHVS_SLRCOL3 115 527464 CHVS_SOLAR11 34.5 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08981 | 112.34 | 527470 CHVS_SLRCOL3 115 527482 CHAVES_CNTY3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.09093 | 112.88 | 527483 CHAVES_CNTY6 230 527799 EDDY_NORTH 6 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08979 | 112.62 | 527508 PRICE 3 115 527509 PRICE_TAP 3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08979 | 112.62 | 527529 RIACBRSH_TP3 115 527533 SW4J795_E 3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08979 | 112.62 | 527533 SW4J795_E 3 115 527564 ROSWLL_INT 3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08979 | 112.62 | 527563 ROSWLL_INT 2 69.0 527575 SW_4702 2 69.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.0899 | 112.67 | 527564 ROSWLL_INT 3 115 527597 TWEEDY 3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08979 | 112.62 | 527575 SW_4702 2 69.0 527589 CV-ORCHARD 2 69.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08974 | 112.78 | 527653 MILO_WIND 1 34.5 527655 RSVLT_CC_E 7 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08967 | 112.66 | 527654 RSVLT_CC_W 7 345 527655 RSVLT_CC_E 7 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08967 | 112.95 | 527654 RSVLT_CC_W 7 345 527666 RSVLT_COL1 7 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08962 | 112.86 | 527655 RSVLT_CC_E 7 345 527656 CROSSROADS 7 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08967 | 112.95 | 527666 RSVLT_COL1 7 345 3WXFMR RSVLT_COL1 7 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08979 | 112.36 | 527736 NAVAJO_5TP 3 115 527739 NAVAJO_4 3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08979 | 112.35 | 527864 CUNNINHAM 3 115 528348 BUCKEYE_TP 3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08979 | 112.63 | 527864 CUNNINHAM 3 115 528568 MONUMNT_TP 3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08971 | 112.91 | 527865 CUNNIGHM_N 6 230 527867 CUNNIGHM_S 6 230 *1
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08977 | 112.64 | 527865 CUNNIGHM_N 6 230 527963 POTASH_JCT 6 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08979 | 112.4 | 527867 CUNNIGHM_S 6 230 3WXFMR WH 7000266 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08975 | 112.86 | 527867 CUNNIGHM_S 6 230 527882 CUNINGHAM2 1 20.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08976 | 112.79 | 527894 HOBBS_INT 6 230 527903 HOBBS_PLT3 1 18.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08979 | 112.36 | 527965 KIOWA 7 345 528027 RDRUNNER 7 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08979 | 112.36 | 528015 PHANTOM 7 345 528027 RDRUNNER 7 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08979 | 112.41 | 528024 RR_SVC_HV 3 115 528021 RDRUNNR_SVC1 15.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08979 | 112.68 | 528025 RDRUNNER 3 115 587990 GEN-2016-121 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08979 | 112.42 | 528185 N_LOVING 7 345 3WXFMR HYO1063400-1 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08979 | 112.41 | 528185 N_LOVING 7 345 528223 CHINA_DRAW 7 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08979 | 112.36 | 528222 CHINA_DRAW 3 115 528225 CD_SVC_HV 3 115 Z1
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08981 | 112.34 | 528333 LE-WEST_SUB3 115 528334 LE-NRTH_INT3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08979 | 112.42 | 528341 LE-SANANDRS3 115 528627 LE-TXACO_TP3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08979 | 112.38 | 528348 BUCKEYE_TP 3 115 528627 LE-TXACO_TP3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08978 | 112.62 | 528394 QUAHADA 3 115 528396 XTO_BIGEDDY3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.0898 | 112.33 | 528463 SANGER_SW 3 115 528575 OXYPERMIAN 3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.0898 | 112.33 | 528463 SANGER_SW 3 115 762442 G18-004-TAP 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08979 | 112.63 | 528568 MONUMNT_TP 3 115 528581 BYRD_TP 3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.0898 | 112.38 | 528574 OXY_NHU_RCF3 115 528575 OXYPERMIAN 3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08979 | 112.69 | 528617 LE-WAITS 2 69.0 528325 LE-WAITS 3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08979 | 112.61 | 528617 LE-WAITS 2 69.0 528714 LE-FORT_SW 2 69.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08979 | 112.42 | 528622 LE-SANANDRS2 69.0 528341 LE-SANANDRS3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08979 | 112.97 | 528626 LE-PLNSINT 2 69.0 526928 PLAINS_INT 3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08979 | 112.97 | 528626 LE-PLNSINT 2 69.0 528709 LE-PLNSGOAB2 69.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08979 | 112.63 | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08979 | 112.69 | 528669 LE-STKLDRTP2 69.0 528740 LE-PLANS_SW2 69.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08979 | 112.85 | 528709 LE-PLNSGOAB2 69.0 528740 LE-PLANS_SW2 69.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08979 | 112.63 | 528709 LE-PLNSGOAB2 69.0 528747 LE-ALLRED 2 69.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08979 | 112.61 | 528714 LE-FORT_SW 2 69.0 528718 LE-NEWTEX 2 69.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08979 | 112.69 | 528735 LE-PLAINSUB2 69.0 528740 LE-PLANS_SW2 69.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08968 | 112.41 | 530583 POSTROCK7 345 588654 G17-021-TAP 345 2
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08979 | 112.41 | 531213 SANTAFE3 115 531408 PIERCVL3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08948 | 112.33 | 531451 MINGO 7 345 531465 SETAB 7 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08977 | 112.62 | 531501 BUCKNER7 345 531502 CIMRRN 7 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08977 | 112.62 | 531502 CIMRRN 7 345 531503 CIMRRN 1 34.5 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08965 | 112.32 | 531510 HARBNGR3 115 3WXFMR HARBGR345 _1 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08978 | 112.64 | 532663 LEC U5 24.0 532854 LEC U5 6 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08978 | 112.64 | 532853 LAWHILL6 230 532854 LEC U5 6 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08978 | 112.69 | 542951 HAW G5 1 22.0 543665 HAWTHN5 161 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08977 | 112.74 | 542955 LAC G1 1 22.0 542981 LACYGNE7 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08977 | 112.72 | 542956 LAC G2 1 24.0 542981 LACYGNE7 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08977 | 112.76 | 542957 IAT G1 1 24.0 542982 IATAN 7 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08977 | 112.82 | 542962 IAT G2 1 24.5 542982 IATAN 7 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08979 | 112.61 | 542966 WGARDNR5 161 543105 BULLCRK5 161 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.09226 | 112.16 | 560022 CRAWFISH_DR 345 762216 G17-151TAP 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.09195 | 113.18 | 560022 CRAWFISH_DR 345 762467 G18-015-TAP 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08979 | 108.98 | 560022 CRAWFISH_DR 345 763087 GEN-2018-073 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.09307 | 113.55 | 560022 CRAWFISH_DR 345 763215 G18-092-TAP 345 2
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08979 | 113.05 | 560252 G10-14 345 560253 G10-14-1 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08979 | 112.78 | 560253 G10-14-1 115 560254 G10-14-SUB1 34.5 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08979 | 112.78 | 560253 G10-14-1 115 560255 G10-14-SUB2 34.5 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08979 | 112.63 | 560581 G06-44-2 34.5 523111 NOVUS1 3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08979 | 112.68 | 560582 G06-44-3 34.5 560577 G06-44 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08979 | 112.66 | 560583 G06-44-4 34.5 560577 G06-44 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08979 | 112.32 | 560757 ASGI13_02_1 69.0 560758 ASGI13_02_2 34.5 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08979 | 112.32 | 560757 ASGI13_02_1 69.0 562731 WHEATLAND 69.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08979 | 112.33 | 560763 ASGI13_03_1 115 560761 ASGI13_03_2 34.5 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08979 | 112.76 | 562015 FIREWHEEL1 34.5 523215 FREWHELCOL17 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08979 | 112.76 | 562016 FIREWHEEL2 34.5 523215 FREWHELCOL17 345 2
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08979 | 112.31 | 562323 AGI1202&1305 115 562324 AGI1202&1305 34.5 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08979 | 112.32 | 562727 LESBIA 115 562728 SANJONTAP 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08979 | 112.32 | 562728 SANJONTAP 115 562729 CAPROCKTAP1 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08979 | 112.32 | 562730 CAPROCKTAP2 69.0 562729 CAPROCKTAP1 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08979 | 112.32 | 562730 CAPROCKTAP2 69.0 562731 WHEATLAND 69.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08979 | 112.72 | 563171 G15082_2 34.5 563170 G15082_1 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08979 | 112.4 | P11:13.8:AEPW:COM1-1
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08979 | 112.41 | P11:13.8:AEPW:COM2-1
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08979 | 112.41 | P11:13.8:AEPW:COM3-1
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08979 | 112.42 | P11:18:AEPW:WELSH1-1
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08979 | 112.42 | P11:18:AEPW:WELSH3-1
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08979 | 112.42 | P11:24:AEPW:PIRKEY 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08979 | 112.39 | P11:24:AEPW:SWS3-1
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08979 | 112.39 | P11:24:AEPW:TURKCOAL
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08992 | 112.7 | P12:138:AEPW-OMPA:DUNCAN-4:OMDUNCN4
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08979 | 112.66 | P12:138:AEPW:112GORE4:SNYDER-4
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08979 | 112.66 | 5841_Dup1
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08988 | 111.96 | 584560 GEN-2015-014 115 584561 G15-014XFMR1 34.5 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08987 | 112.65 | P12:138:AEPW:SANTAFE:DUNCAN-4
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08979 | 112.68 | 587991 G16-121XFMR1 34.5 587990 GEN-2016-121 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08979 | 112.62 | 588480 A16-010_SUB 115 3WXFMR A16-010_SUB 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08992 | 112.7 | P12:138:AEPW:DUNCAN-4:L.E.S.-4
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08979 | 112.06 | 588761 G17-033XFMR1 34.5 588760 GEN-2017-033 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08979 | 112.06 | 588765 G17-033XFMR2 34.5 588760 GEN-2017-033 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08979 | 112.63 | 588861 G17-047XFMR1 34.5 588860 GEN-2017-047 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08941 | 112.2 | P12:138:AEPW:ELKCTY-4:CLINTJC4
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08979 | 112.64 | 589381 G17-100XFMR1 34.5 589380 GEN-2017-100 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08953 | 112.39 | P12:138:AEPW:HOB-JCT4:ELKCTY-4
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08979 | 112.64 | P12:138:AEPW:SHERID4:112GORE4
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08977 | 112.61 | P12:230:AEPW:SWEETWT6:BUFFCK6
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08977 | 112.66 | P12:230:AEPW:SWEETWT6:ROARK6
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.09219 | 114.5 | P12:345:AEPW:L.E.S7:TERRYRD7
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.09219 | 114.49 | P12:345:AEPW:L.E.S7:TERRYRD7
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.09218 | 114.47 | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.09273 | 114.61 | P12:345:AEPW-OKGE:L.E.S.-7:GRACMNT7
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.09273 | 114.58 | P12:345:AEPW-OKGE:L.E.S.-7:GRACMNT7
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08975 | 112.4 | P12:345:AEPW-OKGE:PITTSB-7:SEMINOL7
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.09286 | 115.66 | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08979 | 112.66 | P22:345:AMMO::LABADIE:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08979 | 112.66 | P22:345:AMMO::LABADIE:2
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08979 | 112.66 | P22:345:AMMO::LABADIE:3
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08979 | 112.66 | P22:345:AMMO::LABADIE:4
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08979 | 112.65 | P22:345:AMMO::RUSHISLAND:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08979 | 112.64 | P22:345:AMMO::RUSHISLAND:2
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.0898 | 112.41 | P13:138-13.8:AEPW:COMANC-4_#2
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08802 | 111.28 | P13:138-230:AEPW:ELKCTY-4
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08981 | 112.4 | P13:138-24:AEPW:S.W.S.-4
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.0898 | 112.39 | P13:138-24:AEPW:TURK 4
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08988 | 112.63 | P13:138-345:AEPW:L.E.S.-4_#1
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08996 | 112.75 | P13:138-345:AEPW:L.E.S.-4_#2
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08981 | 112.67 | P23:500:EES-EAI:KEO:B4941
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08981 | 112.66 | P23:500:EES-EAI:KEO:B4921
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08979 | 112.61 | P11:26:EES-EAI:INDEP2:1:D401
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08979 | 112.61 | P11:26:EES-EAI:INDEP2:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08979 | 112.61 | P13:500:EES-EAI:INDEP2:MT2
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.0898 | 112.65 | P23:500:EES-EAI:INDEP2:B6126
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.0898 | 112.64 | P23:500:EES-EAI:PD:INDEP2:LN:FK479
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08977 | 112.61 | P13:230-34.5:AEPW:BUFFCK6
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08977 | 112.67 | P13:230-34.5:AEPW:ROARK6
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08979 | 112.41 | P13:69-13.8:AEPW:COMANC-2
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08979 | 112.66 | P11:024:DPC:ALMA2:6
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08979 | 112.62 | P11:18:ITCM:EMERYGT1:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08979 | 112.63 | P11:18:ITCM:EMERYGT2:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08979 | 112.63 | P11:161:ITCM:MGS CT1:1C
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08979 | 112.63 | P11:161:ITCM:MGS CT2:2C
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08977 | 112.64 | 652537 WHITE 3 345 659286 DEERCREK-BE3 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08977 | 112.64 | 659286 DEERCREK-BE3 345 3WXFMR DEERCRK KU1A 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08979 | 112.63 | 672601 BD 4 230 672306 BD 6G 18.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08979 | 112.63 | 672610 POPLAR 4 230 672310 POPLAR 1G 18.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08979 | 112.63 | 672610 POPLAR 4 230 672311 POPLAR 2G 18.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08979 | 112.62 | 672621 SHAND 4 230 672321 SHAND 1G 18.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08979 | 112.61 | 672649 CODETTE 4 230 672650 NIPAWIN 4 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08979 | 112.62 | 672696 BRADA 4 230 672699 NBEC 4 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08979 | 112.69 | P23:345:MDU::COYOTE::5707-5712-5715::::
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08979 | 112.84 | P23:345:MEC:CBEC 905
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08979 | 112.81 | P23:345:MEC:CBEC 908
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08979 | 112.64 | P23:345:MEC:GDMEC 908
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08979 | 112.74 | P23:345:MEC:RAUN 0180
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08979 | 112.8 | P23:345:MEC:RAUN 0210
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08979 | 112.75 | P23:345:MEC:LOUISA 954
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08979 | 112.75 | P23:345:MEC:LOUISA 964
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08979 | 112.61 | P21:115:XEL:AUTO-SINGLE:CHEMOLT7:LSPOWER7:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08979 | 112.65 | P21:115:XEL:AUTO-SINGLE:COLVILL7:CANONFLSG7:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08979 | 112.61 | P21:115:XEL:AUTO-SINGLE:FARIBALTP7:FARIBALTGEN:Z
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08979 | 112.7 | P21:230:OTP:AUTO-SINGLE:SQBUTTE4:YNG24:1
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08979 | 112.69 | P23:345:OTP:CENTER 3:3215(1)
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08979 | 112.69 | P23:345:OTP:CENTER 3:3225(1)
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08979 | 112.63 | P12:230:UMZW:# 687 #: FT IN SD. FT-BG1 LINE FAULT
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08979 | 112.63 | P12:230:UMZW:# 3617 #: FT IN SD. FT-BG2 LINE FAULT
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08979 | 111.33 | 760494 GEN-2017-146 230 760498 G17-146-TAP 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08979 | 111.32 | 760495 G17-146-XFM1 34.5 760494 GEN-2017-146 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08979 | 112.05 | 761356 G17-239-XFMR 34.5 761355 GEN-2017-239 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08979 | 112.05 | 761359 G17-239-XFMR 34.5 761355 GEN-2017-239 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08979 | 112.23 | 761797 G17-187XFM1 34.5 761796 GEN-2017-187 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08979 | 112.23 | 761800 G17-187XFM2 34.5 761796 GEN-2017-187 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08979 | 107.16 | 762132 GEN-2017-158 230 763252 G18-099-XFM1 34.5 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08979 | 107.16 | 762132 GEN-2017-158 230 763255 G18-099-XFM2 34.5 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08979 | 107.74 | 762133 G17-158XFM1 34.5 762132 GEN-2017-158 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08979 | 107.74 | 762136 G17-158XFM2 34.5 762132 GEN-2017-158 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08979 | 109.9 | 762216 G17-151TAP 345 762217 GEN-2017-151 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.09226 | 113.55 | 762216 G17-151TAP 345 762467 G18-015-TAP 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08979 | 111.85 | 762218 G17-151XFM1 34.5 762217 GEN-2017-151 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08979 | 111.85 | 762221 G17-151XFM2 34.5 762217 GEN-2017-151 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08979 | 111.85 | 762224 G17-151XFM3 34.5 762217 GEN-2017-151 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08979 | 111.85 | 762227 G17-151XFM4 34.5 762217 GEN-2017-151 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08979 | 112.36 | 762438 GEN-2018-004 115 762442 G18-004-TAP 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08979 | 110.89 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08979 | 111.7 | 762461 G18-015-XFM1 34.5 762460 GEN-2018-015 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08979 | 111.7 | 762464 G18-015-XFM2 34.5 762460 GEN-2018-015 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.09114 | 113.07 | 762467 G18-015-TAP 345 763215 G18-092-TAP 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08979 | 110.18 | 763087 GEN-2018-073 345 763088 G18-073-XFM1 34.5 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08979 | 111.33 | 763087 GEN-2018-073 345 763091 G18-073-XFM2 34.5 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08979 | 107.16 | 763120 GEN-2018-081 230 763121 G18-081-XFM1 34.5 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08979 | 109.42 | 763120 GEN-2018-081 230 764011 G19-074-XFM1 34.5 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08979 | 110.21 | 763208 GEN-2018-092 345 763215 G18-092-TAP 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08979 | 111.37 | 763208 GEN-2018-092 345 763220 G18-092-XFM1 34.5 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08979 | 111.37 | 763208 GEN-2018-092 345 763223 G18-092-XFM2 34.5 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08979 | 108.87 | 763241 GEN-2018-097 230 763242 G18-097-XFM1 34.5 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08979 | 109.78 | 763241 GEN-2018-097 230 763296 G18-111-XFM1 34.5 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08979 | 109.14 | 763241 GEN-2018-097 230 763307 G18-112-XFM1 34.5 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08979 | 109.14 | 763241 GEN-2018-097 230 763310 G18-112-XFM2 34.5 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08979 | 108.87 | 763241 GEN-2018-097 230 763395 G18-124-XFM1 34.5 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08979 | 108.87 | 763241 GEN-2018-097 230 763398 G18-124-XFM2 34.5 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08979 | 112.29 | 763318 GEN-2018-115 345 763319 G18-115-XFM1 34.5 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08979 | 112.75 | 763340 GEN-2018-117 230 763341 G18-117-XFM1 34.5 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08979 | 108.51 | 763483 GEN-2019-003 230 763484 G19-003-XFM1 34.5 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08979 | 111.19 | 763483 GEN-2019-003 230 763605 G19-021-XFM1 34.5 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08979 | 111.9 | 763516 GEN-2019-011 345 763517 G19-011-XFM1 34.5 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08979 | 112.26 | 763879 GEN-2019-056 115 763880 G19-056XFM1 34.5 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08928 | 112.68 | P42:345:OKGE:SB_BVTY7305
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08971 | 112.43 | P23:345:WERE:BUFF_345-534::
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08971 | 112.43 | P23:345:WERE:BUFF_345-543::
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08976 | 112.78 | P23:345:WERE:JEC_345-15::
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08975 | 112.75 | P23:345:WERE:JEC_345-16::
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08976 | 112.78 | P23:345:WERE:JEC_345-19::
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08976 | 112.78 | P23:345:WERE:JEC_345-20::
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08979 | 112.95 | P23:345:WERE:WOLF_345-50::
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08979 | 112.95 | P23:345:WERE:WOLF_345-60::
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.0898 | 112.43 | P42:345:AEPW:WELSH CB 10620 NBTB+FAULT
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.09286 | 114.21 | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.09305 | 114.99 | P42:345:AEPW:LAWTON EASTSIDE CB 3413A NBTB+FAULT
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.0934 | 115.4 | P42:345:AEPW:LAWTON EASTSIDE CB 3425A NBTB+FAULT
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.09299 | 115.86 | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08993 | 112.31 | P42:345:AEPW:PITTSBURG CB 3441A NBTB+FAULT
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08975 | 112.4 | P42:345:AEPW:PITTSBURG CB 3445A NBTB+FAULT
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.09219 | 114.49 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.09219 | 114.49 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.09219 | 114.47 | P42:345:AEPW:TERRYRD_CB_3421A_NBTB
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08978 | 112.75 | P23:345:KCPL:LACYGNE_R2-5::LACYGU2-LACYGNE-STILWELL
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.0898 | 112.43 | P23:345:AEPW:WELSH CB 10620 NBTB
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.09286 | 114.54 | P23:345:AEPW:OKLAUNION CB 3401A NBTB
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.09305 | 114.99 | P23:345:AEPW:LAWTON EASTSIDE CB 3413A NBTB
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.0934 | 115.4 | P23:345:AEPW:LAWTON EASTSIDE CB 3425A NBTB
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.09299 | 115.86 | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08993 | 112.31 | P23:345:AEPW:PITTSBURG CB 3441A NBTB
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08975 | 112.4 | P23:345:AEPW:PITTSBURG CB 3445A NBTB
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.09219 | 114.49 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.09219 | 114.49 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.09219 | 114.47 | P23:345:AEPW:TERRYRD_CB_3421A_NBTB
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.0901 | 112.62 | P12:138:AEPW:S.W.S.-4:L.E.S.-4
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08979 | 112.65 | P11:115:SUNC:GARDENCITY_S2:97:531459(2)
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.09236 | 114.72 | P23:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.09487 | 117.32 | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.09236 | 114.72 | P42:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB+FAULT
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.09487 | 117.32 | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08178 | 109.51 | P42:345:OKGE:SB_BVTY7315_PRE19S
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08948 | 112.33 | P23:345:SUNC:MO_BRK182
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08948 | 112.33 | P23:345:SUNC:MO_BRK382
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08977 | 112.42 | P21:345:UMZW:# 725 #: GI IN NE. GI-SWEET LINE FAULT
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.09195 | 112.8 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.0898 | 112.41 | P12:138-13.8:AEPW:COMANC-4_#1
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.08802 | 111.26 | P12:230:AEPW:ELKCITY6:CHISHOLM6
Thermal | 05ALL | 1 | 23SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.09184 | 113.54 | P12:230:AEPW:SWEETWT6:CHISHOLM6
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 511458 ELKCTY-4 138 998036 ELKCTY-6 _1 138 1 |  | 330 | 0.10515 | 112.44 | P12:345:OKGE-AEPW:BKRBKR371::::
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 511458 ELKCTY-4 138 998036 ELKCTY-6 _1 138 1 |  | 330 | 0.10515 | 112.78 | P12:345:OKGE-AEPW:BKRBKR371::::
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.10515 | 108.04 | P12:345:OKGE-AEPW:BKRBKR371::::
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.10515 | 108.6 | P12:345:OKGE-AEPW:BKRBKR371::::
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 511490 ELKCITY6 230 998036 ELKCTY-6 _1 138 1 |  | 330 | 0.10515 | 112.79 | P12:345:OKGE-AEPW:BKRBKR371::::
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 511490 ELKCITY6 230 998036 ELKCTY-6 _1 138 1 |  | 330 | 0.10515 | 113.27 | P12:345:OKGE-AEPW:BKRBKR371::::
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.19791 | 119.61 | P42:345:SPS:YOAKUM:J18####:SLG1:EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.19791 | 119.61 | P43:345:SPS:YOAKUM:TF#####:SLG:EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.19791 | 119.61 | P42:345:SPS:YOAKUM:J17####:SLG:EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.19791 | 119.61 | P42:345:SPS:YOAKUM:J18####:SLG2:EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.19022 | 109.07 | 523097 HITCHLAND 7 345 523961 POTTER_CO 7 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.19888 | 114.37 | 525832 TUCO_INT 7 345 526936 YOAKUM_345 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.19911 | 121.79 | 526936 YOAKUM_345 345 527896 HOBBS_INT 7 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.1993 | 109.51 | P42:345:OKGE:SB_BVTY7315_PRE19S
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 511458 ELKCTY-4 138 998036 ELKCTY-6 _1 138 1 |  | 330 | 0.10515 | 112.44 | P12:345:OKGE-AEPW:BKRBKR371::::
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 511458 ELKCTY-4 138 998036 ELKCTY-6 _1 138 1 |  | 330 | 0.10515 | 112.78 | P12:345:OKGE-AEPW:BKRBKR371::::
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.10515 | 108.04 | P12:345:OKGE-AEPW:BKRBKR371::::
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.10515 | 108.6 | P12:345:OKGE-AEPW:BKRBKR371::::
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 511490 ELKCITY6 230 998036 ELKCTY-6 _1 138 1 |  | 330 | 0.10515 | 112.79 | P12:345:OKGE-AEPW:BKRBKR371::::
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 511490 ELKCITY6 230 998036 ELKCTY-6 _1 138 1 |  | 330 | 0.10515 | 113.27 | P12:345:OKGE-AEPW:BKRBKR371::::
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.19791 | 119.61 | P42:345:SPS:YOAKUM:J18####:SLG1:EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.19791 | 119.61 | P43:345:SPS:YOAKUM:TF#####:SLG:EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.19791 | 119.61 | P42:345:SPS:YOAKUM:J17####:SLG:EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.19791 | 119.61 | P42:345:SPS:YOAKUM:J18####:SLG2:EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.19022 | 109.07 | 523097 HITCHLAND 7 345 523961 POTTER_CO 7 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.19888 | 114.37 | 525832 TUCO_INT 7 345 526936 YOAKUM_345 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.19911 | 121.79 | 526936 YOAKUM_345 345 527896 HOBBS_INT 7 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.1993 | 109.51 | P42:345:OKGE:SB_BVTY7315_PRE19S
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 511458 ELKCTY-4 138 998036 ELKCTY-6 _1 138 1 |  | 330 | 0.10515 | 112.44 | P12:345:OKGE-AEPW:BKRBKR371::::
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 511458 ELKCTY-4 138 998036 ELKCTY-6 _1 138 1 |  | 330 | 0.10515 | 112.78 | P12:345:OKGE-AEPW:BKRBKR371::::
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.10515 | 108.04 | P12:345:OKGE-AEPW:BKRBKR371::::
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.10515 | 108.6 | P12:345:OKGE-AEPW:BKRBKR371::::
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 511490 ELKCITY6 230 998036 ELKCTY-6 _1 138 1 |  | 330 | 0.10515 | 112.79 | P12:345:OKGE-AEPW:BKRBKR371::::
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 511490 ELKCITY6 230 998036 ELKCTY-6 _1 138 1 |  | 330 | 0.10515 | 113.27 | P12:345:OKGE-AEPW:BKRBKR371::::
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.19791 | 119.61 | P42:345:SPS:YOAKUM:J18####:SLG1:EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.19791 | 119.61 | P43:345:SPS:YOAKUM:TF#####:SLG:EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.19791 | 119.61 | P42:345:SPS:YOAKUM:J17####:SLG:EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.19791 | 119.61 | P42:345:SPS:YOAKUM:J18####:SLG2:EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.19022 | 109.07 | 523097 HITCHLAND 7 345 523961 POTTER_CO 7 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.19888 | 114.37 | 525832 TUCO_INT 7 345 526936 YOAKUM_345 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.19911 | 121.79 | 526936 YOAKUM_345 345 527896 HOBBS_INT 7 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.1993 | 109.51 | P42:345:OKGE:SB_BVTY7315_PRE19S
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 511458 ELKCTY-4 138 998036 ELKCTY-6 _1 138 1 |  | 330 | 0.10515 | 112.44 | P12:345:OKGE-AEPW:BKRBKR371::::
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 511458 ELKCTY-4 138 998036 ELKCTY-6 _1 138 1 |  | 330 | 0.10515 | 112.78 | P12:345:OKGE-AEPW:BKRBKR371::::
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.10515 | 108.04 | P12:345:OKGE-AEPW:BKRBKR371::::
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.10515 | 108.6 | P12:345:OKGE-AEPW:BKRBKR371::::
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 511490 ELKCITY6 230 998036 ELKCTY-6 _1 138 1 |  | 330 | 0.10515 | 112.79 | P12:345:OKGE-AEPW:BKRBKR371::::
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 511490 ELKCITY6 230 998036 ELKCTY-6 _1 138 1 |  | 330 | 0.10515 | 113.27 | P12:345:OKGE-AEPW:BKRBKR371::::
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.19791 | 119.61 | P42:345:SPS:YOAKUM:J18####:SLG1:EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.19791 | 119.61 | P43:345:SPS:YOAKUM:TF#####:SLG:EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.19791 | 119.61 | P42:345:SPS:YOAKUM:J17####:SLG:EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.19791 | 119.61 | P42:345:SPS:YOAKUM:J18####:SLG2:EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.19022 | 109.07 | 523097 HITCHLAND 7 345 523961 POTTER_CO 7 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.19888 | 114.37 | 525832 TUCO_INT 7 345 526936 YOAKUM_345 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.19911 | 121.79 | 526936 YOAKUM_345 345 527896 HOBBS_INT 7 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.1993 | 109.51 | P42:345:OKGE:SB_BVTY7315_PRE19S
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 511458 ELKCTY-4 138 998036 ELKCTY-6 _1 138 1 |  | 330 | 0.10515 | 112.44 | P12:345:OKGE-AEPW:BKRBKR371::::
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 511458 ELKCTY-4 138 998036 ELKCTY-6 _1 138 1 |  | 330 | 0.10515 | 112.78 | P12:345:OKGE-AEPW:BKRBKR371::::
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.10515 | 108.04 | P12:345:OKGE-AEPW:BKRBKR371::::
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.10515 | 108.6 | P12:345:OKGE-AEPW:BKRBKR371::::
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 511490 ELKCITY6 230 998036 ELKCTY-6 _1 138 1 |  | 330 | 0.10515 | 112.79 | P12:345:OKGE-AEPW:BKRBKR371::::
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 511490 ELKCITY6 230 998036 ELKCTY-6 _1 138 1 |  | 330 | 0.10515 | 113.27 | P12:345:OKGE-AEPW:BKRBKR371::::
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.19791 | 119.61 | P42:345:SPS:YOAKUM:J18####:SLG1:EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.19791 | 119.61 | P43:345:SPS:YOAKUM:TF#####:SLG:EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.19791 | 119.61 | P42:345:SPS:YOAKUM:J17####:SLG:EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.19791 | 119.61 | P42:345:SPS:YOAKUM:J18####:SLG2:EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.19022 | 109.07 | 523097 HITCHLAND 7 345 523961 POTTER_CO 7 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.19888 | 114.37 | 525832 TUCO_INT 7 345 526936 YOAKUM_345 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.19911 | 121.79 | 526936 YOAKUM_345 345 527896 HOBBS_INT 7 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.1993 | 109.51 | P42:345:OKGE:SB_BVTY7315_PRE19S
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 511458 ELKCTY-4 138 998036 ELKCTY-6 _1 138 1 |  | 330 | 0.10462 | 112.44 | P12:345:OKGE-AEPW:BKRBKR371::::
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 511458 ELKCTY-4 138 998036 ELKCTY-6 _1 138 1 |  | 330 | 0.10462 | 112.78 | P12:345:OKGE-AEPW:BKRBKR371::::
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.10462 | 108.04 | P12:345:OKGE-AEPW:BKRBKR371::::
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.10462 | 108.6 | P12:345:OKGE-AEPW:BKRBKR371::::
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 511490 ELKCITY6 230 998036 ELKCTY-6 _1 138 1 |  | 330 | 0.10462 | 112.79 | P12:345:OKGE-AEPW:BKRBKR371::::
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 511490 ELKCITY6 230 998036 ELKCTY-6 _1 138 1 |  | 330 | 0.10462 | 113.27 | P12:345:OKGE-AEPW:BKRBKR371::::
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14904 | 112.73 | P23:345:KCPL-WERE:237LACYGNE_R1-6::LACYGU1-LACYGNE-NEOSHO
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14902 | 112.64 | P11:230:WERE:LECU5_GEN::
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14902 | 112.63 | P11:161:GMO:DOGWOOD_COMBINED_CYCLE_UNIT_OUTAGE_1_1
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14909 | 111.16 | P11:115:SPS:MUSTANG1&3:153MW::::
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14976 | 114.61 | P12:230:SPS:K37::1_TOLK_LAMB:::
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14922 | 112.61 | P12:230:SPS:K43::1_PRNGLE_HARR_E:::
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14907 | 112.37 | P12:230:SPS:K44::1_EPLNT_HARRW:::
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.1487 | 112.79 | P12:115:SPS:T04::1_TRBLNC_CASTRO:::
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14901 | 112.19 | P12:115:SPS:T13::1_TAYLOR_WHOBBS:::
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.149 | 112.31 | P12:115:SPS:T14::1_MADDOX_TAYLOR:::
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 113.09 | P12:115:SPS:T21::1_GRSSLND_GRAHAM:::
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14904 | 112.41 | P12:115:SPS:T23::1_PCA_POTJCT:::
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.62 | P12:115:SPS:T24B::1_RSWLL_BRSHRF:::
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14911 | 112.64 | P12:115:SPS:T26::1_CHAVES_RSWLCTY:::
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.1507 | 113.18 | P12:115:SPS:T28A::1_LAMTON_PLANTX:::
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14961 | 112.67 | P12:115:SPS:T29::1_LAMTON_HALECTR:::
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.15057 | 113.96 | P12:115:SPS:T30::1_LAMB_HOCKLY:::
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.15057 | 113.13 | P12:115:SPS:T31::1_HOCKLY_SUNDWN:::
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14896 | 112.63 | P12:115:SPS:T35::1_TERRY_YOAKUM:::
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.1491 | 113.32 | P12:115:SPS:T45::1_NORRIS_OASIS:::
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14898 | 112.4 | P12:115:SPS:T57::1_MUSTG_SEGRVS:::
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.15775 | 113.15 | P12:115:SPS:T59::1_CARGIL_CURRY:::
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14994 | 112.42 | P12:115:SPS:T66::1_RNDALL_HAPPY:::
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14994 | 112.9 | P12:115:SPS:T67::1_HAPPY_KRESS:::
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14908 | 112.39 | P12:115:SPS:T68::1_TUCO_FLOYD:::
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14897 | 113.2 | P12:115:SPS:T71::1_CRLSLE_YUMA:::
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14914 | 112.7 | P12:115:SPS:T81::1_COX_FLOYD:::
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.85 | P12:115:SPS:T83::1_SP-FKFD_ALLEN:::
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14878 | 113.01 | P12:115:SPS:T89::1_DC_N_HIGG:::
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.66 | P12:115:SPS:T91::1_HIGG_RUSSELL:::
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14931 | 112.62 | P12:115:SPS:V04::1_EPLANT_RNDALL:::
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14921 | 112.67 | P12:115:SPS:V07::1_COX_HALECTR:::
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.15055 | 112.95 | P12:115:SPS:V09::1_HALECTR_PLANTX:::
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14871 | 112.83 | P12:115:SPS:V12::1_PLANTX_BAILEY:::
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.62 | P12:115:SPS:V15::1_TUCO_INDANA:::
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14857 | 112.67 | P12:115:SPS:V24::1_WOLFTH_TERRY:::
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.15082 | 112.64 | P12:115:SPS:V26::1_RSWLL_EDDY_N:::
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.98 | P12:115:SPS:V33::1_LUBBS_LYNN:::
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.15004 | 113.85 | P12:115:SPS:V37::1_CASTRO_PLANTX:::
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.75 | P12:115:SPS:V46::1_ALLEN_WHEELCK:::
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14901 | 113.09 | P12:115:SPS:V49::1_YOAKUM_SHLCO2:::
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14932 | 113.26 | P12:115:SPS:V55::1_SUNDWN_TERRY:::
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14906 | 113.09 | P12:115:SPS:V56::1_COCHRAN_SUNDWN:::
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.68 | P12:115:SPS:V62::1_CRLSLE_INDANA:::
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14906 | 112.62 | P12:115:SPS:V70::1_S_GORG_RNDALL:::
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.15027 | 112.65 | P12:115:SPS:V78::2_CURRY_RSVLT:::
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14886 | 112.79 | P12:115:SPS:V81::1_LE-WAIT_LE-LVN:::
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.65 | P12:115:SPS:V95::1_DC_N_SHLCO2:::
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.61 | P12:115:SPS:W11::1_DC_S_SMINLE:::
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14902 | 112.61 | P12:115:SPS:W12::1_SMINLE_DOSS:::
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14898 | 112.68 | P12:115:SPS:W14::1_SMINLE_GAINES:::
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 113.14 | P12:115:SPS:W32::1_PRMTR_FE-CLSIN:::
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.61 | P12:115:SPS:W34::1_JNSDRW_MAPCO:::
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14884 | 112.85 | P12:115:SPS:W35::1_GAINES_JNSDRW:::
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14872 | 112.64 | P12:115:SPS:W36::1_TAYLOR_JNSDRW:::
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.15218 | 113.15 | P12:115:SPS:W40::1_WCANYON_TRBLNC:::
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14933 | 112.71 | P12:115:SPS:W52::1_NEWHART_KRESS:::
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 113.2 | P12:115:SPS:W58::1_NORTON_LOPEZ:::
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.82 | P12:115:SPS:W59::1_LOPEZ_CMPBLL:::
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14913 | 113.15 | P12:115:SPS:W62::1_PLSTHL_CURRY:::
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14915 | 112.62 | P12:115:SPS:W63::1_PLSTHL_CURRY:::
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.96 | P12:115:SPS:W64::1_PLSTHL_FE-CLV:::
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14915 | 113.12 | P12:115:SPS:W65::1_PLSTHL_CURRY:::
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.81 | P12:115:SPS:W66::1_PORTA_GREYHUND:::
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.15218 | 112.61 | P12:115:SPS:W77::1_RNDAL_WCANYON:::
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14906 | 112.64 | P12:115:SPS:W99::1_CAPITAN_CHAVES:::
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.1489 | 113.08 | P12:115:SPS:U14::1_DC_STH_INKBSN:::
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14886 | 113.02 | P12:115:SPS:V15::1_INKBSN_LE-WAT:::
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14932 | 112.74 | P12:115:SPS:U16::1_BSHLND_OUTPST:::
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14932 | 112.73 | P12:115:SPS:U17::1_COLTR_OUTPST:::
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14899 | 112.8 | P12:115:SPS:U19::1_DEAN_PLAINS:::
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14932 | 112.67 | P12:115:SPS:U23::1_COLTR_HILSDE:::
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.13544 | 119.61 | P42:345:SPS:YOAKUM:J18####:SLG1:EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.13544 | 119.61 | P43:345:SPS:YOAKUM:TF#####:SLG:EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.13544 | 119.61 | P42:345:SPS:YOAKUM:J17####:SLG:EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.13544 | 119.61 | P42:345:SPS:YOAKUM:J18####:SLG2:EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.62 | P11:18:HAST:::EGYCTR2G WEC2_LOSS OF WEC 2 GEN_:HV:
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.62 | P13:18-115:HAST:::EGYCNTR7 XFMR G2WEC 2 GSU_:HV:
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14902 | 112.63 | P11:161:GMO:DOGWOOD-COMBINED-CYCLE-UNIT-OUTA:::HV:
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14904 | 112.73 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14902 | 112.75 | P23:345:KCPL:LACYGNE-R2-5:::EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.149 | 112.78 | P11:230:WERE:JECU1-GEN:::HV:
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14902 | 112.64 | P11:230:WERE:LECU5-GEN:::HV:
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.149 | 112.78 | P11:345:WERE:JECU2-GEN:::EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.149 | 112.78 | P11:345:WERE:JECU3-GEN:::EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.95 | P11:345:WERE:WOLFU1-GEN:::EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14895 | 112.43 | P23:345:WERE:BUFF-345-534:::EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14895 | 112.43 | P23:345:WERE:BUFF-345-543:::EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.149 | 112.78 | P23:345:WERE:JEC-345-15:::EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14899 | 112.75 | P23:345:WERE:JEC-345-16:::EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.149 | 112.78 | P23:345:WERE:JEC-345-19:::EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.149 | 112.78 | P23:345:WERE:JEC-345-20:::EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.95 | P23:345:WERE:WOLF-345-50:::EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.95 | P23:345:WERE:WOLF-345-60:::EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.89 | P11:022:NPPD:COOPER1G:1:983:::
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14898 | 112.92 | P11:023:NPPD:GENTLM1G:1:757:::
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14898 | 112.94 | P11:024:NPPD:GENTLM2G:2:757:::
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.149 | 112.75 | P13:345:OPPD:NEBCTY1G:::EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14899 | 112.78 | P13:345:OPPD:NEBCTY2G:::EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.77 | P22:345:OPPD:S3458 NEBCTY1G:LT::EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.149 | 112.75 | P22:345:OPPD:S3458 NEBCTY1G:::EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.81 | P22:345:OPPD:S3458 NEBCTY2G:LT::EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14899 | 112.78 | P22:345:OPPD:S3458 NEBCTY2G:::EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.77 | P23:345:OPPD:S3458 NEBCTY1G:LT::EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.149 | 112.75 | P23:345:OPPD:S3458 NEBCTY1G:::EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.81 | P23:345:OPPD:S3458 NEBCTY2G:LT::EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14899 | 112.78 | P23:345:OPPD:S3458 NEBCTY2G:::EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.4 | P12:115:SUNC:PLYMELL-PIERCEVILLE:::HV::
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14901 | 112.64 | P11:018:UMZB:# 5 #:: DCS IN SD. DEERCREEK_MV::
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14902 | 112.61 | P11:022:UMZB:# 15 #:: LO IN ND. LELAND OLDS 1_MV::
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14902 | 112.65 | P11:020:UMZB:# 16 #:: LO IN ND. LELAND OLDS 2_MV::
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14901 | 112.7 | P11:023:UMZB:# 31 #:: AVS IN ND. ANTELOPE VALLEY 1_MV::
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14901 | 112.7 | P11:023:UMZB:# 32 #:: AVS IN ND. ANTELOPE VALLEY 2_MV::
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14898 | 112.9 | P11:024:UMZB:# 33 #:: LRS IN WY. LARAMIE RIVER STATION 1_MV::
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.63 | P12:230:UMZW:# 687 #:: FT IN SD. FT-BG1 BRANCH FAULT:HV:
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.63 | P12:230:UMZW:# 3617 #:: FT IN SD. FT-BG2 BRANCH FAULT:HV:
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.63 | P12:230:UMZW:# 4038 #:: BG-FT IN SD. FAULT FOR TRANSMISSION CIRCUIT (BG-FT).:HV:
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.63 | P12:230:UMZW:# 4039 #:: BG-FT IN SD. FAULT FOR TRANSMISSION CIRCUIT (BG-FT).:HV:
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.61 | P13:230:UMZW:# 5135 #:: OA IN SD. FAULT ON TRANSFORMER (2).:HV:
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.61 | P13:230:UMZW:# 5136 #:: OA IN SD. FAULT ON TRANSFORMER (3).:HV:
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14901 | 112.42 | P21:345:UMZW:# 725 #:: GI IN NE. GI-SWEET BRANCH FAULT:EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14901 | 112.42 | P23:345:UMZW:# 2430 #:: GI IN NE. GI 1492 BKR FAULT:EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14901 | 112.42 | P23:345:UMZW:# 2438 #:: GI IN NE. GI-SWEET BRANCH FAULT & GI 1492 STUCK BKR:EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14906 | 112.37 | P11:138:WFEC:HUGO1:465MW :::
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14899 | 112.4 | P12:345:OKGE-AEPW:BKRBKR20::::
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14939 | 112.75 | P12:345:OKGE:BKRBKR21::::
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14958 | 112.95 | P12:345:OKGE:BKRBKR24::::
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.15146 | 114.47 | P12:345:OKGE-AEPW:BKRBKR25::::
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14894 | 112.42 | P12:345:OKGE:BKRBKR336::::
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14893 | 112.41 | P12:345:OKGE:BKRBKR336_2::::
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.15211 | 114.61 | P12:345:OKGE-AEPW:BKRBKR366::::
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.15211 | 114.58 | P12:345:OKGE-AEPW:BKRBKR366::::
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14959 | 112.87 | P12:345:OKGE:BKRBKR367::::
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14935 | 112.62 | P12:345:OKGE-WFEC:BKRBKR374::::
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14862 | 112.22 | P12:345:OKGE:BKRBKR4193::::
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14862 | 112.22 | P12:345:OKGE:BKRBKR4194::::
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14846 | 112.28 | P12:345:OKGE-SPS:BKRBKR4201::::
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14846 | 112.28 | P12:345:OKGE-SPS:BKRBKR4202::::
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14893 | 112.35 | P12:345:OKGE:BKRBKR443NEW::::
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14893 | 112.35 | P12:345:OKGE:BKRBKR443NEW2::::
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14897 | 112.88 | P12:345:OKGE:BKRBKR604::::
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14896 | 112.94 | P12:345:OKGE:BKRBKR604_2::::
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14855 | 112.62 | P42:345:OKGE:SB_ARIA7381::::
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.1569 | 116.05 | P42:345:OKGE:SB_BVTY7387::::
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14938 | 112.68 | P42:345:OKGE:SB_SPCK7383::::
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14902 | 112.64 | P11:115:SUNC:GARDENCITY_S2:103:531459(2):HV:
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14902 | 112.64 | P11:115:SUNC:FORTDDODGE_4:157:539670(4):HV:
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.62 | P11:345:599:CIMARRON1WIND:200:531603(1):EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.92 | P13:115:SUNC:HOLCOMB_GSU:::HV:
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14902 | 112.64 | P13:115:SUNC:S2_GSU:::HV:
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14902 | 112.64 | P13:115:SUNC:FORTDODGE_GSU:::HV:
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14901 | 112.62 | P23:345:SUNC:BU_BRK682:::EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.71 | 300003 1THLG3 24.0 301503 7THOMHLGSU3 345 3
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.71 | 300049 7THOMHL 345 301503 7THOMHLGSU3 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.66 | P11:20:AMMO:1LAB�� G1:1
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.66 | P11:20:AMMO:1LAB�� G2:2
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.83 | P11:345:AMMO::CALLAWAY:1
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.66 | P11:345:AMMO::LABADIE:3
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.66 | P11:345:AMMO::LABADIE:4
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.66 | P11:345:AMMO::RUSHISLAND:U1
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.66 | P11:345:AMMO::RUSHISLAND:U2
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.64 | P11:138:AMMO::SIOUX:2
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.64 | P12:765:AEP:AEP ROCKP-AEP JEFF 765
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.61 | P11:HV:EES::1ISES U1:1
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.61 | P11:EHV:EES::1ISES U2:1
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.42 | P11:HV:EES::PIRKEY 1:1
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.42 | P11:EHV:EES::WELSH3-1:1
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.39 | P11:HV:EES::TURKCOAL:1
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.61 | P12:HV:EES::5ISES%:1
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.61 | P12:EHV:EES::8ISES%:1
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.82 | P12:EHV:EES::7CALAWY 1:1
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14904 | 112.39 | P12:HV:EES::TURK 4%:1(1)
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.64 | 344011 7HUGHES 345 344012 7HPW-N 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.66 | 344884 7LABADIE1 345 344894 1LAB G1 20.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.66 | 344885 7LABADIE2 345 344895 1LAB G2 20.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.66 | 344886 7LABADIE3 345 344896 1LAB G3 20.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.66 | 344887 7LABADIE4 345 344897 1LAB G4 20.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.65 | 345667 7RUSH 1 345 345670 1RUSH G1 18.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.65 | 345668 7RUSH 2 345 345671 1RUSH G2 18.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.64 | 345755 4SIOUX 1 138 345756 1SIOUX 1 18.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.64 | 345764 4SIOUX 2 138 345765 1SIOUX 2 18.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.69 | P12:345:MDU::CENTER:COYOTE:1::::
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.69 | P13:345:MDU:COYOTE GSU LOSS:COYOTE::1::::
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.61 | P11:345:MEC:GDMEC CT1
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.61 | P11:345:MEC:GDMEC CT2
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.71 | P11:345:MEC:GDMEC ST
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.9 | P11:345:MEC-NPPD:COOPER 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.8 | P11:24:XEL:AUTO-SINGLE:SHERC31G:1
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.8 | P11:24:XEL:AUTO-SINGLE:SHERC32G:2
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.87 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.73 | P11:20:XEL:AUTO-SINGLE:PRIS31G:1
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.73 | P11:20:XEL:AUTO-SINGLE:PRIS32G:2
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.76 | P11:22:XEL:AUTO-SINGLE:MNTCE31G:1
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.73 | P11:20:XEL:AUTO-SINGLE:KING31G:1
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.77 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.77 | P11:22:GRE:AUTO-SINGLE:GRE-COAL42G:2
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.71 | P11:24:OTP:AUTO-SINGLE:BIGSTN1G:1
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.71 | P11:20:OTP:AUTO-SINGLE:CENTER2G:1
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.63 | P11:22:OTP:AUTO-SINGLE:CENTER1G:1
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.7 | P11:24:OTP:AUTO-SINGLE:COYOTE1G:1
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.63 | P11:24:DPC:AUTO-SINGLE:GENOA53G:3
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.61 | P12:115:XEL:AUTO-SINGLE:CHEMOLT7:LSPOWER7:1
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.65 | P12:115:XEL:AUTO-SINGLE:COLVILL7:CANONFLSG7:1
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.61 | P12:115:XEL:AUTO-SINGLE:FARIBALTP7:FARIBALTGEN:Z
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.7 | P12:230:OTP:AUTO-SINGLE:SQBUTTE4:YNG24:1
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.78 | P13:24-345:XEL:AUTO-SINGLE:SHERC31G:SHERCO3:1
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.78 | P13:24-345:XEL:AUTO-SINGLE:SHERC32G:SHERCO3:1
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.85 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.73 | P13:20-345:XEL:AUTO-SINGLE:PRIS31G:PRISLD3:1
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.73 | P13:20-345:XEL:AUTO-SINGLE:PRIS32G:PRISLD3:2
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.76 | P13:22-345:XEL:AUTO-SINGLE:MNTCE31G:MNTCELO3:1
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.72 | P13:20-345:XEL:AUTO-SINGLE:KING31G:ASKING3:1
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.76 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL41G:GRE-COALCR4:1
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.75 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL42G:GRE-COALCR4:1
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.7 | P13:230-24:OTP:AUTO-SINGLE:BIGSTON4:BIGSTN1G:1
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.7 | P13:20-230:OTP:AUTO-SINGLE:CENTER2G:YNG24:1
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.62 | P13:22-230:OTP:AUTO-SINGLE:CENTER1G:CENTER4:1
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.69 | P13:24-345:OTP:AUTO-SINGLE:COYOTE1G:COYOTE3:1
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.63 | P13:24-161:DPC:AUTO-SINGLE:GENOA53G:GENOA5:1
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.64 | P13:24-161:DPC:AUTO-SINGLE:JPM:ALMA5:1
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.7 | P11:115:XEL:RIV COMBINE CYCLE
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.62 | P12:115:XEL:BDS #2 5
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.62 | P11:115:XEL:HBR #6
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.62 | P11:115:XEL:HBR #7
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.73 | P11:115:XEL:HBR #6 7 8
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.73 | P23:345:XEL:8H14 PRI
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.73 | P23:345:XEL:8H17 PRI AS
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.85 | P23:345:XEL:8N28 SHC
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.78 | P23:345:XEL:8N22 SHC
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.78 | P23:345:XEL:8N17 SHC
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.77 | P23:345:XEL:8N8 MNN
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.72 | P23:345:XEL:8P1 KING
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.72 | P23:345:XEL:8P2 KING
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.62 | P23:115:XEL:5P147 IVH AS
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.61 | P11:18:ALTW:AUTO-SINGLE:EMERYST1:1
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.61 | P11:22:ALTW:AUTO-SINGLE:LANS54G:4
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.74 | P11:22:ALTW:AUTO-SINGLE:ARNOLD1G:1
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.77 | P11:24:ALTW:AUTO-SINGLE:OTTUMW1G:1
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.61 | P13:18-161:ALTW:AUTO-SINGLE:EMERYST1:EMERY5:1
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.61 | P13:22-161:ALTW:AUTO-SINGLE:LANS54G:LANSINGL15:1
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.73 | P13:22-161:ALTW:AUTO-SINGLE:ARNOLD1G:ARNOLD5:1
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.76 | P13:24-161:ALTW:AUTO-SINGLE:OTTUMW1G:OTTUMWA5:1
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.82 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.88 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.75 | P11:22:MEC:AUTO-SINGLE:NEAL3G:3
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.81 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.76 | P11:24:MEC:AUTO-SINGLE:LOUIS31G:1
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.81 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.84 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.74 | P13:345-22:MEC:AUTO-SINGLE:RAUN3:NEAL3G:1
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.8 | P13:345-24:MEC:AUTO-SINGLE:RAUN3:NEAL4G:1
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.74 | P13:345-24:MEC:AUTO-SINGLE:LOUISA3:LOUIS31G:1
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.149 | 112.78 | P11:230:WERE:JECU1_GEN::
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.149 | 112.78 | P11:345:WERE:JECU2_GEN::
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.149 | 112.78 | P11:345:WERE:JECU3_GEN::
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.95 | P11:345:WERE:WOLFU1_GEN::
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14904 | 112.63 | 511435 SNYDER-4 138 588779 TAP_G17-036 138 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14878 | 112.38 | 511446 CL-AFTP4 138 511458 ELKCTY-4 138 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14878 | 112.4 | 511446 CL-AFTP4 138 511463 HOB-JCT4 138 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14911 | 112.63 | 511453 DUNCAN-4 138 511552 DUNCHERTP4 138 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14911 | 112.62 | 511455 D.E.S.-4 138 511552 DUNCHERTP4 138 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14911 | 112.62 | 511455 D.E.S.-4 138 529344 OMDUNE-4 138 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.63 | 511456 O.K.U.-7 345 511565 OKLAUN HVDC7 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 111.6 | 511456 O.K.U.-7 345 588760 GEN-2017-033 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.15219 | 114.54 | 511456 O.K.U.-7 345 763215 G18-092-TAP 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.15233 | 115.11 | 511468 L.E.S.-7 345 762467 G18-015-TAP 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.15127 | 114.48 | 511468 L.E.S.-7 345 763215 G18-092-TAP 345 2
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.29 | 511468 L.E.S.-7 345 763318 GEN-2018-115 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14904 | 112.66 | 511488 112GORE4 138 511510 LAIRGST4 138 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14916 | 112.7 | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14904 | 112.65 | 511500 CACHE4 138 511510 LAIRGST4 138 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14904 | 112.64 | 511500 CACHE4 138 588779 TAP_G17-036 138 2
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.15068 | 112.8 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.75 | 511541 SWEETWT6 230 763340 GEN-2018-117 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14434 | 109.9 | 511553 CHISHOLM7 345 523961 POTTER_CO 7 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14434 | 109.9 | 511553 CHISHOLM7 345 523961 POTTER_CO 7 345 2
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.1569 | 116.03 | 515375 WWRDEHV7 345 515458 BORDER 7 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.1569 | 116.05 | 515458 BORDER 7 345 560022 CRAWFISH_DR 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.149 | 112.7 | 515618 BALKOW 7 345 3WXFMR BALKOW 7 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.149 | 112.7 | 515618 BALKOW 7 345 3WXFMR BALKOW 7 1_Dup1
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14896 | 112.95 | 515634 PALDR1W7 345 3WXFMR PALO2 _1 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.7 | 515677 BADGER 7 345 563170 G15082_1 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14897 | 112.61 | 520827 BINGERJ4 138 521017 ONEY 4 138 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14897 | 112.62 | 521017 ONEY 4 138 521089 WASHITA4 138 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.61 | 522800 MU-TULIA 3 115 525179 TULIA_TP 3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.75 | 522892 MU-BROWNFLD2 69.0 526761 BROWNFLD_TP2 69.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.64 | 523090 TEXAS_CNTY 3 115 589380 GEN-2017-100 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14899 | 112.78 | 523093 HITCHLAND 3 115 523174 GOODWELLWND3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.95 | 523097 HITCHLAND 7 345 523112 NOVUS1 7 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 113 | 523097 HITCHLAND 7 345 523215 FREWHELCOL17 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14676 | 111.48 | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.13259 | 109.07 | 523097 HITCHLAND 7 345 523961 POTTER_CO 7 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 113.05 | 523097 HITCHLAND 7 345 560252 G10-14 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.62 | 523099 TC-DRYTRLS 3 115 588480 A16-010_SUB 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.82 | 523112 NOVUS1 7 345 3WXFMR NOVUS XF2 2
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.63 | 523112 NOVUS1 7 345 3WXFMR XIANA2011198 _1 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14902 | 112.61 | 523118 BUFF_DUNES 7 345 523853 FINNEY 7 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.63 | 523120 COLE 3 115 588860 GEN-2017-047 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14901 | 112.64 | 523172 GWELL_COLL11 34.5 523174 GOODWELLWND3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14901 | 112.65 | 523173 GWELL_COLL21 34.5 523174 GOODWELLWND3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14922 | 112.61 | 523267 PRINGLE 6 230 3WXFMR ENRCO13617-1 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14922 | 112.61 | 523267 PRINGLE 6 230 523979 HARRNG_EST 6 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14995 | 113.07 | 523771 GRAPEVINE 6 230 524044 NICHOLS 6 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.15977 | 113.75 | 523959 POTTER_CO 6 230 524267 BUSHLAND 6 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.15641 | 114.67 | 523959 POTTER_CO 6 230 525461 NEWHART 6 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.15623 | 118.42 | 523961 POTTER_CO 7 345 3WXFMR WAUK 90343-A 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14907 | 112.4 | 523978 HARRNG_MID 6 230 523979 HARRNG_EST 6 230 @1
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14904 | 112.39 | 524010 ROLLHILLS 6 230 3WXFMR WAUK WT01104 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14932 | 112.74 | 524267 BUSHLAND 6 230 3WXFMR WH 7001795 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.16806 | 114.31 | 524267 BUSHLAND 6 230 524623 DEAFSMITH 6 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.1489 | 113.07 | 524296 SPNSPUR_WND7 345 524299 SPNSPUR_COL7 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.1489 | 113.07 | 524299 SPNSPUR_COL7 345 3WXFMR SPNSPUR_COL7 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.15255 | 113.32 | 524415 AMA_SOUTH 6 230 525213 SWISHER 6 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 113.2 | 524502 NORTON 3 115 524509 FE-TUCMCARI3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.15218 | 113.01 | 524575 DS-#25+ 3 115 524597 PANDAHFD 3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.15218 | 113.12 | 524575 DS-#25+ 3 115 524630 TIERABLANCA3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.7 | 524604 HEREFRD_SB 2 69.0 524608 HERFRD_STH 2 69.0 *1
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.1537 | 119.12 | 524623 DEAFSMITH 6 230 760498 G17-146-TAP 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 113.1 | 524721 DS-#15&#19+2 69.0 524745 CASTRO_CNTY2 69.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14961 | 112.61 | 524770 PLSNT_HILL 6 230 3WXFMR EFAE1100068A 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.18753 | 117.92 | 524875 OASIS 6 230 524885 SN_JUAN_TAP6 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.15589 | 113.69 | 524875 OASIS 6 230 524909 ROOSEVELT 6 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.18744 | 118.38 | 524885 SN_JUAN_TAP6 230 527483 CHAVES_CNTY6 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.1506 | 112.8 | 524909 ROOSEVELT 6 230 3WXFMR ABB LMM60042 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 113.33 | 524923 PORTALES 2 69.0 524929 RO-PORT_MTR2 69.0 @1
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 113 | 525001 W_MULESHOE 2 69.0 525008 MULESH_CTY 2 69.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 113 | 525008 MULESH_CTY 2 69.0 525027 BAILEYCO 2 69.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 113.28 | 525023 BC-BAIL_MTR2 69.0 525027 BAILEYCO 2 69.0 @1
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.15004 | 113.27 | 525056 BC-EARTH 3 115 525480 PLANT_X 3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 113.09 | 525191 KRESS_INT 2 69.0 525203 SW-KRESS 2 69.0 Z1
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 113.17 | 525192 KRESS_INT 3 115 3WXFMR ENRCO 136155 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.1519 | 113.6 | 525213 SWISHER 6 230 525461 NEWHART 6 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.73 | 525272 KISER 3 115 3WXFMR VON 13819/1 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 113.19 | 525326 COX 3 115 3WXFMR ELCO 13474-3 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 113.21 | 525414 LAMTON 3 115 3WXFMR ASEA MLL9204 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.1507 | 113.03 | 525440 LC-S_OLTON+3 115 525446 RKYFORD_TP 3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.1507 | 113.03 | 525446 RKYFORD_TP 3 115 525480 PLANT_X 3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.16161 | 116.34 | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14772 | 114.35 | 525481 PLANT_X 6 230 3WXFMR WH ALM20171 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.15615 | 118.3 | 525481 PLANT_X 6 230 526435 SUNDOWN 6 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.1537 | 117.38 | 525481 PLANT_X 6 230 760498 G17-146-TAP 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.15075 | 113.07 | 525481 PLANT_X 6 230 762174 G17-218TAP 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.15096 | 113.14 | 525481 PLANT_X 6 230 762174 G17-218TAP 230 2
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.15552 | 118.38 | 525531 TOLK 6 230 525586 NEEDMORE 6 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14976 | 114.61 | 525531 TOLK 6 230 525637 LAMB_CNTY 6 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.1727 | 118.52 | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.15157 | 113.33 | 525531 TOLK 6 230 762174 G17-218TAP 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.15174 | 113.39 | 525531 TOLK 6 230 762174 G17-218TAP 230 2
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.15552 | 118.36 | 525586 NEEDMORE 6 230 526935 YOAKUM 6 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 113.01 | 525599 LC-SANDHLL+2 69.0 525606 AMHERST 2 69.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 113.04 | 525606 AMHERST 2 69.0 525613 W_LITTLFLD 2 69.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 113.07 | 525613 W_LITTLFLD 2 69.0 525635 LAMB_CNTY 2 69.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 113.02 | 525635 LAMB_CNTY 2 69.0 525650 LC-LTTLFLD+2 69.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14976 | 114.61 | 525637 LAMB_CNTY 6 230 3WXFMR WH ALM20172 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.87 | 525828 TUCO_INT 3 115 3WXFMR DS F78800913 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14915 | 112.4 | 525830 TUCO_INT 6 230 3WXFMR ENRCO 136401 2
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.1395 | 114.37 | 525832 TUCO_INT 7 345 526936 YOAKUM_345 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 113.07 | 526086 SW_6786_N 2 69.0 526087 SW_6786_S 2 69.0 Z1
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 113.07 | 526086 SW_6786_N 2 69.0 526102 SP-HETTLER 2 69.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 113.14 | 526087 SW_6786_S 2 69.0 526284 PLANTERS 2 69.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.69 | 526160 CARLISLE 3 115 3WXFMR WH RLP38371 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 113.03 | 526195 QUINCY 3 115 526196 SP-MILWAUKEE 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.93 | 526268 LUBBCK_STH 3 115 3WXFMR NA 70454A 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 113.19 | 526284 PLANTERS 2 69.0 526297 LUBBCK_EST 2 69.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14895 | 112.63 | 526435 SUNDOWN 6 230 3WXFMR UPDATE LATER _12 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14808 | 115 | 526435 SUNDOWN 6 230 526460 AMOCO_SS 6 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14899 | 112.65 | 526525 WOLFFORTH 6 230 3WXFMR UPDATE LATER _13 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 113.07 | 526735 TERRY_CNTY 2 69.0 526747 LG-BROWNFLD2 69.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 113 | 526747 LG-BROWNFLD2 69.0 526754 BROWNFIELD 2 69.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14774 | 114.41 | 526935 YOAKUM 6 230 527028 INK_BASIN 6 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.13675 | 121.79 | 526936 YOAKUM_345 345 527896 HOBBS_INT 7 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14739 | 113.76 | 527028 INK_BASIN 6 230 527894 HOBBS_INT 6 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14878 | 113 | 527130 DENVER_N 3 115 527286 HIGGEAST 3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.61 | 527149 MUSTANG 6 230 3WXFMR ENRCO 136161 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14918 | 110.49 | 527149 MUSTANG 6 230 527151 GS-MUSTANG 6 230 @1
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.86 | 527202 SEAGRAVES 3 115 3WXFMR ABB MLL92408 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.76 | 527212 DIAMONDBACK3 115 3WXFMR HOW 36773714 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.68 | 527261 SULPHUR 2 69.0 527271 LG-FOSTER +2 69.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14878 | 112.98 | 527286 HIGGEAST 3 115 527363 HIGG 3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14884 | 112.82 | 527322 GAINES 3 115 527325 OXY_WSEM_TP3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14884 | 112.74 | 527325 OXY_WSEM_TP3 115 527362 JOHNSON_DRW3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.73 | 527340 DOSS 3 115 3WXFMR ELCO 13566/1 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.71 | 527345 LEGACY 2 69.0 527350 XTO_ROBRTSN2 69.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.71 | 527346 LEGACY 3 115 3WXFMR VROL 13735-1 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.69 | 527350 XTO_ROBRTSN2 69.0 527355 BOARDMAN 2 69.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.63 | 527355 BOARDMAN 2 69.0 527365 FLANNAGAN 2 69.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.61 | 527360 MAPCO 3 115 527362 JOHNSON_DRW3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.65 | 527362 JOHNSON_DRW3 115 528775 LE-ERF 3 115 @1
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14906 | 112.39 | 527455 RSWL_SLRCOL3 115 527482 CHAVES_CNTY3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14905 | 112.41 | 527470 CHVS_SLRCOL3 115 527464 CHVS_SOLAR11 34.5 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14905 | 112.34 | 527470 CHVS_SLRCOL3 115 527482 CHAVES_CNTY3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.16713 | 112.88 | 527483 CHAVES_CNTY6 230 527799 EDDY_NORTH 6 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.62 | 527508 PRICE 3 115 527509 PRICE_TAP 3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.62 | 527529 RIACBRSH_TP3 115 527533 SW4J795_E 3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.62 | 527533 SW4J795_E 3 115 527564 ROSWLL_INT 3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.62 | 527563 ROSWLL_INT 2 69.0 527575 SW_4702 2 69.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.15082 | 112.67 | 527564 ROSWLL_INT 3 115 527597 TWEEDY 3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.62 | 527575 SW_4702 2 69.0 527589 CV-ORCHARD 2 69.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14899 | 112.78 | 527653 MILO_WIND 1 34.5 527655 RSVLT_CC_E 7 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14891 | 112.66 | 527654 RSVLT_CC_W 7 345 527655 RSVLT_CC_E 7 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14891 | 112.95 | 527654 RSVLT_CC_W 7 345 527666 RSVLT_COL1 7 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14886 | 112.86 | 527655 RSVLT_CC_E 7 345 527656 CROSSROADS 7 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14891 | 112.95 | 527666 RSVLT_COL1 7 345 3WXFMR RSVLT_COL1 7 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.36 | 527736 NAVAJO_5TP 3 115 527739 NAVAJO_4 3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14902 | 112.35 | 527864 CUNNINHAM 3 115 528348 BUCKEYE_TP 3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14902 | 112.63 | 527864 CUNNINHAM 3 115 528568 MONUMNT_TP 3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14817 | 112.91 | 527865 CUNNIGHM_N 6 230 527867 CUNNIGHM_S 6 230 *1
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.1488 | 112.64 | 527865 CUNNIGHM_N 6 230 527963 POTASH_JCT 6 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14899 | 112.4 | 527867 CUNNIGHM_S 6 230 3WXFMR WH 7000266 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14899 | 112.86 | 527867 CUNNIGHM_S 6 230 527882 CUNINGHAM2 1 20.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.149 | 112.79 | 527894 HOBBS_INT 6 230 527903 HOBBS_PLT3 1 18.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.149 | 112.36 | 527965 KIOWA 7 345 528027 RDRUNNER 7 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14904 | 112.36 | 528015 PHANTOM 7 345 528027 RDRUNNER 7 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.41 | 528024 RR_SVC_HV 3 115 528021 RDRUNNR_SVC1 15.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.68 | 528025 RDRUNNER 3 115 587990 GEN-2016-121 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14905 | 112.42 | 528185 N_LOVING 7 345 3WXFMR HYO1063400-1 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14902 | 112.41 | 528185 N_LOVING 7 345 528223 CHINA_DRAW 7 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.36 | 528222 CHINA_DRAW 3 115 528225 CD_SVC_HV 3 115 Z1
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14892 | 112.34 | 528333 LE-WEST_SUB3 115 528334 LE-NRTH_INT3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14902 | 112.42 | 528341 LE-SANANDRS3 115 528627 LE-TXACO_TP3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14902 | 112.38 | 528348 BUCKEYE_TP 3 115 528627 LE-TXACO_TP3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14888 | 112.62 | 528394 QUAHADA 3 115 528396 XTO_BIGEDDY3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.149 | 112.33 | 528463 SANGER_SW 3 115 528575 OXYPERMIAN 3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.149 | 112.33 | 528463 SANGER_SW 3 115 762442 G18-004-TAP 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14902 | 112.63 | 528568 MONUMNT_TP 3 115 528581 BYRD_TP 3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.149 | 112.38 | 528574 OXY_NHU_RCF3 115 528575 OXYPERMIAN 3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.69 | 528617 LE-WAITS 2 69.0 528325 LE-WAITS 3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.61 | 528617 LE-WAITS 2 69.0 528714 LE-FORT_SW 2 69.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14902 | 112.42 | 528622 LE-SANANDRS2 69.0 528341 LE-SANANDRS3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.97 | 528626 LE-PLNSINT 2 69.0 526928 PLAINS_INT 3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.97 | 528626 LE-PLNSINT 2 69.0 528709 LE-PLNSGOAB2 69.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.63 | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.69 | 528669 LE-STKLDRTP2 69.0 528740 LE-PLANS_SW2 69.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.85 | 528709 LE-PLNSGOAB2 69.0 528740 LE-PLANS_SW2 69.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.63 | 528709 LE-PLNSGOAB2 69.0 528747 LE-ALLRED 2 69.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.61 | 528714 LE-FORT_SW 2 69.0 528718 LE-NEWTEX 2 69.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.69 | 528735 LE-PLAINSUB2 69.0 528740 LE-PLANS_SW2 69.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14893 | 112.41 | 530583 POSTROCK7 345 588654 G17-021-TAP 345 2
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.41 | 531213 SANTAFE3 115 531408 PIERCVL3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14873 | 112.33 | 531451 MINGO 7 345 531465 SETAB 7 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14901 | 112.62 | 531501 BUCKNER7 345 531502 CIMRRN 7 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14901 | 112.62 | 531502 CIMRRN 7 345 531503 CIMRRN 1 34.5 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14889 | 112.32 | 531510 HARBNGR3 115 3WXFMR HARBGR345 _1 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14902 | 112.64 | 532663 LEC U5 24.0 532854 LEC U5 6 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14902 | 112.64 | 532853 LAWHILL6 230 532854 LEC U5 6 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.69 | 542951 HAW G5 1 22.0 543665 HAWTHN5 161 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14902 | 112.74 | 542955 LAC G1 1 22.0 542981 LACYGNE7 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14901 | 112.72 | 542956 LAC G2 1 24.0 542981 LACYGNE7 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14901 | 112.76 | 542957 IAT G1 1 24.0 542982 IATAN 7 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14901 | 112.82 | 542962 IAT G2 1 24.5 542982 IATAN 7 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.61 | 542966 WGARDNR5 161 543105 BULLCRK5 161 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.15158 | 112.16 | 560022 CRAWFISH_DR 345 762216 G17-151TAP 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.15125 | 113.18 | 560022 CRAWFISH_DR 345 762467 G18-015-TAP 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 108.98 | 560022 CRAWFISH_DR 345 763087 GEN-2018-073 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.15241 | 113.55 | 560022 CRAWFISH_DR 345 763215 G18-092-TAP 345 2
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 113.05 | 560252 G10-14 345 560253 G10-14-1 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.78 | 560253 G10-14-1 115 560254 G10-14-SUB1 34.5 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.78 | 560253 G10-14-1 115 560255 G10-14-SUB2 34.5 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.63 | 560581 G06-44-2 34.5 523111 NOVUS1 3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.68 | 560582 G06-44-3 34.5 560577 G06-44 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.66 | 560583 G06-44-4 34.5 560577 G06-44 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.32 | 560757 ASGI13_02_1 69.0 560758 ASGI13_02_2 34.5 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.32 | 560757 ASGI13_02_1 69.0 562731 WHEATLAND 69.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.33 | 560763 ASGI13_03_1 115 560761 ASGI13_03_2 34.5 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.76 | 562015 FIREWHEEL1 34.5 523215 FREWHELCOL17 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.76 | 562016 FIREWHEEL2 34.5 523215 FREWHELCOL17 345 2
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.31 | 562323 AGI1202&1305 115 562324 AGI1202&1305 34.5 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.32 | 562727 LESBIA 115 562728 SANJONTAP 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.32 | 562728 SANJONTAP 115 562729 CAPROCKTAP1 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.32 | 562730 CAPROCKTAP2 69.0 562729 CAPROCKTAP1 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.32 | 562730 CAPROCKTAP2 69.0 562731 WHEATLAND 69.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.72 | 563171 G15082_2 34.5 563170 G15082_1 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.4 | P11:13.8:AEPW:COM1-1
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.41 | P11:13.8:AEPW:COM2-1
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.41 | P11:13.8:AEPW:COM3-1
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.42 | P11:18:AEPW:WELSH1-1
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.42 | P11:18:AEPW:WELSH3-1
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.42 | P11:24:AEPW:PIRKEY 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.39 | P11:24:AEPW:SWS3-1
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.39 | P11:24:AEPW:TURKCOAL
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14916 | 112.7 | P12:138:AEPW-OMPA:DUNCAN-4:OMDUNCN4
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14904 | 112.66 | P12:138:AEPW:112GORE4:SNYDER-4
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14904 | 112.66 | 5841_Dup1
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14912 | 111.96 | 584560 GEN-2015-014 115 584561 G15-014XFMR1 34.5 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14911 | 112.65 | P12:138:AEPW:SANTAFE:DUNCAN-4
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.68 | 587991 G16-121XFMR1 34.5 587990 GEN-2016-121 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.62 | 588480 A16-010_SUB 115 3WXFMR A16-010_SUB 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14916 | 112.7 | P12:138:AEPW:DUNCAN-4:L.E.S.-4
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.06 | 588761 G17-033XFMR1 34.5 588760 GEN-2017-033 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.06 | 588765 G17-033XFMR2 34.5 588760 GEN-2017-033 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.63 | 588861 G17-047XFMR1 34.5 588860 GEN-2017-047 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14866 | 112.2 | P12:138:AEPW:ELKCTY-4:CLINTJC4
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.64 | 589381 G17-100XFMR1 34.5 589380 GEN-2017-100 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14878 | 112.39 | P12:138:AEPW:HOB-JCT4:ELKCTY-4
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.64 | P12:138:AEPW:SHERID4:112GORE4
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14901 | 112.61 | P12:230:AEPW:SWEETWT6:BUFFCK6
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14901 | 112.66 | P12:230:AEPW:SWEETWT6:ROARK6
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.15146 | 114.5 | P12:345:AEPW:L.E.S7:TERRYRD7
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.15146 | 114.49 | P12:345:AEPW:L.E.S7:TERRYRD7
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.15146 | 114.47 | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.15211 | 114.61 | P12:345:AEPW-OKGE:L.E.S.-7:GRACMNT7
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.15211 | 114.58 | P12:345:AEPW-OKGE:L.E.S.-7:GRACMNT7
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14899 | 112.4 | P12:345:AEPW-OKGE:PITTSB-7:SEMINOL7
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.15219 | 115.66 | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.66 | P22:345:AMMO::LABADIE:1
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.66 | P22:345:AMMO::LABADIE:2
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.66 | P22:345:AMMO::LABADIE:3
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.66 | P22:345:AMMO::LABADIE:4
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.65 | P22:345:AMMO::RUSHISLAND:1
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.64 | P22:345:AMMO::RUSHISLAND:2
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14904 | 112.41 | P13:138-13.8:AEPW:COMANC-4_#2
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14729 | 111.28 | P13:138-230:AEPW:ELKCTY-4
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14905 | 112.4 | P13:138-24:AEPW:S.W.S.-4
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14904 | 112.39 | P13:138-24:AEPW:TURK 4
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14912 | 112.63 | P13:138-345:AEPW:L.E.S.-4_#1
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14921 | 112.75 | P13:138-345:AEPW:L.E.S.-4_#2
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14905 | 112.67 | P23:500:EES-EAI:KEO:B4941
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14905 | 112.66 | P23:500:EES-EAI:KEO:B4921
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.61 | P11:26:EES-EAI:INDEP2:1:D401
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.61 | P11:26:EES-EAI:INDEP2:1
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.61 | P13:500:EES-EAI:INDEP2:MT2
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14904 | 112.65 | P23:500:EES-EAI:INDEP2:B6126
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14904 | 112.64 | P23:500:EES-EAI:PD:INDEP2:LN:FK479
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14901 | 112.61 | P13:230-34.5:AEPW:BUFFCK6
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14901 | 112.67 | P13:230-34.5:AEPW:ROARK6
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.41 | P13:69-13.8:AEPW:COMANC-2
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.66 | P11:024:DPC:ALMA2:6
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.62 | P11:18:ITCM:EMERYGT1:1
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.63 | P11:18:ITCM:EMERYGT2:1
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.63 | P11:161:ITCM:MGS CT1:1C
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.63 | P11:161:ITCM:MGS CT2:2C
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14901 | 112.64 | 652537 WHITE 3 345 659286 DEERCREK-BE3 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14901 | 112.64 | 659286 DEERCREK-BE3 345 3WXFMR DEERCRK KU1A 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.63 | 672601 BD 4 230 672306 BD 6G 18.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.63 | 672610 POPLAR 4 230 672310 POPLAR 1G 18.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.63 | 672610 POPLAR 4 230 672311 POPLAR 2G 18.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.62 | 672621 SHAND 4 230 672321 SHAND 1G 18.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.61 | 672649 CODETTE 4 230 672650 NIPAWIN 4 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.62 | 672696 BRADA 4 230 672699 NBEC 4 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.69 | P23:345:MDU::COYOTE::5707-5712-5715::::
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.84 | P23:345:MEC:CBEC 905
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.81 | P23:345:MEC:CBEC 908
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.64 | P23:345:MEC:GDMEC 908
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.74 | P23:345:MEC:RAUN 0180
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.8 | P23:345:MEC:RAUN 0210
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.75 | P23:345:MEC:LOUISA 954
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14904 | 112.75 | P23:345:MEC:LOUISA 964
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.61 | P21:115:XEL:AUTO-SINGLE:CHEMOLT7:LSPOWER7:1
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.65 | P21:115:XEL:AUTO-SINGLE:COLVILL7:CANONFLSG7:1
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.61 | P21:115:XEL:AUTO-SINGLE:FARIBALTP7:FARIBALTGEN:Z
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.7 | P21:230:OTP:AUTO-SINGLE:SQBUTTE4:YNG24:1
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.69 | P23:345:OTP:CENTER 3:3215(1)
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.69 | P23:345:OTP:CENTER 3:3225(1)
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.63 | P12:230:UMZW:# 687 #: FT IN SD. FT-BG1 LINE FAULT
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.63 | P12:230:UMZW:# 3617 #: FT IN SD. FT-BG2 LINE FAULT
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 111.33 | 760494 GEN-2017-146 230 760498 G17-146-TAP 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 111.32 | 760495 G17-146-XFM1 34.5 760494 GEN-2017-146 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.05 | 761356 G17-239-XFMR 34.5 761355 GEN-2017-239 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.05 | 761359 G17-239-XFMR 34.5 761355 GEN-2017-239 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.23 | 761797 G17-187XFM1 34.5 761796 GEN-2017-187 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.23 | 761800 G17-187XFM2 34.5 761796 GEN-2017-187 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 107.16 | 762132 GEN-2017-158 230 763252 G18-099-XFM1 34.5 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 107.16 | 762132 GEN-2017-158 230 763255 G18-099-XFM2 34.5 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 107.74 | 762133 G17-158XFM1 34.5 762132 GEN-2017-158 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 107.74 | 762136 G17-158XFM2 34.5 762132 GEN-2017-158 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 109.9 | 762216 G17-151TAP 345 762217 GEN-2017-151 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.15158 | 113.55 | 762216 G17-151TAP 345 762467 G18-015-TAP 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 111.85 | 762218 G17-151XFM1 34.5 762217 GEN-2017-151 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 111.85 | 762221 G17-151XFM2 34.5 762217 GEN-2017-151 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 111.85 | 762224 G17-151XFM3 34.5 762217 GEN-2017-151 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 111.85 | 762227 G17-151XFM4 34.5 762217 GEN-2017-151 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.36 | 762438 GEN-2018-004 115 762442 G18-004-TAP 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 110.89 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 111.7 | 762461 G18-015-XFM1 34.5 762460 GEN-2018-015 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 111.7 | 762464 G18-015-XFM2 34.5 762460 GEN-2018-015 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.15043 | 113.07 | 762467 G18-015-TAP 345 763215 G18-092-TAP 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 110.18 | 763087 GEN-2018-073 345 763088 G18-073-XFM1 34.5 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 111.33 | 763087 GEN-2018-073 345 763091 G18-073-XFM2 34.5 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 107.16 | 763120 GEN-2018-081 230 763121 G18-081-XFM1 34.5 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 109.42 | 763120 GEN-2018-081 230 764011 G19-074-XFM1 34.5 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 109.44 | 763186 GEN-2018-089 230 763187 G18-089-XFM1 34.5 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 110.21 | 763208 GEN-2018-092 345 763215 G18-092-TAP 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 111.37 | 763208 GEN-2018-092 345 763220 G18-092-XFM1 34.5 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 111.37 | 763208 GEN-2018-092 345 763223 G18-092-XFM2 34.5 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 108.87 | 763241 GEN-2018-097 230 763242 G18-097-XFM1 34.5 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 109.78 | 763241 GEN-2018-097 230 763296 G18-111-XFM1 34.5 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 109.14 | 763241 GEN-2018-097 230 763307 G18-112-XFM1 34.5 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 109.14 | 763241 GEN-2018-097 230 763310 G18-112-XFM2 34.5 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 108.87 | 763241 GEN-2018-097 230 763395 G18-124-XFM1 34.5 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 108.87 | 763241 GEN-2018-097 230 763398 G18-124-XFM2 34.5 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.29 | 763318 GEN-2018-115 345 763319 G18-115-XFM1 34.5 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.75 | 763340 GEN-2018-117 230 763341 G18-117-XFM1 34.5 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 111.19 | 763483 GEN-2019-003 230 763605 G19-021-XFM1 34.5 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 111.9 | 763516 GEN-2019-011 345 763517 G19-011-XFM1 34.5 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.26 | 763879 GEN-2019-056 115 763880 G19-056XFM1 34.5 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14854 | 112.68 | P42:345:OKGE:SB_BVTY7305
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14895 | 112.43 | P23:345:WERE:BUFF_345-534::
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14895 | 112.43 | P23:345:WERE:BUFF_345-543::
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.149 | 112.78 | P23:345:WERE:JEC_345-15::
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14899 | 112.75 | P23:345:WERE:JEC_345-16::
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.149 | 112.78 | P23:345:WERE:JEC_345-19::
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.149 | 112.78 | P23:345:WERE:JEC_345-20::
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.95 | P23:345:WERE:WOLF_345-50::
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.95 | P23:345:WERE:WOLF_345-60::
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14904 | 112.43 | P42:345:AEPW:WELSH CB 10620 NBTB+FAULT
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.15219 | 114.21 | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.15244 | 114.99 | P42:345:AEPW:LAWTON EASTSIDE CB 3413A NBTB+FAULT
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.1528 | 115.4 | P42:345:AEPW:LAWTON EASTSIDE CB 3425A NBTB+FAULT
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.15233 | 115.86 | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14918 | 112.31 | P42:345:AEPW:PITTSBURG CB 3441A NBTB+FAULT
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14899 | 112.4 | P42:345:AEPW:PITTSBURG CB 3445A NBTB+FAULT
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.15146 | 114.49 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.15146 | 114.49 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.15146 | 114.47 | P42:345:AEPW:TERRYRD_CB_3421A_NBTB
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14902 | 112.75 | P23:345:KCPL:LACYGNE_R2-5::LACYGU2-LACYGNE-STILWELL
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14904 | 112.43 | P23:345:AEPW:WELSH CB 10620 NBTB
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.15219 | 114.54 | P23:345:AEPW:OKLAUNION CB 3401A NBTB
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.15244 | 114.99 | P23:345:AEPW:LAWTON EASTSIDE CB 3413A NBTB
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.1528 | 115.4 | P23:345:AEPW:LAWTON EASTSIDE CB 3425A NBTB
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.15233 | 115.86 | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14918 | 112.31 | P23:345:AEPW:PITTSBURG CB 3441A NBTB
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14899 | 112.4 | P23:345:AEPW:PITTSBURG CB 3445A NBTB
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.15146 | 114.49 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.15146 | 114.49 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.15146 | 114.47 | P23:345:AEPW:TERRYRD_CB_3421A_NBTB
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14935 | 112.62 | P12:138:AEPW:S.W.S.-4:L.E.S.-4
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.65 | P11:115:SUNC:GARDENCITY_S2:97:531459(2)
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.15165 | 114.72 | P23:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.15423 | 117.32 | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.15165 | 114.72 | P42:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB+FAULT
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.15423 | 117.32 | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14129 | 109.51 | P42:345:OKGE:SB_BVTY7315_PRE19S
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14873 | 112.33 | P23:345:SUNC:MO_BRK182
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14873 | 112.33 | P23:345:SUNC:MO_BRK382
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14901 | 112.42 | P21:345:UMZW:# 725 #: GI IN NE. GI-SWEET LINE FAULT
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.15068 | 112.8 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14904 | 112.41 | P12:138-13.8:AEPW:COMANC-4_#1
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14729 | 111.26 | P12:230:AEPW:ELKCITY6:CHISHOLM6
Thermal | 05ALL | 1 | 23SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.15057 | 113.54 | P12:230:AEPW:SWEETWT6:CHISHOLM6
Thermal | 05ALL | 1 | 23SP | GEN-2019-011 | FROM->TO | 511458 ELKCTY-4 138 998036 ELKCTY-6 _1 138 1 |  | 330 | 0.08587 | 112.44 | P12:345:OKGE-AEPW:BKRBKR371::::
Thermal | 05ALL | 1 | 23SP | GEN-2019-011 | FROM->TO | 511458 ELKCTY-4 138 998036 ELKCTY-6 _1 138 1 |  | 330 | 0.08587 | 112.78 | P12:345:OKGE-AEPW:BKRBKR371::::
Thermal | 05ALL | 1 | 23SP | GEN-2019-011 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.08587 | 108.04 | P12:345:OKGE-AEPW:BKRBKR371::::
Thermal | 05ALL | 1 | 23SP | GEN-2019-011 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.08587 | 108.6 | P12:345:OKGE-AEPW:BKRBKR371::::
Thermal | 05ALL | 1 | 23SP | GEN-2019-011 | FROM->TO | 511490 ELKCITY6 230 998036 ELKCTY-6 _1 138 1 |  | 330 | 0.08587 | 112.79 | P12:345:OKGE-AEPW:BKRBKR371::::
Thermal | 05ALL | 1 | 23SP | GEN-2019-011 | FROM->TO | 511490 ELKCITY6 230 998036 ELKCTY-6 _1 138 1 |  | 330 | 0.08587 | 113.27 | P12:345:OKGE-AEPW:BKRBKR371::::
Thermal | 05ALL | 1 | 23SP | GEN-2019-011 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.05486 | 121.79 | 526936 YOAKUM_345 345 527896 HOBBS_INT 7 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 511458 ELKCTY-4 138 998036 ELKCTY-6 _1 138 1 |  | 330 | 0.10462 | 112.44 | P12:345:OKGE-AEPW:BKRBKR371::::
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 511458 ELKCTY-4 138 998036 ELKCTY-6 _1 138 1 |  | 330 | 0.10462 | 112.78 | P12:345:OKGE-AEPW:BKRBKR371::::
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.10462 | 108.04 | P12:345:OKGE-AEPW:BKRBKR371::::
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.10462 | 108.6 | P12:345:OKGE-AEPW:BKRBKR371::::
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 511490 ELKCITY6 230 998036 ELKCTY-6 _1 138 1 |  | 330 | 0.10462 | 112.79 | P12:345:OKGE-AEPW:BKRBKR371::::
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 511490 ELKCITY6 230 998036 ELKCTY-6 _1 138 1 |  | 330 | 0.10462 | 113.27 | P12:345:OKGE-AEPW:BKRBKR371::::
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14904 | 112.73 | P23:345:KCPL-WERE:237LACYGNE_R1-6::LACYGU1-LACYGNE-NEOSHO
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14902 | 112.64 | P11:230:WERE:LECU5_GEN::
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14902 | 112.63 | P11:161:GMO:DOGWOOD_COMBINED_CYCLE_UNIT_OUTAGE_1_1
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14909 | 111.16 | P11:115:SPS:MUSTANG1&3:153MW::::
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14976 | 114.61 | P12:230:SPS:K37::1_TOLK_LAMB:::
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14922 | 112.61 | P12:230:SPS:K43::1_PRNGLE_HARR_E:::
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14907 | 112.37 | P12:230:SPS:K44::1_EPLNT_HARRW:::
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.1487 | 112.79 | P12:115:SPS:T04::1_TRBLNC_CASTRO:::
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14901 | 112.19 | P12:115:SPS:T13::1_TAYLOR_WHOBBS:::
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.149 | 112.31 | P12:115:SPS:T14::1_MADDOX_TAYLOR:::
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 113.09 | P12:115:SPS:T21::1_GRSSLND_GRAHAM:::
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14904 | 112.41 | P12:115:SPS:T23::1_PCA_POTJCT:::
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.62 | P12:115:SPS:T24B::1_RSWLL_BRSHRF:::
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14911 | 112.64 | P12:115:SPS:T26::1_CHAVES_RSWLCTY:::
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.1507 | 113.18 | P12:115:SPS:T28A::1_LAMTON_PLANTX:::
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14961 | 112.67 | P12:115:SPS:T29::1_LAMTON_HALECTR:::
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.15057 | 113.96 | P12:115:SPS:T30::1_LAMB_HOCKLY:::
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.15057 | 113.13 | P12:115:SPS:T31::1_HOCKLY_SUNDWN:::
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14896 | 112.63 | P12:115:SPS:T35::1_TERRY_YOAKUM:::
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.1491 | 113.32 | P12:115:SPS:T45::1_NORRIS_OASIS:::
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14898 | 112.4 | P12:115:SPS:T57::1_MUSTG_SEGRVS:::
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.15775 | 113.15 | P12:115:SPS:T59::1_CARGIL_CURRY:::
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14994 | 112.42 | P12:115:SPS:T66::1_RNDALL_HAPPY:::
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14994 | 112.9 | P12:115:SPS:T67::1_HAPPY_KRESS:::
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14908 | 112.39 | P12:115:SPS:T68::1_TUCO_FLOYD:::
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14897 | 113.2 | P12:115:SPS:T71::1_CRLSLE_YUMA:::
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14914 | 112.7 | P12:115:SPS:T81::1_COX_FLOYD:::
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.85 | P12:115:SPS:T83::1_SP-FKFD_ALLEN:::
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14878 | 113.01 | P12:115:SPS:T89::1_DC_N_HIGG:::
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.66 | P12:115:SPS:T91::1_HIGG_RUSSELL:::
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14931 | 112.62 | P12:115:SPS:V04::1_EPLANT_RNDALL:::
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14921 | 112.67 | P12:115:SPS:V07::1_COX_HALECTR:::
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.15055 | 112.95 | P12:115:SPS:V09::1_HALECTR_PLANTX:::
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14871 | 112.83 | P12:115:SPS:V12::1_PLANTX_BAILEY:::
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.62 | P12:115:SPS:V15::1_TUCO_INDANA:::
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14857 | 112.67 | P12:115:SPS:V24::1_WOLFTH_TERRY:::
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.15082 | 112.64 | P12:115:SPS:V26::1_RSWLL_EDDY_N:::
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.98 | P12:115:SPS:V33::1_LUBBS_LYNN:::
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.15004 | 113.85 | P12:115:SPS:V37::1_CASTRO_PLANTX:::
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.75 | P12:115:SPS:V46::1_ALLEN_WHEELCK:::
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14901 | 113.09 | P12:115:SPS:V49::1_YOAKUM_SHLCO2:::
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14932 | 113.26 | P12:115:SPS:V55::1_SUNDWN_TERRY:::
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14906 | 113.09 | P12:115:SPS:V56::1_COCHRAN_SUNDWN:::
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.68 | P12:115:SPS:V62::1_CRLSLE_INDANA:::
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14906 | 112.62 | P12:115:SPS:V70::1_S_GORG_RNDALL:::
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.15027 | 112.65 | P12:115:SPS:V78::2_CURRY_RSVLT:::
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14886 | 112.79 | P12:115:SPS:V81::1_LE-WAIT_LE-LVN:::
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.65 | P12:115:SPS:V95::1_DC_N_SHLCO2:::
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.61 | P12:115:SPS:W11::1_DC_S_SMINLE:::
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14902 | 112.61 | P12:115:SPS:W12::1_SMINLE_DOSS:::
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14898 | 112.68 | P12:115:SPS:W14::1_SMINLE_GAINES:::
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 113.14 | P12:115:SPS:W32::1_PRMTR_FE-CLSIN:::
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.61 | P12:115:SPS:W34::1_JNSDRW_MAPCO:::
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14884 | 112.85 | P12:115:SPS:W35::1_GAINES_JNSDRW:::
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14872 | 112.64 | P12:115:SPS:W36::1_TAYLOR_JNSDRW:::
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.15218 | 113.15 | P12:115:SPS:W40::1_WCANYON_TRBLNC:::
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14933 | 112.71 | P12:115:SPS:W52::1_NEWHART_KRESS:::
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 113.2 | P12:115:SPS:W58::1_NORTON_LOPEZ:::
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.82 | P12:115:SPS:W59::1_LOPEZ_CMPBLL:::
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14913 | 113.15 | P12:115:SPS:W62::1_PLSTHL_CURRY:::
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14915 | 112.62 | P12:115:SPS:W63::1_PLSTHL_CURRY:::
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.96 | P12:115:SPS:W64::1_PLSTHL_FE-CLV:::
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14915 | 113.12 | P12:115:SPS:W65::1_PLSTHL_CURRY:::
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.81 | P12:115:SPS:W66::1_PORTA_GREYHUND:::
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.15218 | 112.61 | P12:115:SPS:W77::1_RNDAL_WCANYON:::
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14906 | 112.64 | P12:115:SPS:W99::1_CAPITAN_CHAVES:::
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.1489 | 113.08 | P12:115:SPS:U14::1_DC_STH_INKBSN:::
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14886 | 113.02 | P12:115:SPS:V15::1_INKBSN_LE-WAT:::
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14932 | 112.74 | P12:115:SPS:U16::1_BSHLND_OUTPST:::
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14932 | 112.73 | P12:115:SPS:U17::1_COLTR_OUTPST:::
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14899 | 112.8 | P12:115:SPS:U19::1_DEAN_PLAINS:::
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14932 | 112.67 | P12:115:SPS:U23::1_COLTR_HILSDE:::
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.13544 | 119.61 | P42:345:SPS:YOAKUM:J18####:SLG1:EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.13544 | 119.61 | P43:345:SPS:YOAKUM:TF#####:SLG:EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.13544 | 119.61 | P42:345:SPS:YOAKUM:J17####:SLG:EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.13544 | 119.61 | P42:345:SPS:YOAKUM:J18####:SLG2:EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.62 | P11:18:HAST:::EGYCTR2G WEC2_LOSS OF WEC 2 GEN_:HV:
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.62 | P13:18-115:HAST:::EGYCNTR7 XFMR G2WEC 2 GSU_:HV:
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14902 | 112.63 | P11:161:GMO:DOGWOOD-COMBINED-CYCLE-UNIT-OUTA:::HV:
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14904 | 112.73 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14902 | 112.75 | P23:345:KCPL:LACYGNE-R2-5:::EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.149 | 112.78 | P11:230:WERE:JECU1-GEN:::HV:
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14902 | 112.64 | P11:230:WERE:LECU5-GEN:::HV:
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.149 | 112.78 | P11:345:WERE:JECU2-GEN:::EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.149 | 112.78 | P11:345:WERE:JECU3-GEN:::EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.95 | P11:345:WERE:WOLFU1-GEN:::EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14895 | 112.43 | P23:345:WERE:BUFF-345-534:::EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14895 | 112.43 | P23:345:WERE:BUFF-345-543:::EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.149 | 112.78 | P23:345:WERE:JEC-345-15:::EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14899 | 112.75 | P23:345:WERE:JEC-345-16:::EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.149 | 112.78 | P23:345:WERE:JEC-345-19:::EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.149 | 112.78 | P23:345:WERE:JEC-345-20:::EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.95 | P23:345:WERE:WOLF-345-50:::EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.95 | P23:345:WERE:WOLF-345-60:::EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.89 | P11:022:NPPD:COOPER1G:1:983:::
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14898 | 112.92 | P11:023:NPPD:GENTLM1G:1:757:::
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14898 | 112.94 | P11:024:NPPD:GENTLM2G:2:757:::
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.149 | 112.75 | P13:345:OPPD:NEBCTY1G:::EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14899 | 112.78 | P13:345:OPPD:NEBCTY2G:::EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.77 | P22:345:OPPD:S3458 NEBCTY1G:LT::EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.149 | 112.75 | P22:345:OPPD:S3458 NEBCTY1G:::EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.81 | P22:345:OPPD:S3458 NEBCTY2G:LT::EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14899 | 112.78 | P22:345:OPPD:S3458 NEBCTY2G:::EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.77 | P23:345:OPPD:S3458 NEBCTY1G:LT::EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.149 | 112.75 | P23:345:OPPD:S3458 NEBCTY1G:::EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.81 | P23:345:OPPD:S3458 NEBCTY2G:LT::EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14899 | 112.78 | P23:345:OPPD:S3458 NEBCTY2G:::EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.4 | P12:115:SUNC:PLYMELL-PIERCEVILLE:::HV::
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14901 | 112.64 | P11:018:UMZB:# 5 #:: DCS IN SD. DEERCREEK_MV::
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14902 | 112.61 | P11:022:UMZB:# 15 #:: LO IN ND. LELAND OLDS 1_MV::
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14902 | 112.65 | P11:020:UMZB:# 16 #:: LO IN ND. LELAND OLDS 2_MV::
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14901 | 112.7 | P11:023:UMZB:# 31 #:: AVS IN ND. ANTELOPE VALLEY 1_MV::
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14901 | 112.7 | P11:023:UMZB:# 32 #:: AVS IN ND. ANTELOPE VALLEY 2_MV::
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14898 | 112.9 | P11:024:UMZB:# 33 #:: LRS IN WY. LARAMIE RIVER STATION 1_MV::
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.63 | P12:230:UMZW:# 687 #:: FT IN SD. FT-BG1 BRANCH FAULT:HV:
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.63 | P12:230:UMZW:# 3617 #:: FT IN SD. FT-BG2 BRANCH FAULT:HV:
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.63 | P12:230:UMZW:# 4038 #:: BG-FT IN SD. FAULT FOR TRANSMISSION CIRCUIT (BG-FT).:HV:
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.63 | P12:230:UMZW:# 4039 #:: BG-FT IN SD. FAULT FOR TRANSMISSION CIRCUIT (BG-FT).:HV:
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.61 | P13:230:UMZW:# 5135 #:: OA IN SD. FAULT ON TRANSFORMER (2).:HV:
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.61 | P13:230:UMZW:# 5136 #:: OA IN SD. FAULT ON TRANSFORMER (3).:HV:
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14901 | 112.42 | P21:345:UMZW:# 725 #:: GI IN NE. GI-SWEET BRANCH FAULT:EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14901 | 112.42 | P23:345:UMZW:# 2430 #:: GI IN NE. GI 1492 BKR FAULT:EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14901 | 112.42 | P23:345:UMZW:# 2438 #:: GI IN NE. GI-SWEET BRANCH FAULT & GI 1492 STUCK BKR:EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14906 | 112.37 | P11:138:WFEC:HUGO1:465MW :::
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14899 | 112.4 | P12:345:OKGE-AEPW:BKRBKR20::::
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14939 | 112.75 | P12:345:OKGE:BKRBKR21::::
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14958 | 112.95 | P12:345:OKGE:BKRBKR24::::
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.15146 | 114.47 | P12:345:OKGE-AEPW:BKRBKR25::::
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14894 | 112.42 | P12:345:OKGE:BKRBKR336::::
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14893 | 112.41 | P12:345:OKGE:BKRBKR336_2::::
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.15211 | 114.61 | P12:345:OKGE-AEPW:BKRBKR366::::
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.15211 | 114.58 | P12:345:OKGE-AEPW:BKRBKR366::::
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14959 | 112.87 | P12:345:OKGE:BKRBKR367::::
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14935 | 112.62 | P12:345:OKGE-WFEC:BKRBKR374::::
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14862 | 112.22 | P12:345:OKGE:BKRBKR4193::::
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14862 | 112.22 | P12:345:OKGE:BKRBKR4194::::
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14846 | 112.28 | P12:345:OKGE-SPS:BKRBKR4201::::
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14846 | 112.28 | P12:345:OKGE-SPS:BKRBKR4202::::
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14893 | 112.35 | P12:345:OKGE:BKRBKR443NEW::::
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14893 | 112.35 | P12:345:OKGE:BKRBKR443NEW2::::
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14897 | 112.88 | P12:345:OKGE:BKRBKR604::::
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14896 | 112.94 | P12:345:OKGE:BKRBKR604_2::::
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14855 | 112.62 | P42:345:OKGE:SB_ARIA7381::::
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.1569 | 116.05 | P42:345:OKGE:SB_BVTY7387::::
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14938 | 112.68 | P42:345:OKGE:SB_SPCK7383::::
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14902 | 112.64 | P11:115:SUNC:GARDENCITY_S2:103:531459(2):HV:
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14902 | 112.64 | P11:115:SUNC:FORTDDODGE_4:157:539670(4):HV:
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.62 | P11:345:599:CIMARRON1WIND:200:531603(1):EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.92 | P13:115:SUNC:HOLCOMB_GSU:::HV:
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14902 | 112.64 | P13:115:SUNC:S2_GSU:::HV:
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14902 | 112.64 | P13:115:SUNC:FORTDODGE_GSU:::HV:
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14901 | 112.62 | P23:345:SUNC:BU_BRK682:::EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.71 | 300003 1THLG3 24.0 301503 7THOMHLGSU3 345 3
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.71 | 300049 7THOMHL 345 301503 7THOMHLGSU3 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.66 | P11:20:AMMO:1LAB�� G1:1
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.66 | P11:20:AMMO:1LAB�� G2:2
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.83 | P11:345:AMMO::CALLAWAY:1
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.66 | P11:345:AMMO::LABADIE:3
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.66 | P11:345:AMMO::LABADIE:4
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.66 | P11:345:AMMO::RUSHISLAND:U1
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.66 | P11:345:AMMO::RUSHISLAND:U2
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.64 | P11:138:AMMO::SIOUX:2
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.64 | P12:765:AEP:AEP ROCKP-AEP JEFF 765
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.61 | P11:HV:EES::1ISES U1:1
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.61 | P11:EHV:EES::1ISES U2:1
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.42 | P11:HV:EES::PIRKEY 1:1
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.42 | P11:EHV:EES::WELSH3-1:1
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.39 | P11:HV:EES::TURKCOAL:1
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.61 | P12:HV:EES::5ISES%:1
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.61 | P12:EHV:EES::8ISES%:1
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.82 | P12:EHV:EES::7CALAWY 1:1
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14904 | 112.39 | P12:HV:EES::TURK 4%:1(1)
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.64 | 344011 7HUGHES 345 344012 7HPW-N 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.66 | 344884 7LABADIE1 345 344894 1LAB G1 20.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.66 | 344885 7LABADIE2 345 344895 1LAB G2 20.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.66 | 344886 7LABADIE3 345 344896 1LAB G3 20.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.66 | 344887 7LABADIE4 345 344897 1LAB G4 20.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.65 | 345667 7RUSH 1 345 345670 1RUSH G1 18.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.65 | 345668 7RUSH 2 345 345671 1RUSH G2 18.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.64 | 345755 4SIOUX 1 138 345756 1SIOUX 1 18.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.64 | 345764 4SIOUX 2 138 345765 1SIOUX 2 18.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.69 | P12:345:MDU::CENTER:COYOTE:1::::
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.69 | P13:345:MDU:COYOTE GSU LOSS:COYOTE::1::::
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.61 | P11:345:MEC:GDMEC CT1
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.61 | P11:345:MEC:GDMEC CT2
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.71 | P11:345:MEC:GDMEC ST
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.9 | P11:345:MEC-NPPD:COOPER 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.8 | P11:24:XEL:AUTO-SINGLE:SHERC31G:1
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.8 | P11:24:XEL:AUTO-SINGLE:SHERC32G:2
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.87 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.73 | P11:20:XEL:AUTO-SINGLE:PRIS31G:1
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.73 | P11:20:XEL:AUTO-SINGLE:PRIS32G:2
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.76 | P11:22:XEL:AUTO-SINGLE:MNTCE31G:1
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.73 | P11:20:XEL:AUTO-SINGLE:KING31G:1
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.77 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.77 | P11:22:GRE:AUTO-SINGLE:GRE-COAL42G:2
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.71 | P11:24:OTP:AUTO-SINGLE:BIGSTN1G:1
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.71 | P11:20:OTP:AUTO-SINGLE:CENTER2G:1
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.63 | P11:22:OTP:AUTO-SINGLE:CENTER1G:1
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.7 | P11:24:OTP:AUTO-SINGLE:COYOTE1G:1
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.63 | P11:24:DPC:AUTO-SINGLE:GENOA53G:3
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.61 | P12:115:XEL:AUTO-SINGLE:CHEMOLT7:LSPOWER7:1
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.65 | P12:115:XEL:AUTO-SINGLE:COLVILL7:CANONFLSG7:1
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.61 | P12:115:XEL:AUTO-SINGLE:FARIBALTP7:FARIBALTGEN:Z
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.7 | P12:230:OTP:AUTO-SINGLE:SQBUTTE4:YNG24:1
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.78 | P13:24-345:XEL:AUTO-SINGLE:SHERC31G:SHERCO3:1
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.78 | P13:24-345:XEL:AUTO-SINGLE:SHERC32G:SHERCO3:1
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.85 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.73 | P13:20-345:XEL:AUTO-SINGLE:PRIS31G:PRISLD3:1
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.73 | P13:20-345:XEL:AUTO-SINGLE:PRIS32G:PRISLD3:2
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.76 | P13:22-345:XEL:AUTO-SINGLE:MNTCE31G:MNTCELO3:1
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.72 | P13:20-345:XEL:AUTO-SINGLE:KING31G:ASKING3:1
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.76 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL41G:GRE-COALCR4:1
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.75 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL42G:GRE-COALCR4:1
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.7 | P13:230-24:OTP:AUTO-SINGLE:BIGSTON4:BIGSTN1G:1
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.7 | P13:20-230:OTP:AUTO-SINGLE:CENTER2G:YNG24:1
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.62 | P13:22-230:OTP:AUTO-SINGLE:CENTER1G:CENTER4:1
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.69 | P13:24-345:OTP:AUTO-SINGLE:COYOTE1G:COYOTE3:1
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.63 | P13:24-161:DPC:AUTO-SINGLE:GENOA53G:GENOA5:1
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.64 | P13:24-161:DPC:AUTO-SINGLE:JPM:ALMA5:1
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.7 | P11:115:XEL:RIV COMBINE CYCLE
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.62 | P12:115:XEL:BDS #2 5
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.62 | P11:115:XEL:HBR #6
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.62 | P11:115:XEL:HBR #7
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.73 | P11:115:XEL:HBR #6 7 8
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.73 | P23:345:XEL:8H14 PRI
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.73 | P23:345:XEL:8H17 PRI AS
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.85 | P23:345:XEL:8N28 SHC
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.78 | P23:345:XEL:8N22 SHC
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.78 | P23:345:XEL:8N17 SHC
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.77 | P23:345:XEL:8N8 MNN
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.72 | P23:345:XEL:8P1 KING
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.72 | P23:345:XEL:8P2 KING
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.62 | P23:115:XEL:5P147 IVH AS
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.61 | P11:18:ALTW:AUTO-SINGLE:EMERYST1:1
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.61 | P11:22:ALTW:AUTO-SINGLE:LANS54G:4
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.74 | P11:22:ALTW:AUTO-SINGLE:ARNOLD1G:1
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.77 | P11:24:ALTW:AUTO-SINGLE:OTTUMW1G:1
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.61 | P13:18-161:ALTW:AUTO-SINGLE:EMERYST1:EMERY5:1
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.61 | P13:22-161:ALTW:AUTO-SINGLE:LANS54G:LANSINGL15:1
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.73 | P13:22-161:ALTW:AUTO-SINGLE:ARNOLD1G:ARNOLD5:1
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.76 | P13:24-161:ALTW:AUTO-SINGLE:OTTUMW1G:OTTUMWA5:1
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.82 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.88 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.75 | P11:22:MEC:AUTO-SINGLE:NEAL3G:3
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.81 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.76 | P11:24:MEC:AUTO-SINGLE:LOUIS31G:1
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.81 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.84 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.74 | P13:345-22:MEC:AUTO-SINGLE:RAUN3:NEAL3G:1
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.8 | P13:345-24:MEC:AUTO-SINGLE:RAUN3:NEAL4G:1
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.74 | P13:345-24:MEC:AUTO-SINGLE:LOUISA3:LOUIS31G:1
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.149 | 112.78 | P11:230:WERE:JECU1_GEN::
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.149 | 112.78 | P11:345:WERE:JECU2_GEN::
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.149 | 112.78 | P11:345:WERE:JECU3_GEN::
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.95 | P11:345:WERE:WOLFU1_GEN::
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14904 | 112.63 | 511435 SNYDER-4 138 588779 TAP_G17-036 138 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14878 | 112.38 | 511446 CL-AFTP4 138 511458 ELKCTY-4 138 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14878 | 112.4 | 511446 CL-AFTP4 138 511463 HOB-JCT4 138 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14911 | 112.63 | 511453 DUNCAN-4 138 511552 DUNCHERTP4 138 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14911 | 112.62 | 511455 D.E.S.-4 138 511552 DUNCHERTP4 138 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14911 | 112.62 | 511455 D.E.S.-4 138 529344 OMDUNE-4 138 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.63 | 511456 O.K.U.-7 345 511565 OKLAUN HVDC7 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 111.6 | 511456 O.K.U.-7 345 588760 GEN-2017-033 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.15219 | 114.54 | 511456 O.K.U.-7 345 763215 G18-092-TAP 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.15233 | 115.11 | 511468 L.E.S.-7 345 762467 G18-015-TAP 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.15127 | 114.48 | 511468 L.E.S.-7 345 763215 G18-092-TAP 345 2
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.29 | 511468 L.E.S.-7 345 763318 GEN-2018-115 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14904 | 112.66 | 511488 112GORE4 138 511510 LAIRGST4 138 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14916 | 112.7 | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14904 | 112.65 | 511500 CACHE4 138 511510 LAIRGST4 138 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14904 | 112.64 | 511500 CACHE4 138 588779 TAP_G17-036 138 2
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.15068 | 112.8 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.75 | 511541 SWEETWT6 230 763340 GEN-2018-117 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14434 | 109.9 | 511553 CHISHOLM7 345 523961 POTTER_CO 7 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14434 | 109.9 | 511553 CHISHOLM7 345 523961 POTTER_CO 7 345 2
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.1569 | 116.03 | 515375 WWRDEHV7 345 515458 BORDER 7 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.1569 | 116.05 | 515458 BORDER 7 345 560022 CRAWFISH_DR 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.149 | 112.7 | 515618 BALKOW 7 345 3WXFMR BALKOW 7 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.149 | 112.7 | 515618 BALKOW 7 345 3WXFMR BALKOW 7 1_Dup1
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14896 | 112.95 | 515634 PALDR1W7 345 3WXFMR PALO2 _1 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.7 | 515677 BADGER 7 345 563170 G15082_1 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14897 | 112.61 | 520827 BINGERJ4 138 521017 ONEY 4 138 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14897 | 112.62 | 521017 ONEY 4 138 521089 WASHITA4 138 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.61 | 522800 MU-TULIA 3 115 525179 TULIA_TP 3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.75 | 522892 MU-BROWNFLD2 69.0 526761 BROWNFLD_TP2 69.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.64 | 523090 TEXAS_CNTY 3 115 589380 GEN-2017-100 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14899 | 112.78 | 523093 HITCHLAND 3 115 523174 GOODWELLWND3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.95 | 523097 HITCHLAND 7 345 523112 NOVUS1 7 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 113 | 523097 HITCHLAND 7 345 523215 FREWHELCOL17 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14676 | 111.48 | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.13259 | 109.07 | 523097 HITCHLAND 7 345 523961 POTTER_CO 7 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 113.05 | 523097 HITCHLAND 7 345 560252 G10-14 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.62 | 523099 TC-DRYTRLS 3 115 588480 A16-010_SUB 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.82 | 523112 NOVUS1 7 345 3WXFMR NOVUS XF2 2
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.63 | 523112 NOVUS1 7 345 3WXFMR XIANA2011198 _1 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14902 | 112.61 | 523118 BUFF_DUNES 7 345 523853 FINNEY 7 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.63 | 523120 COLE 3 115 588860 GEN-2017-047 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14901 | 112.64 | 523172 GWELL_COLL11 34.5 523174 GOODWELLWND3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14901 | 112.65 | 523173 GWELL_COLL21 34.5 523174 GOODWELLWND3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14922 | 112.61 | 523267 PRINGLE 6 230 3WXFMR ENRCO13617-1 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14922 | 112.61 | 523267 PRINGLE 6 230 523979 HARRNG_EST 6 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14995 | 113.07 | 523771 GRAPEVINE 6 230 524044 NICHOLS 6 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.15977 | 113.75 | 523959 POTTER_CO 6 230 524267 BUSHLAND 6 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.15641 | 114.67 | 523959 POTTER_CO 6 230 525461 NEWHART 6 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.15623 | 118.42 | 523961 POTTER_CO 7 345 3WXFMR WAUK 90343-A 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14907 | 112.4 | 523978 HARRNG_MID 6 230 523979 HARRNG_EST 6 230 @1
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14904 | 112.39 | 524010 ROLLHILLS 6 230 3WXFMR WAUK WT01104 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14932 | 112.74 | 524267 BUSHLAND 6 230 3WXFMR WH 7001795 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.16806 | 114.31 | 524267 BUSHLAND 6 230 524623 DEAFSMITH 6 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.1489 | 113.07 | 524296 SPNSPUR_WND7 345 524299 SPNSPUR_COL7 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.1489 | 113.07 | 524299 SPNSPUR_COL7 345 3WXFMR SPNSPUR_COL7 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.15255 | 113.32 | 524415 AMA_SOUTH 6 230 525213 SWISHER 6 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 113.2 | 524502 NORTON 3 115 524509 FE-TUCMCARI3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.15218 | 113.01 | 524575 DS-#25+ 3 115 524597 PANDAHFD 3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.15218 | 113.12 | 524575 DS-#25+ 3 115 524630 TIERABLANCA3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.7 | 524604 HEREFRD_SB 2 69.0 524608 HERFRD_STH 2 69.0 *1
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.1537 | 119.12 | 524623 DEAFSMITH 6 230 760498 G17-146-TAP 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 113.1 | 524721 DS-#15&#19+2 69.0 524745 CASTRO_CNTY2 69.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14961 | 112.61 | 524770 PLSNT_HILL 6 230 3WXFMR EFAE1100068A 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.18753 | 117.92 | 524875 OASIS 6 230 524885 SN_JUAN_TAP6 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.15589 | 113.69 | 524875 OASIS 6 230 524909 ROOSEVELT 6 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.18744 | 118.38 | 524885 SN_JUAN_TAP6 230 527483 CHAVES_CNTY6 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.1506 | 112.8 | 524909 ROOSEVELT 6 230 3WXFMR ABB LMM60042 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 113.33 | 524923 PORTALES 2 69.0 524929 RO-PORT_MTR2 69.0 @1
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 113 | 525001 W_MULESHOE 2 69.0 525008 MULESH_CTY 2 69.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 113 | 525008 MULESH_CTY 2 69.0 525027 BAILEYCO 2 69.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 113.28 | 525023 BC-BAIL_MTR2 69.0 525027 BAILEYCO 2 69.0 @1
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.15004 | 113.27 | 525056 BC-EARTH 3 115 525480 PLANT_X 3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 113.09 | 525191 KRESS_INT 2 69.0 525203 SW-KRESS 2 69.0 Z1
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 113.17 | 525192 KRESS_INT 3 115 3WXFMR ENRCO 136155 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.1519 | 113.6 | 525213 SWISHER 6 230 525461 NEWHART 6 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.73 | 525272 KISER 3 115 3WXFMR VON 13819/1 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 113.19 | 525326 COX 3 115 3WXFMR ELCO 13474-3 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 113.21 | 525414 LAMTON 3 115 3WXFMR ASEA MLL9204 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.1507 | 113.03 | 525440 LC-S_OLTON+3 115 525446 RKYFORD_TP 3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.1507 | 113.03 | 525446 RKYFORD_TP 3 115 525480 PLANT_X 3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.16161 | 116.34 | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14772 | 114.35 | 525481 PLANT_X 6 230 3WXFMR WH ALM20171 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.15615 | 118.3 | 525481 PLANT_X 6 230 526435 SUNDOWN 6 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.1537 | 117.38 | 525481 PLANT_X 6 230 760498 G17-146-TAP 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.15075 | 113.07 | 525481 PLANT_X 6 230 762174 G17-218TAP 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.15096 | 113.14 | 525481 PLANT_X 6 230 762174 G17-218TAP 230 2
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.15552 | 118.38 | 525531 TOLK 6 230 525586 NEEDMORE 6 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14976 | 114.61 | 525531 TOLK 6 230 525637 LAMB_CNTY 6 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.1727 | 118.52 | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.15157 | 113.33 | 525531 TOLK 6 230 762174 G17-218TAP 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.15174 | 113.39 | 525531 TOLK 6 230 762174 G17-218TAP 230 2
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.15552 | 118.36 | 525586 NEEDMORE 6 230 526935 YOAKUM 6 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 113.01 | 525599 LC-SANDHLL+2 69.0 525606 AMHERST 2 69.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 113.04 | 525606 AMHERST 2 69.0 525613 W_LITTLFLD 2 69.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 113.07 | 525613 W_LITTLFLD 2 69.0 525635 LAMB_CNTY 2 69.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 113.02 | 525635 LAMB_CNTY 2 69.0 525650 LC-LTTLFLD+2 69.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14976 | 114.61 | 525637 LAMB_CNTY 6 230 3WXFMR WH ALM20172 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.87 | 525828 TUCO_INT 3 115 3WXFMR DS F78800913 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14915 | 112.4 | 525830 TUCO_INT 6 230 3WXFMR ENRCO 136401 2
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.1395 | 114.37 | 525832 TUCO_INT 7 345 526936 YOAKUM_345 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 113.07 | 526086 SW_6786_N 2 69.0 526087 SW_6786_S 2 69.0 Z1
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 113.07 | 526086 SW_6786_N 2 69.0 526102 SP-HETTLER 2 69.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 113.14 | 526087 SW_6786_S 2 69.0 526284 PLANTERS 2 69.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.69 | 526160 CARLISLE 3 115 3WXFMR WH RLP38371 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 113.03 | 526195 QUINCY 3 115 526196 SP-MILWAUKEE 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.93 | 526268 LUBBCK_STH 3 115 3WXFMR NA 70454A 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 113.19 | 526284 PLANTERS 2 69.0 526297 LUBBCK_EST 2 69.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14895 | 112.63 | 526435 SUNDOWN 6 230 3WXFMR UPDATE LATER _12 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14808 | 115 | 526435 SUNDOWN 6 230 526460 AMOCO_SS 6 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14899 | 112.65 | 526525 WOLFFORTH 6 230 3WXFMR UPDATE LATER _13 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 113.07 | 526735 TERRY_CNTY 2 69.0 526747 LG-BROWNFLD2 69.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 113 | 526747 LG-BROWNFLD2 69.0 526754 BROWNFIELD 2 69.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14774 | 114.41 | 526935 YOAKUM 6 230 527028 INK_BASIN 6 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.13675 | 121.79 | 526936 YOAKUM_345 345 527896 HOBBS_INT 7 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14739 | 113.76 | 527028 INK_BASIN 6 230 527894 HOBBS_INT 6 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14878 | 113 | 527130 DENVER_N 3 115 527286 HIGGEAST 3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.61 | 527149 MUSTANG 6 230 3WXFMR ENRCO 136161 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14918 | 110.49 | 527149 MUSTANG 6 230 527151 GS-MUSTANG 6 230 @1
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.86 | 527202 SEAGRAVES 3 115 3WXFMR ABB MLL92408 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.76 | 527212 DIAMONDBACK3 115 3WXFMR HOW 36773714 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.68 | 527261 SULPHUR 2 69.0 527271 LG-FOSTER +2 69.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14878 | 112.98 | 527286 HIGGEAST 3 115 527363 HIGG 3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14884 | 112.82 | 527322 GAINES 3 115 527325 OXY_WSEM_TP3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14884 | 112.74 | 527325 OXY_WSEM_TP3 115 527362 JOHNSON_DRW3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.73 | 527340 DOSS 3 115 3WXFMR ELCO 13566/1 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.71 | 527345 LEGACY 2 69.0 527350 XTO_ROBRTSN2 69.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.71 | 527346 LEGACY 3 115 3WXFMR VROL 13735-1 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.69 | 527350 XTO_ROBRTSN2 69.0 527355 BOARDMAN 2 69.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.63 | 527355 BOARDMAN 2 69.0 527365 FLANNAGAN 2 69.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.61 | 527360 MAPCO 3 115 527362 JOHNSON_DRW3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.65 | 527362 JOHNSON_DRW3 115 528775 LE-ERF 3 115 @1
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14906 | 112.39 | 527455 RSWL_SLRCOL3 115 527482 CHAVES_CNTY3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14905 | 112.41 | 527470 CHVS_SLRCOL3 115 527464 CHVS_SOLAR11 34.5 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14905 | 112.34 | 527470 CHVS_SLRCOL3 115 527482 CHAVES_CNTY3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.16713 | 112.88 | 527483 CHAVES_CNTY6 230 527799 EDDY_NORTH 6 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.62 | 527508 PRICE 3 115 527509 PRICE_TAP 3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.62 | 527529 RIACBRSH_TP3 115 527533 SW4J795_E 3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.62 | 527533 SW4J795_E 3 115 527564 ROSWLL_INT 3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.62 | 527563 ROSWLL_INT 2 69.0 527575 SW_4702 2 69.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.15082 | 112.67 | 527564 ROSWLL_INT 3 115 527597 TWEEDY 3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.62 | 527575 SW_4702 2 69.0 527589 CV-ORCHARD 2 69.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14899 | 112.78 | 527653 MILO_WIND 1 34.5 527655 RSVLT_CC_E 7 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14891 | 112.66 | 527654 RSVLT_CC_W 7 345 527655 RSVLT_CC_E 7 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14891 | 112.95 | 527654 RSVLT_CC_W 7 345 527666 RSVLT_COL1 7 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14886 | 112.86 | 527655 RSVLT_CC_E 7 345 527656 CROSSROADS 7 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14891 | 112.95 | 527666 RSVLT_COL1 7 345 3WXFMR RSVLT_COL1 7 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.36 | 527736 NAVAJO_5TP 3 115 527739 NAVAJO_4 3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14902 | 112.35 | 527864 CUNNINHAM 3 115 528348 BUCKEYE_TP 3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14902 | 112.63 | 527864 CUNNINHAM 3 115 528568 MONUMNT_TP 3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14817 | 112.91 | 527865 CUNNIGHM_N 6 230 527867 CUNNIGHM_S 6 230 *1
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.1488 | 112.64 | 527865 CUNNIGHM_N 6 230 527963 POTASH_JCT 6 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14899 | 112.4 | 527867 CUNNIGHM_S 6 230 3WXFMR WH 7000266 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14899 | 112.86 | 527867 CUNNIGHM_S 6 230 527882 CUNINGHAM2 1 20.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.149 | 112.79 | 527894 HOBBS_INT 6 230 527903 HOBBS_PLT3 1 18.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.149 | 112.36 | 527965 KIOWA 7 345 528027 RDRUNNER 7 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14904 | 112.36 | 528015 PHANTOM 7 345 528027 RDRUNNER 7 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.41 | 528024 RR_SVC_HV 3 115 528021 RDRUNNR_SVC1 15.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.68 | 528025 RDRUNNER 3 115 587990 GEN-2016-121 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14905 | 112.42 | 528185 N_LOVING 7 345 3WXFMR HYO1063400-1 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14902 | 112.41 | 528185 N_LOVING 7 345 528223 CHINA_DRAW 7 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.36 | 528222 CHINA_DRAW 3 115 528225 CD_SVC_HV 3 115 Z1
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14892 | 112.34 | 528333 LE-WEST_SUB3 115 528334 LE-NRTH_INT3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14902 | 112.42 | 528341 LE-SANANDRS3 115 528627 LE-TXACO_TP3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14902 | 112.38 | 528348 BUCKEYE_TP 3 115 528627 LE-TXACO_TP3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14888 | 112.62 | 528394 QUAHADA 3 115 528396 XTO_BIGEDDY3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.149 | 112.33 | 528463 SANGER_SW 3 115 528575 OXYPERMIAN 3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.149 | 112.33 | 528463 SANGER_SW 3 115 762442 G18-004-TAP 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14902 | 112.63 | 528568 MONUMNT_TP 3 115 528581 BYRD_TP 3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.149 | 112.38 | 528574 OXY_NHU_RCF3 115 528575 OXYPERMIAN 3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.69 | 528617 LE-WAITS 2 69.0 528325 LE-WAITS 3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.61 | 528617 LE-WAITS 2 69.0 528714 LE-FORT_SW 2 69.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14902 | 112.42 | 528622 LE-SANANDRS2 69.0 528341 LE-SANANDRS3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.97 | 528626 LE-PLNSINT 2 69.0 526928 PLAINS_INT 3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.97 | 528626 LE-PLNSINT 2 69.0 528709 LE-PLNSGOAB2 69.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.63 | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.69 | 528669 LE-STKLDRTP2 69.0 528740 LE-PLANS_SW2 69.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.85 | 528709 LE-PLNSGOAB2 69.0 528740 LE-PLANS_SW2 69.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.63 | 528709 LE-PLNSGOAB2 69.0 528747 LE-ALLRED 2 69.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.61 | 528714 LE-FORT_SW 2 69.0 528718 LE-NEWTEX 2 69.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.69 | 528735 LE-PLAINSUB2 69.0 528740 LE-PLANS_SW2 69.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14893 | 112.41 | 530583 POSTROCK7 345 588654 G17-021-TAP 345 2
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.41 | 531213 SANTAFE3 115 531408 PIERCVL3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14873 | 112.33 | 531451 MINGO 7 345 531465 SETAB 7 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14901 | 112.62 | 531501 BUCKNER7 345 531502 CIMRRN 7 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14901 | 112.62 | 531502 CIMRRN 7 345 531503 CIMRRN 1 34.5 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14889 | 112.32 | 531510 HARBNGR3 115 3WXFMR HARBGR345 _1 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14902 | 112.64 | 532663 LEC U5 24.0 532854 LEC U5 6 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14902 | 112.64 | 532853 LAWHILL6 230 532854 LEC U5 6 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.69 | 542951 HAW G5 1 22.0 543665 HAWTHN5 161 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14902 | 112.74 | 542955 LAC G1 1 22.0 542981 LACYGNE7 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14901 | 112.72 | 542956 LAC G2 1 24.0 542981 LACYGNE7 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14901 | 112.76 | 542957 IAT G1 1 24.0 542982 IATAN 7 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14901 | 112.82 | 542962 IAT G2 1 24.5 542982 IATAN 7 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.61 | 542966 WGARDNR5 161 543105 BULLCRK5 161 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.15158 | 112.16 | 560022 CRAWFISH_DR 345 762216 G17-151TAP 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.15125 | 113.18 | 560022 CRAWFISH_DR 345 762467 G18-015-TAP 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 108.98 | 560022 CRAWFISH_DR 345 763087 GEN-2018-073 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.15241 | 113.55 | 560022 CRAWFISH_DR 345 763215 G18-092-TAP 345 2
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 113.05 | 560252 G10-14 345 560253 G10-14-1 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.78 | 560253 G10-14-1 115 560254 G10-14-SUB1 34.5 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.78 | 560253 G10-14-1 115 560255 G10-14-SUB2 34.5 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.63 | 560581 G06-44-2 34.5 523111 NOVUS1 3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.68 | 560582 G06-44-3 34.5 560577 G06-44 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.66 | 560583 G06-44-4 34.5 560577 G06-44 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.32 | 560757 ASGI13_02_1 69.0 560758 ASGI13_02_2 34.5 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.32 | 560757 ASGI13_02_1 69.0 562731 WHEATLAND 69.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.33 | 560763 ASGI13_03_1 115 560761 ASGI13_03_2 34.5 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.76 | 562015 FIREWHEEL1 34.5 523215 FREWHELCOL17 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.76 | 562016 FIREWHEEL2 34.5 523215 FREWHELCOL17 345 2
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.31 | 562323 AGI1202&1305 115 562324 AGI1202&1305 34.5 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.32 | 562727 LESBIA 115 562728 SANJONTAP 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.32 | 562728 SANJONTAP 115 562729 CAPROCKTAP1 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.32 | 562730 CAPROCKTAP2 69.0 562729 CAPROCKTAP1 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.32 | 562730 CAPROCKTAP2 69.0 562731 WHEATLAND 69.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.72 | 563171 G15082_2 34.5 563170 G15082_1 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.4 | P11:13.8:AEPW:COM1-1
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.41 | P11:13.8:AEPW:COM2-1
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.41 | P11:13.8:AEPW:COM3-1
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.42 | P11:18:AEPW:WELSH1-1
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.42 | P11:18:AEPW:WELSH3-1
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.42 | P11:24:AEPW:PIRKEY 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.39 | P11:24:AEPW:SWS3-1
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.39 | P11:24:AEPW:TURKCOAL
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14916 | 112.7 | P12:138:AEPW-OMPA:DUNCAN-4:OMDUNCN4
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14904 | 112.66 | P12:138:AEPW:112GORE4:SNYDER-4
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14904 | 112.66 | 5841_Dup1
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14912 | 111.96 | 584560 GEN-2015-014 115 584561 G15-014XFMR1 34.5 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14911 | 112.65 | P12:138:AEPW:SANTAFE:DUNCAN-4
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.68 | 587991 G16-121XFMR1 34.5 587990 GEN-2016-121 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.62 | 588480 A16-010_SUB 115 3WXFMR A16-010_SUB 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14916 | 112.7 | P12:138:AEPW:DUNCAN-4:L.E.S.-4
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.06 | 588761 G17-033XFMR1 34.5 588760 GEN-2017-033 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.06 | 588765 G17-033XFMR2 34.5 588760 GEN-2017-033 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.63 | 588861 G17-047XFMR1 34.5 588860 GEN-2017-047 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14866 | 112.2 | P12:138:AEPW:ELKCTY-4:CLINTJC4
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.64 | 589381 G17-100XFMR1 34.5 589380 GEN-2017-100 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14878 | 112.39 | P12:138:AEPW:HOB-JCT4:ELKCTY-4
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.64 | P12:138:AEPW:SHERID4:112GORE4
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14901 | 112.61 | P12:230:AEPW:SWEETWT6:BUFFCK6
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14901 | 112.66 | P12:230:AEPW:SWEETWT6:ROARK6
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.15146 | 114.5 | P12:345:AEPW:L.E.S7:TERRYRD7
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.15146 | 114.49 | P12:345:AEPW:L.E.S7:TERRYRD7
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.15146 | 114.47 | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.15211 | 114.61 | P12:345:AEPW-OKGE:L.E.S.-7:GRACMNT7
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.15211 | 114.58 | P12:345:AEPW-OKGE:L.E.S.-7:GRACMNT7
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14899 | 112.4 | P12:345:AEPW-OKGE:PITTSB-7:SEMINOL7
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.15219 | 115.66 | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.66 | P22:345:AMMO::LABADIE:1
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.66 | P22:345:AMMO::LABADIE:2
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.66 | P22:345:AMMO::LABADIE:3
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.66 | P22:345:AMMO::LABADIE:4
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.65 | P22:345:AMMO::RUSHISLAND:1
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.64 | P22:345:AMMO::RUSHISLAND:2
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14904 | 112.41 | P13:138-13.8:AEPW:COMANC-4_#2
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14729 | 111.28 | P13:138-230:AEPW:ELKCTY-4
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14905 | 112.4 | P13:138-24:AEPW:S.W.S.-4
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14904 | 112.39 | P13:138-24:AEPW:TURK 4
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14912 | 112.63 | P13:138-345:AEPW:L.E.S.-4_#1
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14921 | 112.75 | P13:138-345:AEPW:L.E.S.-4_#2
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14905 | 112.67 | P23:500:EES-EAI:KEO:B4941
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14905 | 112.66 | P23:500:EES-EAI:KEO:B4921
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.61 | P11:26:EES-EAI:INDEP2:1:D401
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.61 | P11:26:EES-EAI:INDEP2:1
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.61 | P13:500:EES-EAI:INDEP2:MT2
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14904 | 112.65 | P23:500:EES-EAI:INDEP2:B6126
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14904 | 112.64 | P23:500:EES-EAI:PD:INDEP2:LN:FK479
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14901 | 112.61 | P13:230-34.5:AEPW:BUFFCK6
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14901 | 112.67 | P13:230-34.5:AEPW:ROARK6
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.41 | P13:69-13.8:AEPW:COMANC-2
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.66 | P11:024:DPC:ALMA2:6
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.62 | P11:18:ITCM:EMERYGT1:1
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.63 | P11:18:ITCM:EMERYGT2:1
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.63 | P11:161:ITCM:MGS CT1:1C
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.63 | P11:161:ITCM:MGS CT2:2C
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14901 | 112.64 | 652537 WHITE 3 345 659286 DEERCREK-BE3 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14901 | 112.64 | 659286 DEERCREK-BE3 345 3WXFMR DEERCRK KU1A 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.63 | 672601 BD 4 230 672306 BD 6G 18.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.63 | 672610 POPLAR 4 230 672310 POPLAR 1G 18.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.63 | 672610 POPLAR 4 230 672311 POPLAR 2G 18.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.62 | 672621 SHAND 4 230 672321 SHAND 1G 18.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.61 | 672649 CODETTE 4 230 672650 NIPAWIN 4 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.62 | 672696 BRADA 4 230 672699 NBEC 4 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.69 | P23:345:MDU::COYOTE::5707-5712-5715::::
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.84 | P23:345:MEC:CBEC 905
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.81 | P23:345:MEC:CBEC 908
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.64 | P23:345:MEC:GDMEC 908
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.74 | P23:345:MEC:RAUN 0180
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.8 | P23:345:MEC:RAUN 0210
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.75 | P23:345:MEC:LOUISA 954
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14904 | 112.75 | P23:345:MEC:LOUISA 964
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.61 | P21:115:XEL:AUTO-SINGLE:CHEMOLT7:LSPOWER7:1
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.65 | P21:115:XEL:AUTO-SINGLE:COLVILL7:CANONFLSG7:1
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.61 | P21:115:XEL:AUTO-SINGLE:FARIBALTP7:FARIBALTGEN:Z
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.7 | P21:230:OTP:AUTO-SINGLE:SQBUTTE4:YNG24:1
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.69 | P23:345:OTP:CENTER 3:3215(1)
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.69 | P23:345:OTP:CENTER 3:3225(1)
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.63 | P12:230:UMZW:# 687 #: FT IN SD. FT-BG1 LINE FAULT
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.63 | P12:230:UMZW:# 3617 #: FT IN SD. FT-BG2 LINE FAULT
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 111.33 | 760494 GEN-2017-146 230 760498 G17-146-TAP 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 111.32 | 760495 G17-146-XFM1 34.5 760494 GEN-2017-146 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.05 | 761356 G17-239-XFMR 34.5 761355 GEN-2017-239 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.05 | 761359 G17-239-XFMR 34.5 761355 GEN-2017-239 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.23 | 761797 G17-187XFM1 34.5 761796 GEN-2017-187 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.23 | 761800 G17-187XFM2 34.5 761796 GEN-2017-187 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 107.16 | 762132 GEN-2017-158 230 763252 G18-099-XFM1 34.5 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 107.16 | 762132 GEN-2017-158 230 763255 G18-099-XFM2 34.5 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 107.74 | 762133 G17-158XFM1 34.5 762132 GEN-2017-158 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 107.74 | 762136 G17-158XFM2 34.5 762132 GEN-2017-158 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 109.9 | 762216 G17-151TAP 345 762217 GEN-2017-151 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.15158 | 113.55 | 762216 G17-151TAP 345 762467 G18-015-TAP 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 111.85 | 762218 G17-151XFM1 34.5 762217 GEN-2017-151 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 111.85 | 762221 G17-151XFM2 34.5 762217 GEN-2017-151 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 111.85 | 762224 G17-151XFM3 34.5 762217 GEN-2017-151 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 111.85 | 762227 G17-151XFM4 34.5 762217 GEN-2017-151 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.36 | 762438 GEN-2018-004 115 762442 G18-004-TAP 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 110.89 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 111.7 | 762461 G18-015-XFM1 34.5 762460 GEN-2018-015 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 111.7 | 762464 G18-015-XFM2 34.5 762460 GEN-2018-015 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.15043 | 113.07 | 762467 G18-015-TAP 345 763215 G18-092-TAP 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 110.18 | 763087 GEN-2018-073 345 763088 G18-073-XFM1 34.5 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 111.33 | 763087 GEN-2018-073 345 763091 G18-073-XFM2 34.5 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 107.16 | 763120 GEN-2018-081 230 763121 G18-081-XFM1 34.5 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 109.42 | 763120 GEN-2018-081 230 764011 G19-074-XFM1 34.5 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 109.44 | 763186 GEN-2018-089 230 763187 G18-089-XFM1 34.5 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 110.21 | 763208 GEN-2018-092 345 763215 G18-092-TAP 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 111.37 | 763208 GEN-2018-092 345 763220 G18-092-XFM1 34.5 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 111.37 | 763208 GEN-2018-092 345 763223 G18-092-XFM2 34.5 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 108.87 | 763241 GEN-2018-097 230 763242 G18-097-XFM1 34.5 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 109.78 | 763241 GEN-2018-097 230 763296 G18-111-XFM1 34.5 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 109.14 | 763241 GEN-2018-097 230 763307 G18-112-XFM1 34.5 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 109.14 | 763241 GEN-2018-097 230 763310 G18-112-XFM2 34.5 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 108.87 | 763241 GEN-2018-097 230 763395 G18-124-XFM1 34.5 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 108.87 | 763241 GEN-2018-097 230 763398 G18-124-XFM2 34.5 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.29 | 763318 GEN-2018-115 345 763319 G18-115-XFM1 34.5 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.75 | 763340 GEN-2018-117 230 763341 G18-117-XFM1 34.5 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 108.51 | 763483 GEN-2019-003 230 763484 G19-003-XFM1 34.5 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 111.9 | 763516 GEN-2019-011 345 763517 G19-011-XFM1 34.5 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.26 | 763879 GEN-2019-056 115 763880 G19-056XFM1 34.5 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14854 | 112.68 | P42:345:OKGE:SB_BVTY7305
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14895 | 112.43 | P23:345:WERE:BUFF_345-534::
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14895 | 112.43 | P23:345:WERE:BUFF_345-543::
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.149 | 112.78 | P23:345:WERE:JEC_345-15::
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14899 | 112.75 | P23:345:WERE:JEC_345-16::
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.149 | 112.78 | P23:345:WERE:JEC_345-19::
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.149 | 112.78 | P23:345:WERE:JEC_345-20::
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.95 | P23:345:WERE:WOLF_345-50::
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.95 | P23:345:WERE:WOLF_345-60::
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14904 | 112.43 | P42:345:AEPW:WELSH CB 10620 NBTB+FAULT
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.15219 | 114.21 | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.15244 | 114.99 | P42:345:AEPW:LAWTON EASTSIDE CB 3413A NBTB+FAULT
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.1528 | 115.4 | P42:345:AEPW:LAWTON EASTSIDE CB 3425A NBTB+FAULT
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.15233 | 115.86 | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14918 | 112.31 | P42:345:AEPW:PITTSBURG CB 3441A NBTB+FAULT
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14899 | 112.4 | P42:345:AEPW:PITTSBURG CB 3445A NBTB+FAULT
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.15146 | 114.49 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.15146 | 114.49 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.15146 | 114.47 | P42:345:AEPW:TERRYRD_CB_3421A_NBTB
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14902 | 112.75 | P23:345:KCPL:LACYGNE_R2-5::LACYGU2-LACYGNE-STILWELL
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14904 | 112.43 | P23:345:AEPW:WELSH CB 10620 NBTB
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.15219 | 114.54 | P23:345:AEPW:OKLAUNION CB 3401A NBTB
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.15244 | 114.99 | P23:345:AEPW:LAWTON EASTSIDE CB 3413A NBTB
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.1528 | 115.4 | P23:345:AEPW:LAWTON EASTSIDE CB 3425A NBTB
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.15233 | 115.86 | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14918 | 112.31 | P23:345:AEPW:PITTSBURG CB 3441A NBTB
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14899 | 112.4 | P23:345:AEPW:PITTSBURG CB 3445A NBTB
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.15146 | 114.49 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.15146 | 114.49 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.15146 | 114.47 | P23:345:AEPW:TERRYRD_CB_3421A_NBTB
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14935 | 112.62 | P12:138:AEPW:S.W.S.-4:L.E.S.-4
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14903 | 112.65 | P11:115:SUNC:GARDENCITY_S2:97:531459(2)
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.15165 | 114.72 | P23:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.15423 | 117.32 | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.15165 | 114.72 | P42:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB+FAULT
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.15423 | 117.32 | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14129 | 109.51 | P42:345:OKGE:SB_BVTY7315_PRE19S
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14873 | 112.33 | P23:345:SUNC:MO_BRK182
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14873 | 112.33 | P23:345:SUNC:MO_BRK382
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14901 | 112.42 | P21:345:UMZW:# 725 #: GI IN NE. GI-SWEET LINE FAULT
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.15068 | 112.8 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14904 | 112.41 | P12:138-13.8:AEPW:COMANC-4_#1
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.14729 | 111.26 | P12:230:AEPW:ELKCITY6:CHISHOLM6
Thermal | 05ALL | 1 | 23SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.15057 | 113.54 | P12:230:AEPW:SWEETWT6:CHISHOLM6
Thermal | 05ALL | 1 | 23SP | GEN-2019-056 | FROM->TO | 511458 ELKCTY-4 138 998036 ELKCTY-6 _1 138 1 |  | 330 | 0.12825 | 112.44 | P12:345:OKGE-AEPW:BKRBKR371::::
Thermal | 05ALL | 1 | 23SP | GEN-2019-056 | FROM->TO | 511458 ELKCTY-4 138 998036 ELKCTY-6 _1 138 1 |  | 330 | 0.12825 | 112.78 | P12:345:OKGE-AEPW:BKRBKR371::::
Thermal | 05ALL | 1 | 23SP | GEN-2019-056 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.12825 | 108.04 | P12:345:OKGE-AEPW:BKRBKR371::::
Thermal | 05ALL | 1 | 23SP | GEN-2019-056 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.12825 | 108.6 | P12:345:OKGE-AEPW:BKRBKR371::::
Thermal | 05ALL | 1 | 23SP | GEN-2019-056 | FROM->TO | 511490 ELKCITY6 230 998036 ELKCTY-6 _1 138 1 |  | 330 | 0.12825 | 112.79 | P12:345:OKGE-AEPW:BKRBKR371::::
Thermal | 05ALL | 1 | 23SP | GEN-2019-056 | FROM->TO | 511490 ELKCITY6 230 998036 ELKCTY-6 _1 138 1 |  | 330 | 0.12825 | 113.27 | P12:345:OKGE-AEPW:BKRBKR371::::
Thermal | 05ALL | 1 | 23SP | GEN-2019-056 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.0769 | 118.42 | 523961 POTTER_CO 7 345 3WXFMR WAUK 90343-A 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 511458 ELKCTY-4 138 998036 ELKCTY-6 _1 138 1 |  | 330 | 0.10462 | 112.44 | P12:345:OKGE-AEPW:BKRBKR371::::
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 511458 ELKCTY-4 138 998036 ELKCTY-6 _1 138 1 |  | 330 | 0.10462 | 112.78 | P12:345:OKGE-AEPW:BKRBKR371::::
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.10462 | 108.04 | P12:345:OKGE-AEPW:BKRBKR371::::
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.10462 | 108.6 | P12:345:OKGE-AEPW:BKRBKR371::::
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 511490 ELKCITY6 230 998036 ELKCTY-6 _1 138 1 |  | 330 | 0.10462 | 112.79 | P12:345:OKGE-AEPW:BKRBKR371::::
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 511490 ELKCITY6 230 998036 ELKCTY-6 _1 138 1 |  | 330 | 0.10462 | 113.27 | P12:345:OKGE-AEPW:BKRBKR371::::
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17493 | 112.73 | P23:345:KCPL-WERE:237LACYGNE_R1-6::LACYGU1-LACYGNE-NEOSHO
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.1749 | 112.64 | P11:230:WERE:LECU5_GEN::
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17491 | 112.63 | P11:161:GMO:DOGWOOD_COMBINED_CYCLE_UNIT_OUTAGE_1_1
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17498 | 111.16 | P11:115:SPS:MUSTANG1&3:153MW::::
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17572 | 114.61 | P12:230:SPS:K37::1_TOLK_LAMB:::
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17511 | 112.61 | P12:230:SPS:K43::1_PRNGLE_HARR_E:::
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17495 | 112.37 | P12:230:SPS:K44::1_EPLNT_HARRW:::
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17509 | 112.79 | P12:115:SPS:T04::1_TRBLNC_CASTRO:::
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.19 | P12:115:SPS:T13::1_TAYLOR_WHOBBS:::
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.31 | P12:115:SPS:T14::1_MADDOX_TAYLOR:::
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 113.09 | P12:115:SPS:T21::1_GRSSLND_GRAHAM:::
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.41 | P12:115:SPS:T23::1_PCA_POTJCT:::
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.62 | P12:115:SPS:T24B::1_RSWLL_BRSHRF:::
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17493 | 112.64 | P12:115:SPS:T26::1_CHAVES_RSWLCTY:::
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17632 | 113.18 | P12:115:SPS:T28A::1_LAMTON_PLANTX:::
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17549 | 112.67 | P12:115:SPS:T29::1_LAMTON_HALECTR:::
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17634 | 113.96 | P12:115:SPS:T30::1_LAMB_HOCKLY:::
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17634 | 113.13 | P12:115:SPS:T31::1_HOCKLY_SUNDWN:::
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.1749 | 112.63 | P12:115:SPS:T35::1_TERRY_YOAKUM:::
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 113.32 | P12:115:SPS:T45::1_NORRIS_OASIS:::
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17493 | 112.4 | P12:115:SPS:T57::1_MUSTG_SEGRVS:::
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17557 | 113.15 | P12:115:SPS:T59::1_CARGIL_CURRY:::
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.176 | 112.42 | P12:115:SPS:T66::1_RNDALL_HAPPY:::
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.176 | 112.9 | P12:115:SPS:T67::1_HAPPY_KRESS:::
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17497 | 112.39 | P12:115:SPS:T68::1_TUCO_FLOYD:::
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17486 | 113.2 | P12:115:SPS:T71::1_CRLSLE_YUMA:::
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17504 | 112.7 | P12:115:SPS:T81::1_COX_FLOYD:::
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17491 | 112.85 | P12:115:SPS:T83::1_SP-FKFD_ALLEN:::
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 113.01 | P12:115:SPS:T89::1_DC_N_HIGG:::
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.66 | P12:115:SPS:T91::1_HIGG_RUSSELL:::
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17517 | 112.62 | P12:115:SPS:V04::1_EPLANT_RNDALL:::
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17508 | 112.67 | P12:115:SPS:V07::1_COX_HALECTR:::
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17628 | 112.95 | P12:115:SPS:V09::1_HALECTR_PLANTX:::
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17493 | 112.83 | P12:115:SPS:V12::1_PLANTX_BAILEY:::
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17491 | 112.62 | P12:115:SPS:V15::1_TUCO_INDANA:::
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17459 | 112.67 | P12:115:SPS:V24::1_WOLFTH_TERRY:::
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17508 | 112.64 | P12:115:SPS:V26::1_RSWLL_EDDY_N:::
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.98 | P12:115:SPS:V33::1_LUBBS_LYNN:::
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17607 | 113.85 | P12:115:SPS:V37::1_CASTRO_PLANTX:::
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.75 | P12:115:SPS:V46::1_ALLEN_WHEELCK:::
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17494 | 113.09 | P12:115:SPS:V49::1_YOAKUM_SHLCO2:::
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17551 | 113.26 | P12:115:SPS:V55::1_SUNDWN_TERRY:::
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17517 | 113.09 | P12:115:SPS:V56::1_COCHRAN_SUNDWN:::
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17491 | 112.68 | P12:115:SPS:V62::1_CRLSLE_INDANA:::
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17493 | 112.62 | P12:115:SPS:V70::1_S_GORG_RNDALL:::
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17496 | 112.65 | P12:115:SPS:V78::2_CURRY_RSVLT:::
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17494 | 112.79 | P12:115:SPS:V81::1_LE-WAIT_LE-LVN:::
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.65 | P12:115:SPS:V95::1_DC_N_SHLCO2:::
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.61 | P12:115:SPS:W11::1_DC_S_SMINLE:::
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.61 | P12:115:SPS:W12::1_SMINLE_DOSS:::
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.68 | P12:115:SPS:W14::1_SMINLE_GAINES:::
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 113.14 | P12:115:SPS:W32::1_PRMTR_FE-CLSIN:::
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.61 | P12:115:SPS:W34::1_JNSDRW_MAPCO:::
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17493 | 112.85 | P12:115:SPS:W35::1_GAINES_JNSDRW:::
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17493 | 112.64 | P12:115:SPS:W36::1_TAYLOR_JNSDRW:::
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17714 | 113.15 | P12:115:SPS:W40::1_WCANYON_TRBLNC:::
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17529 | 112.71 | P12:115:SPS:W52::1_NEWHART_KRESS:::
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 113.2 | P12:115:SPS:W58::1_NORTON_LOPEZ:::
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.82 | P12:115:SPS:W59::1_LOPEZ_CMPBLL:::
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 113.15 | P12:115:SPS:W62::1_PLSTHL_CURRY:::
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17504 | 112.62 | P12:115:SPS:W63::1_PLSTHL_CURRY:::
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.96 | P12:115:SPS:W64::1_PLSTHL_FE-CLV:::
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 113.12 | P12:115:SPS:W65::1_PLSTHL_CURRY:::
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.81 | P12:115:SPS:W66::1_PORTA_GREYHUND:::
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17714 | 112.61 | P12:115:SPS:W77::1_RNDAL_WCANYON:::
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.64 | P12:115:SPS:W99::1_CAPITAN_CHAVES:::
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17491 | 113.08 | P12:115:SPS:U14::1_DC_STH_INKBSN:::
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17494 | 113.02 | P12:115:SPS:V15::1_INKBSN_LE-WAT:::
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17519 | 112.74 | P12:115:SPS:U16::1_BSHLND_OUTPST:::
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17519 | 112.73 | P12:115:SPS:U17::1_COLTR_OUTPST:::
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.1751 | 112.8 | P12:115:SPS:U19::1_DEAN_PLAINS:::
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17519 | 112.67 | P12:115:SPS:U23::1_COLTR_HILSDE:::
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.16753 | 119.61 | P42:345:SPS:YOAKUM:J18####:SLG1:EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.16753 | 119.61 | P43:345:SPS:YOAKUM:TF#####:SLG:EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.16753 | 119.61 | P42:345:SPS:YOAKUM:J17####:SLG:EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.16753 | 119.61 | P42:345:SPS:YOAKUM:J18####:SLG2:EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17491 | 112.62 | P11:18:HAST:::EGYCTR2G WEC2_LOSS OF WEC 2 GEN_:HV:
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17491 | 112.62 | P13:18-115:HAST:::EGYCNTR7 XFMR G2WEC 2 GSU_:HV:
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17491 | 112.63 | P11:161:GMO:DOGWOOD-COMBINED-CYCLE-UNIT-OUTA:::HV:
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17493 | 112.73 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.1749 | 112.75 | P23:345:KCPL:LACYGNE-R2-5:::EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17488 | 112.78 | P11:230:WERE:JECU1-GEN:::HV:
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.1749 | 112.64 | P11:230:WERE:LECU5-GEN:::HV:
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17488 | 112.78 | P11:345:WERE:JECU2-GEN:::EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17488 | 112.78 | P11:345:WERE:JECU3-GEN:::EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.95 | P11:345:WERE:WOLFU1-GEN:::EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17484 | 112.43 | P23:345:WERE:BUFF-345-534:::EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17484 | 112.43 | P23:345:WERE:BUFF-345-543:::EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17488 | 112.78 | P23:345:WERE:JEC-345-15:::EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17487 | 112.75 | P23:345:WERE:JEC-345-16:::EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17488 | 112.78 | P23:345:WERE:JEC-345-19:::EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17488 | 112.78 | P23:345:WERE:JEC-345-20:::EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.95 | P23:345:WERE:WOLF-345-50:::EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.95 | P23:345:WERE:WOLF-345-60:::EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.89 | P11:022:NPPD:COOPER1G:1:983:::
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17487 | 112.92 | P11:023:NPPD:GENTLM1G:1:757:::
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17487 | 112.94 | P11:024:NPPD:GENTLM2G:2:757:::
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17489 | 112.75 | P13:345:OPPD:NEBCTY1G:::EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17487 | 112.78 | P13:345:OPPD:NEBCTY2G:::EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.77 | P22:345:OPPD:S3458 NEBCTY1G:LT::EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17489 | 112.75 | P22:345:OPPD:S3458 NEBCTY1G:::EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.81 | P22:345:OPPD:S3458 NEBCTY2G:LT::EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17487 | 112.78 | P22:345:OPPD:S3458 NEBCTY2G:::EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.77 | P23:345:OPPD:S3458 NEBCTY1G:LT::EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17489 | 112.75 | P23:345:OPPD:S3458 NEBCTY1G:::EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.81 | P23:345:OPPD:S3458 NEBCTY2G:LT::EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17487 | 112.78 | P23:345:OPPD:S3458 NEBCTY2G:::EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.4 | P12:115:SUNC:PLYMELL-PIERCEVILLE:::HV::
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.1749 | 112.64 | P11:018:UMZB:# 5 #:: DCS IN SD. DEERCREEK_MV::
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17491 | 112.61 | P11:022:UMZB:# 15 #:: LO IN ND. LELAND OLDS 1_MV::
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.1749 | 112.65 | P11:020:UMZB:# 16 #:: LO IN ND. LELAND OLDS 2_MV::
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.1749 | 112.7 | P11:023:UMZB:# 31 #:: AVS IN ND. ANTELOPE VALLEY 1_MV::
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.1749 | 112.7 | P11:023:UMZB:# 32 #:: AVS IN ND. ANTELOPE VALLEY 2_MV::
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17486 | 112.9 | P11:024:UMZB:# 33 #:: LRS IN WY. LARAMIE RIVER STATION 1_MV::
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.63 | P12:230:UMZW:# 687 #:: FT IN SD. FT-BG1 BRANCH FAULT:HV:
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.63 | P12:230:UMZW:# 3617 #:: FT IN SD. FT-BG2 BRANCH FAULT:HV:
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.63 | P12:230:UMZW:# 4038 #:: BG-FT IN SD. FAULT FOR TRANSMISSION CIRCUIT (BG-FT).:HV:
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.63 | P12:230:UMZW:# 4039 #:: BG-FT IN SD. FAULT FOR TRANSMISSION CIRCUIT (BG-FT).:HV:
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.61 | P13:230:UMZW:# 5135 #:: OA IN SD. FAULT ON TRANSFORMER (2).:HV:
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.61 | P13:230:UMZW:# 5136 #:: OA IN SD. FAULT ON TRANSFORMER (3).:HV:
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17489 | 112.42 | P21:345:UMZW:# 725 #:: GI IN NE. GI-SWEET BRANCH FAULT:EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17489 | 112.42 | P23:345:UMZW:# 2430 #:: GI IN NE. GI 1492 BKR FAULT:EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17489 | 112.42 | P23:345:UMZW:# 2438 #:: GI IN NE. GI-SWEET BRANCH FAULT & GI 1492 STUCK BKR:EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17494 | 112.37 | P11:138:WFEC:HUGO1:465MW :::
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17488 | 112.4 | P12:345:OKGE-AEPW:BKRBKR20::::
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17528 | 112.75 | P12:345:OKGE:BKRBKR21::::
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17546 | 112.95 | P12:345:OKGE:BKRBKR24::::
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17734 | 114.47 | P12:345:OKGE-AEPW:BKRBKR25::::
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17482 | 112.42 | P12:345:OKGE:BKRBKR336::::
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17482 | 112.41 | P12:345:OKGE:BKRBKR336_2::::
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17799 | 114.61 | P12:345:OKGE-AEPW:BKRBKR366::::
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17799 | 114.58 | P12:345:OKGE-AEPW:BKRBKR366::::
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17547 | 112.87 | P12:345:OKGE:BKRBKR367::::
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17523 | 112.62 | P12:345:OKGE-WFEC:BKRBKR374::::
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.1745 | 112.22 | P12:345:OKGE:BKRBKR4193::::
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.1745 | 112.22 | P12:345:OKGE:BKRBKR4194::::
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17434 | 112.28 | P12:345:OKGE-SPS:BKRBKR4201::::
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17434 | 112.28 | P12:345:OKGE-SPS:BKRBKR4202::::
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17481 | 112.35 | P12:345:OKGE:BKRBKR443NEW::::
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17481 | 112.35 | P12:345:OKGE:BKRBKR443NEW2::::
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17486 | 112.88 | P12:345:OKGE:BKRBKR604::::
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17485 | 112.94 | P12:345:OKGE:BKRBKR604_2::::
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17443 | 112.62 | P42:345:OKGE:SB_ARIA7381::::
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.18278 | 116.05 | P42:345:OKGE:SB_BVTY7387::::
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17527 | 112.68 | P42:345:OKGE:SB_SPCK7383::::
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.1749 | 112.64 | P11:115:SUNC:GARDENCITY_S2:103:531459(2):HV:
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.1749 | 112.64 | P11:115:SUNC:FORTDDODGE_4:157:539670(4):HV:
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.62 | P11:345:599:CIMARRON1WIND:200:531603(1):EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.92 | P13:115:SUNC:HOLCOMB_GSU:::HV:
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.1749 | 112.64 | P13:115:SUNC:S2_GSU:::HV:
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.1749 | 112.64 | P13:115:SUNC:FORTDODGE_GSU:::HV:
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.1749 | 112.62 | P23:345:SUNC:BU_BRK682:::EHV:
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.71 | 300003 1THLG3 24.0 301503 7THOMHLGSU3 345 3
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.71 | 300049 7THOMHL 345 301503 7THOMHLGSU3 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.66 | P11:20:AMMO:1LAB�� G1:1
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.66 | P11:20:AMMO:1LAB�� G2:2
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.83 | P11:345:AMMO::CALLAWAY:1
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.66 | P11:345:AMMO::LABADIE:3
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.66 | P11:345:AMMO::LABADIE:4
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.66 | P11:345:AMMO::RUSHISLAND:U1
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.66 | P11:345:AMMO::RUSHISLAND:U2
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.64 | P11:138:AMMO::SIOUX:2
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.64 | P12:765:AEP:AEP ROCKP-AEP JEFF 765
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.61 | P11:HV:EES::1ISES U1:1
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.61 | P11:EHV:EES::1ISES U2:1
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.42 | P11:HV:EES::PIRKEY 1:1
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.42 | P11:EHV:EES::WELSH3-1:1
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.39 | P11:HV:EES::TURKCOAL:1
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.61 | P12:HV:EES::5ISES%:1
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.61 | P12:EHV:EES::8ISES%:1
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.82 | P12:EHV:EES::7CALAWY 1:1
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17493 | 112.39 | P12:HV:EES::TURK 4%:1(1)
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.64 | 344011 7HUGHES 345 344012 7HPW-N 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.66 | 344884 7LABADIE1 345 344894 1LAB G1 20.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.66 | 344885 7LABADIE2 345 344895 1LAB G2 20.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.66 | 344886 7LABADIE3 345 344896 1LAB G3 20.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.66 | 344887 7LABADIE4 345 344897 1LAB G4 20.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.65 | 345667 7RUSH 1 345 345670 1RUSH G1 18.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.65 | 345668 7RUSH 2 345 345671 1RUSH G2 18.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.64 | 345755 4SIOUX 1 138 345756 1SIOUX 1 18.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.64 | 345764 4SIOUX 2 138 345765 1SIOUX 2 18.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.69 | P12:345:MDU::CENTER:COYOTE:1::::
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.69 | P13:345:MDU:COYOTE GSU LOSS:COYOTE::1::::
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.61 | P11:345:MEC:GDMEC CT1
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.61 | P11:345:MEC:GDMEC CT2
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.71 | P11:345:MEC:GDMEC ST
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.9 | P11:345:MEC-NPPD:COOPER 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.8 | P11:24:XEL:AUTO-SINGLE:SHERC31G:1
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.8 | P11:24:XEL:AUTO-SINGLE:SHERC32G:2
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.87 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.73 | P11:20:XEL:AUTO-SINGLE:PRIS31G:1
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.73 | P11:20:XEL:AUTO-SINGLE:PRIS32G:2
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.76 | P11:22:XEL:AUTO-SINGLE:MNTCE31G:1
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.73 | P11:20:XEL:AUTO-SINGLE:KING31G:1
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.77 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.77 | P11:22:GRE:AUTO-SINGLE:GRE-COAL42G:2
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.71 | P11:24:OTP:AUTO-SINGLE:BIGSTN1G:1
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.71 | P11:20:OTP:AUTO-SINGLE:CENTER2G:1
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.63 | P11:22:OTP:AUTO-SINGLE:CENTER1G:1
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.7 | P11:24:OTP:AUTO-SINGLE:COYOTE1G:1
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.63 | P11:24:DPC:AUTO-SINGLE:GENOA53G:3
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.61 | P12:115:XEL:AUTO-SINGLE:CHEMOLT7:LSPOWER7:1
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.65 | P12:115:XEL:AUTO-SINGLE:COLVILL7:CANONFLSG7:1
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.61 | P12:115:XEL:AUTO-SINGLE:FARIBALTP7:FARIBALTGEN:Z
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.7 | P12:230:OTP:AUTO-SINGLE:SQBUTTE4:YNG24:1
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.78 | P13:24-345:XEL:AUTO-SINGLE:SHERC31G:SHERCO3:1
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.78 | P13:24-345:XEL:AUTO-SINGLE:SHERC32G:SHERCO3:1
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.85 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.73 | P13:20-345:XEL:AUTO-SINGLE:PRIS31G:PRISLD3:1
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.73 | P13:20-345:XEL:AUTO-SINGLE:PRIS32G:PRISLD3:2
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.76 | P13:22-345:XEL:AUTO-SINGLE:MNTCE31G:MNTCELO3:1
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.72 | P13:20-345:XEL:AUTO-SINGLE:KING31G:ASKING3:1
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.76 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL41G:GRE-COALCR4:1
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.75 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL42G:GRE-COALCR4:1
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.7 | P13:230-24:OTP:AUTO-SINGLE:BIGSTON4:BIGSTN1G:1
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.7 | P13:20-230:OTP:AUTO-SINGLE:CENTER2G:YNG24:1
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.62 | P13:22-230:OTP:AUTO-SINGLE:CENTER1G:CENTER4:1
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.69 | P13:24-345:OTP:AUTO-SINGLE:COYOTE1G:COYOTE3:1
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.63 | P13:24-161:DPC:AUTO-SINGLE:GENOA53G:GENOA5:1
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.64 | P13:24-161:DPC:AUTO-SINGLE:JPM:ALMA5:1
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.7 | P11:115:XEL:RIV COMBINE CYCLE
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.62 | P12:115:XEL:BDS #2 5
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.62 | P11:115:XEL:HBR #6
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.62 | P11:115:XEL:HBR #7
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.73 | P11:115:XEL:HBR #6 7 8
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.73 | P23:345:XEL:8H14 PRI
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.73 | P23:345:XEL:8H17 PRI AS
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.85 | P23:345:XEL:8N28 SHC
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.78 | P23:345:XEL:8N22 SHC
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.78 | P23:345:XEL:8N17 SHC
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.77 | P23:345:XEL:8N8 MNN
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.72 | P23:345:XEL:8P1 KING
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.72 | P23:345:XEL:8P2 KING
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.62 | P23:115:XEL:5P147 IVH AS
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.61 | P11:18:ALTW:AUTO-SINGLE:EMERYST1:1
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.61 | P11:22:ALTW:AUTO-SINGLE:LANS54G:4
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.74 | P11:22:ALTW:AUTO-SINGLE:ARNOLD1G:1
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.77 | P11:24:ALTW:AUTO-SINGLE:OTTUMW1G:1
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.61 | P13:18-161:ALTW:AUTO-SINGLE:EMERYST1:EMERY5:1
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.61 | P13:22-161:ALTW:AUTO-SINGLE:LANS54G:LANSINGL15:1
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.73 | P13:22-161:ALTW:AUTO-SINGLE:ARNOLD1G:ARNOLD5:1
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.76 | P13:24-161:ALTW:AUTO-SINGLE:OTTUMW1G:OTTUMWA5:1
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.82 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.88 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.75 | P11:22:MEC:AUTO-SINGLE:NEAL3G:3
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.81 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.76 | P11:24:MEC:AUTO-SINGLE:LOUIS31G:1
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.81 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.84 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.74 | P13:345-22:MEC:AUTO-SINGLE:RAUN3:NEAL3G:1
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.8 | P13:345-24:MEC:AUTO-SINGLE:RAUN3:NEAL4G:1
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.74 | P13:345-24:MEC:AUTO-SINGLE:LOUISA3:LOUIS31G:1
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17488 | 112.78 | P11:230:WERE:JECU1_GEN::
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17488 | 112.78 | P11:345:WERE:JECU2_GEN::
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17488 | 112.78 | P11:345:WERE:JECU3_GEN::
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.95 | P11:345:WERE:WOLFU1_GEN::
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17493 | 112.63 | 511435 SNYDER-4 138 588779 TAP_G17-036 138 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17466 | 112.38 | 511446 CL-AFTP4 138 511458 ELKCTY-4 138 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17466 | 112.4 | 511446 CL-AFTP4 138 511463 HOB-JCT4 138 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.175 | 112.63 | 511453 DUNCAN-4 138 511552 DUNCHERTP4 138 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.175 | 112.62 | 511455 D.E.S.-4 138 511552 DUNCHERTP4 138 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.175 | 112.62 | 511455 D.E.S.-4 138 529344 OMDUNE-4 138 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.63 | 511456 O.K.U.-7 345 511565 OKLAUN HVDC7 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 111.6 | 511456 O.K.U.-7 345 588760 GEN-2017-033 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17807 | 114.54 | 511456 O.K.U.-7 345 763215 G18-092-TAP 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17821 | 115.11 | 511468 L.E.S.-7 345 762467 G18-015-TAP 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17715 | 114.48 | 511468 L.E.S.-7 345 763215 G18-092-TAP 345 2
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.29 | 511468 L.E.S.-7 345 763318 GEN-2018-115 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17493 | 112.66 | 511488 112GORE4 138 511510 LAIRGST4 138 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17504 | 112.7 | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17493 | 112.65 | 511500 CACHE4 138 511510 LAIRGST4 138 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17493 | 112.64 | 511500 CACHE4 138 588779 TAP_G17-036 138 2
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17659 | 112.8 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.75 | 511541 SWEETWT6 230 763340 GEN-2018-117 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17025 | 109.9 | 511553 CHISHOLM7 345 523961 POTTER_CO 7 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17025 | 109.9 | 511553 CHISHOLM7 345 523961 POTTER_CO 7 345 2
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.18278 | 116.03 | 515375 WWRDEHV7 345 515458 BORDER 7 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.18278 | 116.05 | 515458 BORDER 7 345 560022 CRAWFISH_DR 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17489 | 112.7 | 515618 BALKOW 7 345 3WXFMR BALKOW 7 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17489 | 112.7 | 515618 BALKOW 7 345 3WXFMR BALKOW 7 1_Dup1
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17485 | 112.95 | 515634 PALDR1W7 345 3WXFMR PALO2 _1 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.7 | 515677 BADGER 7 345 563170 G15082_1 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17485 | 112.61 | 520827 BINGERJ4 138 521017 ONEY 4 138 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17485 | 112.62 | 521017 ONEY 4 138 521089 WASHITA4 138 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.61 | 522800 MU-TULIA 3 115 525179 TULIA_TP 3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.75 | 522892 MU-BROWNFLD2 69.0 526761 BROWNFLD_TP2 69.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.64 | 523090 TEXAS_CNTY 3 115 589380 GEN-2017-100 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17487 | 112.78 | 523093 HITCHLAND 3 115 523174 GOODWELLWND3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.95 | 523097 HITCHLAND 7 345 523112 NOVUS1 7 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 113 | 523097 HITCHLAND 7 345 523215 FREWHELCOL17 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17264 | 111.48 | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.15856 | 109.07 | 523097 HITCHLAND 7 345 523961 POTTER_CO 7 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 113.05 | 523097 HITCHLAND 7 345 560252 G10-14 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.62 | 523099 TC-DRYTRLS 3 115 588480 A16-010_SUB 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.82 | 523112 NOVUS1 7 345 3WXFMR NOVUS XF2 2
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.63 | 523112 NOVUS1 7 345 3WXFMR XIANA2011198 _1 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.1749 | 112.61 | 523118 BUFF_DUNES 7 345 523853 FINNEY 7 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.63 | 523120 COLE 3 115 588860 GEN-2017-047 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.1749 | 112.64 | 523172 GWELL_COLL11 34.5 523174 GOODWELLWND3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.1749 | 112.65 | 523173 GWELL_COLL21 34.5 523174 GOODWELLWND3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17511 | 112.61 | 523267 PRINGLE 6 230 3WXFMR ENRCO13617-1 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17511 | 112.61 | 523267 PRINGLE 6 230 523979 HARRNG_EST 6 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17585 | 113.07 | 523771 GRAPEVINE 6 230 524044 NICHOLS 6 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.18497 | 113.75 | 523959 POTTER_CO 6 230 524267 BUSHLAND 6 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.18447 | 114.67 | 523959 POTTER_CO 6 230 525461 NEWHART 6 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.18369 | 118.42 | 523961 POTTER_CO 7 345 3WXFMR WAUK 90343-A 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17495 | 112.4 | 523978 HARRNG_MID 6 230 523979 HARRNG_EST 6 230 @1
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.39 | 524010 ROLLHILLS 6 230 3WXFMR WAUK WT01104 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17519 | 112.74 | 524267 BUSHLAND 6 230 3WXFMR WH 7001795 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.19279 | 114.31 | 524267 BUSHLAND 6 230 524623 DEAFSMITH 6 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17479 | 113.07 | 524296 SPNSPUR_WND7 345 524299 SPNSPUR_COL7 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17479 | 113.07 | 524299 SPNSPUR_COL7 345 3WXFMR SPNSPUR_COL7 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17927 | 113.32 | 524415 AMA_SOUTH 6 230 525213 SWISHER 6 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 113.2 | 524502 NORTON 3 115 524509 FE-TUCMCARI3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17714 | 113.01 | 524575 DS-#25+ 3 115 524597 PANDAHFD 3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17714 | 113.12 | 524575 DS-#25+ 3 115 524630 TIERABLANCA3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.7 | 524604 HEREFRD_SB 2 69.0 524608 HERFRD_STH 2 69.0 *1
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.19287 | 119.12 | 524623 DEAFSMITH 6 230 760498 G17-146-TAP 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 113.1 | 524721 DS-#15&#19+2 69.0 524745 CASTRO_CNTY2 69.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17494 | 112.61 | 524770 PLSNT_HILL 6 230 3WXFMR EFAE1100068A 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17893 | 117.92 | 524875 OASIS 6 230 524885 SN_JUAN_TAP6 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17544 | 113.69 | 524875 OASIS 6 230 524909 ROOSEVELT 6 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17884 | 118.38 | 524885 SN_JUAN_TAP6 230 527483 CHAVES_CNTY6 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17497 | 112.8 | 524909 ROOSEVELT 6 230 3WXFMR ABB LMM60042 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17876 | 118.36 | 524909 ROOSEVELT 6 230 525531 TOLK 6 230 2
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 113.33 | 524923 PORTALES 2 69.0 524929 RO-PORT_MTR2 69.0 @1
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 113 | 525001 W_MULESHOE 2 69.0 525008 MULESH_CTY 2 69.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 113 | 525008 MULESH_CTY 2 69.0 525027 BAILEYCO 2 69.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 113.28 | 525023 BC-BAIL_MTR2 69.0 525027 BAILEYCO 2 69.0 @1
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17607 | 113.27 | 525056 BC-EARTH 3 115 525480 PLANT_X 3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 113.09 | 525191 KRESS_INT 2 69.0 525203 SW-KRESS 2 69.0 Z1
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 113.17 | 525192 KRESS_INT 3 115 3WXFMR ENRCO 136155 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17903 | 113.6 | 525213 SWISHER 6 230 525461 NEWHART 6 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.73 | 525272 KISER 3 115 3WXFMR VON 13819/1 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 113.19 | 525326 COX 3 115 3WXFMR ELCO 13474-3 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 113.21 | 525414 LAMTON 3 115 3WXFMR ASEA MLL9204 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17632 | 113.03 | 525440 LC-S_OLTON+3 115 525446 RKYFORD_TP 3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17632 | 113.03 | 525446 RKYFORD_TP 3 115 525480 PLANT_X 3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.19686 | 116.34 | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.18 | 114.35 | 525481 PLANT_X 6 230 3WXFMR WH ALM20171 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.19039 | 118.3 | 525481 PLANT_X 6 230 526435 SUNDOWN 6 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.19287 | 117.38 | 525481 PLANT_X 6 230 760498 G17-146-TAP 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.16851 | 113.07 | 525481 PLANT_X 6 230 762174 G17-218TAP 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.16772 | 113.14 | 525481 PLANT_X 6 230 762174 G17-218TAP 230 2
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.18345 | 118.38 | 525531 TOLK 6 230 525586 NEEDMORE 6 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17572 | 114.61 | 525531 TOLK 6 230 525637 LAMB_CNTY 6 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.1986 | 118.52 | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.16543 | 113.33 | 525531 TOLK 6 230 762174 G17-218TAP 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.16478 | 113.39 | 525531 TOLK 6 230 762174 G17-218TAP 230 2
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.18345 | 118.36 | 525586 NEEDMORE 6 230 526935 YOAKUM 6 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 113.01 | 525599 LC-SANDHLL+2 69.0 525606 AMHERST 2 69.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 113.04 | 525606 AMHERST 2 69.0 525613 W_LITTLFLD 2 69.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 113.07 | 525613 W_LITTLFLD 2 69.0 525635 LAMB_CNTY 2 69.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 113.02 | 525635 LAMB_CNTY 2 69.0 525650 LC-LTTLFLD+2 69.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17572 | 114.61 | 525637 LAMB_CNTY 6 230 3WXFMR WH ALM20172 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.87 | 525828 TUCO_INT 3 115 3WXFMR DS F78800913 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17504 | 112.4 | 525830 TUCO_INT 6 230 3WXFMR ENRCO 136401 2
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.16731 | 114.37 | 525832 TUCO_INT 7 345 526936 YOAKUM_345 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 113.07 | 526086 SW_6786_N 2 69.0 526087 SW_6786_S 2 69.0 Z1
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 113.07 | 526086 SW_6786_N 2 69.0 526102 SP-HETTLER 2 69.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 113.14 | 526087 SW_6786_S 2 69.0 526284 PLANTERS 2 69.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.69 | 526160 CARLISLE 3 115 3WXFMR WH RLP38371 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 113.03 | 526195 QUINCY 3 115 526196 SP-MILWAUKEE 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.93 | 526268 LUBBCK_STH 3 115 3WXFMR NA 70454A 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 113.19 | 526284 PLANTERS 2 69.0 526297 LUBBCK_EST 2 69.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17495 | 112.63 | 526435 SUNDOWN 6 230 3WXFMR UPDATE LATER _12 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17703 | 115 | 526435 SUNDOWN 6 230 526460 AMOCO_SS 6 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17491 | 112.65 | 526525 WOLFFORTH 6 230 3WXFMR UPDATE LATER _13 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 113.07 | 526735 TERRY_CNTY 2 69.0 526747 LG-BROWNFLD2 69.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 113 | 526747 LG-BROWNFLD2 69.0 526754 BROWNFIELD 2 69.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17506 | 114.41 | 526935 YOAKUM 6 230 527028 INK_BASIN 6 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.16868 | 121.79 | 526936 YOAKUM_345 345 527896 HOBBS_INT 7 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17504 | 113.76 | 527028 INK_BASIN 6 230 527894 HOBBS_INT 6 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 113 | 527130 DENVER_N 3 115 527286 HIGGEAST 3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.61 | 527149 MUSTANG 6 230 3WXFMR ENRCO 136161 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17506 | 110.49 | 527149 MUSTANG 6 230 527151 GS-MUSTANG 6 230 @1
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.86 | 527202 SEAGRAVES 3 115 3WXFMR ABB MLL92408 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.76 | 527212 DIAMONDBACK3 115 3WXFMR HOW 36773714 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.68 | 527261 SULPHUR 2 69.0 527271 LG-FOSTER +2 69.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.98 | 527286 HIGGEAST 3 115 527363 HIGG 3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17493 | 112.82 | 527322 GAINES 3 115 527325 OXY_WSEM_TP3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17493 | 112.74 | 527325 OXY_WSEM_TP3 115 527362 JOHNSON_DRW3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.73 | 527340 DOSS 3 115 3WXFMR ELCO 13566/1 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.71 | 527345 LEGACY 2 69.0 527350 XTO_ROBRTSN2 69.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.71 | 527346 LEGACY 3 115 3WXFMR VROL 13735-1 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.69 | 527350 XTO_ROBRTSN2 69.0 527355 BOARDMAN 2 69.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.63 | 527355 BOARDMAN 2 69.0 527365 FLANNAGAN 2 69.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.61 | 527360 MAPCO 3 115 527362 JOHNSON_DRW3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.65 | 527362 JOHNSON_DRW3 115 528775 LE-ERF 3 115 @1
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17494 | 112.39 | 527455 RSWL_SLRCOL3 115 527482 CHAVES_CNTY3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17494 | 112.41 | 527470 CHVS_SLRCOL3 115 527464 CHVS_SOLAR11 34.5 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17494 | 112.34 | 527470 CHVS_SLRCOL3 115 527482 CHAVES_CNTY3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17661 | 112.88 | 527483 CHAVES_CNTY6 230 527799 EDDY_NORTH 6 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.62 | 527508 PRICE 3 115 527509 PRICE_TAP 3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.62 | 527529 RIACBRSH_TP3 115 527533 SW4J795_E 3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.62 | 527533 SW4J795_E 3 115 527564 ROSWLL_INT 3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.62 | 527563 ROSWLL_INT 2 69.0 527575 SW_4702 2 69.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17508 | 112.67 | 527564 ROSWLL_INT 3 115 527597 TWEEDY 3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.62 | 527575 SW_4702 2 69.0 527589 CV-ORCHARD 2 69.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17487 | 112.78 | 527653 MILO_WIND 1 34.5 527655 RSVLT_CC_E 7 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17479 | 112.66 | 527654 RSVLT_CC_W 7 345 527655 RSVLT_CC_E 7 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17479 | 112.95 | 527654 RSVLT_CC_W 7 345 527666 RSVLT_COL1 7 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17475 | 112.86 | 527655 RSVLT_CC_E 7 345 527656 CROSSROADS 7 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17479 | 112.95 | 527666 RSVLT_COL1 7 345 3WXFMR RSVLT_COL1 7 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.36 | 527736 NAVAJO_5TP 3 115 527739 NAVAJO_4 3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.35 | 527864 CUNNINHAM 3 115 528348 BUCKEYE_TP 3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.63 | 527864 CUNNINHAM 3 115 528568 MONUMNT_TP 3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17479 | 112.91 | 527865 CUNNIGHM_N 6 230 527867 CUNNIGHM_S 6 230 *1
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17488 | 112.64 | 527865 CUNNIGHM_N 6 230 527963 POTASH_JCT 6 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17491 | 112.4 | 527867 CUNNIGHM_S 6 230 3WXFMR WH 7000266 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17487 | 112.86 | 527867 CUNNIGHM_S 6 230 527882 CUNINGHAM2 1 20.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17488 | 112.79 | 527894 HOBBS_INT 6 230 527903 HOBBS_PLT3 1 18.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17491 | 112.36 | 527965 KIOWA 7 345 528027 RDRUNNER 7 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.36 | 528015 PHANTOM 7 345 528027 RDRUNNER 7 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.41 | 528024 RR_SVC_HV 3 115 528021 RDRUNNR_SVC1 15.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.68 | 528025 RDRUNNER 3 115 587990 GEN-2016-121 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.42 | 528185 N_LOVING 7 345 3WXFMR HYO1063400-1 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.41 | 528185 N_LOVING 7 345 528223 CHINA_DRAW 7 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.36 | 528222 CHINA_DRAW 3 115 528225 CD_SVC_HV 3 115 Z1
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.34 | 528333 LE-WEST_SUB3 115 528334 LE-NRTH_INT3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.42 | 528341 LE-SANANDRS3 115 528627 LE-TXACO_TP3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.38 | 528348 BUCKEYE_TP 3 115 528627 LE-TXACO_TP3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17489 | 112.62 | 528394 QUAHADA 3 115 528396 XTO_BIGEDDY3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.33 | 528463 SANGER_SW 3 115 528575 OXYPERMIAN 3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.33 | 528463 SANGER_SW 3 115 762442 G18-004-TAP 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.63 | 528568 MONUMNT_TP 3 115 528581 BYRD_TP 3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.38 | 528574 OXY_NHU_RCF3 115 528575 OXYPERMIAN 3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.69 | 528617 LE-WAITS 2 69.0 528325 LE-WAITS 3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.61 | 528617 LE-WAITS 2 69.0 528714 LE-FORT_SW 2 69.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.42 | 528622 LE-SANANDRS2 69.0 528341 LE-SANANDRS3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.97 | 528626 LE-PLNSINT 2 69.0 526928 PLAINS_INT 3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.97 | 528626 LE-PLNSINT 2 69.0 528709 LE-PLNSGOAB2 69.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.63 | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.69 | 528669 LE-STKLDRTP2 69.0 528740 LE-PLANS_SW2 69.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.85 | 528709 LE-PLNSGOAB2 69.0 528740 LE-PLANS_SW2 69.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.63 | 528709 LE-PLNSGOAB2 69.0 528747 LE-ALLRED 2 69.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.61 | 528714 LE-FORT_SW 2 69.0 528718 LE-NEWTEX 2 69.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.69 | 528735 LE-PLAINSUB2 69.0 528740 LE-PLANS_SW2 69.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17481 | 112.41 | 530583 POSTROCK7 345 588654 G17-021-TAP 345 2
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.41 | 531213 SANTAFE3 115 531408 PIERCVL3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17461 | 112.33 | 531451 MINGO 7 345 531465 SETAB 7 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.1749 | 112.62 | 531501 BUCKNER7 345 531502 CIMRRN 7 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.1749 | 112.62 | 531502 CIMRRN 7 345 531503 CIMRRN 1 34.5 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17478 | 112.32 | 531510 HARBNGR3 115 3WXFMR HARBGR345 _1 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.1749 | 112.64 | 532663 LEC U5 24.0 532854 LEC U5 6 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.1749 | 112.64 | 532853 LAWHILL6 230 532854 LEC U5 6 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17491 | 112.69 | 542951 HAW G5 1 22.0 543665 HAWTHN5 161 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.1749 | 112.74 | 542955 LAC G1 1 22.0 542981 LACYGNE7 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.1749 | 112.72 | 542956 LAC G2 1 24.0 542981 LACYGNE7 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17489 | 112.76 | 542957 IAT G1 1 24.0 542982 IATAN 7 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.1749 | 112.82 | 542962 IAT G2 1 24.5 542982 IATAN 7 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17491 | 112.61 | 542966 WGARDNR5 161 543105 BULLCRK5 161 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17746 | 112.16 | 560022 CRAWFISH_DR 345 762216 G17-151TAP 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17714 | 113.18 | 560022 CRAWFISH_DR 345 762467 G18-015-TAP 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 108.98 | 560022 CRAWFISH_DR 345 763087 GEN-2018-073 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17829 | 113.55 | 560022 CRAWFISH_DR 345 763215 G18-092-TAP 345 2
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 113.05 | 560252 G10-14 345 560253 G10-14-1 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.78 | 560253 G10-14-1 115 560254 G10-14-SUB1 34.5 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.78 | 560253 G10-14-1 115 560255 G10-14-SUB2 34.5 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.63 | 560581 G06-44-2 34.5 523111 NOVUS1 3 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.68 | 560582 G06-44-3 34.5 560577 G06-44 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.66 | 560583 G06-44-4 34.5 560577 G06-44 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.32 | 560757 ASGI13_02_1 69.0 560758 ASGI13_02_2 34.5 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.32 | 560757 ASGI13_02_1 69.0 562731 WHEATLAND 69.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.33 | 560763 ASGI13_03_1 115 560761 ASGI13_03_2 34.5 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.76 | 562015 FIREWHEEL1 34.5 523215 FREWHELCOL17 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.76 | 562016 FIREWHEEL2 34.5 523215 FREWHELCOL17 345 2
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.31 | 562323 AGI1202&1305 115 562324 AGI1202&1305 34.5 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.32 | 562727 LESBIA 115 562728 SANJONTAP 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.32 | 562728 SANJONTAP 115 562729 CAPROCKTAP1 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.32 | 562730 CAPROCKTAP2 69.0 562729 CAPROCKTAP1 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.32 | 562730 CAPROCKTAP2 69.0 562731 WHEATLAND 69.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.72 | 563171 G15082_2 34.5 563170 G15082_1 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.4 | P11:13.8:AEPW:COM1-1
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.41 | P11:13.8:AEPW:COM2-1
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.41 | P11:13.8:AEPW:COM3-1
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.42 | P11:18:AEPW:WELSH1-1
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.42 | P11:18:AEPW:WELSH3-1
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.42 | P11:24:AEPW:PIRKEY 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.39 | P11:24:AEPW:SWS3-1
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.39 | P11:24:AEPW:TURKCOAL
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17504 | 112.7 | P12:138:AEPW-OMPA:DUNCAN-4:OMDUNCN4
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17493 | 112.66 | P12:138:AEPW:112GORE4:SNYDER-4
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17493 | 112.66 | 5841_Dup1
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17501 | 111.96 | 584560 GEN-2015-014 115 584561 G15-014XFMR1 34.5 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.175 | 112.65 | P12:138:AEPW:SANTAFE:DUNCAN-4
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.68 | 587991 G16-121XFMR1 34.5 587990 GEN-2016-121 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.62 | 588480 A16-010_SUB 115 3WXFMR A16-010_SUB 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17504 | 112.7 | P12:138:AEPW:DUNCAN-4:L.E.S.-4
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.06 | 588761 G17-033XFMR1 34.5 588760 GEN-2017-033 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.06 | 588765 G17-033XFMR2 34.5 588760 GEN-2017-033 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.63 | 588861 G17-047XFMR1 34.5 588860 GEN-2017-047 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17454 | 112.2 | P12:138:AEPW:ELKCTY-4:CLINTJC4
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.64 | 589381 G17-100XFMR1 34.5 589380 GEN-2017-100 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17466 | 112.39 | P12:138:AEPW:HOB-JCT4:ELKCTY-4
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.64 | P12:138:AEPW:SHERID4:112GORE4
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.1749 | 112.61 | P12:230:AEPW:SWEETWT6:BUFFCK6
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17489 | 112.66 | P12:230:AEPW:SWEETWT6:ROARK6
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17734 | 114.5 | P12:345:AEPW:L.E.S7:TERRYRD7
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17734 | 114.49 | P12:345:AEPW:L.E.S7:TERRYRD7
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17734 | 114.47 | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17799 | 114.61 | P12:345:AEPW-OKGE:L.E.S.-7:GRACMNT7
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17799 | 114.58 | P12:345:AEPW-OKGE:L.E.S.-7:GRACMNT7
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17488 | 112.4 | P12:345:AEPW-OKGE:PITTSB-7:SEMINOL7
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17807 | 115.66 | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.66 | P22:345:AMMO::LABADIE:1
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.66 | P22:345:AMMO::LABADIE:2
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.66 | P22:345:AMMO::LABADIE:3
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.66 | P22:345:AMMO::LABADIE:4
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.65 | P22:345:AMMO::RUSHISLAND:1
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.64 | P22:345:AMMO::RUSHISLAND:2
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17493 | 112.41 | P13:138-13.8:AEPW:COMANC-4_#2
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17317 | 111.28 | P13:138-230:AEPW:ELKCTY-4
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17494 | 112.4 | P13:138-24:AEPW:S.W.S.-4
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17493 | 112.39 | P13:138-24:AEPW:TURK 4
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17501 | 112.63 | P13:138-345:AEPW:L.E.S.-4_#1
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.1751 | 112.75 | P13:138-345:AEPW:L.E.S.-4_#2
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17493 | 112.67 | P23:500:EES-EAI:KEO:B4941
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17493 | 112.66 | P23:500:EES-EAI:KEO:B4921
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.61 | P11:26:EES-EAI:INDEP2:1:D401
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.61 | P11:26:EES-EAI:INDEP2:1
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.61 | P13:500:EES-EAI:INDEP2:MT2
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17493 | 112.65 | P23:500:EES-EAI:INDEP2:B6126
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.64 | P23:500:EES-EAI:PD:INDEP2:LN:FK479
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.1749 | 112.61 | P13:230-34.5:AEPW:BUFFCK6
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17489 | 112.67 | P13:230-34.5:AEPW:ROARK6
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.41 | P13:69-13.8:AEPW:COMANC-2
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.66 | P11:024:DPC:ALMA2:6
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.62 | P11:18:ITCM:EMERYGT1:1
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.63 | P11:18:ITCM:EMERYGT2:1
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.63 | P11:161:ITCM:MGS CT1:1C
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.63 | P11:161:ITCM:MGS CT2:2C
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.1749 | 112.64 | 652537 WHITE 3 345 659286 DEERCREK-BE3 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.1749 | 112.64 | 659286 DEERCREK-BE3 345 3WXFMR DEERCRK KU1A 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.63 | 672601 BD 4 230 672306 BD 6G 18.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.63 | 672610 POPLAR 4 230 672310 POPLAR 1G 18.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.63 | 672610 POPLAR 4 230 672311 POPLAR 2G 18.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.62 | 672621 SHAND 4 230 672321 SHAND 1G 18.0 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.61 | 672649 CODETTE 4 230 672650 NIPAWIN 4 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.62 | 672696 BRADA 4 230 672699 NBEC 4 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.69 | P23:345:MDU::COYOTE::5707-5712-5715::::
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.84 | P23:345:MEC:CBEC 905
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.81 | P23:345:MEC:CBEC 908
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.64 | P23:345:MEC:GDMEC 908
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.74 | P23:345:MEC:RAUN 0180
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.8 | P23:345:MEC:RAUN 0210
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.75 | P23:345:MEC:LOUISA 954
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.75 | P23:345:MEC:LOUISA 964
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.61 | P21:115:XEL:AUTO-SINGLE:CHEMOLT7:LSPOWER7:1
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.65 | P21:115:XEL:AUTO-SINGLE:COLVILL7:CANONFLSG7:1
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.61 | P21:115:XEL:AUTO-SINGLE:FARIBALTP7:FARIBALTGEN:Z
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.7 | P21:230:OTP:AUTO-SINGLE:SQBUTTE4:YNG24:1
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.69 | P23:345:OTP:CENTER 3:3215(1)
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.69 | P23:345:OTP:CENTER 3:3225(1)
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.63 | P12:230:UMZW:# 687 #: FT IN SD. FT-BG1 LINE FAULT
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.63 | P12:230:UMZW:# 3617 #: FT IN SD. FT-BG2 LINE FAULT
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 111.33 | 760494 GEN-2017-146 230 760498 G17-146-TAP 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 111.32 | 760495 G17-146-XFM1 34.5 760494 GEN-2017-146 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.05 | 761356 G17-239-XFMR 34.5 761355 GEN-2017-239 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.05 | 761359 G17-239-XFMR 34.5 761355 GEN-2017-239 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.23 | 761797 G17-187XFM1 34.5 761796 GEN-2017-187 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.23 | 761800 G17-187XFM2 34.5 761796 GEN-2017-187 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 107.16 | 762132 GEN-2017-158 230 763252 G18-099-XFM1 34.5 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 107.16 | 762132 GEN-2017-158 230 763255 G18-099-XFM2 34.5 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 107.74 | 762133 G17-158XFM1 34.5 762132 GEN-2017-158 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 107.74 | 762136 G17-158XFM2 34.5 762132 GEN-2017-158 230 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 109.9 | 762216 G17-151TAP 345 762217 GEN-2017-151 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17746 | 113.55 | 762216 G17-151TAP 345 762467 G18-015-TAP 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 111.85 | 762218 G17-151XFM1 34.5 762217 GEN-2017-151 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 111.85 | 762221 G17-151XFM2 34.5 762217 GEN-2017-151 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 111.85 | 762224 G17-151XFM3 34.5 762217 GEN-2017-151 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 111.85 | 762227 G17-151XFM4 34.5 762217 GEN-2017-151 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.36 | 762438 GEN-2018-004 115 762442 G18-004-TAP 115 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 110.89 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 111.7 | 762461 G18-015-XFM1 34.5 762460 GEN-2018-015 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 111.7 | 762464 G18-015-XFM2 34.5 762460 GEN-2018-015 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17631 | 113.07 | 762467 G18-015-TAP 345 763215 G18-092-TAP 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 110.18 | 763087 GEN-2018-073 345 763088 G18-073-XFM1 34.5 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 111.33 | 763087 GEN-2018-073 345 763091 G18-073-XFM2 34.5 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 107.16 | 763120 GEN-2018-081 230 763121 G18-081-XFM1 34.5 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 109.44 | 763186 GEN-2018-089 230 763187 G18-089-XFM1 34.5 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 110.21 | 763208 GEN-2018-092 345 763215 G18-092-TAP 345 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 111.37 | 763208 GEN-2018-092 345 763220 G18-092-XFM1 34.5 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 111.37 | 763208 GEN-2018-092 345 763223 G18-092-XFM2 34.5 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 108.87 | 763241 GEN-2018-097 230 763242 G18-097-XFM1 34.5 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 109.78 | 763241 GEN-2018-097 230 763296 G18-111-XFM1 34.5 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 109.14 | 763241 GEN-2018-097 230 763307 G18-112-XFM1 34.5 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 109.14 | 763241 GEN-2018-097 230 763310 G18-112-XFM2 34.5 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 108.87 | 763241 GEN-2018-097 230 763395 G18-124-XFM1 34.5 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 108.87 | 763241 GEN-2018-097 230 763398 G18-124-XFM2 34.5 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.29 | 763318 GEN-2018-115 345 763319 G18-115-XFM1 34.5 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.75 | 763340 GEN-2018-117 230 763341 G18-117-XFM1 34.5 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 108.51 | 763483 GEN-2019-003 230 763484 G19-003-XFM1 34.5 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 111.19 | 763483 GEN-2019-003 230 763605 G19-021-XFM1 34.5 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 111.9 | 763516 GEN-2019-011 345 763517 G19-011-XFM1 34.5 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.26 | 763879 GEN-2019-056 115 763880 G19-056XFM1 34.5 1
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17442 | 112.68 | P42:345:OKGE:SB_BVTY7305
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17484 | 112.43 | P23:345:WERE:BUFF_345-534::
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17484 | 112.43 | P23:345:WERE:BUFF_345-543::
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17488 | 112.78 | P23:345:WERE:JEC_345-15::
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17487 | 112.75 | P23:345:WERE:JEC_345-16::
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17488 | 112.78 | P23:345:WERE:JEC_345-19::
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17488 | 112.78 | P23:345:WERE:JEC_345-20::
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.95 | P23:345:WERE:WOLF_345-50::
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.95 | P23:345:WERE:WOLF_345-60::
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17493 | 112.43 | P42:345:AEPW:WELSH CB 10620 NBTB+FAULT
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17807 | 114.21 | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17833 | 114.99 | P42:345:AEPW:LAWTON EASTSIDE CB 3413A NBTB+FAULT
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17868 | 115.4 | P42:345:AEPW:LAWTON EASTSIDE CB 3425A NBTB+FAULT
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17821 | 115.86 | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17506 | 112.31 | P42:345:AEPW:PITTSBURG CB 3441A NBTB+FAULT
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17488 | 112.4 | P42:345:AEPW:PITTSBURG CB 3445A NBTB+FAULT
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17734 | 114.49 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17734 | 114.49 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17734 | 114.47 | P42:345:AEPW:TERRYRD_CB_3421A_NBTB
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.1749 | 112.75 | P23:345:KCPL:LACYGNE_R2-5::LACYGU2-LACYGNE-STILWELL
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17493 | 112.43 | P23:345:AEPW:WELSH CB 10620 NBTB
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17807 | 114.54 | P23:345:AEPW:OKLAUNION CB 3401A NBTB
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17833 | 114.99 | P23:345:AEPW:LAWTON EASTSIDE CB 3413A NBTB
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17868 | 115.4 | P23:345:AEPW:LAWTON EASTSIDE CB 3425A NBTB
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17821 | 115.86 | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17506 | 112.31 | P23:345:AEPW:PITTSBURG CB 3441A NBTB
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17488 | 112.4 | P23:345:AEPW:PITTSBURG CB 3445A NBTB
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17734 | 114.49 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17734 | 114.49 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17734 | 114.47 | P23:345:AEPW:TERRYRD_CB_3421A_NBTB
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17523 | 112.62 | P12:138:AEPW:S.W.S.-4:L.E.S.-4
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17492 | 112.65 | P11:115:SUNC:GARDENCITY_S2:97:531459(2)
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17753 | 114.72 | P23:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.18011 | 117.32 | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17753 | 114.72 | P42:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB+FAULT
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.18011 | 117.32 | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.16716 | 109.51 | P42:345:OKGE:SB_BVTY7315_PRE19S
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17461 | 112.33 | P23:345:SUNC:MO_BRK182
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17461 | 112.33 | P23:345:SUNC:MO_BRK382
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17489 | 112.42 | P21:345:UMZW:# 725 #: GI IN NE. GI-SWEET LINE FAULT
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17659 | 112.8 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17493 | 112.41 | P12:138-13.8:AEPW:COMANC-4_#1
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17317 | 111.26 | P12:230:AEPW:ELKCITY6:CHISHOLM6
Thermal | 05ALL | 1 | 23SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997716 TOLK 6 230 2 |  | 560 | 0.17649 | 113.54 | P12:230:AEPW:SWEETWT6:CHISHOLM6
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997713 ABBXNL844501 230 1 |  | 553 | 0.08273 | 157.44 | 525531 TOLK 6 230 3WXFMR TOLK 6 2
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05075 | 116.18 | P23:345:KCPL-WERE:237LACYGNE_R1-6::LACYGU1-LACYGNE-NEOSHO
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05072 | 116.06 | P11:230:WERE:LECU5_GEN::
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05073 | 116.08 | P11:161:GMO:DOGWOOD_COMBINED_CYCLE_UNIT_OUTAGE_1_1
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05074 | 116.02 | P11:20:KACY:NEARMAN N1::N1 OUT OF SERVICE:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05072 | 116.02 | P12:69:KACY:NMGEN-NMISOBUS::NEARMAN N1-NM ISOBUS OPEN:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05072 | 116.02 | P13:20-161:KACY:NEARMAN5-NMISOBUS:NAMEPLATE:NEARMAN N1 GSU:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05072 | 116.02 | P21:20:KACY:546702NMGENN1-546703NMISOBUSC1::::
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05074 | 116.23 | P11:115:SPS:HOBBS1&3:145MW::::
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.0508 | 114.72 | P11:115:SPS:MUSTANG1&3:153MW::::
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05019 | 118.23 | P12:230:SPS:K37::1_TOLK_LAMB:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05089 | 116.06 | P12:230:SPS:K43::1_PRNGLE_HARR_E:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05077 | 115.81 | P12:230:SPS:K44::1_EPLNT_HARRW:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05102 | 116.22 | P12:115:SPS:T04::1_TRBLNC_CASTRO:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05089 | 116.02 | P12:115:SPS:T06::1_SPRMN_PRNGLE:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05074 | 116.5 | P12:115:SPS:T21::1_GRSSLND_GRAHAM:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05074 | 116.05 | P12:115:SPS:T24B::1_RSWLL_BRSHRF:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05073 | 116.05 | P12:115:SPS:T26::1_CHAVES_RSWLCTY:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.0505 | 116.45 | P12:115:SPS:T28A::1_LAMTON_PLANTX:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05041 | 116.02 | P12:115:SPS:T29::1_LAMTON_HALECTR:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05078 | 116.06 | P12:115:SPS:T35::1_TERRY_YOAKUM:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05074 | 116.78 | P12:115:SPS:T45::1_NORRIS_OASIS:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05078 | 115.82 | P12:115:SPS:T57::1_MUSTG_SEGRVS:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05122 | 116.03 | P12:115:SPS:T58::1_HERFRD_CARGIL:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05122 | 116.57 | P12:115:SPS:T59::1_CARGIL_CURRY:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05074 | 116.02 | P12:115:SPS:T64::1_RNDALL_PULLMN:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05196 | 116.38 | P12:115:SPS:T67::1_HAPPY_KRESS:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05066 | 115.77 | P12:115:SPS:T68::1_TUCO_FLOYD:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05072 | 115.81 | P12:115:SPS:T69::1_LUBBE_CROSBY:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05074 | 116.02 | P12:115:SPS:T70::1_COLTR_S_GORG:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05078 | 116.63 | P12:115:SPS:T71::1_CRLSLE_YUMA:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05055 | 116.1 | P12:115:SPS:T81::1_COX_FLOYD:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05074 | 116.26 | P12:115:SPS:T83::1_SP-FKFD_ALLEN:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05084 | 116.44 | P12:115:SPS:T89::1_DC_N_HIGG:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05074 | 116.07 | P12:115:SPS:T91::1_HIGG_RUSSELL:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05078 | 116.02 | P12:115:SPS:V01::1_MOOREW_RVRVIEW:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05092 | 116.07 | P12:115:SPS:V04::1_EPLANT_RNDALL:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05066 | 116.06 | P12:115:SPS:V07::1_COX_HALECTR:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05029 | 116.23 | P12:115:SPS:V09::1_HALECTR_PLANTX:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05074 | 116.21 | P12:115:SPS:V12::1_PLANTX_BAILEY:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05074 | 116.03 | P12:115:SPS:V15::1_TUCO_INDANA:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05102 | 116.16 | P12:115:SPS:V24::1_WOLFTH_TERRY:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05064 | 116.07 | P12:115:SPS:V26::1_RSWLL_EDDY_N:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05074 | 116.4 | P12:115:SPS:V33::1_LUBBS_LYNN:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.0511 | 117.14 | P12:115:SPS:V37::1_CASTRO_PLANTX:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05074 | 116.05 | P12:115:SPS:V44::1_COLTR_OWENS:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05074 | 116.16 | P12:115:SPS:V46::1_ALLEN_WHEELCK:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05076 | 116.5 | P12:115:SPS:V49::1_YOAKUM_SHLCO2:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05053 | 116.68 | P12:115:SPS:V55::1_SUNDWN_TERRY:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05077 | 116.59 | P12:115:SPS:V56::1_COCHRAN_SUNDWN:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05074 | 116.09 | P12:115:SPS:V62::1_CRLSLE_INDANA:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05077 | 116.07 | P12:115:SPS:V78::2_CURRY_RSVLT:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05082 | 116.19 | P12:115:SPS:V81::1_LE-WAIT_LE-LVN:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05074 | 116.06 | P12:115:SPS:V95::1_DC_N_SHLCO2:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05074 | 116.02 | P12:115:SPS:W11::1_DC_S_SMINLE:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05075 | 116.03 | P12:115:SPS:W12::1_SMINLE_DOSS:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05076 | 116.1 | P12:115:SPS:W14::1_SMINLE_GAINES:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05075 | 116.03 | P12:115:SPS:W26::1_CUNGHM_OILCNTR:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05074 | 116.61 | P12:115:SPS:W32::1_PRMTR_FE-CLSIN:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05082 | 116.26 | P12:115:SPS:W35::1_GAINES_JNSDRW:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05153 | 116.59 | P12:115:SPS:W40::1_WCANYON_TRBLNC:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05059 | 116.11 | P12:115:SPS:W52::1_NEWHART_KRESS:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05074 | 116.67 | P12:115:SPS:W58::1_NORTON_LOPEZ:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05074 | 116.25 | P12:115:SPS:W59::1_LOPEZ_CMPBLL:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05074 | 116.55 | P12:115:SPS:W62::1_PLSTHL_CURRY:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05086 | 116.07 | P12:115:SPS:W63::1_PLSTHL_CURRY:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05074 | 116.36 | P12:115:SPS:W64::1_PLSTHL_FE-CLV:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05074 | 116.57 | P12:115:SPS:W65::1_PLSTHL_CURRY:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05074 | 116.23 | P12:115:SPS:W66::1_PORTA_GREYHUND:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05077 | 116.02 | P12:115:SPS:W76::1_QUAHA_PCA:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05153 | 116.1 | P12:115:SPS:W77::1_RNDAL_WCANYON:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05074 | 116.07 | P12:115:SPS:W99::1_CAPITAN_CHAVES:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05075 | 116.05 | P12:115:SPS:U03::1_CARDNL_NEF:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05078 | 116.53 | P12:115:SPS:U14::1_DC_STH_INKBSN:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05082 | 116.47 | P12:115:SPS:V15::1_INKBSN_LE-WAT:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.0508 | 116.15 | P12:115:SPS:U16::1_BSHLND_OUTPST:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.0508 | 116.16 | P12:115:SPS:U17::1_COLTR_OUTPST:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.0507 | 116.26 | P12:115:SPS:U19::1_DEAN_PLAINS:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.0508 | 116.07 | P12:115:SPS:U23::1_COLTR_HILSDE:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.0604 | 124.36 | P42:345:SPS:YOAKUM:J18####:SLG1:EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.0604 | 124.36 | P43:345:SPS:YOAKUM:TF#####:SLG:EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.0604 | 124.36 | P42:345:SPS:YOAKUM:J17####:SLG:EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.0604 | 124.36 | P42:345:SPS:YOAKUM:J18####:SLG2:EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05073 | 116.06 | P11:18:HAST:::EGYCTR2G WEC2_LOSS OF WEC 2 GEN_:HV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05073 | 116.06 | P13:18-115:HAST:::EGYCNTR7 XFMR G2WEC 2 GSU_:HV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05073 | 116.08 | P11:161:GMO:DOGWOOD-COMBINED-CYCLE-UNIT-OUTA:::HV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05075 | 116.18 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05072 | 116.18 | P23:345:KCPL:LACYGNE-R2-5:::EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.0507 | 116.23 | P11:230:WERE:JECU1-GEN:::HV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05072 | 116.06 | P11:230:WERE:LECU5-GEN:::HV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.0507 | 116.23 | P11:345:WERE:JECU2-GEN:::EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.0507 | 116.22 | P11:345:WERE:JECU3-GEN:::EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05074 | 116.4 | P11:345:WERE:WOLFU1-GEN:::EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05062 | 115.77 | P12:345:PWT:BUFF-THIS-345-1:::EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05062 | 115.77 | P12:345:PWT:BUFF-THIS-345-2:::EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.0506 | 115.75 | P23:345:WERE:BUFF-345-534:::EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.0506 | 115.75 | P23:345:WERE:BUFF-345-543:::EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.0507 | 116.23 | P23:345:WERE:JEC-345-15:::EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05068 | 116.18 | P23:345:WERE:JEC-345-16:::EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.0507 | 116.22 | P23:345:WERE:JEC-345-19:::EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.0507 | 116.22 | P23:345:WERE:JEC-345-20:::EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05073 | 116.39 | P23:345:WERE:WOLF-345-50:::EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05074 | 116.39 | P23:345:WERE:WOLF-345-60:::EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05074 | 116.34 | P11:022:NPPD:COOPER1G:1:983:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05069 | 116.33 | P11:023:NPPD:GENTLM1G:1:757:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05069 | 116.35 | P11:024:NPPD:GENTLM2G:2:757:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05073 | 116.01 | P11:161:OPPD:N OMA 5G:LT::HV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05073 | 116.01 | P11:161:OPPD:N OMA 5G:::HV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.0507 | 116.2 | P13:345:OPPD:NEBCTY1G:::EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05069 | 116.22 | P13:345:OPPD:NEBCTY2G:::EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05073 | 116.01 | P13:161:OPPD:N OMA 5G:::HV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05074 | 116.22 | P22:345:OPPD:S3458 NEBCTY1G:LT::EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.0507 | 116.2 | P22:345:OPPD:S3458 NEBCTY1G:::EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05074 | 116.25 | P22:345:OPPD:S3458 NEBCTY2G:LT::EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05069 | 116.22 | P22:345:OPPD:S3458 NEBCTY2G:::EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05074 | 116.22 | P23:345:OPPD:S3458 NEBCTY1G:LT::EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.0507 | 116.2 | P23:345:OPPD:S3458 NEBCTY1G:::EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05074 | 116.25 | P23:345:OPPD:S3458 NEBCTY2G:LT::EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05069 | 116.22 | P23:345:OPPD:S3458 NEBCTY2G:::EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05074 | 115.8 | P12:115:SUNC:PLYMELL-PIERCEVILLE:::HV::
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05072 | 116.06 | P11:018:UMZB:# 5 #:: DCS IN SD. DEERCREEK_MV::
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05073 | 116.03 | P11:022:UMZB:# 15 #:: LO IN ND. LELAND OLDS 1_MV::
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05072 | 116.07 | P11:020:UMZB:# 16 #:: LO IN ND. LELAND OLDS 2_MV::
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05071 | 116.14 | P11:023:UMZB:# 31 #:: AVS IN ND. ANTELOPE VALLEY 1_MV::
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05071 | 116.14 | P11:023:UMZB:# 32 #:: AVS IN ND. ANTELOPE VALLEY 2_MV::
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05068 | 116.33 | P11:024:UMZB:# 33 #:: LRS IN WY. LARAMIE RIVER STATION 1_MV::
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05074 | 116.06 | P12:230:UMZW:# 687 #:: FT IN SD. FT-BG1 BRANCH FAULT:HV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05074 | 116.06 | P12:230:UMZW:# 3617 #:: FT IN SD. FT-BG2 BRANCH FAULT:HV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05074 | 116.06 | P12:230:UMZW:# 4038 #:: BG-FT IN SD. FAULT FOR TRANSMISSION CIRCUIT (BG-FT).:HV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05074 | 116.06 | P12:230:UMZW:# 4039 #:: BG-FT IN SD. FAULT FOR TRANSMISSION CIRCUIT (BG-FT).:HV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05074 | 116.03 | P13:230:UMZW:# 5135 #:: OA IN SD. FAULT ON TRANSFORMER (2).:HV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05074 | 116.03 | P13:230:UMZW:# 5136 #:: OA IN SD. FAULT ON TRANSFORMER (3).:HV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05073 | 115.82 | P23:345:UMZW:# 2423 #:: GI IN NE. GI 1596 BKR FAULT:EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05073 | 115.82 | P23:345:UMZW:# 2426 #:: GI IN NE. GI 1592 BKR FAULT:EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05073 | 115.82 | P23:345:UMZW:# 2432 #:: GI IN NE. GI 1092 BKR FAULT:EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05073 | 115.82 | P23:345:UMZW:# 2440 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1092 STUCK BKR:EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05073 | 115.82 | P23:345:UMZW:# 2444 #:: GI IN NE. GI-SWEET BRANCH FAULT & GI 1596 STUCK BKR:EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05073 | 115.82 | P23:345:UMZW:# 2446 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1196 STUCK BKR:EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05073 | 115.82 | P42:345:UMZW:# 2413 #:: FT2 IN SD. FT2-LO2 BRANCH FAULT & FT2 2992 STUCK BKR:EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05073 | 115.82 | P42:345:UMZW:# 2415 #:: FT2 IN SD. FT2-GI BRANCH FAULT & FT2 3392 STUCK BKR:EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05077 | 115.74 | P11:138:WFEC:HUGO1:465MW :::
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05072 | 116.02 | P11:138:WFEC:MORLND2:132MW:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05072 | 116.03 | P11:138:WFEC:MORLND3:149MW :::
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05084 | 116.06 | P12:138:WFEC:ANADRKO_CLVLND::::
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05077 | 116.06 | P12:345:OKGE-AEPW:BKRBKR12::::
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05121 | 116.18 | P12:345:OKGE:BKRBKR21::::
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05144 | 116.26 | P12:345:OKGE:BKRBKR24::::
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05387 | 117.75 | P12:345:OKGE-AEPW:BKRBKR25::::
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05054 | 115.72 | P12:345:OKGE:BKRBKR336::::
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05054 | 115.72 | P12:345:OKGE:BKRBKR336_2::::
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05652 | 118.25 | P12:345:OKGE-AEPW:BKRBKR366::::
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05652 | 118.23 | P12:345:OKGE-AEPW:BKRBKR366::::
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05322 | 117.15 | P12:345:OKGE:BKRBKR367::::
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05059 | 115.72 | P12:345:OKGE:BKRBKR4193::::
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05058 | 115.72 | P12:345:OKGE:BKRBKR4194::::
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05074 | 116.02 | P12:345:OKGE:BKRBKR4195::::
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05052 | 115.76 | P12:345:OKGE-SPS:BKRBKR4201::::
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05052 | 115.76 | P12:345:OKGE-SPS:BKRBKR4202::::
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05085 | 116.03 | P12:345:OKGE:BKRBKR421::::
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05053 | 115.6 | P12:345:OKGE:BKRBKR443NEW::::
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05053 | 115.6 | P12:345:OKGE:BKRBKR443NEW2::::
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05059 | 115.79 | P12:345:OKGE-ITC:BKRBKR502::::
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05059 | 115.79 | P12:345:OKGE-ITC:BKRBKR503::::
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05062 | 115.83 | P12:345:OKGE-ITC:BKRBKR502_1::::
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05062 | 115.83 | P12:345:OKGE-ITC:BKRBKR503_1::::
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05067 | 116.33 | P12:345:OKGE:BKRBKR604::::
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05066 | 116.37 | P12:345:OKGE:BKRBKR604_2::::
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05075 | 115.82 | P11:345:OKGE:BKRBKR_GSU07::::
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05076 | 115.81 | P11:345:OKGE:BKRBKR_GSU08::::
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05076 | 115.8 | P11:138:OKGE:BKRBKR_GSU21::::
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05073 | 115.83 | P12:138:OKGE:BKRBKR85_MOS1::::
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05051 | 116.13 | P42:345:OKGE:SB_ARIA7381::::
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.0656 | 120.17 | P42:345:OKGE:SB_BVTY7387::::
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05087 | 116.02 | P41:345:OKGE:SB_REUD7381::::
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05085 | 116.03 | P41:345:OKGE:SB_REUD7383::::
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05086 | 116.06 | P41:345:OKGE:SB_REUD7385::::
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.0509 | 116.06 | P42:345:OKGE:SB_REUD7389::::
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05072 | 116.05 | P11:115:SUNC:GARDENCITY_S2:103:531459(2):HV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05072 | 116.07 | P11:115:SUNC:FORTDDODGE_4:157:539670(4):HV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05074 | 116.04 | P11:345:599:CIMARRON1WIND:200:531603(1):EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05074 | 116.47 | P13:115:SUNC:HOLCOMB_GSU:::HV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05072 | 116.05 | P13:115:SUNC:S2_GSU:::HV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05072 | 116.07 | P13:115:SUNC:FORTDODGE_GSU:::HV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05071 | 116.04 | P23:345:SUNC:BU_BRK682:::EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05074 | 116.14 | 300003 1THLG3 24.0 301503 7THOMHLGSU3 345 3
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05074 | 116.01 | 300007 1NM G2 22.0 301537 7NEWMADGSU2 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05074 | 116.01 | 300046 7NEWMAD 345 301537 7NEWMADGSU2 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05074 | 116.14 | 300049 7THOMHL 345 301503 7THOMHLGSU3 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05074 | 116.08 | P11:20:AMMO:1LAB�� G1:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05074 | 116.08 | P11:20:AMMO:1LAB�� G2:2
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05074 | 116.27 | P11:345:AMMO::CALLAWAY:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05074 | 116.08 | P11:345:AMMO::LABADIE:3
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05074 | 116.08 | P11:345:AMMO::LABADIE:4
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05074 | 116.07 | P11:345:AMMO::RUSHISLAND:U1
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05074 | 116.07 | P11:345:AMMO::RUSHISLAND:U2
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05074 | 116.06 | P11:138:AMMO::SIOUX:2
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05074 | 115.83 | P11:24:CLEC::G1DOLHIL:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05074 | 116.06 | P12:765:AEP:AEP ROCKP-AEP JEFF 765
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05074 | 115.78 | P11:HV:EES::PIRKEY 1:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05074 | 115.79 | P11:EHV:EES::WELSH3-1:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05074 | 115.74 | P11:HV:EES::TURKCOAL:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05074 | 116.25 | P12:EHV:EES::7CALAWY 1:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05075 | 116.02 | 338056 CHALKBLUFFPV 500 338162 8W.MEMPHIS% 500 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05075 | 115.75 | P12:HV:EES::TURK 4%:1(1)
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05076 | 115.79 | P12:EHV:EES::WELSH 7:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05076 | 115.79 | P12:EHV:EES::WELSH 7:1(1)
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05075 | 115.79 | P12:HV:EES::PIRKEY 4:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05077 | 116.06 | P12:EHV:EES::CLARKSV7!:MUSKOGE7!:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05074 | 116.06 | 344011 7HUGHES 345 344012 7HPW-N 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05074 | 116.08 | 344884 7LABADIE1 345 344894 1LAB G1 20.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05074 | 116.08 | 344885 7LABADIE2 345 344895 1LAB G2 20.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05074 | 116.08 | 344886 7LABADIE3 345 344896 1LAB G3 20.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05074 | 116.08 | 344887 7LABADIE4 345 344897 1LAB G4 20.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05074 | 116.07 | 345667 7RUSH 1 345 345670 1RUSH G1 18.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05074 | 116.06 | 345668 7RUSH 2 345 345671 1RUSH G2 18.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05074 | 116.05 | 345755 4SIOUX 1 138 345756 1SIOUX 1 18.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05074 | 116.05 | 345764 4SIOUX 2 138 345765 1SIOUX 2 18.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05074 | 116.12 | P12:345:MDU::CENTER:COYOTE:1::::
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05074 | 116.12 | P13:345:MDU:COYOTE GSU LOSS:COYOTE::1::::
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05074 | 116.03 | P11:345:MEC:GDMEC CT1
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05074 | 116.03 | P11:345:MEC:GDMEC CT2
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05074 | 116.14 | P11:345:MEC:GDMEC ST
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05074 | 116.35 | P11:345:MEC-NPPD:COOPER 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05074 | 116.24 | P11:24:XEL:AUTO-SINGLE:SHERC31G:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05074 | 116.24 | P11:24:XEL:AUTO-SINGLE:SHERC32G:2
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05074 | 116.33 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05074 | 116.16 | P11:20:XEL:AUTO-SINGLE:PRIS31G:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05074 | 116.16 | P11:20:XEL:AUTO-SINGLE:PRIS32G:2
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05074 | 116.2 | P11:22:XEL:AUTO-SINGLE:MNTCE31G:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05074 | 116.16 | P11:20:XEL:AUTO-SINGLE:KING31G:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05074 | 116.02 | P11:13:XEL:AUTO-SINGLE:HBRS73G:9
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05074 | 116.02 | P11:18:XEL:AUTO-SINGLE:BLKD76G:6
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05074 | 116.22 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05074 | 116.22 | P11:22:GRE:AUTO-SINGLE:GRE-COAL42G:2
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05074 | 116.14 | P11:24:OTP:AUTO-SINGLE:BIGSTN1G:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05074 | 116.15 | P11:20:OTP:AUTO-SINGLE:CENTER2G:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05074 | 116.05 | P11:22:OTP:AUTO-SINGLE:CENTER1G:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05074 | 116.13 | P11:24:OTP:AUTO-SINGLE:COYOTE1G:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05074 | 116.05 | P11:24:DPC:AUTO-SINGLE:GENOA53G:3
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05074 | 116.03 | P12:115:XEL:AUTO-SINGLE:CHEMOLT7:LSPOWER7:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05074 | 116.07 | P12:115:XEL:AUTO-SINGLE:COLVILL7:CANONFLSG7:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05074 | 116.03 | P12:115:XEL:AUTO-SINGLE:FARIBALTP7:FARIBALTGEN:Z
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05074 | 116.13 | P12:230:OTP:AUTO-SINGLE:SQBUTTE4:YNG24:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05074 | 116.22 | P13:24-345:XEL:AUTO-SINGLE:SHERC31G:SHERCO3:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05074 | 116.22 | P13:24-345:XEL:AUTO-SINGLE:SHERC32G:SHERCO3:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05074 | 116.3 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05074 | 116.16 | P13:20-345:XEL:AUTO-SINGLE:PRIS31G:PRISLD3:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05074 | 116.16 | P13:20-345:XEL:AUTO-SINGLE:PRIS32G:PRISLD3:2
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05074 | 116.2 | P13:22-345:XEL:AUTO-SINGLE:MNTCE31G:MNTCELO3:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05074 | 116.15 | P13:20-345:XEL:AUTO-SINGLE:KING31G:ASKING3:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05074 | 116.02 | P13:13-115:XEL:AUTO-SINGLE:HBRS73G:HIBRDGE7:9
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05074 | 116.2 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL41G:GRE-COALCR4:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05074 | 116.2 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL42G:GRE-COALCR4:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05074 | 116.13 | P13:230-24:OTP:AUTO-SINGLE:BIGSTON4:BIGSTN1G:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05074 | 116.13 | P13:20-230:OTP:AUTO-SINGLE:CENTER2G:YNG24:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05074 | 116.04 | P13:22-230:OTP:AUTO-SINGLE:CENTER1G:CENTER4:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05074 | 116.12 | P13:24-345:OTP:AUTO-SINGLE:COYOTE1G:COYOTE3:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05074 | 116.05 | P13:24-161:DPC:AUTO-SINGLE:GENOA53G:GENOA5:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05074 | 116.07 | P13:24-161:DPC:AUTO-SINGLE:JPM:ALMA5:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05075 | 116.02 | 38203 J1819 POI 500 337957 8KEO% 500 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05075 | 116.02 | 38203 J1819 POI 500 338056 CHALKBLUFFPV 500 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05074 | 116.13 | P11:115:XEL:RIV COMBINE CYCLE
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05074 | 116.04 | P12:115:XEL:BDS #2 5
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05074 | 116.04 | P11:115:XEL:HBR #6
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05074 | 116.04 | P11:115:XEL:HBR #7
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05074 | 116.16 | P11:115:XEL:HBR #6 7 8
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05074 | 116.16 | P23:345:XEL:8H14 PRI
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05074 | 116.16 | P23:345:XEL:8H17 PRI AS
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05074 | 116.3 | P23:345:XEL:8N28 SHC
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05074 | 116.22 | P23:345:XEL:8N22 SHC
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05074 | 116.22 | P23:345:XEL:8N17 SHC
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05074 | 116.21 | P23:345:XEL:8N8 MNN
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05074 | 116.15 | P23:345:XEL:8P1 KING
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05074 | 116.15 | P23:345:XEL:8P2 KING
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05074 | 116.04 | P23:115:XEL:5P147 IVH AS
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05074 | 116.03 | P11:18:ALTW:AUTO-SINGLE:EMERYST1:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05074 | 116.03 | P11:22:ALTW:AUTO-SINGLE:LANS54G:4
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05074 | 116.17 | P11:22:ALTW:AUTO-SINGLE:ARNOLD1G:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05074 | 116.2 | P11:24:ALTW:AUTO-SINGLE:OTTUMW1G:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05074 | 116.03 | P13:18-161:ALTW:AUTO-SINGLE:EMERYST1:EMERY5:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05074 | 116.03 | P13:22-161:ALTW:AUTO-SINGLE:LANS54G:LANSINGL15:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05074 | 116.16 | P13:22-161:ALTW:AUTO-SINGLE:ARNOLD1G:ARNOLD5:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05074 | 116.19 | P13:24-161:ALTW:AUTO-SINGLE:OTTUMW1G:OTTUMWA5:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05074 | 116.27 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05074 | 116.34 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05074 | 116.19 | P11:22:MEC:AUTO-SINGLE:NEAL3G:3
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05074 | 116.26 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05074 | 116.19 | P11:24:MEC:AUTO-SINGLE:LOUIS31G:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05074 | 116.25 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05074 | 116.3 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05074 | 116.17 | P13:345-22:MEC:AUTO-SINGLE:RAUN3:NEAL3G:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05074 | 116.24 | P13:345-24:MEC:AUTO-SINGLE:RAUN3:NEAL4G:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05074 | 116.18 | P13:345-24:MEC:AUTO-SINGLE:LOUISA3:LOUIS31G:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.0507 | 116.23 | P11:230:WERE:JECU1_GEN::
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.0507 | 116.23 | P11:345:WERE:JECU2_GEN::
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.0507 | 116.22 | P11:345:WERE:JECU3_GEN::
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05074 | 116.4 | P11:345:WERE:WOLFU1_GEN::
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05084 | 116.03 | 511435 SNYDER-4 138 588779 TAP_G17-036 138 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05085 | 116.03 | 511453 DUNCAN-4 138 511552 DUNCHERTP4 138 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05085 | 116.03 | 511455 D.E.S.-4 138 511552 DUNCHERTP4 138 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05085 | 116.02 | 511455 D.E.S.-4 138 529344 OMDUNE-4 138 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05074 | 114.98 | 511456 O.K.U.-7 345 588760 GEN-2017-033 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05542 | 117.74 | 511456 O.K.U.-7 345 763215 G18-092-TAP 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05563 | 118.31 | 511468 L.E.S.-7 345 762467 G18-015-TAP 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05405 | 117.72 | 511468 L.E.S.-7 345 763215 G18-092-TAP 345 2
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05074 | 115.66 | 511468 L.E.S.-7 345 763318 GEN-2018-115 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05084 | 116.05 | 511488 112GORE4 138 511510 LAIRGST4 138 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05091 | 116.11 | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05084 | 116.04 | 511500 CACHE4 138 511510 LAIRGST4 138 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05084 | 116.03 | 511500 CACHE4 138 588779 TAP_G17-036 138 2
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05133 | 116.06 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05121 | 115.5 | 511553 CHISHOLM7 345 755000 WWDBORDT 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05046 | 116.14 | 511557 CHISHOLM6 230 3WXFMR CHISHOLM6 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05089 | 116.02 | 514801 MINCO 7 345 555234 NSUB345 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05 | 115.63 | 515375 WWRDEHV7 345 755000 WWDBORDT 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.0656 | 120.2 | 515458 BORDER 7 345 560022 CRAWFISH_DR 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.0656 | 120.15 | 515458 BORDER 7 345 755000 WWDBORDT 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05085 | 116.02 | 515543 RENFROW7 345 763421 G18-128-TAP 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05071 | 116.12 | 515618 BALKOW 7 345 3WXFMR BALKOW 7 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05071 | 116.13 | 515618 BALKOW 7 345 3WXFMR BALKOW 7 1_Dup1
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05081 | 116.04 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05066 | 116.39 | 515634 PALDR1W7 345 3WXFMR PALO2 _1 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05074 | 116.13 | 515677 BADGER 7 345 563170 G15082_1 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05073 | 116.01 | 521017 ONEY 4 138 521089 WASHITA4 138 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05074 | 116.02 | 522800 MU-TULIA 3 115 525179 TULIA_TP 3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05074 | 116.16 | 522892 MU-BROWNFLD2 69.0 526761 BROWNFLD_TP2 69.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05074 | 116.03 | 523090 TEXAS_CNTY 3 115 589380 GEN-2017-100 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.0507 | 116.16 | 523093 HITCHLAND 3 115 523174 GOODWELLWND3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05074 | 116.34 | 523097 HITCHLAND 7 345 523112 NOVUS1 7 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05074 | 116.4 | 523097 HITCHLAND 7 345 523215 FREWHELCOL17 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05074 | 116.45 | 523097 HITCHLAND 7 345 560252 G10-14 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05074 | 116.01 | 523099 TC-DRYTRLS 3 115 588480 A16-010_SUB 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05074 | 116.23 | 523112 NOVUS1 7 345 3WXFMR NOVUS XF2 2
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05074 | 116.04 | 523112 NOVUS1 7 345 3WXFMR XIANA2011198 _1 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05072 | 116.02 | 523118 BUFF_DUNES 7 345 523853 FINNEY 7 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05074 | 116.02 | 523120 COLE 3 115 588860 GEN-2017-047 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05072 | 116.04 | 523172 GWELL_COLL11 34.5 523174 GOODWELLWND3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05072 | 116.04 | 523173 GWELL_COLL21 34.5 523174 GOODWELLWND3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.0508 | 116.01 | 523221 XIT_INTG 6 230 3WXFMR SIEM_T126401 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05089 | 116.07 | 523267 PRINGLE 6 230 3WXFMR ENRCO13617-1 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05089 | 116.06 | 523267 PRINGLE 6 230 523979 HARRNG_EST 6 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05118 | 116.2 | 523309 MOORE_CNTY 6 230 523323 MCDWL_CREEK6 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05097 | 116.12 | 523323 MCDWL_CREEK6 230 523959 POTTER_CO 6 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05071 | 116.45 | 523959 POTTER_CO 6 230 524010 ROLLHILLS 6 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05459 | 117.19 | 523959 POTTER_CO 6 230 524267 BUSHLAND 6 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05728 | 118.35 | 523959 POTTER_CO 6 230 525461 NEWHART 6 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05689 | 121.11 | 523961 POTTER_CO 7 345 3WXFMR WAUK 90343-A 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05092 | 115.74 | 523978 HARRNG_MID 6 230 523979 HARRNG_EST 6 230 @1
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.0508 | 116.16 | 524267 BUSHLAND 6 230 3WXFMR WH 7001795 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05743 | 117.94 | 524267 BUSHLAND 6 230 524623 DEAFSMITH 6 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05062 | 116.44 | 524296 SPNSPUR_WND7 345 524299 SPNSPUR_COL7 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05062 | 116.44 | 524299 SPNSPUR_COL7 345 3WXFMR SPNSPUR_COL7 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05621 | 117.09 | 524415 AMA_SOUTH 6 230 525213 SWISHER 6 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05074 | 116.67 | 524502 NORTON 3 115 524509 FE-TUCMCARI3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05153 | 116.45 | 524575 DS-#25+ 3 115 524597 PANDAHFD 3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05153 | 116.55 | 524575 DS-#25+ 3 115 524630 TIERABLANCA3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05074 | 116.11 | 524604 HEREFRD_SB 2 69.0 524608 HERFRD_STH 2 69.0 *1
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05563 | 122.73 | 524623 DEAFSMITH 6 230 760498 G17-146-TAP 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05074 | 116.52 | 524721 DS-#15&#19+2 69.0 524745 CASTRO_CNTY2 69.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05075 | 116.03 | 524770 PLSNT_HILL 6 230 3WXFMR EFAE1100068A 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05065 | 117.16 | 524875 OASIS 6 230 524909 ROOSEVELT 6 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05077 | 116.22 | 524909 ROOSEVELT 6 230 3WXFMR ABB LMM60042 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05076 | 122.19 | 524909 ROOSEVELT 6 230 525531 TOLK 6 230 2
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05074 | 116.77 | 524923 PORTALES 2 69.0 524929 RO-PORT_MTR2 69.0 @1
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05074 | 116.42 | 524923 PORTALES 2 69.0 524941 PORTALES#1 2 69.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05074 | 116.66 | 525023 BC-BAIL_MTR2 69.0 525027 BAILEYCO 2 69.0 @1
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.0511 | 116.55 | 525056 BC-EARTH 3 115 525480 PLANT_X 3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05074 | 116.51 | 525191 KRESS_INT 2 69.0 525203 SW-KRESS 2 69.0 Z1
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05074 | 116.6 | 525192 KRESS_INT 3 115 3WXFMR ENRCO 136155 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05074 | 116.15 | 525272 KISER 3 115 3WXFMR VON 13819/1 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05074 | 116.61 | 525326 COX 3 115 3WXFMR ELCO 13474-3 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05074 | 116.61 | 525414 LAMTON 3 115 3WXFMR ASEA MLL9204 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05143 | 119.68 | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05037 | 118.1 | 525481 PLANT_X 6 230 3WXFMR WH ALM20171 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05563 | 121.02 | 525481 PLANT_X 6 230 760498 G17-146-TAP 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05068 | 116.49 | 525481 PLANT_X 6 230 762174 G17-218TAP 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05067 | 116.56 | 525481 PLANT_X 6 230 762174 G17-218TAP 230 2
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05019 | 118.23 | 525531 TOLK 6 230 525637 LAMB_CNTY 6 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05065 | 116.76 | 525531 TOLK 6 230 762174 G17-218TAP 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05065 | 116.82 | 525531 TOLK 6 230 762174 G17-218TAP 230 2
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.08273 | 155.48 | 525549 TOLK 7 345 3WXFMR ABBXNL844501 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05074 | 116.41 | 525599 LC-SANDHLL+2 69.0 525606 AMHERST 2 69.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05074 | 116.45 | 525606 AMHERST 2 69.0 525613 W_LITTLFLD 2 69.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05074 | 116.46 | 525613 W_LITTLFLD 2 69.0 525635 LAMB_CNTY 2 69.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05074 | 116.42 | 525635 LAMB_CNTY 2 69.0 525650 LC-LTTLFLD+2 69.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05019 | 118.23 | 525637 LAMB_CNTY 6 230 3WXFMR WH ALM20172 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05074 | 116.41 | 525779 FLOYD_CNTY 2 69.0 525790 FLOYDADA_TP2 69.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05074 | 116.29 | 525828 TUCO_INT 3 115 3WXFMR DS F78800913 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05805 | 118.38 | 525832 TUCO_INT 7 345 526936 YOAKUM_345 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05074 | 116.49 | 526086 SW_6786_N 2 69.0 526087 SW_6786_S 2 69.0 Z1
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05074 | 116.49 | 526086 SW_6786_N 2 69.0 526102 SP-HETTLER 2 69.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05074 | 116.56 | 526087 SW_6786_S 2 69.0 526284 PLANTERS 2 69.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05074 | 116.1 | 526160 CARLISLE 3 115 3WXFMR WH RLP38371 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05074 | 116.44 | 526195 QUINCY 3 115 526196 SP-MILWAUKEE 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05074 | 116.34 | 526268 LUBBCK_STH 3 115 3WXFMR NA 70454A 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05074 | 116.6 | 526284 PLANTERS 2 69.0 526297 LUBBCK_EST 2 69.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05077 | 116.47 | 526424 PACIFIC 3 115 526434 SUNDOWN 3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05078 | 116.06 | 526435 SUNDOWN 6 230 3WXFMR UPDATE LATER _12 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05104 | 118.87 | 526435 SUNDOWN 6 230 526460 AMOCO_SS 6 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05104 | 116.5 | 526460 AMOCO_SS 6 230 526935 YOAKUM 6 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05076 | 116.08 | 526525 WOLFFORTH 6 230 3WXFMR UPDATE LATER _13 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05074 | 116.48 | 526735 TERRY_CNTY 2 69.0 526747 LG-BROWNFLD2 69.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05137 | 118.02 | 526935 YOAKUM 6 230 527028 INK_BASIN 6 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05964 | 126.57 | 526936 YOAKUM_345 345 527896 HOBBS_INT 7 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05147 | 117.39 | 527028 INK_BASIN 6 230 527894 HOBBS_INT 6 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05084 | 116.43 | 527130 DENVER_N 3 115 527286 HIGGEAST 3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05074 | 116.02 | 527149 MUSTANG 6 230 3WXFMR ENRCO 136161 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05089 | 114.01 | 527149 MUSTANG 6 230 527151 GS-MUSTANG 6 230 @1
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05074 | 116.29 | 527202 SEAGRAVES 3 115 3WXFMR ABB MLL92408 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05074 | 116.17 | 527212 DIAMONDBACK3 115 3WXFMR HOW 36773714 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05084 | 116.41 | 527286 HIGGEAST 3 115 527363 HIGG 3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05082 | 116.16 | 527325 OXY_WSEM_TP3 115 527362 JOHNSON_DRW3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05074 | 116.15 | 527340 DOSS 3 115 3WXFMR ELCO 13566/1 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05074 | 116.14 | 527345 LEGACY 2 69.0 527350 XTO_ROBRTSN2 69.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05074 | 116.14 | 527346 LEGACY 3 115 3WXFMR VROL 13735-1 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05074 | 116.12 | 527350 XTO_ROBRTSN2 69.0 527355 BOARDMAN 2 69.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05074 | 116.05 | 527355 BOARDMAN 2 69.0 527365 FLANNAGAN 2 69.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05074 | 116.02 | 527360 MAPCO 3 115 527362 JOHNSON_DRW3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05074 | 116.08 | 527362 JOHNSON_DRW3 115 528775 LE-ERF 3 115 @1
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05074 | 116.01 | 527370 TENNECO_TAP2 69.0 527371 TENNECO 2 69.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05074 | 116.05 | 527508 PRICE 3 115 527509 PRICE_TAP 3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05074 | 116.02 | 527514 CV-PINE 2 69.0 527563 ROSWLL_INT 2 69.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05074 | 116.05 | 527529 RIACBRSH_TP3 115 527533 SW4J795_E 3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05074 | 116.02 | 527529 RIACBRSH_TP3 115 527536 BRASHER 3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05074 | 116.05 | 527533 SW4J795_E 3 115 527564 ROSWLL_INT 3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05074 | 116.06 | 527563 ROSWLL_INT 2 69.0 527575 SW_4702 2 69.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05064 | 116.1 | 527564 ROSWLL_INT 3 115 527597 TWEEDY 3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05074 | 116.06 | 527575 SW_4702 2 69.0 527589 CV-ORCHARD 2 69.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05074 | 116.02 | 527589 CV-ORCHARD 2 69.0 527619 DEXTER_TP 2 69.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05069 | 116.18 | 527653 MILO_WIND 1 34.5 527655 RSVLT_CC_E 7 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05062 | 116.1 | 527654 RSVLT_CC_W 7 345 527655 RSVLT_CC_E 7 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05062 | 116.36 | 527654 RSVLT_CC_W 7 345 527666 RSVLT_COL1 7 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05057 | 116.3 | 527655 RSVLT_CC_E 7 345 527656 CROSSROADS 7 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05062 | 116.36 | 527666 RSVLT_COL1 7 345 3WXFMR RSVLT_COL1 7 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05074 | 116.15 | 527790 EDDY_SVC 1 8.50 527799 EDDY_NORTH 6 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05075 | 116.05 | 527864 CUNNINHAM 3 115 528568 MONUMNT_TP 3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05086 | 116.16 | 527865 CUNNIGHM_N 6 230 527867 CUNNIGHM_S 6 230 *1
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05074 | 116.14 | 527865 CUNNIGHM_N 6 230 527883 CUNINGHAM3 1 13.8 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05078 | 116.08 | 527865 CUNNIGHM_N 6 230 527963 POTASH_JCT 6 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05078 | 116.02 | 527867 CUNNIGHM_S 6 230 527894 HOBBS_INT 6 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05071 | 116.35 | 527894 HOBBS_INT 6 230 527903 HOBBS_PLT3 1 18.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05078 | 116.23 | 527896 HOBBS_INT 7 345 3WXFMR HICO 68759-1 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05075 | 115.8 | 527965 KIOWA 7 345 528027 RDRUNNER 7 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05074 | 115.81 | 528015 PHANTOM 7 345 528027 RDRUNNER 7 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05074 | 116.11 | 528024 RR_SVC_HV 3 115 528021 RDRUNNR_SVC1 15.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05074 | 116.25 | 528024 RR_SVC_HV 3 115 528025 RDRUNNER 3 115 Z1
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05074 | 115.81 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05074 | 116.08 | 528025 RDRUNNER 3 115 587990 GEN-2016-121 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05074 | 116.14 | 528222 CHINA_DRAW 3 115 528225 CD_SVC_HV 3 115 Z1
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05074 | 115.82 | 528341 LE-SANANDRS3 115 528627 LE-TXACO_TP3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05077 | 116.06 | 528394 QUAHADA 3 115 528396 XTO_BIGEDDY3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05075 | 116.01 | 528552 OIL_CENTER 3 115 528554 COOPER_RNCH3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05075 | 116.02 | 528554 COOPER_RNCH3 115 528581 BYRD_TP 3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05075 | 116.05 | 528568 MONUMNT_TP 3 115 528581 BYRD_TP 3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05075 | 116.04 | 528596 CARDINAL 3 115 528605 TARGA 3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05075 | 116.06 | 528603 NA_ENRICH 3 115 528605 TARGA 3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05074 | 116.11 | 528617 LE-WAITS 2 69.0 528325 LE-WAITS 3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05074 | 116.03 | 528617 LE-WAITS 2 69.0 528714 LE-FORT_SW 2 69.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05075 | 116.05 | 528618 LE-LOVINTON2 69.0 528334 LE-NRTH_INT3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05074 | 116.42 | 528626 LE-PLNSINT 2 69.0 526928 PLAINS_INT 3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05074 | 116.42 | 528626 LE-PLNSINT 2 69.0 528709 LE-PLNSGOAB2 69.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05074 | 116.05 | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05074 | 116.11 | 528669 LE-STKLDRTP2 69.0 528740 LE-PLANS_SW2 69.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05074 | 116.3 | 528709 LE-PLNSGOAB2 69.0 528740 LE-PLANS_SW2 69.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05074 | 116.05 | 528709 LE-PLNSGOAB2 69.0 528747 LE-ALLRED 2 69.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05074 | 116.03 | 528714 LE-FORT_SW 2 69.0 528718 LE-NEWTEX 2 69.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05074 | 116.11 | 528735 LE-PLAINSUB2 69.0 528740 LE-PLANS_SW2 69.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05074 | 116.03 | 528775 LE-ERF 3 115 528779 LE-TALLCOTN3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05063 | 115.79 | 530583 POSTROCK7 345 560082 G16-050-TAP 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05074 | 115.81 | 531213 SANTAFE3 115 531408 PIERCVL3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05071 | 116.04 | 531501 BUCKNER7 345 531502 CIMRRN 7 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05071 | 116.04 | 531502 CIMRRN 7 345 531503 CIMRRN 1 34.5 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05063 | 115.75 | 531510 HARBNGR3 115 3WXFMR HARBGR345 _1 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05072 | 116.06 | 532663 LEC U5 24.0 532854 LEC U5 6 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05081 | 116.04 | 532794 ROSEHIL7 345 560053 G15052_T 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05085 | 116.03 | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05072 | 116.06 | 532853 LAWHILL6 230 532854 LEC U5 6 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05072 | 116.01 | 539117 SPRVILL-EHVB 230 539695 SPEARVL6 230 Z1
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05072 | 116.02 | 539803 IRONWOOD7 345 3WXFMR IRONWOOD MPT 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05073 | 116.13 | 542951 HAW G5 1 22.0 543665 HAWTHN5 161 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05072 | 116.17 | 542955 LAC G1 1 22.0 542981 LACYGNE7 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05072 | 116.15 | 542956 LAC G2 1 24.0 542981 LACYGNE7 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05071 | 116.2 | 542957 IAT G1 1 24.0 542982 IATAN 7 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05071 | 116.27 | 542962 IAT G2 1 24.5 542982 IATAN 7 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05073 | 116.03 | 542966 WGARDNR5 161 543105 BULLCRK5 161 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05452 | 115.57 | 560022 CRAWFISH_DR 345 762216 G17-151TAP 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05403 | 116.52 | 560022 CRAWFISH_DR 345 762467 G18-015-TAP 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05574 | 116.84 | 560022 CRAWFISH_DR 345 763215 G18-092-TAP 345 2
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05063 | 115.8 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05074 | 116.45 | 560252 G10-14 345 560253 G10-14-1 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05074 | 116.18 | 560253 G10-14-1 115 560254 G10-14-SUB1 34.5 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05074 | 116.19 | 560253 G10-14-1 115 560255 G10-14-SUB2 34.5 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05074 | 116.04 | 560581 G06-44-2 34.5 523111 NOVUS1 3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05074 | 116.08 | 560582 G06-44-3 34.5 560577 G06-44 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05074 | 116.07 | 560583 G06-44-4 34.5 560577 G06-44 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05074 | 115.72 | 560757 ASGI13_02_1 69.0 560758 ASGI13_02_2 34.5 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05074 | 115.72 | 560757 ASGI13_02_1 69.0 562731 WHEATLAND 69.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05074 | 115.73 | 560763 ASGI13_03_1 115 560761 ASGI13_03_2 34.5 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05074 | 116.16 | 562015 FIREWHEEL1 34.5 523215 FREWHELCOL17 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05074 | 116.16 | 562016 FIREWHEEL2 34.5 523215 FREWHELCOL17 345 2
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05074 | 115.71 | 562323 AGI1202&1305 115 562324 AGI1202&1305 34.5 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05074 | 115.73 | 562727 LESBIA 115 562728 SANJONTAP 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05074 | 115.72 | 562728 SANJONTAP 115 562729 CAPROCKTAP1 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05074 | 115.72 | 562730 CAPROCKTAP2 69.0 562729 CAPROCKTAP1 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05074 | 115.72 | 562730 CAPROCKTAP2 69.0 562731 WHEATLAND 69.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05074 | 116.15 | 563171 G15082_2 34.5 563170 G15082_1 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05074 | 115.78 | P11:13.8:AEPW:COM1-1
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05074 | 115.79 | P11:13.8:AEPW:COM2-1
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05074 | 115.79 | P11:13.8:AEPW:COM3-1
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05074 | 115.78 | P11:18:AEPW:WELSH1-1
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05074 | 115.79 | P11:18:AEPW:WELSH3-1
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05074 | 115.78 | P11:24:AEPW:PIRKEY 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05074 | 115.68 | P11:24:AEPW:SWS3-1
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05074 | 115.74 | P11:24:AEPW:TURKCOAL
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05091 | 116.11 | P12:138:AEPW-OMPA:DUNCAN-4:OMDUNCN4
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05074 | 116.02 | P12:138:AEPW:112GORE4:L.E.S.-4
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05084 | 116.05 | P12:138:AEPW:112GORE4:SNYDER-4
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05084 | 116.05 | 5841_Dup1
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05083 | 115.37 | 584560 GEN-2015-014 115 584561 G15-014XFMR1 34.5 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05085 | 116.08 | P12:138:AEPW:SANTAFE:DUNCAN-4
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05074 | 116.08 | 587991 G16-121XFMR1 34.5 587990 GEN-2016-121 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05074 | 116.01 | 588480 A16-010_SUB 115 3WXFMR A16-010_SUB 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05091 | 116.1 | P12:138:AEPW:DUNCAN-4:L.E.S.-4
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05074 | 115.46 | 588761 G17-033XFMR1 34.5 588760 GEN-2017-033 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05074 | 115.46 | 588765 G17-033XFMR2 34.5 588760 GEN-2017-033 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05074 | 116.02 | 588861 G17-047XFMR1 34.5 588860 GEN-2017-047 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05063 | 115.79 | P12:138:AEPW:ELKCTY-4:CLINTJC4
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05074 | 116.03 | 589381 G17-100XFMR1 34.5 589380 GEN-2017-100 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05074 | 116.07 | P12:138:AEPW:SHERID4:112GORE4
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05077 | 116.06 | P12:345:AEPW-OKGE:CLARKSV7:MUSKOGE7
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05387 | 117.78 | P12:345:AEPW:L.E.S7:TERRYRD7
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05387 | 117.77 | P12:345:AEPW:L.E.S7:TERRYRD7
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05387 | 117.75 | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05652 | 118.25 | P12:345:AEPW-OKGE:L.E.S.-7:GRACMNT7
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05652 | 118.23 | P12:345:AEPW-OKGE:L.E.S.-7:GRACMNT7
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05542 | 118.8 | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05074 | 116.08 | P22:345:AMMO::LABADIE:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05074 | 116.08 | P22:345:AMMO::LABADIE:2
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05074 | 116.09 | P22:345:AMMO::LABADIE:3
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05074 | 116.08 | P22:345:AMMO::LABADIE:4
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05074 | 116.07 | P22:345:AMMO::RUSHISLAND:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05074 | 116.06 | P22:345:AMMO::RUSHISLAND:2
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05075 | 115.79 | P13:138-13.8:AEPW:COMANC-4_#2
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05074 | 115.8 | P13:138-13.8:AEPW:S.W.S.-4
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.0503 | 115.47 | P13:138-230:AEPW:ELKCTY-4
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05075 | 115.79 | P13:138-24:AEPW:PIRKEY 4
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05079 | 115.69 | P13:138-24:AEPW:S.W.S.-4
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05075 | 115.75 | P13:138-24:AEPW:TURK 4
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05101 | 116.11 | P13:138-345:AEPW:L.E.S.-4_#2
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05075 | 116.02 | P12:500:EES-EAI:KEO:WMPEHV
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05076 | 116.14 | P23:500:EES-EAI:KEO:B4941
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05075 | 116.02 | P23:500:EES-EAI:KEO:B4931
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05076 | 116.13 | P23:500:EES-EAI:KEO:B4921
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05075 | 116.07 | P23:500:EES-EAI:INDEP2:B6126
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05075 | 116.06 | P23:500:EES-EAI:PD:INDEP2:LN:FK479
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05076 | 115.79 | P13:345-18:AEPW:WELSH 7_#1
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05076 | 115.79 | P13:345-18:AEPW:WELSH 7_#3
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05074 | 115.79 | P13:69-13.8:AEPW:COMANC-2
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05074 | 116.08 | P11:024:DPC:ALMA2:6
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05074 | 116.04 | P11:18:ITCM:EMERYGT1:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05074 | 116.05 | P11:18:ITCM:EMERYGT2:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05074 | 116.05 | P11:161:ITCM:MGS CT1:1C
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05074 | 116.05 | P11:161:ITCM:MGS CT2:2C
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05072 | 116.06 | 652537 WHITE 3 345 659286 DEERCREK-BE3 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05072 | 116.02 | 652568 GROTONSOUTH7 115 659275 GROTON_G-BE7 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05072 | 116.06 | 659286 DEERCREK-BE3 345 3WXFMR DEERCRK KU1A 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05074 | 116.05 | 672601 BD 4 230 672306 BD 6G 18.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05074 | 116.05 | 672610 POPLAR 4 230 672310 POPLAR 1G 18.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05074 | 116.05 | 672610 POPLAR 4 230 672311 POPLAR 2G 18.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05074 | 116.04 | 672621 SHAND 4 230 672321 SHAND 1G 18.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05074 | 116.03 | 672649 CODETTE 4 230 672650 NIPAWIN 4 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05074 | 116.04 | 672696 BRADA 4 230 672699 NBEC 4 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05074 | 116.12 | P23:345:MDU::COYOTE::5707-5712-5715::::
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05074 | 116.3 | P23:345:MEC:CBEC 905
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05074 | 116.25 | P23:345:MEC:CBEC 908
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05075 | 116.04 | P23:345:MEC:GDMEC 901
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05075 | 116.04 | P23:345:MEC:GDMEC 902
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05074 | 116.06 | P23:345:MEC:GDMEC 908
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05074 | 116.17 | P23:345:MEC:RAUN 0180
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05074 | 116.24 | P23:345:MEC:RAUN 0210
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05074 | 116.18 | P23:345:MEC:LOUISA 954
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05074 | 116.19 | P23:345:MEC:LOUISA 964
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05074 | 116.03 | P21:115:XEL:AUTO-SINGLE:CHEMOLT7:LSPOWER7:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05074 | 116.07 | P21:115:XEL:AUTO-SINGLE:COLVILL7:CANONFLSG7:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05074 | 116.03 | P21:115:XEL:AUTO-SINGLE:FARIBALTP7:FARIBALTGEN:Z
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05074 | 116.13 | P21:230:OTP:AUTO-SINGLE:SQBUTTE4:YNG24:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05074 | 116.12 | P23:345:OTP:CENTER 3:3215(1)
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05074 | 116.12 | P23:345:OTP:CENTER 3:3225(1)
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05074 | 116.06 | P12:230:UMZW:# 687 #: FT IN SD. FT-BG1 LINE FAULT
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05074 | 116.06 | P12:230:UMZW:# 3617 #: FT IN SD. FT-BG2 LINE FAULT
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05074 | 114.69 | 760494 GEN-2017-146 230 760498 G17-146-TAP 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05074 | 114.68 | 760495 G17-146-XFM1 34.5 760494 GEN-2017-146 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05074 | 115.46 | 761356 G17-239-XFMR 34.5 761355 GEN-2017-239 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05074 | 115.46 | 761359 G17-239-XFMR 34.5 761355 GEN-2017-239 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05074 | 115.63 | 761797 G17-187XFM1 34.5 761796 GEN-2017-187 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05074 | 115.63 | 761800 G17-187XFM2 34.5 761796 GEN-2017-187 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05074 | 110.67 | 762132 GEN-2017-158 230 763252 G18-099-XFM1 34.5 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05074 | 110.67 | 762132 GEN-2017-158 230 763255 G18-099-XFM2 34.5 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05074 | 111.27 | 762133 G17-158XFM1 34.5 762132 GEN-2017-158 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05074 | 111.27 | 762136 G17-158XFM2 34.5 762132 GEN-2017-158 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05074 | 113.54 | 762216 G17-151TAP 345 762217 GEN-2017-151 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05452 | 116.85 | 762216 G17-151TAP 345 762467 G18-015-TAP 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05074 | 115.27 | 762218 G17-151XFM1 34.5 762217 GEN-2017-151 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05074 | 115.27 | 762221 G17-151XFM2 34.5 762217 GEN-2017-151 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05074 | 115.27 | 762224 G17-151XFM3 34.5 762217 GEN-2017-151 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05074 | 115.27 | 762227 G17-151XFM4 34.5 762217 GEN-2017-151 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05074 | 114.55 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05074 | 115.11 | 762461 G18-015-XFM1 34.5 762460 GEN-2018-015 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05074 | 115.11 | 762464 G18-015-XFM2 34.5 762460 GEN-2018-015 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05281 | 116.42 | 762467 G18-015-TAP 345 763215 G18-092-TAP 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05074 | 113.8 | 763087 GEN-2018-073 345 763088 G18-073-XFM1 34.5 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05074 | 114.78 | 763087 GEN-2018-073 345 763091 G18-073-XFM2 34.5 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05074 | 110.64 | 763120 GEN-2018-081 230 763121 G18-081-XFM1 34.5 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05074 | 112.78 | 763120 GEN-2018-081 230 764011 G19-074-XFM1 34.5 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05074 | 112.92 | 763186 GEN-2018-089 230 763187 G18-089-XFM1 34.5 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05074 | 113.84 | 763208 GEN-2018-092 345 763215 G18-092-TAP 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05074 | 114.77 | 763208 GEN-2018-092 345 763220 G18-092-XFM1 34.5 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05074 | 114.77 | 763208 GEN-2018-092 345 763223 G18-092-XFM2 34.5 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05074 | 112.23 | 763241 GEN-2018-097 230 763242 G18-097-XFM1 34.5 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05074 | 113.15 | 763241 GEN-2018-097 230 763296 G18-111-XFM1 34.5 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05074 | 112.51 | 763241 GEN-2018-097 230 763307 G18-112-XFM1 34.5 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05074 | 112.51 | 763241 GEN-2018-097 230 763310 G18-112-XFM2 34.5 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05074 | 112.23 | 763241 GEN-2018-097 230 763395 G18-124-XFM1 34.5 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05074 | 112.23 | 763241 GEN-2018-097 230 763398 G18-124-XFM2 34.5 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05074 | 115.66 | 763318 GEN-2018-115 345 763319 G18-115-XFM1 34.5 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05074 | 112 | 763483 GEN-2019-003 230 763484 G19-003-XFM1 34.5 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05074 | 114.56 | 763483 GEN-2019-003 230 763605 G19-021-XFM1 34.5 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05074 | 115.46 | 763516 GEN-2019-011 345 763517 G19-011-XFM1 34.5 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05074 | 115.55 | 763879 GEN-2019-056 115 763880 G19-056XFM1 34.5 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.0505 | 116.19 | P42:345:OKGE:SB_BVTY7305
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.0506 | 115.75 | P23:345:WERE:BUFF_345-534::
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.0506 | 115.75 | P23:345:WERE:BUFF_345-543::
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.0507 | 116.23 | P23:345:WERE:JEC_345-15::
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05068 | 116.18 | P23:345:WERE:JEC_345-16::
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.0507 | 116.22 | P23:345:WERE:JEC_345-19::
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.0507 | 116.22 | P23:345:WERE:JEC_345-20::
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05073 | 116.39 | P23:345:WERE:WOLF_345-50::
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05074 | 116.39 | P23:345:WERE:WOLF_345-60::
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05075 | 115.8 | P42:345:AEPW:WELSH CB 10620 NBTB+FAULT
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05074 | 115.79 | P41:345:AEPW:WELSH CB 10630 NBTB+FAULT
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05074 | 115.79 | P41:345:AEPW:WELSH CB 11670 NBTB+FAULT
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05086 | 115.78 | P41:345:AEPW:WELSH CB 11680 NBTB+FAULT
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05074 | 115.78 | P41:345:AEPW:WELSH CB 12540 NBTB+FAULT
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05542 | 117.33 | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05706 | 118.58 | P42:345:AEPW:LAWTON EASTSIDE CB 3413A NBTB+FAULT
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05765 | 118.94 | P42:345:AEPW:LAWTON EASTSIDE CB 3425A NBTB+FAULT
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05563 | 118.96 | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05387 | 117.77 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05387 | 117.77 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05387 | 117.74 | P42:345:AEPW:TERRYRD_CB_3421A_NBTB
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05072 | 116.18 | P23:345:KCPL:LACYGNE_R2-5::LACYGU2-LACYGNE-STILWELL
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05073 | 115.82 | P45:345:UMZW:# 1328 #: GI IN NE.
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05075 | 115.8 | P23:345:AEPW:WELSH CB 10620 NBTB
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05074 | 115.79 | P23:345:AEPW:WELSH CB 10630 NBTB
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05074 | 115.79 | P23:345:AEPW:WELSH CB 11670 NBTB
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05086 | 115.78 | P23:345:AEPW:WELSH CB 11680 NBTB
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05074 | 115.78 | P23:345:AEPW:WELSH CB 12540 NBTB
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05542 | 117.74 | P23:345:AEPW:OKLAUNION CB 3401A NBTB
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05706 | 118.58 | P23:345:AEPW:LAWTON EASTSIDE CB 3413A NBTB
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05765 | 118.94 | P23:345:AEPW:LAWTON EASTSIDE CB 3425A NBTB
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05563 | 118.96 | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05387 | 117.77 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05387 | 117.77 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05387 | 117.74 | P23:345:AEPW:TERRYRD_CB_3421A_NBTB
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05074 | 116.05 | P11:161:GMO:DOGWOOD_COMBINED_CYCLE_UNIT_OUTAGE
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05074 | 116.06 | P11:115:SUNC:GARDENCITY_S2:97:531459(2)
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05062 | 115.77 | P12:345:PWT:BUFF-THIS_345_1::
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05062 | 115.77 | P12:345:PWT:BUFF-THIS_345_2::
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05062 | 115.83 | P12:345:PWT:THIS-DGRS_345_1::FUTURE
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05062 | 115.83 | P12:345:PWT:THIS-DGRS_345_2::FUTURE
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05086 | 116.06 | P12:069:WFEC:ANADRKO_WATONGA
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05412 | 117.97 | P23:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.0581 | 120.4 | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05412 | 117.97 | P42:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB+FAULT
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.0581 | 120.4 | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05047 | 115.62 | P23:345:SUNC:MO_BRK182
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05047 | 115.62 | P23:345:SUNC:MO_BRK382
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05042 | 115.79 | P23:345:SUNC:MO_BRK188
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05133 | 116.06 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05075 | 115.79 | P12:138-13.8:AEPW:COMANC-4_#1
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.0503 | 115.47 | P12:230:AEPW:ELKCITY6:CHISHOLM6
Thermal | 05ALL | 1 | 26SP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05126 | 116.62 | P12:230:AEPW:SWEETWT6:CHISHOLM6
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.1781 | 116.18 | P23:345:KCPL-WERE:237LACYGNE_R1-6::LACYGU1-LACYGNE-NEOSHO
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17807 | 116.06 | P11:230:WERE:LECU5_GEN::
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.08 | P11:161:GMO:DOGWOOD_COMBINED_CYCLE_UNIT_OUTAGE_1_1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.02 | P11:20:KACY:NEARMAN N1::N1 OUT OF SERVICE:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17808 | 116.02 | P12:69:KACY:NMGEN-NMISOBUS::NEARMAN N1-NM ISOBUS OPEN:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17808 | 116.02 | P13:20-161:KACY:NEARMAN5-NMISOBUS:NAMEPLATE:NEARMAN N1 GSU:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17808 | 116.02 | P21:20:KACY:546702NMGENN1-546703NMISOBUSC1::::
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.23 | P11:115:SPS:HOBBS1&3:145MW::::
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17815 | 114.72 | P11:115:SPS:MUSTANG1&3:153MW::::
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17887 | 118.23 | P12:230:SPS:K37::1_TOLK_LAMB:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17831 | 116.06 | P12:230:SPS:K43::1_PRNGLE_HARR_E:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17813 | 115.81 | P12:230:SPS:K44::1_EPLNT_HARRW:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17827 | 116.22 | P12:115:SPS:T04::1_TRBLNC_CASTRO:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17831 | 116.02 | P12:115:SPS:T06::1_SPRMN_PRNGLE:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.5 | P12:115:SPS:T21::1_GRSSLND_GRAHAM:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.05 | P12:115:SPS:T24B::1_RSWLL_BRSHRF:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.1781 | 116.05 | P12:115:SPS:T26::1_CHAVES_RSWLCTY:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17951 | 116.45 | P12:115:SPS:T28A::1_LAMTON_PLANTX:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17868 | 116.02 | P12:115:SPS:T29::1_LAMTON_HALECTR:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.1795 | 117.27 | P12:115:SPS:T30::1_LAMB_HOCKLY:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.1795 | 116.37 | P12:115:SPS:T31::1_HOCKLY_SUNDWN:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17808 | 116.06 | P12:115:SPS:T35::1_TERRY_YOAKUM:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.78 | P12:115:SPS:T45::1_NORRIS_OASIS:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.1781 | 115.82 | P12:115:SPS:T57::1_MUSTG_SEGRVS:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17876 | 116.03 | P12:115:SPS:T58::1_HERFRD_CARGIL:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17876 | 116.57 | P12:115:SPS:T59::1_CARGIL_CURRY:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.02 | P12:115:SPS:T64::1_RNDALL_PULLMN:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17919 | 116.38 | P12:115:SPS:T67::1_HAPPY_KRESS:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17815 | 115.77 | P12:115:SPS:T68::1_TUCO_FLOYD:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.1781 | 115.81 | P12:115:SPS:T69::1_LUBBE_CROSBY:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.02 | P12:115:SPS:T70::1_COLTR_S_GORG:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17804 | 116.63 | P12:115:SPS:T71::1_CRLSLE_YUMA:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17822 | 116.1 | P12:115:SPS:T81::1_COX_FLOYD:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.26 | P12:115:SPS:T83::1_SP-FKFD_ALLEN:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.1781 | 116.44 | P12:115:SPS:T89::1_DC_N_HIGG:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.07 | P12:115:SPS:T91::1_HIGG_RUSSELL:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17815 | 116.02 | P12:115:SPS:V01::1_MOOREW_RVRVIEW:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17834 | 116.07 | P12:115:SPS:V04::1_EPLANT_RNDALL:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17826 | 116.06 | P12:115:SPS:V07::1_COX_HALECTR:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17947 | 116.23 | P12:115:SPS:V09::1_HALECTR_PLANTX:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17811 | 116.21 | P12:115:SPS:V12::1_PLANTX_BAILEY:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.03 | P12:115:SPS:V15::1_TUCO_INDANA:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17778 | 116.16 | P12:115:SPS:V24::1_WOLFTH_TERRY:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17825 | 116.07 | P12:115:SPS:V26::1_RSWLL_EDDY_N:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.4 | P12:115:SPS:V33::1_LUBBS_LYNN:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17926 | 117.14 | P12:115:SPS:V37::1_CASTRO_PLANTX:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.1781 | 116.05 | P12:115:SPS:V44::1_COLTR_OWENS:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.16 | P12:115:SPS:V46::1_ALLEN_WHEELCK:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17811 | 116.5 | P12:115:SPS:V49::1_YOAKUM_SHLCO2:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17868 | 116.68 | P12:115:SPS:V55::1_SUNDWN_TERRY:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17834 | 116.59 | P12:115:SPS:V56::1_COCHRAN_SUNDWN:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.09 | P12:115:SPS:V62::1_CRLSLE_INDANA:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17813 | 116.07 | P12:115:SPS:V78::2_CURRY_RSVLT:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17811 | 116.19 | P12:115:SPS:V81::1_LE-WAIT_LE-LVN:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.1781 | 116.06 | P12:115:SPS:V95::1_DC_N_SHLCO2:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.02 | P12:115:SPS:W11::1_DC_S_SMINLE:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.03 | P12:115:SPS:W12::1_SMINLE_DOSS:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.1781 | 116.1 | P12:115:SPS:W14::1_SMINLE_GAINES:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.03 | P12:115:SPS:W26::1_CUNGHM_OILCNTR:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.61 | P12:115:SPS:W32::1_PRMTR_FE-CLSIN:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.1781 | 116.26 | P12:115:SPS:W35::1_GAINES_JNSDRW:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.18032 | 116.59 | P12:115:SPS:W40::1_WCANYON_TRBLNC:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17846 | 116.11 | P12:115:SPS:W52::1_NEWHART_KRESS:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.67 | P12:115:SPS:W58::1_NORTON_LOPEZ:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.25 | P12:115:SPS:W59::1_LOPEZ_CMPBLL:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.1781 | 116.55 | P12:115:SPS:W62::1_PLSTHL_CURRY:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17822 | 116.07 | P12:115:SPS:W63::1_PLSTHL_CURRY:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.36 | P12:115:SPS:W64::1_PLSTHL_FE-CLV:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.1781 | 116.57 | P12:115:SPS:W65::1_PLSTHL_CURRY:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.23 | P12:115:SPS:W66::1_PORTA_GREYHUND:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17807 | 116.02 | P12:115:SPS:W76::1_QUAHA_PCA:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.18032 | 116.1 | P12:115:SPS:W77::1_RNDAL_WCANYON:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.1781 | 116.07 | P12:115:SPS:W99::1_CAPITAN_CHAVES:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.05 | P12:115:SPS:U03::1_CARDNL_NEF:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17808 | 116.53 | P12:115:SPS:U14::1_DC_STH_INKBSN:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17811 | 116.47 | P12:115:SPS:V15::1_INKBSN_LE-WAT:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17836 | 116.15 | P12:115:SPS:U16::1_BSHLND_OUTPST:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17836 | 116.16 | P12:115:SPS:U17::1_COLTR_OUTPST:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17828 | 116.26 | P12:115:SPS:U19::1_DEAN_PLAINS:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17836 | 116.07 | P12:115:SPS:U23::1_COLTR_HILSDE:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17138 | 124.36 | P42:345:SPS:YOAKUM:J18####:SLG1:EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17138 | 124.36 | P43:345:SPS:YOAKUM:TF#####:SLG:EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17138 | 124.36 | P42:345:SPS:YOAKUM:J17####:SLG:EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17138 | 124.36 | P42:345:SPS:YOAKUM:J18####:SLG2:EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17808 | 116.06 | P11:18:HAST:::EGYCTR2G WEC2_LOSS OF WEC 2 GEN_:HV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17808 | 116.06 | P13:18-115:HAST:::EGYCNTR7 XFMR G2WEC 2 GSU_:HV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.08 | P11:161:GMO:DOGWOOD-COMBINED-CYCLE-UNIT-OUTA:::HV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.1781 | 116.18 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17808 | 116.18 | P23:345:KCPL:LACYGNE-R2-5:::EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17805 | 116.23 | P11:230:WERE:JECU1-GEN:::HV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17807 | 116.06 | P11:230:WERE:LECU5-GEN:::HV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17805 | 116.23 | P11:345:WERE:JECU2-GEN:::EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17805 | 116.22 | P11:345:WERE:JECU3-GEN:::EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.4 | P11:345:WERE:WOLFU1-GEN:::EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17795 | 115.77 | P12:345:PWT:BUFF-THIS-345-1:::EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17795 | 115.77 | P12:345:PWT:BUFF-THIS-345-2:::EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17793 | 115.75 | P23:345:WERE:BUFF-345-534:::EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17793 | 115.75 | P23:345:WERE:BUFF-345-543:::EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17805 | 116.23 | P23:345:WERE:JEC-345-15:::EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17804 | 116.18 | P23:345:WERE:JEC-345-16:::EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17805 | 116.22 | P23:345:WERE:JEC-345-19:::EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17805 | 116.22 | P23:345:WERE:JEC-345-20:::EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.39 | P23:345:WERE:WOLF-345-50:::EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.39 | P23:345:WERE:WOLF-345-60:::EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.34 | P11:022:NPPD:COOPER1G:1:983:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17804 | 116.33 | P11:023:NPPD:GENTLM1G:1:757:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17804 | 116.35 | P11:024:NPPD:GENTLM2G:2:757:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17808 | 116.01 | P11:161:OPPD:N OMA 5G:LT::HV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17808 | 116.01 | P11:161:OPPD:N OMA 5G:::HV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17805 | 116.2 | P13:345:OPPD:NEBCTY1G:::EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17804 | 116.22 | P13:345:OPPD:NEBCTY2G:::EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17808 | 116.01 | P13:161:OPPD:N OMA 5G:::HV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.22 | P22:345:OPPD:S3458 NEBCTY1G:LT::EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17805 | 116.2 | P22:345:OPPD:S3458 NEBCTY1G:::EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.25 | P22:345:OPPD:S3458 NEBCTY2G:LT::EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17804 | 116.22 | P22:345:OPPD:S3458 NEBCTY2G:::EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.22 | P23:345:OPPD:S3458 NEBCTY1G:LT::EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17805 | 116.2 | P23:345:OPPD:S3458 NEBCTY1G:::EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.25 | P23:345:OPPD:S3458 NEBCTY2G:LT::EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17804 | 116.22 | P23:345:OPPD:S3458 NEBCTY2G:::EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 115.8 | P12:115:SUNC:PLYMELL-PIERCEVILLE:::HV::
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17807 | 116.06 | P11:018:UMZB:# 5 #:: DCS IN SD. DEERCREEK_MV::
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17808 | 116.03 | P11:022:UMZB:# 15 #:: LO IN ND. LELAND OLDS 1_MV::
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17807 | 116.07 | P11:020:UMZB:# 16 #:: LO IN ND. LELAND OLDS 2_MV::
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17807 | 116.14 | P11:023:UMZB:# 31 #:: AVS IN ND. ANTELOPE VALLEY 1_MV::
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17807 | 116.14 | P11:023:UMZB:# 32 #:: AVS IN ND. ANTELOPE VALLEY 2_MV::
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17803 | 116.33 | P11:024:UMZB:# 33 #:: LRS IN WY. LARAMIE RIVER STATION 1_MV::
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.06 | P12:230:UMZW:# 687 #:: FT IN SD. FT-BG1 BRANCH FAULT:HV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.06 | P12:230:UMZW:# 3617 #:: FT IN SD. FT-BG2 BRANCH FAULT:HV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.06 | P12:230:UMZW:# 4038 #:: BG-FT IN SD. FAULT FOR TRANSMISSION CIRCUIT (BG-FT).:HV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.06 | P12:230:UMZW:# 4039 #:: BG-FT IN SD. FAULT FOR TRANSMISSION CIRCUIT (BG-FT).:HV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.03 | P13:230:UMZW:# 5135 #:: OA IN SD. FAULT ON TRANSFORMER (2).:HV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.03 | P13:230:UMZW:# 5136 #:: OA IN SD. FAULT ON TRANSFORMER (3).:HV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17808 | 115.82 | P23:345:UMZW:# 2423 #:: GI IN NE. GI 1596 BKR FAULT:EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17808 | 115.82 | P23:345:UMZW:# 2426 #:: GI IN NE. GI 1592 BKR FAULT:EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17808 | 115.82 | P23:345:UMZW:# 2432 #:: GI IN NE. GI 1092 BKR FAULT:EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17808 | 115.82 | P23:345:UMZW:# 2440 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1092 STUCK BKR:EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17808 | 115.82 | P23:345:UMZW:# 2444 #:: GI IN NE. GI-SWEET BRANCH FAULT & GI 1596 STUCK BKR:EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17808 | 115.82 | P23:345:UMZW:# 2446 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1196 STUCK BKR:EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17808 | 115.82 | P42:345:UMZW:# 2413 #:: FT2 IN SD. FT2-LO2 BRANCH FAULT & FT2 2992 STUCK BKR:EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17808 | 115.82 | P42:345:UMZW:# 2415 #:: FT2 IN SD. FT2-GI BRANCH FAULT & FT2 3392 STUCK BKR:EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17812 | 115.74 | P11:138:WFEC:HUGO1:465MW :::
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17808 | 116.02 | P11:138:WFEC:MORLND2:132MW:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17808 | 116.03 | P11:138:WFEC:MORLND3:149MW :::
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17818 | 116.06 | P12:138:WFEC:ANADRKO_CLVLND::::
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17812 | 116.06 | P12:345:OKGE-AEPW:BKRBKR12::::
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17846 | 116.18 | P12:345:OKGE:BKRBKR21::::
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17865 | 116.26 | P12:345:OKGE:BKRBKR24::::
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.18056 | 117.75 | P12:345:OKGE-AEPW:BKRBKR25::::
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17778 | 115.72 | P12:345:OKGE:BKRBKR336::::
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17778 | 115.72 | P12:345:OKGE:BKRBKR336_2::::
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.18132 | 118.25 | P12:345:OKGE-AEPW:BKRBKR366::::
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.18132 | 118.23 | P12:345:OKGE-AEPW:BKRBKR366::::
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.18018 | 117.15 | P12:345:OKGE:BKRBKR367::::
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17783 | 115.72 | P12:345:OKGE:BKRBKR4193::::
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17783 | 115.72 | P12:345:OKGE:BKRBKR4194::::
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.02 | P12:345:OKGE:BKRBKR4195::::
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17772 | 115.76 | P12:345:OKGE-SPS:BKRBKR4201::::
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17772 | 115.76 | P12:345:OKGE-SPS:BKRBKR4202::::
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17819 | 116.03 | P12:345:OKGE:BKRBKR421::::
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17776 | 115.6 | P12:345:OKGE:BKRBKR443NEW::::
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17775 | 115.6 | P12:345:OKGE:BKRBKR443NEW2::::
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17793 | 115.79 | P12:345:OKGE-ITC:BKRBKR502::::
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17793 | 115.79 | P12:345:OKGE-ITC:BKRBKR503::::
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17796 | 115.83 | P12:345:OKGE-ITC:BKRBKR502_1::::
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17796 | 115.83 | P12:345:OKGE-ITC:BKRBKR503_1::::
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17803 | 116.33 | P12:345:OKGE:BKRBKR604::::
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17802 | 116.37 | P12:345:OKGE:BKRBKR604_2::::
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17811 | 115.82 | P11:345:OKGE:BKRBKR_GSU07::::
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17811 | 115.81 | P11:345:OKGE:BKRBKR_GSU08::::
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17811 | 115.8 | P11:138:OKGE:BKRBKR_GSU21::::
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17807 | 115.83 | P12:138:OKGE:BKRBKR85_MOS1::::
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17776 | 116.13 | P42:345:OKGE:SB_ARIA7381::::
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.18509 | 120.17 | P42:345:OKGE:SB_BVTY7387::::
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.1782 | 116.02 | P41:345:OKGE:SB_REUD7381::::
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17819 | 116.03 | P41:345:OKGE:SB_REUD7383::::
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17819 | 116.06 | P41:345:OKGE:SB_REUD7385::::
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17822 | 116.06 | P42:345:OKGE:SB_REUD7389::::
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17807 | 116.05 | P11:115:SUNC:GARDENCITY_S2:103:531459(2):HV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17807 | 116.07 | P11:115:SUNC:FORTDDODGE_4:157:539670(4):HV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.04 | P11:345:599:CIMARRON1WIND:200:531603(1):EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.47 | P13:115:SUNC:HOLCOMB_GSU:::HV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17807 | 116.05 | P13:115:SUNC:S2_GSU:::HV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17807 | 116.07 | P13:115:SUNC:FORTDODGE_GSU:::HV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17807 | 116.04 | P23:345:SUNC:BU_BRK682:::EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.14 | 300003 1THLG3 24.0 301503 7THOMHLGSU3 345 3
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.01 | 300007 1NM G2 22.0 301537 7NEWMADGSU2 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.01 | 300046 7NEWMAD 345 301537 7NEWMADGSU2 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.14 | 300049 7THOMHL 345 301503 7THOMHLGSU3 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.08 | P11:20:AMMO:1LAB�� G1:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.08 | P11:20:AMMO:1LAB�� G2:2
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.27 | P11:345:AMMO::CALLAWAY:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.08 | P11:345:AMMO::LABADIE:3
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.08 | P11:345:AMMO::LABADIE:4
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.07 | P11:345:AMMO::RUSHISLAND:U1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.07 | P11:345:AMMO::RUSHISLAND:U2
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.06 | P11:138:AMMO::SIOUX:2
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 115.83 | P11:24:CLEC::G1DOLHIL:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.06 | P12:765:AEP:AEP ROCKP-AEP JEFF 765
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 115.78 | P11:HV:EES::PIRKEY 1:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 115.79 | P11:EHV:EES::WELSH3-1:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 115.74 | P11:HV:EES::TURKCOAL:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.25 | P12:EHV:EES::7CALAWY 1:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.1781 | 116.02 | 338056 CHALKBLUFFPV 500 338162 8W.MEMPHIS% 500 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17811 | 115.75 | P12:HV:EES::TURK 4%:1(1)
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17811 | 115.79 | P12:EHV:EES::WELSH 7:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17811 | 115.79 | P12:EHV:EES::WELSH 7:1(1)
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.1781 | 115.79 | P12:HV:EES::PIRKEY 4:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17812 | 116.06 | P12:EHV:EES::CLARKSV7!:MUSKOGE7!:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.06 | 344011 7HUGHES 345 344012 7HPW-N 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.08 | 344884 7LABADIE1 345 344894 1LAB G1 20.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.08 | 344885 7LABADIE2 345 344895 1LAB G2 20.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.08 | 344886 7LABADIE3 345 344896 1LAB G3 20.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.08 | 344887 7LABADIE4 345 344897 1LAB G4 20.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.07 | 345667 7RUSH 1 345 345670 1RUSH G1 18.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.06 | 345668 7RUSH 2 345 345671 1RUSH G2 18.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.05 | 345755 4SIOUX 1 138 345756 1SIOUX 1 18.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.05 | 345764 4SIOUX 2 138 345765 1SIOUX 2 18.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.12 | P12:345:MDU::CENTER:COYOTE:1::::
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.12 | P13:345:MDU:COYOTE GSU LOSS:COYOTE::1::::
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.03 | P11:345:MEC:GDMEC CT1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.03 | P11:345:MEC:GDMEC CT2
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.14 | P11:345:MEC:GDMEC ST
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.35 | P11:345:MEC-NPPD:COOPER 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.24 | P11:24:XEL:AUTO-SINGLE:SHERC31G:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.24 | P11:24:XEL:AUTO-SINGLE:SHERC32G:2
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.33 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.16 | P11:20:XEL:AUTO-SINGLE:PRIS31G:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.16 | P11:20:XEL:AUTO-SINGLE:PRIS32G:2
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.2 | P11:22:XEL:AUTO-SINGLE:MNTCE31G:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.16 | P11:20:XEL:AUTO-SINGLE:KING31G:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.02 | P11:13:XEL:AUTO-SINGLE:HBRS73G:9
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.02 | P11:18:XEL:AUTO-SINGLE:BLKD76G:6
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.22 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.22 | P11:22:GRE:AUTO-SINGLE:GRE-COAL42G:2
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.14 | P11:24:OTP:AUTO-SINGLE:BIGSTN1G:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.15 | P11:20:OTP:AUTO-SINGLE:CENTER2G:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.05 | P11:22:OTP:AUTO-SINGLE:CENTER1G:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.13 | P11:24:OTP:AUTO-SINGLE:COYOTE1G:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.05 | P11:24:DPC:AUTO-SINGLE:GENOA53G:3
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.03 | P12:115:XEL:AUTO-SINGLE:CHEMOLT7:LSPOWER7:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.07 | P12:115:XEL:AUTO-SINGLE:COLVILL7:CANONFLSG7:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.03 | P12:115:XEL:AUTO-SINGLE:FARIBALTP7:FARIBALTGEN:Z
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.13 | P12:230:OTP:AUTO-SINGLE:SQBUTTE4:YNG24:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.22 | P13:24-345:XEL:AUTO-SINGLE:SHERC31G:SHERCO3:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.22 | P13:24-345:XEL:AUTO-SINGLE:SHERC32G:SHERCO3:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.3 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.16 | P13:20-345:XEL:AUTO-SINGLE:PRIS31G:PRISLD3:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.16 | P13:20-345:XEL:AUTO-SINGLE:PRIS32G:PRISLD3:2
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.2 | P13:22-345:XEL:AUTO-SINGLE:MNTCE31G:MNTCELO3:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.15 | P13:20-345:XEL:AUTO-SINGLE:KING31G:ASKING3:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.02 | P13:13-115:XEL:AUTO-SINGLE:HBRS73G:HIBRDGE7:9
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.2 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL41G:GRE-COALCR4:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.2 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL42G:GRE-COALCR4:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.13 | P13:230-24:OTP:AUTO-SINGLE:BIGSTON4:BIGSTN1G:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.13 | P13:20-230:OTP:AUTO-SINGLE:CENTER2G:YNG24:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.04 | P13:22-230:OTP:AUTO-SINGLE:CENTER1G:CENTER4:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.12 | P13:24-345:OTP:AUTO-SINGLE:COYOTE1G:COYOTE3:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.05 | P13:24-161:DPC:AUTO-SINGLE:GENOA53G:GENOA5:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.07 | P13:24-161:DPC:AUTO-SINGLE:JPM:ALMA5:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.1781 | 116.02 | 38203 J1819 POI 500 337957 8KEO% 500 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.1781 | 116.02 | 38203 J1819 POI 500 338056 CHALKBLUFFPV 500 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.13 | P11:115:XEL:RIV COMBINE CYCLE
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.04 | P12:115:XEL:BDS #2 5
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.04 | P11:115:XEL:HBR #6
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.04 | P11:115:XEL:HBR #7
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.16 | P11:115:XEL:HBR #6 7 8
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.16 | P23:345:XEL:8H14 PRI
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.16 | P23:345:XEL:8H17 PRI AS
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.3 | P23:345:XEL:8N28 SHC
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.22 | P23:345:XEL:8N22 SHC
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.22 | P23:345:XEL:8N17 SHC
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.21 | P23:345:XEL:8N8 MNN
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.15 | P23:345:XEL:8P1 KING
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.15 | P23:345:XEL:8P2 KING
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.04 | P23:115:XEL:5P147 IVH AS
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.03 | P11:18:ALTW:AUTO-SINGLE:EMERYST1:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.03 | P11:22:ALTW:AUTO-SINGLE:LANS54G:4
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.17 | P11:22:ALTW:AUTO-SINGLE:ARNOLD1G:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.2 | P11:24:ALTW:AUTO-SINGLE:OTTUMW1G:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.03 | P13:18-161:ALTW:AUTO-SINGLE:EMERYST1:EMERY5:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.03 | P13:22-161:ALTW:AUTO-SINGLE:LANS54G:LANSINGL15:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.16 | P13:22-161:ALTW:AUTO-SINGLE:ARNOLD1G:ARNOLD5:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.19 | P13:24-161:ALTW:AUTO-SINGLE:OTTUMW1G:OTTUMWA5:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.27 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.34 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.19 | P11:22:MEC:AUTO-SINGLE:NEAL3G:3
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.26 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.19 | P11:24:MEC:AUTO-SINGLE:LOUIS31G:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.25 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.3 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.17 | P13:345-22:MEC:AUTO-SINGLE:RAUN3:NEAL3G:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.24 | P13:345-24:MEC:AUTO-SINGLE:RAUN3:NEAL4G:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.18 | P13:345-24:MEC:AUTO-SINGLE:LOUISA3:LOUIS31G:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17805 | 116.23 | P11:230:WERE:JECU1_GEN::
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17805 | 116.23 | P11:345:WERE:JECU2_GEN::
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17805 | 116.22 | P11:345:WERE:JECU3_GEN::
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.4 | P11:345:WERE:WOLFU1_GEN::
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17811 | 116.03 | 511435 SNYDER-4 138 588779 TAP_G17-036 138 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17817 | 116.03 | 511453 DUNCAN-4 138 511552 DUNCHERTP4 138 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17817 | 116.03 | 511455 D.E.S.-4 138 511552 DUNCHERTP4 138 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17817 | 116.02 | 511455 D.E.S.-4 138 529344 OMDUNE-4 138 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 114.98 | 511456 O.K.U.-7 345 588760 GEN-2017-033 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.18116 | 117.74 | 511456 O.K.U.-7 345 763215 G18-092-TAP 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.18129 | 118.31 | 511468 L.E.S.-7 345 762467 G18-015-TAP 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.18026 | 117.72 | 511468 L.E.S.-7 345 763215 G18-092-TAP 345 2
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 115.66 | 511468 L.E.S.-7 345 763318 GEN-2018-115 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17811 | 116.05 | 511488 112GORE4 138 511510 LAIRGST4 138 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17822 | 116.11 | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17811 | 116.04 | 511500 CACHE4 138 511510 LAIRGST4 138 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17811 | 116.03 | 511500 CACHE4 138 588779 TAP_G17-036 138 2
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17936 | 116.06 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17161 | 113.09 | 511553 CHISHOLM7 345 523961 POTTER_CO 7 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17161 | 113.09 | 511553 CHISHOLM7 345 523961 POTTER_CO 7 345 2
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.1752 | 115.5 | 511553 CHISHOLM7 345 755000 WWDBORDT 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17816 | 116.14 | 511557 CHISHOLM6 230 3WXFMR CHISHOLM6 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17823 | 116.02 | 514801 MINCO 7 345 555234 NSUB345 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17735 | 115.63 | 515375 WWRDEHV7 345 755000 WWDBORDT 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.18509 | 120.2 | 515458 BORDER 7 345 560022 CRAWFISH_DR 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.18509 | 120.15 | 515458 BORDER 7 345 755000 WWDBORDT 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17819 | 116.02 | 515543 RENFROW7 345 763421 G18-128-TAP 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17806 | 116.12 | 515618 BALKOW 7 345 3WXFMR BALKOW 7 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17806 | 116.13 | 515618 BALKOW 7 345 3WXFMR BALKOW 7 1_Dup1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17815 | 116.04 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17802 | 116.39 | 515634 PALDR1W7 345 3WXFMR PALO2 _1 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.13 | 515677 BADGER 7 345 563170 G15082_1 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17805 | 116.01 | 521017 ONEY 4 138 521089 WASHITA4 138 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.02 | 522800 MU-TULIA 3 115 525179 TULIA_TP 3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.16 | 522892 MU-BROWNFLD2 69.0 526761 BROWNFLD_TP2 69.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.03 | 523090 TEXAS_CNTY 3 115 589380 GEN-2017-100 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17805 | 116.16 | 523093 HITCHLAND 3 115 523174 GOODWELLWND3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.34 | 523097 HITCHLAND 7 345 523112 NOVUS1 7 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.4 | 523097 HITCHLAND 7 345 523215 FREWHELCOL17 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17606 | 114.83 | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.16538 | 112.81 | 523097 HITCHLAND 7 345 523961 POTTER_CO 7 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.45 | 523097 HITCHLAND 7 345 560252 G10-14 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.01 | 523099 TC-DRYTRLS 3 115 588480 A16-010_SUB 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.23 | 523112 NOVUS1 7 345 3WXFMR NOVUS XF2 2
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.04 | 523112 NOVUS1 7 345 3WXFMR XIANA2011198 _1 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17807 | 116.02 | 523118 BUFF_DUNES 7 345 523853 FINNEY 7 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.02 | 523120 COLE 3 115 588860 GEN-2017-047 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17807 | 116.04 | 523172 GWELL_COLL11 34.5 523174 GOODWELLWND3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17807 | 116.04 | 523173 GWELL_COLL21 34.5 523174 GOODWELLWND3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17819 | 116.01 | 523221 XIT_INTG 6 230 3WXFMR SIEM_T126401 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17831 | 116.07 | 523267 PRINGLE 6 230 3WXFMR ENRCO13617-1 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17831 | 116.06 | 523267 PRINGLE 6 230 523979 HARRNG_EST 6 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17875 | 116.2 | 523309 MOORE_CNTY 6 230 523323 MCDWL_CREEK6 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17845 | 116.12 | 523323 MCDWL_CREEK6 230 523959 POTTER_CO 6 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17783 | 116.45 | 523959 POTTER_CO 6 230 524010 ROLLHILLS 6 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.18821 | 117.19 | 523959 POTTER_CO 6 230 524267 BUSHLAND 6 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.18772 | 118.35 | 523959 POTTER_CO 6 230 525461 NEWHART 6 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.18806 | 121.11 | 523961 POTTER_CO 7 345 3WXFMR WAUK 90343-A 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17812 | 115.74 | 523978 HARRNG_MID 6 230 523979 HARRNG_EST 6 230 @1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17836 | 116.16 | 524267 BUSHLAND 6 230 3WXFMR WH 7001795 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.19604 | 117.94 | 524267 BUSHLAND 6 230 524623 DEAFSMITH 6 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17797 | 116.44 | 524296 SPNSPUR_WND7 345 524299 SPNSPUR_COL7 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17797 | 116.44 | 524299 SPNSPUR_COL7 345 3WXFMR SPNSPUR_COL7 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.1825 | 117.09 | 524415 AMA_SOUTH 6 230 525213 SWISHER 6 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.67 | 524502 NORTON 3 115 524509 FE-TUCMCARI3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.18032 | 116.45 | 524575 DS-#25+ 3 115 524597 PANDAHFD 3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.18032 | 116.55 | 524575 DS-#25+ 3 115 524630 TIERABLANCA3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.11 | 524604 HEREFRD_SB 2 69.0 524608 HERFRD_STH 2 69.0 *1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.19608 | 122.73 | 524623 DEAFSMITH 6 230 760498 G17-146-TAP 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.52 | 524721 DS-#15&#19+2 69.0 524745 CASTRO_CNTY2 69.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17811 | 116.03 | 524770 PLSNT_HILL 6 230 3WXFMR EFAE1100068A 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.18203 | 121.59 | 524875 OASIS 6 230 524885 SN_JUAN_TAP6 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17861 | 117.16 | 524875 OASIS 6 230 524909 ROOSEVELT 6 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.18194 | 121.97 | 524885 SN_JUAN_TAP6 230 527483 CHAVES_CNTY6 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17815 | 116.22 | 524909 ROOSEVELT 6 230 3WXFMR ABB LMM60042 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.1819 | 122.19 | 524909 ROOSEVELT 6 230 525531 TOLK 6 230 2
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.77 | 524923 PORTALES 2 69.0 524929 RO-PORT_MTR2 69.0 @1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.42 | 524923 PORTALES 2 69.0 524941 PORTALES#1 2 69.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.66 | 525023 BC-BAIL_MTR2 69.0 525027 BAILEYCO 2 69.0 @1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17926 | 116.55 | 525056 BC-EARTH 3 115 525480 PLANT_X 3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.51 | 525191 KRESS_INT 2 69.0 525203 SW-KRESS 2 69.0 Z1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.6 | 525192 KRESS_INT 3 115 3WXFMR ENRCO 136155 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.18224 | 116.83 | 525213 SWISHER 6 230 525461 NEWHART 6 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.15 | 525272 KISER 3 115 3WXFMR VON 13819/1 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.61 | 525326 COX 3 115 3WXFMR ELCO 13474-3 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.61 | 525414 LAMTON 3 115 3WXFMR ASEA MLL9204 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.18313 | 118.1 | 525481 PLANT_X 6 230 3WXFMR WH ALM20171 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.19356 | 121 | 525481 PLANT_X 6 230 526435 SUNDOWN 6 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.19608 | 121.02 | 525481 PLANT_X 6 230 760498 G17-146-TAP 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17166 | 116.49 | 525481 PLANT_X 6 230 762174 G17-218TAP 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17088 | 116.56 | 525481 PLANT_X 6 230 762174 G17-218TAP 230 2
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.18648 | 121.7 | 525531 TOLK 6 230 525586 NEEDMORE 6 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17887 | 118.23 | 525531 TOLK 6 230 525637 LAMB_CNTY 6 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.16858 | 116.76 | 525531 TOLK 6 230 762174 G17-218TAP 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.16792 | 116.82 | 525531 TOLK 6 230 762174 G17-218TAP 230 2
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.18648 | 121.69 | 525586 NEEDMORE 6 230 526935 YOAKUM 6 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.41 | 525599 LC-SANDHLL+2 69.0 525606 AMHERST 2 69.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.45 | 525606 AMHERST 2 69.0 525613 W_LITTLFLD 2 69.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.46 | 525613 W_LITTLFLD 2 69.0 525635 LAMB_CNTY 2 69.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.42 | 525635 LAMB_CNTY 2 69.0 525650 LC-LTTLFLD+2 69.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17887 | 118.23 | 525637 LAMB_CNTY 6 230 3WXFMR WH ALM20172 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.41 | 525779 FLOYD_CNTY 2 69.0 525790 FLOYDADA_TP2 69.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.29 | 525828 TUCO_INT 3 115 3WXFMR DS F78800913 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.1711 | 118.38 | 525832 TUCO_INT 7 345 526936 YOAKUM_345 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.49 | 526086 SW_6786_N 2 69.0 526087 SW_6786_S 2 69.0 Z1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.49 | 526086 SW_6786_N 2 69.0 526102 SP-HETTLER 2 69.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.56 | 526087 SW_6786_S 2 69.0 526284 PLANTERS 2 69.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.1 | 526160 CARLISLE 3 115 3WXFMR WH RLP38371 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.44 | 526195 QUINCY 3 115 526196 SP-MILWAUKEE 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.34 | 526268 LUBBCK_STH 3 115 3WXFMR NA 70454A 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.6 | 526284 PLANTERS 2 69.0 526297 LUBBCK_EST 2 69.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17834 | 116.47 | 526424 PACIFIC 3 115 526434 SUNDOWN 3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17813 | 116.06 | 526435 SUNDOWN 6 230 3WXFMR UPDATE LATER _12 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.18017 | 118.87 | 526435 SUNDOWN 6 230 526460 AMOCO_SS 6 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.18017 | 116.5 | 526460 AMOCO_SS 6 230 526935 YOAKUM 6 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.08 | 526525 WOLFFORTH 6 230 3WXFMR UPDATE LATER _13 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.48 | 526735 TERRY_CNTY 2 69.0 526747 LG-BROWNFLD2 69.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17822 | 118.02 | 526935 YOAKUM 6 230 527028 INK_BASIN 6 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.18275 | 116.3 | 526936 YOAKUM_345 345 3WXFMR SPX WT04221 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17216 | 126.57 | 526936 YOAKUM_345 345 527896 HOBBS_INT 7 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17819 | 117.39 | 527028 INK_BASIN 6 230 527894 HOBBS_INT 6 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.1781 | 116.43 | 527130 DENVER_N 3 115 527286 HIGGEAST 3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.1781 | 116.02 | 527149 MUSTANG 6 230 3WXFMR ENRCO 136161 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17825 | 114.01 | 527149 MUSTANG 6 230 527151 GS-MUSTANG 6 230 @1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.29 | 527202 SEAGRAVES 3 115 3WXFMR ABB MLL92408 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.17 | 527212 DIAMONDBACK3 115 3WXFMR HOW 36773714 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.1781 | 116.41 | 527286 HIGGEAST 3 115 527363 HIGG 3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.1781 | 116.16 | 527325 OXY_WSEM_TP3 115 527362 JOHNSON_DRW3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.15 | 527340 DOSS 3 115 3WXFMR ELCO 13566/1 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.14 | 527345 LEGACY 2 69.0 527350 XTO_ROBRTSN2 69.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.14 | 527346 LEGACY 3 115 3WXFMR VROL 13735-1 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.12 | 527350 XTO_ROBRTSN2 69.0 527355 BOARDMAN 2 69.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.05 | 527355 BOARDMAN 2 69.0 527365 FLANNAGAN 2 69.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.02 | 527360 MAPCO 3 115 527362 JOHNSON_DRW3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.08 | 527362 JOHNSON_DRW3 115 528775 LE-ERF 3 115 @1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.01 | 527370 TENNECO_TAP2 69.0 527371 TENNECO 2 69.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17973 | 116.35 | 527483 CHAVES_CNTY6 230 527799 EDDY_NORTH 6 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.05 | 527508 PRICE 3 115 527509 PRICE_TAP 3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.02 | 527514 CV-PINE 2 69.0 527563 ROSWLL_INT 2 69.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.05 | 527529 RIACBRSH_TP3 115 527533 SW4J795_E 3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.02 | 527529 RIACBRSH_TP3 115 527536 BRASHER 3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.05 | 527533 SW4J795_E 3 115 527564 ROSWLL_INT 3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.06 | 527563 ROSWLL_INT 2 69.0 527575 SW_4702 2 69.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17825 | 116.1 | 527564 ROSWLL_INT 3 115 527597 TWEEDY 3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.06 | 527575 SW_4702 2 69.0 527589 CV-ORCHARD 2 69.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.02 | 527589 CV-ORCHARD 2 69.0 527619 DEXTER_TP 2 69.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17805 | 116.18 | 527653 MILO_WIND 1 34.5 527655 RSVLT_CC_E 7 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17797 | 116.1 | 527654 RSVLT_CC_W 7 345 527655 RSVLT_CC_E 7 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17797 | 116.36 | 527654 RSVLT_CC_W 7 345 527666 RSVLT_COL1 7 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17793 | 116.3 | 527655 RSVLT_CC_E 7 345 527656 CROSSROADS 7 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17797 | 116.36 | 527666 RSVLT_COL1 7 345 3WXFMR RSVLT_COL1 7 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.15 | 527790 EDDY_SVC 1 8.50 527799 EDDY_NORTH 6 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.05 | 527864 CUNNINHAM 3 115 528568 MONUMNT_TP 3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17799 | 116.16 | 527865 CUNNIGHM_N 6 230 527867 CUNNIGHM_S 6 230 *1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.14 | 527865 CUNNIGHM_N 6 230 527883 CUNINGHAM3 1 13.8 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17806 | 116.08 | 527865 CUNNIGHM_N 6 230 527963 POTASH_JCT 6 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17806 | 116.02 | 527867 CUNNIGHM_S 6 230 527894 HOBBS_INT 6 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17807 | 116.35 | 527894 HOBBS_INT 6 230 527903 HOBBS_PLT3 1 18.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17821 | 116.23 | 527896 HOBBS_INT 7 345 3WXFMR HICO 68759-1 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 115.8 | 527965 KIOWA 7 345 528027 RDRUNNER 7 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 115.81 | 528015 PHANTOM 7 345 528027 RDRUNNER 7 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.11 | 528024 RR_SVC_HV 3 115 528021 RDRUNNR_SVC1 15.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.25 | 528024 RR_SVC_HV 3 115 528025 RDRUNNER 3 115 Z1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 115.81 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.08 | 528025 RDRUNNER 3 115 587990 GEN-2016-121 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.14 | 528222 CHINA_DRAW 3 115 528225 CD_SVC_HV 3 115 Z1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 115.82 | 528341 LE-SANANDRS3 115 528627 LE-TXACO_TP3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17807 | 116.06 | 528394 QUAHADA 3 115 528396 XTO_BIGEDDY3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.01 | 528552 OIL_CENTER 3 115 528554 COOPER_RNCH3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.02 | 528554 COOPER_RNCH3 115 528581 BYRD_TP 3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.05 | 528568 MONUMNT_TP 3 115 528581 BYRD_TP 3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.04 | 528596 CARDINAL 3 115 528605 TARGA 3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.06 | 528603 NA_ENRICH 3 115 528605 TARGA 3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.11 | 528617 LE-WAITS 2 69.0 528325 LE-WAITS 3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.03 | 528617 LE-WAITS 2 69.0 528714 LE-FORT_SW 2 69.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.1781 | 116.05 | 528618 LE-LOVINTON2 69.0 528334 LE-NRTH_INT3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.42 | 528626 LE-PLNSINT 2 69.0 526928 PLAINS_INT 3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.42 | 528626 LE-PLNSINT 2 69.0 528709 LE-PLNSGOAB2 69.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.05 | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.11 | 528669 LE-STKLDRTP2 69.0 528740 LE-PLANS_SW2 69.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.3 | 528709 LE-PLNSGOAB2 69.0 528740 LE-PLANS_SW2 69.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.05 | 528709 LE-PLNSGOAB2 69.0 528747 LE-ALLRED 2 69.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.03 | 528714 LE-FORT_SW 2 69.0 528718 LE-NEWTEX 2 69.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.11 | 528735 LE-PLAINSUB2 69.0 528740 LE-PLANS_SW2 69.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.03 | 528775 LE-ERF 3 115 528779 LE-TALLCOTN3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17798 | 115.79 | 530583 POSTROCK7 345 560082 G16-050-TAP 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 115.81 | 531213 SANTAFE3 115 531408 PIERCVL3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17807 | 116.04 | 531501 BUCKNER7 345 531502 CIMRRN 7 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17807 | 116.04 | 531502 CIMRRN 7 345 531503 CIMRRN 1 34.5 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17796 | 115.75 | 531510 HARBNGR3 115 3WXFMR HARBGR345 _1 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17807 | 116.06 | 532663 LEC U5 24.0 532854 LEC U5 6 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17815 | 116.04 | 532794 ROSEHIL7 345 560053 G15052_T 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17819 | 116.03 | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17807 | 116.06 | 532853 LAWHILL6 230 532854 LEC U5 6 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17807 | 116.01 | 539117 SPRVILL-EHVB 230 539695 SPEARVL6 230 Z1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17807 | 116.02 | 539803 IRONWOOD7 345 3WXFMR IRONWOOD MPT 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17808 | 116.13 | 542951 HAW G5 1 22.0 543665 HAWTHN5 161 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17808 | 116.17 | 542955 LAC G1 1 22.0 542981 LACYGNE7 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17807 | 116.15 | 542956 LAC G2 1 24.0 542981 LACYGNE7 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17806 | 116.2 | 542957 IAT G1 1 24.0 542982 IATAN 7 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17807 | 116.27 | 542962 IAT G2 1 24.5 542982 IATAN 7 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.03 | 542966 WGARDNR5 161 543105 BULLCRK5 161 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.18057 | 115.57 | 560022 CRAWFISH_DR 345 762216 G17-151TAP 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.18025 | 116.52 | 560022 CRAWFISH_DR 345 762467 G18-015-TAP 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 112.71 | 560022 CRAWFISH_DR 345 763087 GEN-2018-073 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.18137 | 116.84 | 560022 CRAWFISH_DR 345 763215 G18-092-TAP 345 2
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17798 | 115.8 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.45 | 560252 G10-14 345 560253 G10-14-1 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.18 | 560253 G10-14-1 115 560254 G10-14-SUB1 34.5 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.19 | 560253 G10-14-1 115 560255 G10-14-SUB2 34.5 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.04 | 560581 G06-44-2 34.5 523111 NOVUS1 3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.08 | 560582 G06-44-3 34.5 560577 G06-44 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.07 | 560583 G06-44-4 34.5 560577 G06-44 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 115.72 | 560757 ASGI13_02_1 69.0 560758 ASGI13_02_2 34.5 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 115.72 | 560757 ASGI13_02_1 69.0 562731 WHEATLAND 69.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 115.73 | 560763 ASGI13_03_1 115 560761 ASGI13_03_2 34.5 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.16 | 562015 FIREWHEEL1 34.5 523215 FREWHELCOL17 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.16 | 562016 FIREWHEEL2 34.5 523215 FREWHELCOL17 345 2
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 115.71 | 562323 AGI1202&1305 115 562324 AGI1202&1305 34.5 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 115.73 | 562727 LESBIA 115 562728 SANJONTAP 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 115.72 | 562728 SANJONTAP 115 562729 CAPROCKTAP1 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 115.72 | 562730 CAPROCKTAP2 69.0 562729 CAPROCKTAP1 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 115.72 | 562730 CAPROCKTAP2 69.0 562731 WHEATLAND 69.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.15 | 563171 G15082_2 34.5 563170 G15082_1 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 115.78 | P11:13.8:AEPW:COM1-1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 115.79 | P11:13.8:AEPW:COM2-1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 115.79 | P11:13.8:AEPW:COM3-1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 115.78 | P11:18:AEPW:WELSH1-1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 115.79 | P11:18:AEPW:WELSH3-1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 115.78 | P11:24:AEPW:PIRKEY 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 115.68 | P11:24:AEPW:SWS3-1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 115.74 | P11:24:AEPW:TURKCOAL
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17822 | 116.11 | P12:138:AEPW-OMPA:DUNCAN-4:OMDUNCN4
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.02 | P12:138:AEPW:112GORE4:L.E.S.-4
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17811 | 116.05 | P12:138:AEPW:112GORE4:SNYDER-4
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17811 | 116.05 | 5841_Dup1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17818 | 115.37 | 584560 GEN-2015-014 115 584561 G15-014XFMR1 34.5 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17817 | 116.08 | P12:138:AEPW:SANTAFE:DUNCAN-4
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.08 | 587991 G16-121XFMR1 34.5 587990 GEN-2016-121 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.01 | 588480 A16-010_SUB 115 3WXFMR A16-010_SUB 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17822 | 116.1 | P12:138:AEPW:DUNCAN-4:L.E.S.-4
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 115.46 | 588761 G17-033XFMR1 34.5 588760 GEN-2017-033 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 115.46 | 588765 G17-033XFMR2 34.5 588760 GEN-2017-033 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.02 | 588861 G17-047XFMR1 34.5 588860 GEN-2017-047 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17795 | 115.79 | P12:138:AEPW:ELKCTY-4:CLINTJC4
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.03 | 589381 G17-100XFMR1 34.5 589380 GEN-2017-100 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.07 | P12:138:AEPW:SHERID4:112GORE4
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17812 | 116.06 | P12:345:AEPW-OKGE:CLARKSV7:MUSKOGE7
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.18057 | 117.78 | P12:345:AEPW:L.E.S7:TERRYRD7
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.18057 | 117.77 | P12:345:AEPW:L.E.S7:TERRYRD7
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.18056 | 117.75 | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.18132 | 118.25 | P12:345:AEPW-OKGE:L.E.S.-7:GRACMNT7
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.18132 | 118.23 | P12:345:AEPW-OKGE:L.E.S.-7:GRACMNT7
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.18116 | 118.8 | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.08 | P22:345:AMMO::LABADIE:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.08 | P22:345:AMMO::LABADIE:2
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.09 | P22:345:AMMO::LABADIE:3
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.08 | P22:345:AMMO::LABADIE:4
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.07 | P22:345:AMMO::RUSHISLAND:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.06 | P22:345:AMMO::RUSHISLAND:2
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.1781 | 115.79 | P13:138-13.8:AEPW:COMANC-4_#2
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 115.8 | P13:138-13.8:AEPW:S.W.S.-4
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.1775 | 115.47 | P13:138-230:AEPW:ELKCTY-4
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.1781 | 115.79 | P13:138-24:AEPW:PIRKEY 4
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17814 | 115.69 | P13:138-24:AEPW:S.W.S.-4
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17811 | 115.75 | P13:138-24:AEPW:TURK 4
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17826 | 116.11 | P13:138-345:AEPW:L.E.S.-4_#2
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.1781 | 116.02 | P12:500:EES-EAI:KEO:WMPEHV
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17811 | 116.14 | P23:500:EES-EAI:KEO:B4941
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.1781 | 116.02 | P23:500:EES-EAI:KEO:B4931
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17811 | 116.13 | P23:500:EES-EAI:KEO:B4921
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.1781 | 116.07 | P23:500:EES-EAI:INDEP2:B6126
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.1781 | 116.06 | P23:500:EES-EAI:PD:INDEP2:LN:FK479
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17811 | 115.79 | P13:345-18:AEPW:WELSH 7_#1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17811 | 115.79 | P13:345-18:AEPW:WELSH 7_#3
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 115.79 | P13:69-13.8:AEPW:COMANC-2
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.08 | P11:024:DPC:ALMA2:6
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.04 | P11:18:ITCM:EMERYGT1:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.05 | P11:18:ITCM:EMERYGT2:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.05 | P11:161:ITCM:MGS CT1:1C
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.05 | P11:161:ITCM:MGS CT2:2C
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17807 | 116.06 | 652537 WHITE 3 345 659286 DEERCREK-BE3 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17808 | 116.02 | 652568 GROTONSOUTH7 115 659275 GROTON_G-BE7 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17807 | 116.06 | 659286 DEERCREK-BE3 345 3WXFMR DEERCRK KU1A 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.05 | 672601 BD 4 230 672306 BD 6G 18.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.05 | 672610 POPLAR 4 230 672310 POPLAR 1G 18.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.05 | 672610 POPLAR 4 230 672311 POPLAR 2G 18.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.04 | 672621 SHAND 4 230 672321 SHAND 1G 18.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.03 | 672649 CODETTE 4 230 672650 NIPAWIN 4 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.04 | 672696 BRADA 4 230 672699 NBEC 4 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.12 | P23:345:MDU::COYOTE::5707-5712-5715::::
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.3 | P23:345:MEC:CBEC 905
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.25 | P23:345:MEC:CBEC 908
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.1781 | 116.04 | P23:345:MEC:GDMEC 901
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.1781 | 116.04 | P23:345:MEC:GDMEC 902
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.06 | P23:345:MEC:GDMEC 908
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.17 | P23:345:MEC:RAUN 0180
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.24 | P23:345:MEC:RAUN 0210
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.18 | P23:345:MEC:LOUISA 954
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.1781 | 116.19 | P23:345:MEC:LOUISA 964
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.03 | P21:115:XEL:AUTO-SINGLE:CHEMOLT7:LSPOWER7:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.07 | P21:115:XEL:AUTO-SINGLE:COLVILL7:CANONFLSG7:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.03 | P21:115:XEL:AUTO-SINGLE:FARIBALTP7:FARIBALTGEN:Z
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.13 | P21:230:OTP:AUTO-SINGLE:SQBUTTE4:YNG24:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.12 | P23:345:OTP:CENTER 3:3215(1)
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.12 | P23:345:OTP:CENTER 3:3225(1)
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.06 | P12:230:UMZW:# 687 #: FT IN SD. FT-BG1 LINE FAULT
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.06 | P12:230:UMZW:# 3617 #: FT IN SD. FT-BG2 LINE FAULT
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 114.69 | 760494 GEN-2017-146 230 760498 G17-146-TAP 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 114.68 | 760495 G17-146-XFM1 34.5 760494 GEN-2017-146 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 115.46 | 761356 G17-239-XFMR 34.5 761355 GEN-2017-239 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 115.46 | 761359 G17-239-XFMR 34.5 761355 GEN-2017-239 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 115.63 | 761797 G17-187XFM1 34.5 761796 GEN-2017-187 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 115.63 | 761800 G17-187XFM2 34.5 761796 GEN-2017-187 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 110.67 | 762132 GEN-2017-158 230 763252 G18-099-XFM1 34.5 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 110.67 | 762132 GEN-2017-158 230 763255 G18-099-XFM2 34.5 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 111.27 | 762133 G17-158XFM1 34.5 762132 GEN-2017-158 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 111.27 | 762136 G17-158XFM2 34.5 762132 GEN-2017-158 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 113.54 | 762216 G17-151TAP 345 762217 GEN-2017-151 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.18057 | 116.85 | 762216 G17-151TAP 345 762467 G18-015-TAP 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 115.27 | 762218 G17-151XFM1 34.5 762217 GEN-2017-151 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 115.27 | 762221 G17-151XFM2 34.5 762217 GEN-2017-151 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 115.27 | 762224 G17-151XFM3 34.5 762217 GEN-2017-151 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 115.27 | 762227 G17-151XFM4 34.5 762217 GEN-2017-151 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 114.55 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 115.11 | 762461 G18-015-XFM1 34.5 762460 GEN-2018-015 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 115.11 | 762464 G18-015-XFM2 34.5 762460 GEN-2018-015 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17945 | 116.42 | 762467 G18-015-TAP 345 763215 G18-092-TAP 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 113.8 | 763087 GEN-2018-073 345 763088 G18-073-XFM1 34.5 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 114.78 | 763087 GEN-2018-073 345 763091 G18-073-XFM2 34.5 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 112.78 | 763120 GEN-2018-081 230 764011 G19-074-XFM1 34.5 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 112.92 | 763186 GEN-2018-089 230 763187 G18-089-XFM1 34.5 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 113.84 | 763208 GEN-2018-092 345 763215 G18-092-TAP 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 114.77 | 763208 GEN-2018-092 345 763220 G18-092-XFM1 34.5 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 114.77 | 763208 GEN-2018-092 345 763223 G18-092-XFM2 34.5 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 112.23 | 763241 GEN-2018-097 230 763242 G18-097-XFM1 34.5 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 113.15 | 763241 GEN-2018-097 230 763296 G18-111-XFM1 34.5 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 112.51 | 763241 GEN-2018-097 230 763307 G18-112-XFM1 34.5 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 112.51 | 763241 GEN-2018-097 230 763310 G18-112-XFM2 34.5 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 112.23 | 763241 GEN-2018-097 230 763395 G18-124-XFM1 34.5 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 112.23 | 763241 GEN-2018-097 230 763398 G18-124-XFM2 34.5 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 115.66 | 763318 GEN-2018-115 345 763319 G18-115-XFM1 34.5 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 112 | 763483 GEN-2019-003 230 763484 G19-003-XFM1 34.5 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 114.56 | 763483 GEN-2019-003 230 763605 G19-021-XFM1 34.5 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 115.46 | 763516 GEN-2019-011 345 763517 G19-011-XFM1 34.5 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 115.55 | 763879 GEN-2019-056 115 763880 G19-056XFM1 34.5 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17775 | 116.19 | P42:345:OKGE:SB_BVTY7305
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17793 | 115.75 | P23:345:WERE:BUFF_345-534::
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17793 | 115.75 | P23:345:WERE:BUFF_345-543::
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17805 | 116.23 | P23:345:WERE:JEC_345-15::
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17804 | 116.18 | P23:345:WERE:JEC_345-16::
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17805 | 116.22 | P23:345:WERE:JEC_345-19::
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17805 | 116.22 | P23:345:WERE:JEC_345-20::
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.39 | P23:345:WERE:WOLF_345-50::
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.39 | P23:345:WERE:WOLF_345-60::
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.1781 | 115.8 | P42:345:AEPW:WELSH CB 10620 NBTB+FAULT
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.1781 | 115.79 | P41:345:AEPW:WELSH CB 10630 NBTB+FAULT
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 115.79 | P41:345:AEPW:WELSH CB 11670 NBTB+FAULT
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17821 | 115.78 | P41:345:AEPW:WELSH CB 11680 NBTB+FAULT
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 115.78 | P41:345:AEPW:WELSH CB 12540 NBTB+FAULT
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.18116 | 117.33 | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.18165 | 118.58 | P42:345:AEPW:LAWTON EASTSIDE CB 3413A NBTB+FAULT
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.18199 | 118.94 | P42:345:AEPW:LAWTON EASTSIDE CB 3425A NBTB+FAULT
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.18129 | 118.96 | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.18057 | 117.77 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.18057 | 117.77 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.18057 | 117.74 | P42:345:AEPW:TERRYRD_CB_3421A_NBTB
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17808 | 116.18 | P23:345:KCPL:LACYGNE_R2-5::LACYGU2-LACYGNE-STILWELL
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17808 | 115.82 | P45:345:UMZW:# 1328 #: GI IN NE.
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.1781 | 115.8 | P23:345:AEPW:WELSH CB 10620 NBTB
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.1781 | 115.79 | P23:345:AEPW:WELSH CB 10630 NBTB
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 115.79 | P23:345:AEPW:WELSH CB 11670 NBTB
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17821 | 115.78 | P23:345:AEPW:WELSH CB 11680 NBTB
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 115.78 | P23:345:AEPW:WELSH CB 12540 NBTB
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.18116 | 117.74 | P23:345:AEPW:OKLAUNION CB 3401A NBTB
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.18165 | 118.58 | P23:345:AEPW:LAWTON EASTSIDE CB 3413A NBTB
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.18199 | 118.94 | P23:345:AEPW:LAWTON EASTSIDE CB 3425A NBTB
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.18129 | 118.96 | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.18057 | 117.77 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.18057 | 117.77 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.18057 | 117.74 | P23:345:AEPW:TERRYRD_CB_3421A_NBTB
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.05 | P11:161:GMO:DOGWOOD_COMBINED_CYCLE_UNIT_OUTAGE
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.06 | P11:115:SUNC:GARDENCITY_S2:97:531459(2)
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17795 | 115.77 | P12:345:PWT:BUFF-THIS_345_1::
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17795 | 115.77 | P12:345:PWT:BUFF-THIS_345_2::
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17796 | 115.83 | P12:345:PWT:THIS-DGRS_345_1::FUTURE
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17796 | 115.83 | P12:345:PWT:THIS-DGRS_345_2::FUTURE
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17819 | 116.06 | P12:069:WFEC:ANADRKO_WATONGA
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.18074 | 117.97 | P23:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.1833 | 120.4 | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.18074 | 117.97 | P42:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB+FAULT
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.1833 | 120.4 | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17341 | 114.13 | P42:345:OKGE:SB_BVTY7315_PRE19S
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17778 | 115.62 | P23:345:SUNC:MO_BRK182
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17778 | 115.62 | P23:345:SUNC:MO_BRK382
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17773 | 115.79 | P23:345:SUNC:MO_BRK188
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17936 | 116.06 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.1781 | 115.79 | P12:138-13.8:AEPW:COMANC-4_#1
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.1775 | 115.47 | P12:230:AEPW:ELKCITY6:CHISHOLM6
Thermal | 05ALL | 1 | 26SP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17929 | 116.62 | P12:230:AEPW:SWEETWT6:CHISHOLM6
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997713 ABBXNL844501 230 1 |  | 553 | 0.15164 | 157.44 | 525531 TOLK 6 230 3WXFMR TOLK 6 2
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.09301 | 116.18 | P23:345:KCPL-WERE:237LACYGNE_R1-6::LACYGU1-LACYGNE-NEOSHO
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.09298 | 116.06 | P11:230:WERE:LECU5_GEN::
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.09299 | 116.08 | P11:161:GMO:DOGWOOD_COMBINED_CYCLE_UNIT_OUTAGE_1_1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 116.02 | P11:20:KACY:NEARMAN N1::N1 OUT OF SERVICE:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.09298 | 116.02 | P12:69:KACY:NMGEN-NMISOBUS::NEARMAN N1-NM ISOBUS OPEN:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.09298 | 116.02 | P13:20-161:KACY:NEARMAN5-NMISOBUS:NAMEPLATE:NEARMAN N1 GSU:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.09298 | 116.02 | P21:20:KACY:546702NMGENN1-546703NMISOBUSC1::::
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 116.23 | P11:115:SPS:HOBBS1&3:145MW::::
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.09306 | 114.72 | P11:115:SPS:MUSTANG1&3:153MW::::
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.09221 | 118.23 | P12:230:SPS:K37::1_TOLK_LAMB:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.09326 | 116.06 | P12:230:SPS:K43::1_PRNGLE_HARR_E:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.09304 | 115.81 | P12:230:SPS:K44::1_EPLNT_HARRW:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.09418 | 116.22 | P12:115:SPS:T04::1_TRBLNC_CASTRO:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.09326 | 116.02 | P12:115:SPS:T06::1_SPRMN_PRNGLE:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 116.5 | P12:115:SPS:T21::1_GRSSLND_GRAHAM:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 116.05 | P12:115:SPS:T24B::1_RSWLL_BRSHRF:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 116.05 | P12:115:SPS:T26::1_CHAVES_RSWLCTY:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.09148 | 116.45 | P12:115:SPS:T28A::1_LAMTON_PLANTX:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.09375 | 116.02 | P12:115:SPS:T29::1_LAMTON_HALECTR:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.09403 | 117.27 | P12:115:SPS:T30::1_LAMB_HOCKLY:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.09403 | 116.37 | P12:115:SPS:T31::1_HOCKLY_SUNDWN:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.09303 | 116.06 | P12:115:SPS:T35::1_TERRY_YOAKUM:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.09299 | 116.78 | P12:115:SPS:T45::1_NORRIS_OASIS:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.09303 | 115.82 | P12:115:SPS:T57::1_MUSTG_SEGRVS:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.09275 | 116.03 | P12:115:SPS:T58::1_HERFRD_CARGIL:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.09275 | 116.57 | P12:115:SPS:T59::1_CARGIL_CURRY:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 116.02 | P12:115:SPS:T64::1_RNDALL_PULLMN:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.09519 | 116.38 | P12:115:SPS:T67::1_HAPPY_KRESS:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.09313 | 115.77 | P12:115:SPS:T68::1_TUCO_FLOYD:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.09305 | 115.81 | P12:115:SPS:T69::1_LUBBE_CROSBY:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 116.02 | P12:115:SPS:T70::1_COLTR_S_GORG:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.09299 | 116.63 | P12:115:SPS:T71::1_CRLSLE_YUMA:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.09336 | 116.1 | P12:115:SPS:T81::1_COX_FLOYD:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 116.26 | P12:115:SPS:T83::1_SP-FKFD_ALLEN:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.09303 | 116.44 | P12:115:SPS:T89::1_DC_N_HIGG:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 116.07 | P12:115:SPS:T91::1_HIGG_RUSSELL:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.09307 | 116.02 | P12:115:SPS:V01::1_MOOREW_RVRVIEW:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.09331 | 116.07 | P12:115:SPS:V04::1_EPLANT_RNDALL:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.0931 | 116.06 | P12:115:SPS:V07::1_COX_HALECTR:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.09279 | 116.23 | P12:115:SPS:V09::1_HALECTR_PLANTX:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.09303 | 116.21 | P12:115:SPS:V12::1_PLANTX_BAILEY:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 116.03 | P12:115:SPS:V15::1_TUCO_INDANA:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.09297 | 116.16 | P12:115:SPS:V24::1_WOLFTH_TERRY:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.0931 | 116.07 | P12:115:SPS:V26::1_RSWLL_EDDY_N:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 116.4 | P12:115:SPS:V33::1_LUBBS_LYNN:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.09152 | 117.14 | P12:115:SPS:V37::1_CASTRO_PLANTX:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 116.05 | P12:115:SPS:V44::1_COLTR_OWENS:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 116.16 | P12:115:SPS:V46::1_ALLEN_WHEELCK:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.09302 | 116.5 | P12:115:SPS:V49::1_YOAKUM_SHLCO2:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.09331 | 116.68 | P12:115:SPS:V55::1_SUNDWN_TERRY:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.09321 | 116.59 | P12:115:SPS:V56::1_COCHRAN_SUNDWN:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 116.09 | P12:115:SPS:V62::1_CRLSLE_INDANA:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.09294 | 116.07 | P12:115:SPS:V78::2_CURRY_RSVLT:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.09303 | 116.19 | P12:115:SPS:V81::1_LE-WAIT_LE-LVN:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 116.06 | P12:115:SPS:V95::1_DC_N_SHLCO2:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 116.02 | P12:115:SPS:W11::1_DC_S_SMINLE:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 116.03 | P12:115:SPS:W12::1_SMINLE_DOSS:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 116.1 | P12:115:SPS:W14::1_SMINLE_GAINES:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 116.03 | P12:115:SPS:W26::1_CUNGHM_OILCNTR:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 116.61 | P12:115:SPS:W32::1_PRMTR_FE-CLSIN:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.09302 | 116.26 | P12:115:SPS:W35::1_GAINES_JNSDRW:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.094 | 116.59 | P12:115:SPS:W40::1_WCANYON_TRBLNC:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.09436 | 116.11 | P12:115:SPS:W52::1_NEWHART_KRESS:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 116.67 | P12:115:SPS:W58::1_NORTON_LOPEZ:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 116.25 | P12:115:SPS:W59::1_LOPEZ_CMPBLL:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.09299 | 116.55 | P12:115:SPS:W62::1_PLSTHL_CURRY:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.09312 | 116.07 | P12:115:SPS:W63::1_PLSTHL_CURRY:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 116.36 | P12:115:SPS:W64::1_PLSTHL_FE-CLV:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.09299 | 116.57 | P12:115:SPS:W65::1_PLSTHL_CURRY:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 116.23 | P12:115:SPS:W66::1_PORTA_GREYHUND:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.09299 | 116.02 | P12:115:SPS:W76::1_QUAHA_PCA:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.094 | 116.1 | P12:115:SPS:W77::1_RNDAL_WCANYON:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 116.07 | P12:115:SPS:W99::1_CAPITAN_CHAVES:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 116.05 | P12:115:SPS:U03::1_CARDNL_NEF:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.09301 | 116.53 | P12:115:SPS:U14::1_DC_STH_INKBSN:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.09303 | 116.47 | P12:115:SPS:V15::1_INKBSN_LE-WAT:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.09304 | 116.15 | P12:115:SPS:U16::1_BSHLND_OUTPST:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.09304 | 116.16 | P12:115:SPS:U17::1_COLTR_OUTPST:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.09315 | 116.26 | P12:115:SPS:U19::1_DEAN_PLAINS:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.09304 | 116.07 | P12:115:SPS:U23::1_COLTR_HILSDE:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.08993 | 124.36 | P42:345:SPS:YOAKUM:J18####:SLG1:EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.08993 | 124.36 | P43:345:SPS:YOAKUM:TF#####:SLG:EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.08993 | 124.36 | P42:345:SPS:YOAKUM:J17####:SLG:EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.08993 | 124.36 | P42:345:SPS:YOAKUM:J18####:SLG2:EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.09299 | 116.06 | P11:18:HAST:::EGYCTR2G WEC2_LOSS OF WEC 2 GEN_:HV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.09299 | 116.06 | P13:18-115:HAST:::EGYCNTR7 XFMR G2WEC 2 GSU_:HV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.09299 | 116.08 | P11:161:GMO:DOGWOOD-COMBINED-CYCLE-UNIT-OUTA:::HV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.09301 | 116.18 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.09298 | 116.18 | P23:345:KCPL:LACYGNE-R2-5:::EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.09296 | 116.23 | P11:230:WERE:JECU1-GEN:::HV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.09298 | 116.06 | P11:230:WERE:LECU5-GEN:::HV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.09296 | 116.23 | P11:345:WERE:JECU2-GEN:::EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.09296 | 116.22 | P11:345:WERE:JECU3-GEN:::EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 116.4 | P11:345:WERE:WOLFU1-GEN:::EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.09285 | 115.77 | P12:345:PWT:BUFF-THIS-345-1:::EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.09285 | 115.77 | P12:345:PWT:BUFF-THIS-345-2:::EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.09284 | 115.75 | P23:345:WERE:BUFF-345-534:::EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.09284 | 115.75 | P23:345:WERE:BUFF-345-543:::EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.09296 | 116.23 | P23:345:WERE:JEC-345-15:::EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.09294 | 116.18 | P23:345:WERE:JEC-345-16:::EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.09296 | 116.22 | P23:345:WERE:JEC-345-19:::EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.09296 | 116.22 | P23:345:WERE:JEC-345-20:::EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.09299 | 116.39 | P23:345:WERE:WOLF-345-50:::EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 116.39 | P23:345:WERE:WOLF-345-60:::EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 116.34 | P11:022:NPPD:COOPER1G:1:983:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.09295 | 116.33 | P11:023:NPPD:GENTLM1G:1:757:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.09295 | 116.35 | P11:024:NPPD:GENTLM2G:2:757:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.09299 | 116.01 | P11:161:OPPD:N OMA 5G:LT::HV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.09299 | 116.01 | P11:161:OPPD:N OMA 5G:::HV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.09296 | 116.2 | P13:345:OPPD:NEBCTY1G:::EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.09295 | 116.22 | P13:345:OPPD:NEBCTY2G:::EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.09299 | 116.01 | P13:161:OPPD:N OMA 5G:::HV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 116.22 | P22:345:OPPD:S3458 NEBCTY1G:LT::EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.09296 | 116.2 | P22:345:OPPD:S3458 NEBCTY1G:::EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 116.25 | P22:345:OPPD:S3458 NEBCTY2G:LT::EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.09295 | 116.22 | P22:345:OPPD:S3458 NEBCTY2G:::EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 116.22 | P23:345:OPPD:S3458 NEBCTY1G:LT::EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.09296 | 116.2 | P23:345:OPPD:S3458 NEBCTY1G:::EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 116.25 | P23:345:OPPD:S3458 NEBCTY2G:LT::EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.09295 | 116.22 | P23:345:OPPD:S3458 NEBCTY2G:::EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 115.8 | P12:115:SUNC:PLYMELL-PIERCEVILLE:::HV::
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.09298 | 116.06 | P11:018:UMZB:# 5 #:: DCS IN SD. DEERCREEK_MV::
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.09299 | 116.03 | P11:022:UMZB:# 15 #:: LO IN ND. LELAND OLDS 1_MV::
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.09298 | 116.07 | P11:020:UMZB:# 16 #:: LO IN ND. LELAND OLDS 2_MV::
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.09297 | 116.14 | P11:023:UMZB:# 31 #:: AVS IN ND. ANTELOPE VALLEY 1_MV::
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.09297 | 116.14 | P11:023:UMZB:# 32 #:: AVS IN ND. ANTELOPE VALLEY 2_MV::
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.09294 | 116.33 | P11:024:UMZB:# 33 #:: LRS IN WY. LARAMIE RIVER STATION 1_MV::
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 116.06 | P12:230:UMZW:# 687 #:: FT IN SD. FT-BG1 BRANCH FAULT:HV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 116.06 | P12:230:UMZW:# 3617 #:: FT IN SD. FT-BG2 BRANCH FAULT:HV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 116.06 | P12:230:UMZW:# 4038 #:: BG-FT IN SD. FAULT FOR TRANSMISSION CIRCUIT (BG-FT).:HV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 116.06 | P12:230:UMZW:# 4039 #:: BG-FT IN SD. FAULT FOR TRANSMISSION CIRCUIT (BG-FT).:HV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 116.03 | P13:230:UMZW:# 5135 #:: OA IN SD. FAULT ON TRANSFORMER (2).:HV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 116.03 | P13:230:UMZW:# 5136 #:: OA IN SD. FAULT ON TRANSFORMER (3).:HV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.09298 | 115.82 | P23:345:UMZW:# 2423 #:: GI IN NE. GI 1596 BKR FAULT:EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.09298 | 115.82 | P23:345:UMZW:# 2426 #:: GI IN NE. GI 1592 BKR FAULT:EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.09298 | 115.82 | P23:345:UMZW:# 2432 #:: GI IN NE. GI 1092 BKR FAULT:EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.09298 | 115.82 | P23:345:UMZW:# 2440 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1092 STUCK BKR:EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.09298 | 115.82 | P23:345:UMZW:# 2444 #:: GI IN NE. GI-SWEET BRANCH FAULT & GI 1596 STUCK BKR:EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.09298 | 115.82 | P23:345:UMZW:# 2446 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1196 STUCK BKR:EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.09298 | 115.82 | P42:345:UMZW:# 2413 #:: FT2 IN SD. FT2-LO2 BRANCH FAULT & FT2 2992 STUCK BKR:EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.09298 | 115.82 | P42:345:UMZW:# 2415 #:: FT2 IN SD. FT2-GI BRANCH FAULT & FT2 3392 STUCK BKR:EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.09303 | 115.74 | P11:138:WFEC:HUGO1:465MW :::
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.09298 | 116.02 | P11:138:WFEC:MORLND2:132MW:::
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.09298 | 116.03 | P11:138:WFEC:MORLND3:149MW :::
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.09308 | 116.06 | P12:138:WFEC:ANADRKO_CLVLND::::
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.09302 | 116.06 | P12:345:OKGE-AEPW:BKRBKR12::::
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.09336 | 116.18 | P12:345:OKGE:BKRBKR21::::
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.09355 | 116.26 | P12:345:OKGE:BKRBKR24::::
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.09544 | 117.75 | P12:345:OKGE-AEPW:BKRBKR25::::
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.09268 | 115.72 | P12:345:OKGE:BKRBKR336::::
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.09268 | 115.72 | P12:345:OKGE:BKRBKR336_2::::
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.09612 | 118.25 | P12:345:OKGE-AEPW:BKRBKR366::::
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.09612 | 118.23 | P12:345:OKGE-AEPW:BKRBKR366::::
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.09506 | 117.15 | P12:345:OKGE:BKRBKR367::::
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.09272 | 115.72 | P12:345:OKGE:BKRBKR4193::::
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.09272 | 115.72 | P12:345:OKGE:BKRBKR4194::::
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 116.02 | P12:345:OKGE:BKRBKR4195::::
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.09261 | 115.76 | P12:345:OKGE-SPS:BKRBKR4201::::
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.09261 | 115.76 | P12:345:OKGE-SPS:BKRBKR4202::::
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.09309 | 116.03 | P12:345:OKGE:BKRBKR421::::
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.09265 | 115.6 | P12:345:OKGE:BKRBKR443NEW::::
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.09265 | 115.6 | P12:345:OKGE:BKRBKR443NEW2::::
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.09283 | 115.79 | P12:345:OKGE-ITC:BKRBKR502::::
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.09283 | 115.79 | P12:345:OKGE-ITC:BKRBKR503::::
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.09287 | 115.83 | P12:345:OKGE-ITC:BKRBKR502_1::::
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.09287 | 115.83 | P12:345:OKGE-ITC:BKRBKR503_1::::
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.09293 | 116.33 | P12:345:OKGE:BKRBKR604::::
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.09292 | 116.37 | P12:345:OKGE:BKRBKR604_2::::
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.09301 | 115.82 | P11:345:OKGE:BKRBKR_GSU07::::
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.09302 | 115.81 | P11:345:OKGE:BKRBKR_GSU08::::
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.09302 | 115.8 | P11:138:OKGE:BKRBKR_GSU21::::
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.09298 | 115.83 | P12:138:OKGE:BKRBKR85_MOS1::::
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.09265 | 116.13 | P42:345:OKGE:SB_ARIA7381::::
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.09967 | 120.17 | P42:345:OKGE:SB_BVTY7387::::
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.0931 | 116.02 | P41:345:OKGE:SB_REUD7381::::
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.09309 | 116.03 | P41:345:OKGE:SB_REUD7383::::
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.0931 | 116.06 | P41:345:OKGE:SB_REUD7385::::
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.09313 | 116.06 | P42:345:OKGE:SB_REUD7389::::
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.09298 | 116.05 | P11:115:SUNC:GARDENCITY_S2:103:531459(2):HV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.09298 | 116.07 | P11:115:SUNC:FORTDDODGE_4:157:539670(4):HV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 116.04 | P11:345:599:CIMARRON1WIND:200:531603(1):EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 116.47 | P13:115:SUNC:HOLCOMB_GSU:::HV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.09298 | 116.05 | P13:115:SUNC:S2_GSU:::HV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.09298 | 116.07 | P13:115:SUNC:FORTDODGE_GSU:::HV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.09297 | 116.04 | P23:345:SUNC:BU_BRK682:::EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 116.14 | 300003 1THLG3 24.0 301503 7THOMHLGSU3 345 3
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 116.01 | 300007 1NM G2 22.0 301537 7NEWMADGSU2 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 116.01 | 300046 7NEWMAD 345 301537 7NEWMADGSU2 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 116.14 | 300049 7THOMHL 345 301503 7THOMHLGSU3 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 116.08 | P11:20:AMMO:1LAB�� G1:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 116.08 | P11:20:AMMO:1LAB�� G2:2
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 116.27 | P11:345:AMMO::CALLAWAY:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 116.08 | P11:345:AMMO::LABADIE:3
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 116.08 | P11:345:AMMO::LABADIE:4
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 116.07 | P11:345:AMMO::RUSHISLAND:U1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 116.07 | P11:345:AMMO::RUSHISLAND:U2
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 116.06 | P11:138:AMMO::SIOUX:2
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 115.83 | P11:24:CLEC::G1DOLHIL:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 116.06 | P12:765:AEP:AEP ROCKP-AEP JEFF 765
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 115.78 | P11:HV:EES::PIRKEY 1:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 115.79 | P11:EHV:EES::WELSH3-1:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 115.74 | P11:HV:EES::TURKCOAL:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 116.25 | P12:EHV:EES::7CALAWY 1:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.09301 | 116.02 | 338056 CHALKBLUFFPV 500 338162 8W.MEMPHIS% 500 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.09301 | 115.75 | P12:HV:EES::TURK 4%:1(1)
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.09302 | 115.79 | P12:EHV:EES::WELSH 7:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.09302 | 115.79 | P12:EHV:EES::WELSH 7:1(1)
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.09301 | 115.79 | P12:HV:EES::PIRKEY 4:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.09302 | 116.06 | P12:EHV:EES::CLARKSV7!:MUSKOGE7!:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 116.06 | 344011 7HUGHES 345 344012 7HPW-N 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 116.08 | 344884 7LABADIE1 345 344894 1LAB G1 20.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 116.08 | 344885 7LABADIE2 345 344895 1LAB G2 20.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 116.08 | 344886 7LABADIE3 345 344896 1LAB G3 20.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 116.08 | 344887 7LABADIE4 345 344897 1LAB G4 20.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 116.07 | 345667 7RUSH 1 345 345670 1RUSH G1 18.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 116.06 | 345668 7RUSH 2 345 345671 1RUSH G2 18.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 116.05 | 345755 4SIOUX 1 138 345756 1SIOUX 1 18.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 116.05 | 345764 4SIOUX 2 138 345765 1SIOUX 2 18.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 116.12 | P12:345:MDU::CENTER:COYOTE:1::::
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 116.12 | P13:345:MDU:COYOTE GSU LOSS:COYOTE::1::::
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 116.03 | P11:345:MEC:GDMEC CT1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 116.03 | P11:345:MEC:GDMEC CT2
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 116.14 | P11:345:MEC:GDMEC ST
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 116.35 | P11:345:MEC-NPPD:COOPER 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 116.24 | P11:24:XEL:AUTO-SINGLE:SHERC31G:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 116.24 | P11:24:XEL:AUTO-SINGLE:SHERC32G:2
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 116.33 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 116.16 | P11:20:XEL:AUTO-SINGLE:PRIS31G:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 116.16 | P11:20:XEL:AUTO-SINGLE:PRIS32G:2
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 116.2 | P11:22:XEL:AUTO-SINGLE:MNTCE31G:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 116.16 | P11:20:XEL:AUTO-SINGLE:KING31G:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 116.02 | P11:13:XEL:AUTO-SINGLE:HBRS73G:9
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 116.02 | P11:18:XEL:AUTO-SINGLE:BLKD76G:6
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 116.22 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 116.22 | P11:22:GRE:AUTO-SINGLE:GRE-COAL42G:2
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 116.14 | P11:24:OTP:AUTO-SINGLE:BIGSTN1G:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 116.15 | P11:20:OTP:AUTO-SINGLE:CENTER2G:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 116.05 | P11:22:OTP:AUTO-SINGLE:CENTER1G:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 116.13 | P11:24:OTP:AUTO-SINGLE:COYOTE1G:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 116.05 | P11:24:DPC:AUTO-SINGLE:GENOA53G:3
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 116.03 | P12:115:XEL:AUTO-SINGLE:CHEMOLT7:LSPOWER7:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 116.07 | P12:115:XEL:AUTO-SINGLE:COLVILL7:CANONFLSG7:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 116.03 | P12:115:XEL:AUTO-SINGLE:FARIBALTP7:FARIBALTGEN:Z
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 116.13 | P12:230:OTP:AUTO-SINGLE:SQBUTTE4:YNG24:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 116.22 | P13:24-345:XEL:AUTO-SINGLE:SHERC31G:SHERCO3:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 116.22 | P13:24-345:XEL:AUTO-SINGLE:SHERC32G:SHERCO3:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 116.3 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 116.16 | P13:20-345:XEL:AUTO-SINGLE:PRIS31G:PRISLD3:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 116.16 | P13:20-345:XEL:AUTO-SINGLE:PRIS32G:PRISLD3:2
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 116.2 | P13:22-345:XEL:AUTO-SINGLE:MNTCE31G:MNTCELO3:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 116.15 | P13:20-345:XEL:AUTO-SINGLE:KING31G:ASKING3:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 116.02 | P13:13-115:XEL:AUTO-SINGLE:HBRS73G:HIBRDGE7:9
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 116.2 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL41G:GRE-COALCR4:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 116.2 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL42G:GRE-COALCR4:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 116.13 | P13:230-24:OTP:AUTO-SINGLE:BIGSTON4:BIGSTN1G:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 116.13 | P13:20-230:OTP:AUTO-SINGLE:CENTER2G:YNG24:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 116.04 | P13:22-230:OTP:AUTO-SINGLE:CENTER1G:CENTER4:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 116.12 | P13:24-345:OTP:AUTO-SINGLE:COYOTE1G:COYOTE3:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 116.05 | P13:24-161:DPC:AUTO-SINGLE:GENOA53G:GENOA5:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 116.07 | P13:24-161:DPC:AUTO-SINGLE:JPM:ALMA5:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.09301 | 116.02 | 38203 J1819 POI 500 337957 8KEO% 500 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.09301 | 116.02 | 38203 J1819 POI 500 338056 CHALKBLUFFPV 500 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 116.13 | P11:115:XEL:RIV COMBINE CYCLE
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 116.04 | P12:115:XEL:BDS #2 5
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 116.04 | P11:115:XEL:HBR #6
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 116.04 | P11:115:XEL:HBR #7
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 116.16 | P11:115:XEL:HBR #6 7 8
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 116.16 | P23:345:XEL:8H14 PRI
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 116.16 | P23:345:XEL:8H17 PRI AS
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 116.3 | P23:345:XEL:8N28 SHC
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 116.22 | P23:345:XEL:8N22 SHC
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 116.22 | P23:345:XEL:8N17 SHC
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 116.21 | P23:345:XEL:8N8 MNN
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 116.15 | P23:345:XEL:8P1 KING
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 116.15 | P23:345:XEL:8P2 KING
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 116.04 | P23:115:XEL:5P147 IVH AS
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 116.03 | P11:18:ALTW:AUTO-SINGLE:EMERYST1:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 116.03 | P11:22:ALTW:AUTO-SINGLE:LANS54G:4
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 116.17 | P11:22:ALTW:AUTO-SINGLE:ARNOLD1G:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 116.2 | P11:24:ALTW:AUTO-SINGLE:OTTUMW1G:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 116.03 | P13:18-161:ALTW:AUTO-SINGLE:EMERYST1:EMERY5:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 116.03 | P13:22-161:ALTW:AUTO-SINGLE:LANS54G:LANSINGL15:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 116.16 | P13:22-161:ALTW:AUTO-SINGLE:ARNOLD1G:ARNOLD5:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 116.19 | P13:24-161:ALTW:AUTO-SINGLE:OTTUMW1G:OTTUMWA5:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 116.27 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 116.34 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 116.19 | P11:22:MEC:AUTO-SINGLE:NEAL3G:3
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 116.26 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 116.19 | P11:24:MEC:AUTO-SINGLE:LOUIS31G:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 116.25 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 116.3 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 116.17 | P13:345-22:MEC:AUTO-SINGLE:RAUN3:NEAL3G:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 116.24 | P13:345-24:MEC:AUTO-SINGLE:RAUN3:NEAL4G:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 116.18 | P13:345-24:MEC:AUTO-SINGLE:LOUISA3:LOUIS31G:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.09296 | 116.23 | P11:230:WERE:JECU1_GEN::
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.09296 | 116.23 | P11:345:WERE:JECU2_GEN::
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.09296 | 116.22 | P11:345:WERE:JECU3_GEN::
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 116.4 | P11:345:WERE:WOLFU1_GEN::
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 116.03 | 511435 SNYDER-4 138 588779 TAP_G17-036 138 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.09307 | 116.03 | 511453 DUNCAN-4 138 511552 DUNCHERTP4 138 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.09307 | 116.03 | 511455 D.E.S.-4 138 511552 DUNCHERTP4 138 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.09307 | 116.02 | 511455 D.E.S.-4 138 529344 OMDUNE-4 138 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 114.98 | 511456 O.K.U.-7 345 588760 GEN-2017-033 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.09598 | 117.74 | 511456 O.K.U.-7 345 763215 G18-092-TAP 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.09611 | 118.31 | 511468 L.E.S.-7 345 762467 G18-015-TAP 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.09511 | 117.72 | 511468 L.E.S.-7 345 763215 G18-092-TAP 345 2
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 115.66 | 511468 L.E.S.-7 345 763318 GEN-2018-115 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 116.05 | 511488 112GORE4 138 511510 LAIRGST4 138 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.09312 | 116.11 | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 116.04 | 511500 CACHE4 138 511510 LAIRGST4 138 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 116.03 | 511500 CACHE4 138 588779 TAP_G17-036 138 2
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.09458 | 116.06 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.0869 | 113.09 | 511553 CHISHOLM7 345 523961 POTTER_CO 7 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.0869 | 113.09 | 511553 CHISHOLM7 345 523961 POTTER_CO 7 345 2
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.09007 | 115.5 | 511553 CHISHOLM7 345 755000 WWDBORDT 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.09332 | 116.14 | 511557 CHISHOLM6 230 3WXFMR CHISHOLM6 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.09314 | 116.02 | 514801 MINCO 7 345 555234 NSUB345 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.09227 | 115.63 | 515375 WWRDEHV7 345 755000 WWDBORDT 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.09967 | 120.2 | 515458 BORDER 7 345 560022 CRAWFISH_DR 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.09967 | 120.15 | 515458 BORDER 7 345 755000 WWDBORDT 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.09309 | 116.02 | 515543 RENFROW7 345 763421 G18-128-TAP 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.09297 | 116.12 | 515618 BALKOW 7 345 3WXFMR BALKOW 7 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.09297 | 116.13 | 515618 BALKOW 7 345 3WXFMR BALKOW 7 1_Dup1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.09306 | 116.04 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.09292 | 116.39 | 515634 PALDR1W7 345 3WXFMR PALO2 _1 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 116.13 | 515677 BADGER 7 345 563170 G15082_1 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.09296 | 116.01 | 521017 ONEY 4 138 521089 WASHITA4 138 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 116.02 | 522800 MU-TULIA 3 115 525179 TULIA_TP 3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 116.16 | 522892 MU-BROWNFLD2 69.0 526761 BROWNFLD_TP2 69.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 116.03 | 523090 TEXAS_CNTY 3 115 589380 GEN-2017-100 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.09296 | 116.16 | 523093 HITCHLAND 3 115 523174 GOODWELLWND3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 116.34 | 523097 HITCHLAND 7 345 523112 NOVUS1 7 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 116.4 | 523097 HITCHLAND 7 345 523215 FREWHELCOL17 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.09094 | 114.83 | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.08136 | 112.81 | 523097 HITCHLAND 7 345 523961 POTTER_CO 7 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 116.45 | 523097 HITCHLAND 7 345 560252 G10-14 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 116.01 | 523099 TC-DRYTRLS 3 115 588480 A16-010_SUB 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 116.23 | 523112 NOVUS1 7 345 3WXFMR NOVUS XF2 2
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 116.04 | 523112 NOVUS1 7 345 3WXFMR XIANA2011198 _1 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.09298 | 116.02 | 523118 BUFF_DUNES 7 345 523853 FINNEY 7 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 116.02 | 523120 COLE 3 115 588860 GEN-2017-047 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.09298 | 116.04 | 523172 GWELL_COLL11 34.5 523174 GOODWELLWND3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.09298 | 116.04 | 523173 GWELL_COLL21 34.5 523174 GOODWELLWND3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.09311 | 116.01 | 523221 XIT_INTG 6 230 3WXFMR SIEM_T126401 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.09326 | 116.07 | 523267 PRINGLE 6 230 3WXFMR ENRCO13617-1 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.09326 | 116.06 | 523267 PRINGLE 6 230 523979 HARRNG_EST 6 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.09377 | 116.2 | 523309 MOORE_CNTY 6 230 523323 MCDWL_CREEK6 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.09341 | 116.12 | 523323 MCDWL_CREEK6 230 523959 POTTER_CO 6 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.09293 | 116.45 | 523959 POTTER_CO 6 230 524010 ROLLHILLS 6 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.09775 | 117.19 | 523959 POTTER_CO 6 230 524267 BUSHLAND 6 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.12249 | 118.35 | 523959 POTTER_CO 6 230 525461 NEWHART 6 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.12536 | 121.11 | 523961 POTTER_CO 7 345 3WXFMR WAUK 90343-A 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.09326 | 115.74 | 523978 HARRNG_MID 6 230 523979 HARRNG_EST 6 230 @1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.09304 | 116.16 | 524267 BUSHLAND 6 230 3WXFMR WH 7001795 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.10093 | 117.94 | 524267 BUSHLAND 6 230 524623 DEAFSMITH 6 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.09288 | 116.44 | 524296 SPNSPUR_WND7 345 524299 SPNSPUR_COL7 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.09288 | 116.44 | 524299 SPNSPUR_COL7 345 3WXFMR SPNSPUR_COL7 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.10364 | 117.09 | 524415 AMA_SOUTH 6 230 525213 SWISHER 6 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 116.67 | 524502 NORTON 3 115 524509 FE-TUCMCARI3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.094 | 116.45 | 524575 DS-#25+ 3 115 524597 PANDAHFD 3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.094 | 116.55 | 524575 DS-#25+ 3 115 524630 TIERABLANCA3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 116.11 | 524604 HEREFRD_SB 2 69.0 524608 HERFRD_STH 2 69.0 *1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.09593 | 122.73 | 524623 DEAFSMITH 6 230 760498 G17-146-TAP 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 116.52 | 524721 DS-#15&#19+2 69.0 524745 CASTRO_CNTY2 69.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.09297 | 116.03 | 524770 PLSNT_HILL 6 230 3WXFMR EFAE1100068A 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.09578 | 121.59 | 524875 OASIS 6 230 524885 SN_JUAN_TAP6 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.09318 | 117.16 | 524875 OASIS 6 230 524909 ROOSEVELT 6 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.09569 | 121.97 | 524885 SN_JUAN_TAP6 230 527483 CHAVES_CNTY6 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.09293 | 116.22 | 524909 ROOSEVELT 6 230 3WXFMR ABB LMM60042 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.09289 | 122.19 | 524909 ROOSEVELT 6 230 525531 TOLK 6 230 2
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 116.77 | 524923 PORTALES 2 69.0 524929 RO-PORT_MTR2 69.0 @1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 116.42 | 524923 PORTALES 2 69.0 524941 PORTALES#1 2 69.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 116.66 | 525023 BC-BAIL_MTR2 69.0 525027 BAILEYCO 2 69.0 @1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.09152 | 116.55 | 525056 BC-EARTH 3 115 525480 PLANT_X 3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 116.51 | 525191 KRESS_INT 2 69.0 525203 SW-KRESS 2 69.0 Z1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 116.6 | 525192 KRESS_INT 3 115 3WXFMR ENRCO 136155 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.11016 | 116.83 | 525213 SWISHER 6 230 525461 NEWHART 6 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 116.15 | 525272 KISER 3 115 3WXFMR VON 13819/1 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 116.61 | 525326 COX 3 115 3WXFMR ELCO 13474-3 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 116.61 | 525414 LAMTON 3 115 3WXFMR ASEA MLL9204 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05003 | 119.68 | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.09122 | 118.1 | 525481 PLANT_X 6 230 3WXFMR WH ALM20171 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.09907 | 121 | 525481 PLANT_X 6 230 526435 SUNDOWN 6 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.09593 | 121.02 | 525481 PLANT_X 6 230 760498 G17-146-TAP 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.09014 | 116.49 | 525481 PLANT_X 6 230 762174 G17-218TAP 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.08979 | 116.56 | 525481 PLANT_X 6 230 762174 G17-218TAP 230 2
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.09687 | 121.7 | 525531 TOLK 6 230 525586 NEEDMORE 6 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.09221 | 118.23 | 525531 TOLK 6 230 525637 LAMB_CNTY 6 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.1006 | 120.42 | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.08877 | 116.76 | 525531 TOLK 6 230 762174 G17-218TAP 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.08848 | 116.82 | 525531 TOLK 6 230 762174 G17-218TAP 230 2
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15164 | 155.48 | 525549 TOLK 7 345 3WXFMR ABBXNL844501 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.09687 | 121.69 | 525586 NEEDMORE 6 230 526935 YOAKUM 6 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 116.41 | 525599 LC-SANDHLL+2 69.0 525606 AMHERST 2 69.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 116.45 | 525606 AMHERST 2 69.0 525613 W_LITTLFLD 2 69.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 116.46 | 525613 W_LITTLFLD 2 69.0 525635 LAMB_CNTY 2 69.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 116.42 | 525635 LAMB_CNTY 2 69.0 525650 LC-LTTLFLD+2 69.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.09221 | 118.23 | 525637 LAMB_CNTY 6 230 3WXFMR WH ALM20172 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 116.41 | 525779 FLOYD_CNTY 2 69.0 525790 FLOYDADA_TP2 69.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 116.29 | 525828 TUCO_INT 3 115 3WXFMR DS F78800913 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.08942 | 118.38 | 525832 TUCO_INT 7 345 526936 YOAKUM_345 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 116.49 | 526086 SW_6786_N 2 69.0 526087 SW_6786_S 2 69.0 Z1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 116.49 | 526086 SW_6786_N 2 69.0 526102 SP-HETTLER 2 69.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 116.56 | 526087 SW_6786_S 2 69.0 526284 PLANTERS 2 69.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 116.1 | 526160 CARLISLE 3 115 3WXFMR WH RLP38371 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 116.44 | 526195 QUINCY 3 115 526196 SP-MILWAUKEE 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 116.34 | 526268 LUBBCK_STH 3 115 3WXFMR NA 70454A 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 116.6 | 526284 PLANTERS 2 69.0 526297 LUBBCK_EST 2 69.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.09321 | 116.47 | 526424 PACIFIC 3 115 526434 SUNDOWN 3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.09301 | 116.06 | 526435 SUNDOWN 6 230 3WXFMR UPDATE LATER _12 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.09462 | 118.87 | 526435 SUNDOWN 6 230 526460 AMOCO_SS 6 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.09462 | 116.5 | 526460 AMOCO_SS 6 230 526935 YOAKUM 6 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 116.08 | 526525 WOLFFORTH 6 230 3WXFMR UPDATE LATER _13 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 116.48 | 526735 TERRY_CNTY 2 69.0 526747 LG-BROWNFLD2 69.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.09316 | 118.02 | 526935 YOAKUM 6 230 527028 INK_BASIN 6 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.09561 | 116.3 | 526936 YOAKUM_345 345 3WXFMR SPX WT04221 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.09034 | 126.57 | 526936 YOAKUM_345 345 527896 HOBBS_INT 7 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.09318 | 117.39 | 527028 INK_BASIN 6 230 527894 HOBBS_INT 6 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.09303 | 116.43 | 527130 DENVER_N 3 115 527286 HIGGEAST 3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 116.02 | 527149 MUSTANG 6 230 3WXFMR ENRCO 136161 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.09315 | 114.01 | 527149 MUSTANG 6 230 527151 GS-MUSTANG 6 230 @1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 116.29 | 527202 SEAGRAVES 3 115 3WXFMR ABB MLL92408 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 116.17 | 527212 DIAMONDBACK3 115 3WXFMR HOW 36773714 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.09303 | 116.41 | 527286 HIGGEAST 3 115 527363 HIGG 3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.09302 | 116.16 | 527325 OXY_WSEM_TP3 115 527362 JOHNSON_DRW3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 116.15 | 527340 DOSS 3 115 3WXFMR ELCO 13566/1 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 116.14 | 527345 LEGACY 2 69.0 527350 XTO_ROBRTSN2 69.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 116.14 | 527346 LEGACY 3 115 3WXFMR VROL 13735-1 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 116.12 | 527350 XTO_ROBRTSN2 69.0 527355 BOARDMAN 2 69.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 116.05 | 527355 BOARDMAN 2 69.0 527365 FLANNAGAN 2 69.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 116.02 | 527360 MAPCO 3 115 527362 JOHNSON_DRW3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 116.08 | 527362 JOHNSON_DRW3 115 528775 LE-ERF 3 115 @1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 116.01 | 527370 TENNECO_TAP2 69.0 527371 TENNECO 2 69.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.09409 | 116.35 | 527483 CHAVES_CNTY6 230 527799 EDDY_NORTH 6 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 116.05 | 527508 PRICE 3 115 527509 PRICE_TAP 3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 116.02 | 527514 CV-PINE 2 69.0 527563 ROSWLL_INT 2 69.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 116.05 | 527529 RIACBRSH_TP3 115 527533 SW4J795_E 3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 116.02 | 527529 RIACBRSH_TP3 115 527536 BRASHER 3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 116.05 | 527533 SW4J795_E 3 115 527564 ROSWLL_INT 3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 116.06 | 527563 ROSWLL_INT 2 69.0 527575 SW_4702 2 69.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.0931 | 116.1 | 527564 ROSWLL_INT 3 115 527597 TWEEDY 3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 116.06 | 527575 SW_4702 2 69.0 527589 CV-ORCHARD 2 69.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 116.02 | 527589 CV-ORCHARD 2 69.0 527619 DEXTER_TP 2 69.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.09295 | 116.18 | 527653 MILO_WIND 1 34.5 527655 RSVLT_CC_E 7 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.09288 | 116.1 | 527654 RSVLT_CC_W 7 345 527655 RSVLT_CC_E 7 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.09288 | 116.36 | 527654 RSVLT_CC_W 7 345 527666 RSVLT_COL1 7 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.09283 | 116.3 | 527655 RSVLT_CC_E 7 345 527656 CROSSROADS 7 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.09288 | 116.36 | 527666 RSVLT_COL1 7 345 3WXFMR RSVLT_COL1 7 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 116.15 | 527790 EDDY_SVC 1 8.50 527799 EDDY_NORTH 6 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 116.05 | 527864 CUNNINHAM 3 115 528568 MONUMNT_TP 3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.09294 | 116.16 | 527865 CUNNIGHM_N 6 230 527867 CUNNIGHM_S 6 230 *1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 116.14 | 527865 CUNNIGHM_N 6 230 527883 CUNINGHAM3 1 13.8 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.09298 | 116.08 | 527865 CUNNIGHM_N 6 230 527963 POTASH_JCT 6 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.09298 | 116.02 | 527867 CUNNIGHM_S 6 230 527894 HOBBS_INT 6 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.09297 | 116.35 | 527894 HOBBS_INT 6 230 527903 HOBBS_PLT3 1 18.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.09307 | 116.23 | 527896 HOBBS_INT 7 345 3WXFMR HICO 68759-1 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 115.8 | 527965 KIOWA 7 345 528027 RDRUNNER 7 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 115.81 | 528015 PHANTOM 7 345 528027 RDRUNNER 7 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 116.11 | 528024 RR_SVC_HV 3 115 528021 RDRUNNR_SVC1 15.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 116.25 | 528024 RR_SVC_HV 3 115 528025 RDRUNNER 3 115 Z1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 115.81 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 116.08 | 528025 RDRUNNER 3 115 587990 GEN-2016-121 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 116.14 | 528222 CHINA_DRAW 3 115 528225 CD_SVC_HV 3 115 Z1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 115.82 | 528341 LE-SANANDRS3 115 528627 LE-TXACO_TP3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.09299 | 116.06 | 528394 QUAHADA 3 115 528396 XTO_BIGEDDY3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 116.01 | 528552 OIL_CENTER 3 115 528554 COOPER_RNCH3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 116.02 | 528554 COOPER_RNCH3 115 528581 BYRD_TP 3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 116.05 | 528568 MONUMNT_TP 3 115 528581 BYRD_TP 3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 116.04 | 528596 CARDINAL 3 115 528605 TARGA 3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 116.06 | 528603 NA_ENRICH 3 115 528605 TARGA 3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 116.11 | 528617 LE-WAITS 2 69.0 528325 LE-WAITS 3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 116.03 | 528617 LE-WAITS 2 69.0 528714 LE-FORT_SW 2 69.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 116.05 | 528618 LE-LOVINTON2 69.0 528334 LE-NRTH_INT3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 116.42 | 528626 LE-PLNSINT 2 69.0 526928 PLAINS_INT 3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 116.42 | 528626 LE-PLNSINT 2 69.0 528709 LE-PLNSGOAB2 69.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 116.05 | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 116.11 | 528669 LE-STKLDRTP2 69.0 528740 LE-PLANS_SW2 69.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 116.3 | 528709 LE-PLNSGOAB2 69.0 528740 LE-PLANS_SW2 69.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 116.05 | 528709 LE-PLNSGOAB2 69.0 528747 LE-ALLRED 2 69.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 116.03 | 528714 LE-FORT_SW 2 69.0 528718 LE-NEWTEX 2 69.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 116.11 | 528735 LE-PLAINSUB2 69.0 528740 LE-PLANS_SW2 69.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 116.03 | 528775 LE-ERF 3 115 528779 LE-TALLCOTN3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.09288 | 115.79 | 530583 POSTROCK7 345 560082 G16-050-TAP 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 115.81 | 531213 SANTAFE3 115 531408 PIERCVL3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.09297 | 116.04 | 531501 BUCKNER7 345 531502 CIMRRN 7 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.09297 | 116.04 | 531502 CIMRRN 7 345 531503 CIMRRN 1 34.5 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.09287 | 115.75 | 531510 HARBNGR3 115 3WXFMR HARBGR345 _1 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.09298 | 116.06 | 532663 LEC U5 24.0 532854 LEC U5 6 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.09306 | 116.04 | 532794 ROSEHIL7 345 560053 G15052_T 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.09309 | 116.03 | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.09298 | 116.06 | 532853 LAWHILL6 230 532854 LEC U5 6 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.09298 | 116.01 | 539117 SPRVILL-EHVB 230 539695 SPEARVL6 230 Z1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.09298 | 116.02 | 539803 IRONWOOD7 345 3WXFMR IRONWOOD MPT 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.09299 | 116.13 | 542951 HAW G5 1 22.0 543665 HAWTHN5 161 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.09298 | 116.17 | 542955 LAC G1 1 22.0 542981 LACYGNE7 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.09298 | 116.15 | 542956 LAC G2 1 24.0 542981 LACYGNE7 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.09297 | 116.2 | 542957 IAT G1 1 24.0 542982 IATAN 7 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.09297 | 116.27 | 542962 IAT G2 1 24.5 542982 IATAN 7 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.09299 | 116.03 | 542966 WGARDNR5 161 543105 BULLCRK5 161 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.09541 | 115.57 | 560022 CRAWFISH_DR 345 762216 G17-151TAP 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.0951 | 116.52 | 560022 CRAWFISH_DR 345 762467 G18-015-TAP 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 112.71 | 560022 CRAWFISH_DR 345 763087 GEN-2018-073 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.09619 | 116.84 | 560022 CRAWFISH_DR 345 763215 G18-092-TAP 345 2
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.09288 | 115.8 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 116.45 | 560252 G10-14 345 560253 G10-14-1 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 116.18 | 560253 G10-14-1 115 560254 G10-14-SUB1 34.5 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 116.19 | 560253 G10-14-1 115 560255 G10-14-SUB2 34.5 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 116.04 | 560581 G06-44-2 34.5 523111 NOVUS1 3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 116.08 | 560582 G06-44-3 34.5 560577 G06-44 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 116.07 | 560583 G06-44-4 34.5 560577 G06-44 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 115.72 | 560757 ASGI13_02_1 69.0 560758 ASGI13_02_2 34.5 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 115.72 | 560757 ASGI13_02_1 69.0 562731 WHEATLAND 69.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 115.73 | 560763 ASGI13_03_1 115 560761 ASGI13_03_2 34.5 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 116.16 | 562015 FIREWHEEL1 34.5 523215 FREWHELCOL17 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 116.16 | 562016 FIREWHEEL2 34.5 523215 FREWHELCOL17 345 2
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 115.71 | 562323 AGI1202&1305 115 562324 AGI1202&1305 34.5 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 115.73 | 562727 LESBIA 115 562728 SANJONTAP 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 115.72 | 562728 SANJONTAP 115 562729 CAPROCKTAP1 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 115.72 | 562730 CAPROCKTAP2 69.0 562729 CAPROCKTAP1 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 115.72 | 562730 CAPROCKTAP2 69.0 562731 WHEATLAND 69.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 116.15 | 563171 G15082_2 34.5 563170 G15082_1 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 115.78 | P11:13.8:AEPW:COM1-1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 115.79 | P11:13.8:AEPW:COM2-1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 115.79 | P11:13.8:AEPW:COM3-1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 115.78 | P11:18:AEPW:WELSH1-1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 115.79 | P11:18:AEPW:WELSH3-1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 115.78 | P11:24:AEPW:PIRKEY 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 115.68 | P11:24:AEPW:SWS3-1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 115.74 | P11:24:AEPW:TURKCOAL
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.09312 | 116.11 | P12:138:AEPW-OMPA:DUNCAN-4:OMDUNCN4
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 116.02 | P12:138:AEPW:112GORE4:L.E.S.-4
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 116.05 | P12:138:AEPW:112GORE4:SNYDER-4
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 116.05 | 5841_Dup1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.09309 | 115.37 | 584560 GEN-2015-014 115 584561 G15-014XFMR1 34.5 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.09307 | 116.08 | P12:138:AEPW:SANTAFE:DUNCAN-4
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 116.08 | 587991 G16-121XFMR1 34.5 587990 GEN-2016-121 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 116.01 | 588480 A16-010_SUB 115 3WXFMR A16-010_SUB 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.09312 | 116.1 | P12:138:AEPW:DUNCAN-4:L.E.S.-4
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 115.46 | 588761 G17-033XFMR1 34.5 588760 GEN-2017-033 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 115.46 | 588765 G17-033XFMR2 34.5 588760 GEN-2017-033 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 116.02 | 588861 G17-047XFMR1 34.5 588860 GEN-2017-047 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.09285 | 115.79 | P12:138:AEPW:ELKCTY-4:CLINTJC4
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 116.03 | 589381 G17-100XFMR1 34.5 589380 GEN-2017-100 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 116.07 | P12:138:AEPW:SHERID4:112GORE4
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.09302 | 116.06 | P12:345:AEPW-OKGE:CLARKSV7:MUSKOGE7
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.09544 | 117.78 | P12:345:AEPW:L.E.S7:TERRYRD7
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.09544 | 117.77 | P12:345:AEPW:L.E.S7:TERRYRD7
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.09544 | 117.75 | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.09612 | 118.25 | P12:345:AEPW-OKGE:L.E.S.-7:GRACMNT7
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.09612 | 118.23 | P12:345:AEPW-OKGE:L.E.S.-7:GRACMNT7
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.09598 | 118.8 | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 116.08 | P22:345:AMMO::LABADIE:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 116.08 | P22:345:AMMO::LABADIE:2
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 116.09 | P22:345:AMMO::LABADIE:3
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 116.08 | P22:345:AMMO::LABADIE:4
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 116.07 | P22:345:AMMO::RUSHISLAND:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 116.06 | P22:345:AMMO::RUSHISLAND:2
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.09301 | 115.79 | P13:138-13.8:AEPW:COMANC-4_#2
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 115.8 | P13:138-13.8:AEPW:S.W.S.-4
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.0924 | 115.47 | P13:138-230:AEPW:ELKCTY-4
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.09301 | 115.79 | P13:138-24:AEPW:PIRKEY 4
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.09305 | 115.69 | P13:138-24:AEPW:S.W.S.-4
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.09301 | 115.75 | P13:138-24:AEPW:TURK 4
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.09316 | 116.11 | P13:138-345:AEPW:L.E.S.-4_#2
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.09301 | 116.02 | P12:500:EES-EAI:KEO:WMPEHV
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.09302 | 116.14 | P23:500:EES-EAI:KEO:B4941
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.09301 | 116.02 | P23:500:EES-EAI:KEO:B4931
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.09302 | 116.13 | P23:500:EES-EAI:KEO:B4921
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.09301 | 116.07 | P23:500:EES-EAI:INDEP2:B6126
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 116.06 | P23:500:EES-EAI:PD:INDEP2:LN:FK479
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.09302 | 115.79 | P13:345-18:AEPW:WELSH 7_#1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.09302 | 115.79 | P13:345-18:AEPW:WELSH 7_#3
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 115.79 | P13:69-13.8:AEPW:COMANC-2
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 116.08 | P11:024:DPC:ALMA2:6
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 116.04 | P11:18:ITCM:EMERYGT1:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 116.05 | P11:18:ITCM:EMERYGT2:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 116.05 | P11:161:ITCM:MGS CT1:1C
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 116.05 | P11:161:ITCM:MGS CT2:2C
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.09298 | 116.06 | 652537 WHITE 3 345 659286 DEERCREK-BE3 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.09298 | 116.02 | 652568 GROTONSOUTH7 115 659275 GROTON_G-BE7 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.09298 | 116.06 | 659286 DEERCREK-BE3 345 3WXFMR DEERCRK KU1A 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 116.05 | 672601 BD 4 230 672306 BD 6G 18.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 116.05 | 672610 POPLAR 4 230 672310 POPLAR 1G 18.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 116.05 | 672610 POPLAR 4 230 672311 POPLAR 2G 18.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 116.04 | 672621 SHAND 4 230 672321 SHAND 1G 18.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 116.03 | 672649 CODETTE 4 230 672650 NIPAWIN 4 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 116.04 | 672696 BRADA 4 230 672699 NBEC 4 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 116.12 | P23:345:MDU::COYOTE::5707-5712-5715::::
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 116.3 | P23:345:MEC:CBEC 905
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 116.25 | P23:345:MEC:CBEC 908
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.09301 | 116.04 | P23:345:MEC:GDMEC 901
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.09301 | 116.04 | P23:345:MEC:GDMEC 902
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 116.06 | P23:345:MEC:GDMEC 908
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 116.17 | P23:345:MEC:RAUN 0180
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 116.24 | P23:345:MEC:RAUN 0210
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 116.18 | P23:345:MEC:LOUISA 954
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 116.19 | P23:345:MEC:LOUISA 964
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 116.03 | P21:115:XEL:AUTO-SINGLE:CHEMOLT7:LSPOWER7:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 116.07 | P21:115:XEL:AUTO-SINGLE:COLVILL7:CANONFLSG7:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 116.03 | P21:115:XEL:AUTO-SINGLE:FARIBALTP7:FARIBALTGEN:Z
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 116.13 | P21:230:OTP:AUTO-SINGLE:SQBUTTE4:YNG24:1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 116.12 | P23:345:OTP:CENTER 3:3215(1)
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 116.12 | P23:345:OTP:CENTER 3:3225(1)
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 116.06 | P12:230:UMZW:# 687 #: FT IN SD. FT-BG1 LINE FAULT
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 116.06 | P12:230:UMZW:# 3617 #: FT IN SD. FT-BG2 LINE FAULT
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 114.69 | 760494 GEN-2017-146 230 760498 G17-146-TAP 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 114.68 | 760495 G17-146-XFM1 34.5 760494 GEN-2017-146 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 115.46 | 761356 G17-239-XFMR 34.5 761355 GEN-2017-239 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 115.46 | 761359 G17-239-XFMR 34.5 761355 GEN-2017-239 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 115.63 | 761797 G17-187XFM1 34.5 761796 GEN-2017-187 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 115.63 | 761800 G17-187XFM2 34.5 761796 GEN-2017-187 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 110.67 | 762132 GEN-2017-158 230 763252 G18-099-XFM1 34.5 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 110.67 | 762132 GEN-2017-158 230 763255 G18-099-XFM2 34.5 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 111.27 | 762133 G17-158XFM1 34.5 762132 GEN-2017-158 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 111.27 | 762136 G17-158XFM2 34.5 762132 GEN-2017-158 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 113.54 | 762216 G17-151TAP 345 762217 GEN-2017-151 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.09541 | 116.85 | 762216 G17-151TAP 345 762467 G18-015-TAP 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 115.27 | 762218 G17-151XFM1 34.5 762217 GEN-2017-151 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 115.27 | 762221 G17-151XFM2 34.5 762217 GEN-2017-151 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 115.27 | 762224 G17-151XFM3 34.5 762217 GEN-2017-151 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 115.27 | 762227 G17-151XFM4 34.5 762217 GEN-2017-151 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 114.55 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 115.11 | 762461 G18-015-XFM1 34.5 762460 GEN-2018-015 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 115.11 | 762464 G18-015-XFM2 34.5 762460 GEN-2018-015 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.09432 | 116.42 | 762467 G18-015-TAP 345 763215 G18-092-TAP 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 113.8 | 763087 GEN-2018-073 345 763088 G18-073-XFM1 34.5 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 114.78 | 763087 GEN-2018-073 345 763091 G18-073-XFM2 34.5 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 110.64 | 763120 GEN-2018-081 230 763121 G18-081-XFM1 34.5 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 112.78 | 763120 GEN-2018-081 230 764011 G19-074-XFM1 34.5 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 113.84 | 763208 GEN-2018-092 345 763215 G18-092-TAP 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 114.77 | 763208 GEN-2018-092 345 763220 G18-092-XFM1 34.5 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 114.77 | 763208 GEN-2018-092 345 763223 G18-092-XFM2 34.5 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 112.23 | 763241 GEN-2018-097 230 763242 G18-097-XFM1 34.5 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 113.15 | 763241 GEN-2018-097 230 763296 G18-111-XFM1 34.5 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 112.51 | 763241 GEN-2018-097 230 763307 G18-112-XFM1 34.5 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 112.51 | 763241 GEN-2018-097 230 763310 G18-112-XFM2 34.5 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 112.23 | 763241 GEN-2018-097 230 763395 G18-124-XFM1 34.5 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 112.23 | 763241 GEN-2018-097 230 763398 G18-124-XFM2 34.5 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 115.66 | 763318 GEN-2018-115 345 763319 G18-115-XFM1 34.5 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 112 | 763483 GEN-2019-003 230 763484 G19-003-XFM1 34.5 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 114.56 | 763483 GEN-2019-003 230 763605 G19-021-XFM1 34.5 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 115.46 | 763516 GEN-2019-011 345 763517 G19-011-XFM1 34.5 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 115.55 | 763879 GEN-2019-056 115 763880 G19-056XFM1 34.5 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.09264 | 116.19 | P42:345:OKGE:SB_BVTY7305
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.09284 | 115.75 | P23:345:WERE:BUFF_345-534::
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.09284 | 115.75 | P23:345:WERE:BUFF_345-543::
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.09296 | 116.23 | P23:345:WERE:JEC_345-15::
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.09294 | 116.18 | P23:345:WERE:JEC_345-16::
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.09296 | 116.22 | P23:345:WERE:JEC_345-19::
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.09296 | 116.22 | P23:345:WERE:JEC_345-20::
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.09299 | 116.39 | P23:345:WERE:WOLF_345-50::
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 116.39 | P23:345:WERE:WOLF_345-60::
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.09301 | 115.8 | P42:345:AEPW:WELSH CB 10620 NBTB+FAULT
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 115.79 | P41:345:AEPW:WELSH CB 10630 NBTB+FAULT
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 115.79 | P41:345:AEPW:WELSH CB 11670 NBTB+FAULT
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.09311 | 115.78 | P41:345:AEPW:WELSH CB 11680 NBTB+FAULT
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 115.78 | P41:345:AEPW:WELSH CB 12540 NBTB+FAULT
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.09598 | 117.33 | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.09643 | 118.58 | P42:345:AEPW:LAWTON EASTSIDE CB 3413A NBTB+FAULT
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.09676 | 118.94 | P42:345:AEPW:LAWTON EASTSIDE CB 3425A NBTB+FAULT
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.09611 | 118.96 | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.09544 | 117.77 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.09544 | 117.77 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.09544 | 117.74 | P42:345:AEPW:TERRYRD_CB_3421A_NBTB
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.09298 | 116.18 | P23:345:KCPL:LACYGNE_R2-5::LACYGU2-LACYGNE-STILWELL
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.09298 | 115.82 | P45:345:UMZW:# 1328 #: GI IN NE.
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.09301 | 115.8 | P23:345:AEPW:WELSH CB 10620 NBTB
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 115.79 | P23:345:AEPW:WELSH CB 10630 NBTB
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 115.79 | P23:345:AEPW:WELSH CB 11670 NBTB
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.09311 | 115.78 | P23:345:AEPW:WELSH CB 11680 NBTB
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 115.78 | P23:345:AEPW:WELSH CB 12540 NBTB
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.09598 | 117.74 | P23:345:AEPW:OKLAUNION CB 3401A NBTB
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.09643 | 118.58 | P23:345:AEPW:LAWTON EASTSIDE CB 3413A NBTB
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.09676 | 118.94 | P23:345:AEPW:LAWTON EASTSIDE CB 3425A NBTB
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.09611 | 118.96 | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.09544 | 117.77 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.09544 | 117.77 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.09544 | 117.74 | P23:345:AEPW:TERRYRD_CB_3421A_NBTB
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 116.05 | P11:161:GMO:DOGWOOD_COMBINED_CYCLE_UNIT_OUTAGE
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.093 | 116.06 | P11:115:SUNC:GARDENCITY_S2:97:531459(2)
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.09285 | 115.77 | P12:345:PWT:BUFF-THIS_345_1::
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.09285 | 115.77 | P12:345:PWT:BUFF-THIS_345_2::
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.09287 | 115.83 | P12:345:PWT:THIS-DGRS_345_1::FUTURE
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.09287 | 115.83 | P12:345:PWT:THIS-DGRS_345_2::FUTURE
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.09309 | 116.06 | P12:069:WFEC:ANADRKO_WATONGA
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.0956 | 117.97 | P23:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.09809 | 120.4 | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.0956 | 117.97 | P42:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB+FAULT
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.09809 | 120.4 | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.08815 | 114.13 | P42:345:OKGE:SB_BVTY7315_PRE19S
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.09268 | 115.62 | P23:345:SUNC:MO_BRK182
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.09268 | 115.62 | P23:345:SUNC:MO_BRK382
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.09264 | 115.79 | P23:345:SUNC:MO_BRK188
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.09458 | 116.06 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.09301 | 115.79 | P12:138-13.8:AEPW:COMANC-4_#1
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.0924 | 115.47 | P12:230:AEPW:ELKCITY6:CHISHOLM6
Thermal | 05ALL | 1 | 26SP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.09452 | 116.62 | P12:230:AEPW:SWEETWT6:CHISHOLM6
Thermal | 05ALL | 1 | 26SP | GEN-2018-097 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.19718 | 112.81 | 523097 HITCHLAND 7 345 523961 POTTER_CO 7 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-099 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.19718 | 112.81 | 523097 HITCHLAND 7 345 523961 POTTER_CO 7 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-111 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.19718 | 112.81 | 523097 HITCHLAND 7 345 523961 POTTER_CO 7 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-112 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.19718 | 112.81 | 523097 HITCHLAND 7 345 523961 POTTER_CO 7 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2018-124 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.19718 | 112.81 | 523097 HITCHLAND 7 345 523961 POTTER_CO 7 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15222 | 116.18 | P23:345:KCPL-WERE:237LACYGNE_R1-6::LACYGU1-LACYGNE-NEOSHO
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15219 | 116.06 | P11:230:WERE:LECU5_GEN::
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.1522 | 116.08 | P11:161:GMO:DOGWOOD_COMBINED_CYCLE_UNIT_OUTAGE_1_1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.02 | P11:20:KACY:NEARMAN N1::N1 OUT OF SERVICE:::
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.1522 | 116.02 | P12:69:KACY:NMGEN-NMISOBUS::NEARMAN N1-NM ISOBUS OPEN:::
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.1522 | 116.02 | P13:20-161:KACY:NEARMAN5-NMISOBUS:NAMEPLATE:NEARMAN N1 GSU:::
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.1522 | 116.02 | P21:20:KACY:546702NMGENN1-546703NMISOBUSC1::::
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.23 | P11:115:SPS:HOBBS1&3:145MW::::
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15227 | 114.72 | P11:115:SPS:MUSTANG1&3:153MW::::
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.1529 | 118.23 | P12:230:SPS:K37::1_TOLK_LAMB:::
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15242 | 116.06 | P12:230:SPS:K43::1_PRNGLE_HARR_E:::
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15225 | 115.81 | P12:230:SPS:K44::1_EPLNT_HARRW:::
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.1519 | 116.22 | P12:115:SPS:T04::1_TRBLNC_CASTRO:::
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15242 | 116.02 | P12:115:SPS:T06::1_SPRMN_PRNGLE:::
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.5 | P12:115:SPS:T21::1_GRSSLND_GRAHAM:::
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.05 | P12:115:SPS:T24B::1_RSWLL_BRSHRF:::
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15229 | 116.05 | P12:115:SPS:T26::1_CHAVES_RSWLCTY:::
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15389 | 116.45 | P12:115:SPS:T28A::1_LAMTON_PLANTX:::
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15279 | 116.02 | P12:115:SPS:T29::1_LAMTON_HALECTR:::
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15374 | 117.27 | P12:115:SPS:T30::1_LAMB_HOCKLY:::
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15374 | 116.37 | P12:115:SPS:T31::1_HOCKLY_SUNDWN:::
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15214 | 116.06 | P12:115:SPS:T35::1_TERRY_YOAKUM:::
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15228 | 116.78 | P12:115:SPS:T45::1_NORRIS_OASIS:::
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15216 | 115.82 | P12:115:SPS:T57::1_MUSTG_SEGRVS:::
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.16085 | 116.03 | P12:115:SPS:T58::1_HERFRD_CARGIL:::
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.16085 | 116.57 | P12:115:SPS:T59::1_CARGIL_CURRY:::
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.02 | P12:115:SPS:T64::1_RNDALL_PULLMN:::
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15313 | 116.38 | P12:115:SPS:T67::1_HAPPY_KRESS:::
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15227 | 115.77 | P12:115:SPS:T68::1_TUCO_FLOYD:::
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15222 | 115.81 | P12:115:SPS:T69::1_LUBBE_CROSBY:::
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.02 | P12:115:SPS:T70::1_COLTR_S_GORG:::
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15215 | 116.63 | P12:115:SPS:T71::1_CRLSLE_YUMA:::
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15233 | 116.1 | P12:115:SPS:T81::1_COX_FLOYD:::
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.26 | P12:115:SPS:T83::1_SP-FKFD_ALLEN:::
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15196 | 116.44 | P12:115:SPS:T89::1_DC_N_HIGG:::
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.07 | P12:115:SPS:T91::1_HIGG_RUSSELL:::
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15227 | 116.02 | P12:115:SPS:V01::1_MOOREW_RVRVIEW:::
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15249 | 116.07 | P12:115:SPS:V04::1_EPLANT_RNDALL:::
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15239 | 116.06 | P12:115:SPS:V07::1_COX_HALECTR:::
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15375 | 116.23 | P12:115:SPS:V09::1_HALECTR_PLANTX:::
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15191 | 116.21 | P12:115:SPS:V12::1_PLANTX_BAILEY:::
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.03 | P12:115:SPS:V15::1_TUCO_INDANA:::
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15177 | 116.16 | P12:115:SPS:V24::1_WOLFTH_TERRY:::
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.154 | 116.07 | P12:115:SPS:V26::1_RSWLL_EDDY_N:::
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.4 | P12:115:SPS:V33::1_LUBBS_LYNN:::
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15324 | 117.14 | P12:115:SPS:V37::1_CASTRO_PLANTX:::
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15222 | 116.05 | P12:115:SPS:V44::1_COLTR_OWENS:::
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.16 | P12:115:SPS:V46::1_ALLEN_WHEELCK:::
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15219 | 116.5 | P12:115:SPS:V49::1_YOAKUM_SHLCO2:::
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15249 | 116.68 | P12:115:SPS:V55::1_SUNDWN_TERRY:::
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15223 | 116.59 | P12:115:SPS:V56::1_COCHRAN_SUNDWN:::
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.09 | P12:115:SPS:V62::1_CRLSLE_INDANA:::
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15344 | 116.07 | P12:115:SPS:V78::2_CURRY_RSVLT:::
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15204 | 116.19 | P12:115:SPS:V81::1_LE-WAIT_LE-LVN:::
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.1522 | 116.06 | P12:115:SPS:V95::1_DC_N_SHLCO2:::
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.02 | P12:115:SPS:W11::1_DC_S_SMINLE:::
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15219 | 116.03 | P12:115:SPS:W12::1_SMINLE_DOSS:::
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15216 | 116.1 | P12:115:SPS:W14::1_SMINLE_GAINES:::
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.1522 | 116.03 | P12:115:SPS:W26::1_CUNGHM_OILCNTR:::
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.61 | P12:115:SPS:W32::1_PRMTR_FE-CLSIN:::
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15202 | 116.26 | P12:115:SPS:W35::1_GAINES_JNSDRW:::
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15535 | 116.59 | P12:115:SPS:W40::1_WCANYON_TRBLNC:::
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15251 | 116.11 | P12:115:SPS:W52::1_NEWHART_KRESS:::
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.67 | P12:115:SPS:W58::1_NORTON_LOPEZ:::
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.25 | P12:115:SPS:W59::1_LOPEZ_CMPBLL:::
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15231 | 116.55 | P12:115:SPS:W62::1_PLSTHL_CURRY:::
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15233 | 116.07 | P12:115:SPS:W63::1_PLSTHL_CURRY:::
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.36 | P12:115:SPS:W64::1_PLSTHL_FE-CLV:::
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15233 | 116.57 | P12:115:SPS:W65::1_PLSTHL_CURRY:::
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.23 | P12:115:SPS:W66::1_PORTA_GREYHUND:::
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15207 | 116.02 | P12:115:SPS:W76::1_QUAHA_PCA:::
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15535 | 116.1 | P12:115:SPS:W77::1_RNDAL_WCANYON:::
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15224 | 116.07 | P12:115:SPS:W99::1_CAPITAN_CHAVES:::
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15219 | 116.05 | P12:115:SPS:U03::1_CARDNL_NEF:::
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15208 | 116.53 | P12:115:SPS:U14::1_DC_STH_INKBSN:::
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15204 | 116.47 | P12:115:SPS:V15::1_INKBSN_LE-WAT:::
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15249 | 116.15 | P12:115:SPS:U16::1_BSHLND_OUTPST:::
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15249 | 116.16 | P12:115:SPS:U17::1_COLTR_OUTPST:::
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15217 | 116.26 | P12:115:SPS:U19::1_DEAN_PLAINS:::
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15249 | 116.07 | P12:115:SPS:U23::1_COLTR_HILSDE:::
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.13943 | 124.36 | P42:345:SPS:YOAKUM:J18####:SLG1:EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.13943 | 124.36 | P43:345:SPS:YOAKUM:TF#####:SLG:EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.13943 | 124.36 | P42:345:SPS:YOAKUM:J17####:SLG:EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.13943 | 124.36 | P42:345:SPS:YOAKUM:J18####:SLG2:EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.1522 | 116.06 | P11:18:HAST:::EGYCTR2G WEC2_LOSS OF WEC 2 GEN_:HV:
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.1522 | 116.06 | P13:18-115:HAST:::EGYCNTR7 XFMR G2WEC 2 GSU_:HV:
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.1522 | 116.08 | P11:161:GMO:DOGWOOD-COMBINED-CYCLE-UNIT-OUTA:::HV:
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15222 | 116.18 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.1522 | 116.18 | P23:345:KCPL:LACYGNE-R2-5:::EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15217 | 116.23 | P11:230:WERE:JECU1-GEN:::HV:
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15219 | 116.06 | P11:230:WERE:LECU5-GEN:::HV:
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15217 | 116.23 | P11:345:WERE:JECU2-GEN:::EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15217 | 116.22 | P11:345:WERE:JECU3-GEN:::EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.4 | P11:345:WERE:WOLFU1-GEN:::EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15207 | 115.77 | P12:345:PWT:BUFF-THIS-345-1:::EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15207 | 115.77 | P12:345:PWT:BUFF-THIS-345-2:::EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15205 | 115.75 | P23:345:WERE:BUFF-345-534:::EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15205 | 115.75 | P23:345:WERE:BUFF-345-543:::EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15217 | 116.23 | P23:345:WERE:JEC-345-15:::EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15216 | 116.18 | P23:345:WERE:JEC-345-16:::EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15217 | 116.22 | P23:345:WERE:JEC-345-19:::EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15217 | 116.22 | P23:345:WERE:JEC-345-20:::EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.1522 | 116.39 | P23:345:WERE:WOLF-345-50:::EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.39 | P23:345:WERE:WOLF-345-60:::EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.34 | P11:022:NPPD:COOPER1G:1:983:::
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15216 | 116.33 | P11:023:NPPD:GENTLM1G:1:757:::
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15216 | 116.35 | P11:024:NPPD:GENTLM2G:2:757:::
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.1522 | 116.01 | P11:161:OPPD:N OMA 5G:LT::HV:
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.1522 | 116.01 | P11:161:OPPD:N OMA 5G:::HV:
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15217 | 116.2 | P13:345:OPPD:NEBCTY1G:::EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15216 | 116.22 | P13:345:OPPD:NEBCTY2G:::EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.1522 | 116.01 | P13:161:OPPD:N OMA 5G:::HV:
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.22 | P22:345:OPPD:S3458 NEBCTY1G:LT::EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15217 | 116.2 | P22:345:OPPD:S3458 NEBCTY1G:::EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.25 | P22:345:OPPD:S3458 NEBCTY2G:LT::EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15216 | 116.22 | P22:345:OPPD:S3458 NEBCTY2G:::EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.22 | P23:345:OPPD:S3458 NEBCTY1G:LT::EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15217 | 116.2 | P23:345:OPPD:S3458 NEBCTY1G:::EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.25 | P23:345:OPPD:S3458 NEBCTY2G:LT::EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15216 | 116.22 | P23:345:OPPD:S3458 NEBCTY2G:::EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 115.8 | P12:115:SUNC:PLYMELL-PIERCEVILLE:::HV::
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15219 | 116.06 | P11:018:UMZB:# 5 #:: DCS IN SD. DEERCREEK_MV::
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.1522 | 116.03 | P11:022:UMZB:# 15 #:: LO IN ND. LELAND OLDS 1_MV::
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15219 | 116.07 | P11:020:UMZB:# 16 #:: LO IN ND. LELAND OLDS 2_MV::
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15218 | 116.14 | P11:023:UMZB:# 31 #:: AVS IN ND. ANTELOPE VALLEY 1_MV::
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15218 | 116.14 | P11:023:UMZB:# 32 #:: AVS IN ND. ANTELOPE VALLEY 2_MV::
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15215 | 116.33 | P11:024:UMZB:# 33 #:: LRS IN WY. LARAMIE RIVER STATION 1_MV::
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.06 | P12:230:UMZW:# 687 #:: FT IN SD. FT-BG1 BRANCH FAULT:HV:
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.06 | P12:230:UMZW:# 3617 #:: FT IN SD. FT-BG2 BRANCH FAULT:HV:
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.06 | P12:230:UMZW:# 4038 #:: BG-FT IN SD. FAULT FOR TRANSMISSION CIRCUIT (BG-FT).:HV:
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.06 | P12:230:UMZW:# 4039 #:: BG-FT IN SD. FAULT FOR TRANSMISSION CIRCUIT (BG-FT).:HV:
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.03 | P13:230:UMZW:# 5135 #:: OA IN SD. FAULT ON TRANSFORMER (2).:HV:
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.03 | P13:230:UMZW:# 5136 #:: OA IN SD. FAULT ON TRANSFORMER (3).:HV:
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15219 | 115.82 | P23:345:UMZW:# 2423 #:: GI IN NE. GI 1596 BKR FAULT:EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15219 | 115.82 | P23:345:UMZW:# 2426 #:: GI IN NE. GI 1592 BKR FAULT:EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15219 | 115.82 | P23:345:UMZW:# 2432 #:: GI IN NE. GI 1092 BKR FAULT:EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15219 | 115.82 | P23:345:UMZW:# 2440 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1092 STUCK BKR:EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15219 | 115.82 | P23:345:UMZW:# 2444 #:: GI IN NE. GI-SWEET BRANCH FAULT & GI 1596 STUCK BKR:EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15219 | 115.82 | P23:345:UMZW:# 2446 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1196 STUCK BKR:EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15219 | 115.82 | P42:345:UMZW:# 2413 #:: FT2 IN SD. FT2-LO2 BRANCH FAULT & FT2 2992 STUCK BKR:EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15219 | 115.82 | P42:345:UMZW:# 2415 #:: FT2 IN SD. FT2-GI BRANCH FAULT & FT2 3392 STUCK BKR:EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15224 | 115.74 | P11:138:WFEC:HUGO1:465MW :::
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.1522 | 116.02 | P11:138:WFEC:MORLND2:132MW:::
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.1522 | 116.03 | P11:138:WFEC:MORLND3:149MW :::
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.1523 | 116.06 | P12:138:WFEC:ANADRKO_CLVLND::::
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15223 | 116.06 | P12:345:OKGE-AEPW:BKRBKR12::::
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15258 | 116.18 | P12:345:OKGE:BKRBKR21::::
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15277 | 116.26 | P12:345:OKGE:BKRBKR24::::
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15468 | 117.75 | P12:345:OKGE-AEPW:BKRBKR25::::
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.1519 | 115.72 | P12:345:OKGE:BKRBKR336::::
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.1519 | 115.72 | P12:345:OKGE:BKRBKR336_2::::
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15545 | 118.25 | P12:345:OKGE-AEPW:BKRBKR366::::
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15545 | 118.23 | P12:345:OKGE-AEPW:BKRBKR366::::
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.1543 | 117.15 | P12:345:OKGE:BKRBKR367::::
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15194 | 115.72 | P12:345:OKGE:BKRBKR4193::::
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15194 | 115.72 | P12:345:OKGE:BKRBKR4194::::
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.02 | P12:345:OKGE:BKRBKR4195::::
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15184 | 115.76 | P12:345:OKGE-SPS:BKRBKR4201::::
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15184 | 115.76 | P12:345:OKGE-SPS:BKRBKR4202::::
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15231 | 116.03 | P12:345:OKGE:BKRBKR421::::
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15187 | 115.6 | P12:345:OKGE:BKRBKR443NEW::::
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15187 | 115.6 | P12:345:OKGE:BKRBKR443NEW2::::
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15205 | 115.79 | P12:345:OKGE-ITC:BKRBKR502::::
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15205 | 115.79 | P12:345:OKGE-ITC:BKRBKR503::::
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15208 | 115.83 | P12:345:OKGE-ITC:BKRBKR502_1::::
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15208 | 115.83 | P12:345:OKGE-ITC:BKRBKR503_1::::
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15215 | 116.33 | P12:345:OKGE:BKRBKR604::::
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15214 | 116.37 | P12:345:OKGE:BKRBKR604_2::::
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15223 | 115.82 | P11:345:OKGE:BKRBKR_GSU07::::
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15223 | 115.81 | P11:345:OKGE:BKRBKR_GSU08::::
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15223 | 115.8 | P11:138:OKGE:BKRBKR_GSU21::::
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15219 | 115.83 | P12:138:OKGE:BKRBKR85_MOS1::::
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15187 | 116.13 | P42:345:OKGE:SB_ARIA7381::::
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15921 | 120.17 | P42:345:OKGE:SB_BVTY7387::::
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15232 | 116.02 | P41:345:OKGE:SB_REUD7381::::
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15231 | 116.03 | P41:345:OKGE:SB_REUD7383::::
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15231 | 116.06 | P41:345:OKGE:SB_REUD7385::::
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15234 | 116.06 | P42:345:OKGE:SB_REUD7389::::
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15219 | 116.05 | P11:115:SUNC:GARDENCITY_S2:103:531459(2):HV:
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15219 | 116.07 | P11:115:SUNC:FORTDDODGE_4:157:539670(4):HV:
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.04 | P11:345:599:CIMARRON1WIND:200:531603(1):EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.47 | P13:115:SUNC:HOLCOMB_GSU:::HV:
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15219 | 116.05 | P13:115:SUNC:S2_GSU:::HV:
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15219 | 116.07 | P13:115:SUNC:FORTDODGE_GSU:::HV:
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15219 | 116.04 | P23:345:SUNC:BU_BRK682:::EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.14 | 300003 1THLG3 24.0 301503 7THOMHLGSU3 345 3
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.01 | 300007 1NM G2 22.0 301537 7NEWMADGSU2 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.01 | 300046 7NEWMAD 345 301537 7NEWMADGSU2 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.14 | 300049 7THOMHL 345 301503 7THOMHLGSU3 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.08 | P11:20:AMMO:1LAB�� G1:1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.08 | P11:20:AMMO:1LAB�� G2:2
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.27 | P11:345:AMMO::CALLAWAY:1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.08 | P11:345:AMMO::LABADIE:3
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.08 | P11:345:AMMO::LABADIE:4
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.07 | P11:345:AMMO::RUSHISLAND:U1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.07 | P11:345:AMMO::RUSHISLAND:U2
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.06 | P11:138:AMMO::SIOUX:2
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 115.83 | P11:24:CLEC::G1DOLHIL:1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.06 | P12:765:AEP:AEP ROCKP-AEP JEFF 765
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 115.78 | P11:HV:EES::PIRKEY 1:1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 115.79 | P11:EHV:EES::WELSH3-1:1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 115.74 | P11:HV:EES::TURKCOAL:1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.25 | P12:EHV:EES::7CALAWY 1:1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15222 | 116.02 | 338056 CHALKBLUFFPV 500 338162 8W.MEMPHIS% 500 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15223 | 115.75 | P12:HV:EES::TURK 4%:1(1)
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15223 | 115.79 | P12:EHV:EES::WELSH 7:1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15223 | 115.79 | P12:EHV:EES::WELSH 7:1(1)
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15222 | 115.79 | P12:HV:EES::PIRKEY 4:1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15223 | 116.06 | P12:EHV:EES::CLARKSV7!:MUSKOGE7!:1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.06 | 344011 7HUGHES 345 344012 7HPW-N 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.08 | 344884 7LABADIE1 345 344894 1LAB G1 20.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.08 | 344885 7LABADIE2 345 344895 1LAB G2 20.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.08 | 344886 7LABADIE3 345 344896 1LAB G3 20.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.08 | 344887 7LABADIE4 345 344897 1LAB G4 20.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.07 | 345667 7RUSH 1 345 345670 1RUSH G1 18.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.06 | 345668 7RUSH 2 345 345671 1RUSH G2 18.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.05 | 345755 4SIOUX 1 138 345756 1SIOUX 1 18.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.05 | 345764 4SIOUX 2 138 345765 1SIOUX 2 18.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.12 | P12:345:MDU::CENTER:COYOTE:1::::
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.12 | P13:345:MDU:COYOTE GSU LOSS:COYOTE::1::::
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.03 | P11:345:MEC:GDMEC CT1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.03 | P11:345:MEC:GDMEC CT2
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.14 | P11:345:MEC:GDMEC ST
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.35 | P11:345:MEC-NPPD:COOPER 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.24 | P11:24:XEL:AUTO-SINGLE:SHERC31G:1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.24 | P11:24:XEL:AUTO-SINGLE:SHERC32G:2
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.33 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.16 | P11:20:XEL:AUTO-SINGLE:PRIS31G:1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.16 | P11:20:XEL:AUTO-SINGLE:PRIS32G:2
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.2 | P11:22:XEL:AUTO-SINGLE:MNTCE31G:1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.16 | P11:20:XEL:AUTO-SINGLE:KING31G:1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.02 | P11:13:XEL:AUTO-SINGLE:HBRS73G:9
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.02 | P11:18:XEL:AUTO-SINGLE:BLKD76G:6
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.22 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.22 | P11:22:GRE:AUTO-SINGLE:GRE-COAL42G:2
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.14 | P11:24:OTP:AUTO-SINGLE:BIGSTN1G:1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.15 | P11:20:OTP:AUTO-SINGLE:CENTER2G:1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.05 | P11:22:OTP:AUTO-SINGLE:CENTER1G:1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.13 | P11:24:OTP:AUTO-SINGLE:COYOTE1G:1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.05 | P11:24:DPC:AUTO-SINGLE:GENOA53G:3
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.03 | P12:115:XEL:AUTO-SINGLE:CHEMOLT7:LSPOWER7:1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.07 | P12:115:XEL:AUTO-SINGLE:COLVILL7:CANONFLSG7:1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.03 | P12:115:XEL:AUTO-SINGLE:FARIBALTP7:FARIBALTGEN:Z
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.13 | P12:230:OTP:AUTO-SINGLE:SQBUTTE4:YNG24:1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.22 | P13:24-345:XEL:AUTO-SINGLE:SHERC31G:SHERCO3:1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.22 | P13:24-345:XEL:AUTO-SINGLE:SHERC32G:SHERCO3:1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.3 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.16 | P13:20-345:XEL:AUTO-SINGLE:PRIS31G:PRISLD3:1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.16 | P13:20-345:XEL:AUTO-SINGLE:PRIS32G:PRISLD3:2
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.2 | P13:22-345:XEL:AUTO-SINGLE:MNTCE31G:MNTCELO3:1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.15 | P13:20-345:XEL:AUTO-SINGLE:KING31G:ASKING3:1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.02 | P13:13-115:XEL:AUTO-SINGLE:HBRS73G:HIBRDGE7:9
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.2 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL41G:GRE-COALCR4:1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.2 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL42G:GRE-COALCR4:1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.13 | P13:230-24:OTP:AUTO-SINGLE:BIGSTON4:BIGSTN1G:1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.13 | P13:20-230:OTP:AUTO-SINGLE:CENTER2G:YNG24:1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.04 | P13:22-230:OTP:AUTO-SINGLE:CENTER1G:CENTER4:1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.12 | P13:24-345:OTP:AUTO-SINGLE:COYOTE1G:COYOTE3:1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.05 | P13:24-161:DPC:AUTO-SINGLE:GENOA53G:GENOA5:1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.07 | P13:24-161:DPC:AUTO-SINGLE:JPM:ALMA5:1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15222 | 116.02 | 38203 J1819 POI 500 337957 8KEO% 500 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15222 | 116.02 | 38203 J1819 POI 500 338056 CHALKBLUFFPV 500 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.13 | P11:115:XEL:RIV COMBINE CYCLE
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.04 | P12:115:XEL:BDS #2 5
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.04 | P11:115:XEL:HBR #6
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.04 | P11:115:XEL:HBR #7
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.16 | P11:115:XEL:HBR #6 7 8
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.16 | P23:345:XEL:8H14 PRI
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.16 | P23:345:XEL:8H17 PRI AS
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.3 | P23:345:XEL:8N28 SHC
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.22 | P23:345:XEL:8N22 SHC
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.22 | P23:345:XEL:8N17 SHC
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.21 | P23:345:XEL:8N8 MNN
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.15 | P23:345:XEL:8P1 KING
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.15 | P23:345:XEL:8P2 KING
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.04 | P23:115:XEL:5P147 IVH AS
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.03 | P11:18:ALTW:AUTO-SINGLE:EMERYST1:1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.03 | P11:22:ALTW:AUTO-SINGLE:LANS54G:4
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.17 | P11:22:ALTW:AUTO-SINGLE:ARNOLD1G:1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.2 | P11:24:ALTW:AUTO-SINGLE:OTTUMW1G:1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.03 | P13:18-161:ALTW:AUTO-SINGLE:EMERYST1:EMERY5:1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.03 | P13:22-161:ALTW:AUTO-SINGLE:LANS54G:LANSINGL15:1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.16 | P13:22-161:ALTW:AUTO-SINGLE:ARNOLD1G:ARNOLD5:1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.19 | P13:24-161:ALTW:AUTO-SINGLE:OTTUMW1G:OTTUMWA5:1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.27 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.34 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.19 | P11:22:MEC:AUTO-SINGLE:NEAL3G:3
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.26 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.19 | P11:24:MEC:AUTO-SINGLE:LOUIS31G:1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.25 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.3 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.17 | P13:345-22:MEC:AUTO-SINGLE:RAUN3:NEAL3G:1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.24 | P13:345-24:MEC:AUTO-SINGLE:RAUN3:NEAL4G:1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.18 | P13:345-24:MEC:AUTO-SINGLE:LOUISA3:LOUIS31G:1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15217 | 116.23 | P11:230:WERE:JECU1_GEN::
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15217 | 116.23 | P11:345:WERE:JECU2_GEN::
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15217 | 116.22 | P11:345:WERE:JECU3_GEN::
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.4 | P11:345:WERE:WOLFU1_GEN::
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15223 | 116.03 | 511435 SNYDER-4 138 588779 TAP_G17-036 138 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15229 | 116.03 | 511453 DUNCAN-4 138 511552 DUNCHERTP4 138 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15229 | 116.03 | 511455 D.E.S.-4 138 511552 DUNCHERTP4 138 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15229 | 116.02 | 511455 D.E.S.-4 138 529344 OMDUNE-4 138 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 114.98 | 511456 O.K.U.-7 345 588760 GEN-2017-033 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15528 | 117.74 | 511456 O.K.U.-7 345 763215 G18-092-TAP 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15542 | 118.31 | 511468 L.E.S.-7 345 762467 G18-015-TAP 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15438 | 117.72 | 511468 L.E.S.-7 345 763215 G18-092-TAP 345 2
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 115.66 | 511468 L.E.S.-7 345 763318 GEN-2018-115 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15223 | 116.05 | 511488 112GORE4 138 511510 LAIRGST4 138 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15234 | 116.11 | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15223 | 116.04 | 511500 CACHE4 138 511510 LAIRGST4 138 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15223 | 116.03 | 511500 CACHE4 138 588779 TAP_G17-036 138 2
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15346 | 116.06 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.1457 | 113.09 | 511553 CHISHOLM7 345 523961 POTTER_CO 7 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.1457 | 113.09 | 511553 CHISHOLM7 345 523961 POTTER_CO 7 345 2
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.14931 | 115.5 | 511553 CHISHOLM7 345 755000 WWDBORDT 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15226 | 116.14 | 511557 CHISHOLM6 230 3WXFMR CHISHOLM6 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15235 | 116.02 | 514801 MINCO 7 345 555234 NSUB345 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15147 | 115.63 | 515375 WWRDEHV7 345 755000 WWDBORDT 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15921 | 120.2 | 515458 BORDER 7 345 560022 CRAWFISH_DR 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15921 | 120.15 | 515458 BORDER 7 345 755000 WWDBORDT 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15231 | 116.02 | 515543 RENFROW7 345 763421 G18-128-TAP 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15218 | 116.12 | 515618 BALKOW 7 345 3WXFMR BALKOW 7 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15218 | 116.13 | 515618 BALKOW 7 345 3WXFMR BALKOW 7 1_Dup1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15227 | 116.04 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15214 | 116.39 | 515634 PALDR1W7 345 3WXFMR PALO2 _1 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.13 | 515677 BADGER 7 345 563170 G15082_1 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15217 | 116.01 | 521017 ONEY 4 138 521089 WASHITA4 138 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.02 | 522800 MU-TULIA 3 115 525179 TULIA_TP 3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.16 | 522892 MU-BROWNFLD2 69.0 526761 BROWNFLD_TP2 69.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.03 | 523090 TEXAS_CNTY 3 115 589380 GEN-2017-100 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15217 | 116.16 | 523093 HITCHLAND 3 115 523174 GOODWELLWND3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.34 | 523097 HITCHLAND 7 345 523112 NOVUS1 7 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.4 | 523097 HITCHLAND 7 345 523215 FREWHELCOL17 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15018 | 114.83 | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.13942 | 112.81 | 523097 HITCHLAND 7 345 523961 POTTER_CO 7 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.45 | 523097 HITCHLAND 7 345 560252 G10-14 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.01 | 523099 TC-DRYTRLS 3 115 588480 A16-010_SUB 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.23 | 523112 NOVUS1 7 345 3WXFMR NOVUS XF2 2
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.04 | 523112 NOVUS1 7 345 3WXFMR XIANA2011198 _1 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15219 | 116.02 | 523118 BUFF_DUNES 7 345 523853 FINNEY 7 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.02 | 523120 COLE 3 115 588860 GEN-2017-047 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15219 | 116.04 | 523172 GWELL_COLL11 34.5 523174 GOODWELLWND3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15219 | 116.04 | 523173 GWELL_COLL21 34.5 523174 GOODWELLWND3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.1523 | 116.01 | 523221 XIT_INTG 6 230 3WXFMR SIEM_T126401 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15242 | 116.07 | 523267 PRINGLE 6 230 3WXFMR ENRCO13617-1 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15242 | 116.06 | 523267 PRINGLE 6 230 523979 HARRNG_EST 6 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15286 | 116.2 | 523309 MOORE_CNTY 6 230 523323 MCDWL_CREEK6 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15256 | 116.12 | 523323 MCDWL_CREEK6 230 523959 POTTER_CO 6 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15196 | 116.45 | 523959 POTTER_CO 6 230 524010 ROLLHILLS 6 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.16301 | 117.19 | 523959 POTTER_CO 6 230 524267 BUSHLAND 6 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.1597 | 118.35 | 523959 POTTER_CO 6 230 525461 NEWHART 6 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.16065 | 121.11 | 523961 POTTER_CO 7 345 3WXFMR WAUK 90343-A 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15224 | 115.74 | 523978 HARRNG_MID 6 230 523979 HARRNG_EST 6 230 @1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15249 | 116.16 | 524267 BUSHLAND 6 230 3WXFMR WH 7001795 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.1713 | 117.94 | 524267 BUSHLAND 6 230 524623 DEAFSMITH 6 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15209 | 116.44 | 524296 SPNSPUR_WND7 345 524299 SPNSPUR_COL7 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15209 | 116.44 | 524299 SPNSPUR_COL7 345 3WXFMR SPNSPUR_COL7 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.1558 | 117.09 | 524415 AMA_SOUTH 6 230 525213 SWISHER 6 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.67 | 524502 NORTON 3 115 524509 FE-TUCMCARI3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15535 | 116.45 | 524575 DS-#25+ 3 115 524597 PANDAHFD 3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15535 | 116.55 | 524575 DS-#25+ 3 115 524630 TIERABLANCA3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.11 | 524604 HEREFRD_SB 2 69.0 524608 HERFRD_STH 2 69.0 *1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15702 | 122.73 | 524623 DEAFSMITH 6 230 760498 G17-146-TAP 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.52 | 524721 DS-#15&#19+2 69.0 524745 CASTRO_CNTY2 69.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15278 | 116.03 | 524770 PLSNT_HILL 6 230 3WXFMR EFAE1100068A 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.19074 | 121.59 | 524875 OASIS 6 230 524885 SN_JUAN_TAP6 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15907 | 117.16 | 524875 OASIS 6 230 524909 ROOSEVELT 6 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.19065 | 121.97 | 524885 SN_JUAN_TAP6 230 527483 CHAVES_CNTY6 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15377 | 116.22 | 524909 ROOSEVELT 6 230 3WXFMR ABB LMM60042 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.77 | 524923 PORTALES 2 69.0 524929 RO-PORT_MTR2 69.0 @1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.42 | 524923 PORTALES 2 69.0 524941 PORTALES#1 2 69.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.66 | 525023 BC-BAIL_MTR2 69.0 525027 BAILEYCO 2 69.0 @1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15324 | 116.55 | 525056 BC-EARTH 3 115 525480 PLANT_X 3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.51 | 525191 KRESS_INT 2 69.0 525203 SW-KRESS 2 69.0 Z1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.6 | 525192 KRESS_INT 3 115 3WXFMR ENRCO 136155 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15508 | 116.83 | 525213 SWISHER 6 230 525461 NEWHART 6 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.15 | 525272 KISER 3 115 3WXFMR VON 13819/1 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.61 | 525326 COX 3 115 3WXFMR ELCO 13474-3 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.61 | 525414 LAMTON 3 115 3WXFMR ASEA MLL9204 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.16483 | 119.68 | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15083 | 118.1 | 525481 PLANT_X 6 230 3WXFMR WH ALM20171 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15923 | 121 | 525481 PLANT_X 6 230 526435 SUNDOWN 6 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15702 | 121.02 | 525481 PLANT_X 6 230 760498 G17-146-TAP 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15392 | 116.49 | 525481 PLANT_X 6 230 762174 G17-218TAP 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15413 | 116.56 | 525481 PLANT_X 6 230 762174 G17-218TAP 230 2
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15854 | 121.7 | 525531 TOLK 6 230 525586 NEEDMORE 6 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.1529 | 118.23 | 525531 TOLK 6 230 525637 LAMB_CNTY 6 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.1757 | 120.42 | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15474 | 116.76 | 525531 TOLK 6 230 762174 G17-218TAP 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15491 | 116.82 | 525531 TOLK 6 230 762174 G17-218TAP 230 2
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15854 | 121.69 | 525586 NEEDMORE 6 230 526935 YOAKUM 6 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.41 | 525599 LC-SANDHLL+2 69.0 525606 AMHERST 2 69.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.45 | 525606 AMHERST 2 69.0 525613 W_LITTLFLD 2 69.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.46 | 525613 W_LITTLFLD 2 69.0 525635 LAMB_CNTY 2 69.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.42 | 525635 LAMB_CNTY 2 69.0 525650 LC-LTTLFLD+2 69.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.1529 | 118.23 | 525637 LAMB_CNTY 6 230 3WXFMR WH ALM20172 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.41 | 525779 FLOYD_CNTY 2 69.0 525790 FLOYDADA_TP2 69.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.29 | 525828 TUCO_INT 3 115 3WXFMR DS F78800913 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.1434 | 118.38 | 525832 TUCO_INT 7 345 526936 YOAKUM_345 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.49 | 526086 SW_6786_N 2 69.0 526087 SW_6786_S 2 69.0 Z1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.49 | 526086 SW_6786_N 2 69.0 526102 SP-HETTLER 2 69.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.56 | 526087 SW_6786_S 2 69.0 526284 PLANTERS 2 69.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.1 | 526160 CARLISLE 3 115 3WXFMR WH RLP38371 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.44 | 526195 QUINCY 3 115 526196 SP-MILWAUKEE 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.34 | 526268 LUBBCK_STH 3 115 3WXFMR NA 70454A 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.6 | 526284 PLANTERS 2 69.0 526297 LUBBCK_EST 2 69.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15223 | 116.47 | 526424 PACIFIC 3 115 526434 SUNDOWN 3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15213 | 116.06 | 526435 SUNDOWN 6 230 3WXFMR UPDATE LATER _12 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15122 | 118.87 | 526435 SUNDOWN 6 230 526460 AMOCO_SS 6 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15122 | 116.5 | 526460 AMOCO_SS 6 230 526935 YOAKUM 6 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15217 | 116.08 | 526525 WOLFFORTH 6 230 3WXFMR UPDATE LATER _13 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.48 | 526735 TERRY_CNTY 2 69.0 526747 LG-BROWNFLD2 69.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15091 | 118.02 | 526935 YOAKUM 6 230 527028 INK_BASIN 6 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15531 | 116.3 | 526936 YOAKUM_345 345 3WXFMR SPX WT04221 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.14032 | 126.57 | 526936 YOAKUM_345 345 527896 HOBBS_INT 7 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15056 | 117.39 | 527028 INK_BASIN 6 230 527894 HOBBS_INT 6 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15196 | 116.43 | 527130 DENVER_N 3 115 527286 HIGGEAST 3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.02 | 527149 MUSTANG 6 230 3WXFMR ENRCO 136161 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15237 | 114.01 | 527149 MUSTANG 6 230 527151 GS-MUSTANG 6 230 @1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.29 | 527202 SEAGRAVES 3 115 3WXFMR ABB MLL92408 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.17 | 527212 DIAMONDBACK3 115 3WXFMR HOW 36773714 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15196 | 116.41 | 527286 HIGGEAST 3 115 527363 HIGG 3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15202 | 116.16 | 527325 OXY_WSEM_TP3 115 527362 JOHNSON_DRW3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.15 | 527340 DOSS 3 115 3WXFMR ELCO 13566/1 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.14 | 527345 LEGACY 2 69.0 527350 XTO_ROBRTSN2 69.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.14 | 527346 LEGACY 3 115 3WXFMR VROL 13735-1 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.12 | 527350 XTO_ROBRTSN2 69.0 527355 BOARDMAN 2 69.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.05 | 527355 BOARDMAN 2 69.0 527365 FLANNAGAN 2 69.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.02 | 527360 MAPCO 3 115 527362 JOHNSON_DRW3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.08 | 527362 JOHNSON_DRW3 115 528775 LE-ERF 3 115 @1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.01 | 527370 TENNECO_TAP2 69.0 527371 TENNECO 2 69.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17031 | 116.35 | 527483 CHAVES_CNTY6 230 527799 EDDY_NORTH 6 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.05 | 527508 PRICE 3 115 527509 PRICE_TAP 3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.02 | 527514 CV-PINE 2 69.0 527563 ROSWLL_INT 2 69.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.05 | 527529 RIACBRSH_TP3 115 527533 SW4J795_E 3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.02 | 527529 RIACBRSH_TP3 115 527536 BRASHER 3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.05 | 527533 SW4J795_E 3 115 527564 ROSWLL_INT 3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.06 | 527563 ROSWLL_INT 2 69.0 527575 SW_4702 2 69.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.154 | 116.1 | 527564 ROSWLL_INT 3 115 527597 TWEEDY 3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.06 | 527575 SW_4702 2 69.0 527589 CV-ORCHARD 2 69.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.02 | 527589 CV-ORCHARD 2 69.0 527619 DEXTER_TP 2 69.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15217 | 116.18 | 527653 MILO_WIND 1 34.5 527655 RSVLT_CC_E 7 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15209 | 116.1 | 527654 RSVLT_CC_W 7 345 527655 RSVLT_CC_E 7 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15209 | 116.36 | 527654 RSVLT_CC_W 7 345 527666 RSVLT_COL1 7 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15204 | 116.3 | 527655 RSVLT_CC_E 7 345 527656 CROSSROADS 7 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15209 | 116.36 | 527666 RSVLT_COL1 7 345 3WXFMR RSVLT_COL1 7 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.15 | 527790 EDDY_SVC 1 8.50 527799 EDDY_NORTH 6 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.1522 | 116.05 | 527864 CUNNINHAM 3 115 528568 MONUMNT_TP 3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15139 | 116.16 | 527865 CUNNIGHM_N 6 230 527867 CUNNIGHM_S 6 230 *1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.14 | 527865 CUNNIGHM_N 6 230 527883 CUNINGHAM3 1 13.8 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15198 | 116.08 | 527865 CUNNIGHM_N 6 230 527963 POTASH_JCT 6 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15194 | 116.02 | 527867 CUNNIGHM_S 6 230 527894 HOBBS_INT 6 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15219 | 116.35 | 527894 HOBBS_INT 6 230 527903 HOBBS_PLT3 1 18.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15284 | 116.23 | 527896 HOBBS_INT 7 345 3WXFMR HICO 68759-1 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15218 | 115.8 | 527965 KIOWA 7 345 528027 RDRUNNER 7 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15222 | 115.81 | 528015 PHANTOM 7 345 528027 RDRUNNER 7 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.11 | 528024 RR_SVC_HV 3 115 528021 RDRUNNR_SVC1 15.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.25 | 528024 RR_SVC_HV 3 115 528025 RDRUNNER 3 115 Z1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 115.81 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.08 | 528025 RDRUNNER 3 115 587990 GEN-2016-121 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.14 | 528222 CHINA_DRAW 3 115 528225 CD_SVC_HV 3 115 Z1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.1522 | 115.82 | 528341 LE-SANANDRS3 115 528627 LE-TXACO_TP3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15207 | 116.06 | 528394 QUAHADA 3 115 528396 XTO_BIGEDDY3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.1522 | 116.01 | 528552 OIL_CENTER 3 115 528554 COOPER_RNCH3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.1522 | 116.02 | 528554 COOPER_RNCH3 115 528581 BYRD_TP 3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.1522 | 116.05 | 528568 MONUMNT_TP 3 115 528581 BYRD_TP 3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15219 | 116.04 | 528596 CARDINAL 3 115 528605 TARGA 3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15219 | 116.06 | 528603 NA_ENRICH 3 115 528605 TARGA 3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.11 | 528617 LE-WAITS 2 69.0 528325 LE-WAITS 3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.03 | 528617 LE-WAITS 2 69.0 528714 LE-FORT_SW 2 69.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.1522 | 116.05 | 528618 LE-LOVINTON2 69.0 528334 LE-NRTH_INT3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.42 | 528626 LE-PLNSINT 2 69.0 526928 PLAINS_INT 3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.42 | 528626 LE-PLNSINT 2 69.0 528709 LE-PLNSGOAB2 69.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.05 | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.11 | 528669 LE-STKLDRTP2 69.0 528740 LE-PLANS_SW2 69.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.3 | 528709 LE-PLNSGOAB2 69.0 528740 LE-PLANS_SW2 69.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.05 | 528709 LE-PLNSGOAB2 69.0 528747 LE-ALLRED 2 69.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.03 | 528714 LE-FORT_SW 2 69.0 528718 LE-NEWTEX 2 69.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.11 | 528735 LE-PLAINSUB2 69.0 528740 LE-PLANS_SW2 69.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.03 | 528775 LE-ERF 3 115 528779 LE-TALLCOTN3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.1521 | 115.79 | 530583 POSTROCK7 345 560082 G16-050-TAP 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 115.81 | 531213 SANTAFE3 115 531408 PIERCVL3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15219 | 116.04 | 531501 BUCKNER7 345 531502 CIMRRN 7 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15219 | 116.04 | 531502 CIMRRN 7 345 531503 CIMRRN 1 34.5 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15208 | 115.75 | 531510 HARBNGR3 115 3WXFMR HARBGR345 _1 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15219 | 116.06 | 532663 LEC U5 24.0 532854 LEC U5 6 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15227 | 116.04 | 532794 ROSEHIL7 345 560053 G15052_T 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15231 | 116.03 | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15219 | 116.06 | 532853 LAWHILL6 230 532854 LEC U5 6 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15219 | 116.01 | 539117 SPRVILL-EHVB 230 539695 SPEARVL6 230 Z1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15219 | 116.02 | 539803 IRONWOOD7 345 3WXFMR IRONWOOD MPT 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.1522 | 116.13 | 542951 HAW G5 1 22.0 543665 HAWTHN5 161 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15219 | 116.17 | 542955 LAC G1 1 22.0 542981 LACYGNE7 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15219 | 116.15 | 542956 LAC G2 1 24.0 542981 LACYGNE7 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15218 | 116.2 | 542957 IAT G1 1 24.0 542982 IATAN 7 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15219 | 116.27 | 542962 IAT G2 1 24.5 542982 IATAN 7 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.03 | 542966 WGARDNR5 161 543105 BULLCRK5 161 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15469 | 115.57 | 560022 CRAWFISH_DR 345 762216 G17-151TAP 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15437 | 116.52 | 560022 CRAWFISH_DR 345 762467 G18-015-TAP 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 112.71 | 560022 CRAWFISH_DR 345 763087 GEN-2018-073 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15549 | 116.84 | 560022 CRAWFISH_DR 345 763215 G18-092-TAP 345 2
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.1521 | 115.8 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.45 | 560252 G10-14 345 560253 G10-14-1 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.18 | 560253 G10-14-1 115 560254 G10-14-SUB1 34.5 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.19 | 560253 G10-14-1 115 560255 G10-14-SUB2 34.5 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.04 | 560581 G06-44-2 34.5 523111 NOVUS1 3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.08 | 560582 G06-44-3 34.5 560577 G06-44 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.07 | 560583 G06-44-4 34.5 560577 G06-44 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 115.72 | 560757 ASGI13_02_1 69.0 560758 ASGI13_02_2 34.5 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 115.72 | 560757 ASGI13_02_1 69.0 562731 WHEATLAND 69.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 115.73 | 560763 ASGI13_03_1 115 560761 ASGI13_03_2 34.5 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.16 | 562015 FIREWHEEL1 34.5 523215 FREWHELCOL17 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.16 | 562016 FIREWHEEL2 34.5 523215 FREWHELCOL17 345 2
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 115.71 | 562323 AGI1202&1305 115 562324 AGI1202&1305 34.5 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 115.73 | 562727 LESBIA 115 562728 SANJONTAP 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 115.72 | 562728 SANJONTAP 115 562729 CAPROCKTAP1 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 115.72 | 562730 CAPROCKTAP2 69.0 562729 CAPROCKTAP1 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 115.72 | 562730 CAPROCKTAP2 69.0 562731 WHEATLAND 69.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.15 | 563171 G15082_2 34.5 563170 G15082_1 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 115.78 | P11:13.8:AEPW:COM1-1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 115.79 | P11:13.8:AEPW:COM2-1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 115.79 | P11:13.8:AEPW:COM3-1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 115.78 | P11:18:AEPW:WELSH1-1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 115.79 | P11:18:AEPW:WELSH3-1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 115.78 | P11:24:AEPW:PIRKEY 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 115.68 | P11:24:AEPW:SWS3-1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 115.74 | P11:24:AEPW:TURKCOAL
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15234 | 116.11 | P12:138:AEPW-OMPA:DUNCAN-4:OMDUNCN4
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.02 | P12:138:AEPW:112GORE4:L.E.S.-4
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15223 | 116.05 | P12:138:AEPW:112GORE4:SNYDER-4
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15223 | 116.05 | 5841_Dup1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.1523 | 115.37 | 584560 GEN-2015-014 115 584561 G15-014XFMR1 34.5 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15229 | 116.08 | P12:138:AEPW:SANTAFE:DUNCAN-4
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.08 | 587991 G16-121XFMR1 34.5 587990 GEN-2016-121 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.01 | 588480 A16-010_SUB 115 3WXFMR A16-010_SUB 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15234 | 116.1 | P12:138:AEPW:DUNCAN-4:L.E.S.-4
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 115.46 | 588761 G17-033XFMR1 34.5 588760 GEN-2017-033 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 115.46 | 588765 G17-033XFMR2 34.5 588760 GEN-2017-033 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.02 | 588861 G17-047XFMR1 34.5 588860 GEN-2017-047 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15206 | 115.79 | P12:138:AEPW:ELKCTY-4:CLINTJC4
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.03 | 589381 G17-100XFMR1 34.5 589380 GEN-2017-100 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.07 | P12:138:AEPW:SHERID4:112GORE4
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15223 | 116.06 | P12:345:AEPW-OKGE:CLARKSV7:MUSKOGE7
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15469 | 117.78 | P12:345:AEPW:L.E.S7:TERRYRD7
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15469 | 117.77 | P12:345:AEPW:L.E.S7:TERRYRD7
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15468 | 117.75 | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15545 | 118.25 | P12:345:AEPW-OKGE:L.E.S.-7:GRACMNT7
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15545 | 118.23 | P12:345:AEPW-OKGE:L.E.S.-7:GRACMNT7
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15528 | 118.8 | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.08 | P22:345:AMMO::LABADIE:1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.08 | P22:345:AMMO::LABADIE:2
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.09 | P22:345:AMMO::LABADIE:3
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.08 | P22:345:AMMO::LABADIE:4
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.07 | P22:345:AMMO::RUSHISLAND:1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.06 | P22:345:AMMO::RUSHISLAND:2
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15222 | 115.79 | P13:138-13.8:AEPW:COMANC-4_#2
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 115.8 | P13:138-13.8:AEPW:S.W.S.-4
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15162 | 115.47 | P13:138-230:AEPW:ELKCTY-4
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15222 | 115.79 | P13:138-24:AEPW:PIRKEY 4
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15226 | 115.69 | P13:138-24:AEPW:S.W.S.-4
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15223 | 115.75 | P13:138-24:AEPW:TURK 4
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15238 | 116.11 | P13:138-345:AEPW:L.E.S.-4_#2
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15222 | 116.02 | P12:500:EES-EAI:KEO:WMPEHV
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15223 | 116.14 | P23:500:EES-EAI:KEO:B4941
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15222 | 116.02 | P23:500:EES-EAI:KEO:B4931
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15223 | 116.13 | P23:500:EES-EAI:KEO:B4921
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15222 | 116.07 | P23:500:EES-EAI:INDEP2:B6126
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15222 | 116.06 | P23:500:EES-EAI:PD:INDEP2:LN:FK479
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15223 | 115.79 | P13:345-18:AEPW:WELSH 7_#1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15223 | 115.79 | P13:345-18:AEPW:WELSH 7_#3
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 115.79 | P13:69-13.8:AEPW:COMANC-2
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.08 | P11:024:DPC:ALMA2:6
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.04 | P11:18:ITCM:EMERYGT1:1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.05 | P11:18:ITCM:EMERYGT2:1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.05 | P11:161:ITCM:MGS CT1:1C
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.05 | P11:161:ITCM:MGS CT2:2C
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15219 | 116.06 | 652537 WHITE 3 345 659286 DEERCREK-BE3 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.1522 | 116.02 | 652568 GROTONSOUTH7 115 659275 GROTON_G-BE7 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15219 | 116.06 | 659286 DEERCREK-BE3 345 3WXFMR DEERCRK KU1A 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.05 | 672601 BD 4 230 672306 BD 6G 18.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.05 | 672610 POPLAR 4 230 672310 POPLAR 1G 18.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.05 | 672610 POPLAR 4 230 672311 POPLAR 2G 18.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.04 | 672621 SHAND 4 230 672321 SHAND 1G 18.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.03 | 672649 CODETTE 4 230 672650 NIPAWIN 4 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.04 | 672696 BRADA 4 230 672699 NBEC 4 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.12 | P23:345:MDU::COYOTE::5707-5712-5715::::
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.3 | P23:345:MEC:CBEC 905
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.25 | P23:345:MEC:CBEC 908
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15222 | 116.04 | P23:345:MEC:GDMEC 901
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15222 | 116.04 | P23:345:MEC:GDMEC 902
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.06 | P23:345:MEC:GDMEC 908
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.17 | P23:345:MEC:RAUN 0180
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.24 | P23:345:MEC:RAUN 0210
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.18 | P23:345:MEC:LOUISA 954
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.19 | P23:345:MEC:LOUISA 964
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.03 | P21:115:XEL:AUTO-SINGLE:CHEMOLT7:LSPOWER7:1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.07 | P21:115:XEL:AUTO-SINGLE:COLVILL7:CANONFLSG7:1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.03 | P21:115:XEL:AUTO-SINGLE:FARIBALTP7:FARIBALTGEN:Z
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.13 | P21:230:OTP:AUTO-SINGLE:SQBUTTE4:YNG24:1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.12 | P23:345:OTP:CENTER 3:3215(1)
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.12 | P23:345:OTP:CENTER 3:3225(1)
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.06 | P12:230:UMZW:# 687 #: FT IN SD. FT-BG1 LINE FAULT
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.06 | P12:230:UMZW:# 3617 #: FT IN SD. FT-BG2 LINE FAULT
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 114.69 | 760494 GEN-2017-146 230 760498 G17-146-TAP 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 114.68 | 760495 G17-146-XFM1 34.5 760494 GEN-2017-146 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 115.46 | 761356 G17-239-XFMR 34.5 761355 GEN-2017-239 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 115.46 | 761359 G17-239-XFMR 34.5 761355 GEN-2017-239 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 115.63 | 761797 G17-187XFM1 34.5 761796 GEN-2017-187 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 115.63 | 761800 G17-187XFM2 34.5 761796 GEN-2017-187 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 110.67 | 762132 GEN-2017-158 230 763252 G18-099-XFM1 34.5 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 110.67 | 762132 GEN-2017-158 230 763255 G18-099-XFM2 34.5 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 111.27 | 762133 G17-158XFM1 34.5 762132 GEN-2017-158 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 111.27 | 762136 G17-158XFM2 34.5 762132 GEN-2017-158 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 113.54 | 762216 G17-151TAP 345 762217 GEN-2017-151 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15469 | 116.85 | 762216 G17-151TAP 345 762467 G18-015-TAP 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 115.27 | 762218 G17-151XFM1 34.5 762217 GEN-2017-151 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 115.27 | 762221 G17-151XFM2 34.5 762217 GEN-2017-151 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 115.27 | 762224 G17-151XFM3 34.5 762217 GEN-2017-151 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 115.27 | 762227 G17-151XFM4 34.5 762217 GEN-2017-151 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 114.55 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 115.11 | 762461 G18-015-XFM1 34.5 762460 GEN-2018-015 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 115.11 | 762464 G18-015-XFM2 34.5 762460 GEN-2018-015 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15357 | 116.42 | 762467 G18-015-TAP 345 763215 G18-092-TAP 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 113.8 | 763087 GEN-2018-073 345 763088 G18-073-XFM1 34.5 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 114.78 | 763087 GEN-2018-073 345 763091 G18-073-XFM2 34.5 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 110.64 | 763120 GEN-2018-081 230 763121 G18-081-XFM1 34.5 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 112.78 | 763120 GEN-2018-081 230 764011 G19-074-XFM1 34.5 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 112.92 | 763186 GEN-2018-089 230 763187 G18-089-XFM1 34.5 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 113.84 | 763208 GEN-2018-092 345 763215 G18-092-TAP 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 114.77 | 763208 GEN-2018-092 345 763220 G18-092-XFM1 34.5 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 114.77 | 763208 GEN-2018-092 345 763223 G18-092-XFM2 34.5 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 112.23 | 763241 GEN-2018-097 230 763242 G18-097-XFM1 34.5 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 113.15 | 763241 GEN-2018-097 230 763296 G18-111-XFM1 34.5 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 112.51 | 763241 GEN-2018-097 230 763307 G18-112-XFM1 34.5 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 112.51 | 763241 GEN-2018-097 230 763310 G18-112-XFM2 34.5 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 112.23 | 763241 GEN-2018-097 230 763395 G18-124-XFM1 34.5 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 112.23 | 763241 GEN-2018-097 230 763398 G18-124-XFM2 34.5 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 115.66 | 763318 GEN-2018-115 345 763319 G18-115-XFM1 34.5 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 114.56 | 763483 GEN-2019-003 230 763605 G19-021-XFM1 34.5 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 115.46 | 763516 GEN-2019-011 345 763517 G19-011-XFM1 34.5 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 115.55 | 763879 GEN-2019-056 115 763880 G19-056XFM1 34.5 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15186 | 116.19 | P42:345:OKGE:SB_BVTY7305
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15205 | 115.75 | P23:345:WERE:BUFF_345-534::
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15205 | 115.75 | P23:345:WERE:BUFF_345-543::
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15217 | 116.23 | P23:345:WERE:JEC_345-15::
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15216 | 116.18 | P23:345:WERE:JEC_345-16::
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15217 | 116.22 | P23:345:WERE:JEC_345-19::
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15217 | 116.22 | P23:345:WERE:JEC_345-20::
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.1522 | 116.39 | P23:345:WERE:WOLF_345-50::
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.39 | P23:345:WERE:WOLF_345-60::
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15222 | 115.8 | P42:345:AEPW:WELSH CB 10620 NBTB+FAULT
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15222 | 115.79 | P41:345:AEPW:WELSH CB 10630 NBTB+FAULT
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 115.79 | P41:345:AEPW:WELSH CB 11670 NBTB+FAULT
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15233 | 115.78 | P41:345:AEPW:WELSH CB 11680 NBTB+FAULT
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 115.78 | P41:345:AEPW:WELSH CB 12540 NBTB+FAULT
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15528 | 117.33 | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15577 | 118.58 | P42:345:AEPW:LAWTON EASTSIDE CB 3413A NBTB+FAULT
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15611 | 118.94 | P42:345:AEPW:LAWTON EASTSIDE CB 3425A NBTB+FAULT
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15541 | 118.96 | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15469 | 117.77 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15469 | 117.77 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15469 | 117.74 | P42:345:AEPW:TERRYRD_CB_3421A_NBTB
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.1522 | 116.18 | P23:345:KCPL:LACYGNE_R2-5::LACYGU2-LACYGNE-STILWELL
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15219 | 115.82 | P45:345:UMZW:# 1328 #: GI IN NE.
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15222 | 115.8 | P23:345:AEPW:WELSH CB 10620 NBTB
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15222 | 115.79 | P23:345:AEPW:WELSH CB 10630 NBTB
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 115.79 | P23:345:AEPW:WELSH CB 11670 NBTB
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15233 | 115.78 | P23:345:AEPW:WELSH CB 11680 NBTB
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 115.78 | P23:345:AEPW:WELSH CB 12540 NBTB
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15528 | 117.74 | P23:345:AEPW:OKLAUNION CB 3401A NBTB
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15577 | 118.58 | P23:345:AEPW:LAWTON EASTSIDE CB 3413A NBTB
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15611 | 118.94 | P23:345:AEPW:LAWTON EASTSIDE CB 3425A NBTB
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15541 | 118.96 | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15469 | 117.77 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15469 | 117.77 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15469 | 117.74 | P23:345:AEPW:TERRYRD_CB_3421A_NBTB
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.05 | P11:161:GMO:DOGWOOD_COMBINED_CYCLE_UNIT_OUTAGE
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.06 | P11:115:SUNC:GARDENCITY_S2:97:531459(2)
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15207 | 115.77 | P12:345:PWT:BUFF-THIS_345_1::
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15207 | 115.77 | P12:345:PWT:BUFF-THIS_345_2::
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15208 | 115.83 | P12:345:PWT:THIS-DGRS_345_1::FUTURE
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15208 | 115.83 | P12:345:PWT:THIS-DGRS_345_2::FUTURE
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15231 | 116.06 | P12:069:WFEC:ANADRKO_WATONGA
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15486 | 117.97 | P23:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15742 | 120.4 | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15486 | 117.97 | P42:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB+FAULT
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15742 | 120.4 | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.14754 | 114.13 | P42:345:OKGE:SB_BVTY7315_PRE19S
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.1519 | 115.62 | P23:345:SUNC:MO_BRK182
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.1519 | 115.62 | P23:345:SUNC:MO_BRK382
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15185 | 115.79 | P23:345:SUNC:MO_BRK188
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15346 | 116.06 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15222 | 115.79 | P12:138-13.8:AEPW:COMANC-4_#1
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15162 | 115.47 | P12:230:AEPW:ELKCITY6:CHISHOLM6
Thermal | 05ALL | 1 | 26SP | GEN-2019-003 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15339 | 116.62 | P12:230:AEPW:SWEETWT6:CHISHOLM6
Thermal | 05ALL | 1 | 26SP | GEN-2019-011 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.05622 | 126.57 | 526936 YOAKUM_345 345 527896 HOBBS_INT 7 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15222 | 116.18 | P23:345:KCPL-WERE:237LACYGNE_R1-6::LACYGU1-LACYGNE-NEOSHO
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15219 | 116.06 | P11:230:WERE:LECU5_GEN::
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.1522 | 116.08 | P11:161:GMO:DOGWOOD_COMBINED_CYCLE_UNIT_OUTAGE_1_1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.02 | P11:20:KACY:NEARMAN N1::N1 OUT OF SERVICE:::
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.1522 | 116.02 | P12:69:KACY:NMGEN-NMISOBUS::NEARMAN N1-NM ISOBUS OPEN:::
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.1522 | 116.02 | P13:20-161:KACY:NEARMAN5-NMISOBUS:NAMEPLATE:NEARMAN N1 GSU:::
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.1522 | 116.02 | P21:20:KACY:546702NMGENN1-546703NMISOBUSC1::::
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.23 | P11:115:SPS:HOBBS1&3:145MW::::
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15227 | 114.72 | P11:115:SPS:MUSTANG1&3:153MW::::
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.1529 | 118.23 | P12:230:SPS:K37::1_TOLK_LAMB:::
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15242 | 116.06 | P12:230:SPS:K43::1_PRNGLE_HARR_E:::
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15225 | 115.81 | P12:230:SPS:K44::1_EPLNT_HARRW:::
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.1519 | 116.22 | P12:115:SPS:T04::1_TRBLNC_CASTRO:::
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15242 | 116.02 | P12:115:SPS:T06::1_SPRMN_PRNGLE:::
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.5 | P12:115:SPS:T21::1_GRSSLND_GRAHAM:::
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.05 | P12:115:SPS:T24B::1_RSWLL_BRSHRF:::
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15229 | 116.05 | P12:115:SPS:T26::1_CHAVES_RSWLCTY:::
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15389 | 116.45 | P12:115:SPS:T28A::1_LAMTON_PLANTX:::
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15279 | 116.02 | P12:115:SPS:T29::1_LAMTON_HALECTR:::
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15374 | 117.27 | P12:115:SPS:T30::1_LAMB_HOCKLY:::
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15374 | 116.37 | P12:115:SPS:T31::1_HOCKLY_SUNDWN:::
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15214 | 116.06 | P12:115:SPS:T35::1_TERRY_YOAKUM:::
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15228 | 116.78 | P12:115:SPS:T45::1_NORRIS_OASIS:::
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15216 | 115.82 | P12:115:SPS:T57::1_MUSTG_SEGRVS:::
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.16085 | 116.03 | P12:115:SPS:T58::1_HERFRD_CARGIL:::
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.16085 | 116.57 | P12:115:SPS:T59::1_CARGIL_CURRY:::
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.02 | P12:115:SPS:T64::1_RNDALL_PULLMN:::
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15313 | 116.38 | P12:115:SPS:T67::1_HAPPY_KRESS:::
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15227 | 115.77 | P12:115:SPS:T68::1_TUCO_FLOYD:::
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15222 | 115.81 | P12:115:SPS:T69::1_LUBBE_CROSBY:::
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.02 | P12:115:SPS:T70::1_COLTR_S_GORG:::
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15215 | 116.63 | P12:115:SPS:T71::1_CRLSLE_YUMA:::
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15233 | 116.1 | P12:115:SPS:T81::1_COX_FLOYD:::
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.26 | P12:115:SPS:T83::1_SP-FKFD_ALLEN:::
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15196 | 116.44 | P12:115:SPS:T89::1_DC_N_HIGG:::
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.07 | P12:115:SPS:T91::1_HIGG_RUSSELL:::
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15227 | 116.02 | P12:115:SPS:V01::1_MOOREW_RVRVIEW:::
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15249 | 116.07 | P12:115:SPS:V04::1_EPLANT_RNDALL:::
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15239 | 116.06 | P12:115:SPS:V07::1_COX_HALECTR:::
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15375 | 116.23 | P12:115:SPS:V09::1_HALECTR_PLANTX:::
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15191 | 116.21 | P12:115:SPS:V12::1_PLANTX_BAILEY:::
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.03 | P12:115:SPS:V15::1_TUCO_INDANA:::
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15177 | 116.16 | P12:115:SPS:V24::1_WOLFTH_TERRY:::
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.154 | 116.07 | P12:115:SPS:V26::1_RSWLL_EDDY_N:::
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.4 | P12:115:SPS:V33::1_LUBBS_LYNN:::
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15324 | 117.14 | P12:115:SPS:V37::1_CASTRO_PLANTX:::
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15222 | 116.05 | P12:115:SPS:V44::1_COLTR_OWENS:::
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.16 | P12:115:SPS:V46::1_ALLEN_WHEELCK:::
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15219 | 116.5 | P12:115:SPS:V49::1_YOAKUM_SHLCO2:::
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15249 | 116.68 | P12:115:SPS:V55::1_SUNDWN_TERRY:::
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15223 | 116.59 | P12:115:SPS:V56::1_COCHRAN_SUNDWN:::
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.09 | P12:115:SPS:V62::1_CRLSLE_INDANA:::
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15344 | 116.07 | P12:115:SPS:V78::2_CURRY_RSVLT:::
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15204 | 116.19 | P12:115:SPS:V81::1_LE-WAIT_LE-LVN:::
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.1522 | 116.06 | P12:115:SPS:V95::1_DC_N_SHLCO2:::
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.02 | P12:115:SPS:W11::1_DC_S_SMINLE:::
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15219 | 116.03 | P12:115:SPS:W12::1_SMINLE_DOSS:::
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15216 | 116.1 | P12:115:SPS:W14::1_SMINLE_GAINES:::
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.1522 | 116.03 | P12:115:SPS:W26::1_CUNGHM_OILCNTR:::
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.61 | P12:115:SPS:W32::1_PRMTR_FE-CLSIN:::
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15202 | 116.26 | P12:115:SPS:W35::1_GAINES_JNSDRW:::
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15535 | 116.59 | P12:115:SPS:W40::1_WCANYON_TRBLNC:::
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15251 | 116.11 | P12:115:SPS:W52::1_NEWHART_KRESS:::
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.67 | P12:115:SPS:W58::1_NORTON_LOPEZ:::
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.25 | P12:115:SPS:W59::1_LOPEZ_CMPBLL:::
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15231 | 116.55 | P12:115:SPS:W62::1_PLSTHL_CURRY:::
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15233 | 116.07 | P12:115:SPS:W63::1_PLSTHL_CURRY:::
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.36 | P12:115:SPS:W64::1_PLSTHL_FE-CLV:::
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15233 | 116.57 | P12:115:SPS:W65::1_PLSTHL_CURRY:::
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.23 | P12:115:SPS:W66::1_PORTA_GREYHUND:::
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15207 | 116.02 | P12:115:SPS:W76::1_QUAHA_PCA:::
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15535 | 116.1 | P12:115:SPS:W77::1_RNDAL_WCANYON:::
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15224 | 116.07 | P12:115:SPS:W99::1_CAPITAN_CHAVES:::
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15219 | 116.05 | P12:115:SPS:U03::1_CARDNL_NEF:::
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15208 | 116.53 | P12:115:SPS:U14::1_DC_STH_INKBSN:::
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15204 | 116.47 | P12:115:SPS:V15::1_INKBSN_LE-WAT:::
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15249 | 116.15 | P12:115:SPS:U16::1_BSHLND_OUTPST:::
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15249 | 116.16 | P12:115:SPS:U17::1_COLTR_OUTPST:::
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15217 | 116.26 | P12:115:SPS:U19::1_DEAN_PLAINS:::
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15249 | 116.07 | P12:115:SPS:U23::1_COLTR_HILSDE:::
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.13943 | 124.36 | P42:345:SPS:YOAKUM:J18####:SLG1:EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.13943 | 124.36 | P43:345:SPS:YOAKUM:TF#####:SLG:EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.13943 | 124.36 | P42:345:SPS:YOAKUM:J17####:SLG:EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.13943 | 124.36 | P42:345:SPS:YOAKUM:J18####:SLG2:EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.1522 | 116.06 | P11:18:HAST:::EGYCTR2G WEC2_LOSS OF WEC 2 GEN_:HV:
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.1522 | 116.06 | P13:18-115:HAST:::EGYCNTR7 XFMR G2WEC 2 GSU_:HV:
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.1522 | 116.08 | P11:161:GMO:DOGWOOD-COMBINED-CYCLE-UNIT-OUTA:::HV:
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15222 | 116.18 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.1522 | 116.18 | P23:345:KCPL:LACYGNE-R2-5:::EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15217 | 116.23 | P11:230:WERE:JECU1-GEN:::HV:
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15219 | 116.06 | P11:230:WERE:LECU5-GEN:::HV:
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15217 | 116.23 | P11:345:WERE:JECU2-GEN:::EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15217 | 116.22 | P11:345:WERE:JECU3-GEN:::EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.4 | P11:345:WERE:WOLFU1-GEN:::EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15207 | 115.77 | P12:345:PWT:BUFF-THIS-345-1:::EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15207 | 115.77 | P12:345:PWT:BUFF-THIS-345-2:::EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15205 | 115.75 | P23:345:WERE:BUFF-345-534:::EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15205 | 115.75 | P23:345:WERE:BUFF-345-543:::EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15217 | 116.23 | P23:345:WERE:JEC-345-15:::EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15216 | 116.18 | P23:345:WERE:JEC-345-16:::EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15217 | 116.22 | P23:345:WERE:JEC-345-19:::EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15217 | 116.22 | P23:345:WERE:JEC-345-20:::EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.1522 | 116.39 | P23:345:WERE:WOLF-345-50:::EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.39 | P23:345:WERE:WOLF-345-60:::EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.34 | P11:022:NPPD:COOPER1G:1:983:::
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15216 | 116.33 | P11:023:NPPD:GENTLM1G:1:757:::
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15216 | 116.35 | P11:024:NPPD:GENTLM2G:2:757:::
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.1522 | 116.01 | P11:161:OPPD:N OMA 5G:LT::HV:
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.1522 | 116.01 | P11:161:OPPD:N OMA 5G:::HV:
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15217 | 116.2 | P13:345:OPPD:NEBCTY1G:::EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15216 | 116.22 | P13:345:OPPD:NEBCTY2G:::EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.1522 | 116.01 | P13:161:OPPD:N OMA 5G:::HV:
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.22 | P22:345:OPPD:S3458 NEBCTY1G:LT::EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15217 | 116.2 | P22:345:OPPD:S3458 NEBCTY1G:::EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.25 | P22:345:OPPD:S3458 NEBCTY2G:LT::EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15216 | 116.22 | P22:345:OPPD:S3458 NEBCTY2G:::EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.22 | P23:345:OPPD:S3458 NEBCTY1G:LT::EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15217 | 116.2 | P23:345:OPPD:S3458 NEBCTY1G:::EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.25 | P23:345:OPPD:S3458 NEBCTY2G:LT::EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15216 | 116.22 | P23:345:OPPD:S3458 NEBCTY2G:::EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 115.8 | P12:115:SUNC:PLYMELL-PIERCEVILLE:::HV::
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15219 | 116.06 | P11:018:UMZB:# 5 #:: DCS IN SD. DEERCREEK_MV::
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.1522 | 116.03 | P11:022:UMZB:# 15 #:: LO IN ND. LELAND OLDS 1_MV::
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15219 | 116.07 | P11:020:UMZB:# 16 #:: LO IN ND. LELAND OLDS 2_MV::
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15218 | 116.14 | P11:023:UMZB:# 31 #:: AVS IN ND. ANTELOPE VALLEY 1_MV::
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15218 | 116.14 | P11:023:UMZB:# 32 #:: AVS IN ND. ANTELOPE VALLEY 2_MV::
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15215 | 116.33 | P11:024:UMZB:# 33 #:: LRS IN WY. LARAMIE RIVER STATION 1_MV::
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.06 | P12:230:UMZW:# 687 #:: FT IN SD. FT-BG1 BRANCH FAULT:HV:
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.06 | P12:230:UMZW:# 3617 #:: FT IN SD. FT-BG2 BRANCH FAULT:HV:
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.06 | P12:230:UMZW:# 4038 #:: BG-FT IN SD. FAULT FOR TRANSMISSION CIRCUIT (BG-FT).:HV:
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.06 | P12:230:UMZW:# 4039 #:: BG-FT IN SD. FAULT FOR TRANSMISSION CIRCUIT (BG-FT).:HV:
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.03 | P13:230:UMZW:# 5135 #:: OA IN SD. FAULT ON TRANSFORMER (2).:HV:
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.03 | P13:230:UMZW:# 5136 #:: OA IN SD. FAULT ON TRANSFORMER (3).:HV:
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15219 | 115.82 | P23:345:UMZW:# 2423 #:: GI IN NE. GI 1596 BKR FAULT:EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15219 | 115.82 | P23:345:UMZW:# 2426 #:: GI IN NE. GI 1592 BKR FAULT:EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15219 | 115.82 | P23:345:UMZW:# 2432 #:: GI IN NE. GI 1092 BKR FAULT:EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15219 | 115.82 | P23:345:UMZW:# 2440 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1092 STUCK BKR:EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15219 | 115.82 | P23:345:UMZW:# 2444 #:: GI IN NE. GI-SWEET BRANCH FAULT & GI 1596 STUCK BKR:EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15219 | 115.82 | P23:345:UMZW:# 2446 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1196 STUCK BKR:EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15219 | 115.82 | P42:345:UMZW:# 2413 #:: FT2 IN SD. FT2-LO2 BRANCH FAULT & FT2 2992 STUCK BKR:EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15219 | 115.82 | P42:345:UMZW:# 2415 #:: FT2 IN SD. FT2-GI BRANCH FAULT & FT2 3392 STUCK BKR:EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15224 | 115.74 | P11:138:WFEC:HUGO1:465MW :::
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.1522 | 116.02 | P11:138:WFEC:MORLND2:132MW:::
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.1522 | 116.03 | P11:138:WFEC:MORLND3:149MW :::
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.1523 | 116.06 | P12:138:WFEC:ANADRKO_CLVLND::::
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15223 | 116.06 | P12:345:OKGE-AEPW:BKRBKR12::::
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15258 | 116.18 | P12:345:OKGE:BKRBKR21::::
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15277 | 116.26 | P12:345:OKGE:BKRBKR24::::
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15468 | 117.75 | P12:345:OKGE-AEPW:BKRBKR25::::
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.1519 | 115.72 | P12:345:OKGE:BKRBKR336::::
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.1519 | 115.72 | P12:345:OKGE:BKRBKR336_2::::
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15545 | 118.25 | P12:345:OKGE-AEPW:BKRBKR366::::
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15545 | 118.23 | P12:345:OKGE-AEPW:BKRBKR366::::
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.1543 | 117.15 | P12:345:OKGE:BKRBKR367::::
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15194 | 115.72 | P12:345:OKGE:BKRBKR4193::::
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15194 | 115.72 | P12:345:OKGE:BKRBKR4194::::
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.02 | P12:345:OKGE:BKRBKR4195::::
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15184 | 115.76 | P12:345:OKGE-SPS:BKRBKR4201::::
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15184 | 115.76 | P12:345:OKGE-SPS:BKRBKR4202::::
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15231 | 116.03 | P12:345:OKGE:BKRBKR421::::
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15187 | 115.6 | P12:345:OKGE:BKRBKR443NEW::::
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15187 | 115.6 | P12:345:OKGE:BKRBKR443NEW2::::
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15205 | 115.79 | P12:345:OKGE-ITC:BKRBKR502::::
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15205 | 115.79 | P12:345:OKGE-ITC:BKRBKR503::::
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15208 | 115.83 | P12:345:OKGE-ITC:BKRBKR502_1::::
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15208 | 115.83 | P12:345:OKGE-ITC:BKRBKR503_1::::
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15215 | 116.33 | P12:345:OKGE:BKRBKR604::::
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15214 | 116.37 | P12:345:OKGE:BKRBKR604_2::::
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15223 | 115.82 | P11:345:OKGE:BKRBKR_GSU07::::
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15223 | 115.81 | P11:345:OKGE:BKRBKR_GSU08::::
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15223 | 115.8 | P11:138:OKGE:BKRBKR_GSU21::::
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15219 | 115.83 | P12:138:OKGE:BKRBKR85_MOS1::::
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15187 | 116.13 | P42:345:OKGE:SB_ARIA7381::::
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15921 | 120.17 | P42:345:OKGE:SB_BVTY7387::::
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15232 | 116.02 | P41:345:OKGE:SB_REUD7381::::
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15231 | 116.03 | P41:345:OKGE:SB_REUD7383::::
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15231 | 116.06 | P41:345:OKGE:SB_REUD7385::::
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15234 | 116.06 | P42:345:OKGE:SB_REUD7389::::
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15219 | 116.05 | P11:115:SUNC:GARDENCITY_S2:103:531459(2):HV:
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15219 | 116.07 | P11:115:SUNC:FORTDDODGE_4:157:539670(4):HV:
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.04 | P11:345:599:CIMARRON1WIND:200:531603(1):EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.47 | P13:115:SUNC:HOLCOMB_GSU:::HV:
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15219 | 116.05 | P13:115:SUNC:S2_GSU:::HV:
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15219 | 116.07 | P13:115:SUNC:FORTDODGE_GSU:::HV:
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15219 | 116.04 | P23:345:SUNC:BU_BRK682:::EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.14 | 300003 1THLG3 24.0 301503 7THOMHLGSU3 345 3
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.01 | 300007 1NM G2 22.0 301537 7NEWMADGSU2 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.01 | 300046 7NEWMAD 345 301537 7NEWMADGSU2 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.14 | 300049 7THOMHL 345 301503 7THOMHLGSU3 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.08 | P11:20:AMMO:1LAB�� G1:1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.08 | P11:20:AMMO:1LAB�� G2:2
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.27 | P11:345:AMMO::CALLAWAY:1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.08 | P11:345:AMMO::LABADIE:3
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.08 | P11:345:AMMO::LABADIE:4
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.07 | P11:345:AMMO::RUSHISLAND:U1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.07 | P11:345:AMMO::RUSHISLAND:U2
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.06 | P11:138:AMMO::SIOUX:2
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 115.83 | P11:24:CLEC::G1DOLHIL:1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.06 | P12:765:AEP:AEP ROCKP-AEP JEFF 765
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 115.78 | P11:HV:EES::PIRKEY 1:1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 115.79 | P11:EHV:EES::WELSH3-1:1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 115.74 | P11:HV:EES::TURKCOAL:1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.25 | P12:EHV:EES::7CALAWY 1:1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15222 | 116.02 | 338056 CHALKBLUFFPV 500 338162 8W.MEMPHIS% 500 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15223 | 115.75 | P12:HV:EES::TURK 4%:1(1)
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15223 | 115.79 | P12:EHV:EES::WELSH 7:1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15223 | 115.79 | P12:EHV:EES::WELSH 7:1(1)
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15222 | 115.79 | P12:HV:EES::PIRKEY 4:1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15223 | 116.06 | P12:EHV:EES::CLARKSV7!:MUSKOGE7!:1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.06 | 344011 7HUGHES 345 344012 7HPW-N 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.08 | 344884 7LABADIE1 345 344894 1LAB G1 20.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.08 | 344885 7LABADIE2 345 344895 1LAB G2 20.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.08 | 344886 7LABADIE3 345 344896 1LAB G3 20.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.08 | 344887 7LABADIE4 345 344897 1LAB G4 20.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.07 | 345667 7RUSH 1 345 345670 1RUSH G1 18.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.06 | 345668 7RUSH 2 345 345671 1RUSH G2 18.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.05 | 345755 4SIOUX 1 138 345756 1SIOUX 1 18.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.05 | 345764 4SIOUX 2 138 345765 1SIOUX 2 18.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.12 | P12:345:MDU::CENTER:COYOTE:1::::
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.12 | P13:345:MDU:COYOTE GSU LOSS:COYOTE::1::::
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.03 | P11:345:MEC:GDMEC CT1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.03 | P11:345:MEC:GDMEC CT2
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.14 | P11:345:MEC:GDMEC ST
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.35 | P11:345:MEC-NPPD:COOPER 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.24 | P11:24:XEL:AUTO-SINGLE:SHERC31G:1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.24 | P11:24:XEL:AUTO-SINGLE:SHERC32G:2
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.33 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.16 | P11:20:XEL:AUTO-SINGLE:PRIS31G:1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.16 | P11:20:XEL:AUTO-SINGLE:PRIS32G:2
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.2 | P11:22:XEL:AUTO-SINGLE:MNTCE31G:1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.16 | P11:20:XEL:AUTO-SINGLE:KING31G:1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.02 | P11:13:XEL:AUTO-SINGLE:HBRS73G:9
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.02 | P11:18:XEL:AUTO-SINGLE:BLKD76G:6
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.22 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.22 | P11:22:GRE:AUTO-SINGLE:GRE-COAL42G:2
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.14 | P11:24:OTP:AUTO-SINGLE:BIGSTN1G:1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.15 | P11:20:OTP:AUTO-SINGLE:CENTER2G:1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.05 | P11:22:OTP:AUTO-SINGLE:CENTER1G:1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.13 | P11:24:OTP:AUTO-SINGLE:COYOTE1G:1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.05 | P11:24:DPC:AUTO-SINGLE:GENOA53G:3
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.03 | P12:115:XEL:AUTO-SINGLE:CHEMOLT7:LSPOWER7:1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.07 | P12:115:XEL:AUTO-SINGLE:COLVILL7:CANONFLSG7:1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.03 | P12:115:XEL:AUTO-SINGLE:FARIBALTP7:FARIBALTGEN:Z
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.13 | P12:230:OTP:AUTO-SINGLE:SQBUTTE4:YNG24:1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.22 | P13:24-345:XEL:AUTO-SINGLE:SHERC31G:SHERCO3:1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.22 | P13:24-345:XEL:AUTO-SINGLE:SHERC32G:SHERCO3:1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.3 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.16 | P13:20-345:XEL:AUTO-SINGLE:PRIS31G:PRISLD3:1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.16 | P13:20-345:XEL:AUTO-SINGLE:PRIS32G:PRISLD3:2
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.2 | P13:22-345:XEL:AUTO-SINGLE:MNTCE31G:MNTCELO3:1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.15 | P13:20-345:XEL:AUTO-SINGLE:KING31G:ASKING3:1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.02 | P13:13-115:XEL:AUTO-SINGLE:HBRS73G:HIBRDGE7:9
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.2 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL41G:GRE-COALCR4:1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.2 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL42G:GRE-COALCR4:1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.13 | P13:230-24:OTP:AUTO-SINGLE:BIGSTON4:BIGSTN1G:1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.13 | P13:20-230:OTP:AUTO-SINGLE:CENTER2G:YNG24:1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.04 | P13:22-230:OTP:AUTO-SINGLE:CENTER1G:CENTER4:1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.12 | P13:24-345:OTP:AUTO-SINGLE:COYOTE1G:COYOTE3:1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.05 | P13:24-161:DPC:AUTO-SINGLE:GENOA53G:GENOA5:1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.07 | P13:24-161:DPC:AUTO-SINGLE:JPM:ALMA5:1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15222 | 116.02 | 38203 J1819 POI 500 337957 8KEO% 500 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15222 | 116.02 | 38203 J1819 POI 500 338056 CHALKBLUFFPV 500 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.13 | P11:115:XEL:RIV COMBINE CYCLE
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.04 | P12:115:XEL:BDS #2 5
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.04 | P11:115:XEL:HBR #6
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.04 | P11:115:XEL:HBR #7
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.16 | P11:115:XEL:HBR #6 7 8
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.16 | P23:345:XEL:8H14 PRI
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.16 | P23:345:XEL:8H17 PRI AS
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.3 | P23:345:XEL:8N28 SHC
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.22 | P23:345:XEL:8N22 SHC
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.22 | P23:345:XEL:8N17 SHC
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.21 | P23:345:XEL:8N8 MNN
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.15 | P23:345:XEL:8P1 KING
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.15 | P23:345:XEL:8P2 KING
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.04 | P23:115:XEL:5P147 IVH AS
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.03 | P11:18:ALTW:AUTO-SINGLE:EMERYST1:1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.03 | P11:22:ALTW:AUTO-SINGLE:LANS54G:4
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.17 | P11:22:ALTW:AUTO-SINGLE:ARNOLD1G:1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.2 | P11:24:ALTW:AUTO-SINGLE:OTTUMW1G:1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.03 | P13:18-161:ALTW:AUTO-SINGLE:EMERYST1:EMERY5:1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.03 | P13:22-161:ALTW:AUTO-SINGLE:LANS54G:LANSINGL15:1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.16 | P13:22-161:ALTW:AUTO-SINGLE:ARNOLD1G:ARNOLD5:1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.19 | P13:24-161:ALTW:AUTO-SINGLE:OTTUMW1G:OTTUMWA5:1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.27 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.34 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.19 | P11:22:MEC:AUTO-SINGLE:NEAL3G:3
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.26 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.19 | P11:24:MEC:AUTO-SINGLE:LOUIS31G:1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.25 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.3 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.17 | P13:345-22:MEC:AUTO-SINGLE:RAUN3:NEAL3G:1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.24 | P13:345-24:MEC:AUTO-SINGLE:RAUN3:NEAL4G:1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.18 | P13:345-24:MEC:AUTO-SINGLE:LOUISA3:LOUIS31G:1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15217 | 116.23 | P11:230:WERE:JECU1_GEN::
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15217 | 116.23 | P11:345:WERE:JECU2_GEN::
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15217 | 116.22 | P11:345:WERE:JECU3_GEN::
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.4 | P11:345:WERE:WOLFU1_GEN::
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15223 | 116.03 | 511435 SNYDER-4 138 588779 TAP_G17-036 138 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15229 | 116.03 | 511453 DUNCAN-4 138 511552 DUNCHERTP4 138 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15229 | 116.03 | 511455 D.E.S.-4 138 511552 DUNCHERTP4 138 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15229 | 116.02 | 511455 D.E.S.-4 138 529344 OMDUNE-4 138 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 114.98 | 511456 O.K.U.-7 345 588760 GEN-2017-033 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15528 | 117.74 | 511456 O.K.U.-7 345 763215 G18-092-TAP 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15542 | 118.31 | 511468 L.E.S.-7 345 762467 G18-015-TAP 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15438 | 117.72 | 511468 L.E.S.-7 345 763215 G18-092-TAP 345 2
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 115.66 | 511468 L.E.S.-7 345 763318 GEN-2018-115 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15223 | 116.05 | 511488 112GORE4 138 511510 LAIRGST4 138 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15234 | 116.11 | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15223 | 116.04 | 511500 CACHE4 138 511510 LAIRGST4 138 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15223 | 116.03 | 511500 CACHE4 138 588779 TAP_G17-036 138 2
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15346 | 116.06 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.1457 | 113.09 | 511553 CHISHOLM7 345 523961 POTTER_CO 7 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.1457 | 113.09 | 511553 CHISHOLM7 345 523961 POTTER_CO 7 345 2
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.14931 | 115.5 | 511553 CHISHOLM7 345 755000 WWDBORDT 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15226 | 116.14 | 511557 CHISHOLM6 230 3WXFMR CHISHOLM6 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15235 | 116.02 | 514801 MINCO 7 345 555234 NSUB345 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15147 | 115.63 | 515375 WWRDEHV7 345 755000 WWDBORDT 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15921 | 120.2 | 515458 BORDER 7 345 560022 CRAWFISH_DR 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15921 | 120.15 | 515458 BORDER 7 345 755000 WWDBORDT 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15231 | 116.02 | 515543 RENFROW7 345 763421 G18-128-TAP 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15218 | 116.12 | 515618 BALKOW 7 345 3WXFMR BALKOW 7 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15218 | 116.13 | 515618 BALKOW 7 345 3WXFMR BALKOW 7 1_Dup1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15227 | 116.04 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15214 | 116.39 | 515634 PALDR1W7 345 3WXFMR PALO2 _1 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.13 | 515677 BADGER 7 345 563170 G15082_1 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15217 | 116.01 | 521017 ONEY 4 138 521089 WASHITA4 138 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.02 | 522800 MU-TULIA 3 115 525179 TULIA_TP 3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.16 | 522892 MU-BROWNFLD2 69.0 526761 BROWNFLD_TP2 69.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.03 | 523090 TEXAS_CNTY 3 115 589380 GEN-2017-100 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15217 | 116.16 | 523093 HITCHLAND 3 115 523174 GOODWELLWND3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.34 | 523097 HITCHLAND 7 345 523112 NOVUS1 7 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.4 | 523097 HITCHLAND 7 345 523215 FREWHELCOL17 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15018 | 114.83 | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.13942 | 112.81 | 523097 HITCHLAND 7 345 523961 POTTER_CO 7 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.45 | 523097 HITCHLAND 7 345 560252 G10-14 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.01 | 523099 TC-DRYTRLS 3 115 588480 A16-010_SUB 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.23 | 523112 NOVUS1 7 345 3WXFMR NOVUS XF2 2
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.04 | 523112 NOVUS1 7 345 3WXFMR XIANA2011198 _1 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15219 | 116.02 | 523118 BUFF_DUNES 7 345 523853 FINNEY 7 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.02 | 523120 COLE 3 115 588860 GEN-2017-047 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15219 | 116.04 | 523172 GWELL_COLL11 34.5 523174 GOODWELLWND3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15219 | 116.04 | 523173 GWELL_COLL21 34.5 523174 GOODWELLWND3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.1523 | 116.01 | 523221 XIT_INTG 6 230 3WXFMR SIEM_T126401 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15242 | 116.07 | 523267 PRINGLE 6 230 3WXFMR ENRCO13617-1 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15242 | 116.06 | 523267 PRINGLE 6 230 523979 HARRNG_EST 6 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15286 | 116.2 | 523309 MOORE_CNTY 6 230 523323 MCDWL_CREEK6 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15256 | 116.12 | 523323 MCDWL_CREEK6 230 523959 POTTER_CO 6 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15196 | 116.45 | 523959 POTTER_CO 6 230 524010 ROLLHILLS 6 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.16301 | 117.19 | 523959 POTTER_CO 6 230 524267 BUSHLAND 6 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.1597 | 118.35 | 523959 POTTER_CO 6 230 525461 NEWHART 6 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.16065 | 121.11 | 523961 POTTER_CO 7 345 3WXFMR WAUK 90343-A 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15224 | 115.74 | 523978 HARRNG_MID 6 230 523979 HARRNG_EST 6 230 @1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15249 | 116.16 | 524267 BUSHLAND 6 230 3WXFMR WH 7001795 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.1713 | 117.94 | 524267 BUSHLAND 6 230 524623 DEAFSMITH 6 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15209 | 116.44 | 524296 SPNSPUR_WND7 345 524299 SPNSPUR_COL7 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15209 | 116.44 | 524299 SPNSPUR_COL7 345 3WXFMR SPNSPUR_COL7 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.1558 | 117.09 | 524415 AMA_SOUTH 6 230 525213 SWISHER 6 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.67 | 524502 NORTON 3 115 524509 FE-TUCMCARI3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15535 | 116.45 | 524575 DS-#25+ 3 115 524597 PANDAHFD 3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15535 | 116.55 | 524575 DS-#25+ 3 115 524630 TIERABLANCA3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.11 | 524604 HEREFRD_SB 2 69.0 524608 HERFRD_STH 2 69.0 *1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15702 | 122.73 | 524623 DEAFSMITH 6 230 760498 G17-146-TAP 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.52 | 524721 DS-#15&#19+2 69.0 524745 CASTRO_CNTY2 69.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15278 | 116.03 | 524770 PLSNT_HILL 6 230 3WXFMR EFAE1100068A 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.19074 | 121.59 | 524875 OASIS 6 230 524885 SN_JUAN_TAP6 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15907 | 117.16 | 524875 OASIS 6 230 524909 ROOSEVELT 6 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.19065 | 121.97 | 524885 SN_JUAN_TAP6 230 527483 CHAVES_CNTY6 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15377 | 116.22 | 524909 ROOSEVELT 6 230 3WXFMR ABB LMM60042 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.77 | 524923 PORTALES 2 69.0 524929 RO-PORT_MTR2 69.0 @1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.42 | 524923 PORTALES 2 69.0 524941 PORTALES#1 2 69.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.66 | 525023 BC-BAIL_MTR2 69.0 525027 BAILEYCO 2 69.0 @1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15324 | 116.55 | 525056 BC-EARTH 3 115 525480 PLANT_X 3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.51 | 525191 KRESS_INT 2 69.0 525203 SW-KRESS 2 69.0 Z1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.6 | 525192 KRESS_INT 3 115 3WXFMR ENRCO 136155 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15508 | 116.83 | 525213 SWISHER 6 230 525461 NEWHART 6 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.15 | 525272 KISER 3 115 3WXFMR VON 13819/1 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.61 | 525326 COX 3 115 3WXFMR ELCO 13474-3 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.61 | 525414 LAMTON 3 115 3WXFMR ASEA MLL9204 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.16483 | 119.68 | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15083 | 118.1 | 525481 PLANT_X 6 230 3WXFMR WH ALM20171 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15923 | 121 | 525481 PLANT_X 6 230 526435 SUNDOWN 6 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15702 | 121.02 | 525481 PLANT_X 6 230 760498 G17-146-TAP 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15392 | 116.49 | 525481 PLANT_X 6 230 762174 G17-218TAP 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15413 | 116.56 | 525481 PLANT_X 6 230 762174 G17-218TAP 230 2
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15854 | 121.7 | 525531 TOLK 6 230 525586 NEEDMORE 6 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.1529 | 118.23 | 525531 TOLK 6 230 525637 LAMB_CNTY 6 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.1757 | 120.42 | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15474 | 116.76 | 525531 TOLK 6 230 762174 G17-218TAP 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15491 | 116.82 | 525531 TOLK 6 230 762174 G17-218TAP 230 2
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15854 | 121.69 | 525586 NEEDMORE 6 230 526935 YOAKUM 6 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.41 | 525599 LC-SANDHLL+2 69.0 525606 AMHERST 2 69.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.45 | 525606 AMHERST 2 69.0 525613 W_LITTLFLD 2 69.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.46 | 525613 W_LITTLFLD 2 69.0 525635 LAMB_CNTY 2 69.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.42 | 525635 LAMB_CNTY 2 69.0 525650 LC-LTTLFLD+2 69.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.1529 | 118.23 | 525637 LAMB_CNTY 6 230 3WXFMR WH ALM20172 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.41 | 525779 FLOYD_CNTY 2 69.0 525790 FLOYDADA_TP2 69.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.29 | 525828 TUCO_INT 3 115 3WXFMR DS F78800913 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.1434 | 118.38 | 525832 TUCO_INT 7 345 526936 YOAKUM_345 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.49 | 526086 SW_6786_N 2 69.0 526087 SW_6786_S 2 69.0 Z1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.49 | 526086 SW_6786_N 2 69.0 526102 SP-HETTLER 2 69.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.56 | 526087 SW_6786_S 2 69.0 526284 PLANTERS 2 69.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.1 | 526160 CARLISLE 3 115 3WXFMR WH RLP38371 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.44 | 526195 QUINCY 3 115 526196 SP-MILWAUKEE 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.34 | 526268 LUBBCK_STH 3 115 3WXFMR NA 70454A 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.6 | 526284 PLANTERS 2 69.0 526297 LUBBCK_EST 2 69.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15223 | 116.47 | 526424 PACIFIC 3 115 526434 SUNDOWN 3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15213 | 116.06 | 526435 SUNDOWN 6 230 3WXFMR UPDATE LATER _12 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15122 | 118.87 | 526435 SUNDOWN 6 230 526460 AMOCO_SS 6 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15122 | 116.5 | 526460 AMOCO_SS 6 230 526935 YOAKUM 6 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15217 | 116.08 | 526525 WOLFFORTH 6 230 3WXFMR UPDATE LATER _13 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.48 | 526735 TERRY_CNTY 2 69.0 526747 LG-BROWNFLD2 69.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15091 | 118.02 | 526935 YOAKUM 6 230 527028 INK_BASIN 6 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15531 | 116.3 | 526936 YOAKUM_345 345 3WXFMR SPX WT04221 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.14032 | 126.57 | 526936 YOAKUM_345 345 527896 HOBBS_INT 7 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15056 | 117.39 | 527028 INK_BASIN 6 230 527894 HOBBS_INT 6 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15196 | 116.43 | 527130 DENVER_N 3 115 527286 HIGGEAST 3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.02 | 527149 MUSTANG 6 230 3WXFMR ENRCO 136161 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15237 | 114.01 | 527149 MUSTANG 6 230 527151 GS-MUSTANG 6 230 @1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.29 | 527202 SEAGRAVES 3 115 3WXFMR ABB MLL92408 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.17 | 527212 DIAMONDBACK3 115 3WXFMR HOW 36773714 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15196 | 116.41 | 527286 HIGGEAST 3 115 527363 HIGG 3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15202 | 116.16 | 527325 OXY_WSEM_TP3 115 527362 JOHNSON_DRW3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.15 | 527340 DOSS 3 115 3WXFMR ELCO 13566/1 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.14 | 527345 LEGACY 2 69.0 527350 XTO_ROBRTSN2 69.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.14 | 527346 LEGACY 3 115 3WXFMR VROL 13735-1 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.12 | 527350 XTO_ROBRTSN2 69.0 527355 BOARDMAN 2 69.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.05 | 527355 BOARDMAN 2 69.0 527365 FLANNAGAN 2 69.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.02 | 527360 MAPCO 3 115 527362 JOHNSON_DRW3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.08 | 527362 JOHNSON_DRW3 115 528775 LE-ERF 3 115 @1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.01 | 527370 TENNECO_TAP2 69.0 527371 TENNECO 2 69.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17031 | 116.35 | 527483 CHAVES_CNTY6 230 527799 EDDY_NORTH 6 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.05 | 527508 PRICE 3 115 527509 PRICE_TAP 3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.02 | 527514 CV-PINE 2 69.0 527563 ROSWLL_INT 2 69.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.05 | 527529 RIACBRSH_TP3 115 527533 SW4J795_E 3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.02 | 527529 RIACBRSH_TP3 115 527536 BRASHER 3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.05 | 527533 SW4J795_E 3 115 527564 ROSWLL_INT 3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.06 | 527563 ROSWLL_INT 2 69.0 527575 SW_4702 2 69.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.154 | 116.1 | 527564 ROSWLL_INT 3 115 527597 TWEEDY 3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.06 | 527575 SW_4702 2 69.0 527589 CV-ORCHARD 2 69.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.02 | 527589 CV-ORCHARD 2 69.0 527619 DEXTER_TP 2 69.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15217 | 116.18 | 527653 MILO_WIND 1 34.5 527655 RSVLT_CC_E 7 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15209 | 116.1 | 527654 RSVLT_CC_W 7 345 527655 RSVLT_CC_E 7 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15209 | 116.36 | 527654 RSVLT_CC_W 7 345 527666 RSVLT_COL1 7 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15204 | 116.3 | 527655 RSVLT_CC_E 7 345 527656 CROSSROADS 7 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15209 | 116.36 | 527666 RSVLT_COL1 7 345 3WXFMR RSVLT_COL1 7 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.15 | 527790 EDDY_SVC 1 8.50 527799 EDDY_NORTH 6 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.1522 | 116.05 | 527864 CUNNINHAM 3 115 528568 MONUMNT_TP 3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15139 | 116.16 | 527865 CUNNIGHM_N 6 230 527867 CUNNIGHM_S 6 230 *1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.14 | 527865 CUNNIGHM_N 6 230 527883 CUNINGHAM3 1 13.8 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15198 | 116.08 | 527865 CUNNIGHM_N 6 230 527963 POTASH_JCT 6 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15194 | 116.02 | 527867 CUNNIGHM_S 6 230 527894 HOBBS_INT 6 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15219 | 116.35 | 527894 HOBBS_INT 6 230 527903 HOBBS_PLT3 1 18.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15284 | 116.23 | 527896 HOBBS_INT 7 345 3WXFMR HICO 68759-1 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15218 | 115.8 | 527965 KIOWA 7 345 528027 RDRUNNER 7 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15222 | 115.81 | 528015 PHANTOM 7 345 528027 RDRUNNER 7 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.11 | 528024 RR_SVC_HV 3 115 528021 RDRUNNR_SVC1 15.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.25 | 528024 RR_SVC_HV 3 115 528025 RDRUNNER 3 115 Z1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 115.81 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.08 | 528025 RDRUNNER 3 115 587990 GEN-2016-121 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.14 | 528222 CHINA_DRAW 3 115 528225 CD_SVC_HV 3 115 Z1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.1522 | 115.82 | 528341 LE-SANANDRS3 115 528627 LE-TXACO_TP3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15207 | 116.06 | 528394 QUAHADA 3 115 528396 XTO_BIGEDDY3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.1522 | 116.01 | 528552 OIL_CENTER 3 115 528554 COOPER_RNCH3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.1522 | 116.02 | 528554 COOPER_RNCH3 115 528581 BYRD_TP 3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.1522 | 116.05 | 528568 MONUMNT_TP 3 115 528581 BYRD_TP 3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15219 | 116.04 | 528596 CARDINAL 3 115 528605 TARGA 3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15219 | 116.06 | 528603 NA_ENRICH 3 115 528605 TARGA 3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.11 | 528617 LE-WAITS 2 69.0 528325 LE-WAITS 3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.03 | 528617 LE-WAITS 2 69.0 528714 LE-FORT_SW 2 69.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.1522 | 116.05 | 528618 LE-LOVINTON2 69.0 528334 LE-NRTH_INT3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.42 | 528626 LE-PLNSINT 2 69.0 526928 PLAINS_INT 3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.42 | 528626 LE-PLNSINT 2 69.0 528709 LE-PLNSGOAB2 69.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.05 | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.11 | 528669 LE-STKLDRTP2 69.0 528740 LE-PLANS_SW2 69.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.3 | 528709 LE-PLNSGOAB2 69.0 528740 LE-PLANS_SW2 69.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.05 | 528709 LE-PLNSGOAB2 69.0 528747 LE-ALLRED 2 69.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.03 | 528714 LE-FORT_SW 2 69.0 528718 LE-NEWTEX 2 69.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.11 | 528735 LE-PLAINSUB2 69.0 528740 LE-PLANS_SW2 69.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.03 | 528775 LE-ERF 3 115 528779 LE-TALLCOTN3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.1521 | 115.79 | 530583 POSTROCK7 345 560082 G16-050-TAP 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 115.81 | 531213 SANTAFE3 115 531408 PIERCVL3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15219 | 116.04 | 531501 BUCKNER7 345 531502 CIMRRN 7 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15219 | 116.04 | 531502 CIMRRN 7 345 531503 CIMRRN 1 34.5 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15208 | 115.75 | 531510 HARBNGR3 115 3WXFMR HARBGR345 _1 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15219 | 116.06 | 532663 LEC U5 24.0 532854 LEC U5 6 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15227 | 116.04 | 532794 ROSEHIL7 345 560053 G15052_T 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15231 | 116.03 | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15219 | 116.06 | 532853 LAWHILL6 230 532854 LEC U5 6 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15219 | 116.01 | 539117 SPRVILL-EHVB 230 539695 SPEARVL6 230 Z1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15219 | 116.02 | 539803 IRONWOOD7 345 3WXFMR IRONWOOD MPT 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.1522 | 116.13 | 542951 HAW G5 1 22.0 543665 HAWTHN5 161 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15219 | 116.17 | 542955 LAC G1 1 22.0 542981 LACYGNE7 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15219 | 116.15 | 542956 LAC G2 1 24.0 542981 LACYGNE7 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15218 | 116.2 | 542957 IAT G1 1 24.0 542982 IATAN 7 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15219 | 116.27 | 542962 IAT G2 1 24.5 542982 IATAN 7 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.03 | 542966 WGARDNR5 161 543105 BULLCRK5 161 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15469 | 115.57 | 560022 CRAWFISH_DR 345 762216 G17-151TAP 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15437 | 116.52 | 560022 CRAWFISH_DR 345 762467 G18-015-TAP 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 112.71 | 560022 CRAWFISH_DR 345 763087 GEN-2018-073 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15549 | 116.84 | 560022 CRAWFISH_DR 345 763215 G18-092-TAP 345 2
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.1521 | 115.8 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.45 | 560252 G10-14 345 560253 G10-14-1 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.18 | 560253 G10-14-1 115 560254 G10-14-SUB1 34.5 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.19 | 560253 G10-14-1 115 560255 G10-14-SUB2 34.5 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.04 | 560581 G06-44-2 34.5 523111 NOVUS1 3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.08 | 560582 G06-44-3 34.5 560577 G06-44 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.07 | 560583 G06-44-4 34.5 560577 G06-44 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 115.72 | 560757 ASGI13_02_1 69.0 560758 ASGI13_02_2 34.5 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 115.72 | 560757 ASGI13_02_1 69.0 562731 WHEATLAND 69.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 115.73 | 560763 ASGI13_03_1 115 560761 ASGI13_03_2 34.5 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.16 | 562015 FIREWHEEL1 34.5 523215 FREWHELCOL17 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.16 | 562016 FIREWHEEL2 34.5 523215 FREWHELCOL17 345 2
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 115.71 | 562323 AGI1202&1305 115 562324 AGI1202&1305 34.5 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 115.73 | 562727 LESBIA 115 562728 SANJONTAP 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 115.72 | 562728 SANJONTAP 115 562729 CAPROCKTAP1 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 115.72 | 562730 CAPROCKTAP2 69.0 562729 CAPROCKTAP1 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 115.72 | 562730 CAPROCKTAP2 69.0 562731 WHEATLAND 69.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.15 | 563171 G15082_2 34.5 563170 G15082_1 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 115.78 | P11:13.8:AEPW:COM1-1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 115.79 | P11:13.8:AEPW:COM2-1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 115.79 | P11:13.8:AEPW:COM3-1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 115.78 | P11:18:AEPW:WELSH1-1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 115.79 | P11:18:AEPW:WELSH3-1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 115.78 | P11:24:AEPW:PIRKEY 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 115.68 | P11:24:AEPW:SWS3-1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 115.74 | P11:24:AEPW:TURKCOAL
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15234 | 116.11 | P12:138:AEPW-OMPA:DUNCAN-4:OMDUNCN4
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.02 | P12:138:AEPW:112GORE4:L.E.S.-4
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15223 | 116.05 | P12:138:AEPW:112GORE4:SNYDER-4
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15223 | 116.05 | 5841_Dup1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.1523 | 115.37 | 584560 GEN-2015-014 115 584561 G15-014XFMR1 34.5 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15229 | 116.08 | P12:138:AEPW:SANTAFE:DUNCAN-4
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.08 | 587991 G16-121XFMR1 34.5 587990 GEN-2016-121 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.01 | 588480 A16-010_SUB 115 3WXFMR A16-010_SUB 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15234 | 116.1 | P12:138:AEPW:DUNCAN-4:L.E.S.-4
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 115.46 | 588761 G17-033XFMR1 34.5 588760 GEN-2017-033 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 115.46 | 588765 G17-033XFMR2 34.5 588760 GEN-2017-033 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.02 | 588861 G17-047XFMR1 34.5 588860 GEN-2017-047 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15206 | 115.79 | P12:138:AEPW:ELKCTY-4:CLINTJC4
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.03 | 589381 G17-100XFMR1 34.5 589380 GEN-2017-100 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.07 | P12:138:AEPW:SHERID4:112GORE4
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15223 | 116.06 | P12:345:AEPW-OKGE:CLARKSV7:MUSKOGE7
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15469 | 117.78 | P12:345:AEPW:L.E.S7:TERRYRD7
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15469 | 117.77 | P12:345:AEPW:L.E.S7:TERRYRD7
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15468 | 117.75 | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15545 | 118.25 | P12:345:AEPW-OKGE:L.E.S.-7:GRACMNT7
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15545 | 118.23 | P12:345:AEPW-OKGE:L.E.S.-7:GRACMNT7
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15528 | 118.8 | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.08 | P22:345:AMMO::LABADIE:1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.08 | P22:345:AMMO::LABADIE:2
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.09 | P22:345:AMMO::LABADIE:3
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.08 | P22:345:AMMO::LABADIE:4
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.07 | P22:345:AMMO::RUSHISLAND:1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.06 | P22:345:AMMO::RUSHISLAND:2
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15222 | 115.79 | P13:138-13.8:AEPW:COMANC-4_#2
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 115.8 | P13:138-13.8:AEPW:S.W.S.-4
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15162 | 115.47 | P13:138-230:AEPW:ELKCTY-4
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15222 | 115.79 | P13:138-24:AEPW:PIRKEY 4
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15226 | 115.69 | P13:138-24:AEPW:S.W.S.-4
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15223 | 115.75 | P13:138-24:AEPW:TURK 4
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15238 | 116.11 | P13:138-345:AEPW:L.E.S.-4_#2
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15222 | 116.02 | P12:500:EES-EAI:KEO:WMPEHV
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15223 | 116.14 | P23:500:EES-EAI:KEO:B4941
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15222 | 116.02 | P23:500:EES-EAI:KEO:B4931
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15223 | 116.13 | P23:500:EES-EAI:KEO:B4921
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15222 | 116.07 | P23:500:EES-EAI:INDEP2:B6126
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15222 | 116.06 | P23:500:EES-EAI:PD:INDEP2:LN:FK479
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15223 | 115.79 | P13:345-18:AEPW:WELSH 7_#1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15223 | 115.79 | P13:345-18:AEPW:WELSH 7_#3
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 115.79 | P13:69-13.8:AEPW:COMANC-2
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.08 | P11:024:DPC:ALMA2:6
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.04 | P11:18:ITCM:EMERYGT1:1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.05 | P11:18:ITCM:EMERYGT2:1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.05 | P11:161:ITCM:MGS CT1:1C
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.05 | P11:161:ITCM:MGS CT2:2C
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15219 | 116.06 | 652537 WHITE 3 345 659286 DEERCREK-BE3 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.1522 | 116.02 | 652568 GROTONSOUTH7 115 659275 GROTON_G-BE7 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15219 | 116.06 | 659286 DEERCREK-BE3 345 3WXFMR DEERCRK KU1A 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.05 | 672601 BD 4 230 672306 BD 6G 18.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.05 | 672610 POPLAR 4 230 672310 POPLAR 1G 18.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.05 | 672610 POPLAR 4 230 672311 POPLAR 2G 18.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.04 | 672621 SHAND 4 230 672321 SHAND 1G 18.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.03 | 672649 CODETTE 4 230 672650 NIPAWIN 4 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.04 | 672696 BRADA 4 230 672699 NBEC 4 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.12 | P23:345:MDU::COYOTE::5707-5712-5715::::
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.3 | P23:345:MEC:CBEC 905
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.25 | P23:345:MEC:CBEC 908
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15222 | 116.04 | P23:345:MEC:GDMEC 901
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15222 | 116.04 | P23:345:MEC:GDMEC 902
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.06 | P23:345:MEC:GDMEC 908
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.17 | P23:345:MEC:RAUN 0180
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.24 | P23:345:MEC:RAUN 0210
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.18 | P23:345:MEC:LOUISA 954
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.19 | P23:345:MEC:LOUISA 964
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.03 | P21:115:XEL:AUTO-SINGLE:CHEMOLT7:LSPOWER7:1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.07 | P21:115:XEL:AUTO-SINGLE:COLVILL7:CANONFLSG7:1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.03 | P21:115:XEL:AUTO-SINGLE:FARIBALTP7:FARIBALTGEN:Z
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.13 | P21:230:OTP:AUTO-SINGLE:SQBUTTE4:YNG24:1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.12 | P23:345:OTP:CENTER 3:3215(1)
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.12 | P23:345:OTP:CENTER 3:3225(1)
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.06 | P12:230:UMZW:# 687 #: FT IN SD. FT-BG1 LINE FAULT
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.06 | P12:230:UMZW:# 3617 #: FT IN SD. FT-BG2 LINE FAULT
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 114.69 | 760494 GEN-2017-146 230 760498 G17-146-TAP 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 114.68 | 760495 G17-146-XFM1 34.5 760494 GEN-2017-146 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 115.46 | 761356 G17-239-XFMR 34.5 761355 GEN-2017-239 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 115.46 | 761359 G17-239-XFMR 34.5 761355 GEN-2017-239 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 115.63 | 761797 G17-187XFM1 34.5 761796 GEN-2017-187 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 115.63 | 761800 G17-187XFM2 34.5 761796 GEN-2017-187 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 110.67 | 762132 GEN-2017-158 230 763252 G18-099-XFM1 34.5 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 110.67 | 762132 GEN-2017-158 230 763255 G18-099-XFM2 34.5 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 111.27 | 762133 G17-158XFM1 34.5 762132 GEN-2017-158 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 111.27 | 762136 G17-158XFM2 34.5 762132 GEN-2017-158 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 113.54 | 762216 G17-151TAP 345 762217 GEN-2017-151 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15469 | 116.85 | 762216 G17-151TAP 345 762467 G18-015-TAP 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 115.27 | 762218 G17-151XFM1 34.5 762217 GEN-2017-151 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 115.27 | 762221 G17-151XFM2 34.5 762217 GEN-2017-151 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 115.27 | 762224 G17-151XFM3 34.5 762217 GEN-2017-151 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 115.27 | 762227 G17-151XFM4 34.5 762217 GEN-2017-151 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 114.55 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 115.11 | 762461 G18-015-XFM1 34.5 762460 GEN-2018-015 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 115.11 | 762464 G18-015-XFM2 34.5 762460 GEN-2018-015 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15357 | 116.42 | 762467 G18-015-TAP 345 763215 G18-092-TAP 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 113.8 | 763087 GEN-2018-073 345 763088 G18-073-XFM1 34.5 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 114.78 | 763087 GEN-2018-073 345 763091 G18-073-XFM2 34.5 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 110.64 | 763120 GEN-2018-081 230 763121 G18-081-XFM1 34.5 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 112.78 | 763120 GEN-2018-081 230 764011 G19-074-XFM1 34.5 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 112.92 | 763186 GEN-2018-089 230 763187 G18-089-XFM1 34.5 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 113.84 | 763208 GEN-2018-092 345 763215 G18-092-TAP 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 114.77 | 763208 GEN-2018-092 345 763220 G18-092-XFM1 34.5 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 114.77 | 763208 GEN-2018-092 345 763223 G18-092-XFM2 34.5 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 112.23 | 763241 GEN-2018-097 230 763242 G18-097-XFM1 34.5 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 113.15 | 763241 GEN-2018-097 230 763296 G18-111-XFM1 34.5 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 112.51 | 763241 GEN-2018-097 230 763307 G18-112-XFM1 34.5 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 112.51 | 763241 GEN-2018-097 230 763310 G18-112-XFM2 34.5 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 112.23 | 763241 GEN-2018-097 230 763395 G18-124-XFM1 34.5 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 112.23 | 763241 GEN-2018-097 230 763398 G18-124-XFM2 34.5 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 115.66 | 763318 GEN-2018-115 345 763319 G18-115-XFM1 34.5 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 112 | 763483 GEN-2019-003 230 763484 G19-003-XFM1 34.5 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 115.46 | 763516 GEN-2019-011 345 763517 G19-011-XFM1 34.5 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 115.55 | 763879 GEN-2019-056 115 763880 G19-056XFM1 34.5 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15186 | 116.19 | P42:345:OKGE:SB_BVTY7305
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15205 | 115.75 | P23:345:WERE:BUFF_345-534::
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15205 | 115.75 | P23:345:WERE:BUFF_345-543::
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15217 | 116.23 | P23:345:WERE:JEC_345-15::
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15216 | 116.18 | P23:345:WERE:JEC_345-16::
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15217 | 116.22 | P23:345:WERE:JEC_345-19::
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15217 | 116.22 | P23:345:WERE:JEC_345-20::
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.1522 | 116.39 | P23:345:WERE:WOLF_345-50::
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.39 | P23:345:WERE:WOLF_345-60::
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15222 | 115.8 | P42:345:AEPW:WELSH CB 10620 NBTB+FAULT
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15222 | 115.79 | P41:345:AEPW:WELSH CB 10630 NBTB+FAULT
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 115.79 | P41:345:AEPW:WELSH CB 11670 NBTB+FAULT
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15233 | 115.78 | P41:345:AEPW:WELSH CB 11680 NBTB+FAULT
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 115.78 | P41:345:AEPW:WELSH CB 12540 NBTB+FAULT
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15528 | 117.33 | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15577 | 118.58 | P42:345:AEPW:LAWTON EASTSIDE CB 3413A NBTB+FAULT
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15611 | 118.94 | P42:345:AEPW:LAWTON EASTSIDE CB 3425A NBTB+FAULT
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15541 | 118.96 | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15469 | 117.77 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15469 | 117.77 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15469 | 117.74 | P42:345:AEPW:TERRYRD_CB_3421A_NBTB
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.1522 | 116.18 | P23:345:KCPL:LACYGNE_R2-5::LACYGU2-LACYGNE-STILWELL
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15219 | 115.82 | P45:345:UMZW:# 1328 #: GI IN NE.
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15222 | 115.8 | P23:345:AEPW:WELSH CB 10620 NBTB
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15222 | 115.79 | P23:345:AEPW:WELSH CB 10630 NBTB
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 115.79 | P23:345:AEPW:WELSH CB 11670 NBTB
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15233 | 115.78 | P23:345:AEPW:WELSH CB 11680 NBTB
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 115.78 | P23:345:AEPW:WELSH CB 12540 NBTB
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15528 | 117.74 | P23:345:AEPW:OKLAUNION CB 3401A NBTB
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15577 | 118.58 | P23:345:AEPW:LAWTON EASTSIDE CB 3413A NBTB
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15611 | 118.94 | P23:345:AEPW:LAWTON EASTSIDE CB 3425A NBTB
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15541 | 118.96 | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15469 | 117.77 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15469 | 117.77 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15469 | 117.74 | P23:345:AEPW:TERRYRD_CB_3421A_NBTB
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.05 | P11:161:GMO:DOGWOOD_COMBINED_CYCLE_UNIT_OUTAGE
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15221 | 116.06 | P11:115:SUNC:GARDENCITY_S2:97:531459(2)
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15207 | 115.77 | P12:345:PWT:BUFF-THIS_345_1::
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15207 | 115.77 | P12:345:PWT:BUFF-THIS_345_2::
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15208 | 115.83 | P12:345:PWT:THIS-DGRS_345_1::FUTURE
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15208 | 115.83 | P12:345:PWT:THIS-DGRS_345_2::FUTURE
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15231 | 116.06 | P12:069:WFEC:ANADRKO_WATONGA
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15486 | 117.97 | P23:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15742 | 120.4 | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15486 | 117.97 | P42:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB+FAULT
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15742 | 120.4 | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.14754 | 114.13 | P42:345:OKGE:SB_BVTY7315_PRE19S
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.1519 | 115.62 | P23:345:SUNC:MO_BRK182
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.1519 | 115.62 | P23:345:SUNC:MO_BRK382
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15185 | 115.79 | P23:345:SUNC:MO_BRK188
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15346 | 116.06 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15222 | 115.79 | P12:138-13.8:AEPW:COMANC-4_#1
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15162 | 115.47 | P12:230:AEPW:ELKCITY6:CHISHOLM6
Thermal | 05ALL | 1 | 26SP | GEN-2019-021 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.15339 | 116.62 | P12:230:AEPW:SWEETWT6:CHISHOLM6
Thermal | 05ALL | 1 | 26SP | GEN-2019-056 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.08185 | 121.11 | 523961 POTTER_CO 7 345 3WXFMR WAUK 90343-A 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.1781 | 116.18 | P23:345:KCPL-WERE:237LACYGNE_R1-6::LACYGU1-LACYGNE-NEOSHO
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17807 | 116.06 | P11:230:WERE:LECU5_GEN::
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.08 | P11:161:GMO:DOGWOOD_COMBINED_CYCLE_UNIT_OUTAGE_1_1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.02 | P11:20:KACY:NEARMAN N1::N1 OUT OF SERVICE:::
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17808 | 116.02 | P12:69:KACY:NMGEN-NMISOBUS::NEARMAN N1-NM ISOBUS OPEN:::
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17808 | 116.02 | P13:20-161:KACY:NEARMAN5-NMISOBUS:NAMEPLATE:NEARMAN N1 GSU:::
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17808 | 116.02 | P21:20:KACY:546702NMGENN1-546703NMISOBUSC1::::
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.23 | P11:115:SPS:HOBBS1&3:145MW::::
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17815 | 114.72 | P11:115:SPS:MUSTANG1&3:153MW::::
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17887 | 118.23 | P12:230:SPS:K37::1_TOLK_LAMB:::
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17831 | 116.06 | P12:230:SPS:K43::1_PRNGLE_HARR_E:::
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17813 | 115.81 | P12:230:SPS:K44::1_EPLNT_HARRW:::
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17827 | 116.22 | P12:115:SPS:T04::1_TRBLNC_CASTRO:::
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17831 | 116.02 | P12:115:SPS:T06::1_SPRMN_PRNGLE:::
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.5 | P12:115:SPS:T21::1_GRSSLND_GRAHAM:::
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.05 | P12:115:SPS:T24B::1_RSWLL_BRSHRF:::
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.1781 | 116.05 | P12:115:SPS:T26::1_CHAVES_RSWLCTY:::
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17951 | 116.45 | P12:115:SPS:T28A::1_LAMTON_PLANTX:::
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17868 | 116.02 | P12:115:SPS:T29::1_LAMTON_HALECTR:::
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.1795 | 117.27 | P12:115:SPS:T30::1_LAMB_HOCKLY:::
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.1795 | 116.37 | P12:115:SPS:T31::1_HOCKLY_SUNDWN:::
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17808 | 116.06 | P12:115:SPS:T35::1_TERRY_YOAKUM:::
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.78 | P12:115:SPS:T45::1_NORRIS_OASIS:::
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.1781 | 115.82 | P12:115:SPS:T57::1_MUSTG_SEGRVS:::
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17876 | 116.03 | P12:115:SPS:T58::1_HERFRD_CARGIL:::
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17876 | 116.57 | P12:115:SPS:T59::1_CARGIL_CURRY:::
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.02 | P12:115:SPS:T64::1_RNDALL_PULLMN:::
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17919 | 116.38 | P12:115:SPS:T67::1_HAPPY_KRESS:::
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17815 | 115.77 | P12:115:SPS:T68::1_TUCO_FLOYD:::
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.1781 | 115.81 | P12:115:SPS:T69::1_LUBBE_CROSBY:::
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.02 | P12:115:SPS:T70::1_COLTR_S_GORG:::
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17804 | 116.63 | P12:115:SPS:T71::1_CRLSLE_YUMA:::
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17822 | 116.1 | P12:115:SPS:T81::1_COX_FLOYD:::
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.26 | P12:115:SPS:T83::1_SP-FKFD_ALLEN:::
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.1781 | 116.44 | P12:115:SPS:T89::1_DC_N_HIGG:::
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.07 | P12:115:SPS:T91::1_HIGG_RUSSELL:::
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17815 | 116.02 | P12:115:SPS:V01::1_MOOREW_RVRVIEW:::
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17834 | 116.07 | P12:115:SPS:V04::1_EPLANT_RNDALL:::
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17826 | 116.06 | P12:115:SPS:V07::1_COX_HALECTR:::
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17947 | 116.23 | P12:115:SPS:V09::1_HALECTR_PLANTX:::
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17811 | 116.21 | P12:115:SPS:V12::1_PLANTX_BAILEY:::
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.03 | P12:115:SPS:V15::1_TUCO_INDANA:::
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17778 | 116.16 | P12:115:SPS:V24::1_WOLFTH_TERRY:::
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17825 | 116.07 | P12:115:SPS:V26::1_RSWLL_EDDY_N:::
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.4 | P12:115:SPS:V33::1_LUBBS_LYNN:::
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17926 | 117.14 | P12:115:SPS:V37::1_CASTRO_PLANTX:::
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.1781 | 116.05 | P12:115:SPS:V44::1_COLTR_OWENS:::
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.16 | P12:115:SPS:V46::1_ALLEN_WHEELCK:::
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17811 | 116.5 | P12:115:SPS:V49::1_YOAKUM_SHLCO2:::
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17868 | 116.68 | P12:115:SPS:V55::1_SUNDWN_TERRY:::
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17834 | 116.59 | P12:115:SPS:V56::1_COCHRAN_SUNDWN:::
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.09 | P12:115:SPS:V62::1_CRLSLE_INDANA:::
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17813 | 116.07 | P12:115:SPS:V78::2_CURRY_RSVLT:::
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17811 | 116.19 | P12:115:SPS:V81::1_LE-WAIT_LE-LVN:::
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.1781 | 116.06 | P12:115:SPS:V95::1_DC_N_SHLCO2:::
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.02 | P12:115:SPS:W11::1_DC_S_SMINLE:::
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.03 | P12:115:SPS:W12::1_SMINLE_DOSS:::
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.1781 | 116.1 | P12:115:SPS:W14::1_SMINLE_GAINES:::
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.03 | P12:115:SPS:W26::1_CUNGHM_OILCNTR:::
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.61 | P12:115:SPS:W32::1_PRMTR_FE-CLSIN:::
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.1781 | 116.26 | P12:115:SPS:W35::1_GAINES_JNSDRW:::
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.18032 | 116.59 | P12:115:SPS:W40::1_WCANYON_TRBLNC:::
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17846 | 116.11 | P12:115:SPS:W52::1_NEWHART_KRESS:::
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.67 | P12:115:SPS:W58::1_NORTON_LOPEZ:::
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.25 | P12:115:SPS:W59::1_LOPEZ_CMPBLL:::
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.1781 | 116.55 | P12:115:SPS:W62::1_PLSTHL_CURRY:::
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17822 | 116.07 | P12:115:SPS:W63::1_PLSTHL_CURRY:::
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.36 | P12:115:SPS:W64::1_PLSTHL_FE-CLV:::
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.1781 | 116.57 | P12:115:SPS:W65::1_PLSTHL_CURRY:::
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.23 | P12:115:SPS:W66::1_PORTA_GREYHUND:::
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17807 | 116.02 | P12:115:SPS:W76::1_QUAHA_PCA:::
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.18032 | 116.1 | P12:115:SPS:W77::1_RNDAL_WCANYON:::
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.1781 | 116.07 | P12:115:SPS:W99::1_CAPITAN_CHAVES:::
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.05 | P12:115:SPS:U03::1_CARDNL_NEF:::
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17808 | 116.53 | P12:115:SPS:U14::1_DC_STH_INKBSN:::
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17811 | 116.47 | P12:115:SPS:V15::1_INKBSN_LE-WAT:::
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17836 | 116.15 | P12:115:SPS:U16::1_BSHLND_OUTPST:::
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17836 | 116.16 | P12:115:SPS:U17::1_COLTR_OUTPST:::
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17828 | 116.26 | P12:115:SPS:U19::1_DEAN_PLAINS:::
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17836 | 116.07 | P12:115:SPS:U23::1_COLTR_HILSDE:::
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17138 | 124.36 | P42:345:SPS:YOAKUM:J18####:SLG1:EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17138 | 124.36 | P43:345:SPS:YOAKUM:TF#####:SLG:EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17138 | 124.36 | P42:345:SPS:YOAKUM:J17####:SLG:EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17138 | 124.36 | P42:345:SPS:YOAKUM:J18####:SLG2:EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17808 | 116.06 | P11:18:HAST:::EGYCTR2G WEC2_LOSS OF WEC 2 GEN_:HV:
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17808 | 116.06 | P13:18-115:HAST:::EGYCNTR7 XFMR G2WEC 2 GSU_:HV:
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.08 | P11:161:GMO:DOGWOOD-COMBINED-CYCLE-UNIT-OUTA:::HV:
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.1781 | 116.18 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17808 | 116.18 | P23:345:KCPL:LACYGNE-R2-5:::EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17805 | 116.23 | P11:230:WERE:JECU1-GEN:::HV:
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17807 | 116.06 | P11:230:WERE:LECU5-GEN:::HV:
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17805 | 116.23 | P11:345:WERE:JECU2-GEN:::EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17805 | 116.22 | P11:345:WERE:JECU3-GEN:::EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.4 | P11:345:WERE:WOLFU1-GEN:::EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17795 | 115.77 | P12:345:PWT:BUFF-THIS-345-1:::EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17795 | 115.77 | P12:345:PWT:BUFF-THIS-345-2:::EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17793 | 115.75 | P23:345:WERE:BUFF-345-534:::EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17793 | 115.75 | P23:345:WERE:BUFF-345-543:::EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17805 | 116.23 | P23:345:WERE:JEC-345-15:::EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17804 | 116.18 | P23:345:WERE:JEC-345-16:::EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17805 | 116.22 | P23:345:WERE:JEC-345-19:::EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17805 | 116.22 | P23:345:WERE:JEC-345-20:::EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.39 | P23:345:WERE:WOLF-345-50:::EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.39 | P23:345:WERE:WOLF-345-60:::EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.34 | P11:022:NPPD:COOPER1G:1:983:::
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17804 | 116.33 | P11:023:NPPD:GENTLM1G:1:757:::
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17804 | 116.35 | P11:024:NPPD:GENTLM2G:2:757:::
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17808 | 116.01 | P11:161:OPPD:N OMA 5G:LT::HV:
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17808 | 116.01 | P11:161:OPPD:N OMA 5G:::HV:
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17805 | 116.2 | P13:345:OPPD:NEBCTY1G:::EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17804 | 116.22 | P13:345:OPPD:NEBCTY2G:::EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17808 | 116.01 | P13:161:OPPD:N OMA 5G:::HV:
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.22 | P22:345:OPPD:S3458 NEBCTY1G:LT::EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17805 | 116.2 | P22:345:OPPD:S3458 NEBCTY1G:::EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.25 | P22:345:OPPD:S3458 NEBCTY2G:LT::EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17804 | 116.22 | P22:345:OPPD:S3458 NEBCTY2G:::EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.22 | P23:345:OPPD:S3458 NEBCTY1G:LT::EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17805 | 116.2 | P23:345:OPPD:S3458 NEBCTY1G:::EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.25 | P23:345:OPPD:S3458 NEBCTY2G:LT::EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17804 | 116.22 | P23:345:OPPD:S3458 NEBCTY2G:::EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 115.8 | P12:115:SUNC:PLYMELL-PIERCEVILLE:::HV::
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17807 | 116.06 | P11:018:UMZB:# 5 #:: DCS IN SD. DEERCREEK_MV::
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17808 | 116.03 | P11:022:UMZB:# 15 #:: LO IN ND. LELAND OLDS 1_MV::
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17807 | 116.07 | P11:020:UMZB:# 16 #:: LO IN ND. LELAND OLDS 2_MV::
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17807 | 116.14 | P11:023:UMZB:# 31 #:: AVS IN ND. ANTELOPE VALLEY 1_MV::
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17807 | 116.14 | P11:023:UMZB:# 32 #:: AVS IN ND. ANTELOPE VALLEY 2_MV::
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17803 | 116.33 | P11:024:UMZB:# 33 #:: LRS IN WY. LARAMIE RIVER STATION 1_MV::
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.06 | P12:230:UMZW:# 687 #:: FT IN SD. FT-BG1 BRANCH FAULT:HV:
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.06 | P12:230:UMZW:# 3617 #:: FT IN SD. FT-BG2 BRANCH FAULT:HV:
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.06 | P12:230:UMZW:# 4038 #:: BG-FT IN SD. FAULT FOR TRANSMISSION CIRCUIT (BG-FT).:HV:
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.06 | P12:230:UMZW:# 4039 #:: BG-FT IN SD. FAULT FOR TRANSMISSION CIRCUIT (BG-FT).:HV:
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.03 | P13:230:UMZW:# 5135 #:: OA IN SD. FAULT ON TRANSFORMER (2).:HV:
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.03 | P13:230:UMZW:# 5136 #:: OA IN SD. FAULT ON TRANSFORMER (3).:HV:
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17808 | 115.82 | P23:345:UMZW:# 2423 #:: GI IN NE. GI 1596 BKR FAULT:EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17808 | 115.82 | P23:345:UMZW:# 2426 #:: GI IN NE. GI 1592 BKR FAULT:EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17808 | 115.82 | P23:345:UMZW:# 2432 #:: GI IN NE. GI 1092 BKR FAULT:EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17808 | 115.82 | P23:345:UMZW:# 2440 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1092 STUCK BKR:EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17808 | 115.82 | P23:345:UMZW:# 2444 #:: GI IN NE. GI-SWEET BRANCH FAULT & GI 1596 STUCK BKR:EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17808 | 115.82 | P23:345:UMZW:# 2446 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1196 STUCK BKR:EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17808 | 115.82 | P42:345:UMZW:# 2413 #:: FT2 IN SD. FT2-LO2 BRANCH FAULT & FT2 2992 STUCK BKR:EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17808 | 115.82 | P42:345:UMZW:# 2415 #:: FT2 IN SD. FT2-GI BRANCH FAULT & FT2 3392 STUCK BKR:EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17812 | 115.74 | P11:138:WFEC:HUGO1:465MW :::
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17808 | 116.02 | P11:138:WFEC:MORLND2:132MW:::
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17808 | 116.03 | P11:138:WFEC:MORLND3:149MW :::
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17818 | 116.06 | P12:138:WFEC:ANADRKO_CLVLND::::
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17812 | 116.06 | P12:345:OKGE-AEPW:BKRBKR12::::
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17846 | 116.18 | P12:345:OKGE:BKRBKR21::::
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17865 | 116.26 | P12:345:OKGE:BKRBKR24::::
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.18056 | 117.75 | P12:345:OKGE-AEPW:BKRBKR25::::
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17778 | 115.72 | P12:345:OKGE:BKRBKR336::::
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17778 | 115.72 | P12:345:OKGE:BKRBKR336_2::::
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.18132 | 118.25 | P12:345:OKGE-AEPW:BKRBKR366::::
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.18132 | 118.23 | P12:345:OKGE-AEPW:BKRBKR366::::
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.18018 | 117.15 | P12:345:OKGE:BKRBKR367::::
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17783 | 115.72 | P12:345:OKGE:BKRBKR4193::::
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17783 | 115.72 | P12:345:OKGE:BKRBKR4194::::
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.02 | P12:345:OKGE:BKRBKR4195::::
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17772 | 115.76 | P12:345:OKGE-SPS:BKRBKR4201::::
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17772 | 115.76 | P12:345:OKGE-SPS:BKRBKR4202::::
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17819 | 116.03 | P12:345:OKGE:BKRBKR421::::
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17776 | 115.6 | P12:345:OKGE:BKRBKR443NEW::::
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17775 | 115.6 | P12:345:OKGE:BKRBKR443NEW2::::
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17793 | 115.79 | P12:345:OKGE-ITC:BKRBKR502::::
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17793 | 115.79 | P12:345:OKGE-ITC:BKRBKR503::::
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17796 | 115.83 | P12:345:OKGE-ITC:BKRBKR502_1::::
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17796 | 115.83 | P12:345:OKGE-ITC:BKRBKR503_1::::
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17803 | 116.33 | P12:345:OKGE:BKRBKR604::::
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17802 | 116.37 | P12:345:OKGE:BKRBKR604_2::::
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17811 | 115.82 | P11:345:OKGE:BKRBKR_GSU07::::
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17811 | 115.81 | P11:345:OKGE:BKRBKR_GSU08::::
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17811 | 115.8 | P11:138:OKGE:BKRBKR_GSU21::::
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17807 | 115.83 | P12:138:OKGE:BKRBKR85_MOS1::::
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17776 | 116.13 | P42:345:OKGE:SB_ARIA7381::::
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.18509 | 120.17 | P42:345:OKGE:SB_BVTY7387::::
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.1782 | 116.02 | P41:345:OKGE:SB_REUD7381::::
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17819 | 116.03 | P41:345:OKGE:SB_REUD7383::::
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17819 | 116.06 | P41:345:OKGE:SB_REUD7385::::
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17822 | 116.06 | P42:345:OKGE:SB_REUD7389::::
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17807 | 116.05 | P11:115:SUNC:GARDENCITY_S2:103:531459(2):HV:
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17807 | 116.07 | P11:115:SUNC:FORTDDODGE_4:157:539670(4):HV:
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.04 | P11:345:599:CIMARRON1WIND:200:531603(1):EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.47 | P13:115:SUNC:HOLCOMB_GSU:::HV:
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17807 | 116.05 | P13:115:SUNC:S2_GSU:::HV:
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17807 | 116.07 | P13:115:SUNC:FORTDODGE_GSU:::HV:
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17807 | 116.04 | P23:345:SUNC:BU_BRK682:::EHV:
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.14 | 300003 1THLG3 24.0 301503 7THOMHLGSU3 345 3
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.01 | 300007 1NM G2 22.0 301537 7NEWMADGSU2 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.01 | 300046 7NEWMAD 345 301537 7NEWMADGSU2 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.14 | 300049 7THOMHL 345 301503 7THOMHLGSU3 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.08 | P11:20:AMMO:1LAB�� G1:1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.08 | P11:20:AMMO:1LAB�� G2:2
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.27 | P11:345:AMMO::CALLAWAY:1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.08 | P11:345:AMMO::LABADIE:3
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.08 | P11:345:AMMO::LABADIE:4
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.07 | P11:345:AMMO::RUSHISLAND:U1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.07 | P11:345:AMMO::RUSHISLAND:U2
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.06 | P11:138:AMMO::SIOUX:2
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 115.83 | P11:24:CLEC::G1DOLHIL:1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.06 | P12:765:AEP:AEP ROCKP-AEP JEFF 765
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 115.78 | P11:HV:EES::PIRKEY 1:1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 115.79 | P11:EHV:EES::WELSH3-1:1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 115.74 | P11:HV:EES::TURKCOAL:1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.25 | P12:EHV:EES::7CALAWY 1:1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.1781 | 116.02 | 338056 CHALKBLUFFPV 500 338162 8W.MEMPHIS% 500 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17811 | 115.75 | P12:HV:EES::TURK 4%:1(1)
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17811 | 115.79 | P12:EHV:EES::WELSH 7:1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17811 | 115.79 | P12:EHV:EES::WELSH 7:1(1)
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.1781 | 115.79 | P12:HV:EES::PIRKEY 4:1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17812 | 116.06 | P12:EHV:EES::CLARKSV7!:MUSKOGE7!:1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.06 | 344011 7HUGHES 345 344012 7HPW-N 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.08 | 344884 7LABADIE1 345 344894 1LAB G1 20.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.08 | 344885 7LABADIE2 345 344895 1LAB G2 20.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.08 | 344886 7LABADIE3 345 344896 1LAB G3 20.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.08 | 344887 7LABADIE4 345 344897 1LAB G4 20.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.07 | 345667 7RUSH 1 345 345670 1RUSH G1 18.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.06 | 345668 7RUSH 2 345 345671 1RUSH G2 18.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.05 | 345755 4SIOUX 1 138 345756 1SIOUX 1 18.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.05 | 345764 4SIOUX 2 138 345765 1SIOUX 2 18.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.12 | P12:345:MDU::CENTER:COYOTE:1::::
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.12 | P13:345:MDU:COYOTE GSU LOSS:COYOTE::1::::
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.03 | P11:345:MEC:GDMEC CT1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.03 | P11:345:MEC:GDMEC CT2
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.14 | P11:345:MEC:GDMEC ST
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.35 | P11:345:MEC-NPPD:COOPER 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.24 | P11:24:XEL:AUTO-SINGLE:SHERC31G:1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.24 | P11:24:XEL:AUTO-SINGLE:SHERC32G:2
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.33 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.16 | P11:20:XEL:AUTO-SINGLE:PRIS31G:1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.16 | P11:20:XEL:AUTO-SINGLE:PRIS32G:2
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.2 | P11:22:XEL:AUTO-SINGLE:MNTCE31G:1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.16 | P11:20:XEL:AUTO-SINGLE:KING31G:1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.02 | P11:13:XEL:AUTO-SINGLE:HBRS73G:9
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.02 | P11:18:XEL:AUTO-SINGLE:BLKD76G:6
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.22 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.22 | P11:22:GRE:AUTO-SINGLE:GRE-COAL42G:2
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.14 | P11:24:OTP:AUTO-SINGLE:BIGSTN1G:1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.15 | P11:20:OTP:AUTO-SINGLE:CENTER2G:1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.05 | P11:22:OTP:AUTO-SINGLE:CENTER1G:1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.13 | P11:24:OTP:AUTO-SINGLE:COYOTE1G:1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.05 | P11:24:DPC:AUTO-SINGLE:GENOA53G:3
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.03 | P12:115:XEL:AUTO-SINGLE:CHEMOLT7:LSPOWER7:1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.07 | P12:115:XEL:AUTO-SINGLE:COLVILL7:CANONFLSG7:1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.03 | P12:115:XEL:AUTO-SINGLE:FARIBALTP7:FARIBALTGEN:Z
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.13 | P12:230:OTP:AUTO-SINGLE:SQBUTTE4:YNG24:1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.22 | P13:24-345:XEL:AUTO-SINGLE:SHERC31G:SHERCO3:1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.22 | P13:24-345:XEL:AUTO-SINGLE:SHERC32G:SHERCO3:1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.3 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.16 | P13:20-345:XEL:AUTO-SINGLE:PRIS31G:PRISLD3:1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.16 | P13:20-345:XEL:AUTO-SINGLE:PRIS32G:PRISLD3:2
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.2 | P13:22-345:XEL:AUTO-SINGLE:MNTCE31G:MNTCELO3:1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.15 | P13:20-345:XEL:AUTO-SINGLE:KING31G:ASKING3:1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.02 | P13:13-115:XEL:AUTO-SINGLE:HBRS73G:HIBRDGE7:9
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.2 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL41G:GRE-COALCR4:1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.2 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL42G:GRE-COALCR4:1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.13 | P13:230-24:OTP:AUTO-SINGLE:BIGSTON4:BIGSTN1G:1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.13 | P13:20-230:OTP:AUTO-SINGLE:CENTER2G:YNG24:1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.04 | P13:22-230:OTP:AUTO-SINGLE:CENTER1G:CENTER4:1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.12 | P13:24-345:OTP:AUTO-SINGLE:COYOTE1G:COYOTE3:1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.05 | P13:24-161:DPC:AUTO-SINGLE:GENOA53G:GENOA5:1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.07 | P13:24-161:DPC:AUTO-SINGLE:JPM:ALMA5:1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.1781 | 116.02 | 38203 J1819 POI 500 337957 8KEO% 500 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.1781 | 116.02 | 38203 J1819 POI 500 338056 CHALKBLUFFPV 500 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.13 | P11:115:XEL:RIV COMBINE CYCLE
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.04 | P12:115:XEL:BDS #2 5
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.04 | P11:115:XEL:HBR #6
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.04 | P11:115:XEL:HBR #7
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.16 | P11:115:XEL:HBR #6 7 8
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.16 | P23:345:XEL:8H14 PRI
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.16 | P23:345:XEL:8H17 PRI AS
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.3 | P23:345:XEL:8N28 SHC
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.22 | P23:345:XEL:8N22 SHC
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.22 | P23:345:XEL:8N17 SHC
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.21 | P23:345:XEL:8N8 MNN
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.15 | P23:345:XEL:8P1 KING
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.15 | P23:345:XEL:8P2 KING
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.04 | P23:115:XEL:5P147 IVH AS
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.03 | P11:18:ALTW:AUTO-SINGLE:EMERYST1:1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.03 | P11:22:ALTW:AUTO-SINGLE:LANS54G:4
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.17 | P11:22:ALTW:AUTO-SINGLE:ARNOLD1G:1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.2 | P11:24:ALTW:AUTO-SINGLE:OTTUMW1G:1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.03 | P13:18-161:ALTW:AUTO-SINGLE:EMERYST1:EMERY5:1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.03 | P13:22-161:ALTW:AUTO-SINGLE:LANS54G:LANSINGL15:1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.16 | P13:22-161:ALTW:AUTO-SINGLE:ARNOLD1G:ARNOLD5:1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.19 | P13:24-161:ALTW:AUTO-SINGLE:OTTUMW1G:OTTUMWA5:1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.27 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.34 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.19 | P11:22:MEC:AUTO-SINGLE:NEAL3G:3
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.26 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.19 | P11:24:MEC:AUTO-SINGLE:LOUIS31G:1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.25 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.3 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.17 | P13:345-22:MEC:AUTO-SINGLE:RAUN3:NEAL3G:1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.24 | P13:345-24:MEC:AUTO-SINGLE:RAUN3:NEAL4G:1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.18 | P13:345-24:MEC:AUTO-SINGLE:LOUISA3:LOUIS31G:1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17805 | 116.23 | P11:230:WERE:JECU1_GEN::
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17805 | 116.23 | P11:345:WERE:JECU2_GEN::
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17805 | 116.22 | P11:345:WERE:JECU3_GEN::
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.4 | P11:345:WERE:WOLFU1_GEN::
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17811 | 116.03 | 511435 SNYDER-4 138 588779 TAP_G17-036 138 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17817 | 116.03 | 511453 DUNCAN-4 138 511552 DUNCHERTP4 138 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17817 | 116.03 | 511455 D.E.S.-4 138 511552 DUNCHERTP4 138 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17817 | 116.02 | 511455 D.E.S.-4 138 529344 OMDUNE-4 138 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 114.98 | 511456 O.K.U.-7 345 588760 GEN-2017-033 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.18116 | 117.74 | 511456 O.K.U.-7 345 763215 G18-092-TAP 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.18129 | 118.31 | 511468 L.E.S.-7 345 762467 G18-015-TAP 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.18026 | 117.72 | 511468 L.E.S.-7 345 763215 G18-092-TAP 345 2
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 115.66 | 511468 L.E.S.-7 345 763318 GEN-2018-115 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17811 | 116.05 | 511488 112GORE4 138 511510 LAIRGST4 138 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17822 | 116.11 | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17811 | 116.04 | 511500 CACHE4 138 511510 LAIRGST4 138 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17811 | 116.03 | 511500 CACHE4 138 588779 TAP_G17-036 138 2
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17936 | 116.06 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17161 | 113.09 | 511553 CHISHOLM7 345 523961 POTTER_CO 7 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17161 | 113.09 | 511553 CHISHOLM7 345 523961 POTTER_CO 7 345 2
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.1752 | 115.5 | 511553 CHISHOLM7 345 755000 WWDBORDT 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17816 | 116.14 | 511557 CHISHOLM6 230 3WXFMR CHISHOLM6 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17823 | 116.02 | 514801 MINCO 7 345 555234 NSUB345 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17735 | 115.63 | 515375 WWRDEHV7 345 755000 WWDBORDT 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.18509 | 120.2 | 515458 BORDER 7 345 560022 CRAWFISH_DR 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.18509 | 120.15 | 515458 BORDER 7 345 755000 WWDBORDT 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17819 | 116.02 | 515543 RENFROW7 345 763421 G18-128-TAP 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17806 | 116.12 | 515618 BALKOW 7 345 3WXFMR BALKOW 7 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17806 | 116.13 | 515618 BALKOW 7 345 3WXFMR BALKOW 7 1_Dup1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17815 | 116.04 | 515621 OPENSKY7 345 560053 G15052_T 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17802 | 116.39 | 515634 PALDR1W7 345 3WXFMR PALO2 _1 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.13 | 515677 BADGER 7 345 563170 G15082_1 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17805 | 116.01 | 521017 ONEY 4 138 521089 WASHITA4 138 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.02 | 522800 MU-TULIA 3 115 525179 TULIA_TP 3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.16 | 522892 MU-BROWNFLD2 69.0 526761 BROWNFLD_TP2 69.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.03 | 523090 TEXAS_CNTY 3 115 589380 GEN-2017-100 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17805 | 116.16 | 523093 HITCHLAND 3 115 523174 GOODWELLWND3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.34 | 523097 HITCHLAND 7 345 523112 NOVUS1 7 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.4 | 523097 HITCHLAND 7 345 523215 FREWHELCOL17 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17606 | 114.83 | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.16538 | 112.81 | 523097 HITCHLAND 7 345 523961 POTTER_CO 7 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.45 | 523097 HITCHLAND 7 345 560252 G10-14 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.01 | 523099 TC-DRYTRLS 3 115 588480 A16-010_SUB 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.23 | 523112 NOVUS1 7 345 3WXFMR NOVUS XF2 2
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.04 | 523112 NOVUS1 7 345 3WXFMR XIANA2011198 _1 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17807 | 116.02 | 523118 BUFF_DUNES 7 345 523853 FINNEY 7 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.02 | 523120 COLE 3 115 588860 GEN-2017-047 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17807 | 116.04 | 523172 GWELL_COLL11 34.5 523174 GOODWELLWND3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17807 | 116.04 | 523173 GWELL_COLL21 34.5 523174 GOODWELLWND3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17819 | 116.01 | 523221 XIT_INTG 6 230 3WXFMR SIEM_T126401 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17831 | 116.07 | 523267 PRINGLE 6 230 3WXFMR ENRCO13617-1 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17831 | 116.06 | 523267 PRINGLE 6 230 523979 HARRNG_EST 6 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17875 | 116.2 | 523309 MOORE_CNTY 6 230 523323 MCDWL_CREEK6 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17845 | 116.12 | 523323 MCDWL_CREEK6 230 523959 POTTER_CO 6 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17783 | 116.45 | 523959 POTTER_CO 6 230 524010 ROLLHILLS 6 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.18821 | 117.19 | 523959 POTTER_CO 6 230 524267 BUSHLAND 6 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.18772 | 118.35 | 523959 POTTER_CO 6 230 525461 NEWHART 6 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.18806 | 121.11 | 523961 POTTER_CO 7 345 3WXFMR WAUK 90343-A 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17812 | 115.74 | 523978 HARRNG_MID 6 230 523979 HARRNG_EST 6 230 @1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17836 | 116.16 | 524267 BUSHLAND 6 230 3WXFMR WH 7001795 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.19604 | 117.94 | 524267 BUSHLAND 6 230 524623 DEAFSMITH 6 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17797 | 116.44 | 524296 SPNSPUR_WND7 345 524299 SPNSPUR_COL7 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17797 | 116.44 | 524299 SPNSPUR_COL7 345 3WXFMR SPNSPUR_COL7 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.1825 | 117.09 | 524415 AMA_SOUTH 6 230 525213 SWISHER 6 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.67 | 524502 NORTON 3 115 524509 FE-TUCMCARI3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.18032 | 116.45 | 524575 DS-#25+ 3 115 524597 PANDAHFD 3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.18032 | 116.55 | 524575 DS-#25+ 3 115 524630 TIERABLANCA3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.11 | 524604 HEREFRD_SB 2 69.0 524608 HERFRD_STH 2 69.0 *1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.19608 | 122.73 | 524623 DEAFSMITH 6 230 760498 G17-146-TAP 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.52 | 524721 DS-#15&#19+2 69.0 524745 CASTRO_CNTY2 69.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17811 | 116.03 | 524770 PLSNT_HILL 6 230 3WXFMR EFAE1100068A 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.18203 | 121.59 | 524875 OASIS 6 230 524885 SN_JUAN_TAP6 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17861 | 117.16 | 524875 OASIS 6 230 524909 ROOSEVELT 6 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.18194 | 121.97 | 524885 SN_JUAN_TAP6 230 527483 CHAVES_CNTY6 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17815 | 116.22 | 524909 ROOSEVELT 6 230 3WXFMR ABB LMM60042 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.1819 | 122.19 | 524909 ROOSEVELT 6 230 525531 TOLK 6 230 2
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.77 | 524923 PORTALES 2 69.0 524929 RO-PORT_MTR2 69.0 @1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.42 | 524923 PORTALES 2 69.0 524941 PORTALES#1 2 69.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.66 | 525023 BC-BAIL_MTR2 69.0 525027 BAILEYCO 2 69.0 @1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17926 | 116.55 | 525056 BC-EARTH 3 115 525480 PLANT_X 3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.51 | 525191 KRESS_INT 2 69.0 525203 SW-KRESS 2 69.0 Z1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.6 | 525192 KRESS_INT 3 115 3WXFMR ENRCO 136155 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.18224 | 116.83 | 525213 SWISHER 6 230 525461 NEWHART 6 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.15 | 525272 KISER 3 115 3WXFMR VON 13819/1 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.61 | 525326 COX 3 115 3WXFMR ELCO 13474-3 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.61 | 525414 LAMTON 3 115 3WXFMR ASEA MLL9204 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.18313 | 118.1 | 525481 PLANT_X 6 230 3WXFMR WH ALM20171 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.19356 | 121 | 525481 PLANT_X 6 230 526435 SUNDOWN 6 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.19608 | 121.02 | 525481 PLANT_X 6 230 760498 G17-146-TAP 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17166 | 116.49 | 525481 PLANT_X 6 230 762174 G17-218TAP 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17088 | 116.56 | 525481 PLANT_X 6 230 762174 G17-218TAP 230 2
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.18648 | 121.7 | 525531 TOLK 6 230 525586 NEEDMORE 6 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17887 | 118.23 | 525531 TOLK 6 230 525637 LAMB_CNTY 6 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.16858 | 116.76 | 525531 TOLK 6 230 762174 G17-218TAP 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.16792 | 116.82 | 525531 TOLK 6 230 762174 G17-218TAP 230 2
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.18648 | 121.69 | 525586 NEEDMORE 6 230 526935 YOAKUM 6 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.41 | 525599 LC-SANDHLL+2 69.0 525606 AMHERST 2 69.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.45 | 525606 AMHERST 2 69.0 525613 W_LITTLFLD 2 69.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.46 | 525613 W_LITTLFLD 2 69.0 525635 LAMB_CNTY 2 69.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.42 | 525635 LAMB_CNTY 2 69.0 525650 LC-LTTLFLD+2 69.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17887 | 118.23 | 525637 LAMB_CNTY 6 230 3WXFMR WH ALM20172 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.41 | 525779 FLOYD_CNTY 2 69.0 525790 FLOYDADA_TP2 69.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.29 | 525828 TUCO_INT 3 115 3WXFMR DS F78800913 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.1711 | 118.38 | 525832 TUCO_INT 7 345 526936 YOAKUM_345 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.49 | 526086 SW_6786_N 2 69.0 526087 SW_6786_S 2 69.0 Z1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.49 | 526086 SW_6786_N 2 69.0 526102 SP-HETTLER 2 69.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.56 | 526087 SW_6786_S 2 69.0 526284 PLANTERS 2 69.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.1 | 526160 CARLISLE 3 115 3WXFMR WH RLP38371 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.44 | 526195 QUINCY 3 115 526196 SP-MILWAUKEE 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.34 | 526268 LUBBCK_STH 3 115 3WXFMR NA 70454A 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.6 | 526284 PLANTERS 2 69.0 526297 LUBBCK_EST 2 69.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17834 | 116.47 | 526424 PACIFIC 3 115 526434 SUNDOWN 3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17813 | 116.06 | 526435 SUNDOWN 6 230 3WXFMR UPDATE LATER _12 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.18017 | 118.87 | 526435 SUNDOWN 6 230 526460 AMOCO_SS 6 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.18017 | 116.5 | 526460 AMOCO_SS 6 230 526935 YOAKUM 6 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.08 | 526525 WOLFFORTH 6 230 3WXFMR UPDATE LATER _13 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.48 | 526735 TERRY_CNTY 2 69.0 526747 LG-BROWNFLD2 69.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17822 | 118.02 | 526935 YOAKUM 6 230 527028 INK_BASIN 6 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.18275 | 116.3 | 526936 YOAKUM_345 345 3WXFMR SPX WT04221 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17216 | 126.57 | 526936 YOAKUM_345 345 527896 HOBBS_INT 7 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17819 | 117.39 | 527028 INK_BASIN 6 230 527894 HOBBS_INT 6 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.1781 | 116.43 | 527130 DENVER_N 3 115 527286 HIGGEAST 3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.1781 | 116.02 | 527149 MUSTANG 6 230 3WXFMR ENRCO 136161 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17825 | 114.01 | 527149 MUSTANG 6 230 527151 GS-MUSTANG 6 230 @1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.29 | 527202 SEAGRAVES 3 115 3WXFMR ABB MLL92408 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.17 | 527212 DIAMONDBACK3 115 3WXFMR HOW 36773714 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.1781 | 116.41 | 527286 HIGGEAST 3 115 527363 HIGG 3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.1781 | 116.16 | 527325 OXY_WSEM_TP3 115 527362 JOHNSON_DRW3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.15 | 527340 DOSS 3 115 3WXFMR ELCO 13566/1 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.14 | 527345 LEGACY 2 69.0 527350 XTO_ROBRTSN2 69.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.14 | 527346 LEGACY 3 115 3WXFMR VROL 13735-1 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.12 | 527350 XTO_ROBRTSN2 69.0 527355 BOARDMAN 2 69.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.05 | 527355 BOARDMAN 2 69.0 527365 FLANNAGAN 2 69.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.02 | 527360 MAPCO 3 115 527362 JOHNSON_DRW3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.08 | 527362 JOHNSON_DRW3 115 528775 LE-ERF 3 115 @1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.01 | 527370 TENNECO_TAP2 69.0 527371 TENNECO 2 69.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17973 | 116.35 | 527483 CHAVES_CNTY6 230 527799 EDDY_NORTH 6 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.05 | 527508 PRICE 3 115 527509 PRICE_TAP 3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.02 | 527514 CV-PINE 2 69.0 527563 ROSWLL_INT 2 69.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.05 | 527529 RIACBRSH_TP3 115 527533 SW4J795_E 3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.02 | 527529 RIACBRSH_TP3 115 527536 BRASHER 3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.05 | 527533 SW4J795_E 3 115 527564 ROSWLL_INT 3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.06 | 527563 ROSWLL_INT 2 69.0 527575 SW_4702 2 69.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17825 | 116.1 | 527564 ROSWLL_INT 3 115 527597 TWEEDY 3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.06 | 527575 SW_4702 2 69.0 527589 CV-ORCHARD 2 69.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.02 | 527589 CV-ORCHARD 2 69.0 527619 DEXTER_TP 2 69.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17805 | 116.18 | 527653 MILO_WIND 1 34.5 527655 RSVLT_CC_E 7 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17797 | 116.1 | 527654 RSVLT_CC_W 7 345 527655 RSVLT_CC_E 7 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17797 | 116.36 | 527654 RSVLT_CC_W 7 345 527666 RSVLT_COL1 7 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17793 | 116.3 | 527655 RSVLT_CC_E 7 345 527656 CROSSROADS 7 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17797 | 116.36 | 527666 RSVLT_COL1 7 345 3WXFMR RSVLT_COL1 7 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.15 | 527790 EDDY_SVC 1 8.50 527799 EDDY_NORTH 6 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.05 | 527864 CUNNINHAM 3 115 528568 MONUMNT_TP 3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17799 | 116.16 | 527865 CUNNIGHM_N 6 230 527867 CUNNIGHM_S 6 230 *1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.14 | 527865 CUNNIGHM_N 6 230 527883 CUNINGHAM3 1 13.8 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17806 | 116.08 | 527865 CUNNIGHM_N 6 230 527963 POTASH_JCT 6 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17806 | 116.02 | 527867 CUNNIGHM_S 6 230 527894 HOBBS_INT 6 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17807 | 116.35 | 527894 HOBBS_INT 6 230 527903 HOBBS_PLT3 1 18.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17821 | 116.23 | 527896 HOBBS_INT 7 345 3WXFMR HICO 68759-1 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 115.8 | 527965 KIOWA 7 345 528027 RDRUNNER 7 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 115.81 | 528015 PHANTOM 7 345 528027 RDRUNNER 7 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.11 | 528024 RR_SVC_HV 3 115 528021 RDRUNNR_SVC1 15.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.25 | 528024 RR_SVC_HV 3 115 528025 RDRUNNER 3 115 Z1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 115.81 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.08 | 528025 RDRUNNER 3 115 587990 GEN-2016-121 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.14 | 528222 CHINA_DRAW 3 115 528225 CD_SVC_HV 3 115 Z1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 115.82 | 528341 LE-SANANDRS3 115 528627 LE-TXACO_TP3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17807 | 116.06 | 528394 QUAHADA 3 115 528396 XTO_BIGEDDY3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.01 | 528552 OIL_CENTER 3 115 528554 COOPER_RNCH3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.02 | 528554 COOPER_RNCH3 115 528581 BYRD_TP 3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.05 | 528568 MONUMNT_TP 3 115 528581 BYRD_TP 3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.04 | 528596 CARDINAL 3 115 528605 TARGA 3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.06 | 528603 NA_ENRICH 3 115 528605 TARGA 3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.11 | 528617 LE-WAITS 2 69.0 528325 LE-WAITS 3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.03 | 528617 LE-WAITS 2 69.0 528714 LE-FORT_SW 2 69.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.1781 | 116.05 | 528618 LE-LOVINTON2 69.0 528334 LE-NRTH_INT3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.42 | 528626 LE-PLNSINT 2 69.0 526928 PLAINS_INT 3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.42 | 528626 LE-PLNSINT 2 69.0 528709 LE-PLNSGOAB2 69.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.05 | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.11 | 528669 LE-STKLDRTP2 69.0 528740 LE-PLANS_SW2 69.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.3 | 528709 LE-PLNSGOAB2 69.0 528740 LE-PLANS_SW2 69.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.05 | 528709 LE-PLNSGOAB2 69.0 528747 LE-ALLRED 2 69.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.03 | 528714 LE-FORT_SW 2 69.0 528718 LE-NEWTEX 2 69.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.11 | 528735 LE-PLAINSUB2 69.0 528740 LE-PLANS_SW2 69.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.03 | 528775 LE-ERF 3 115 528779 LE-TALLCOTN3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17798 | 115.79 | 530583 POSTROCK7 345 560082 G16-050-TAP 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 115.81 | 531213 SANTAFE3 115 531408 PIERCVL3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17807 | 116.04 | 531501 BUCKNER7 345 531502 CIMRRN 7 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17807 | 116.04 | 531502 CIMRRN 7 345 531503 CIMRRN 1 34.5 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17796 | 115.75 | 531510 HARBNGR3 115 3WXFMR HARBGR345 _1 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17807 | 116.06 | 532663 LEC U5 24.0 532854 LEC U5 6 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17815 | 116.04 | 532794 ROSEHIL7 345 560053 G15052_T 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17819 | 116.03 | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17807 | 116.06 | 532853 LAWHILL6 230 532854 LEC U5 6 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17807 | 116.01 | 539117 SPRVILL-EHVB 230 539695 SPEARVL6 230 Z1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17807 | 116.02 | 539803 IRONWOOD7 345 3WXFMR IRONWOOD MPT 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17808 | 116.13 | 542951 HAW G5 1 22.0 543665 HAWTHN5 161 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17808 | 116.17 | 542955 LAC G1 1 22.0 542981 LACYGNE7 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17807 | 116.15 | 542956 LAC G2 1 24.0 542981 LACYGNE7 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17806 | 116.2 | 542957 IAT G1 1 24.0 542982 IATAN 7 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17807 | 116.27 | 542962 IAT G2 1 24.5 542982 IATAN 7 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.03 | 542966 WGARDNR5 161 543105 BULLCRK5 161 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.18057 | 115.57 | 560022 CRAWFISH_DR 345 762216 G17-151TAP 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.18025 | 116.52 | 560022 CRAWFISH_DR 345 762467 G18-015-TAP 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 112.71 | 560022 CRAWFISH_DR 345 763087 GEN-2018-073 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.18137 | 116.84 | 560022 CRAWFISH_DR 345 763215 G18-092-TAP 345 2
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17798 | 115.8 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.45 | 560252 G10-14 345 560253 G10-14-1 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.18 | 560253 G10-14-1 115 560254 G10-14-SUB1 34.5 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.19 | 560253 G10-14-1 115 560255 G10-14-SUB2 34.5 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.04 | 560581 G06-44-2 34.5 523111 NOVUS1 3 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.08 | 560582 G06-44-3 34.5 560577 G06-44 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.07 | 560583 G06-44-4 34.5 560577 G06-44 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 115.72 | 560757 ASGI13_02_1 69.0 560758 ASGI13_02_2 34.5 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 115.72 | 560757 ASGI13_02_1 69.0 562731 WHEATLAND 69.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 115.73 | 560763 ASGI13_03_1 115 560761 ASGI13_03_2 34.5 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.16 | 562015 FIREWHEEL1 34.5 523215 FREWHELCOL17 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.16 | 562016 FIREWHEEL2 34.5 523215 FREWHELCOL17 345 2
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 115.71 | 562323 AGI1202&1305 115 562324 AGI1202&1305 34.5 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 115.73 | 562727 LESBIA 115 562728 SANJONTAP 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 115.72 | 562728 SANJONTAP 115 562729 CAPROCKTAP1 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 115.72 | 562730 CAPROCKTAP2 69.0 562729 CAPROCKTAP1 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 115.72 | 562730 CAPROCKTAP2 69.0 562731 WHEATLAND 69.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.15 | 563171 G15082_2 34.5 563170 G15082_1 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 115.78 | P11:13.8:AEPW:COM1-1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 115.79 | P11:13.8:AEPW:COM2-1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 115.79 | P11:13.8:AEPW:COM3-1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 115.78 | P11:18:AEPW:WELSH1-1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 115.79 | P11:18:AEPW:WELSH3-1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 115.78 | P11:24:AEPW:PIRKEY 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 115.68 | P11:24:AEPW:SWS3-1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 115.74 | P11:24:AEPW:TURKCOAL
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17822 | 116.11 | P12:138:AEPW-OMPA:DUNCAN-4:OMDUNCN4
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.02 | P12:138:AEPW:112GORE4:L.E.S.-4
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17811 | 116.05 | P12:138:AEPW:112GORE4:SNYDER-4
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17811 | 116.05 | 5841_Dup1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17818 | 115.37 | 584560 GEN-2015-014 115 584561 G15-014XFMR1 34.5 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17817 | 116.08 | P12:138:AEPW:SANTAFE:DUNCAN-4
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.08 | 587991 G16-121XFMR1 34.5 587990 GEN-2016-121 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.01 | 588480 A16-010_SUB 115 3WXFMR A16-010_SUB 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17822 | 116.1 | P12:138:AEPW:DUNCAN-4:L.E.S.-4
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 115.46 | 588761 G17-033XFMR1 34.5 588760 GEN-2017-033 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 115.46 | 588765 G17-033XFMR2 34.5 588760 GEN-2017-033 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.02 | 588861 G17-047XFMR1 34.5 588860 GEN-2017-047 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17795 | 115.79 | P12:138:AEPW:ELKCTY-4:CLINTJC4
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.03 | 589381 G17-100XFMR1 34.5 589380 GEN-2017-100 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.07 | P12:138:AEPW:SHERID4:112GORE4
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17812 | 116.06 | P12:345:AEPW-OKGE:CLARKSV7:MUSKOGE7
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.18057 | 117.78 | P12:345:AEPW:L.E.S7:TERRYRD7
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.18057 | 117.77 | P12:345:AEPW:L.E.S7:TERRYRD7
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.18056 | 117.75 | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.18132 | 118.25 | P12:345:AEPW-OKGE:L.E.S.-7:GRACMNT7
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.18132 | 118.23 | P12:345:AEPW-OKGE:L.E.S.-7:GRACMNT7
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.18116 | 118.8 | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.08 | P22:345:AMMO::LABADIE:1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.08 | P22:345:AMMO::LABADIE:2
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.09 | P22:345:AMMO::LABADIE:3
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.08 | P22:345:AMMO::LABADIE:4
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.07 | P22:345:AMMO::RUSHISLAND:1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.06 | P22:345:AMMO::RUSHISLAND:2
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.1781 | 115.79 | P13:138-13.8:AEPW:COMANC-4_#2
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 115.8 | P13:138-13.8:AEPW:S.W.S.-4
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.1775 | 115.47 | P13:138-230:AEPW:ELKCTY-4
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.1781 | 115.79 | P13:138-24:AEPW:PIRKEY 4
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17814 | 115.69 | P13:138-24:AEPW:S.W.S.-4
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17811 | 115.75 | P13:138-24:AEPW:TURK 4
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17826 | 116.11 | P13:138-345:AEPW:L.E.S.-4_#2
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.1781 | 116.02 | P12:500:EES-EAI:KEO:WMPEHV
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17811 | 116.14 | P23:500:EES-EAI:KEO:B4941
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.1781 | 116.02 | P23:500:EES-EAI:KEO:B4931
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17811 | 116.13 | P23:500:EES-EAI:KEO:B4921
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.1781 | 116.07 | P23:500:EES-EAI:INDEP2:B6126
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.1781 | 116.06 | P23:500:EES-EAI:PD:INDEP2:LN:FK479
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17811 | 115.79 | P13:345-18:AEPW:WELSH 7_#1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17811 | 115.79 | P13:345-18:AEPW:WELSH 7_#3
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 115.79 | P13:69-13.8:AEPW:COMANC-2
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.08 | P11:024:DPC:ALMA2:6
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.04 | P11:18:ITCM:EMERYGT1:1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.05 | P11:18:ITCM:EMERYGT2:1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.05 | P11:161:ITCM:MGS CT1:1C
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.05 | P11:161:ITCM:MGS CT2:2C
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17807 | 116.06 | 652537 WHITE 3 345 659286 DEERCREK-BE3 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17808 | 116.02 | 652568 GROTONSOUTH7 115 659275 GROTON_G-BE7 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17807 | 116.06 | 659286 DEERCREK-BE3 345 3WXFMR DEERCRK KU1A 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.05 | 672601 BD 4 230 672306 BD 6G 18.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.05 | 672610 POPLAR 4 230 672310 POPLAR 1G 18.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.05 | 672610 POPLAR 4 230 672311 POPLAR 2G 18.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.04 | 672621 SHAND 4 230 672321 SHAND 1G 18.0 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.03 | 672649 CODETTE 4 230 672650 NIPAWIN 4 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.04 | 672696 BRADA 4 230 672699 NBEC 4 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.12 | P23:345:MDU::COYOTE::5707-5712-5715::::
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.3 | P23:345:MEC:CBEC 905
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.25 | P23:345:MEC:CBEC 908
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.1781 | 116.04 | P23:345:MEC:GDMEC 901
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.1781 | 116.04 | P23:345:MEC:GDMEC 902
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.06 | P23:345:MEC:GDMEC 908
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.17 | P23:345:MEC:RAUN 0180
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.24 | P23:345:MEC:RAUN 0210
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.18 | P23:345:MEC:LOUISA 954
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.1781 | 116.19 | P23:345:MEC:LOUISA 964
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.03 | P21:115:XEL:AUTO-SINGLE:CHEMOLT7:LSPOWER7:1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.07 | P21:115:XEL:AUTO-SINGLE:COLVILL7:CANONFLSG7:1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.03 | P21:115:XEL:AUTO-SINGLE:FARIBALTP7:FARIBALTGEN:Z
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.13 | P21:230:OTP:AUTO-SINGLE:SQBUTTE4:YNG24:1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.12 | P23:345:OTP:CENTER 3:3215(1)
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.12 | P23:345:OTP:CENTER 3:3225(1)
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.06 | P12:230:UMZW:# 687 #: FT IN SD. FT-BG1 LINE FAULT
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.06 | P12:230:UMZW:# 3617 #: FT IN SD. FT-BG2 LINE FAULT
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 114.69 | 760494 GEN-2017-146 230 760498 G17-146-TAP 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 114.68 | 760495 G17-146-XFM1 34.5 760494 GEN-2017-146 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 115.46 | 761356 G17-239-XFMR 34.5 761355 GEN-2017-239 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 115.46 | 761359 G17-239-XFMR 34.5 761355 GEN-2017-239 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 115.63 | 761797 G17-187XFM1 34.5 761796 GEN-2017-187 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 115.63 | 761800 G17-187XFM2 34.5 761796 GEN-2017-187 115 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 110.67 | 762132 GEN-2017-158 230 763252 G18-099-XFM1 34.5 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 110.67 | 762132 GEN-2017-158 230 763255 G18-099-XFM2 34.5 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 111.27 | 762133 G17-158XFM1 34.5 762132 GEN-2017-158 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 111.27 | 762136 G17-158XFM2 34.5 762132 GEN-2017-158 230 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 113.54 | 762216 G17-151TAP 345 762217 GEN-2017-151 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.18057 | 116.85 | 762216 G17-151TAP 345 762467 G18-015-TAP 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 115.27 | 762218 G17-151XFM1 34.5 762217 GEN-2017-151 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 115.27 | 762221 G17-151XFM2 34.5 762217 GEN-2017-151 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 115.27 | 762224 G17-151XFM3 34.5 762217 GEN-2017-151 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 115.27 | 762227 G17-151XFM4 34.5 762217 GEN-2017-151 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 114.55 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 115.11 | 762461 G18-015-XFM1 34.5 762460 GEN-2018-015 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 115.11 | 762464 G18-015-XFM2 34.5 762460 GEN-2018-015 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17945 | 116.42 | 762467 G18-015-TAP 345 763215 G18-092-TAP 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 113.8 | 763087 GEN-2018-073 345 763088 G18-073-XFM1 34.5 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 114.78 | 763087 GEN-2018-073 345 763091 G18-073-XFM2 34.5 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 110.64 | 763120 GEN-2018-081 230 763121 G18-081-XFM1 34.5 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 112.92 | 763186 GEN-2018-089 230 763187 G18-089-XFM1 34.5 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 113.84 | 763208 GEN-2018-092 345 763215 G18-092-TAP 345 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 114.77 | 763208 GEN-2018-092 345 763220 G18-092-XFM1 34.5 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 114.77 | 763208 GEN-2018-092 345 763223 G18-092-XFM2 34.5 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 112.23 | 763241 GEN-2018-097 230 763242 G18-097-XFM1 34.5 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 113.15 | 763241 GEN-2018-097 230 763296 G18-111-XFM1 34.5 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 112.51 | 763241 GEN-2018-097 230 763307 G18-112-XFM1 34.5 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 112.51 | 763241 GEN-2018-097 230 763310 G18-112-XFM2 34.5 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 112.23 | 763241 GEN-2018-097 230 763395 G18-124-XFM1 34.5 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 112.23 | 763241 GEN-2018-097 230 763398 G18-124-XFM2 34.5 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 115.66 | 763318 GEN-2018-115 345 763319 G18-115-XFM1 34.5 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 112 | 763483 GEN-2019-003 230 763484 G19-003-XFM1 34.5 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 114.56 | 763483 GEN-2019-003 230 763605 G19-021-XFM1 34.5 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 115.46 | 763516 GEN-2019-011 345 763517 G19-011-XFM1 34.5 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 115.55 | 763879 GEN-2019-056 115 763880 G19-056XFM1 34.5 1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17775 | 116.19 | P42:345:OKGE:SB_BVTY7305
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17793 | 115.75 | P23:345:WERE:BUFF_345-534::
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17793 | 115.75 | P23:345:WERE:BUFF_345-543::
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17805 | 116.23 | P23:345:WERE:JEC_345-15::
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17804 | 116.18 | P23:345:WERE:JEC_345-16::
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17805 | 116.22 | P23:345:WERE:JEC_345-19::
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17805 | 116.22 | P23:345:WERE:JEC_345-20::
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.39 | P23:345:WERE:WOLF_345-50::
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.39 | P23:345:WERE:WOLF_345-60::
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.1781 | 115.8 | P42:345:AEPW:WELSH CB 10620 NBTB+FAULT
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.1781 | 115.79 | P41:345:AEPW:WELSH CB 10630 NBTB+FAULT
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 115.79 | P41:345:AEPW:WELSH CB 11670 NBTB+FAULT
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17821 | 115.78 | P41:345:AEPW:WELSH CB 11680 NBTB+FAULT
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 115.78 | P41:345:AEPW:WELSH CB 12540 NBTB+FAULT
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.18116 | 117.33 | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.18165 | 118.58 | P42:345:AEPW:LAWTON EASTSIDE CB 3413A NBTB+FAULT
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.18199 | 118.94 | P42:345:AEPW:LAWTON EASTSIDE CB 3425A NBTB+FAULT
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.18129 | 118.96 | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.18057 | 117.77 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.18057 | 117.77 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.18057 | 117.74 | P42:345:AEPW:TERRYRD_CB_3421A_NBTB
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17808 | 116.18 | P23:345:KCPL:LACYGNE_R2-5::LACYGU2-LACYGNE-STILWELL
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17808 | 115.82 | P45:345:UMZW:# 1328 #: GI IN NE.
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.1781 | 115.8 | P23:345:AEPW:WELSH CB 10620 NBTB
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.1781 | 115.79 | P23:345:AEPW:WELSH CB 10630 NBTB
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 115.79 | P23:345:AEPW:WELSH CB 11670 NBTB
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17821 | 115.78 | P23:345:AEPW:WELSH CB 11680 NBTB
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 115.78 | P23:345:AEPW:WELSH CB 12540 NBTB
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.18116 | 117.74 | P23:345:AEPW:OKLAUNION CB 3401A NBTB
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.18165 | 118.58 | P23:345:AEPW:LAWTON EASTSIDE CB 3413A NBTB
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.18199 | 118.94 | P23:345:AEPW:LAWTON EASTSIDE CB 3425A NBTB
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.18129 | 118.96 | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.18057 | 117.77 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.18057 | 117.77 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.18057 | 117.74 | P23:345:AEPW:TERRYRD_CB_3421A_NBTB
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.05 | P11:161:GMO:DOGWOOD_COMBINED_CYCLE_UNIT_OUTAGE
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17809 | 116.06 | P11:115:SUNC:GARDENCITY_S2:97:531459(2)
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17795 | 115.77 | P12:345:PWT:BUFF-THIS_345_1::
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17795 | 115.77 | P12:345:PWT:BUFF-THIS_345_2::
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17796 | 115.83 | P12:345:PWT:THIS-DGRS_345_1::FUTURE
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17796 | 115.83 | P12:345:PWT:THIS-DGRS_345_2::FUTURE
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17819 | 116.06 | P12:069:WFEC:ANADRKO_WATONGA
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.18074 | 117.97 | P23:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.1833 | 120.4 | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.18074 | 117.97 | P42:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB+FAULT
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.1833 | 120.4 | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17341 | 114.13 | P42:345:OKGE:SB_BVTY7315_PRE19S
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17778 | 115.62 | P23:345:SUNC:MO_BRK182
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17778 | 115.62 | P23:345:SUNC:MO_BRK382
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17773 | 115.79 | P23:345:SUNC:MO_BRK188
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17936 | 116.06 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.1781 | 115.79 | P12:138-13.8:AEPW:COMANC-4_#1
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.1775 | 115.47 | P12:230:AEPW:ELKCITY6:CHISHOLM6
Thermal | 05ALL | 1 | 26SP | GEN-2019-074 | FROM->TO | 525531 TOLK 6 230 997714 TOLK 6 230 2 |  | 560 | 0.17929 | 116.62 | P12:230:AEPW:SWEETWT6:CHISHOLM6
Thermal | 05ALL | 1 | 26WP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997711 ABBXNL844501 230 1 |  | 552.5 | 0.08108 | 164.23 | 525531 TOLK 6 230 3WXFMR TOLK 6 2
Thermal | 05ALL | 1 | 26WP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.05 | 120.61 | P12:115:SPS:T04::1_TRBLNC_CASTRO:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.05019 | 120.73 | P12:115:SPS:T59::1_CARGIL_CURRY:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.05095 | 120.66 | P12:115:SPS:T67::1_HAPPY_KRESS:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.05001 | 120.62 | P12:115:SPS:V24::1_WOLFTH_TERRY:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.05008 | 121.13 | P12:115:SPS:V37::1_CASTRO_PLANTX:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.05051 | 120.93 | P12:115:SPS:W40::1_WCANYON_TRBLNC:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.05051 | 120.53 | P12:115:SPS:W77::1_RNDAL_WCANYON:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.05954 | 127.42 | P42:345:SPS:YOAKUM:J18####:SLG1:EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.05954 | 127.42 | P43:345:SPS:YOAKUM:TF#####:SLG:EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.05954 | 127.42 | P42:345:SPS:YOAKUM:J17####:SLG:EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.0571 | 122.69 | P43:345:SPS:TUCO:SLG::EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.05954 | 127.42 | P42:345:SPS:YOAKUM:J18####:SLG2:EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.05019 | 120.7 | P12:345:OKGE:BKRBKR21::::
Thermal | 05ALL | 1 | 26WP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.05041 | 120.7 | P12:345:OKGE:BKRBKR24::::
Thermal | 05ALL | 1 | 26WP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.05285 | 122.65 | P12:345:OKGE-AEPW:BKRBKR25::::
Thermal | 05ALL | 1 | 26WP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.05016 | 120.48 | P12:345:OKGE-AEPW:BKRBKR343::::
Thermal | 05ALL | 1 | 26WP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.0555 | 122.27 | P12:345:OKGE-AEPW:BKRBKR366::::
Thermal | 05ALL | 1 | 26WP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.0555 | 122.24 | P12:345:OKGE-AEPW:BKRBKR366::::
Thermal | 05ALL | 1 | 26WP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.05218 | 121.66 | P12:345:OKGE:BKRBKR367::::
Thermal | 05ALL | 1 | 26WP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.05015 | 120.59 | P12:345:OKGE-WFEC:BKRBKR374::::
Thermal | 05ALL | 1 | 26WP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.05015 | 120.56 | P12:345:OKGE-WFEC:BKRBKR374::::
Thermal | 05ALL | 1 | 26WP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.06465 | 123.72 | P42:345:OKGE:SB_BVTY7387::::
Thermal | 05ALL | 1 | 26WP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.0502 | 120.63 | P42:345:OKGE:SB_SPCK7383::::
Thermal | 05ALL | 1 | 26WP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.05441 | 122.19 | 511456 O.K.U.-7 345 763215 G18-092-TAP 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.05462 | 122.76 | 511468 L.E.S.-7 345 762467 G18-015-TAP 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.05304 | 122.19 | 511468 L.E.S.-7 345 763215 G18-092-TAP 345 2
Thermal | 05ALL | 1 | 26WP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.05031 | 120.68 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.05022 | 119.86 | 511553 CHISHOLM7 345 755000 WWDBORDT 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.06465 | 123.76 | 515458 BORDER 7 345 560022 CRAWFISH_DR 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.06465 | 123.7 | 515458 BORDER 7 345 755000 WWDBORDT 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.05064 | 120.53 | 523095 HITCHLAND 6 230 523309 MOORE_CNTY 6 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.05016 | 120.61 | 523309 MOORE_CNTY 6 230 523323 MCDWL_CREEK6 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.05353 | 121.98 | 523959 POTTER_CO 6 230 524267 BUSHLAND 6 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.05628 | 122.4 | 523959 POTTER_CO 6 230 525461 NEWHART 6 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.05586 | 129.34 | 523961 POTTER_CO 7 345 3WXFMR WAUK 90343-A 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.05639 | 122.23 | 524267 BUSHLAND 6 230 524623 DEAFSMITH 6 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.05522 | 120.9 | 524415 AMA_SOUTH 6 230 525213 SWISHER 6 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.05051 | 120.82 | 524575 DS-#25+ 3 115 524597 PANDAHFD 3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.05051 | 120.9 | 524575 DS-#25+ 3 115 524630 TIERABLANCA3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.05459 | 125.98 | 524623 DEAFSMITH 6 230 760498 G17-146-TAP 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.05008 | 120.8 | 525056 BC-EARTH 3 115 525480 PLANT_X 3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.05032 | 123.54 | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.05459 | 124.03 | 525481 PLANT_X 6 230 760498 G17-146-TAP 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.08108 | 162.04 | 525549 TOLK 7 345 3WXFMR ABBXNL844501 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.0571 | 122.69 | 525832 TUCO_INT 7 345 526936 YOAKUM_345 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.05038 | 122.38 | 526935 YOAKUM 6 230 527028 INK_BASIN 6 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.05878 | 129.67 | 526936 YOAKUM_345 345 527896 HOBBS_INT 7 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.05048 | 121.79 | 527028 INK_BASIN 6 230 527894 HOBBS_INT 6 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.05351 | 119.99 | 560022 CRAWFISH_DR 345 762216 G17-151TAP 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.05302 | 120.98 | 560022 CRAWFISH_DR 345 762467 G18-015-TAP 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.05474 | 121.28 | 560022 CRAWFISH_DR 345 763215 G18-092-TAP 345 2
Thermal | 05ALL | 1 | 26WP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.05285 | 122.68 | P12:345:AEPW:L.E.S7:TERRYRD7
Thermal | 05ALL | 1 | 26WP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.05285 | 122.67 | P12:345:AEPW:L.E.S7:TERRYRD7
Thermal | 05ALL | 1 | 26WP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.05285 | 122.65 | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7
Thermal | 05ALL | 1 | 26WP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.0555 | 122.27 | P12:345:AEPW-OKGE:L.E.S.-7:GRACMNT7
Thermal | 05ALL | 1 | 26WP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.0555 | 122.24 | P12:345:AEPW-OKGE:L.E.S.-7:GRACMNT7
Thermal | 05ALL | 1 | 26WP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.05016 | 120.48 | P12:345:AEPW-OKGE:PITTSB-7:JOHNCO7
Thermal | 05ALL | 1 | 26WP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.05441 | 123.25 | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Thermal | 05ALL | 1 | 26WP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.05 | 120.54 | P13:138-345:AEPW:L.E.S.-4_#2
Thermal | 05ALL | 1 | 26WP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.05351 | 121.31 | 762216 G17-151TAP 345 762467 G18-015-TAP 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.05179 | 120.87 | 762467 G18-015-TAP 345 763215 G18-092-TAP 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.05441 | 121.76 | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Thermal | 05ALL | 1 | 26WP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.05605 | 122.49 | P42:345:AEPW:LAWTON EASTSIDE CB 3413A NBTB+FAULT
Thermal | 05ALL | 1 | 26WP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.05664 | 122.73 | P42:345:AEPW:LAWTON EASTSIDE CB 3425A NBTB+FAULT
Thermal | 05ALL | 1 | 26WP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.05463 | 123.34 | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Thermal | 05ALL | 1 | 26WP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.05016 | 120.48 | P42:345:AEPW:PITTSBURG CB 3433A NBTB+FAULT
Thermal | 05ALL | 1 | 26WP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.05285 | 122.67 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 05ALL | 1 | 26WP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.05285 | 122.67 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 05ALL | 1 | 26WP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.05285 | 122.65 | P42:345:AEPW:TERRYRD_CB_3421A_NBTB
Thermal | 05ALL | 1 | 26WP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.05441 | 122.19 | P23:345:AEPW:OKLAUNION CB 3401A NBTB
Thermal | 05ALL | 1 | 26WP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.05605 | 122.49 | P23:345:AEPW:LAWTON EASTSIDE CB 3413A NBTB
Thermal | 05ALL | 1 | 26WP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.05664 | 122.73 | P23:345:AEPW:LAWTON EASTSIDE CB 3425A NBTB
Thermal | 05ALL | 1 | 26WP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.05463 | 123.34 | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Thermal | 05ALL | 1 | 26WP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.05016 | 120.48 | P23:345:AEPW:PITTSBURG CB 3433A NBTB
Thermal | 05ALL | 1 | 26WP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.05285 | 122.67 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 05ALL | 1 | 26WP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.05285 | 122.67 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 05ALL | 1 | 26WP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.05285 | 122.65 | P23:345:AEPW:TERRYRD_CB_3421A_NBTB
Thermal | 05ALL | 1 | 26WP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.05019 | 120.48 | P12:138:AEPW:S.W.S.-4:L.E.S.-4
Thermal | 05ALL | 1 | 26WP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.05 | 120.56 | P23:345:AEPW:VALLIANT CB 3417A NBTB
Thermal | 05ALL | 1 | 26WP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.05311 | 122.82 | P23:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB
Thermal | 05ALL | 1 | 26WP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.05709 | 125.21 | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Thermal | 05ALL | 1 | 26WP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.05 | 120.56 | P42:345:AEPW:VALLIANT CB 3417A NBTB+FAULT
Thermal | 05ALL | 1 | 26WP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.05311 | 122.82 | P42:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB+FAULT
Thermal | 05ALL | 1 | 26WP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.05709 | 125.21 | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Thermal | 05ALL | 1 | 26WP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.05031 | 120.68 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6
Thermal | 05ALL | 1 | 26WP | GEN-2018-073 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.05022 | 121.03 | P12:230:AEPW:SWEETWT6:CHISHOLM6
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1771 | 120.49 | P12:345:AEPW-AEPW:CHAMPSP-CLARKSV
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17709 | 120.61 | P23:345:KCPL-WERE:237LACYGNE_R1-6::LACYGU1-LACYGNE-NEOSHO
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17707 | 120.5 | P11:161:GMO:DOGWOOD_COMBINED_CYCLE_UNIT_OUTAGE_1_1
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17715 | 118.96 | P11:115:SPS:MUSTANG1&3:153MW::::
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17782 | 122.27 | P12:230:SPS:K37::1_TOLK_LAMB:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17729 | 120.48 | P12:230:SPS:K43::1_PRNGLE_HARR_E:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17711 | 120.26 | P12:230:SPS:K44::1_EPLNT_HARRW:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17725 | 120.61 | P12:115:SPS:T04::1_TRBLNC_CASTRO:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.48 | P12:115:SPS:T13::1_TAYLOR_WHOBBS:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.26 | P12:115:SPS:T14::1_MADDOX_TAYLOR:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.73 | P12:115:SPS:T21::1_GRSSLND_GRAHAM:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.29 | P12:115:SPS:T23::1_PCA_POTJCT:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.52 | P12:115:SPS:T26::1_CHAVES_RSWLCTY:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17849 | 120.8 | P12:115:SPS:T28A::1_LAMTON_PLANTX:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17765 | 120.54 | P12:115:SPS:T29::1_LAMTON_HALECTR:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17845 | 121.92 | P12:115:SPS:T30::1_LAMB_HOCKLY:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17845 | 121.43 | P12:115:SPS:T31::1_HOCKLY_SUNDWN:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17706 | 120.59 | P12:115:SPS:T35::1_TERRY_YOAKUM:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 121.24 | P12:115:SPS:T45::1_NORRIS_OASIS:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17774 | 120.73 | P12:115:SPS:T59::1_CARGIL_CURRY:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17818 | 120.66 | P12:115:SPS:T67::1_HAPPY_KRESS:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17702 | 120.96 | P12:115:SPS:T71::1_CRLSLE_YUMA:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1772 | 120.57 | P12:115:SPS:T81::1_COX_FLOYD:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17707 | 120.57 | P12:115:SPS:T83::1_SP-FKFD_ALLEN:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.91 | P12:115:SPS:T89::1_DC_N_HIGG:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.54 | P12:115:SPS:T91::1_HIGG_RUSSELL:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17733 | 120.51 | P12:115:SPS:V04::1_EPLANT_RNDALL:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17724 | 120.5 | P12:115:SPS:V07::1_COX_HALECTR:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17845 | 120.71 | P12:115:SPS:V09::1_HALECTR_PLANTX:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17709 | 120.56 | P12:115:SPS:V12::1_PLANTX_BAILEY:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17707 | 120.5 | P12:115:SPS:V15::1_TUCO_INDANA:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17707 | 120.51 | P12:115:SPS:V16::1_TERRY_DC_N:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17677 | 120.62 | P12:115:SPS:V24::1_WOLFTH_TERRY:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17723 | 120.6 | P12:115:SPS:V26::1_RSWLL_EDDY_N:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.58 | P12:115:SPS:V33::1_LUBBS_LYNN:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17824 | 121.13 | P12:115:SPS:V37::1_CASTRO_PLANTX:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.63 | P12:115:SPS:V46::1_ALLEN_WHEELCK:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1771 | 120.95 | P12:115:SPS:V49::1_YOAKUM_SHLCO2:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17766 | 121.15 | P12:115:SPS:V55::1_SUNDWN_TERRY:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1773 | 120.98 | P12:115:SPS:V56::1_COCHRAN_SUNDWN:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17711 | 120.5 | P12:115:SPS:V78::2_CURRY_RSVLT:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1771 | 120.67 | P12:115:SPS:V81::1_LE-WAIT_LE-LVN:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.54 | P12:115:SPS:V95::1_DC_N_SHLCO2:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.5 | P12:115:SPS:W11::1_DC_S_SMINLE:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.54 | P12:115:SPS:W14::1_SMINLE_GAINES:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.5 | P12:115:SPS:W26::1_CUNGHM_OILCNTR:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 121.13 | P12:115:SPS:W32::1_PRMTR_FE-CLSIN:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.5 | P12:115:SPS:W34::1_JNSDRW_MAPCO:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17709 | 120.73 | P12:115:SPS:W35::1_GAINES_JNSDRW:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17709 | 120.52 | P12:115:SPS:W36::1_TAYLOR_JNSDRW:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1793 | 120.93 | P12:115:SPS:W40::1_WCANYON_TRBLNC:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1772 | 120.29 | P12:115:SPS:W46::1_RHILLS_NWEST:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17744 | 120.55 | P12:115:SPS:W52::1_NEWHART_KRESS:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 121.01 | P12:115:SPS:W58::1_NORTON_LOPEZ:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.69 | P12:115:SPS:W59::1_LOPEZ_CMPBLL:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.96 | P12:115:SPS:W62::1_PLSTHL_CURRY:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.84 | P12:115:SPS:W64::1_PLSTHL_FE-CLV:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.81 | P12:115:SPS:W65::1_PLSTHL_CURRY:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.68 | P12:115:SPS:W66::1_PORTA_GREYHUND:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1793 | 120.53 | P12:115:SPS:W77::1_RNDAL_WCANYON:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.51 | P12:115:SPS:W99::1_CAPITAN_CHAVES:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17707 | 120.51 | P12:115:SPS:U03::1_CARDNL_NEF:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17707 | 121.04 | P12:115:SPS:U14::1_DC_STH_INKBSN:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1771 | 120.92 | P12:115:SPS:V15::1_INKBSN_LE-WAT:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17734 | 120.55 | P12:115:SPS:U16::1_BSHLND_OUTPST:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17734 | 120.54 | P12:115:SPS:U17::1_COLTR_OUTPST:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17727 | 120.76 | P12:115:SPS:U19::1_DEAN_PLAINS:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17734 | 120.49 | P12:115:SPS:U23::1_COLTR_HILSDE:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17052 | 127.42 | P42:345:SPS:YOAKUM:J18####:SLG1:EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17052 | 127.42 | P43:345:SPS:YOAKUM:TF#####:SLG:EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17052 | 127.42 | P42:345:SPS:YOAKUM:J17####:SLG:EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17015 | 122.69 | P43:345:SPS:TUCO:SLG::EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17052 | 127.42 | P42:345:SPS:YOAKUM:J18####:SLG2:EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1771 | 120.49 | P12:345:AEPW-AEPW:CHAMPSP-CLARKSV:::EHV::
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17707 | 120.52 | P11:18:HAST:::EGYCTR2G WEC2_LOSS OF WEC 2 GEN_:HV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17707 | 120.52 | P13:18-115:HAST:::EGYCNTR7 XFMR G2WEC 2 GSU_:HV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17707 | 120.5 | P11:161:GMO:DOGWOOD-COMBINED-CYCLE-UNIT-OUTA:::HV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17709 | 120.61 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17706 | 120.65 | P23:345:KCPL:LACYGNE-R2-5:::EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17704 | 120.66 | P11:230:WERE:JECU1-GEN:::HV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17704 | 120.66 | P11:345:WERE:JECU2-GEN:::EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17704 | 120.66 | P11:345:WERE:JECU3-GEN:::EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.88 | P11:345:WERE:WOLFU1-GEN:::EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17694 | 120.25 | P12:345:PWT:BUFF-THIS-345-1:::EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17694 | 120.25 | P12:345:PWT:BUFF-THIS-345-2:::EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17692 | 120.23 | P23:345:WERE:BUFF-345-534:::EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17692 | 120.23 | P23:345:WERE:BUFF-345-543:::EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17704 | 120.66 | P23:345:WERE:JEC-345-15:::EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17702 | 120.62 | P23:345:WERE:JEC-345-16:::EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17704 | 120.66 | P23:345:WERE:JEC-345-19:::EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17704 | 120.66 | P23:345:WERE:JEC-345-20:::EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17702 | 120.29 | P23:345:WERE:WICH-345-50:::EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17707 | 120.87 | P23:345:WERE:WOLF-345-50:::EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.87 | P23:345:WERE:WOLF-345-60:::EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.81 | P11:022:NPPD:COOPER1G:1:983:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17701 | 120.83 | P11:023:NPPD:GENTLM1G:1:757:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17706 | 120.68 | P11:024:NPPD:GENTLM2G:2:757:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17703 | 120.68 | P13:345:OPPD:NEBCTY1G:::EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17702 | 120.69 | P13:345:OPPD:NEBCTY2G:::EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.69 | P22:345:OPPD:S3458 NEBCTY1G:LT::EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17703 | 120.68 | P22:345:OPPD:S3458 NEBCTY1G:::EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.72 | P22:345:OPPD:S3458 NEBCTY2G:LT::EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17702 | 120.69 | P22:345:OPPD:S3458 NEBCTY2G:::EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.69 | P23:345:OPPD:S3458 NEBCTY1G:LT::EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17703 | 120.68 | P23:345:OPPD:S3458 NEBCTY1G:::EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.72 | P23:345:OPPD:S3458 NEBCTY2G:LT::EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17702 | 120.69 | P23:345:OPPD:S3458 NEBCTY2G:::EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.29 | P12:115:SUNC:PLYMELL-PIERCEVILLE:::HV::
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17705 | 120.53 | P11:018:UMZB:# 5 #:: DCS IN SD. DEERCREEK_MV::
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17706 | 120.5 | P11:022:UMZB:# 15 #:: LO IN ND. LELAND OLDS 1_MV::
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17707 | 120.5 | P11:020:UMZB:# 16 #:: LO IN ND. LELAND OLDS 2_MV::
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17705 | 120.61 | P11:023:UMZB:# 31 #:: AVS IN ND. ANTELOPE VALLEY 1_MV::
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17705 | 120.61 | P11:023:UMZB:# 32 #:: AVS IN ND. ANTELOPE VALLEY 2_MV::
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.177 | 120.82 | P11:024:UMZB:# 33 #:: LRS IN WY. LARAMIE RIVER STATION 1_MV::
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.49 | P13:230:UMZW:# 5135 #:: OA IN SD. FAULT ON TRANSFORMER (2).:HV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.49 | P13:230:UMZW:# 5136 #:: OA IN SD. FAULT ON TRANSFORMER (3).:HV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.5 | P13:230:UMZW:# 5137 #:: OA IN SD. FAULT ON TRANSFORMER (4).:HV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17706 | 120.28 | P23:345:UMZW:# 2423 #:: GI IN NE. GI 1596 BKR FAULT:EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17706 | 120.28 | P23:345:UMZW:# 2426 #:: GI IN NE. GI 1592 BKR FAULT:EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17706 | 120.28 | P23:345:UMZW:# 2432 #:: GI IN NE. GI 1092 BKR FAULT:EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17706 | 120.28 | P23:345:UMZW:# 2440 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1092 STUCK BKR:EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17706 | 120.28 | P23:345:UMZW:# 2444 #:: GI IN NE. GI-SWEET BRANCH FAULT & GI 1596 STUCK BKR:EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17706 | 120.28 | P23:345:UMZW:# 2446 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1196 STUCK BKR:EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17706 | 120.28 | P42:345:UMZW:# 2413 #:: FT2 IN SD. FT2-LO2 BRANCH FAULT & FT2 2992 STUCK BKR:EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17706 | 120.28 | P42:345:UMZW:# 2415 #:: FT2 IN SD. FT2-GI BRANCH FAULT & FT2 3392 STUCK BKR:EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17711 | 120.2 | P11:138:WFEC:HUGO1:465MW :::
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17706 | 120.49 | P11:138:WFEC:MORLND2:132MW:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17706 | 120.5 | P11:138:WFEC:MORLND3:149MW :::
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17716 | 120.52 | P12:138:WFEC:ANADRKO_CLVLND::::
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17702 | 120.25 | P12:345:OKGE-AEPW:BKRBKR20::::
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17743 | 120.7 | P12:345:OKGE:BKRBKR21::::
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17763 | 120.7 | P12:345:OKGE:BKRBKR24::::
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17955 | 122.65 | P12:345:OKGE-AEPW:BKRBKR25::::
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17677 | 120.12 | P12:345:OKGE:BKRBKR336::::
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17676 | 120.11 | P12:345:OKGE:BKRBKR336_2::::
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17742 | 120.48 | P12:345:OKGE-AEPW:BKRBKR343::::
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1803 | 122.27 | P12:345:OKGE-AEPW:BKRBKR366::::
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1803 | 122.24 | P12:345:OKGE-AEPW:BKRBKR366::::
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17914 | 121.66 | P12:345:OKGE:BKRBKR367::::
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17744 | 120.59 | P12:345:OKGE-WFEC:BKRBKR374::::
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17744 | 120.56 | P12:345:OKGE-WFEC:BKRBKR374::::
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17681 | 120.16 | P12:345:OKGE:BKRBKR4193::::
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17681 | 120.16 | P12:345:OKGE:BKRBKR4194::::
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17671 | 120.16 | P12:345:OKGE-SPS:BKRBKR4201::::
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17671 | 120.16 | P12:345:OKGE-SPS:BKRBKR4202::::
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17675 | 119.95 | P12:345:OKGE:BKRBKR443NEW::::
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17675 | 119.95 | P12:345:OKGE:BKRBKR443NEW2::::
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17691 | 120.27 | P12:345:OKGE-ITC:BKRBKR502::::
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17691 | 120.27 | P12:345:OKGE-ITC:BKRBKR503::::
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17703 | 120.61 | P12:345:OKGE:BKRBKR604::::
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17701 | 120.72 | P12:345:OKGE:BKRBKR604_2::::
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.18414 | 123.72 | P42:345:OKGE:SB_BVTY7387::::
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17748 | 120.63 | P42:345:OKGE:SB_SPCK7383::::
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17705 | 120.53 | P11:115:SUNC:GARDENCITY_S2:103:531459(2):HV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17705 | 120.54 | P11:115:SUNC:FORTDDODGE_4:157:539670(4):HV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1767 | 120.5 | P12:345:SUNC-NPPD:MINGO-REDWILLOW::531451-640325(1):EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.61 | P13:115:SUNC:HOLCOMB_GSU:::HV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17705 | 120.53 | P13:115:SUNC:S2_GSU:::HV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17705 | 120.54 | P13:115:SUNC:FORTDODGE_GSU:::HV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.48 | 300002 1THLG2 22.0 301505 5THOMHLGSU2 161 2
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.62 | 300003 1THLG3 24.0 301503 7THOMHLGSU3 345 3
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.48 | 300006 1NM G1 22.0 301536 5NEWMADGSU1 161 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.48 | 300007 1NM G2 22.0 301537 7NEWMADGSU2 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.48 | 300046 7NEWMAD 345 301537 7NEWMADGSU2 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.62 | 300049 7THOMHL 345 301503 7THOMHLGSU3 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.48 | 300103 5NEWMAD 161 301536 5NEWMADGSU1 161 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.48 | 300132 5THMHLB2 161 301505 5THOMHLGSU2 161 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17707 | 120.29 | 300739 7BLACKBERRY 345 532797 WOLFCRK7 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.56 | P11:20:AMMO:1LAB�� G1:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.54 | P11:20:AMMO:1LAB�� G2:2
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.75 | P11:345:AMMO::CALLAWAY:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.56 | P11:345:AMMO::LABADIE:3
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.56 | P11:345:AMMO::LABADIE:4
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.55 | P11:345:AMMO::RUSHISLAND:U1
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.54 | P11:345:AMMO::RUSHISLAND:U2
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.53 | P11:138:AMMO::SIOUX:2
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.49 | P13:345-230:CLEC::DOLHILL7:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.29 | P11:345-24:CLEC::DOLHILL7:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.29 | P11:24:CLEC::G1DOLHIL:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.53 | P12:765:AEP:AEP ROCKP-AEP JEFF 765
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.48 | P11:HV:EES::1ISES U1:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.25 | P11:HV:EES::PIRKEY 1:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.26 | P11:EHV:EES::WELSH3-1:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.2 | P11:HV:EES::TURKCOAL:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.48 | P12:HV:EES::5ISES%:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.74 | P12:EHV:EES::7CALAWY 1:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1771 | 120.49 | P12:EHV:EES::CHAMSPR7!:CLARKSV7!:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17709 | 120.21 | P12:HV:EES::TURK 4%:1(1)
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1771 | 120.26 | P12:EHV:EES::WELSH 7:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1771 | 120.26 | P12:EHV:EES::WELSH 7:1(1)
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17709 | 120.26 | P12:HV:EES::PIRKEY 4:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.53 | 344011 7HUGHES 345 344012 7HPW-N 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.55 | 344884 7LABADIE1 345 344894 1LAB G1 20.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.53 | 344885 7LABADIE2 345 344895 1LAB G2 20.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.55 | 344886 7LABADIE3 345 344896 1LAB G3 20.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.55 | 344887 7LABADIE4 345 344897 1LAB G4 20.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.54 | 345667 7RUSH 1 345 345670 1RUSH G1 18.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.53 | 345668 7RUSH 2 345 345671 1RUSH G2 18.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.52 | 345755 4SIOUX 1 138 345756 1SIOUX 1 18.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.52 | 345764 4SIOUX 2 138 345765 1SIOUX 2 18.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.6 | P12:345:MDU::CENTER:COYOTE:1::::
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.6 | P13:345:MDU:COYOTE GSU LOSS:COYOTE::1::::
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.82 | P11:345:MEC-NPPD:COOPER 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.72 | P11:24:XEL:AUTO-SINGLE:SHERC31G:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.72 | P11:24:XEL:AUTO-SINGLE:SHERC32G:2
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.81 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.64 | P11:20:XEL:AUTO-SINGLE:PRIS31G:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.63 | P11:20:XEL:AUTO-SINGLE:PRIS32G:2
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.68 | P11:22:XEL:AUTO-SINGLE:MNTCE31G:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.64 | P11:20:XEL:AUTO-SINGLE:KING31G:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.48 | P11:18:XEL:AUTO-SINGLE:BLKD76G:6
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.69 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.69 | P11:22:GRE:AUTO-SINGLE:GRE-COAL42G:2
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.61 | P11:24:OTP:AUTO-SINGLE:BIGSTN1G:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.63 | P11:20:OTP:AUTO-SINGLE:CENTER2G:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.52 | P11:22:OTP:AUTO-SINGLE:CENTER1G:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.61 | P11:24:OTP:AUTO-SINGLE:COYOTE1G:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.51 | P11:24:DPC:AUTO-SINGLE:GENOA53G:3
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.5 | P12:115:XEL:AUTO-SINGLE:CHEMOLT7:LSPOWER7:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.49 | P12:115:XEL:AUTO-SINGLE:FARIBALTP7:FARIBALTGEN:Z
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.61 | P12:230:OTP:AUTO-SINGLE:SQBUTTE4:YNG24:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.69 | P13:24-345:XEL:AUTO-SINGLE:SHERC31G:SHERCO3:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.69 | P13:24-345:XEL:AUTO-SINGLE:SHERC32G:SHERCO3:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.78 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.64 | P13:20-345:XEL:AUTO-SINGLE:PRIS31G:PRISLD3:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.64 | P13:20-345:XEL:AUTO-SINGLE:PRIS32G:PRISLD3:2
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.68 | P13:22-345:XEL:AUTO-SINGLE:MNTCE31G:MNTCELO3:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.62 | P13:20-345:XEL:AUTO-SINGLE:KING31G:ASKING3:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.48 | P13:18-115:XEL:AUTO-SINGLE:BLKD76G:BLKDG27:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.67 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL41G:GRE-COALCR4:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.67 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL42G:GRE-COALCR4:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.6 | P13:230-24:OTP:AUTO-SINGLE:BIGSTON4:BIGSTN1G:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.61 | P13:20-230:OTP:AUTO-SINGLE:CENTER2G:YNG24:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.51 | P13:22-230:OTP:AUTO-SINGLE:CENTER1G:CENTER4:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.6 | P13:24-345:OTP:AUTO-SINGLE:COYOTE1G:COYOTE3:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.5 | P13:24-161:DPC:AUTO-SINGLE:GENOA53G:GENOA5:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.55 | P13:24-161:DPC:AUTO-SINGLE:JPM:ALMA5:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.6 | P11:115:XEL:RIV COMBINE CYCLE
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.51 | P12:115:XEL:BDS #2 5
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.49 | P11:115:XEL:HBR #6 7 8
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.63 | P23:345:XEL:8H14 PRI
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.64 | P23:345:XEL:8H17 PRI AS
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.78 | P23:345:XEL:8N28 SHC
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.7 | P23:345:XEL:8N22 SHC
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.69 | P23:345:XEL:8N17 SHC
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.68 | P23:345:XEL:8N8 MNN
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.63 | P23:345:XEL:8P1 KING
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.63 | P23:345:XEL:8P2 KING
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.5 | P11:22:ALTW:AUTO-SINGLE:LANS54G:4
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.64 | P11:22:ALTW:AUTO-SINGLE:ARNOLD1G:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.67 | P11:24:ALTW:AUTO-SINGLE:OTTUMW1G:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.49 | P13:22-161:ALTW:AUTO-SINGLE:LANS54G:LANSINGL15:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.63 | P13:22-161:ALTW:AUTO-SINGLE:ARNOLD1G:ARNOLD5:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.66 | P13:24-161:ALTW:AUTO-SINGLE:OTTUMW1G:OTTUMWA5:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.74 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.8 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.65 | P11:22:MEC:AUTO-SINGLE:NEAL3G:3
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.73 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.66 | P11:24:MEC:AUTO-SINGLE:LOUIS31G:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.72 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.76 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.64 | P13:345-22:MEC:AUTO-SINGLE:RAUN3:NEAL3G:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.71 | P13:345-24:MEC:AUTO-SINGLE:RAUN3:NEAL4G:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.64 | P13:345-24:MEC:AUTO-SINGLE:LOUISA3:LOUIS31G:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17704 | 120.66 | P11:230:WERE:JECU1_GEN::
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17704 | 120.66 | P11:345:WERE:JECU2_GEN::
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17704 | 120.66 | P11:345:WERE:JECU3_GEN::
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.88 | P11:345:WERE:WOLFU1_GEN::
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17715 | 120.48 | 511453 DUNCAN-4 138 511552 DUNCHERTP4 138 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17715 | 120.48 | 511455 D.E.S.-4 138 511552 DUNCHERTP4 138 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.48 | 511456 O.K.U.-7 345 511565 OKLAUN HVDC7 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 119.42 | 511456 O.K.U.-7 345 588760 GEN-2017-033 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.18015 | 122.19 | 511456 O.K.U.-7 345 763215 G18-092-TAP 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.18029 | 122.76 | 511468 L.E.S.-7 345 762467 G18-015-TAP 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17925 | 122.19 | 511468 L.E.S.-7 345 763215 G18-092-TAP 345 2
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1772 | 120.56 | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17834 | 120.68 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17062 | 117.21 | 511553 CHISHOLM7 345 523961 POTTER_CO 7 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17062 | 117.21 | 511553 CHISHOLM7 345 523961 POTTER_CO 7 345 2
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17421 | 119.86 | 511553 CHISHOLM7 345 755000 WWDBORDT 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17712 | 120.5 | 511557 CHISHOLM6 230 3WXFMR CHISHOLM6 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17721 | 120.51 | 514801 MINCO 7 345 555234 NSUB345 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17634 | 120.15 | 515375 WWRDEHV7 345 755000 WWDBORDT 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.18414 | 123.76 | 515458 BORDER 7 345 560022 CRAWFISH_DR 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.18414 | 123.7 | 515458 BORDER 7 345 755000 WWDBORDT 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17706 | 120.51 | 515618 BALKOW 7 345 3WXFMR BALKOW 7 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17706 | 120.5 | 515618 BALKOW 7 345 3WXFMR BALKOW 7 1_Dup1
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17701 | 120.73 | 515634 PALDR1W7 345 3WXFMR PALO2 _1 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.63 | 515677 BADGER 7 345 563170 G15082_1 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.49 | 522800 MU-TULIA 3 115 525179 TULIA_TP 3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.63 | 522892 MU-BROWNFLD2 69.0 526761 BROWNFLD_TP2 69.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17705 | 120.52 | 523093 HITCHLAND 3 115 523174 GOODWELLWND3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17842 | 120.53 | 523095 HITCHLAND 6 230 523309 MOORE_CNTY 6 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.88 | 523097 HITCHLAND 7 345 523112 NOVUS1 7 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.93 | 523097 HITCHLAND 7 345 523215 FREWHELCOL17 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17499 | 119.43 | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.16437 | 117.75 | 523097 HITCHLAND 7 345 523961 POTTER_CO 7 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.99 | 523097 HITCHLAND 7 345 560252 G10-14 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.5 | 523099 TC-DRYTRLS 3 115 588480 A16-010_SUB 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.74 | 523112 NOVUS1 7 345 3WXFMR NOVUS XF2 2
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.52 | 523112 NOVUS1 7 345 3WXFMR XIANA2011198 _1 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17705 | 120.5 | 523118 BUFF_DUNES 7 345 523853 FINNEY 7 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.51 | 523120 COLE 3 115 588860 GEN-2017-047 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17717 | 120.48 | 523221 XIT_INTG 6 230 3WXFMR SIEM_T126401 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17729 | 120.48 | 523267 PRINGLE 6 230 3WXFMR ENRCO13617-1 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17729 | 120.48 | 523267 PRINGLE 6 230 523979 HARRNG_EST 6 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17773 | 120.61 | 523309 MOORE_CNTY 6 230 523323 MCDWL_CREEK6 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17743 | 120.53 | 523323 MCDWL_CREEK6 230 523959 POTTER_CO 6 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17682 | 120.85 | 523959 POTTER_CO 6 230 523979 HARRNG_EST 6 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.18715 | 121.98 | 523959 POTTER_CO 6 230 524267 BUSHLAND 6 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.18671 | 122.4 | 523959 POTTER_CO 6 230 525461 NEWHART 6 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.18702 | 129.34 | 523961 POTTER_CO 7 345 3WXFMR WAUK 90343-A 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17694 | 120.79 | 523961 POTTER_CO 7 345 524296 SPNSPUR_WND7 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1771 | 120.27 | 523977 HARRNG_WST 6 230 523971 HARRNGTON1 1 24.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17689 | 120.79 | 523977 HARRNG_WST 6 230 524010 ROLLHILLS 6 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17712 | 120.22 | 523978 HARRNG_MID 6 230 523979 HARRNG_EST 6 230 @1
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.29 | 524010 ROLLHILLS 6 230 3WXFMR WAUK WT01104 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17734 | 120.55 | 524267 BUSHLAND 6 230 3WXFMR WH 7001795 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.195 | 122.23 | 524267 BUSHLAND 6 230 524623 DEAFSMITH 6 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17694 | 120.89 | 524296 SPNSPUR_WND7 345 524299 SPNSPUR_COL7 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17694 | 120.89 | 524299 SPNSPUR_COL7 345 3WXFMR SPNSPUR_COL7 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.18151 | 120.9 | 524415 AMA_SOUTH 6 230 525213 SWISHER 6 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 121.01 | 524502 NORTON 3 115 524509 FE-TUCMCARI3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1793 | 120.82 | 524575 DS-#25+ 3 115 524597 PANDAHFD 3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1793 | 120.9 | 524575 DS-#25+ 3 115 524630 TIERABLANCA3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.5 | 524604 HEREFRD_SB 2 69.0 524608 HERFRD_STH 2 69.0 *1
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.19503 | 125.98 | 524623 DEAFSMITH 6 230 760498 G17-146-TAP 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.78 | 524721 DS-#15&#19+2 69.0 524745 CASTRO_CNTY2 69.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.84 | 524764 NORRIS_TP 3 115 524801 NORRIS 3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17709 | 120.49 | 524770 PLSNT_HILL 6 230 3WXFMR EFAE1100068A 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.84 | 524776 N_CLOVIS_TP3 115 524777 N_CLOVIS 3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.78 | 524790 CANNON_TP 3 115 524794 CANNONAFB 3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.18095 | 127.03 | 524875 OASIS 6 230 524885 SN_JUAN_TAP6 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17759 | 121.66 | 524875 OASIS 6 230 524909 ROOSEVELT 6 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.18077 | 127.79 | 524885 SN_JUAN_TAP6 230 527483 CHAVES_CNTY6 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17713 | 120.65 | 524909 ROOSEVELT 6 230 3WXFMR ABB LMM60042 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.18087 | 125.82 | 524909 ROOSEVELT 6 230 525531 TOLK 6 230 2
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 121.25 | 524923 PORTALES 2 69.0 524929 RO-PORT_MTR2 69.0 @1
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.88 | 524923 PORTALES 2 69.0 524941 PORTALES#1 2 69.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.84 | 525023 BC-BAIL_MTR2 69.0 525027 BAILEYCO 2 69.0 @1
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17824 | 120.8 | 525056 BC-EARTH 3 115 525480 PLANT_X 3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.57 | 525192 KRESS_INT 3 115 3WXFMR ENRCO 136155 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1772 | 120.29 | 525213 SWISHER 6 230 3WXFMR SIEM_T127101 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.18118 | 121.59 | 525213 SWISHER 6 230 525461 NEWHART 6 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.54 | 525272 KISER 3 115 3WXFMR VON 13819/1 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.81 | 525326 COX 3 115 3WXFMR ELCO 13474-3 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.81 | 525414 LAMTON 3 115 3WXFMR ASEA MLL9204 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.19896 | 123.54 | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.18209 | 122.16 | 525481 PLANT_X 6 230 3WXFMR WH ALM20171 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.19237 | 127.05 | 525481 PLANT_X 6 230 526435 SUNDOWN 6 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.19503 | 124.03 | 525481 PLANT_X 6 230 760498 G17-146-TAP 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17063 | 120.86 | 525481 PLANT_X 6 230 762174 G17-218TAP 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.16984 | 120.92 | 525481 PLANT_X 6 230 762174 G17-218TAP 230 2
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.18527 | 128.41 | 525531 TOLK 6 230 525586 NEEDMORE 6 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17782 | 122.27 | 525531 TOLK 6 230 525637 LAMB_CNTY 6 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.16753 | 121.08 | 525531 TOLK 6 230 762174 G17-218TAP 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.16688 | 121.13 | 525531 TOLK 6 230 762174 G17-218TAP 230 2
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.18527 | 128.41 | 525586 NEEDMORE 6 230 526935 YOAKUM 6 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17782 | 122.27 | 525637 LAMB_CNTY 6 230 3WXFMR WH ALM20172 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.54 | 525828 TUCO_INT 3 115 3WXFMR DS F78800913 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.18153 | 120.96 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.18275 | 121.11 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _9 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17015 | 122.69 | 525832 TUCO_INT 7 345 526936 YOAKUM_345 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17845 | 121.33 | 526020 HOCKLEY 3 115 526036 LC-OPDYKE 3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17845 | 121.18 | 526036 LC-OPDYKE 3 115 526434 SUNDOWN 3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.57 | 526160 CARLISLE 3 115 3WXFMR WH RLP38371 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.79 | 526162 LP-DOUD_TP 3 115 526176 LP-DOUD 3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.82 | 526268 LUBBCK_STH 3 115 3WXFMR NA 70454A 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1773 | 120.81 | 526361 COCHRAN 3 115 526424 PACIFIC 3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1773 | 120.9 | 526424 PACIFIC 3 115 526434 SUNDOWN 3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17766 | 120.94 | 526434 SUNDOWN 3 115 526445 AMOCO_TP 3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17711 | 120.51 | 526435 SUNDOWN 6 230 3WXFMR UPDATE LATER _12 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17912 | 124.22 | 526435 SUNDOWN 6 230 526460 AMOCO_SS 6 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17766 | 120.8 | 526445 AMOCO_TP 3 115 526484 LG-LEVELAND3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17912 | 121.88 | 526460 AMOCO_SS 6 230 526935 YOAKUM 6 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17766 | 120.79 | 526484 LG-LEVELAND3 115 526491 LG-CLAUENE 3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17707 | 120.51 | 526525 WOLFFORTH 6 230 3WXFMR UPDATE LATER _13 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17723 | 122.38 | 526935 YOAKUM 6 230 527028 INK_BASIN 6 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1713 | 129.67 | 526936 YOAKUM_345 345 527896 HOBBS_INT 7 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1772 | 121.79 | 527028 INK_BASIN 6 230 527894 HOBBS_INT 6 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.9 | 527130 DENVER_N 3 115 527286 HIGGEAST 3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1771 | 119.59 | 527149 MUSTANG 6 230 527151 GS-MUSTANG 6 230 @1
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.62 | 527202 SEAGRAVES 3 115 3WXFMR ABB MLL92408 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.59 | 527212 DIAMONDBACK3 115 3WXFMR HOW 36773714 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.88 | 527286 HIGGEAST 3 115 527363 HIGG 3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17709 | 120.62 | 527325 OXY_WSEM_TP3 115 527362 JOHNSON_DRW3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.59 | 527340 DOSS 3 115 3WXFMR ELCO 13566/1 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.58 | 527345 LEGACY 2 69.0 527350 XTO_ROBRTSN2 69.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.58 | 527346 LEGACY 3 115 3WXFMR VROL 13735-1 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.56 | 527350 XTO_ROBRTSN2 69.0 527355 BOARDMAN 2 69.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.51 | 527355 BOARDMAN 2 69.0 527365 FLANNAGAN 2 69.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.5 | 527360 MAPCO 3 115 527362 JOHNSON_DRW3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.58 | 527362 JOHNSON_DRW3 115 528775 LE-ERF 3 115 @1
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.48 | 527370 TENNECO_TAP2 69.0 527371 TENNECO 2 69.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1771 | 120.29 | 527470 CHVS_SLRCOL3 115 527482 CHAVES_CNTY3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1787 | 121.58 | 527483 CHAVES_CNTY6 230 527799 EDDY_NORTH 6 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.49 | 527508 PRICE 3 115 527509 PRICE_TAP 3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.5 | 527514 CV-PINE 2 69.0 527563 ROSWLL_INT 2 69.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.52 | 527563 ROSWLL_INT 2 69.0 527575 SW_4702 2 69.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17723 | 120.61 | 527564 ROSWLL_INT 3 115 527597 TWEEDY 3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.52 | 527575 SW_4702 2 69.0 527589 CV-ORCHARD 2 69.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.48 | 527589 CV-ORCHARD 2 69.0 527619 DEXTER_TP 2 69.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17701 | 120.69 | 527653 MILO_WIND 1 34.5 527655 RSVLT_CC_E 7 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1769 | 120.67 | 527654 RSVLT_CC_W 7 345 527655 RSVLT_CC_E 7 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1769 | 120.92 | 527654 RSVLT_CC_W 7 345 527666 RSVLT_COL1 7 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17684 | 120.92 | 527655 RSVLT_CC_E 7 345 527656 CROSSROADS 7 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1769 | 120.92 | 527666 RSVLT_COL1 7 345 3WXFMR RSVLT_COL1 7 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.63 | 527790 EDDY_SVC 1 8.50 527799 EDDY_NORTH 6 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.22 | 527864 CUNNINHAM 3 115 528348 BUCKEYE_TP 3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.52 | 527864 CUNNINHAM 3 115 528568 MONUMNT_TP 3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17698 | 120.69 | 527865 CUNNIGHM_N 6 230 527867 CUNNIGHM_S 6 230 *1
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17705 | 120.51 | 527865 CUNNIGHM_N 6 230 527963 POTASH_JCT 6 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17704 | 120.51 | 527867 CUNNIGHM_S 6 230 527894 HOBBS_INT 6 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17707 | 120.3 | 527894 HOBBS_INT 6 230 3WXFMR ME C0482951 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17705 | 120.57 | 527894 HOBBS_INT 6 230 527903 HOBBS_PLT3 1 18.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.23 | 527896 HOBBS_INT 7 345 527965 KIOWA 7 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.2 | 527896 HOBBS_INT 7 345 528027 RDRUNNER 7 345 UC
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.2 | 527896 HOBBS_INT 7 345 528027 RDRUNNER 7 345 XA
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17707 | 120.29 | 527965 KIOWA 7 345 528027 RDRUNNER 7 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.55 | 528024 RR_SVC_HV 3 115 528021 RDRUNNR_SVC1 15.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.64 | 528024 RR_SVC_HV 3 115 528025 RDRUNNER 3 115 Z1
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.25 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.5 | 528182 NORTH_LOVNG3 115 528193 BLACKRIVER 3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.63 | 528222 CHINA_DRAW 3 115 528225 CD_SVC_HV 3 115 Z1
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.22 | 528333 LE-WEST_SUB3 115 528334 LE-NRTH_INT3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.29 | 528341 LE-SANANDRS3 115 528627 LE-TXACO_TP3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.25 | 528348 BUCKEYE_TP 3 115 528627 LE-TXACO_TP3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.24 | 528463 SANGER_SW 3 115 528575 OXYPERMIAN 3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.24 | 528463 SANGER_SW 3 115 762442 G18-004-TAP 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.52 | 528568 MONUMNT_TP 3 115 528581 BYRD_TP 3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.28 | 528574 OXY_NHU_RCF3 115 528575 OXYPERMIAN 3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17707 | 120.5 | 528596 CARDINAL 3 115 528605 TARGA 3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17707 | 120.53 | 528603 NA_ENRICH 3 115 528605 TARGA 3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.61 | 528617 LE-WAITS 2 69.0 528325 LE-WAITS 3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.51 | 528617 LE-WAITS 2 69.0 528714 LE-FORT_SW 2 69.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.49 | 528617 LE-WAITS 2 69.0 528759 LE-TP51 2 69.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.29 | 528622 LE-SANANDRS2 69.0 528341 LE-SANANDRS3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.92 | 528626 LE-PLNSINT 2 69.0 526928 PLAINS_INT 3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.92 | 528626 LE-PLNSINT 2 69.0 528709 LE-PLNSGOAB2 69.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.52 | 528669 LE-STKLDRTP2 69.0 528725 LE-PRICE 2 69.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.59 | 528669 LE-STKLDRTP2 69.0 528740 LE-PLANS_SW2 69.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.79 | 528709 LE-PLNSGOAB2 69.0 528740 LE-PLANS_SW2 69.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.52 | 528709 LE-PLNSGOAB2 69.0 528747 LE-ALLRED 2 69.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.51 | 528714 LE-FORT_SW 2 69.0 528718 LE-NEWTEX 2 69.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.59 | 528735 LE-PLAINSUB2 69.0 528740 LE-PLANS_SW2 69.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.52 | 528775 LE-ERF 3 115 528779 LE-TALLCOTN3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.3 | 531213 SANTAFE3 115 531408 PIERCVL3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17706 | 120.48 | 531501 BUCKNER7 345 531502 CIMRRN 7 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17706 | 120.48 | 531502 CIMRRN 7 345 531503 CIMRRN 1 34.5 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17694 | 120.24 | 531510 HARBNGR3 115 3WXFMR HARBGR345 _1 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17705 | 120.5 | 539803 IRONWOOD7 345 3WXFMR IRONWOOD MPT 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17707 | 120.59 | 542951 HAW G5 1 22.0 543665 HAWTHN5 161 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17706 | 120.63 | 542955 LAC G1 1 22.0 542981 LACYGNE7 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17705 | 120.62 | 542956 LAC G2 1 24.0 542981 LACYGNE7 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17704 | 120.67 | 542957 IAT G1 1 24.0 542982 IATAN 7 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17705 | 120.74 | 542962 IAT G2 1 24.5 542982 IATAN 7 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17956 | 119.99 | 560022 CRAWFISH_DR 345 762216 G17-151TAP 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17924 | 120.98 | 560022 CRAWFISH_DR 345 762467 G18-015-TAP 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 116.89 | 560022 CRAWFISH_DR 345 763087 GEN-2018-073 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.18036 | 121.28 | 560022 CRAWFISH_DR 345 763215 G18-092-TAP 345 2
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.99 | 560252 G10-14 345 560253 G10-14-1 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.69 | 560253 G10-14-1 115 560254 G10-14-SUB1 34.5 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.69 | 560253 G10-14-1 115 560255 G10-14-SUB2 34.5 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.52 | 560581 G06-44-2 34.5 523111 NOVUS1 3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.57 | 560582 G06-44-3 34.5 560577 G06-44 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.56 | 560583 G06-44-4 34.5 560577 G06-44 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.17 | 560757 ASGI13_02_1 69.0 560758 ASGI13_02_2 34.5 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.17 | 560757 ASGI13_02_1 69.0 562731 WHEATLAND 69.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.17 | 560763 ASGI13_03_1 115 560761 ASGI13_03_2 34.5 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.66 | 562015 FIREWHEEL1 34.5 523215 FREWHELCOL17 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.66 | 562016 FIREWHEEL2 34.5 523215 FREWHELCOL17 345 2
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.16 | 562323 AGI1202&1305 115 562324 AGI1202&1305 34.5 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.17 | 562727 LESBIA 115 562728 SANJONTAP 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.17 | 562728 SANJONTAP 115 562729 CAPROCKTAP1 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.17 | 562730 CAPROCKTAP2 69.0 562729 CAPROCKTAP1 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.17 | 562730 CAPROCKTAP2 69.0 562731 WHEATLAND 69.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.65 | 563171 G15082_2 34.5 563170 G15082_1 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.23 | P11:13.8:AEPW:COM1-1
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.24 | P11:13.8:AEPW:COM2-1
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.25 | P11:13.8:AEPW:COM3-1
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.26 | P11:18:AEPW:WELSH1-1
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.26 | P11:18:AEPW:WELSH3-1
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.25 | P11:24:AEPW:PIRKEY 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.13 | P11:24:AEPW:SWS3-1
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.2 | P11:24:AEPW:TURKCOAL
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1772 | 120.56 | P12:138:AEPW-OMPA:DUNCAN-4:OMDUNCN4
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17712 | 120.09 | 584560 GEN-2015-014 115 584561 G15-014XFMR1 34.5 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17709 | 120.29 | P12:138:AEPW:ARSHILL4:STLGENS4
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17715 | 120.51 | P12:138:AEPW:SANTAFE:DUNCAN-4
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.5 | 588480 A16-010_SUB 115 3WXFMR A16-010_SUB 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1772 | 120.55 | P12:138:AEPW:DUNCAN-4:L.E.S.-4
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 119.91 | 588761 G17-033XFMR1 34.5 588760 GEN-2017-033 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 119.91 | 588765 G17-033XFMR2 34.5 588760 GEN-2017-033 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.51 | 588861 G17-047XFMR1 34.5 588860 GEN-2017-047 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17693 | 120.25 | P12:138:AEPW:ELKCTY-4:CLINTJC4
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.49 | P12:138:AEPW:SHERID4:112GORE4
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17955 | 122.68 | P12:345:AEPW:L.E.S7:TERRYRD7
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17955 | 122.67 | P12:345:AEPW:L.E.S7:TERRYRD7
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17955 | 122.65 | P12:345:AEPW-OKGE:TERRYRD7:SUNNYSD7
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1803 | 122.27 | P12:345:AEPW-OKGE:L.E.S.-7:GRACMNT7
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1803 | 122.24 | P12:345:AEPW-OKGE:L.E.S.-7:GRACMNT7
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17742 | 120.48 | P12:345:AEPW-OKGE:PITTSB-7:JOHNCO7
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17702 | 120.25 | P12:345:AEPW-OKGE:PITTSB-7:SEMINOL7
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17723 | 120.52 | P12:345:AEPW-WFEC:VALIANT7:HUGO7
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.18015 | 123.25 | P12:345:AEPW:O.K.U.-7:L.E.S.-7
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.55 | P22:345:AMMO::LABADIE:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.53 | P22:345:AMMO::LABADIE:2
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.55 | P22:345:AMMO::LABADIE:3
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.55 | P22:345:AMMO::LABADIE:4
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.54 | P22:345:AMMO::RUSHISLAND:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.51 | P22:345:AMMO::RUSHISLAND:2
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17709 | 120.24 | P13:138-13.8:AEPW:COMANC-4_#2
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17649 | 119.94 | P13:138-230:AEPW:ELKCTY-4
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17709 | 120.26 | P13:138-24:AEPW:PIRKEY 4
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17713 | 120.15 | P13:138-24:AEPW:S.W.S.-4
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17709 | 120.21 | P13:138-24:AEPW:TURK 4
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17725 | 120.54 | P13:138-345:AEPW:L.E.S.-4_#2
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1771 | 120.55 | P23:500:EES-EAI:KEO:B4941
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1771 | 120.53 | P23:500:EES-EAI:KEO:B4921
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17691 | 120.51 | 640183 GENTLMN3 345 640325 REDWILO3 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.48 | P11:26:EES-EAI:INDEP2:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17709 | 120.51 | P23:500:EES-EAI:INDEP2:B6126
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.51 | P23:500:EES-EAI:PD:INDEP2:LN:FK479
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1771 | 120.26 | P13:345-18:AEPW:WELSH 7_#1
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1771 | 120.26 | P13:345-18:AEPW:WELSH 7_#3
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.25 | P13:69-13.8:AEPW:COMANC-2
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17705 | 120.5 | 648513 GRPR1 3 345 652532 GR PRAIRIE 3 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.56 | P11:024:DPC:ALMA2:6
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17705 | 120.53 | 652537 WHITE 3 345 659286 DEERCREK-BE3 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17706 | 120.48 | 652568 GROTONSOUTH7 115 659275 GROTON_G-BE7 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17705 | 120.53 | 659286 DEERCREK-BE3 345 3WXFMR DEERCRK KU1A 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.49 | 672540 QE 6 138 672541 CORY 6 138 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.53 | 672601 BD 4 230 672306 BD 6G 18.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.53 | 672610 POPLAR 4 230 672310 POPLAR 1G 18.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.53 | 672610 POPLAR 4 230 672311 POPLAR 2G 18.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.53 | 672621 SHAND 4 230 672321 SHAND 1G 18.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.51 | 672649 CODETTE 4 230 672650 NIPAWIN 4 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.5 | 672685 SWIFTCU 4 230 672389 CHINOOK 1G 18.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.5 | 672688 PASQUA 4 230 673390 FUT-PQ1X 18.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.55 | 672696 BRADA 4 230 672699 NBEC 4 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.48 | 672699 NBEC 4 230 672392 NBEC GT 1G 18.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.49 | P13:345-230:CLEC:DOLET:5092
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.6 | P23:345:MDU::COYOTE::5707-5712-5715::::
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.76 | P23:345:MEC:CBEC 905
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.72 | P23:345:MEC:CBEC 908
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.64 | P23:345:MEC:RAUN 0180
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.71 | P23:345:MEC:RAUN 0210
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.64 | P23:345:MEC:LOUISA 954
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.64 | P23:345:MEC:LOUISA 964
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.5 | P21:115:XEL:AUTO-SINGLE:CHEMOLT7:LSPOWER7:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.49 | P21:115:XEL:AUTO-SINGLE:FARIBALTP7:FARIBALTGEN:Z
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.61 | P21:230:OTP:AUTO-SINGLE:SQBUTTE4:YNG24:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.59 | P23:345:OTP:CENTER 3:3215(1)
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.59 | P23:345:OTP:CENTER 3:3225(1)
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 119 | 760494 GEN-2017-146 230 760498 G17-146-TAP 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 119 | 760495 G17-146-XFM1 34.5 760494 GEN-2017-146 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.26 | 761356 G17-239-XFMR 34.5 761355 GEN-2017-239 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.26 | 761359 G17-239-XFMR 34.5 761355 GEN-2017-239 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 114.95 | 762132 GEN-2017-158 230 763252 G18-099-XFM1 34.5 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 114.95 | 762132 GEN-2017-158 230 763255 G18-099-XFM2 34.5 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 115.52 | 762133 G17-158XFM1 34.5 762132 GEN-2017-158 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 115.52 | 762136 G17-158XFM2 34.5 762132 GEN-2017-158 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 117.81 | 762216 G17-151TAP 345 762217 GEN-2017-151 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17956 | 121.31 | 762216 G17-151TAP 345 762467 G18-015-TAP 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 119.71 | 762218 G17-151XFM1 34.5 762217 GEN-2017-151 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 119.71 | 762221 G17-151XFM2 34.5 762217 GEN-2017-151 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 119.71 | 762224 G17-151XFM3 34.5 762217 GEN-2017-151 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 119.71 | 762227 G17-151XFM4 34.5 762217 GEN-2017-151 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.26 | 762438 GEN-2018-004 115 762442 G18-004-TAP 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 118.8 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 119.55 | 762461 G18-015-XFM1 34.5 762460 GEN-2018-015 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 119.55 | 762464 G18-015-XFM2 34.5 762460 GEN-2018-015 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17843 | 120.87 | 762467 G18-015-TAP 345 763215 G18-092-TAP 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 118.04 | 763087 GEN-2018-073 345 763088 G18-073-XFM1 34.5 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 119.21 | 763087 GEN-2018-073 345 763091 G18-073-XFM2 34.5 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 117.23 | 763120 GEN-2018-081 230 764011 G19-074-XFM1 34.5 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 117.2 | 763186 GEN-2018-089 230 763187 G18-089-XFM1 34.5 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 118.06 | 763208 GEN-2018-092 345 763215 G18-092-TAP 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 119.2 | 763208 GEN-2018-092 345 763220 G18-092-XFM1 34.5 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 119.2 | 763208 GEN-2018-092 345 763223 G18-092-XFM2 34.5 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 116.67 | 763241 GEN-2018-097 230 763242 G18-097-XFM1 34.5 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 117.6 | 763241 GEN-2018-097 230 763296 G18-111-XFM1 34.5 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 116.95 | 763241 GEN-2018-097 230 763307 G18-112-XFM1 34.5 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 116.95 | 763241 GEN-2018-097 230 763310 G18-112-XFM2 34.5 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 116.67 | 763241 GEN-2018-097 230 763395 G18-124-XFM1 34.5 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 116.67 | 763241 GEN-2018-097 230 763398 G18-124-XFM2 34.5 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 116.31 | 763483 GEN-2019-003 230 763484 G19-003-XFM1 34.5 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 119.03 | 763483 GEN-2019-003 230 763605 G19-021-XFM1 34.5 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 119.65 | 763516 GEN-2019-011 345 763517 G19-011-XFM1 34.5 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.06 | 763879 GEN-2019-056 115 763880 G19-056XFM1 34.5 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.49 | P13:345,230:CLEC::DOLHILL::1
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.29 | P13:345,24:CLEC::G1DOLHILL::1
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17674 | 120.51 | P42:345:OKGE:SB_BVTY7305
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17692 | 120.23 | P23:345:WERE:BUFF_345-534::
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17692 | 120.23 | P23:345:WERE:BUFF_345-543::
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17704 | 120.66 | P23:345:WERE:JEC_345-15::
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17702 | 120.62 | P23:345:WERE:JEC_345-16::
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17704 | 120.66 | P23:345:WERE:JEC_345-19::
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17704 | 120.66 | P23:345:WERE:JEC_345-20::
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17702 | 120.29 | P23:345:WERE:WICH_345-50::
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17707 | 120.87 | P23:345:WERE:WOLF_345-50::
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.87 | P23:345:WERE:WOLF_345-60::
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17709 | 120.28 | P42:345:AEPW:WELSH CB 10620 NBTB+FAULT
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.27 | P41:345:AEPW:WELSH CB 10630 NBTB+FAULT
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.26 | P41:345:AEPW:WELSH CB 11670 NBTB+FAULT
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17711 | 120.53 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.26 | P41:345:AEPW:WELSH CB 12540 NBTB+FAULT
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1771 | 120.49 | P43:345:AEPW:CHAMBERS SPRING CB 12720 NBTB+FAULT
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1771 | 120.49 | P42:345:AEPW:CHAMBERS SPRING CB 13720 NBTB+FAULT
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1771 | 120.49 | P42:345:AEPW:CHAMBERS SPRING CB 13850 NBTB+FAULT
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.18015 | 121.76 | P42:345:AEPW:OKLAUNION CB 3409A NBTB+FAULT
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.18063 | 122.49 | P42:345:AEPW:LAWTON EASTSIDE CB 3413A NBTB+FAULT
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.18098 | 122.73 | P42:345:AEPW:LAWTON EASTSIDE CB 3425A NBTB+FAULT
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.18028 | 123.34 | P43:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB+FAULT
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17742 | 120.48 | P42:345:AEPW:PITTSBURG CB 3433A NBTB+FAULT
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17718 | 120.18 | P42:345:AEPW:PITTSBURG CB 3441A NBTB+FAULT
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17702 | 120.25 | P42:345:AEPW:PITTSBURG CB 3445A NBTB+FAULT
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17955 | 122.67 | P42:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17955 | 122.67 | P42:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17955 | 122.65 | P42:345:AEPW:TERRYRD_CB_3421A_NBTB
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17706 | 120.65 | P23:345:KCPL:LACYGNE_R2-5::LACYGU2-LACYGNE-STILWELL
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17706 | 120.28 | P45:345:UMZW:# 1328 #: GI IN NE.
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17709 | 120.28 | P23:345:AEPW:WELSH CB 10620 NBTB
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.27 | P23:345:AEPW:WELSH CB 10630 NBTB
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.26 | P23:345:AEPW:WELSH CB 11670 NBTB
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17711 | 120.53 | P23:345:AEPW:WELSH CB 11990 NBTB
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.26 | P23:345:AEPW:WELSH CB 12540 NBTB
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1771 | 120.49 | P23:345:AEPW:CHAMBERS SPRING CB 12720 NBTB
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1771 | 120.49 | P23:345:AEPW:CHAMBERS SPRING CB 13720 NBTB
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1771 | 120.49 | P23:345:AEPW:CHAMBERS SPRING CB 13850 NBTB
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.18015 | 122.19 | P23:345:AEPW:OKLAUNION CB 3401A NBTB
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.18063 | 122.49 | P23:345:AEPW:LAWTON EASTSIDE CB 3413A NBTB
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.18098 | 122.73 | P23:345:AEPW:LAWTON EASTSIDE CB 3425A NBTB
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.18028 | 123.34 | P23:345:AEPW:LAWTON EASTSIDE CB 3429B NBTB
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17742 | 120.48 | P23:345:AEPW:PITTSBURG CB 3433A NBTB
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17718 | 120.18 | P23:345:AEPW:PITTSBURG CB 3441A NBTB
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17702 | 120.25 | P23:345:AEPW:PITTSBURG CB 3445A NBTB
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17955 | 122.67 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17955 | 122.67 | P23:345:AEPW:TERRYRD_CB_3417A_NBTB
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17955 | 122.65 | P23:345:AEPW:TERRYRD_CB_3421A_NBTB
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17738 | 120.48 | P12:138:AEPW:S.W.S.-4:L.E.S.-4
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17707 | 120.54 | P11:161:GMO:DOGWOOD_COMBINED_CYCLE_UNIT_OUTAGE
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17708 | 120.54 | P11:115:SUNC:GARDENCITY_S2:97:531459(2)
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17694 | 120.25 | P12:345:PWT:BUFF-THIS_345_1::
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17694 | 120.25 | P12:345:PWT:BUFF-THIS_345_2::
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17717 | 120.52 | P12:069:WFEC:ANADRKO_WATONGA
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17726 | 120.54 | P23:345:AEPW:VALLIANT CB 3413A NBTB
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17732 | 120.56 | P23:345:AEPW:VALLIANT CB 3417A NBTB
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17972 | 122.82 | P23:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.18229 | 125.21 | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17726 | 120.54 | P42:345:AEPW:VALLIANT CB 3413A NBTB+FAULT
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17732 | 120.56 | P42:345:AEPW:VALLIANT CB 3417A NBTB+FAULT
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17972 | 122.82 | P42:345:AEPW:LAWTON EASTSIDE CB 3417A NBTB+FAULT
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.18229 | 125.21 | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17247 | 117.77 | P42:345:OKGE:SB_BVTY7315_PRE19S
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.1767 | 120.52 | P23:345:SUNC:MO_BRK188
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17834 | 120.68 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17709 | 120.23 | P12:138-13.8:AEPW:COMANC-4_#1
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17649 | 119.93 | P12:230:AEPW:ELKCITY6:CHISHOLM6
Thermal | 05ALL | 1 | 26WP | GEN-2018-081 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.17825 | 121.03 | P12:230:AEPW:SWEETWT6:CHISHOLM6
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997711 ABBXNL844501 230 1 |  | 552.5 | 0.14998 | 164.23 | 525531 TOLK 6 230 3WXFMR TOLK 6 2
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.092 | 120.49 | P12:345:AEPW-AEPW:CHAMPSP-CLARKSV
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09199 | 120.61 | P23:345:KCPL-WERE:237LACYGNE_R1-6::LACYGU1-LACYGNE-NEOSHO
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09198 | 120.5 | P11:161:GMO:DOGWOOD_COMBINED_CYCLE_UNIT_OUTAGE_1_1
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09205 | 118.96 | P11:115:SPS:MUSTANG1&3:153MW::::
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09117 | 122.27 | P12:230:SPS:K37::1_TOLK_LAMB:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09224 | 120.48 | P12:230:SPS:K43::1_PRNGLE_HARR_E:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09202 | 120.26 | P12:230:SPS:K44::1_EPLNT_HARRW:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09317 | 120.61 | P12:115:SPS:T04::1_TRBLNC_CASTRO:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09198 | 120.48 | P12:115:SPS:T13::1_TAYLOR_WHOBBS:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09199 | 120.26 | P12:115:SPS:T14::1_MADDOX_TAYLOR:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09198 | 120.73 | P12:115:SPS:T21::1_GRSSLND_GRAHAM:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09198 | 120.29 | P12:115:SPS:T23::1_PCA_POTJCT:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09199 | 120.52 | P12:115:SPS:T26::1_CHAVES_RSWLCTY:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09046 | 120.8 | P12:115:SPS:T28A::1_LAMTON_PLANTX:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09272 | 120.54 | P12:115:SPS:T29::1_LAMTON_HALECTR:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09297 | 121.92 | P12:115:SPS:T30::1_LAMB_HOCKLY:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09297 | 121.43 | P12:115:SPS:T31::1_HOCKLY_SUNDWN:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09201 | 120.59 | P12:115:SPS:T35::1_TERRY_YOAKUM:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09198 | 121.24 | P12:115:SPS:T45::1_NORRIS_OASIS:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09173 | 120.73 | P12:115:SPS:T59::1_CARGIL_CURRY:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09418 | 120.66 | P12:115:SPS:T67::1_HAPPY_KRESS:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09198 | 120.96 | P12:115:SPS:T71::1_CRLSLE_YUMA:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09234 | 120.57 | P12:115:SPS:T81::1_COX_FLOYD:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09198 | 120.57 | P12:115:SPS:T83::1_SP-FKFD_ALLEN:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09202 | 120.91 | P12:115:SPS:T89::1_DC_N_HIGG:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09198 | 120.54 | P12:115:SPS:T91::1_HIGG_RUSSELL:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09229 | 120.51 | P12:115:SPS:V04::1_EPLANT_RNDALL:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09208 | 120.5 | P12:115:SPS:V07::1_COX_HALECTR:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09177 | 120.71 | P12:115:SPS:V09::1_HALECTR_PLANTX:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09201 | 120.56 | P12:115:SPS:V12::1_PLANTX_BAILEY:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09198 | 120.5 | P12:115:SPS:V15::1_TUCO_INDANA:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09207 | 120.51 | P12:115:SPS:V16::1_TERRY_DC_N:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09196 | 120.62 | P12:115:SPS:V24::1_WOLFTH_TERRY:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09208 | 120.6 | P12:115:SPS:V26::1_RSWLL_EDDY_N:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09198 | 120.58 | P12:115:SPS:V33::1_LUBBS_LYNN:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.0905 | 121.13 | P12:115:SPS:V37::1_CASTRO_PLANTX:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09198 | 120.63 | P12:115:SPS:V46::1_ALLEN_WHEELCK:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.092 | 120.95 | P12:115:SPS:V49::1_YOAKUM_SHLCO2:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09229 | 121.15 | P12:115:SPS:V55::1_SUNDWN_TERRY:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09217 | 120.98 | P12:115:SPS:V56::1_COCHRAN_SUNDWN:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09192 | 120.5 | P12:115:SPS:V78::2_CURRY_RSVLT:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09201 | 120.67 | P12:115:SPS:V81::1_LE-WAIT_LE-LVN:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09199 | 120.54 | P12:115:SPS:V95::1_DC_N_SHLCO2:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09198 | 120.5 | P12:115:SPS:W11::1_DC_S_SMINLE:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09199 | 120.54 | P12:115:SPS:W14::1_SMINLE_GAINES:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09198 | 120.5 | P12:115:SPS:W26::1_CUNGHM_OILCNTR:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09198 | 121.13 | P12:115:SPS:W32::1_PRMTR_FE-CLSIN:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09198 | 120.5 | P12:115:SPS:W34::1_JNSDRW_MAPCO:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.092 | 120.73 | P12:115:SPS:W35::1_GAINES_JNSDRW:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09202 | 120.52 | P12:115:SPS:W36::1_TAYLOR_JNSDRW:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09298 | 120.93 | P12:115:SPS:W40::1_WCANYON_TRBLNC:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09211 | 120.29 | P12:115:SPS:W46::1_RHILLS_NWEST:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09334 | 120.55 | P12:115:SPS:W52::1_NEWHART_KRESS:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09198 | 121.01 | P12:115:SPS:W58::1_NORTON_LOPEZ:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09198 | 120.69 | P12:115:SPS:W59::1_LOPEZ_CMPBLL:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09198 | 120.96 | P12:115:SPS:W62::1_PLSTHL_CURRY:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09198 | 120.84 | P12:115:SPS:W64::1_PLSTHL_FE-CLV:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09197 | 120.81 | P12:115:SPS:W65::1_PLSTHL_CURRY:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09198 | 120.68 | P12:115:SPS:W66::1_PORTA_GREYHUND:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09298 | 120.53 | P12:115:SPS:W77::1_RNDAL_WCANYON:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09198 | 120.51 | P12:115:SPS:W99::1_CAPITAN_CHAVES:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09198 | 120.51 | P12:115:SPS:U03::1_CARDNL_NEF:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.092 | 121.04 | P12:115:SPS:U14::1_DC_STH_INKBSN:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09201 | 120.92 | P12:115:SPS:V15::1_INKBSN_LE-WAT:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09202 | 120.55 | P12:115:SPS:U16::1_BSHLND_OUTPST:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09202 | 120.54 | P12:115:SPS:U17::1_COLTR_OUTPST:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09214 | 120.76 | P12:115:SPS:U19::1_DEAN_PLAINS:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09202 | 120.49 | P12:115:SPS:U23::1_COLTR_HILSDE:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.08907 | 127.42 | P42:345:SPS:YOAKUM:J18####:SLG1:EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.08907 | 127.42 | P43:345:SPS:YOAKUM:TF#####:SLG:EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.08907 | 127.42 | P42:345:SPS:YOAKUM:J17####:SLG:EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.08847 | 122.69 | P43:345:SPS:TUCO:SLG::EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.08907 | 127.42 | P42:345:SPS:YOAKUM:J18####:SLG2:EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.092 | 120.49 | P12:345:AEPW-AEPW:CHAMPSP-CLARKSV:::EHV::
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09197 | 120.52 | P11:18:HAST:::EGYCTR2G WEC2_LOSS OF WEC 2 GEN_:HV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09197 | 120.52 | P13:18-115:HAST:::EGYCNTR7 XFMR G2WEC 2 GSU_:HV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09198 | 120.5 | P11:161:GMO:DOGWOOD-COMBINED-CYCLE-UNIT-OUTA:::HV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09199 | 120.61 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09196 | 120.65 | P23:345:KCPL:LACYGNE-R2-5:::EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09194 | 120.66 | P11:230:WERE:JECU1-GEN:::HV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09194 | 120.66 | P11:345:WERE:JECU2-GEN:::EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09194 | 120.66 | P11:345:WERE:JECU3-GEN:::EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09198 | 120.88 | P11:345:WERE:WOLFU1-GEN:::EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09184 | 120.25 | P12:345:PWT:BUFF-THIS-345-1:::EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09184 | 120.25 | P12:345:PWT:BUFF-THIS-345-2:::EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09182 | 120.23 | P23:345:WERE:BUFF-345-534:::EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09182 | 120.23 | P23:345:WERE:BUFF-345-543:::EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09194 | 120.66 | P23:345:WERE:JEC-345-15:::EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09193 | 120.62 | P23:345:WERE:JEC-345-16:::EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09194 | 120.66 | P23:345:WERE:JEC-345-19:::EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09194 | 120.66 | P23:345:WERE:JEC-345-20:::EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09193 | 120.29 | P23:345:WERE:WICH-345-50:::EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09197 | 120.87 | P23:345:WERE:WOLF-345-50:::EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09198 | 120.87 | P23:345:WERE:WOLF-345-60:::EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09198 | 120.81 | P11:022:NPPD:COOPER1G:1:983:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09192 | 120.83 | P11:023:NPPD:GENTLM1G:1:757:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09196 | 120.68 | P11:024:NPPD:GENTLM2G:2:757:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09194 | 120.68 | P13:345:OPPD:NEBCTY1G:::EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09192 | 120.69 | P13:345:OPPD:NEBCTY2G:::EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09198 | 120.69 | P22:345:OPPD:S3458 NEBCTY1G:LT::EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09194 | 120.68 | P22:345:OPPD:S3458 NEBCTY1G:::EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09198 | 120.72 | P22:345:OPPD:S3458 NEBCTY2G:LT::EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09192 | 120.69 | P22:345:OPPD:S3458 NEBCTY2G:::EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09198 | 120.69 | P23:345:OPPD:S3458 NEBCTY1G:LT::EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09194 | 120.68 | P23:345:OPPD:S3458 NEBCTY1G:::EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09198 | 120.72 | P23:345:OPPD:S3458 NEBCTY2G:LT::EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09192 | 120.69 | P23:345:OPPD:S3458 NEBCTY2G:::EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09198 | 120.29 | P12:115:SUNC:PLYMELL-PIERCEVILLE:::HV::
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09196 | 120.53 | P11:018:UMZB:# 5 #:: DCS IN SD. DEERCREEK_MV::
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09197 | 120.5 | P11:022:UMZB:# 15 #:: LO IN ND. LELAND OLDS 1_MV::
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09197 | 120.5 | P11:020:UMZB:# 16 #:: LO IN ND. LELAND OLDS 2_MV::
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09195 | 120.61 | P11:023:UMZB:# 31 #:: AVS IN ND. ANTELOPE VALLEY 1_MV::
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09195 | 120.61 | P11:023:UMZB:# 32 #:: AVS IN ND. ANTELOPE VALLEY 2_MV::
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09191 | 120.82 | P11:024:UMZB:# 33 #:: LRS IN WY. LARAMIE RIVER STATION 1_MV::
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09198 | 120.49 | P13:230:UMZW:# 5135 #:: OA IN SD. FAULT ON TRANSFORMER (2).:HV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09198 | 120.49 | P13:230:UMZW:# 5136 #:: OA IN SD. FAULT ON TRANSFORMER (3).:HV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09198 | 120.5 | P13:230:UMZW:# 5137 #:: OA IN SD. FAULT ON TRANSFORMER (4).:HV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09197 | 120.28 | P23:345:UMZW:# 2423 #:: GI IN NE. GI 1596 BKR FAULT:EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09197 | 120.28 | P23:345:UMZW:# 2426 #:: GI IN NE. GI 1592 BKR FAULT:EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09197 | 120.28 | P23:345:UMZW:# 2432 #:: GI IN NE. GI 1092 BKR FAULT:EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09197 | 120.28 | P23:345:UMZW:# 2440 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1092 STUCK BKR:EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09197 | 120.28 | P23:345:UMZW:# 2444 #:: GI IN NE. GI-SWEET BRANCH FAULT & GI 1596 STUCK BKR:EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09197 | 120.28 | P23:345:UMZW:# 2446 #:: GI IN NE. GI-FT2 BRANCH FAULT & GI 1196 STUCK BKR:EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09197 | 120.28 | P42:345:UMZW:# 2413 #:: FT2 IN SD. FT2-LO2 BRANCH FAULT & FT2 2992 STUCK BKR:EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09197 | 120.28 | P42:345:UMZW:# 2415 #:: FT2 IN SD. FT2-GI BRANCH FAULT & FT2 3392 STUCK BKR:EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09202 | 120.2 | P11:138:WFEC:HUGO1:465MW :::
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09197 | 120.49 | P11:138:WFEC:MORLND2:132MW:::
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09196 | 120.5 | P11:138:WFEC:MORLND3:149MW :::
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09206 | 120.52 | P12:138:WFEC:ANADRKO_CLVLND::::
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09192 | 120.25 | P12:345:OKGE-AEPW:BKRBKR20::::
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09233 | 120.7 | P12:345:OKGE:BKRBKR21::::
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09253 | 120.7 | P12:345:OKGE:BKRBKR24::::
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09442 | 122.65 | P12:345:OKGE-AEPW:BKRBKR25::::
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09167 | 120.12 | P12:345:OKGE:BKRBKR336::::
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09166 | 120.11 | P12:345:OKGE:BKRBKR336_2::::
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09232 | 120.48 | P12:345:OKGE-AEPW:BKRBKR343::::
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.0951 | 122.27 | P12:345:OKGE-AEPW:BKRBKR366::::
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.0951 | 122.24 | P12:345:OKGE-AEPW:BKRBKR366::::
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09401 | 121.66 | P12:345:OKGE:BKRBKR367::::
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09234 | 120.59 | P12:345:OKGE-WFEC:BKRBKR374::::
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09234 | 120.56 | P12:345:OKGE-WFEC:BKRBKR374::::
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09171 | 120.16 | P12:345:OKGE:BKRBKR4193::::
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09171 | 120.16 | P12:345:OKGE:BKRBKR4194::::
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.0916 | 120.16 | P12:345:OKGE-SPS:BKRBKR4201::::
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.0916 | 120.16 | P12:345:OKGE-SPS:BKRBKR4202::::
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09165 | 119.95 | P12:345:OKGE:BKRBKR443NEW::::
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09165 | 119.95 | P12:345:OKGE:BKRBKR443NEW2::::
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09181 | 120.27 | P12:345:OKGE-ITC:BKRBKR502::::
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09181 | 120.27 | P12:345:OKGE-ITC:BKRBKR503::::
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09194 | 120.61 | P12:345:OKGE:BKRBKR604::::
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09192 | 120.72 | P12:345:OKGE:BKRBKR604_2::::
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09872 | 123.72 | P42:345:OKGE:SB_BVTY7387::::
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09238 | 120.63 | P42:345:OKGE:SB_SPCK7383::::
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09196 | 120.53 | P11:115:SUNC:GARDENCITY_S2:103:531459(2):HV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09196 | 120.54 | P11:115:SUNC:FORTDDODGE_4:157:539670(4):HV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.0916 | 120.5 | P12:345:SUNC-NPPD:MINGO-REDWILLOW::531451-640325(1):EHV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09198 | 120.61 | P13:115:SUNC:HOLCOMB_GSU:::HV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09196 | 120.53 | P13:115:SUNC:S2_GSU:::HV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09196 | 120.54 | P13:115:SUNC:FORTDODGE_GSU:::HV:
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09198 | 120.48 | 300002 1THLG2 22.0 301505 5THOMHLGSU2 161 2
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09198 | 120.62 | 300003 1THLG3 24.0 301503 7THOMHLGSU3 345 3
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09198 | 120.48 | 300006 1NM G1 22.0 301536 5NEWMADGSU1 161 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09198 | 120.48 | 300007 1NM G2 22.0 301537 7NEWMADGSU2 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09198 | 120.48 | 300046 7NEWMAD 345 301537 7NEWMADGSU2 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09198 | 120.62 | 300049 7THOMHL 345 301503 7THOMHLGSU3 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09198 | 120.48 | 300103 5NEWMAD 161 301536 5NEWMADGSU1 161 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09198 | 120.48 | 300132 5THMHLB2 161 301505 5THOMHLGSU2 161 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09198 | 120.29 | 300739 7BLACKBERRY 345 532797 WOLFCRK7 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09198 | 120.56 | P11:20:AMMO:1LAB�� G1:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09198 | 120.54 | P11:20:AMMO:1LAB�� G2:2
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09198 | 120.75 | P11:345:AMMO::CALLAWAY:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09198 | 120.56 | P11:345:AMMO::LABADIE:3
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09198 | 120.56 | P11:345:AMMO::LABADIE:4
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09198 | 120.55 | P11:345:AMMO::RUSHISLAND:U1
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09198 | 120.54 | P11:345:AMMO::RUSHISLAND:U2
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09198 | 120.53 | P11:138:AMMO::SIOUX:2
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09199 | 120.49 | P13:345-230:CLEC::DOLHILL7:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09198 | 120.29 | P11:345-24:CLEC::DOLHILL7:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09198 | 120.29 | P11:24:CLEC::G1DOLHIL:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09198 | 120.53 | P12:765:AEP:AEP ROCKP-AEP JEFF 765
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09198 | 120.48 | P11:HV:EES::1ISES U1:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09198 | 120.25 | P11:HV:EES::PIRKEY 1:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09198 | 120.26 | P11:EHV:EES::WELSH3-1:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09198 | 120.2 | P11:HV:EES::TURKCOAL:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09198 | 120.48 | P12:HV:EES::5ISES%:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09198 | 120.74 | P12:EHV:EES::7CALAWY 1:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.092 | 120.49 | P12:EHV:EES::CHAMSPR7!:CLARKSV7!:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.092 | 120.21 | P12:HV:EES::TURK 4%:1(1)
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.092 | 120.26 | P12:EHV:EES::WELSH 7:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.092 | 120.26 | P12:EHV:EES::WELSH 7:1(1)
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09199 | 120.26 | P12:HV:EES::PIRKEY 4:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09198 | 120.53 | 344011 7HUGHES 345 344012 7HPW-N 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09198 | 120.55 | 344884 7LABADIE1 345 344894 1LAB G1 20.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09198 | 120.53 | 344885 7LABADIE2 345 344895 1LAB G2 20.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09198 | 120.55 | 344886 7LABADIE3 345 344896 1LAB G3 20.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09198 | 120.55 | 344887 7LABADIE4 345 344897 1LAB G4 20.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09198 | 120.54 | 345667 7RUSH 1 345 345670 1RUSH G1 18.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09198 | 120.53 | 345668 7RUSH 2 345 345671 1RUSH G2 18.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09198 | 120.52 | 345755 4SIOUX 1 138 345756 1SIOUX 1 18.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09198 | 120.52 | 345764 4SIOUX 2 138 345765 1SIOUX 2 18.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09198 | 120.6 | P12:345:MDU::CENTER:COYOTE:1::::
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09198 | 120.6 | P13:345:MDU:COYOTE GSU LOSS:COYOTE::1::::
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09198 | 120.82 | P11:345:MEC-NPPD:COOPER 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09198 | 120.72 | P11:24:XEL:AUTO-SINGLE:SHERC31G:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09198 | 120.72 | P11:24:XEL:AUTO-SINGLE:SHERC32G:2
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09198 | 120.81 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09198 | 120.64 | P11:20:XEL:AUTO-SINGLE:PRIS31G:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09198 | 120.63 | P11:20:XEL:AUTO-SINGLE:PRIS32G:2
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09198 | 120.68 | P11:22:XEL:AUTO-SINGLE:MNTCE31G:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09198 | 120.64 | P11:20:XEL:AUTO-SINGLE:KING31G:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09198 | 120.48 | P11:18:XEL:AUTO-SINGLE:BLKD76G:6
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09198 | 120.69 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09198 | 120.69 | P11:22:GRE:AUTO-SINGLE:GRE-COAL42G:2
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09198 | 120.61 | P11:24:OTP:AUTO-SINGLE:BIGSTN1G:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09198 | 120.63 | P11:20:OTP:AUTO-SINGLE:CENTER2G:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09198 | 120.52 | P11:22:OTP:AUTO-SINGLE:CENTER1G:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09198 | 120.61 | P11:24:OTP:AUTO-SINGLE:COYOTE1G:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09198 | 120.51 | P11:24:DPC:AUTO-SINGLE:GENOA53G:3
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09198 | 120.5 | P12:115:XEL:AUTO-SINGLE:CHEMOLT7:LSPOWER7:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09198 | 120.49 | P12:115:XEL:AUTO-SINGLE:FARIBALTP7:FARIBALTGEN:Z
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09198 | 120.61 | P12:230:OTP:AUTO-SINGLE:SQBUTTE4:YNG24:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09198 | 120.69 | P13:24-345:XEL:AUTO-SINGLE:SHERC31G:SHERCO3:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09198 | 120.69 | P13:24-345:XEL:AUTO-SINGLE:SHERC32G:SHERCO3:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09198 | 120.78 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09198 | 120.64 | P13:20-345:XEL:AUTO-SINGLE:PRIS31G:PRISLD3:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09198 | 120.64 | P13:20-345:XEL:AUTO-SINGLE:PRIS32G:PRISLD3:2
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09198 | 120.68 | P13:22-345:XEL:AUTO-SINGLE:MNTCE31G:MNTCELO3:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09198 | 120.62 | P13:20-345:XEL:AUTO-SINGLE:KING31G:ASKING3:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09198 | 120.48 | P13:18-115:XEL:AUTO-SINGLE:BLKD76G:BLKDG27:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09198 | 120.67 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL41G:GRE-COALCR4:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09198 | 120.67 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL42G:GRE-COALCR4:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09198 | 120.6 | P13:230-24:OTP:AUTO-SINGLE:BIGSTON4:BIGSTN1G:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09198 | 120.61 | P13:20-230:OTP:AUTO-SINGLE:CENTER2G:YNG24:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09198 | 120.51 | P13:22-230:OTP:AUTO-SINGLE:CENTER1G:CENTER4:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09198 | 120.6 | P13:24-345:OTP:AUTO-SINGLE:COYOTE1G:COYOTE3:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09198 | 120.5 | P13:24-161:DPC:AUTO-SINGLE:GENOA53G:GENOA5:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09198 | 120.55 | P13:24-161:DPC:AUTO-SINGLE:JPM:ALMA5:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09198 | 120.6 | P11:115:XEL:RIV COMBINE CYCLE
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09198 | 120.51 | P12:115:XEL:BDS #2 5
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09198 | 120.49 | P11:115:XEL:HBR #6 7 8
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09198 | 120.63 | P23:345:XEL:8H14 PRI
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09198 | 120.64 | P23:345:XEL:8H17 PRI AS
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09198 | 120.78 | P23:345:XEL:8N28 SHC
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09198 | 120.7 | P23:345:XEL:8N22 SHC
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09198 | 120.69 | P23:345:XEL:8N17 SHC
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09198 | 120.68 | P23:345:XEL:8N8 MNN
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09198 | 120.63 | P23:345:XEL:8P1 KING
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09198 | 120.63 | P23:345:XEL:8P2 KING
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09198 | 120.5 | P11:22:ALTW:AUTO-SINGLE:LANS54G:4
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09198 | 120.64 | P11:22:ALTW:AUTO-SINGLE:ARNOLD1G:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09198 | 120.67 | P11:24:ALTW:AUTO-SINGLE:OTTUMW1G:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09198 | 120.49 | P13:22-161:ALTW:AUTO-SINGLE:LANS54G:LANSINGL15:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09198 | 120.63 | P13:22-161:ALTW:AUTO-SINGLE:ARNOLD1G:ARNOLD5:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09198 | 120.66 | P13:24-161:ALTW:AUTO-SINGLE:OTTUMW1G:OTTUMWA5:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09198 | 120.74 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09198 | 120.8 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09198 | 120.65 | P11:22:MEC:AUTO-SINGLE:NEAL3G:3
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09198 | 120.73 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09198 | 120.66 | P11:24:MEC:AUTO-SINGLE:LOUIS31G:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09198 | 120.72 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09198 | 120.76 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09198 | 120.64 | P13:345-22:MEC:AUTO-SINGLE:RAUN3:NEAL3G:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09198 | 120.71 | P13:345-24:MEC:AUTO-SINGLE:RAUN3:NEAL4G:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09198 | 120.64 | P13:345-24:MEC:AUTO-SINGLE:LOUISA3:LOUIS31G:1
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09194 | 120.66 | P11:230:WERE:JECU1_GEN::
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09194 | 120.66 | P11:345:WERE:JECU2_GEN::
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09194 | 120.66 | P11:345:WERE:JECU3_GEN::
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09198 | 120.88 | P11:345:WERE:WOLFU1_GEN::
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09206 | 120.48 | 511453 DUNCAN-4 138 511552 DUNCHERTP4 138 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09206 | 120.48 | 511455 D.E.S.-4 138 511552 DUNCHERTP4 138 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09198 | 120.48 | 511456 O.K.U.-7 345 511565 OKLAUN HVDC7 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09198 | 119.42 | 511456 O.K.U.-7 345 588760 GEN-2017-033 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09497 | 122.19 | 511456 O.K.U.-7 345 763215 G18-092-TAP 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09511 | 122.76 | 511468 L.E.S.-7 345 762467 G18-015-TAP 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.0941 | 122.19 | 511468 L.E.S.-7 345 763215 G18-092-TAP 345 2
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.0921 | 120.56 | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09356 | 120.68 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.08592 | 117.21 | 511553 CHISHOLM7 345 523961 POTTER_CO 7 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.08592 | 117.21 | 511553 CHISHOLM7 345 523961 POTTER_CO 7 345 2
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.08908 | 119.86 | 511553 CHISHOLM7 345 755000 WWDBORDT 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09229 | 120.5 | 511557 CHISHOLM6 230 3WXFMR CHISHOLM6 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09212 | 120.51 | 514801 MINCO 7 345 555234 NSUB345 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09126 | 120.15 | 515375 WWRDEHV7 345 755000 WWDBORDT 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09872 | 123.76 | 515458 BORDER 7 345 560022 CRAWFISH_DR 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09872 | 123.7 | 515458 BORDER 7 345 755000 WWDBORDT 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09196 | 120.51 | 515618 BALKOW 7 345 3WXFMR BALKOW 7 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09196 | 120.5 | 515618 BALKOW 7 345 3WXFMR BALKOW 7 1_Dup1
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09192 | 120.73 | 515634 PALDR1W7 345 3WXFMR PALO2 _1 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09198 | 120.63 | 515677 BADGER 7 345 563170 G15082_1 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09198 | 120.49 | 522800 MU-TULIA 3 115 525179 TULIA_TP 3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09198 | 120.63 | 522892 MU-BROWNFLD2 69.0 526761 BROWNFLD_TP2 69.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09196 | 120.52 | 523093 HITCHLAND 3 115 523174 GOODWELLWND3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09357 | 120.53 | 523095 HITCHLAND 6 230 523309 MOORE_CNTY 6 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09198 | 120.88 | 523097 HITCHLAND 7 345 523112 NOVUS1 7 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09198 | 120.93 | 523097 HITCHLAND 7 345 523215 FREWHELCOL17 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.08987 | 119.43 | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.08035 | 117.75 | 523097 HITCHLAND 7 345 523961 POTTER_CO 7 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09198 | 120.99 | 523097 HITCHLAND 7 345 560252 G10-14 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09198 | 120.5 | 523099 TC-DRYTRLS 3 115 588480 A16-010_SUB 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09198 | 120.74 | 523112 NOVUS1 7 345 3WXFMR NOVUS XF2 2
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09198 | 120.52 | 523112 NOVUS1 7 345 3WXFMR XIANA2011198 _1 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09196 | 120.5 | 523118 BUFF_DUNES 7 345 523853 FINNEY 7 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09198 | 120.51 | 523120 COLE 3 115 588860 GEN-2017-047 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09209 | 120.48 | 523221 XIT_INTG 6 230 3WXFMR SIEM_T126401 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09224 | 120.48 | 523267 PRINGLE 6 230 3WXFMR ENRCO13617-1 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09224 | 120.48 | 523267 PRINGLE 6 230 523979 HARRNG_EST 6 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09275 | 120.61 | 523309 MOORE_CNTY 6 230 523323 MCDWL_CREEK6 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09239 | 120.53 | 523323 MCDWL_CREEK6 230 523959 POTTER_CO 6 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.0919 | 120.85 | 523959 POTTER_CO 6 230 523979 HARRNG_EST 6 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09669 | 121.98 | 523959 POTTER_CO 6 230 524267 BUSHLAND 6 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.12148 | 122.4 | 523959 POTTER_CO 6 230 525461 NEWHART 6 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.12433 | 129.34 | 523961 POTTER_CO 7 345 3WXFMR WAUK 90343-A 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09184 | 120.79 | 523961 POTTER_CO 7 345 524296 SPNSPUR_WND7 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09201 | 120.27 | 523977 HARRNG_WST 6 230 523971 HARRNGTON1 1 24.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09192 | 120.79 | 523977 HARRNG_WST 6 230 524010 ROLLHILLS 6 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09226 | 120.22 | 523978 HARRNG_MID 6 230 523979 HARRNG_EST 6 230 @1
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.092 | 120.29 | 524010 ROLLHILLS 6 230 3WXFMR WAUK WT01104 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09202 | 120.55 | 524267 BUSHLAND 6 230 3WXFMR WH 7001795 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09989 | 122.23 | 524267 BUSHLAND 6 230 524623 DEAFSMITH 6 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09184 | 120.89 | 524296 SPNSPUR_WND7 345 524299 SPNSPUR_COL7 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09184 | 120.89 | 524299 SPNSPUR_COL7 345 3WXFMR SPNSPUR_COL7 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.10266 | 120.9 | 524415 AMA_SOUTH 6 230 525213 SWISHER 6 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09198 | 121.01 | 524502 NORTON 3 115 524509 FE-TUCMCARI3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09298 | 120.82 | 524575 DS-#25+ 3 115 524597 PANDAHFD 3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09298 | 120.9 | 524575 DS-#25+ 3 115 524630 TIERABLANCA3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09198 | 120.5 | 524604 HEREFRD_SB 2 69.0 524608 HERFRD_STH 2 69.0 *1
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09489 | 125.98 | 524623 DEAFSMITH 6 230 760498 G17-146-TAP 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09198 | 120.78 | 524721 DS-#15&#19+2 69.0 524745 CASTRO_CNTY2 69.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09198 | 120.84 | 524764 NORRIS_TP 3 115 524801 NORRIS 3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09195 | 120.49 | 524770 PLSNT_HILL 6 230 3WXFMR EFAE1100068A 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09198 | 120.84 | 524776 N_CLOVIS_TP3 115 524777 N_CLOVIS 3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09198 | 120.78 | 524790 CANNON_TP 3 115 524794 CANNONAFB 3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09471 | 127.03 | 524875 OASIS 6 230 524885 SN_JUAN_TAP6 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09215 | 121.66 | 524875 OASIS 6 230 524909 ROOSEVELT 6 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09452 | 127.79 | 524885 SN_JUAN_TAP6 230 527483 CHAVES_CNTY6 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09192 | 120.65 | 524909 ROOSEVELT 6 230 3WXFMR ABB LMM60042 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09185 | 125.82 | 524909 ROOSEVELT 6 230 525531 TOLK 6 230 2
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09198 | 121.25 | 524923 PORTALES 2 69.0 524929 RO-PORT_MTR2 69.0 @1
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09198 | 120.88 | 524923 PORTALES 2 69.0 524941 PORTALES#1 2 69.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09198 | 120.84 | 525023 BC-BAIL_MTR2 69.0 525027 BAILEYCO 2 69.0 @1
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.0905 | 120.8 | 525056 BC-EARTH 3 115 525480 PLANT_X 3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09198 | 120.57 | 525192 KRESS_INT 3 115 3WXFMR ENRCO 136155 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09175 | 120.29 | 525213 SWISHER 6 230 3WXFMR SIEM_T127101 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.10911 | 121.59 | 525213 SWISHER 6 230 525461 NEWHART 6 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09198 | 120.54 | 525272 KISER 3 115 3WXFMR VON 13819/1 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09198 | 120.81 | 525326 COX 3 115 3WXFMR ELCO 13474-3 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09198 | 120.81 | 525414 LAMTON 3 115 3WXFMR ASEA MLL9204 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09019 | 122.16 | 525481 PLANT_X 6 230 3WXFMR WH ALM20171 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09788 | 127.05 | 525481 PLANT_X 6 230 526435 SUNDOWN 6 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09489 | 124.03 | 525481 PLANT_X 6 230 760498 G17-146-TAP 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.08911 | 120.86 | 525481 PLANT_X 6 230 762174 G17-218TAP 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.08876 | 120.92 | 525481 PLANT_X 6 230 762174 G17-218TAP 230 2
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09566 | 128.41 | 525531 TOLK 6 230 525586 NEEDMORE 6 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09117 | 122.27 | 525531 TOLK 6 230 525637 LAMB_CNTY 6 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09924 | 127.4 | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.08773 | 121.08 | 525531 TOLK 6 230 762174 G17-218TAP 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.08744 | 121.13 | 525531 TOLK 6 230 762174 G17-218TAP 230 2
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.14998 | 162.04 | 525549 TOLK 7 345 3WXFMR ABBXNL844501 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09566 | 128.41 | 525586 NEEDMORE 6 230 526935 YOAKUM 6 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09117 | 122.27 | 525637 LAMB_CNTY 6 230 3WXFMR WH ALM20172 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09198 | 120.54 | 525828 TUCO_INT 3 115 3WXFMR DS F78800913 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09701 | 120.96 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.0984 | 121.11 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _9 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.08847 | 122.69 | 525832 TUCO_INT 7 345 526936 YOAKUM_345 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09297 | 121.33 | 526020 HOCKLEY 3 115 526036 LC-OPDYKE 3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09297 | 121.18 | 526036 LC-OPDYKE 3 115 526434 SUNDOWN 3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09198 | 120.57 | 526160 CARLISLE 3 115 3WXFMR WH RLP38371 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09198 | 120.79 | 526162 LP-DOUD_TP 3 115 526176 LP-DOUD 3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09198 | 120.82 | 526268 LUBBCK_STH 3 115 3WXFMR NA 70454A 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09217 | 120.81 | 526361 COCHRAN 3 115 526424 PACIFIC 3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09217 | 120.9 | 526424 PACIFIC 3 115 526434 SUNDOWN 3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09229 | 120.94 | 526434 SUNDOWN 3 115 526445 AMOCO_TP 3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09199 | 120.51 | 526435 SUNDOWN 6 230 3WXFMR UPDATE LATER _12 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09358 | 124.22 | 526435 SUNDOWN 6 230 526460 AMOCO_SS 6 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09229 | 120.8 | 526445 AMOCO_TP 3 115 526484 LG-LEVELAND3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09358 | 121.88 | 526460 AMOCO_SS 6 230 526935 YOAKUM 6 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09229 | 120.79 | 526484 LG-LEVELAND3 115 526491 LG-CLAUENE 3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09198 | 120.51 | 526525 WOLFFORTH 6 230 3WXFMR UPDATE LATER _13 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09217 | 122.38 | 526935 YOAKUM 6 230 527028 INK_BASIN 6 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.08947 | 129.67 | 526936 YOAKUM_345 345 527896 HOBBS_INT 7 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09218 | 121.79 | 527028 INK_BASIN 6 230 527894 HOBBS_INT 6 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09202 | 120.9 | 527130 DENVER_N 3 115 527286 HIGGEAST 3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.092 | 119.59 | 527149 MUSTANG 6 230 527151 GS-MUSTANG 6 230 @1
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09198 | 120.62 | 527202 SEAGRAVES 3 115 3WXFMR ABB MLL92408 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09198 | 120.59 | 527212 DIAMONDBACK3 115 3WXFMR HOW 36773714 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09202 | 120.88 | 527286 HIGGEAST 3 115 527363 HIGG 3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.092 | 120.62 | 527325 OXY_WSEM_TP3 115 527362 JOHNSON_DRW3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09198 | 120.59 | 527340 DOSS 3 115 3WXFMR ELCO 13566/1 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09198 | 120.58 | 527345 LEGACY 2 69.0 527350 XTO_ROBRTSN2 69.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09198 | 120.58 | 527346 LEGACY 3 115 3WXFMR VROL 13735-1 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09198 | 120.56 | 527350 XTO_ROBRTSN2 69.0 527355 BOARDMAN 2 69.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09198 | 120.51 | 527355 BOARDMAN 2 69.0 527365 FLANNAGAN 2 69.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09198 | 120.5 | 527360 MAPCO 3 115 527362 JOHNSON_DRW3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09198 | 120.58 | 527362 JOHNSON_DRW3 115 528775 LE-ERF 3 115 @1
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09198 | 120.48 | 527370 TENNECO_TAP2 69.0 527371 TENNECO 2 69.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.092 | 120.29 | 527470 CHVS_SLRCOL3 115 527482 CHAVES_CNTY3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09306 | 121.58 | 527483 CHAVES_CNTY6 230 527799 EDDY_NORTH 6 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09198 | 120.49 | 527508 PRICE 3 115 527509 PRICE_TAP 3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09198 | 120.5 | 527514 CV-PINE 2 69.0 527563 ROSWLL_INT 2 69.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09198 | 120.52 | 527563 ROSWLL_INT 2 69.0 527575 SW_4702 2 69.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09208 | 120.61 | 527564 ROSWLL_INT 3 115 527597 TWEEDY 3 115 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09198 | 120.52 | 527575 SW_4702 2 69.0 527589 CV-ORCHARD 2 69.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09198 | 120.48 | 527589 CV-ORCHARD 2 69.0 527619 DEXTER_TP 2 69.0 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09192 | 120.69 | 527653 MILO_WIND 1 34.5 527655 RSVLT_CC_E 7 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09181 | 120.67 | 527654 RSVLT_CC_W 7 345 527655 RSVLT_CC_E 7 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09181 | 120.92 | 527654 RSVLT_CC_W 7 345 527666 RSVLT_COL1 7 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09174 | 120.92 | 527655 RSVLT_CC_E 7 345 527656 CROSSROADS 7 345 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09181 | 120.92 | 527666 RSVLT_COL1 7 345 3WXFMR RSVLT_COL1 7 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09198 | 120.63 | 527790 EDDY_SVC 1 8.50 527799 EDDY_NORTH 6 230 1
Thermal | 05ALL | 1 | 26WP | GEN-2018-089 | FROM->TO | 525531 TOLK 6 230 997712 TOLK 6 230 2 |  | 560 | 0.09198 | 120.22 | 527864 CUNNINHAM 3 115 528348 BUCKEYE_TP 3 115 1