## tblAllFacilityLog
STUDYDES | FacilityName | FacilityUpgradeCode | ModelArea1 | ModelArea2 | FZONENAME | TZONENAME | MONTFLAG | MONTFB | MONTFNAME | MONTTB1 | MONTTNAME1 | MONTTB2 | MONTTNAME2 | MONTCKT | Case | RATEA | RATEB | RATEC | Assessment Loading | BaseCaseLoading | TransferCaseLoading | NameOfBusWithMonitoredVoltage | Assessment Voltage | BaseCaseVoltage | TransferCaseVoltage | VINIT | VMIN | VMAX | CATEGORY | CONTTYPE | CONTNAME | CONTXFMRFLAG | CONTFB | CONTFNAME | CONTTB1 | CONTTNAME1 | CONTTB2 | CONTTNAME2 | CONTCKT | TransmissionProviderCommentsNotes | RequiredRateB | TransmissionOwnerComments | OwnerDesignation | UpgradeName | UpgradeComponentWithinFacility | NewSummerA | NewSummerB | NewOtherA | NewOtherB | DistToConstruct | TotalLead | ConstructionLeadOnly | NewOrConstructWhileEnergized | NewR | NewX | NewB | CommentsRegardingUpgradeRequirements | NewCost | EffDate | NetPlantDate | ReusableEx_GrossValue | ReusableEx_NetValue | Reusable_EndofDepr | SalvageValue | NewCostWhileExpediting | EffDateExpedited | StartDeprExpedited | EndDeprExpedited | NetPlantDateExpedited | ReusableEx_GrossExpedited | ReusableEx_NetExpedited | Reusable_EndofDeprExpedited | SalvageValueExpedited | Generation 1 Owner & Unit (Name) | Generation 1 Redispatch Cost ($) | Generation 1 Redispatch Date (M/D/Y) | Generation 2 Owner & Unit (Name) | Generation 2 Redispatch Cost ($) | Generation 2 Redispatch Date (M/D/Y) | Generation 3 Owner & Unit (Name) | Generation 3 Redispatch Cost ($) | Generation 3 Redispatch Date (M/D/Y) | ActualCompletion | ActualNewCost | ActualNetPlantDate | ActualReusableEx_GrossValue | ActualReusableEx_NetValue | ActualReusable_EndofDepr | ActualSalvageValue | Actual_NewCostWhileExpediting | Actual_StartDeprExp | Actual_EndDeprExp | Actual_NetPlantDateExpedited | ActualReusableEx_GrossExpedited | ActualReusableEx_NetExpedited | ActualReusable_EndofDeprExpedited | Actual_SalvageValueExpedited | SPPReliabilityDate | DUN | EOC | EarliestDate
2006-AG1 | 166TH STREET - JAGGARD JUNCTION 115KV CKT 1 | U | WERE | WERE |  |  | 0 | 533233 |  | 533243 |  | 0 |  | 1 | [15 empty] | BASECASE | BASE CASE | [8 empty] | Credit Flowgate |  |  | WERE | 166TH STREET - JAGGARD JUNCTION 115KV CKT 1 | Rebuild 166th Street - Jaggard Junction 115 kV line. | [53 empty] | 2010-02-03 | 2010-02-03
GI | ALBION - PETERSBURG 115KV CKT 1 | U | NPPD | NPPD | NPPD_686 | NPPD_686 | 0 | 640318 | PETRSBG7 115.00 | 640054 | ALBION 7 115.00 | 0 |  | 1 | [15 empty] | BASECASE | BASE CASE | [8 empty] | Credit Flowgate |  |  | NPPD | Albion - Petersburg 115kV Ckt 1 Petersburg Upgrade | Replace Breaker Switch 1106-D & jumpers; Replace Petersburg 115kV Substation main bus; Upgrade and replace transmission structures on 115kV lines TL1168 A & B to facilitate 100 degrees Centigrade line operation | [13 empty] | 2011-01-01 | [39 empty] | 2012-12-31 | 2012-12-31
2006-AG1 | ALUMAX TAP - BANN 138KV CKT 1 | U | AEPW | AEPW |  |  | 0 | 508049 | ALUMXT 4 138 | 508054 | BANN 4 138 | 0 |  | 1 | [15 empty] | BASECASE | BASE CASE | [8 empty] | Credit Flowgate |  |  | AEPW | ALUMAX TAP - BANN 138KV CKT 1 | Replace six (6) 138 kV switches, five at Bann & one at Alumax Tap. Rebuild 0.67 miles of 1024 ACAR with 2156 ACSR. Replace wavetrap & jumpers @ Bann. Replace breaker 3300 @ Bann. | [53 empty] | 2008-06-01 | 2008-06-01
GI-DP | Ashdown REC (AECC delivery point) | U | AEPW | AEPW | SARK | SARKAECC | 0 | 507428 | OKAY 4 138.00 | 507402 | ASHDWNR4 138.00 | 507431 |  | 1 | [15 empty] | BASECASE | BASE CASE | [8 empty] | Credit Flowgate |  |  | AEPW | Ashdown REC (AECC delivery point) | Replace switches 6276 and 6277 with 3000 A, 138 kV switches and replace the conductor between them with 1590 ACSR. | [13 empty] | 2007-10-01 | [39 empty] | 2011-12-01 | 2011-12-01
GI | ASHDOWN REC (MILLWOOD) - OKAY 138KV CKT 1 | U | AEPW | AEPW | SARK | SARKAECC | 0 | 507428 | OKAY 4 138.00 | 507402 | ASHDWNR4 138.00 | 0 |  | 1 | [15 empty] | BASECASE | BASE CASE | [8 empty] | Credit Flowgate |  |  | AEPW | ASHDOWN REC (MILLWOOD) - OKAY 138KV CKT 1 | Rebuild fourteen (14.3) miles of 115 kV line to 138 kV and reconductor with 1590 ACSR. | [13 empty] | 2007-10-01 | [39 empty] | 2011-12-01 | 2011-12-01
GI | ASHDOWN REC (MILLWOOD) - PATTERSON 138KV CKT 1 | U | AEPW | AEPW | SARKAECC | SARK | 0 | 507402 | ASHDWNR4 138.00 | 507431 | PATTERS4 138.00 | 0 |  | 1 | [15 empty] | BASECASE | BASE CASE | [8 empty] | Credit Flowgate |  |  | AEPW | ASHDOWN REC (MILLWOOD) - PATTERSON 138KV CKT 1 | Reconductor line and convert line to 138 kV. Convert Patterson station to breaker-and-a half configuration. | [13 empty] | 2007-10-01 | [39 empty] | 2011-12-01 | 2011-12-01
2019-AG2 | BAILEYV3 - SENECA 3 - 1 | EXP | WERE | WERE |  |  | 0 | 533322 | BAILEYV3 | 533337 | SENECA 3 | 0 |  | 1 | 21LP | 86 | 92 | 0 | 98.1 | 60.914 | 100.6 | [7 empty] | CATEGORYB | SINGLE | HARBINE7 - STEELEC7 - 1 | 0 | 640208 | HARBINE7 | 640426 | STEELEC7 | 0 |  | 1 |  |  |  | WERE | Baileyville - South Seneca 115kV Rebuild | Rebuild 115kV line from Baileyville - South Seneca | [12 empty] | 6178208 | 2019-05-08 | [39 empty] | 2021-04-01 | 2022-06-01
2019-AG2 | BAILEYV3 - SMITTYV3 - 1 | EXP | WERE | WERE |  |  | 0 | 533338 | SMITTYV3 | 533322 | BAILEYV3 | 0 |  | 1 | 21LP | 86 | 92 | 0 | 98.6 | 61.8546 | 101.2 | [7 empty] | CATEGORYB | SINGLE | HARBINE7 - STEELEC7 - 1 | 0 | 640208 | HARBINE7 | 640426 | STEELEC7 | 0 |  | 1 |  |  |  | WERE | Baileyville - Smittyville 115kV Rebuild | Rebuild 115kV line from Baileyville - Smittyville | [12 empty] | 8839308 | 2019-05-08 | [39 empty] | 2021-04-01 | 2022-06-01
2007-AG3 | BARBER - MEDICINE LODGE 115KV CKT 1 | U | MKEC | MKEC |  |  | 0 | 539673 | MED-LDG3 115.00 | 539760 | BARBER 3 115.00 | 0 |  | 1 | [15 empty] | BASECASE | BASE CASE | [8 empty] | Credit Flowgate |  |  | MKEC | BARBER - MEDICINE LODGE 115KV CKT 1 | Rebuild line | [53 empty] | 2009-12-01 | 2013-06-01
2007-AG3 | BARBER - SAWYER 115KV CKT 1 | U | MKEC | MKEC |  |  | 0 | 539760 | BARBER 3 115.00 | 539649 | SAWYER 3 138 | 0 |  | 1 | [15 empty] | BASECASE | BASE CASE | [8 empty] | Credit Flowgate |  |  | MKEC | BARBER - SAWYER 115KV CKT 1 | Rebuild line | [53 empty] | 2009-12-01 | 2013-06-01
2007-AG3 | BARBER (BARBER 4) 138/115/2.72KV TRANSFORMER CKT 1 | U | MKEC |  |  |  | 2 | 539674 | BARBER 4 138.00 | 539760 | BARBER 3 115.00 | 539917 | BARBER-T 2.7200 | 1 | [15 empty] | BASECASE | BASE CASE | [8 empty] | Credit Flowgate |  |  | MKEC | MEDICINE LODGE 138/115KV TRANSFORMER CKT 1 | Upgrade transformer | [53 empty] | 2009-12-01 | 2013-06-01
2005-AG2 | BEELINE - EXPLORER GLENPOOL 138KV CKT 1 | U | OKGE | OKGE |  |  | 0 | 515473 | EXPGLNT4 | 515247 | BEELINE4 138 | 0 |  | 1 | [15 empty] | BASECASE | BASE CASE | [8 empty] | Credit Flowgate |  |  | OKGE | BEELINE - EXPLORER GLENPOOL 138KV CKT 1 | Reconductor .92miles of line with Drake ACCC/TW. | [53 empty] | 2009-06-01 | 2009-06-01
2019-AG2 | BRKN BW4 - BETHEL 4 - 1 | S | AEPW | SWPA |  |  | 0 | 510928 | BETHEL 4 | 505614 | BRKN BW4 | 0 |  | 1 | 22LP | 191 | 191 | 0 |  | 45.8792 | 105.7 | [7 empty] | CATEGORYB | NONSINGLE | 84224 | 0 | 0 |  | 0 |  | 0 | [5 empty] | SWPA | Broken Bow 138 kV Terminal Upgrades | Replace 1 wave trap and 3 CTs at Broken Bow 138 kV substation | [12 empty] | 102977 | 2020-03-09 | [39 empty] | 2022-04-01 | 2022-04-01
2019-AG2 | BRKN BW4 - BETHEL 4 - 1 | S | AEPW | SWPA |  |  | 0 | 510928 | BETHEL 4 | 505614 | BRKN BW4 | 0 |  | 1 | 25LP | 191 | 191 | 0 | 66.3 | 45.4803 | 104.9 | [7 empty] | CATEGORYB | NONSINGLE | 84224 | 0 | 0 |  | 0 |  | 0 | [5 empty] | SWPA | Broken Bow 138 kV Terminal Upgrades | Replace 1 wave trap and 3 CTs at Broken Bow 138 kV substation | [12 empty] | 102977 | 2020-03-09 | [39 empty] | 2022-04-01 | 2022-04-01
2005-AG2 | BROWN - STRAIGHT ROAD TAP 138KV CKT 1 | U | OKGE | OKGE |  |  | 0 | 515157 | BROWN 4 138 | 515944 | STRRDTP4 138.00 | 0 |  | 1 | [15 empty] | BASECASE | BASE CASE | [8 empty] | Credit Flowgate |  |  | OKGE | BROWN - STRAIGHT ROAD TAP 138KV CKT 1 | Upgrade CT at Brown. | [53 empty] | 2006-06-01 | 2006-06-01
2005-AG2 | CACHE - SNYDER 138KV CKT 1 | U | AEPW | AEPW |  |  | 0 | 511500 | CACHE4 138 | 511435 | SNYDER-4 138 | 0 |  | 1 | [15 empty] | BASECASE | BASE CASE | [8 empty] | Credit Flowgate |  |  | AEPW | CACHE - SNYDER 138KV CKT 1 | Replace Snyder wavetrap | [53 empty] | 2008-05-21 | 2008-05-21
2019-AG2 | CIMARON7 - CIMARON2 - 1 | S | OKGE | OKGE |  |  | 1 | 514901 | CIMARON7 | 514898 | CIMARON4 | 515715 |  | 1 | 30SP | 478 | 478 | 0 | 95.9 | 103 | 103 | [7 empty] | CATEGORYB | SINGLE | CIMARON4 - CIMARON7 - 1 | 1 | 514898 | CIMARON4 | 514901 | CIMARON7 | 515714 | CIMARO11 | 1 |  |  |  | OKGE | New Cimarron South 345 kV Substation and 345/138 kV transformer | Build new Cimarron South 345 kV substation located 2 miles south of existing Cimarron 345 kV substation. Reroute two 345 kV lines and four 138 kV lines coming south out of the existing substation into and out of the new substation. Install new 345/138 k | [12 empty] | 30120110 | 2020-03-10 | [39 empty] | 2026-06-01 | 2026-06-01
2019-AG2 | CLEOCOR2 - CLEOSW 2 - 1 | S | OKGE | WFEC |  |  | 0 | 514777 | CLEOCOR2 | 520855 | CLEOSW 2 | 0 |  | 1 | 20WP | 36 | 36 | 0 |  | 5.7842e-13 | 262.9 | [7 empty] | CATEGORYB | SINGLE | CLEOCOR4 - CLEOPLT4 - 1 | 0 | 514778 | CLEOCOR4 | 515562 | CLEOPLT4 | 0 |  | 1 |  |  |  | WFEC | Cleo SW 138/69 kV transformer | Add new 138/69 kV transformer at Cleo SW to connect 138 kV segment from Cleo Corner with 69 kV segments to Fairview, Eagle Chief, and Nash/Wakita. | [12 empty] | 2000000 | 2020-03-10 | [39 empty] | 2020-10-01 | 2023-06-01
2019-AG2 | CLEOCOR2 - CLEOSW 2 - 1 | S | OKGE | WFEC |  |  | 0 | 514777 | CLEOCOR2 | 520855 | CLEOSW 2 | 0 |  | 1 | 20WP | 36 | 36 | 0 |  | 5.7842e-13 | 262.9 | [7 empty] | CATEGORYB | SINGLE | CLEOCOR4 - CLEOPLT4 - 1 | 0 | 514778 | CLEOCOR4 | 515562 | CLEOPLT4 | 0 |  | 1 |  |  |  | OKGE | Cleo Corner 138 kV Terminal Upgrades | Upgrade terminal equipment at Cleo Corner 138 kV substation in order to convert Cleo Corner - Cleo SW 69 kV line to 138 kV. Includes a breaker, terminal, and reconfiguration of lines. The line is designed at 138 kV but has been operated at 69 kV, with a | [12 empty] | 1500000 | 2020-03-10 | [39 empty] | 2020-10-01 | 2021-06-01
2019-AG2 | CLEOCOR2 - CLEOSW 2 - 1 | S | OKGE | WFEC |  |  | 0 | 514777 | CLEOCOR2 | 520855 | CLEOSW 2 | 0 |  | 1 | 20WP | 36 | 36 | 0 | 66.1 | 5.7842e-13 | 262.8 | [7 empty] | CATEGORYB | NONSINGLE | 90675 | 0 | 0 |  | 0 |  | 0 | [5 empty] | WFEC | Cleo SW 138/69 kV transformer | Add new 138/69 kV transformer at Cleo SW to connect 138 kV segment from Cleo Corner with 69 kV segments to Fairview, Eagle Chief, and Nash/Wakita. | [12 empty] | 2000000 | 2020-03-10 | [39 empty] | 2020-10-01 | 2023-06-01
2019-AG2 | CLEOCOR2 - CLEOSW 2 - 1 | S | OKGE | WFEC |  |  | 0 | 514777 | CLEOCOR2 | 520855 | CLEOSW 2 | 0 |  | 1 | 20WP | 36 | 36 | 0 | 66.1 | 5.7842e-13 | 262.8 | [7 empty] | CATEGORYB | NONSINGLE | 90675 | 0 | 0 |  | 0 |  | 0 | [5 empty] | OKGE | Cleo Corner 138 kV Terminal Upgrades | Upgrade terminal equipment at Cleo Corner 138 kV substation in order to convert Cleo Corner - Cleo SW 69 kV line to 138 kV. Includes a breaker, terminal, and reconfiguration of lines. The line is designed at 138 kV but has been operated at 69 kV, with a | [12 empty] | 1500000 | 2020-03-10 | [39 empty] | 2020-10-01 | 2021-06-01
2019-AG2 | CLEOCOR2 - CLEOSW 2 - 1 | S | OKGE | WFEC |  |  | 0 | 514777 | CLEOCOR2 | 520855 | CLEOSW 2 | 0 |  | 1 | 20WP | 36 | 36 | 0 |  | 5.7842e-13 | 261.5 | [7 empty] | CATEGORYB | SINGLE | MENOTAP4 - CLEOPLT4 - 1 | 0 | 514789 | MENOTAP4 | 515562 | CLEOPLT4 | 0 |  | 1 |  |  |  | WFEC | Cleo SW 138/69 kV transformer | Add new 138/69 kV transformer at Cleo SW to connect 138 kV segment from Cleo Corner with 69 kV segments to Fairview, Eagle Chief, and Nash/Wakita. | [12 empty] | 2000000 | 2020-03-10 | [39 empty] | 2020-10-01 | 2023-06-01
2019-AG2 | CLEOCOR2 - CLEOSW 2 - 1 | S | OKGE | WFEC |  |  | 0 | 514777 | CLEOCOR2 | 520855 | CLEOSW 2 | 0 |  | 1 | 20WP | 36 | 36 | 0 |  | 5.7842e-13 | 261.5 | [7 empty] | CATEGORYB | SINGLE | MENOTAP4 - CLEOPLT4 - 1 | 0 | 514789 | MENOTAP4 | 515562 | CLEOPLT4 | 0 |  | 1 |  |  |  | OKGE | Cleo Corner 138 kV Terminal Upgrades | Upgrade terminal equipment at Cleo Corner 138 kV substation in order to convert Cleo Corner - Cleo SW 69 kV line to 138 kV. Includes a breaker, terminal, and reconfiguration of lines. The line is designed at 138 kV but has been operated at 69 kV, with a | [12 empty] | 1500000 | 2020-03-10 | [39 empty] | 2020-10-01 | 2021-06-01
2019-AG2 | CLEOCOR2 - CLEOSW 2 - 1 | S | OKGE | WFEC |  |  | 0 | 514777 | CLEOCOR2 | 520855 | CLEOSW 2 | 0 |  | 1 | 20WP | 36 | 36 | 0 |  | 5.7842e-13 | 135.3 | [7 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 | [5 empty] | WFEC | Cleo SW 138/69 kV transformer | Add new 138/69 kV transformer at Cleo SW to connect 138 kV segment from Cleo Corner with 69 kV segments to Fairview, Eagle Chief, and Nash/Wakita. | [12 empty] | 2000000 | 2020-03-10 | [39 empty] | 2020-10-01 | 2023-06-01
2019-AG2 | CLEOCOR2 - CLEOSW 2 - 1 | S | OKGE | WFEC |  |  | 0 | 514777 | CLEOCOR2 | 520855 | CLEOSW 2 | 0 |  | 1 | 20WP | 36 | 36 | 0 |  | 5.7842e-13 | 135.3 | [7 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 | [5 empty] | OKGE | Cleo Corner 138 kV Terminal Upgrades | Upgrade terminal equipment at Cleo Corner 138 kV substation in order to convert Cleo Corner - Cleo SW 69 kV line to 138 kV. Includes a breaker, terminal, and reconfiguration of lines. The line is designed at 138 kV but has been operated at 69 kV, with a | [12 empty] | 1500000 | 2020-03-10 | [39 empty] | 2020-10-01 | 2021-06-01
2019-AG2 | CLEOCOR2 - CLEOSW 2 - 1 | S | OKGE | WFEC |  |  | 0 | 514777 | CLEOCOR2 | 520855 | CLEOSW 2 | 0 |  | 1 | 21LP | 36 | 36 | 0 |  | 7.7665e-12 | 247.7 | [7 empty] | CATEGORYB | NONSINGLE | 90675 | 0 | 0 |  | 0 |  | 0 | [5 empty] | WFEC | Cleo SW 138/69 kV transformer | Add new 138/69 kV transformer at Cleo SW to connect 138 kV segment from Cleo Corner with 69 kV segments to Fairview, Eagle Chief, and Nash/Wakita. | [12 empty] | 2000000 | 2020-03-10 | [39 empty] | 2020-10-01 | 2023-06-01
2019-AG2 | CLEOCOR2 - CLEOSW 2 - 1 | S | OKGE | WFEC |  |  | 0 | 514777 | CLEOCOR2 | 520855 | CLEOSW 2 | 0 |  | 1 | 21LP | 36 | 36 | 0 |  | 7.7665e-12 | 247.7 | [7 empty] | CATEGORYB | NONSINGLE | 90675 | 0 | 0 |  | 0 |  | 0 | [5 empty] | OKGE | Cleo Corner 138 kV Terminal Upgrades | Upgrade terminal equipment at Cleo Corner 138 kV substation in order to convert Cleo Corner - Cleo SW 69 kV line to 138 kV. Includes a breaker, terminal, and reconfiguration of lines. The line is designed at 138 kV but has been operated at 69 kV, with a | [12 empty] | 1500000 | 2020-03-10 | [39 empty] | 2020-10-01 | 2021-06-01
2019-AG2 | CLEOCOR2 - CLEOSW 2 - 1 | S | OKGE | WFEC |  |  | 0 | 514777 | CLEOCOR2 | 520855 | CLEOSW 2 | 0 |  | 1 | 21LP | 36 | 36 | 0 |  | 7.7665e-12 | 246.9 | [7 empty] | CATEGORYB | SINGLE | MENOTAP4 - CLEOPLT4 - 1 | 0 | 514789 | MENOTAP4 | 515562 | CLEOPLT4 | 0 |  | 1 |  |  |  | WFEC | Cleo SW 138/69 kV transformer | Add new 138/69 kV transformer at Cleo SW to connect 138 kV segment from Cleo Corner with 69 kV segments to Fairview, Eagle Chief, and Nash/Wakita. | [12 empty] | 2000000 | 2020-03-10 | [39 empty] | 2020-10-01 | 2023-06-01
2019-AG2 | CLEOCOR2 - CLEOSW 2 - 1 | S | OKGE | WFEC |  |  | 0 | 514777 | CLEOCOR2 | 520855 | CLEOSW 2 | 0 |  | 1 | 21LP | 36 | 36 | 0 |  | 7.7665e-12 | 246.9 | [7 empty] | CATEGORYB | SINGLE | MENOTAP4 - CLEOPLT4 - 1 | 0 | 514789 | MENOTAP4 | 515562 | CLEOPLT4 | 0 |  | 1 |  |  |  | OKGE | Cleo Corner 138 kV Terminal Upgrades | Upgrade terminal equipment at Cleo Corner 138 kV substation in order to convert Cleo Corner - Cleo SW 69 kV line to 138 kV. Includes a breaker, terminal, and reconfiguration of lines. The line is designed at 138 kV but has been operated at 69 kV, with a | [12 empty] | 1500000 | 2020-03-10 | [39 empty] | 2020-10-01 | 2021-06-01
2019-AG2 | CLEOCOR2 - CLEOSW 2 - 1 | S | OKGE | WFEC |  |  | 0 | 514777 | CLEOCOR2 | 520855 | CLEOSW 2 | 0 |  | 1 | 21LP | 36 | 36 | 0 |  | 7.7665e-12 | 115.1 | [7 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 | [5 empty] | WFEC | Cleo SW 138/69 kV transformer | Add new 138/69 kV transformer at Cleo SW to connect 138 kV segment from Cleo Corner with 69 kV segments to Fairview, Eagle Chief, and Nash/Wakita. | [12 empty] | 2000000 | 2020-03-10 | [39 empty] | 2020-10-01 | 2023-06-01
2019-AG2 | CLEOCOR2 - CLEOSW 2 - 1 | S | OKGE | WFEC |  |  | 0 | 514777 | CLEOCOR2 | 520855 | CLEOSW 2 | 0 |  | 1 | 21LP | 36 | 36 | 0 |  | 7.7665e-12 | 115.1 | [7 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 | [5 empty] | OKGE | Cleo Corner 138 kV Terminal Upgrades | Upgrade terminal equipment at Cleo Corner 138 kV substation in order to convert Cleo Corner - Cleo SW 69 kV line to 138 kV. Includes a breaker, terminal, and reconfiguration of lines. The line is designed at 138 kV but has been operated at 69 kV, with a | [12 empty] | 1500000 | 2020-03-10 | [39 empty] | 2020-10-01 | 2021-06-01
2019-AG2 | CLEOCOR2 - CLEOSW 2 - 1 | S | OKGE | WFEC |  |  | 0 | 514777 | CLEOCOR2 | 520855 | CLEOSW 2 | 0 |  | 1 | 21SP | 36 | 36 | 0 |  | 7.7399e-13 | 272.3 | [7 empty] | CATEGORYB | SINGLE | CLEOCOR4 - CLEOPLT4 - 1 | 0 | 514778 | CLEOCOR4 | 515562 | CLEOPLT4 | 0 |  | 1 |  |  |  | WFEC | Cleo SW 138/69 kV transformer | Add new 138/69 kV transformer at Cleo SW to connect 138 kV segment from Cleo Corner with 69 kV segments to Fairview, Eagle Chief, and Nash/Wakita. | [12 empty] | 2000000 | 2020-03-10 | [39 empty] | 2020-10-01 | 2023-06-01
2019-AG2 | CLEOCOR2 - CLEOSW 2 - 1 | S | OKGE | WFEC |  |  | 0 | 514777 | CLEOCOR2 | 520855 | CLEOSW 2 | 0 |  | 1 | 21SP | 36 | 36 | 0 |  | 7.7399e-13 | 272.3 | [7 empty] | CATEGORYB | SINGLE | CLEOCOR4 - CLEOPLT4 - 1 | 0 | 514778 | CLEOCOR4 | 515562 | CLEOPLT4 | 0 |  | 1 |  |  |  | OKGE | Cleo Corner 138 kV Terminal Upgrades | Upgrade terminal equipment at Cleo Corner 138 kV substation in order to convert Cleo Corner - Cleo SW 69 kV line to 138 kV. Includes a breaker, terminal, and reconfiguration of lines. The line is designed at 138 kV but has been operated at 69 kV, with a | [12 empty] | 1500000 | 2020-03-10 | [39 empty] | 2020-10-01 | 2021-06-01
2019-AG2 | CLEOCOR2 - CLEOSW 2 - 1 | S | OKGE | WFEC |  |  | 0 | 514777 | CLEOCOR2 | 520855 | CLEOSW 2 | 0 |  | 1 | 21SP | 36 | 36 | 0 | 75.6 | 7.7399e-13 | 272.2 | [7 empty] | CATEGORYB | NONSINGLE | 90675 | 0 | 0 |  | 0 |  | 0 | [5 empty] | WFEC | Cleo SW 138/69 kV transformer | Add new 138/69 kV transformer at Cleo SW to connect 138 kV segment from Cleo Corner with 69 kV segments to Fairview, Eagle Chief, and Nash/Wakita. | [12 empty] | 2000000 | 2020-03-10 | [39 empty] | 2020-10-01 | 2023-06-01
2019-AG2 | CLEOCOR2 - CLEOSW 2 - 1 | S | OKGE | WFEC |  |  | 0 | 514777 | CLEOCOR2 | 520855 | CLEOSW 2 | 0 |  | 1 | 21SP | 36 | 36 | 0 | 75.6 | 7.7399e-13 | 272.2 | [7 empty] | CATEGORYB | NONSINGLE | 90675 | 0 | 0 |  | 0 |  | 0 | [5 empty] | OKGE | Cleo Corner 138 kV Terminal Upgrades | Upgrade terminal equipment at Cleo Corner 138 kV substation in order to convert Cleo Corner - Cleo SW 69 kV line to 138 kV. Includes a breaker, terminal, and reconfiguration of lines. The line is designed at 138 kV but has been operated at 69 kV, with a | [12 empty] | 1500000 | 2020-03-10 | [39 empty] | 2020-10-01 | 2021-06-01
2019-AG2 | CLEOCOR2 - CLEOSW 2 - 1 | S | OKGE | WFEC |  |  | 0 | 514777 | CLEOCOR2 | 520855 | CLEOSW 2 | 0 |  | 1 | 21SP | 36 | 36 | 0 |  | 7.7399e-13 | 270.1 | [7 empty] | CATEGORYB | SINGLE | MENOTAP4 - CLEOPLT4 - 1 | 0 | 514789 | MENOTAP4 | 515562 | CLEOPLT4 | 0 |  | 1 |  |  |  | WFEC | Cleo SW 138/69 kV transformer | Add new 138/69 kV transformer at Cleo SW to connect 138 kV segment from Cleo Corner with 69 kV segments to Fairview, Eagle Chief, and Nash/Wakita. | [12 empty] | 2000000 | 2020-03-10 | [39 empty] | 2020-10-01 | 2023-06-01
2019-AG2 | CLEOCOR2 - CLEOSW 2 - 1 | S | OKGE | WFEC |  |  | 0 | 514777 | CLEOCOR2 | 520855 | CLEOSW 2 | 0 |  | 1 | 21SP | 36 | 36 | 0 |  | 7.7399e-13 | 270.1 | [7 empty] | CATEGORYB | SINGLE | MENOTAP4 - CLEOPLT4 - 1 | 0 | 514789 | MENOTAP4 | 515562 | CLEOPLT4 | 0 |  | 1 |  |  |  | OKGE | Cleo Corner 138 kV Terminal Upgrades | Upgrade terminal equipment at Cleo Corner 138 kV substation in order to convert Cleo Corner - Cleo SW 69 kV line to 138 kV. Includes a breaker, terminal, and reconfiguration of lines. The line is designed at 138 kV but has been operated at 69 kV, with a | [12 empty] | 1500000 | 2020-03-10 | [39 empty] | 2020-10-01 | 2021-06-01
2019-AG2 | CLEOCOR2 - CLEOSW 2 - 1 | S | OKGE | WFEC |  |  | 0 | 514777 | CLEOCOR2 | 520855 | CLEOSW 2 | 0 |  | 1 | 21SP | 36 | 36 | 0 |  | 7.7399e-13 | 147.4 | [7 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 | [5 empty] | WFEC | Cleo SW 138/69 kV transformer | Add new 138/69 kV transformer at Cleo SW to connect 138 kV segment from Cleo Corner with 69 kV segments to Fairview, Eagle Chief, and Nash/Wakita. | [12 empty] | 2000000 | 2020-03-10 | [39 empty] | 2020-10-01 | 2023-06-01
2019-AG2 | CLEOCOR2 - CLEOSW 2 - 1 | S | OKGE | WFEC |  |  | 0 | 514777 | CLEOCOR2 | 520855 | CLEOSW 2 | 0 |  | 1 | 21SP | 36 | 36 | 0 |  | 7.7399e-13 | 147.4 | [7 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 | [5 empty] | OKGE | Cleo Corner 138 kV Terminal Upgrades | Upgrade terminal equipment at Cleo Corner 138 kV substation in order to convert Cleo Corner - Cleo SW 69 kV line to 138 kV. Includes a breaker, terminal, and reconfiguration of lines. The line is designed at 138 kV but has been operated at 69 kV, with a | [12 empty] | 1500000 | 2020-03-10 | [39 empty] | 2020-10-01 | 2021-06-01
2019-AG2 | CLEOCOR2 - CLEOSW 2 - 1 | S | OKGE | WFEC |  |  | 0 | 514777 | CLEOCOR2 | 520855 | CLEOSW 2 | 0 |  | 1 | 21WP | 36 | 36 | 0 |  | 5.4422e-13 | 253.5 | [7 empty] | CATEGORYB | SINGLE | CLEOCOR4 - CLEOPLT4 - 1 | 0 | 514778 | CLEOCOR4 | 515562 | CLEOPLT4 | 0 |  | 1 |  |  |  | WFEC | Cleo SW 138/69 kV transformer | Add new 138/69 kV transformer at Cleo SW to connect 138 kV segment from Cleo Corner with 69 kV segments to Fairview, Eagle Chief, and Nash/Wakita. | [12 empty] | 2000000 | 2020-03-10 | [39 empty] | 2020-10-01 | 2023-06-01
2019-AG2 | CLEOCOR2 - CLEOSW 2 - 1 | S | OKGE | WFEC |  |  | 0 | 514777 | CLEOCOR2 | 520855 | CLEOSW 2 | 0 |  | 1 | 21WP | 36 | 36 | 0 |  | 5.4422e-13 | 253.5 | [7 empty] | CATEGORYB | SINGLE | CLEOCOR4 - CLEOPLT4 - 1 | 0 | 514778 | CLEOCOR4 | 515562 | CLEOPLT4 | 0 |  | 1 |  |  |  | OKGE | Cleo Corner 138 kV Terminal Upgrades | Upgrade terminal equipment at Cleo Corner 138 kV substation in order to convert Cleo Corner - Cleo SW 69 kV line to 138 kV. Includes a breaker, terminal, and reconfiguration of lines. The line is designed at 138 kV but has been operated at 69 kV, with a | [12 empty] | 1500000 | 2020-03-10 | [39 empty] | 2020-10-01 | 2021-06-01
2019-AG2 | CLEOCOR2 - CLEOSW 2 - 1 | S | OKGE | WFEC |  |  | 0 | 514777 | CLEOCOR2 | 520855 | CLEOSW 2 | 0 |  | 1 | 21WP | 36 | 36 | 0 |  | 5.4422e-13 | 252.1 | [7 empty] | CATEGORYB | SINGLE | MENOTAP4 - CLEOPLT4 - 1 | 0 | 514789 | MENOTAP4 | 515562 | CLEOPLT4 | 0 |  | 1 |  |  |  | WFEC | Cleo SW 138/69 kV transformer | Add new 138/69 kV transformer at Cleo SW to connect 138 kV segment from Cleo Corner with 69 kV segments to Fairview, Eagle Chief, and Nash/Wakita. | [12 empty] | 2000000 | 2020-03-10 | [39 empty] | 2020-10-01 | 2023-06-01
2019-AG2 | CLEOCOR2 - CLEOSW 2 - 1 | S | OKGE | WFEC |  |  | 0 | 514777 | CLEOCOR2 | 520855 | CLEOSW 2 | 0 |  | 1 | 21WP | 36 | 36 | 0 |  | 5.4422e-13 | 252.1 | [7 empty] | CATEGORYB | SINGLE | MENOTAP4 - CLEOPLT4 - 1 | 0 | 514789 | MENOTAP4 | 515562 | CLEOPLT4 | 0 |  | 1 |  |  |  | OKGE | Cleo Corner 138 kV Terminal Upgrades | Upgrade terminal equipment at Cleo Corner 138 kV substation in order to convert Cleo Corner - Cleo SW 69 kV line to 138 kV. Includes a breaker, terminal, and reconfiguration of lines. The line is designed at 138 kV but has been operated at 69 kV, with a | [12 empty] | 1500000 | 2020-03-10 | [39 empty] | 2020-10-01 | 2021-06-01
2019-AG2 | CLEOCOR2 - CLEOSW 2 - 1 | S | OKGE | WFEC |  |  | 0 | 514777 | CLEOCOR2 | 520855 | CLEOSW 2 | 0 |  | 1 | 21WP | 36 | 36 | 0 |  | 5.4422e-13 | 132.5 | [7 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 | [5 empty] | WFEC | Cleo SW 138/69 kV transformer | Add new 138/69 kV transformer at Cleo SW to connect 138 kV segment from Cleo Corner with 69 kV segments to Fairview, Eagle Chief, and Nash/Wakita. | [12 empty] | 2000000 | 2020-03-10 | [39 empty] | 2020-10-01 | 2023-06-01
2019-AG2 | CLEOCOR2 - CLEOSW 2 - 1 | S | OKGE | WFEC |  |  | 0 | 514777 | CLEOCOR2 | 520855 | CLEOSW 2 | 0 |  | 1 | 21WP | 36 | 36 | 0 |  | 5.4422e-13 | 132.5 | [7 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 | [5 empty] | OKGE | Cleo Corner 138 kV Terminal Upgrades | Upgrade terminal equipment at Cleo Corner 138 kV substation in order to convert Cleo Corner - Cleo SW 69 kV line to 138 kV. Includes a breaker, terminal, and reconfiguration of lines. The line is designed at 138 kV but has been operated at 69 kV, with a | [12 empty] | 1500000 | 2020-03-10 | [39 empty] | 2020-10-01 | 2021-06-01
2019-AG2 | CLEOCOR2 - CLEOSW 2 - 1 | S | OKGE | WFEC |  |  | 0 | 514777 | CLEOCOR2 | 520855 | CLEOSW 2 | 0 |  | 1 | 22LP | 36 | 36 | 0 |  | 4.0934e-12 | 253.3 | [7 empty] | CATEGORYB | NONSINGLE | 90675 | 0 | 0 |  | 0 |  | 0 | [5 empty] | WFEC | Cleo SW 138/69 kV transformer | Add new 138/69 kV transformer at Cleo SW to connect 138 kV segment from Cleo Corner with 69 kV segments to Fairview, Eagle Chief, and Nash/Wakita. | [12 empty] | 2000000 | 2020-03-10 | [39 empty] | 2020-10-01 | 2023-06-01
2019-AG2 | CLEOCOR2 - CLEOSW 2 - 1 | S | OKGE | WFEC |  |  | 0 | 514777 | CLEOCOR2 | 520855 | CLEOSW 2 | 0 |  | 1 | 22LP | 36 | 36 | 0 |  | 4.0934e-12 | 253.3 | [7 empty] | CATEGORYB | NONSINGLE | 90675 | 0 | 0 |  | 0 |  | 0 | [5 empty] | OKGE | Cleo Corner 138 kV Terminal Upgrades | Upgrade terminal equipment at Cleo Corner 138 kV substation in order to convert Cleo Corner - Cleo SW 69 kV line to 138 kV. Includes a breaker, terminal, and reconfiguration of lines. The line is designed at 138 kV but has been operated at 69 kV, with a | [12 empty] | 1500000 | 2020-03-10 | [39 empty] | 2020-10-01 | 2021-06-01
2019-AG2 | CLEOCOR2 - CLEOSW 2 - 1 | S | OKGE | WFEC |  |  | 0 | 514777 | CLEOCOR2 | 520855 | CLEOSW 2 | 0 |  | 1 | 22LP | 36 | 36 | 0 |  | 4.0934e-12 | 252.6 | [7 empty] | CATEGORYB | SINGLE | MENOTAP4 - CLEOPLT4 - 1 | 0 | 514789 | MENOTAP4 | 515562 | CLEOPLT4 | 0 |  | 1 |  |  |  | WFEC | Cleo SW 138/69 kV transformer | Add new 138/69 kV transformer at Cleo SW to connect 138 kV segment from Cleo Corner with 69 kV segments to Fairview, Eagle Chief, and Nash/Wakita. | [12 empty] | 2000000 | 2020-03-10 | [39 empty] | 2020-10-01 | 2023-06-01
2019-AG2 | CLEOCOR2 - CLEOSW 2 - 1 | S | OKGE | WFEC |  |  | 0 | 514777 | CLEOCOR2 | 520855 | CLEOSW 2 | 0 |  | 1 | 22LP | 36 | 36 | 0 |  | 4.0934e-12 | 252.6 | [7 empty] | CATEGORYB | SINGLE | MENOTAP4 - CLEOPLT4 - 1 | 0 | 514789 | MENOTAP4 | 515562 | CLEOPLT4 | 0 |  | 1 |  |  |  | OKGE | Cleo Corner 138 kV Terminal Upgrades | Upgrade terminal equipment at Cleo Corner 138 kV substation in order to convert Cleo Corner - Cleo SW 69 kV line to 138 kV. Includes a breaker, terminal, and reconfiguration of lines. The line is designed at 138 kV but has been operated at 69 kV, with a | [12 empty] | 1500000 | 2020-03-10 | [39 empty] | 2020-10-01 | 2021-06-01
2019-AG2 | CLEOCOR2 - CLEOSW 2 - 1 | S | OKGE | WFEC |  |  | 0 | 514777 | CLEOCOR2 | 520855 | CLEOSW 2 | 0 |  | 1 | 22LP | 36 | 36 | 0 |  | 4.0934e-12 | 129.7 | [7 empty] | CATEGORYB | SINGLE | SO4TH 4 - IMO 4 - 1 | 0 | 514731 | SO4TH 4 | 514790 | IMO 4 | 0 |  | 1 |  |  |  | WFEC | Cleo SW 138/69 kV transformer | Add new 138/69 kV transformer at Cleo SW to connect 138 kV segment from Cleo Corner with 69 kV segments to Fairview, Eagle Chief, and Nash/Wakita. | [12 empty] | 2000000 | 2020-03-10 | [39 empty] | 2020-10-01 | 2023-06-01
2019-AG2 | CLEOCOR2 - CLEOSW 2 - 1 | S | OKGE | WFEC |  |  | 0 | 514777 | CLEOCOR2 | 520855 | CLEOSW 2 | 0 |  | 1 | 22LP | 36 | 36 | 0 |  | 4.0934e-12 | 129.7 | [7 empty] | CATEGORYB | SINGLE | SO4TH 4 - IMO 4 - 1 | 0 | 514731 | SO4TH 4 | 514790 | IMO 4 | 0 |  | 1 |  |  |  | OKGE | Cleo Corner 138 kV Terminal Upgrades | Upgrade terminal equipment at Cleo Corner 138 kV substation in order to convert Cleo Corner - Cleo SW 69 kV line to 138 kV. Includes a breaker, terminal, and reconfiguration of lines. The line is designed at 138 kV but has been operated at 69 kV, with a | [12 empty] | 1500000 | 2020-03-10 | [39 empty] | 2020-10-01 | 2021-06-01
2019-AG2 | CLEOCOR2 - CLEOSW 2 - 1 | S | OKGE | WFEC |  |  | 0 | 514777 | CLEOCOR2 | 520855 | CLEOSW 2 | 0 |  | 1 | 22LP | 36 | 36 | 0 |  | 4.0934e-12 | 116.1 | [7 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 | [5 empty] | WFEC | Cleo SW 138/69 kV transformer | Add new 138/69 kV transformer at Cleo SW to connect 138 kV segment from Cleo Corner with 69 kV segments to Fairview, Eagle Chief, and Nash/Wakita. | [12 empty] | 2000000 | 2020-03-10 | [39 empty] | 2020-10-01 | 2023-06-01
2019-AG2 | CLEOCOR2 - CLEOSW 2 - 1 | S | OKGE | WFEC |  |  | 0 | 514777 | CLEOCOR2 | 520855 | CLEOSW 2 | 0 |  | 1 | 22LP | 36 | 36 | 0 |  | 4.0934e-12 | 116.1 | [7 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 | [5 empty] | OKGE | Cleo Corner 138 kV Terminal Upgrades | Upgrade terminal equipment at Cleo Corner 138 kV substation in order to convert Cleo Corner - Cleo SW 69 kV line to 138 kV. Includes a breaker, terminal, and reconfiguration of lines. The line is designed at 138 kV but has been operated at 69 kV, with a | [12 empty] | 1500000 | 2020-03-10 | [39 empty] | 2020-10-01 | 2021-06-01
2019-AG2 | CLEOCOR2 - CLEOSW 2 - 1 | S | OKGE | WFEC |  |  | 0 | 514777 | CLEOCOR2 | 520855 | CLEOSW 2 | 0 |  | 1 | 22SP | 48 | 48 | 0 |  | 2.1396e-12 | 200.6 | [7 empty] | CATEGORYB | SINGLE | CLEOCOR4 - CLEOPLT4 - 1 | 0 | 514778 | CLEOCOR4 | 515562 | CLEOPLT4 | 0 |  | 1 |  |  |  | WFEC | Cleo SW 138/69 kV transformer | Add new 138/69 kV transformer at Cleo SW to connect 138 kV segment from Cleo Corner with 69 kV segments to Fairview, Eagle Chief, and Nash/Wakita. | [12 empty] | 2000000 | 2020-03-10 | [39 empty] | 2020-10-01 | 2023-06-01
2019-AG2 | CLEOCOR2 - CLEOSW 2 - 1 | S | OKGE | WFEC |  |  | 0 | 514777 | CLEOCOR2 | 520855 | CLEOSW 2 | 0 |  | 1 | 22SP | 48 | 48 | 0 |  | 2.1396e-12 | 200.6 | [7 empty] | CATEGORYB | SINGLE | CLEOCOR4 - CLEOPLT4 - 1 | 0 | 514778 | CLEOCOR4 | 515562 | CLEOPLT4 | 0 |  | 1 |  |  |  | OKGE | Cleo Corner 138 kV Terminal Upgrades | Upgrade terminal equipment at Cleo Corner 138 kV substation in order to convert Cleo Corner - Cleo SW 69 kV line to 138 kV. Includes a breaker, terminal, and reconfiguration of lines. The line is designed at 138 kV but has been operated at 69 kV, with a | [12 empty] | 1500000 | 2020-03-10 | [39 empty] | 2020-10-01 | 2021-06-01
2019-AG2 | CLEOCOR2 - CLEOSW 2 - 1 | S | OKGE | WFEC |  |  | 0 | 514777 | CLEOCOR2 | 520855 | CLEOSW 2 | 0 |  | 1 | 22SP | 48 | 48 | 0 |  | 2.1396e-12 | 200.5 | [7 empty] | CATEGORYB | NONSINGLE | 90675 | 0 | 0 |  | 0 |  | 0 | [5 empty] | WFEC | Cleo SW 138/69 kV transformer | Add new 138/69 kV transformer at Cleo SW to connect 138 kV segment from Cleo Corner with 69 kV segments to Fairview, Eagle Chief, and Nash/Wakita. | [12 empty] | 2000000 | 2020-03-10 | [39 empty] | 2020-10-01 | 2023-06-01
2019-AG2 | CLEOCOR2 - CLEOSW 2 - 1 | S | OKGE | WFEC |  |  | 0 | 514777 | CLEOCOR2 | 520855 | CLEOSW 2 | 0 |  | 1 | 22SP | 48 | 48 | 0 |  | 2.1396e-12 | 200.5 | [7 empty] | CATEGORYB | NONSINGLE | 90675 | 0 | 0 |  | 0 |  | 0 | [5 empty] | OKGE | Cleo Corner 138 kV Terminal Upgrades | Upgrade terminal equipment at Cleo Corner 138 kV substation in order to convert Cleo Corner - Cleo SW 69 kV line to 138 kV. Includes a breaker, terminal, and reconfiguration of lines. The line is designed at 138 kV but has been operated at 69 kV, with a | [12 empty] | 1500000 | 2020-03-10 | [39 empty] | 2020-10-01 | 2021-06-01
2019-AG2 | CLEOCOR2 - CLEOSW 2 - 1 | S | OKGE | WFEC |  |  | 0 | 514777 | CLEOCOR2 | 520855 | CLEOSW 2 | 0 |  | 1 | 22SP | 48 | 48 | 0 |  | 2.1396e-12 | 198.9 | [7 empty] | CATEGORYB | SINGLE | MENOTAP4 - CLEOPLT4 - 1 | 0 | 514789 | MENOTAP4 | 515562 | CLEOPLT4 | 0 |  | 1 |  |  |  | WFEC | Cleo SW 138/69 kV transformer | Add new 138/69 kV transformer at Cleo SW to connect 138 kV segment from Cleo Corner with 69 kV segments to Fairview, Eagle Chief, and Nash/Wakita. | [12 empty] | 2000000 | 2020-03-10 | [39 empty] | 2020-10-01 | 2023-06-01
2019-AG2 | CLEOCOR2 - CLEOSW 2 - 1 | S | OKGE | WFEC |  |  | 0 | 514777 | CLEOCOR2 | 520855 | CLEOSW 2 | 0 |  | 1 | 22SP | 48 | 48 | 0 |  | 2.1396e-12 | 198.9 | [7 empty] | CATEGORYB | SINGLE | MENOTAP4 - CLEOPLT4 - 1 | 0 | 514789 | MENOTAP4 | 515562 | CLEOPLT4 | 0 |  | 1 |  |  |  | OKGE | Cleo Corner 138 kV Terminal Upgrades | Upgrade terminal equipment at Cleo Corner 138 kV substation in order to convert Cleo Corner - Cleo SW 69 kV line to 138 kV. Includes a breaker, terminal, and reconfiguration of lines. The line is designed at 138 kV but has been operated at 69 kV, with a | [12 empty] | 1500000 | 2020-03-10 | [39 empty] | 2020-10-01 | 2021-06-01
2019-AG2 | CLEOCOR2 - CLEOSW 2 - 1 | S | OKGE | WFEC |  |  | 0 | 514777 | CLEOCOR2 | 520855 | CLEOSW 2 | 0 |  | 1 | 22SP | 48 | 48 | 0 |  | 2.1396e-12 | 107.4 | [7 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 | [5 empty] | WFEC | Cleo SW 138/69 kV transformer | Add new 138/69 kV transformer at Cleo SW to connect 138 kV segment from Cleo Corner with 69 kV segments to Fairview, Eagle Chief, and Nash/Wakita. | [12 empty] | 2000000 | 2020-03-10 | [39 empty] | 2020-10-01 | 2023-06-01
2019-AG2 | CLEOCOR2 - CLEOSW 2 - 1 | S | OKGE | WFEC |  |  | 0 | 514777 | CLEOCOR2 | 520855 | CLEOSW 2 | 0 |  | 1 | 22SP | 48 | 48 | 0 |  | 2.1396e-12 | 107.4 | [7 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 | [5 empty] | OKGE | Cleo Corner 138 kV Terminal Upgrades | Upgrade terminal equipment at Cleo Corner 138 kV substation in order to convert Cleo Corner - Cleo SW 69 kV line to 138 kV. Includes a breaker, terminal, and reconfiguration of lines. The line is designed at 138 kV but has been operated at 69 kV, with a | [12 empty] | 1500000 | 2020-03-10 | [39 empty] | 2020-10-01 | 2021-06-01
2019-AG2 | CLEOCOR2 - CLEOSW 2 - 1 | S | OKGE | WFEC |  |  | 0 | 514777 | CLEOCOR2 | 520855 | CLEOSW 2 | 0 |  | 1 | 22WP | 48 | 48 | 0 |  | 3.6114e-13 | 189.1 | [7 empty] | CATEGORYB | SINGLE | CLEOCOR4 - CLEOPLT4 - 1 | 0 | 514778 | CLEOCOR4 | 515562 | CLEOPLT4 | 0 |  | 1 |  |  |  | WFEC | Cleo SW 138/69 kV transformer | Add new 138/69 kV transformer at Cleo SW to connect 138 kV segment from Cleo Corner with 69 kV segments to Fairview, Eagle Chief, and Nash/Wakita. | [12 empty] | 2000000 | 2020-03-10 | [39 empty] | 2020-10-01 | 2023-06-01
2019-AG2 | CLEOCOR2 - CLEOSW 2 - 1 | S | OKGE | WFEC |  |  | 0 | 514777 | CLEOCOR2 | 520855 | CLEOSW 2 | 0 |  | 1 | 22WP | 48 | 48 | 0 |  | 3.6114e-13 | 189.1 | [7 empty] | CATEGORYB | SINGLE | CLEOCOR4 - CLEOPLT4 - 1 | 0 | 514778 | CLEOCOR4 | 515562 | CLEOPLT4 | 0 |  | 1 |  |  |  | OKGE | Cleo Corner 138 kV Terminal Upgrades | Upgrade terminal equipment at Cleo Corner 138 kV substation in order to convert Cleo Corner - Cleo SW 69 kV line to 138 kV. Includes a breaker, terminal, and reconfiguration of lines. The line is designed at 138 kV but has been operated at 69 kV, with a | [12 empty] | 1500000 | 2020-03-10 | [39 empty] | 2020-10-01 | 2021-06-01
2019-AG2 | CLEOCOR2 - CLEOSW 2 - 1 | S | OKGE | WFEC |  |  | 0 | 514777 | CLEOCOR2 | 520855 | CLEOSW 2 | 0 |  | 1 | 22WP | 48 | 48 | 0 |  | 3.6114e-13 | 188 | [7 empty] | CATEGORYB | SINGLE | MENOTAP4 - CLEOPLT4 - 1 | 0 | 514789 | MENOTAP4 | 515562 | CLEOPLT4 | 0 |  | 1 |  |  |  | WFEC | Cleo SW 138/69 kV transformer | Add new 138/69 kV transformer at Cleo SW to connect 138 kV segment from Cleo Corner with 69 kV segments to Fairview, Eagle Chief, and Nash/Wakita. | [12 empty] | 2000000 | 2020-03-10 | [39 empty] | 2020-10-01 | 2023-06-01
2019-AG2 | CLEOCOR2 - CLEOSW 2 - 1 | S | OKGE | WFEC |  |  | 0 | 514777 | CLEOCOR2 | 520855 | CLEOSW 2 | 0 |  | 1 | 22WP | 48 | 48 | 0 |  | 3.6114e-13 | 188 | [7 empty] | CATEGORYB | SINGLE | MENOTAP4 - CLEOPLT4 - 1 | 0 | 514789 | MENOTAP4 | 515562 | CLEOPLT4 | 0 |  | 1 |  |  |  | OKGE | Cleo Corner 138 kV Terminal Upgrades | Upgrade terminal equipment at Cleo Corner 138 kV substation in order to convert Cleo Corner - Cleo SW 69 kV line to 138 kV. Includes a breaker, terminal, and reconfiguration of lines. The line is designed at 138 kV but has been operated at 69 kV, with a | [12 empty] | 1500000 | 2020-03-10 | [39 empty] | 2020-10-01 | 2021-06-01
2019-AG2 | CLEOCOR2 - CLEOSW 2 - 1 | S | OKGE | WFEC |  |  | 0 | 514777 | CLEOCOR2 | 520855 | CLEOSW 2 | 0 |  | 1 | 25LP | 48 | 48 | 0 |  | 1.7831e-11 | 181.1 | [7 empty] | CATEGORYB | SINGLE | CLEOCOR4 - CLEOPLT4 - 1 | 0 | 514778 | CLEOCOR4 | 515562 | CLEOPLT4 | 0 |  | 1 |  |  |  | WFEC | Cleo SW 138/69 kV transformer | Add new 138/69 kV transformer at Cleo SW to connect 138 kV segment from Cleo Corner with 69 kV segments to Fairview, Eagle Chief, and Nash/Wakita. | [12 empty] | 2000000 | 2020-03-10 | [39 empty] | 2020-10-01 | 2023-06-01
2019-AG2 | CLEOCOR2 - CLEOSW 2 - 1 | S | OKGE | WFEC |  |  | 0 | 514777 | CLEOCOR2 | 520855 | CLEOSW 2 | 0 |  | 1 | 25LP | 48 | 48 | 0 |  | 1.7831e-11 | 181.1 | [7 empty] | CATEGORYB | SINGLE | CLEOCOR4 - CLEOPLT4 - 1 | 0 | 514778 | CLEOCOR4 | 515562 | CLEOPLT4 | 0 |  | 1 |  |  |  | OKGE | Cleo Corner 138 kV Terminal Upgrades | Upgrade terminal equipment at Cleo Corner 138 kV substation in order to convert Cleo Corner - Cleo SW 69 kV line to 138 kV. Includes a breaker, terminal, and reconfiguration of lines. The line is designed at 138 kV but has been operated at 69 kV, with a | [12 empty] | 1500000 | 2020-03-10 | [39 empty] | 2020-10-01 | 2021-06-01
2019-AG2 | CLEOCOR2 - CLEOSW 2 - 1 | S | OKGE | WFEC |  |  | 0 | 514777 | CLEOCOR2 | 520855 | CLEOSW 2 | 0 |  | 1 | 25LP | 48 | 48 | 0 |  | 1.7831e-11 | 180.6 | [7 empty] | CATEGORYB | SINGLE | MENOTAP4 - CLEOPLT4 - 1 | 0 | 514789 | MENOTAP4 | 515562 | CLEOPLT4 | 0 |  | 1 |  |  |  | WFEC | Cleo SW 138/69 kV transformer | Add new 138/69 kV transformer at Cleo SW to connect 138 kV segment from Cleo Corner with 69 kV segments to Fairview, Eagle Chief, and Nash/Wakita. | [12 empty] | 2000000 | 2020-03-10 | [39 empty] | 2020-10-01 | 2023-06-01
2019-AG2 | CLEOCOR2 - CLEOSW 2 - 1 | S | OKGE | WFEC |  |  | 0 | 514777 | CLEOCOR2 | 520855 | CLEOSW 2 | 0 |  | 1 | 25LP | 48 | 48 | 0 |  | 1.7831e-11 | 180.6 | [7 empty] | CATEGORYB | SINGLE | MENOTAP4 - CLEOPLT4 - 1 | 0 | 514789 | MENOTAP4 | 515562 | CLEOPLT4 | 0 |  | 1 |  |  |  | OKGE | Cleo Corner 138 kV Terminal Upgrades | Upgrade terminal equipment at Cleo Corner 138 kV substation in order to convert Cleo Corner - Cleo SW 69 kV line to 138 kV. Includes a breaker, terminal, and reconfiguration of lines. The line is designed at 138 kV but has been operated at 69 kV, with a | [12 empty] | 1500000 | 2020-03-10 | [39 empty] | 2020-10-01 | 2021-06-01
2019-AG2 | CLEOCOR2 - CLEOSW 2 - 1 | S | OKGE | WFEC |  |  | 0 | 514777 | CLEOCOR2 | 520855 | CLEOSW 2 | 0 |  | 1 | 25SP | 48 | 48 | 0 |  | 4.5636e-13 | 200.6 | [7 empty] | CATEGORYB | SINGLE | CLEOCOR4 - CLEOPLT4 - 1 | 0 | 514778 | CLEOCOR4 | 515562 | CLEOPLT4 | 0 |  | 1 |  |  |  | WFEC | Cleo SW 138/69 kV transformer | Add new 138/69 kV transformer at Cleo SW to connect 138 kV segment from Cleo Corner with 69 kV segments to Fairview, Eagle Chief, and Nash/Wakita. | [12 empty] | 2000000 | 2020-03-10 | [39 empty] | 2020-10-01 | 2023-06-01
2019-AG2 | CLEOCOR2 - CLEOSW 2 - 1 | S | OKGE | WFEC |  |  | 0 | 514777 | CLEOCOR2 | 520855 | CLEOSW 2 | 0 |  | 1 | 25SP | 48 | 48 | 0 |  | 4.5636e-13 | 200.6 | [7 empty] | CATEGORYB | SINGLE | CLEOCOR4 - CLEOPLT4 - 1 | 0 | 514778 | CLEOCOR4 | 515562 | CLEOPLT4 | 0 |  | 1 |  |  |  | OKGE | Cleo Corner 138 kV Terminal Upgrades | Upgrade terminal equipment at Cleo Corner 138 kV substation in order to convert Cleo Corner - Cleo SW 69 kV line to 138 kV. Includes a breaker, terminal, and reconfiguration of lines. The line is designed at 138 kV but has been operated at 69 kV, with a | [12 empty] | 1500000 | 2020-03-10 | [39 empty] | 2020-10-01 | 2021-06-01
2019-AG2 | CLEOCOR2 - CLEOSW 2 - 1 | S | OKGE | WFEC |  |  | 0 | 514777 | CLEOCOR2 | 520855 | CLEOSW 2 | 0 |  | 1 | 25SP | 48 | 48 | 0 |  | 4.5636e-13 | 199 | [7 empty] | CATEGORYB | SINGLE | MENOTAP4 - CLEOPLT4 - 1 | 0 | 514789 | MENOTAP4 | 515562 | CLEOPLT4 | 0 |  | 1 |  |  |  | WFEC | Cleo SW 138/69 kV transformer | Add new 138/69 kV transformer at Cleo SW to connect 138 kV segment from Cleo Corner with 69 kV segments to Fairview, Eagle Chief, and Nash/Wakita. | [12 empty] | 2000000 | 2020-03-10 | [39 empty] | 2020-10-01 | 2023-06-01
2019-AG2 | CLEOCOR2 - CLEOSW 2 - 1 | S | OKGE | WFEC |  |  | 0 | 514777 | CLEOCOR2 | 520855 | CLEOSW 2 | 0 |  | 1 | 25SP | 48 | 48 | 0 |  | 4.5636e-13 | 199 | [7 empty] | CATEGORYB | SINGLE | MENOTAP4 - CLEOPLT4 - 1 | 0 | 514789 | MENOTAP4 | 515562 | CLEOPLT4 | 0 |  | 1 |  |  |  | OKGE | Cleo Corner 138 kV Terminal Upgrades | Upgrade terminal equipment at Cleo Corner 138 kV substation in order to convert Cleo Corner - Cleo SW 69 kV line to 138 kV. Includes a breaker, terminal, and reconfiguration of lines. The line is designed at 138 kV but has been operated at 69 kV, with a | [12 empty] | 1500000 | 2020-03-10 | [39 empty] | 2020-10-01 | 2021-06-01
2019-AG2 | CLEOCOR2 - CLEOSW 2 - 1 | S | OKGE | WFEC |  |  | 0 | 514777 | CLEOCOR2 | 520855 | CLEOSW 2 | 0 |  | 1 | 25SP | 48 | 48 | 0 |  | 4.5636e-13 | 107.6 | [7 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 | [5 empty] | WFEC | Cleo SW 138/69 kV transformer | Add new 138/69 kV transformer at Cleo SW to connect 138 kV segment from Cleo Corner with 69 kV segments to Fairview, Eagle Chief, and Nash/Wakita. | [12 empty] | 2000000 | 2020-03-10 | [39 empty] | 2020-10-01 | 2023-06-01
2019-AG2 | CLEOCOR2 - CLEOSW 2 - 1 | S | OKGE | WFEC |  |  | 0 | 514777 | CLEOCOR2 | 520855 | CLEOSW 2 | 0 |  | 1 | 25SP | 48 | 48 | 0 |  | 4.5636e-13 | 107.6 | [7 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 | [5 empty] | OKGE | Cleo Corner 138 kV Terminal Upgrades | Upgrade terminal equipment at Cleo Corner 138 kV substation in order to convert Cleo Corner - Cleo SW 69 kV line to 138 kV. Includes a breaker, terminal, and reconfiguration of lines. The line is designed at 138 kV but has been operated at 69 kV, with a | [12 empty] | 1500000 | 2020-03-10 | [39 empty] | 2020-10-01 | 2021-06-01
2019-AG2 | CLEOCOR2 - CLEOSW 2 - 1 | S | OKGE | WFEC |  |  | 0 | 514777 | CLEOCOR2 | 520855 | CLEOSW 2 | 0 |  | 1 | 25WP | 48 | 48 | 0 |  | 4.3352e-13 | 184.5 | [7 empty] | CATEGORYB | NONSINGLE | 90675 | 0 | 0 |  | 0 |  | 0 | [5 empty] | WFEC | Cleo SW 138/69 kV transformer | Add new 138/69 kV transformer at Cleo SW to connect 138 kV segment from Cleo Corner with 69 kV segments to Fairview, Eagle Chief, and Nash/Wakita. | [12 empty] | 2000000 | 2020-03-10 | [39 empty] | 2020-10-01 | 2023-06-01
2019-AG2 | CLEOCOR2 - CLEOSW 2 - 1 | S | OKGE | WFEC |  |  | 0 | 514777 | CLEOCOR2 | 520855 | CLEOSW 2 | 0 |  | 1 | 25WP | 48 | 48 | 0 |  | 4.3352e-13 | 184.5 | [7 empty] | CATEGORYB | NONSINGLE | 90675 | 0 | 0 |  | 0 |  | 0 | [5 empty] | OKGE | Cleo Corner 138 kV Terminal Upgrades | Upgrade terminal equipment at Cleo Corner 138 kV substation in order to convert Cleo Corner - Cleo SW 69 kV line to 138 kV. Includes a breaker, terminal, and reconfiguration of lines. The line is designed at 138 kV but has been operated at 69 kV, with a | [12 empty] | 1500000 | 2020-03-10 | [39 empty] | 2020-10-01 | 2021-06-01
2019-AG2 | CLEOCOR2 - CLEOSW 2 - 1 | S | OKGE | WFEC |  |  | 0 | 514777 | CLEOCOR2 | 520855 | CLEOSW 2 | 0 |  | 1 | 25WP | 48 | 48 | 0 |  | 4.3352e-13 | 183.5 | [7 empty] | CATEGORYB | SINGLE | MENOTAP4 - CLEOPLT4 - 1 | 0 | 514789 | MENOTAP4 | 515562 | CLEOPLT4 | 0 |  | 1 |  |  |  | WFEC | Cleo SW 138/69 kV transformer | Add new 138/69 kV transformer at Cleo SW to connect 138 kV segment from Cleo Corner with 69 kV segments to Fairview, Eagle Chief, and Nash/Wakita. | [12 empty] | 2000000 | 2020-03-10 | [39 empty] | 2020-10-01 | 2023-06-01
2019-AG2 | CLEOCOR2 - CLEOSW 2 - 1 | S | OKGE | WFEC |  |  | 0 | 514777 | CLEOCOR2 | 520855 | CLEOSW 2 | 0 |  | 1 | 25WP | 48 | 48 | 0 |  | 4.3352e-13 | 183.5 | [7 empty] | CATEGORYB | SINGLE | MENOTAP4 - CLEOPLT4 - 1 | 0 | 514789 | MENOTAP4 | 515562 | CLEOPLT4 | 0 |  | 1 |  |  |  | OKGE | Cleo Corner 138 kV Terminal Upgrades | Upgrade terminal equipment at Cleo Corner 138 kV substation in order to convert Cleo Corner - Cleo SW 69 kV line to 138 kV. Includes a breaker, terminal, and reconfiguration of lines. The line is designed at 138 kV but has been operated at 69 kV, with a | [12 empty] | 1500000 | 2020-03-10 | [39 empty] | 2020-10-01 | 2021-06-01
2019-AG2 | CLEOCOR2 - CLEOSW 2 - 1 | S | OKGE | WFEC |  |  | 0 | 514777 | CLEOCOR2 | 520855 | CLEOSW 2 | 0 |  | 1 | 30LP | 48 | 48 | 0 |  | 1.6111e-11 | 178.4 | [7 empty] | CATEGORYB | SINGLE | CLEOCOR4 - CLEOPLT4 - 1 | 0 | 514778 | CLEOCOR4 | 515562 | CLEOPLT4 | 0 |  | 1 |  |  |  | WFEC | Cleo SW 138/69 kV transformer | Add new 138/69 kV transformer at Cleo SW to connect 138 kV segment from Cleo Corner with 69 kV segments to Fairview, Eagle Chief, and Nash/Wakita. | [12 empty] | 2000000 | 2020-03-10 | [39 empty] | 2020-10-01 | 2023-06-01
2019-AG2 | CLEOCOR2 - CLEOSW 2 - 1 | S | OKGE | WFEC |  |  | 0 | 514777 | CLEOCOR2 | 520855 | CLEOSW 2 | 0 |  | 1 | 30LP | 48 | 48 | 0 |  | 1.6111e-11 | 178.4 | [7 empty] | CATEGORYB | SINGLE | CLEOCOR4 - CLEOPLT4 - 1 | 0 | 514778 | CLEOCOR4 | 515562 | CLEOPLT4 | 0 |  | 1 |  |  |  | OKGE | Cleo Corner 138 kV Terminal Upgrades | Upgrade terminal equipment at Cleo Corner 138 kV substation in order to convert Cleo Corner - Cleo SW 69 kV line to 138 kV. Includes a breaker, terminal, and reconfiguration of lines. The line is designed at 138 kV but has been operated at 69 kV, with a | [12 empty] | 1500000 | 2020-03-10 | [39 empty] | 2020-10-01 | 2021-06-01
2019-AG2 | CLEOCOR2 - CLEOSW 2 - 1 | S | OKGE | WFEC |  |  | 0 | 514777 | CLEOCOR2 | 520855 | CLEOSW 2 | 0 |  | 1 | 30LP | 48 | 48 | 0 |  | 1.6111e-11 | 177.9 | [7 empty] | CATEGORYB | SINGLE | MENOTAP4 - CLEOPLT4 - 1 | 0 | 514789 | MENOTAP4 | 515562 | CLEOPLT4 | 0 |  | 1 |  |  |  | WFEC | Cleo SW 138/69 kV transformer | Add new 138/69 kV transformer at Cleo SW to connect 138 kV segment from Cleo Corner with 69 kV segments to Fairview, Eagle Chief, and Nash/Wakita. | [12 empty] | 2000000 | 2020-03-10 | [39 empty] | 2020-10-01 | 2023-06-01
2019-AG2 | CLEOCOR2 - CLEOSW 2 - 1 | S | OKGE | WFEC |  |  | 0 | 514777 | CLEOCOR2 | 520855 | CLEOSW 2 | 0 |  | 1 | 30LP | 48 | 48 | 0 |  | 1.6111e-11 | 177.9 | [7 empty] | CATEGORYB | SINGLE | MENOTAP4 - CLEOPLT4 - 1 | 0 | 514789 | MENOTAP4 | 515562 | CLEOPLT4 | 0 |  | 1 |  |  |  | OKGE | Cleo Corner 138 kV Terminal Upgrades | Upgrade terminal equipment at Cleo Corner 138 kV substation in order to convert Cleo Corner - Cleo SW 69 kV line to 138 kV. Includes a breaker, terminal, and reconfiguration of lines. The line is designed at 138 kV but has been operated at 69 kV, with a | [12 empty] | 1500000 | 2020-03-10 | [39 empty] | 2020-10-01 | 2021-06-01
2019-AG2 | CLEOCOR2 - CLEOSW 2 - 1 | S | OKGE | WFEC |  |  | 0 | 514777 | CLEOCOR2 | 520855 | CLEOSW 2 | 0 |  | 1 | 30SP | 48 | 48 | 0 |  | 2.5487e-13 | 201.7 | [7 empty] | CATEGORYB | SINGLE | CLEOCOR4 - CLEOPLT4 - 1 | 0 | 514778 | CLEOCOR4 | 515562 | CLEOPLT4 | 0 |  | 1 |  |  |  | WFEC | Cleo SW 138/69 kV transformer | Add new 138/69 kV transformer at Cleo SW to connect 138 kV segment from Cleo Corner with 69 kV segments to Fairview, Eagle Chief, and Nash/Wakita. | [12 empty] | 2000000 | 2020-03-10 | [39 empty] | 2020-10-01 | 2023-06-01
2019-AG2 | CLEOCOR2 - CLEOSW 2 - 1 | S | OKGE | WFEC |  |  | 0 | 514777 | CLEOCOR2 | 520855 | CLEOSW 2 | 0 |  | 1 | 30SP | 48 | 48 | 0 |  | 2.5487e-13 | 201.7 | [7 empty] | CATEGORYB | SINGLE | CLEOCOR4 - CLEOPLT4 - 1 | 0 | 514778 | CLEOCOR4 | 515562 | CLEOPLT4 | 0 |  | 1 |  |  |  | OKGE | Cleo Corner 138 kV Terminal Upgrades | Upgrade terminal equipment at Cleo Corner 138 kV substation in order to convert Cleo Corner - Cleo SW 69 kV line to 138 kV. Includes a breaker, terminal, and reconfiguration of lines. The line is designed at 138 kV but has been operated at 69 kV, with a | [12 empty] | 1500000 | 2020-03-10 | [39 empty] | 2020-10-01 | 2021-06-01
2019-AG2 | CLEOCOR2 - CLEOSW 2 - 1 | S | OKGE | WFEC |  |  | 0 | 514777 | CLEOCOR2 | 520855 | CLEOSW 2 | 0 |  | 1 | 30SP | 48 | 48 | 0 |  | 2.5487e-13 | 201.6 | [7 empty] | CATEGORYB | NONSINGLE | 90675 | 0 | 0 |  | 0 |  | 0 | [5 empty] | WFEC | Cleo SW 138/69 kV transformer | Add new 138/69 kV transformer at Cleo SW to connect 138 kV segment from Cleo Corner with 69 kV segments to Fairview, Eagle Chief, and Nash/Wakita. | [12 empty] | 2000000 | 2020-03-10 | [39 empty] | 2020-10-01 | 2023-06-01
2019-AG2 | CLEOCOR2 - CLEOSW 2 - 1 | S | OKGE | WFEC |  |  | 0 | 514777 | CLEOCOR2 | 520855 | CLEOSW 2 | 0 |  | 1 | 30SP | 48 | 48 | 0 |  | 2.5487e-13 | 201.6 | [7 empty] | CATEGORYB | NONSINGLE | 90675 | 0 | 0 |  | 0 |  | 0 | [5 empty] | OKGE | Cleo Corner 138 kV Terminal Upgrades | Upgrade terminal equipment at Cleo Corner 138 kV substation in order to convert Cleo Corner - Cleo SW 69 kV line to 138 kV. Includes a breaker, terminal, and reconfiguration of lines. The line is designed at 138 kV but has been operated at 69 kV, with a | [12 empty] | 1500000 | 2020-03-10 | [39 empty] | 2020-10-01 | 2021-06-01
2019-AG2 | CLEOCOR2 - CLEOSW 2 - 1 | S | OKGE | WFEC |  |  | 0 | 514777 | CLEOCOR2 | 520855 | CLEOSW 2 | 0 |  | 1 | 30SP | 48 | 48 | 0 |  | 2.5487e-13 | 200 | [7 empty] | CATEGORYB | SINGLE | MENOTAP4 - CLEOPLT4 - 1 | 0 | 514789 | MENOTAP4 | 515562 | CLEOPLT4 | 0 |  | 1 |  |  |  | WFEC | Cleo SW 138/69 kV transformer | Add new 138/69 kV transformer at Cleo SW to connect 138 kV segment from Cleo Corner with 69 kV segments to Fairview, Eagle Chief, and Nash/Wakita. | [12 empty] | 2000000 | 2020-03-10 | [39 empty] | 2020-10-01 | 2023-06-01
2019-AG2 | CLEOCOR2 - CLEOSW 2 - 1 | S | OKGE | WFEC |  |  | 0 | 514777 | CLEOCOR2 | 520855 | CLEOSW 2 | 0 |  | 1 | 30SP | 48 | 48 | 0 |  | 2.5487e-13 | 200 | [7 empty] | CATEGORYB | SINGLE | MENOTAP4 - CLEOPLT4 - 1 | 0 | 514789 | MENOTAP4 | 515562 | CLEOPLT4 | 0 |  | 1 |  |  |  | OKGE | Cleo Corner 138 kV Terminal Upgrades | Upgrade terminal equipment at Cleo Corner 138 kV substation in order to convert Cleo Corner - Cleo SW 69 kV line to 138 kV. Includes a breaker, terminal, and reconfiguration of lines. The line is designed at 138 kV but has been operated at 69 kV, with a | [12 empty] | 1500000 | 2020-03-10 | [39 empty] | 2020-10-01 | 2021-06-01
2019-AG2 | CLEOCOR2 - CLEOSW 2 - 1 | S | OKGE | WFEC |  |  | 0 | 514777 | CLEOCOR2 | 520855 | CLEOSW 2 | 0 |  | 1 | 30SP | 48 | 48 | 0 |  | 2.5487e-13 | 105.3 | [7 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 | [5 empty] | WFEC | Cleo SW 138/69 kV transformer | Add new 138/69 kV transformer at Cleo SW to connect 138 kV segment from Cleo Corner with 69 kV segments to Fairview, Eagle Chief, and Nash/Wakita. | [12 empty] | 2000000 | 2020-03-10 | [39 empty] | 2020-10-01 | 2023-06-01
2019-AG2 | CLEOCOR2 - CLEOSW 2 - 1 | S | OKGE | WFEC |  |  | 0 | 514777 | CLEOCOR2 | 520855 | CLEOSW 2 | 0 |  | 1 | 30SP | 48 | 48 | 0 |  | 2.5487e-13 | 105.3 | [7 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 | [5 empty] | OKGE | Cleo Corner 138 kV Terminal Upgrades | Upgrade terminal equipment at Cleo Corner 138 kV substation in order to convert Cleo Corner - Cleo SW 69 kV line to 138 kV. Includes a breaker, terminal, and reconfiguration of lines. The line is designed at 138 kV but has been operated at 69 kV, with a | [12 empty] | 1500000 | 2020-03-10 | [39 empty] | 2020-10-01 | 2021-06-01
2019-AG2 | CLEOCOR2 - CLEOSW 2 - 1 | S | OKGE | WFEC |  |  | 0 | 514777 | CLEOCOR2 | 520855 | CLEOSW 2 | 0 |  | 1 | 30WP | 48 | 48 | 0 |  | 3.2448e-12 | 189.2 | [7 empty] | CATEGORYB | SINGLE | CLEOCOR4 - CLEOPLT4 - 1 | 0 | 514778 | CLEOCOR4 | 515562 | CLEOPLT4 | 0 |  | 1 |  |  |  | WFEC | Cleo SW 138/69 kV transformer | Add new 138/69 kV transformer at Cleo SW to connect 138 kV segment from Cleo Corner with 69 kV segments to Fairview, Eagle Chief, and Nash/Wakita. | [12 empty] | 2000000 | 2020-03-10 | [39 empty] | 2020-10-01 | 2023-06-01
2019-AG2 | CLEOCOR2 - CLEOSW 2 - 1 | S | OKGE | WFEC |  |  | 0 | 514777 | CLEOCOR2 | 520855 | CLEOSW 2 | 0 |  | 1 | 30WP | 48 | 48 | 0 |  | 3.2448e-12 | 189.2 | [7 empty] | CATEGORYB | SINGLE | CLEOCOR4 - CLEOPLT4 - 1 | 0 | 514778 | CLEOCOR4 | 515562 | CLEOPLT4 | 0 |  | 1 |  |  |  | OKGE | Cleo Corner 138 kV Terminal Upgrades | Upgrade terminal equipment at Cleo Corner 138 kV substation in order to convert Cleo Corner - Cleo SW 69 kV line to 138 kV. Includes a breaker, terminal, and reconfiguration of lines. The line is designed at 138 kV but has been operated at 69 kV, with a | [12 empty] | 1500000 | 2020-03-10 | [39 empty] | 2020-10-01 | 2021-06-01
2019-AG2 | CLEOCOR2 - CLEOSW 2 - 1 | S | OKGE | WFEC |  |  | 0 | 514777 | CLEOCOR2 | 520855 | CLEOSW 2 | 0 |  | 1 | 30WP | 48 | 48 | 0 |  | 3.2448e-12 | 189.1 | [7 empty] | CATEGORYB | NONSINGLE | 90675 | 0 | 0 |  | 0 |  | 0 | [5 empty] | WFEC | Cleo SW 138/69 kV transformer | Add new 138/69 kV transformer at Cleo SW to connect 138 kV segment from Cleo Corner with 69 kV segments to Fairview, Eagle Chief, and Nash/Wakita. | [12 empty] | 2000000 | 2020-03-10 | [39 empty] | 2020-10-01 | 2023-06-01
2019-AG2 | CLEOCOR2 - CLEOSW 2 - 1 | S | OKGE | WFEC |  |  | 0 | 514777 | CLEOCOR2 | 520855 | CLEOSW 2 | 0 |  | 1 | 30WP | 48 | 48 | 0 |  | 3.2448e-12 | 189.1 | [7 empty] | CATEGORYB | NONSINGLE | 90675 | 0 | 0 |  | 0 |  | 0 | [5 empty] | OKGE | Cleo Corner 138 kV Terminal Upgrades | Upgrade terminal equipment at Cleo Corner 138 kV substation in order to convert Cleo Corner - Cleo SW 69 kV line to 138 kV. Includes a breaker, terminal, and reconfiguration of lines. The line is designed at 138 kV but has been operated at 69 kV, with a | [12 empty] | 1500000 | 2020-03-10 | [39 empty] | 2020-10-01 | 2021-06-01
2019-AG2 | CLEOCOR2 - CLEOSW 2 - 1 | S | OKGE | WFEC |  |  | 0 | 514777 | CLEOCOR2 | 520855 | CLEOSW 2 | 0 |  | 1 | 30WP | 48 | 48 | 0 |  | 3.2448e-12 | 188.1 | [7 empty] | CATEGORYB | SINGLE | MENOTAP4 - CLEOPLT4 - 1 | 0 | 514789 | MENOTAP4 | 515562 | CLEOPLT4 | 0 |  | 1 |  |  |  | WFEC | Cleo SW 138/69 kV transformer | Add new 138/69 kV transformer at Cleo SW to connect 138 kV segment from Cleo Corner with 69 kV segments to Fairview, Eagle Chief, and Nash/Wakita. | [12 empty] | 2000000 | 2020-03-10 | [39 empty] | 2020-10-01 | 2023-06-01
2019-AG2 | CLEOCOR2 - CLEOSW 2 - 1 | S | OKGE | WFEC |  |  | 0 | 514777 | CLEOCOR2 | 520855 | CLEOSW 2 | 0 |  | 1 | 30WP | 48 | 48 | 0 |  | 3.2448e-12 | 188.1 | [7 empty] | CATEGORYB | SINGLE | MENOTAP4 - CLEOPLT4 - 1 | 0 | 514789 | MENOTAP4 | 515562 | CLEOPLT4 | 0 |  | 1 |  |  |  | OKGE | Cleo Corner 138 kV Terminal Upgrades | Upgrade terminal equipment at Cleo Corner 138 kV substation in order to convert Cleo Corner - Cleo SW 69 kV line to 138 kV. Includes a breaker, terminal, and reconfiguration of lines. The line is designed at 138 kV but has been operated at 69 kV, with a | [12 empty] | 1500000 | 2020-03-10 | [39 empty] | 2020-10-01 | 2021-06-01
2019-AG2 | CLEOSW 2 - RNGWODJ2 - 1 | S | WFEC | WFEC |  |  | 0 | 520855 | CLEOSW 2 | 521039 | RNGWODJ2 | 0 |  | 1 | 21LP | 58 | 68 | 0 |  | 17.3153 | 100.4 | [7 empty] | CATEGORYB | NONSINGLE | 90675 | 0 | 0 |  | 0 |  | 0 | [5 empty] | WFEC | Cleo SW 138/69 kV transformer | Add new 138/69 kV transformer at Cleo SW to connect 138 kV segment from Cleo Corner with 69 kV segments to Fairview, Eagle Chief, and Nash/Wakita. | [12 empty] | 2000000 | 2020-03-10 | [39 empty] | 2020-10-01 | 2023-06-01
2019-AG2 | CLEOSW 2 - RNGWODJ2 - 1 | S | WFEC | WFEC |  |  | 0 | 520855 | CLEOSW 2 | 521039 | RNGWODJ2 | 0 |  | 1 | 21LP | 58 | 68 | 0 |  | 17.3153 | 100.4 | [7 empty] | CATEGORYB | NONSINGLE | 90675 | 0 | 0 |  | 0 |  | 0 | [5 empty] | OKGE | Cleo Corner 138 kV Terminal Upgrades | Upgrade terminal equipment at Cleo Corner 138 kV substation in order to convert Cleo Corner - Cleo SW 69 kV line to 138 kV. Includes a breaker, terminal, and reconfiguration of lines. The line is designed at 138 kV but has been operated at 69 kV, with a | [12 empty] | 1500000 | 2020-03-10 | [39 empty] | 2020-10-01 | 2021-06-01
2019-AG2 | CLEOSW 2 - RNGWODJ2 - 1 | S | WFEC | WFEC |  |  | 0 | 520855 | CLEOSW 2 | 521039 | RNGWODJ2 | 0 |  | 1 | 21LP | 58 | 68 | 0 |  | 17.3153 | 100.1 | [7 empty] | CATEGORYB | SINGLE | MENOTAP4 - CLEOPLT4 - 1 | 0 | 514789 | MENOTAP4 | 515562 | CLEOPLT4 | 0 |  | 1 |  |  |  | WFEC | Cleo SW 138/69 kV transformer | Add new 138/69 kV transformer at Cleo SW to connect 138 kV segment from Cleo Corner with 69 kV segments to Fairview, Eagle Chief, and Nash/Wakita. | [12 empty] | 2000000 | 2020-03-10 | [39 empty] | 2020-10-01 | 2023-06-01
2019-AG2 | CLEOSW 2 - RNGWODJ2 - 1 | S | WFEC | WFEC |  |  | 0 | 520855 | CLEOSW 2 | 521039 | RNGWODJ2 | 0 |  | 1 | 21LP | 58 | 68 | 0 |  | 17.3153 | 100.1 | [7 empty] | CATEGORYB | SINGLE | MENOTAP4 - CLEOPLT4 - 1 | 0 | 514789 | MENOTAP4 | 515562 | CLEOPLT4 | 0 |  | 1 |  |  |  | OKGE | Cleo Corner 138 kV Terminal Upgrades | Upgrade terminal equipment at Cleo Corner 138 kV substation in order to convert Cleo Corner - Cleo SW 69 kV line to 138 kV. Includes a breaker, terminal, and reconfiguration of lines. The line is designed at 138 kV but has been operated at 69 kV, with a | [12 empty] | 1500000 | 2020-03-10 | [39 empty] | 2020-10-01 | 2021-06-01
2019-AG2 | CLEOSW 2 - RNGWODJ2 - 1 | S | WFEC | WFEC |  |  | 0 | 520855 | CLEOSW 2 | 521039 | RNGWODJ2 | 0 |  | 1 | 21SP | 58 | 68 | 0 |  | 30.4666 | 110.1 | [7 empty] | CATEGORYB | SINGLE | CLEOCOR4 - CLEOPLT4 - 1 | 0 | 514778 | CLEOCOR4 | 515562 | CLEOPLT4 | 0 |  | 1 |  |  |  | WFEC | Cleo SW 138/69 kV transformer | Add new 138/69 kV transformer at Cleo SW to connect 138 kV segment from Cleo Corner with 69 kV segments to Fairview, Eagle Chief, and Nash/Wakita. | [12 empty] | 2000000 | 2020-03-10 | [39 empty] | 2020-10-01 | 2023-06-01
2019-AG2 | CLEOSW 2 - RNGWODJ2 - 1 | S | WFEC | WFEC |  |  | 0 | 520855 | CLEOSW 2 | 521039 | RNGWODJ2 | 0 |  | 1 | 21SP | 58 | 68 | 0 |  | 30.4666 | 110.1 | [7 empty] | CATEGORYB | SINGLE | CLEOCOR4 - CLEOPLT4 - 1 | 0 | 514778 | CLEOCOR4 | 515562 | CLEOPLT4 | 0 |  | 1 |  |  |  | OKGE | Cleo Corner 138 kV Terminal Upgrades | Upgrade terminal equipment at Cleo Corner 138 kV substation in order to convert Cleo Corner - Cleo SW 69 kV line to 138 kV. Includes a breaker, terminal, and reconfiguration of lines. The line is designed at 138 kV but has been operated at 69 kV, with a | [12 empty] | 1500000 | 2020-03-10 | [39 empty] | 2020-10-01 | 2021-06-01
2019-AG2 | CLEOSW 2 - RNGWODJ2 - 1 | S | WFEC | WFEC |  |  | 0 | 520855 | CLEOSW 2 | 521039 | RNGWODJ2 | 0 |  | 1 | 21SP | 58 | 68 | 0 |  | 30.4666 | 110 | [7 empty] | CATEGORYB | NONSINGLE | 90675 | 0 | 0 |  | 0 |  | 0 | [5 empty] | WFEC | Cleo SW 138/69 kV transformer | Add new 138/69 kV transformer at Cleo SW to connect 138 kV segment from Cleo Corner with 69 kV segments to Fairview, Eagle Chief, and Nash/Wakita. | [12 empty] | 2000000 | 2020-03-10 | [39 empty] | 2020-10-01 | 2023-06-01
2019-AG2 | CLEOSW 2 - RNGWODJ2 - 1 | S | WFEC | WFEC |  |  | 0 | 520855 | CLEOSW 2 | 521039 | RNGWODJ2 | 0 |  | 1 | 21SP | 58 | 68 | 0 |  | 30.4666 | 110 | [7 empty] | CATEGORYB | NONSINGLE | 90675 | 0 | 0 |  | 0 |  | 0 | [5 empty] | OKGE | Cleo Corner 138 kV Terminal Upgrades | Upgrade terminal equipment at Cleo Corner 138 kV substation in order to convert Cleo Corner - Cleo SW 69 kV line to 138 kV. Includes a breaker, terminal, and reconfiguration of lines. The line is designed at 138 kV but has been operated at 69 kV, with a | [12 empty] | 1500000 | 2020-03-10 | [39 empty] | 2020-10-01 | 2021-06-01
2019-AG2 | CLEOSW 2 - RNGWODJ2 - 1 | S | WFEC | WFEC |  |  | 0 | 520855 | CLEOSW 2 | 521039 | RNGWODJ2 | 0 |  | 1 | 21SP | 58 | 68 | 0 |  | 30.4666 | 109.2 | [7 empty] | CATEGORYB | SINGLE | MENOTAP4 - CLEOPLT4 - 1 | 0 | 514789 | MENOTAP4 | 515562 | CLEOPLT4 | 0 |  | 1 |  |  |  | WFEC | Cleo SW 138/69 kV transformer | Add new 138/69 kV transformer at Cleo SW to connect 138 kV segment from Cleo Corner with 69 kV segments to Fairview, Eagle Chief, and Nash/Wakita. | [12 empty] | 2000000 | 2020-03-10 | [39 empty] | 2020-10-01 | 2023-06-01
2019-AG2 | CLEOSW 2 - RNGWODJ2 - 1 | S | WFEC | WFEC |  |  | 0 | 520855 | CLEOSW 2 | 521039 | RNGWODJ2 | 0 |  | 1 | 21SP | 58 | 68 | 0 |  | 30.4666 | 109.2 | [7 empty] | CATEGORYB | SINGLE | MENOTAP4 - CLEOPLT4 - 1 | 0 | 514789 | MENOTAP4 | 515562 | CLEOPLT4 | 0 |  | 1 |  |  |  | OKGE | Cleo Corner 138 kV Terminal Upgrades | Upgrade terminal equipment at Cleo Corner 138 kV substation in order to convert Cleo Corner - Cleo SW 69 kV line to 138 kV. Includes a breaker, terminal, and reconfiguration of lines. The line is designed at 138 kV but has been operated at 69 kV, with a | [12 empty] | 1500000 | 2020-03-10 | [39 empty] | 2020-10-01 | 2021-06-01
2019-AG2 | CLEOSW 2 - RNGWODJ2 - 1 | S | WFEC | WFEC |  |  | 0 | 520855 | CLEOSW 2 | 521039 | RNGWODJ2 | 0 |  | 1 | 22SP | 58 | 68 | 0 |  | 29.815 | 104.4 | [7 empty] | CATEGORYB | SINGLE | CLEOCOR4 - CLEOPLT4 - 1 | 0 | 514778 | CLEOCOR4 | 515562 | CLEOPLT4 | 0 |  | 1 |  |  |  | WFEC | Cleo SW 138/69 kV transformer | Add new 138/69 kV transformer at Cleo SW to connect 138 kV segment from Cleo Corner with 69 kV segments to Fairview, Eagle Chief, and Nash/Wakita. | [12 empty] | 2000000 | 2020-03-10 | [39 empty] | 2020-10-01 | 2023-06-01
2019-AG2 | CLEOSW 2 - RNGWODJ2 - 1 | S | WFEC | WFEC |  |  | 0 | 520855 | CLEOSW 2 | 521039 | RNGWODJ2 | 0 |  | 1 | 22SP | 58 | 68 | 0 |  | 29.815 | 104.4 | [7 empty] | CATEGORYB | SINGLE | CLEOCOR4 - CLEOPLT4 - 1 | 0 | 514778 | CLEOCOR4 | 515562 | CLEOPLT4 | 0 |  | 1 |  |  |  | OKGE | Cleo Corner 138 kV Terminal Upgrades | Upgrade terminal equipment at Cleo Corner 138 kV substation in order to convert Cleo Corner - Cleo SW 69 kV line to 138 kV. Includes a breaker, terminal, and reconfiguration of lines. The line is designed at 138 kV but has been operated at 69 kV, with a | [12 empty] | 1500000 | 2020-03-10 | [39 empty] | 2020-10-01 | 2021-06-01
2019-AG2 | CLEOSW 2 - RNGWODJ2 - 1 | S | WFEC | WFEC |  |  | 0 | 520855 | CLEOSW 2 | 521039 | RNGWODJ2 | 0 |  | 1 | 22SP | 58 | 68 | 0 |  | 29.815 | 104.3 | [7 empty] | CATEGORYB | NONSINGLE | 90675 | 0 | 0 |  | 0 |  | 0 | [5 empty] | WFEC | Cleo SW 138/69 kV transformer | Add new 138/69 kV transformer at Cleo SW to connect 138 kV segment from Cleo Corner with 69 kV segments to Fairview, Eagle Chief, and Nash/Wakita. | [12 empty] | 2000000 | 2020-03-10 | [39 empty] | 2020-10-01 | 2023-06-01
2019-AG2 | CLEOSW 2 - RNGWODJ2 - 1 | S | WFEC | WFEC |  |  | 0 | 520855 | CLEOSW 2 | 521039 | RNGWODJ2 | 0 |  | 1 | 22SP | 58 | 68 | 0 |  | 29.815 | 104.3 | [7 empty] | CATEGORYB | NONSINGLE | 90675 | 0 | 0 |  | 0 |  | 0 | [5 empty] | OKGE | Cleo Corner 138 kV Terminal Upgrades | Upgrade terminal equipment at Cleo Corner 138 kV substation in order to convert Cleo Corner - Cleo SW 69 kV line to 138 kV. Includes a breaker, terminal, and reconfiguration of lines. The line is designed at 138 kV but has been operated at 69 kV, with a | [12 empty] | 1500000 | 2020-03-10 | [39 empty] | 2020-10-01 | 2021-06-01
2019-AG2 | CLEOSW 2 - RNGWODJ2 - 1 | S | WFEC | WFEC |  |  | 0 | 520855 | CLEOSW 2 | 521039 | RNGWODJ2 | 0 |  | 1 | 22SP | 58 | 68 | 0 |  | 29.815 | 103.5 | [7 empty] | CATEGORYB | SINGLE | MENOTAP4 - CLEOPLT4 - 1 | 0 | 514789 | MENOTAP4 | 515562 | CLEOPLT4 | 0 |  | 1 |  |  |  | WFEC | Cleo SW 138/69 kV transformer | Add new 138/69 kV transformer at Cleo SW to connect 138 kV segment from Cleo Corner with 69 kV segments to Fairview, Eagle Chief, and Nash/Wakita. | [12 empty] | 2000000 | 2020-03-10 | [39 empty] | 2020-10-01 | 2023-06-01
2019-AG2 | CLEOSW 2 - RNGWODJ2 - 1 | S | WFEC | WFEC |  |  | 0 | 520855 | CLEOSW 2 | 521039 | RNGWODJ2 | 0 |  | 1 | 22SP | 58 | 68 | 0 |  | 29.815 | 103.5 | [7 empty] | CATEGORYB | SINGLE | MENOTAP4 - CLEOPLT4 - 1 | 0 | 514789 | MENOTAP4 | 515562 | CLEOPLT4 | 0 |  | 1 |  |  |  | OKGE | Cleo Corner 138 kV Terminal Upgrades | Upgrade terminal equipment at Cleo Corner 138 kV substation in order to convert Cleo Corner - Cleo SW 69 kV line to 138 kV. Includes a breaker, terminal, and reconfiguration of lines. The line is designed at 138 kV but has been operated at 69 kV, with a | [12 empty] | 1500000 | 2020-03-10 | [39 empty] | 2020-10-01 | 2021-06-01
2019-AG2 | CLEOSW 2 - RNGWODJ2 - 1 | S | WFEC | WFEC |  |  | 0 | 520855 | CLEOSW 2 | 521039 | RNGWODJ2 | 0 |  | 1 | 25SP | 58 | 68 | 0 |  | 30.5804 | 104.9 | [7 empty] | CATEGORYB | SINGLE | CLEOCOR4 - CLEOPLT4 - 1 | 0 | 514778 | CLEOCOR4 | 515562 | CLEOPLT4 | 0 |  | 1 |  |  |  | WFEC | Cleo SW 138/69 kV transformer | Add new 138/69 kV transformer at Cleo SW to connect 138 kV segment from Cleo Corner with 69 kV segments to Fairview, Eagle Chief, and Nash/Wakita. | [12 empty] | 2000000 | 2020-03-10 | [39 empty] | 2020-10-01 | 2023-06-01
2019-AG2 | CLEOSW 2 - RNGWODJ2 - 1 | S | WFEC | WFEC |  |  | 0 | 520855 | CLEOSW 2 | 521039 | RNGWODJ2 | 0 |  | 1 | 25SP | 58 | 68 | 0 |  | 30.5804 | 104.9 | [7 empty] | CATEGORYB | SINGLE | CLEOCOR4 - CLEOPLT4 - 1 | 0 | 514778 | CLEOCOR4 | 515562 | CLEOPLT4 | 0 |  | 1 |  |  |  | OKGE | Cleo Corner 138 kV Terminal Upgrades | Upgrade terminal equipment at Cleo Corner 138 kV substation in order to convert Cleo Corner - Cleo SW 69 kV line to 138 kV. Includes a breaker, terminal, and reconfiguration of lines. The line is designed at 138 kV but has been operated at 69 kV, with a | [12 empty] | 1500000 | 2020-03-10 | [39 empty] | 2020-10-01 | 2021-06-01
2019-AG2 | CLEOSW 2 - RNGWODJ2 - 1 | S | WFEC | WFEC |  |  | 0 | 520855 | CLEOSW 2 | 521039 | RNGWODJ2 | 0 |  | 1 | 25SP | 58 | 68 | 0 |  | 30.5804 | 104.8 | [7 empty] | CATEGORYB | NONSINGLE | 90675 | 0 | 0 |  | 0 |  | 0 | [5 empty] | WFEC | Cleo SW 138/69 kV transformer | Add new 138/69 kV transformer at Cleo SW to connect 138 kV segment from Cleo Corner with 69 kV segments to Fairview, Eagle Chief, and Nash/Wakita. | [12 empty] | 2000000 | 2020-03-10 | [39 empty] | 2020-10-01 | 2023-06-01
2019-AG2 | CLEOSW 2 - RNGWODJ2 - 1 | S | WFEC | WFEC |  |  | 0 | 520855 | CLEOSW 2 | 521039 | RNGWODJ2 | 0 |  | 1 | 25SP | 58 | 68 | 0 |  | 30.5804 | 104.8 | [7 empty] | CATEGORYB | NONSINGLE | 90675 | 0 | 0 |  | 0 |  | 0 | [5 empty] | OKGE | Cleo Corner 138 kV Terminal Upgrades | Upgrade terminal equipment at Cleo Corner 138 kV substation in order to convert Cleo Corner - Cleo SW 69 kV line to 138 kV. Includes a breaker, terminal, and reconfiguration of lines. The line is designed at 138 kV but has been operated at 69 kV, with a | [12 empty] | 1500000 | 2020-03-10 | [39 empty] | 2020-10-01 | 2021-06-01
2019-AG2 | CLEOSW 2 - RNGWODJ2 - 1 | S | WFEC | WFEC |  |  | 0 | 520855 | CLEOSW 2 | 521039 | RNGWODJ2 | 0 |  | 1 | 25SP | 58 | 68 | 0 |  | 30.5804 | 104 | [7 empty] | CATEGORYB | SINGLE | MENOTAP4 - CLEOPLT4 - 1 | 0 | 514789 | MENOTAP4 | 515562 | CLEOPLT4 | 0 |  | 1 |  |  |  | WFEC | Cleo SW 138/69 kV transformer | Add new 138/69 kV transformer at Cleo SW to connect 138 kV segment from Cleo Corner with 69 kV segments to Fairview, Eagle Chief, and Nash/Wakita. | [12 empty] | 2000000 | 2020-03-10 | [39 empty] | 2020-10-01 | 2023-06-01
2019-AG2 | CLEOSW 2 - RNGWODJ2 - 1 | S | WFEC | WFEC |  |  | 0 | 520855 | CLEOSW 2 | 521039 | RNGWODJ2 | 0 |  | 1 | 25SP | 58 | 68 | 0 |  | 30.5804 | 104 | [7 empty] | CATEGORYB | SINGLE | MENOTAP4 - CLEOPLT4 - 1 | 0 | 514789 | MENOTAP4 | 515562 | CLEOPLT4 | 0 |  | 1 |  |  |  | OKGE | Cleo Corner 138 kV Terminal Upgrades | Upgrade terminal equipment at Cleo Corner 138 kV substation in order to convert Cleo Corner - Cleo SW 69 kV line to 138 kV. Includes a breaker, terminal, and reconfiguration of lines. The line is designed at 138 kV but has been operated at 69 kV, with a | [12 empty] | 1500000 | 2020-03-10 | [39 empty] | 2020-10-01 | 2021-06-01
2019-AG2 | CLEOSW 2 - RNGWODJ2 - 1 | S | WFEC | WFEC |  |  | 0 | 520855 | CLEOSW 2 | 521039 | RNGWODJ2 | 0 |  | 1 | 30SP | 58 | 68 | 0 |  | 29.2553 | 105.3 | [7 empty] | CATEGORYB | NONSINGLE | 90675 | 0 | 0 |  | 0 |  | 0 | [5 empty] | WFEC | Cleo SW 138/69 kV transformer | Add new 138/69 kV transformer at Cleo SW to connect 138 kV segment from Cleo Corner with 69 kV segments to Fairview, Eagle Chief, and Nash/Wakita. | [12 empty] | 2000000 | 2020-03-10 | [39 empty] | 2020-10-01 | 2023-06-01
2019-AG2 | CLEOSW 2 - RNGWODJ2 - 1 | S | WFEC | WFEC |  |  | 0 | 520855 | CLEOSW 2 | 521039 | RNGWODJ2 | 0 |  | 1 | 30SP | 58 | 68 | 0 |  | 29.2553 | 105.3 | [7 empty] | CATEGORYB | NONSINGLE | 90675 | 0 | 0 |  | 0 |  | 0 | [5 empty] | OKGE | Cleo Corner 138 kV Terminal Upgrades | Upgrade terminal equipment at Cleo Corner 138 kV substation in order to convert Cleo Corner - Cleo SW 69 kV line to 138 kV. Includes a breaker, terminal, and reconfiguration of lines. The line is designed at 138 kV but has been operated at 69 kV, with a | [12 empty] | 1500000 | 2020-03-10 | [39 empty] | 2020-10-01 | 2021-06-01
2019-AG2 | CLEOSW 2 - RNGWODJ2 - 1 | S | WFEC | WFEC |  |  | 0 | 520855 | CLEOSW 2 | 521039 | RNGWODJ2 | 0 |  | 1 | 30SP | 58 | 68 | 0 |  | 29.2553 | 104.5 | [7 empty] | CATEGORYB | SINGLE | MENOTAP4 - CLEOPLT4 - 1 | 0 | 514789 | MENOTAP4 | 515562 | CLEOPLT4 | 0 |  | 1 |  |  |  | WFEC | Cleo SW 138/69 kV transformer | Add new 138/69 kV transformer at Cleo SW to connect 138 kV segment from Cleo Corner with 69 kV segments to Fairview, Eagle Chief, and Nash/Wakita. | [12 empty] | 2000000 | 2020-03-10 | [39 empty] | 2020-10-01 | 2023-06-01
2019-AG2 | CLEOSW 2 - RNGWODJ2 - 1 | S | WFEC | WFEC |  |  | 0 | 520855 | CLEOSW 2 | 521039 | RNGWODJ2 | 0 |  | 1 | 30SP | 58 | 68 | 0 |  | 29.2553 | 104.5 | [7 empty] | CATEGORYB | SINGLE | MENOTAP4 - CLEOPLT4 - 1 | 0 | 514789 | MENOTAP4 | 515562 | CLEOPLT4 | 0 |  | 1 |  |  |  | OKGE | Cleo Corner 138 kV Terminal Upgrades | Upgrade terminal equipment at Cleo Corner 138 kV substation in order to convert Cleo Corner - Cleo SW 69 kV line to 138 kV. Includes a breaker, terminal, and reconfiguration of lines. The line is designed at 138 kV but has been operated at 69 kV, with a | [12 empty] | 1500000 | 2020-03-10 | [39 empty] | 2020-10-01 | 2021-06-01
2007-AG3 | CLIFTON - GREENLEAF 115KV CKT 1 | U | MKEC | MKEC |  |  | 0 | 539656 | CLIFTON3 115.00 | 539665 | GRNLEAF3 115.00 | 0 |  | 1 | [15 empty] | BASECASE | BASE CASE | [8 empty] | Credit Flowgate |  |  | MKEC | CLIFTON - GREENLEAF 115KV CKT 1 | Rebuild 14.4 miles | [53 empty] | 2011-06-01 | 2013-06-01
2007-AG1 | Coffeyville Tap - Dearing 138kV CKT 1 WERE #2 | U | WERE | AEPW |  |  | 0 | 510422 | COFFEYT4 | 533002 | DEARING4 | 0 |  | 1 | [15 empty] | BASECASE | BASE CASE | [8 empty] | Credit Flowgate |  |  | WERE | COFFEYVILLE TAP - DEARING 138KV CKT 1 (WR) #2 | Replace Disconnect Switches, Wavetrap, Breaker, Jumpers with a minimum 2000 amp emergency rating equipment | [53 empty] | 2010-06-09 | 2010-06-09
GI | COUNTY LINE - BATTLE CREEK 115KV CKT 1 | U | NPPD | NPPD | NPPD_686 | NPPD_686 | 0 | 640115 | CO.LINE7 | 640072 | BATTLCRK7 | 0 |  | 1 | [15 empty] | BASECASE | BASE CASE | [8 empty] | Credit Flowgate |  |  | NPPD | Battle Creek - County Line 115kV Rebuild | Rebuild/Upgrade the Battle Creek – County Line 115kV to rerate line segments to greater than 125 MVA. | [53 empty] | 2017-05-01 | 2017-05-01
2007-AG3 | DEARING 138KV | U | WERE |  | SEAST |  |  | 533002 | DEARING4 138.00 | [20 empty] | BASECASE | BASE CASE | [8 empty] | Credit Flowgate |  |  | WERE | DEARING 138KV | Dearing 138 kV 20 MVAR Capacitor Addition | [53 empty] | 2012-06-01 | 2012-06-01
GI | DICKINSON 230/115/13.8kV CKT 2 | U | WAPA | MDU |  |  | 1 | 659124 | DICKNSN4 230.00 | 659125 | DKSN-NK7 115.00 | 659197 | DK.KW1A_-BE913.800 | 1 | [15 empty] | BASECASE | BASE CASE | [8 empty] | Credit Flowgate |  |  | BEPC | DICKINSON 230/115/13.8KV CKT 2 | Build new 230/115/13.8kV Transformer circuit #2 at Dickinson. | [53 empty] | 2019-03-01 | 2019-03-01
GI | DRY CREEK - RAPID CITY 115 kV CKT 1 | U | WAPA | WAPA |  |  | 0 | 659377 | DRYCREEK-BE7115.00 | 652490 | RAPIDCY7 115.00 | 0 |  | 1 | [15 empty] | BASECASE | BASE CASE | [8 empty] | Credit Flowgate |  |  | WAPA | Dry Creek - Rapid City 115 kV Ckt 1 | Rapid City Substation - Replacement of the main and transfer 115 kV buses, transfer bay, and transmission line bay (to Dry Creek). | [53 empty] | 2020-02-28 | 2020-02-28
2019-AG2 | EAGLCHF2 - RNGWODJ2 - 1 | S | WFEC | WFEC |  |  | 0 | 521039 | RNGWODJ2 | 520890 | EAGLCHF2 | 0 |  | 1 | 21SP | 29 | 29 | 0 |  | 25.7307 | 106.2 | [7 empty] | CATEGORYB | SINGLE | CLEOCOR4 - CLEOPLT4 - 1 | 0 | 514778 | CLEOCOR4 | 515562 | CLEOPLT4 | 0 |  | 1 |  |  |  | WFEC | Eagle Chief 69 kV Terminal Upgrades | Modify breaker at Eagle Chief 69 kV substation to increase Eagle Chief - Cleo SW 69 kV Emergency Rating to 68 MVA. Line to bypass Ringwood Jct 69 kV substation. | [12 empty] | 150000 | 2020-03-10 | [39 empty] | 2021-06-01 | 2023-06-01
2019-AG2 | EAGLCHF2 - RNGWODJ2 - 1 | S | WFEC | WFEC |  |  | 0 | 521039 | RNGWODJ2 | 520890 | EAGLCHF2 | 0 |  | 1 | 21SP | 29 | 29 | 0 |  | 25.7307 | 105.4 | [7 empty] | CATEGORYB | SINGLE | MENOTAP4 - CLEOPLT4 - 1 | 0 | 514789 | MENOTAP4 | 515562 | CLEOPLT4 | 0 |  | 1 |  |  |  | WFEC | Eagle Chief 69 kV Terminal Upgrades | Modify breaker at Eagle Chief 69 kV substation to increase Eagle Chief - Cleo SW 69 kV Emergency Rating to 68 MVA. Line to bypass Ringwood Jct 69 kV substation. | [12 empty] | 150000 | 2020-03-10 | [39 empty] | 2021-06-01 | 2023-06-01
2019-AG2 | EAGLCHF2 - RNGWODJ2 - 1 | S | WFEC | WFEC |  |  | 0 | 521039 | RNGWODJ2 | 520890 | EAGLCHF2 | 0 |  | 1 | 22LP | 29 | 29 | 0 |  | 19.5943 | 111.7 | [7 empty] | CATEGORYB | NONSINGLE | 90675 | 0 | 0 |  | 0 |  | 0 | [5 empty] | WFEC | Eagle Chief 69 kV Terminal Upgrades | Modify breaker at Eagle Chief 69 kV substation to increase Eagle Chief - Cleo SW 69 kV Emergency Rating to 68 MVA. Line to bypass Ringwood Jct 69 kV substation. | [12 empty] | 150000 | 2020-03-10 | [39 empty] | 2021-06-01 | 2023-06-01
2019-AG2 | EAGLCHF2 - RNGWODJ2 - 1 | S | WFEC | WFEC |  |  | 0 | 521039 | RNGWODJ2 | 520890 | EAGLCHF2 | 0 |  | 1 | 22LP | 29 | 29 | 0 |  | 19.5943 | 111.5 | [7 empty] | CATEGORYB | SINGLE | MENOTAP4 - CLEOPLT4 - 1 | 0 | 514789 | MENOTAP4 | 515562 | CLEOPLT4 | 0 |  | 1 |  |  |  | WFEC | Eagle Chief 69 kV Terminal Upgrades | Modify breaker at Eagle Chief 69 kV substation to increase Eagle Chief - Cleo SW 69 kV Emergency Rating to 68 MVA. Line to bypass Ringwood Jct 69 kV substation. | [12 empty] | 150000 | 2020-03-10 | [39 empty] | 2021-06-01 | 2023-06-01
2019-AG2 | EAGLCHF2 - RNGWODJ2 - 1 | S | WFEC | WFEC |  |  | 0 | 521039 | RNGWODJ2 | 520890 | EAGLCHF2 | 0 |  | 1 | 22SP | 29 | 29 | 0 |  | 23.4091 | 113.8 | [7 empty] | CATEGORYB | SINGLE | CLEOCOR4 - CLEOPLT4 - 1 | 0 | 514778 | CLEOCOR4 | 515562 | CLEOPLT4 | 0 |  | 1 |  |  |  | WFEC | Eagle Chief 69 kV Terminal Upgrades | Modify breaker at Eagle Chief 69 kV substation to increase Eagle Chief - Cleo SW 69 kV Emergency Rating to 68 MVA. Line to bypass Ringwood Jct 69 kV substation. | [12 empty] | 150000 | 2020-03-10 | [39 empty] | 2021-06-01 | 2023-06-01
2019-AG2 | EAGLCHF2 - RNGWODJ2 - 1 | S | WFEC | WFEC |  |  | 0 | 521039 | RNGWODJ2 | 520890 | EAGLCHF2 | 0 |  | 1 | 22SP | 29 | 29 | 0 |  | 23.4091 | 113 | [7 empty] | CATEGORYB | SINGLE | MENOTAP4 - CLEOPLT4 - 1 | 0 | 514789 | MENOTAP4 | 515562 | CLEOPLT4 | 0 |  | 1 |  |  |  | WFEC | Eagle Chief 69 kV Terminal Upgrades | Modify breaker at Eagle Chief 69 kV substation to increase Eagle Chief - Cleo SW 69 kV Emergency Rating to 68 MVA. Line to bypass Ringwood Jct 69 kV substation. | [12 empty] | 150000 | 2020-03-10 | [39 empty] | 2021-06-01 | 2023-06-01
2019-AG2 | EAGLCHF2 - RNGWODJ2 - 1 | S | WFEC | WFEC |  |  | 0 | 521039 | RNGWODJ2 | 520890 | EAGLCHF2 | 0 |  | 1 | 25LP | 29 | 29 | 0 |  | 20.5554 | 103.9 | [7 empty] | CATEGORYB | NONSINGLE | 90675 | 0 | 0 |  | 0 |  | 0 | [5 empty] | WFEC | Eagle Chief 69 kV Terminal Upgrades | Modify breaker at Eagle Chief 69 kV substation to increase Eagle Chief - Cleo SW 69 kV Emergency Rating to 68 MVA. Line to bypass Ringwood Jct 69 kV substation. | [12 empty] | 150000 | 2020-03-10 | [39 empty] | 2021-06-01 | 2023-06-01
2019-AG2 | EAGLCHF2 - RNGWODJ2 - 1 | S | WFEC | WFEC |  |  | 0 | 521039 | RNGWODJ2 | 520890 | EAGLCHF2 | 0 |  | 1 | 25LP | 29 | 29 | 0 |  | 20.5554 | 103.6 | [7 empty] | CATEGORYB | SINGLE | MENOTAP4 - CLEOPLT4 - 1 | 0 | 514789 | MENOTAP4 | 515562 | CLEOPLT4 | 0 |  | 1 |  |  |  | WFEC | Eagle Chief 69 kV Terminal Upgrades | Modify breaker at Eagle Chief 69 kV substation to increase Eagle Chief - Cleo SW 69 kV Emergency Rating to 68 MVA. Line to bypass Ringwood Jct 69 kV substation. | [12 empty] | 150000 | 2020-03-10 | [39 empty] | 2021-06-01 | 2023-06-01
2019-AG2 | EAGLCHF2 - RNGWODJ2 - 1 | S | WFEC | WFEC |  |  | 0 | 521039 | RNGWODJ2 | 520890 | EAGLCHF2 | 0 |  | 1 | 25SP | 29 | 29 | 0 |  | 21.8782 | 111.6 | [7 empty] | CATEGORYB | SINGLE | CLEOCOR4 - CLEOPLT4 - 1 | 0 | 514778 | CLEOCOR4 | 515562 | CLEOPLT4 | 0 |  | 1 |  |  |  | WFEC | Eagle Chief 69 kV Terminal Upgrades | Modify breaker at Eagle Chief 69 kV substation to increase Eagle Chief - Cleo SW 69 kV Emergency Rating to 68 MVA. Line to bypass Ringwood Jct 69 kV substation. | [12 empty] | 150000 | 2020-03-10 | [39 empty] | 2021-06-01 | 2023-06-01
2019-AG2 | EAGLCHF2 - RNGWODJ2 - 1 | S | WFEC | WFEC |  |  | 0 | 521039 | RNGWODJ2 | 520890 | EAGLCHF2 | 0 |  | 1 | 25SP | 29 | 29 | 0 |  | 21.8782 | 110.8 | [7 empty] | CATEGORYB | SINGLE | MENOTAP4 - CLEOPLT4 - 1 | 0 | 514789 | MENOTAP4 | 515562 | CLEOPLT4 | 0 |  | 1 |  |  |  | WFEC | Eagle Chief 69 kV Terminal Upgrades | Modify breaker at Eagle Chief 69 kV substation to increase Eagle Chief - Cleo SW 69 kV Emergency Rating to 68 MVA. Line to bypass Ringwood Jct 69 kV substation. | [12 empty] | 150000 | 2020-03-10 | [39 empty] | 2021-06-01 | 2023-06-01
2019-AG2 | EAGLCHF2 - RNGWODJ2 - 1 | S | WFEC | WFEC |  |  | 0 | 521039 | RNGWODJ2 | 520890 | EAGLCHF2 | 0 |  | 1 | 30SP | 29 | 29 | 0 |  | 16.4597 | 109.2 | [7 empty] | CATEGORYB | SINGLE | CLEOCOR4 - CLEOPLT4 - 1 | 0 | 514778 | CLEOCOR4 | 515562 | CLEOPLT4 | 0 |  | 1 |  |  |  | WFEC | Eagle Chief 69 kV Terminal Upgrades | Modify breaker at Eagle Chief 69 kV substation to increase Eagle Chief - Cleo SW 69 kV Emergency Rating to 68 MVA. Line to bypass Ringwood Jct 69 kV substation. | [12 empty] | 150000 | 2020-03-10 | [39 empty] | 2021-06-01 | 2023-06-01
2019-AG2 | EAGLCHF2 - RNGWODJ2 - 1 | S | WFEC | WFEC |  |  | 0 | 521039 | RNGWODJ2 | 520890 | EAGLCHF2 | 0 |  | 1 | 30SP | 29 | 29 | 0 |  | 16.4597 | 108.3 | [7 empty] | CATEGORYB | SINGLE | MENOTAP4 - CLEOPLT4 - 1 | 0 | 514789 | MENOTAP4 | 515562 | CLEOPLT4 | 0 |  | 1 |  |  |  | WFEC | Eagle Chief 69 kV Terminal Upgrades | Modify breaker at Eagle Chief 69 kV substation to increase Eagle Chief - Cleo SW 69 kV Emergency Rating to 68 MVA. Line to bypass Ringwood Jct 69 kV substation. | [12 empty] | 150000 | 2020-03-10 | [39 empty] | 2021-06-01 | 2023-06-01
GI | ELK CREEK - NEWELL 115 kV CKT 1 | U | WAPA | WAPA |  |  | 0 | 652483 | NEWELL 7 115.00 | 652473 | ELKCRK 7 115.00 | 0 |  | 1 | [15 empty] | BASECASE | BASE CASE | [8 empty] | Credit Flowgate |  |  | WAPA | Elk Creek - Newell 115 kV Ckt 1 | Replace the 115 kV strain bus, circuit switchers, and jumpers at Newell substation. | [53 empty] | 2020-02-28 | 2020-02-28
GI | ELK CREEK - RAPID CITY 115 kV CKT 1 | U | WAPA | WAPA |  |  | 0 | 652473 | ELKCRK 7 115.00 | 652490 | RAPIDCY7 115.00 | 0 |  | 1 | [15 empty] | BASECASE | BASE CASE | [8 empty] | Credit Flowgate |  |  | WAPA | Elk Creek - Rapid City 115 kV Ckt 1 | Replace the 115 kV strain bus and jumpers. Reset relays. | [53 empty] | 2020-02-28 | 2020-02-28
2005-AG2 | EXPLORER GLENPOOL TAP - RIVERSIDE STATION 138KV CKT 1 AEPW | U | AEPW | OKGE |  |  | 0 | 509783 | R.S.S.-4 138 | 515473 | EXPGLNT4 | 0 |  | 1 | [15 empty] | BASECASE | BASE CASE | [8 empty] | Credit Flowgate |  |  | AEPW | EXPLORER GLENPOOL - RIVERSIDE STATION 138KV CKT 1 (AEP) | Reconductor 1.82 miles with ACCC. Replace wave trap jumpers at Riverside. | [53 empty] | 2009-03-23 | 2009-03-23
2005-AG2 | EXPLORER GLENPOOL TAP - RIVERSIDE STATION 138KV CKT 1 OKGE | U | AEPW | OKGE |  |  | 0 | 509783 | R.S.S.-4 138 | 515473 | EXPGLNT4 | 0 |  | 1 | [15 empty] | BASECASE | BASE CASE | [8 empty] | Credit Flowgate |  |  | OKGE | EXPLORER GLENPOOL - RIVERSIDE STATION 138KV CKT 1 (OGE) | Reconductor 1.82 miles line with Drake ACCC/TW. | [53 empty] | 2009-06-01 | 2009-06-01
GI | Fairfax - Pawnee 138kV Ckt 1 | U |  |  |  |  | 0 | 300139 |  | 512749 |  |  |  | 1 | [15 empty] | BASECASE | BASE CASE | [8 empty] | Credit Flowgate |  |  | GRDA | FAIRFAX - PAWNEE 138KV CKT 1 | Construct Approx. 15 miles of 138kV transmission line from Fairfax to a new substation on the Cleveland-Stillwater 138kV line near Pawnee. & Fairfax Substation: Install 138kV line terminal and any additional modifications that are necessary to connect to | [13 empty] | 2011-06-15 | [39 empty] | 2014-06-30 | 2014-06-30
2019-AG2 | FAIRVEW2 - RNGWODJ2 - 1 | S | WFEC | WFEC |  |  | 0 | 521039 | RNGWODJ2 | 520909 | FAIRVEW2 | 0 |  | 1 | 21SP | 37 | 42 | 0 |  | 28.0744 | 104.9 | [7 empty] | CATEGORYB | SINGLE | CLEOCOR4 - CLEOPLT4 - 1 | 0 | 514778 | CLEOCOR4 | 515562 | CLEOPLT4 | 0 |  | 1 |  |  |  | WFEC | Cleo SW - Fairview 69 kV Rebuild | Upgrade structures and 211ACSR span across Cimarron River between Fairview and Ringwood Jct 69 kV. Extend Fairview - Ringwood Jct 69 kV line by 1.7 miles to go from Fairview - Cleo SW 69 kV, bypassing the Ringwood Jct 69 kV substation. | [12 empty] | 1450000 | 2020-03-10 | [39 empty] | 2021-06-01 | 2023-06-01
2019-AG2 | FAIRVEW2 - RNGWODJ2 - 1 | S | WFEC | WFEC |  |  | 0 | 521039 | RNGWODJ2 | 520909 | FAIRVEW2 | 0 |  | 1 | 21SP | 37 | 42 | 0 |  | 28.0744 | 104.8 | [7 empty] | CATEGORYB | NONSINGLE | 90675 | 0 | 0 |  | 0 |  | 0 | [5 empty] | WFEC | Cleo SW - Fairview 69 kV Rebuild | Upgrade structures and 211ACSR span across Cimarron River between Fairview and Ringwood Jct 69 kV. Extend Fairview - Ringwood Jct 69 kV line by 1.7 miles to go from Fairview - Cleo SW 69 kV, bypassing the Ringwood Jct 69 kV substation. | [12 empty] | 1450000 | 2020-03-10 | [39 empty] | 2021-06-01 | 2023-06-01
2019-AG2 | FAIRVEW2 - RNGWODJ2 - 1 | S | WFEC | WFEC |  |  | 0 | 521039 | RNGWODJ2 | 520909 | FAIRVEW2 | 0 |  | 1 | 21SP | 37 | 42 | 0 |  | 28.0744 | 104.1 | [7 empty] | CATEGORYB | SINGLE | MENOTAP4 - CLEOPLT4 - 1 | 0 | 514789 | MENOTAP4 | 515562 | CLEOPLT4 | 0 |  | 1 |  |  |  | WFEC | Cleo SW - Fairview 69 kV Rebuild | Upgrade structures and 211ACSR span across Cimarron River between Fairview and Ringwood Jct 69 kV. Extend Fairview - Ringwood Jct 69 kV line by 1.7 miles to go from Fairview - Cleo SW 69 kV, bypassing the Ringwood Jct 69 kV substation. | [12 empty] | 1450000 | 2020-03-10 | [39 empty] | 2021-06-01 | 2023-06-01
2007-AG3 | FLATRDG3 138.00 - MEDICINE LODGE 138KV CKT 1 | U | MKEC | MKEC |  |  | 0 | 539638 | FLATRDG3 138.00 | 539674 | MED-LDG4 138.00 | 0 |  | 1 | [15 empty] | BASECASE | BASE CASE | [8 empty] | Credit Flowgate |  |  | MKEC | FLATRDG3 - MEDICINE LODGE 138KV CKT 1 | Rebuild 8.05 mile line | [53 empty] | 2009-12-01 | 2013-06-01
2007-AG3 | FLATRDG3 138.00 - HARPER 138KV CKT 1 | U | MKEC | MKEC |  |  | 0 | 539638 | FLATRDG3 138.00 | 539668 | HARPER 4 138.00 | 0 |  | 1 | [15 empty] | BASECASE | BASE CASE | [8 empty] | Credit Flowgate |  |  | MKEC | FLATRDG3 - HARPER 138KV CKT 1 | Rebuild 24.15 mile line | 286 | 286 |  |  | 24.15 | 24 | 24 | [46 empty] | 2009-12-01 | 2013-06-01
GI | Fort Randall - Madison County 230kV Ckt 1 | U |  |  |  |  | 0 | 640540 |  | 652509 |  |  |  | 1 | [15 empty] | BASECASE | BASE CASE | [8 empty] | Credit Flowgate |  |  | NPPD | Fort Randall - Madison County 230kV Ckt 1 | Raise structures and line clearances as necessary to re-rate the transmission line to 320 MVA | [53 empty] | 2014-10-01 | 2014-10-01
2006-AG1 | FT SUPPLY 138/69KV TRANSFORMER CKT 1 | U | WFEC | WFEC |  |  | 1 | 520920 | FTSUPLY4 138 | 520919 | FTSUPLY269.0 | 521182 |  | 2 | [15 empty] | BASECASE | BASE CASE | [8 empty] | Credit Flowgate |  |  | WFEC | FT SUPPLY 138/69KV TRANSFORMER CKT 2 | Install 2nd 70 MVA auto at Ft Supply | [53 empty] | 2006-12-01 | 2008-06-01
GI | Ft. Dodge - North Ft. Dodge 115 kV Ckt 2 | U | MKEC | MKEC |  |  | 0 | 539671 |  | 539771 |  |  |  | 2 | [15 empty] | BASECASE | BASE CASE | [8 empty] | Credit Flowgate |  |  | MKEC | Ft. Dodge - North Ft. Dodge 115 kV Ckt 2 | Build appoximately 0.5 mile 115 kV line | [53 empty] | 2015-05-01 | 2015-05-01
GI | GAVINS POINT - YANKTON JUNCTION 115 kV | U | WAPA | WAPA |  |  | 0 | 652511 | GAVINS 7 | 660006 | YKNTJCT7 | 0 |  | 1 | [15 empty] | BASECASE | BASE CASE | [8 empty] | Credit Flowgate |  |  | WAPA | Gavins Point - Yankton Junction 115 kV | Rebuild approximately four (4) miles of 115 kV and replace associated terminal equipment. | [53 empty] | 2019-12-31 | 2019-12-31
GI | Kingfisher Co TAP - MATHEWSON 345kV CKT 1 | U | OKGE | OKGE |  |  | 0 | 515875 | REDNGTN7 345.00 | 515497 | MATHWSON7 345.00 |  |  | 1 | [15 empty] | BASECASE | BASE CASE | [8 empty] | Credit Flowgate |  |  | OKGE | Kingfisher Co Tap - Mathewson 345kV CKT 1 | Replace terminal equipment to achieve conductor limit | [53 empty] | 2018-03-01 | 2018-03-01
GI | GRACMNT4 138.00 - WASHITA 138KV CKT 2 OKGE | U | WFEC | OKGE | AEP-CS | ARDMORE | 0 | 521089 | WASHITA4 138.00 | 515802 | GRACMNT4 138.00 | 0 |  | 2 | [15 empty] | BASECASE | BASE CASE | [8 empty] | Credit Flowgate |  |  | OKGE | Gracemont 138kV line terminal addition | [14 empty] | 2010-11-20 | [39 empty] | 2012-10-12 | 2012-10-12
GI | GRACMNT4 138.00 - WASHITA 138KV CKT 2 WFEC | U | WFEC | OKGE | AEP-CS | ARDMORE | 0 | 521089 | WASHITA4 138.00 | 515802 | GRACMNT4 138.00 | 0 |  | 2 | [15 empty] | BASECASE | BASE CASE | [8 empty] | Credit Flowgate |  |  | WFEC | WASHITA - GRACEMONT 138 KV CKT 2 | BUILD WASHITA - GRACEMONT 138KV CKT 2 (APPROXIMATELY 7 MILES). ADD LINE TERMINAL AT WASHITA AND PROCURE RIGHT OF WAY. REQUIRED AS SHARED NETWORK UPGRADE FOR INTERCONNECTION OF COMMANCHE CO. | [13 empty] | 2010-11-20 | [39 empty] | 2012-10-12 | 2012-10-12
GI | GRAPEVINE - WHEELER 230 kV CKT 1 | U | SPS | SPS |  |  | 0 | 523777 | WHEELER 6230.00 | 523771 | GRAPEVINE 6230.00 | 0 |  | 1 | [15 empty] | BASECASE | BASE CASE | [8 empty] | Credit Flowgate |  |  | SPS | Grapevine - Wheeler 230 kV Ckt 1 Terminal Equipment (SPS) | Replace wavetrap at Grapevine to achieve 814 amps (324 MVA). | [53 empty] | 2020-12-07 | 2020-12-07
2008-AGP1 | GREENLEAF - KNOB HILL 115KV CKT 1 | U | SUNC | WERE |  | NCENTRAL | 0 | 539665 | GRNLEAF3 115.00 | 533332 | KNOB HL3 115.00 | 0 |  | 1 | [15 empty] | BASECASE | BASE CASE | [8 empty] | Credit Flowgate |  |  | MKEC | GREENLEAF - KNOB HILL 115KV CKT 1 (MKEC) | Rebuild 43.5% Ownership of 20.9 miles | [53 empty] | 2013-06-01 | 2013-06-01
2019-AG2 | GRNWD 5 - LEESUM 5 - 1 | S | KCPL | KCPL |  |  | 0 | 541218 | GRNWD 5 | 541233 | LEESUM 5 | 0 |  | 1 | 20SP | 446 | 446 | 0 | 99 | 72.5227 | 100.9 | [7 empty] | CATEGORYB | SINGLE | PHILL 5 - LKWINBG5 - 1 | 0 | 541225 | PHILL 5 | 541243 | LKWINBG5 | 0 |  | 1 |  |  |  | WERE | Greenwood 161 kV Terminal Equipment Upgrade | Replace 2 breakers and relay upgrades at Greenwood 161 kV substation | [12 empty] | 1500000 | 2020-03-04 | [39 empty] | 2020-06-01 | 2021-12-31
GI | Harrington Mid - Nichols 230 kV Ckt 2 | U | SPS | SPS |  |  | 0 | 523978 |  | 524044 |  |  |  | 2 | [15 empty] | BASECASE | BASE CASE | [8 empty] | Credit Flowgate |  |  | SPS | Harrington Mid - Nichols 230 kV Ckt 2 | Reconductor Harrington Mid - Nichols 230kV. Replace switches and breakers to get circuit to 727/727 MVA rating. New limit should be bus rating. | [13 empty] | 2011-10-01 | [39 empty] | 2012-12-01 | 2012-12-01
GI | Harrington West - Nichols 230kV Ckt 1 | U | SPS | SPS |  |  | 0 | 523977 |  | 524044 |  |  |  | 1 | [15 empty] | BASECASE | BASE CASE | [8 empty] | Credit Flowgate |  |  | SPS | Harrington West - Nichols 230kV Ckt 1 | Reconductor Harrington West - Nichols 230kV. Replace switches and breakers to get circuit to 727/727 MVA rating. New limit should be bus rating. | [13 empty] | 2011-10-01 | [39 empty] | 2012-12-01 | 2012-12-01
GI | Hoskins - Dixon County 230kV Line Upgrade | U | NPPD | NPPD |  |  | 0 | 640560 | WAKEFIELD 4 | 640227 | HOSKINS4 |  |  | 1 | [15 empty] | BASECASE | BASE CASE | [8 empty] | Credit Flowgate |  |  | NPPD | Hoskins - Dixon County 230kV Line Upgrade | Increase clearances to accommodate 320MVA facility rating to address loading issues | [53 empty] | 2015-10-24 | 2015-10-24
2019-AG2 | HUGO 7 345.0 | S | WFEC |  |  |  |  | 521157 | HUGO 7 | [5 empty] | 22LP | [9 empty] | 0.88016 | 1.0021 | 0.9 | 1.05 | CATEGORYB | NONSINGLE | 87311 | 0 | 0 |  | 0 |  | 0 | [5 empty] | AEPW | Valliant 130 MVAR Capacitance | Add new 130 MVAR cap bank at Valliant 345kV | [12 empty] | 7500000 | 2020-03-04 | [39 empty] | 2022-04-01 | 2022-12-01
2019-AG2 | HUGO 7 345.0 | S | WFEC |  |  |  |  | 521157 | HUGO 7 | [5 empty] | 25LP | [9 empty] | 0.88536 | 1.0001 | 0.9 | 1.05 | CATEGORYB | NONSINGLE | 87311 | 0 | 0 |  | 0 |  | 0 | [5 empty] | AEPW | Valliant 130 MVAR Capacitance | Add new 130 MVAR cap bank at Valliant 345kV | [12 empty] | 7500000 | 2020-03-04 | [39 empty] | 2022-04-01 | 2022-12-01
2005-AG2 | HUGO POWER PLANT - VALLIANT 138KV CKT 1 | U | WFEC | AEPW |  |  | 0 | 521157 | HUGO PP4 138 | 510911 | VALIANT4 138 | 0 |  | 1 | [15 empty] | BASECASE | BASE CASE | [8 empty] | Credit Flowgate |  |  | ITCGP | HUGO - VALLIANT 345KV CKT 1 | New 19 miles 345 KV | [53 empty] | 2012-07-01 | 2012-07-01
2005-AG2 | HUGO POWER PLANT - VALLIANT 138KV CKT 1 | U | WFEC | AEPW |  |  | 0 | 521157 | HUGO PP4 138 | 510911 | VALIANT4 138 | 0 |  | 1 | [15 empty] | BASECASE | BASE CASE | [8 empty] | Credit Flowgate |  |  | AEPW | Valliant 345 kV (AEP) | Vallient 345 KV line terminal | [53 empty] | 2012-07-01 | 2012-07-01
2005-AG2 | HUGO POWER PLANT 345/138KV TRANSFORMER CKT 1 | U | WFEC | AEPW |  |  | 1 | 521157 | HUGO PP4 138 | 520948 | HUGO PP4 138.00 | 521189 |  | 1 | [15 empty] | BASECASE | BASE CASE | [8 empty] | Credit Flowgate |  |  | ITCGP | HUGO 345/138KV TRANSFORMER CKT 1 | New 345/138 kv Auto | [53 empty] | 2012-07-01 | 2012-07-01
2019-AG2 | HUGO PP4 138.0 | S | WFEC |  |  |  |  | 520948 | HUGO PP4 | [5 empty] | 25LP | [9 empty] | 0.89273 | 1.0033 | 0.9 | 1.05 | CATEGORYB | NONSINGLE | 84206 | 0 | 0 |  | 0 |  | 0 | [5 empty] | AEPW | Valliant 130 MVAR Capacitance | Add new 130 MVAR cap bank at Valliant 345kV | [12 empty] | 7500000 | 2020-03-04 | [39 empty] | 2022-04-01 | 2022-12-01
2019-AG2 | HUGO---2 69.0 | S | AEPW |  |  |  |  | 510893 | HUGO---2 | [5 empty] | 25LP | [9 empty] | 0.8971 | 1.0023 | 0.92 | 1.05 | CATEGORYB | NONSINGLE | 84206 | 0 | 0 |  | 0 |  | 0 | [5 empty] | AEPW | Valliant 130 MVAR Capacitance | Add new 130 MVAR cap bank at Valliant 345kV | [12 empty] | 7500000 | 2020-03-04 | [39 empty] | 2022-04-01 | 2022-12-01
2019-AG2 | HUGO---4 138.0 | S | AEPW |  |  |  |  | 510901 | HUGO---4 | [5 empty] | 25LP | [9 empty] | 0.89786 | 1.0035 | 0.92 | 1.05 | CATEGORYB | NONSINGLE | 84206 | 0 | 0 |  | 0 |  | 0 | [5 empty] | AEPW | Valliant 130 MVAR Capacitance | Add new 130 MVAR cap bank at Valliant 345kV | [12 empty] | 7500000 | 2020-03-04 | [39 empty] | 2022-04-01 | 2022-12-01
2006-AG1 | JAGGARD JUNCTION - PENTAGON 115KV CKT 1 | U | WERE | WERE |  |  | 0 | 533243 |  | 533261 |  | 0 |  | 1 | [15 empty] | BASECASE | BASE CASE | [8 empty] | Credit Flowgate |  |  | WERE | JAGGARD JUNCTION - PENTAGON 115KV CKT 1 | Rebuild Jaggard Junction - Pentagon 115 kV line. | [53 empty] | 2010-05-13 | 2010-05-13
2006-AG1 | JARBALO JUNCTION SWITCHING STATION - 166TH STREET 115KV CKT 1 | U | WERE | WERE |  |  | 0 | 533244 |  | 533233 |  | 0 |  | 1 | [15 empty] | BASECASE | BASE CASE | [8 empty] | Credit Flowgate |  |  | WERE | 166TH STREET - JARBALO JUNCTION SWITCHING STATION 115KV CKT 1 | Rebuild Jarbalo - 166th Street 115 kV line. | [53 empty] | 2010-09-18 | 2010-09-18
GI | KC SOUTH - LONGVIEW 161 KV CKT 1 | U | MIPU | MIPU |  |  | 0 | 541245 |  | 541224 |  |  |  | 1 | [15 empty] | BASECASE | BASE CASE | [8 empty] | Credit Flowgate |  |  | MIPU | Longview - KC South 161kV | Install new 161kV wavetrap in place of existing wavetrap | [13 empty] | 2011-01-05 | [39 empty] | 2011-01-31 | 2011-01-31
2008-AGP1 | KCI - Platte City 161kV Ckt 1 | U | KCPL | KCPL |  |  | 0 | 541221 |  | 541212 |  | 0 |  | 1 | [15 empty] | BASECASE | BASE CASE | [8 empty] | Credit Flowgate |  |  | MIPU | KCI - Platte City 161kV Ckt 1 | Replace 800 amp wavetrap at KCI | [53 empty] | 2010-08-31 | 2010-08-31
GEN | KELLY - MADISONCO 230.00 230KV CKT 1 | U | NPPD | NPPD | NPPD_686 | NPPD_686 | 0 | 640540 | MADISONCO 230.00 | 640133 | COLMBUS4 230.00 | 0 |  | 1 | [15 empty] | BASECASE | BASE CASE | [8 empty] | Credit Flowgate |  |  | NPPD | Kelly - Madison County 230kV Ckt 1 | Raise structures and line clearances as necessary to re-rate the transmission line to 320MVA | 320 | 320 |  |  |  | 24 | 24 | [5 empty] | 480000 | 2011-01-01 | [39 empty] | 2014-11-01 | 2014-11-01
2019-AG2 | KELLY 3 - GOFF 3 - 1 | S | WERE | WERE |  |  | 0 | 533331 | GOFF 3 | 533217 | KELLY 3 | 0 |  | 1 | 25SP | 86 | 92 | 0 | 96.8 | 68.885 | 104.2 | [7 empty] | CATEGORYB | NONSINGLE | 4284 | 0 | 0 |  | 0 |  | 0 | [5 empty] | WERE | Kelly - Goff 115 kV Rebuild | Tear down and rebuild the 9.6 mile Kelly-Kinghill 115 kV line using single 1192.5 kcmil ACSR conductor. | [12 empty] | 7763570 | 2020-03-04 | [39 empty] | 2024-06-01 | 2024-06-01
2019-AG2 | KELLY 3 - GOFF 3 - 1 | S | WERE | WERE |  |  | 0 | 533331 | GOFF 3 | 533217 | KELLY 3 | 0 |  | 1 | 30SP | 86 | 92 | 0 | 95.4 | 67.4389 | 104.1 | [7 empty] | CATEGORYB | NONSINGLE | 4284 | 0 | 0 |  | 0 |  | 0 | [5 empty] | WERE | Kelly - Goff 115 kV Rebuild | Tear down and rebuild the 9.6 mile Kelly-Kinghill 115 kV line using single 1192.5 kcmil ACSR conductor. | [12 empty] | 7763570 | 2020-03-04 | [39 empty] | 2024-06-01 | 2024-06-01
2006-AG1 | KNOBHILL (KNOBHIL4) 138/69/13.2KV TRANSFORMER CKT 1 | U | OKGE |  |  |  | 1 | 514795 | KNOBHIL4 138 | 514794 | KNOBHIL269.0 | 515732 | KNOBHIL113.2 | 1 | [15 empty] | BASECASE | BASE CASE | [8 empty] | Credit Flowgate |  |  | OKGE | KNOBHILL 138/69KV TRANSFORMER CKT 1 | Replace bus tie with 100MVA transformer | [53 empty] | 2006-06-01 | 2008-06-01
2019-AG2 | L GROVE3 - KERR GR3 - 1 | S | GRDA | AEPW |  |  | 0 | 512634 | KERR GR3 | 510423 | L GROVE3 | 0 |  | 1 | 22SP | 140 | 140 | 0 | 97 | 70.6362 | 100.8 | [7 empty] | CATEGORYB | SINGLE | INOLATP4 - CATOOSA4 - 1 | 0 | 509752 | INOLATP4 | 509790 | CATOOSA4 | 0 |  | 1 |  |  |  | AEPW | Locust Grove - Kerr 115 kV Rebuild | Rebuild 115 kV line from Locust Grove - Kerr | [12 empty] | 3000000 | 2020-03-04 | [39 empty] | 2022-06-01 | 2022-12-01
2019-AG2 | L GROVE3 - KERR GR3 - 1 | S | GRDA | AEPW |  |  | 0 | 512634 | KERR GR3 | 510423 | L GROVE3 | 0 |  | 1 | 25SP | 140 | 140 | 0 | 97.1 | 70.7994 | 101 | [7 empty] | CATEGORYB | SINGLE | INOLATP4 - CATOOSA4 - 1 | 0 | 509752 | INOLATP4 | 509790 | CATOOSA4 | 0 |  | 1 |  |  |  | AEPW | Locust Grove - Kerr 115 kV Rebuild | Rebuild 115 kV line from Locust Grove - Kerr | [12 empty] | 3000000 | 2020-03-04 | [39 empty] | 2022-06-01 | 2022-12-01
2019-AG2 | L GROVE3 - KERR GR3 - 1 | S | GRDA | AEPW |  |  | 0 | 512634 | KERR GR3 | 510423 | L GROVE3 | 0 |  | 1 | 30SP | 140 | 140 | 0 | 98.1 | 72.7185 | 102.5 | [7 empty] | CATEGORYB | SINGLE | INOLATP4 - CATOOSA4 - 1 | 0 | 509752 | INOLATP4 | 509790 | CATOOSA4 | 0 |  | 1 |  |  |  | AEPW | Locust Grove - Kerr 115 kV Rebuild | Rebuild 115 kV line from Locust Grove - Kerr | [12 empty] | 3000000 | 2020-03-04 | [39 empty] | 2022-06-01 | 2022-12-01
NA | LACYGNE - WEST GARDNER 345KV CKT 1 | U | KACP | KACP |  |  | 0 | 542981 | LACYGNE7 | 542965 | W.GRDNR7 | 0 |  | 1 | [15 empty] | BASECASE | BASE CASE | [8 empty] | Credit Flowgate |  |  | KACP | LACYGNE - WEST GARDNER 345KV CKT 1 | KCPL Sponsored Project to Reconductor Line to be In-Service by 6/1/2006 | [53 empty] | 2006-06-01 | 2006-06-01
GI | Lake Creek - Lone Wolf 69kV Ckt 1 | U | WFEC | WFEC |  |  |  | 520982 |  | 520978 |  |  |  | 1 | [15 empty] | BASECASE | BASE CASE | [8 empty] | Credit Flowgate |  |  | WFEC | Lake Creek - Lone Wolf 69kV Ckt 1 Current Transformers | Replace current transformers at Lake Creek and Lone Wolf substation | [53 empty] | 2015-08-08 | 2015-08-08
2019-AG2 | LYDIA 7 345.0 | S | AEPW |  |  |  |  | 508298 | LYDIA 7 | [5 empty] | 25LP | [9 empty] | 0.94596 | 0.99811 | 0.95 | 1.05 | CATEGORYA | BASECASE | BASE CASE | 0 | 510911 | VALIANT7 345.00 | 508298 | LYDIA 7 345.00 | 0 |  | 1 |  |  |  | AEPW | Valliant 130 MVAR Capacitance | Add new 130 MVAR cap bank at Valliant 345kV | [12 empty] | 7500000 | 2020-03-04 | [39 empty] | 2022-04-01 | 2022-12-01
GI | LYONS - WHEATLAND 115KV CKT 1 #2 | U | WERE | WERE |  |  | 0 | 530620 | LYONS 3 115.00 | 533439 | WHEATLD3 115.00 | 0 |  | 1 | [15 empty] | BASECASE | BASE CASE | [8 empty] | Credit Flowgate |  |  | WERE | Wheatland 115 kV #2 | Install metering equipment at the Wheatland 115 kV substation for Lincoln Co. | [13 empty] | 2011-12-27 | [39 empty] | 2012-12-31 | 2012-12-31
GEN-2006-010 | MANDEVILTP4 - SE TEXARKANA 138KV CKT 1 | U | AEPW | AEPW | SARK | TEXARK | 0 | 508105 | MANDEVILTP4 | 508078 | SETEXAR4 138.00 | 0 |  | 1 | [15 empty] | BASECASE | BASE CASE | [8 empty] | Credit Flowgate |  |  | AEPW | MANDEVILTP4 - SE TEXARKANA 138KV CKT 1 | Build new Turk-SE Texarkana 138 kV line and add SE Texarkana 138 kV terminal. | [53 empty] | 2012-07-01 | 2012-07-01
GEN-2006-010 | MANDEVILTP4 - TURK 138KV CKT 1 | U | AEPW | AEPW | SARK | TEXARK | 0 | 507454 | TURK 4 138.00 | 508105 | MANDEVILTP4 | 0 |  | 1 | [15 empty] | BASECASE | BASE CASE | [8 empty] | Credit Flowgate |  |  | AEPW | MANDEVILTP4 - TURK 138KV CKT 1 | Build new Turk-SE Texarkana 138 kV line and add SE Texarkana 138 kV terminal. | [53 empty] | 2012-07-01 | 2012-07-01
2019-AG2 | MARSHAL3 - SMITTYV3 - 1 | EXP | WERE | WERE |  |  | 0 | 533303 | MARSHAL3 | 533338 | SMITTYV3 | 0 |  | 1 | 21LP | 86 | 92 | 0 | 99 | 4.031e-12 | 101.6 | [7 empty] | CATEGORYB | SINGLE | HARBINE7 - STEELEC7 - 1 | 0 | 640208 | HARBINE7 | 640426 | STEELEC7 | 0 |  | 1 |  |  |  | WERE | Marshall County - Smittyville 115kV Rebuild | Rebuild 115kV line from Marshall County - Smittyville | [12 empty] | 2618506 | 2019-05-08 | [39 empty] | 2021-04-01 | 2022-06-01
NA | MATHEWSON - NORTHWEST 345KV CKT 1 | U | OKGE | OKGE | ENID | ENID | 0 | 514880 |  | 515497 |  |  |  | 1 | [15 empty] | BASECASE | BASE CASE | [8 empty] | Credit Flowgate |  |  | OKGE | MATHEWSON - NORTHWEST 345KV CKT 1 | Build 345 kV line | [53 empty] | 2010-01-01 | 2010-01-01
NA | MATHEWSON - TATONGA 345KV CKT 1 | U | OKGE | OKGE | ENID | ENID | 0 | 515497 |  | 515407 |  |  |  | 1 | [15 empty] | BASECASE | BASE CASE | [8 empty] | Credit Flowgate |  |  | OKGE | MATHEWSON - TATONGA 345KV CKT 1 | Build 345 kV line | [53 empty] | 2010-01-01 | 2010-01-01
GI | MAURINE - NEWELL 115 kV CKT 1 | U | WAPA | WAPA |  |  | 0 | 652480 | MAURINE7 115.00 | 652483 | NEWELL 7 115.00 | 0 |  | 1 | [15 empty] | BASECASE | BASE CASE | [8 empty] | Credit Flowgate |  |  | WAPA | Maurine - Newell 115 kV Ckt 1 | Replace thirty-five (35) 115 kV transmission structures. | [53 empty] | 2020-02-28 | 2020-02-28
GI | MCNAB REC - TURK 115KV CKT 1 | U | AEPW | AEPW | SARK | SARKAECC | 0 | 507456 | HEMPSTD3 115.00 | 504122 | MCNAB 3 115.00 |  |  | 1 | [15 empty] | BASECASE | BASE CASE | [8 empty] | Credit Flowgate |  |  | AEPW | MCNAB REC - Turk 115KV CKT 1 #2 (AEP) | Build a new two mile, 138kV, 1590 ACSR line section (operated at 115kV) from Turk Substation to the existing Okay-Hope 115kV line to form a Turk - Hope 115kV line. | [13 empty] | 2007-10-01 | [39 empty] | 2011-12-01 | 2011-12-01
2019-AG2 | MTRIVER4 138.0 | S | WFEC |  |  |  |  | 521004 | MTRIVER4 | [5 empty] | 25LP | [9 empty] | 0.9431 | 0.99649 | 0.95 | 1.05 | CATEGORYA | BASECASE | BASE CASE | 0 | 520823 | HOCHJCT4 138.00 | 521004 | MTRIVER4 138.00 | 0 |  | 1 |  |  |  | AEPW | Valliant 130 MVAR Capacitance | Add new 130 MVAR cap bank at Valliant 345kV | [12 empty] | 7500000 | 2020-03-04 | [39 empty] | 2022-04-01 | 2022-12-01
GI | NELIGH - PETERSBURG 115KV CKT 1 | U | NPPD | NPPD | NPPD_686 | NPPD_686 | 0 | 640444 |  | 640293 | NELIGH 7 115.00 | 0 |  | 1 | [15 empty] | BASECASE | BASE CASE | [8 empty] | Credit Flowgate |  |  | NPPD | Neligh - Petersburg North 115kV Ckt 1 | Replace Breaker 1106, jumpers, & 115kV Switch 1106-D2; Replace Petersburg 115kV Substation main bus; Upgrade and replace transmission structures on 115kV lines TL1168 A & B to facilitate 100 degrees Centigrade line operation | [13 empty] | 2011-01-01 | [39 empty] | 2012-12-31 | 2012-12-31
GI | NELIGH EAST - COUNTY LINE 115KV CKT 1 | U | NPPD | NPPD | NPPD_686 | NPPD_686 | 0 | 640521 | NELIGH.EAST7 | 640115 | CO.LINE7 | 0 |  | 1 | [15 empty] | BASECASE | BASE CASE | [8 empty] | Credit Flowgate |  |  | NPPD | Antelope - County Line - 115kV Rebuild | Rebuild/Upgrade the Antelope ΓÇô County Line 115kV to rerate line segments to greater than 125 MVA. | [53 empty] | 2017-05-01 | 2017-05-01
2007-AG1 | NEOSHO - NORTHEAST PARSONS 138KV CKT 1 | U | WERE | WERE |  |  | 0 | 533022 | NEOSHO 4 | 533005 | NEPARSN4 | 0 |  | 1 | [15 empty] | BASECASE | BASE CASE | [8 empty] | Credit Flowgate |  |  | WERE | NEOSHO - NORTHEAST PARSONS 138KV CKT 1 | Replace bus and Jumpers at NE Parsons 138 kV substation | [53 empty] | 2011-06-01 | 2011-06-01
2019-AG1 | Neosho - Riverton 161kV Line Rebuild (EMDE) | U | EMDE | WERE |  |  | 0 | 532937 | NEOSHO 5 | 547469 | RIV4525 | 0 |  | 1 | [15 empty] | BASECASE | BASE CASE | [8 empty] | Credit Flowgate |  |  | EMDE | Neosho - Riverton 161kV Line Rebuild (EMDE) | Rebuild 28.41 miles of 161kV line from Neosho to Riverton and upgrade any necessary terminal equipment | [13 empty] | 2023-10-01 | [39 empty] | 2023-10-01 | 2023-10-01
2019-AG1 | Neosho - Riverton 161kV Line Rebuild (WERE) | U | EMDE | WERE |  |  | 0 | 532937 | NEOSHO 5 | 547469 | RIV4525 | 0 |  | 1 | [15 empty] | BASECASE | BASE CASE | [8 empty] | Credit Flowgate |  |  | WERE | Neosho - Riverton 161kV Line Rebuild (WERE) | Rebuild 2.44 miles of Neosho-Riverton 161kV line using bundled 1590 Lapwing ACSR and OPGW. Remove the wavetrap. | [13 empty] | 2023-10-01 | [39 empty] | 2023-10-01 | 2023-10-01
GI | North Ft. Dodge - Spearville 115 kV Ckt 2 | U | MKEC | MKEC |  |  | 0 | 539771 |  | 539759 |  |  |  | 1 | [15 empty] | BASECASE | BASE CASE | [8 empty] | Credit Flowgate |  |  | MKEC | North Ft. Dodge - Spearville 115kV Ckt 2 | Build appoximately 20 mile 115 kV line | [53 empty] | 2015-05-01 | 2015-05-01
GI | OKAY - TURK 138KV CKT 1 | U | AEPW | AEPW | SARK | SARK | 0 | 507454 | HEMPSTD4 138.00 | 507428 | OKAY 4 138.00 | 0 |  | 1 | [15 empty] | BASECASE | BASE CASE | [8 empty] | Credit Flowgate |  |  | AEPW | OKAY - TURK 138KV CKT 1 | Build a new two mile, 138kV, 1590 ACSR line section from Turk Substation to the existing Okay-Hope 115kV line and rebuild twelve miles of 115kV line to Okay Substation to 138kV, 1590 ACSR, to form a Turk - Okay 138kV line. | [13 empty] | 2007-10-01 | [39 empty] | 2011-12-01 | 2011-12-01
GI | OKAY 138/69KV TRANSFORMER CKT 1 | U | AEPW | AEPW | SARK | SARK | 1 | 507428 | OKAY 4 138.00 | 507427 | OKAY 2 69.000 | 507442 |  | 1 | [15 empty] | BASECASE | BASE CASE | [8 empty] | Credit Flowgate |  |  | AEPW | OKAY 138/69KV TRANSFORMER CKT 1 | Replace three single-phase 115-69kV autotransformers with one 90 MVA, three-phase 138-69kV autotransformer and convert high side of station to 138kV. | [13 empty] | 2007-10-01 | [39 empty] | 2011-12-01 | 2011-12-01
GI | Osage - Shidler 138kV | U |  |  |  |  | 0 | 301369 |  | 510403 |  |  |  | 1 | [15 empty] | BASECASE | BASE CASE | [8 empty] | Credit Flowgate |  |  | AEPW | Osage - Shidler 138kV | Osage Substation:Replace Shidler 138kV line terminal primary and redundant relaying with SEL uProcessor based relays, install 3-138kV PTs, Install 1-138kV CB, Install metering, Install 2000A line Trap | [13 empty] | 2012-01-15 | [39 empty] | 2014-01-15 | 2014-01-15
GI | Pawnee 138 kV | U |  |  |  |  | 0 | 300139 |  | 512749 |  |  |  | 1 | [15 empty] | BASECASE | BASE CASE | [8 empty] | Credit Flowgate |  |  | GRDA | Pawnee 138 kV | New three breaker ring bus on the Cleveland-Stillwater 138kV line near Pawnee. Station will have terminals to Cleveland, Stillwater, and Fairfax. | [13 empty] | 2011-06-15 | [39 empty] | 2014-06-30 | 2014-06-30
GI | RENFROW - RENFROW TAP 138KV | U | OKGE | WFEC |  |  | 0 | 515544 | RENFROW4 138.00 | 520409 | RENFROW4 138.00 | 0 |  | 1 | [15 empty] | BASECASE | BASE CASE | [8 empty] | Credit Flowgate |  |  | WFEC | Renfrow-Renfrow Tap 138kV Ckt 1 | Replace terminal equipment. | [53 empty] | 2017-09-25 | 2017-09-25
GI | Rice - Circle 230 kV Ckt 1 (MIDW portion) | U | WERE | MIDW |  |  | 0 | 530686 | RICECO 230.00 | 532871 | CIRCLE 6 230.00 | 0 |  | 1 | [15 empty] | BASECASE | BASE CASE | [8 empty] | Credit Flowgate |  |  | MIDW | Rice - Circle 230 kV Ckt 1 (MIDW portion) | ALL WORK REQUIRED TO CONVERT RICE - CIRCLE 115KV TO 230KV OPERATION. INCLUDES NEW 230KV 3 BREAKER RING BUS, AN EXTENSION OF THE 230KV FROM CURRENT RICE STATION TO NEW RICE SUBSTATION, AND ANY ADDITIONAL WORK REQUIRED FOR THE CONVERSION. | [13 empty] | 2011-12-27 | [39 empty] | 2012-11-07 | 2012-11-07
GI | Rice - Circle 230 kV Ckt 1 (WR portion) | U | WERE | MIDW |  |  | 0 | 530686 | RICECO 230.00 | 532871 | CIRCLE 6 230.00 | 0 |  | 1 | [15 empty] | BASECASE | BASE CASE | [8 empty] | Credit Flowgate |  |  | MIDW | Rice - Circle 230 kV Ckt 1 (WR portion) | Install necessary equipment and perform line work at Circle substation to accommodate new bus position. | [13 empty] | 2012-01-15 | [39 empty] | 2012-11-29 | 2012-11-29
GI | Rice - Lyons 115 kV Ckt 1 | U | MIDW | WERE |  |  | 0 | 530623 | RICE 3 115.00 | 530620 | LYONS 3 115.00 | 0 |  | 1 | [15 empty] | BASECASE | BASE CASE | [8 empty] | Credit Flowgate |  |  | MIDW | Rice - Lyons 115 kV Ckt 1 | Rebuild and extend 115 kV transmission line from existing Rice Co. substation to new Rice Co. substation, including engineering, surveying, and modification of existing easements as required. | [13 empty] | 2011-12-27 | [39 empty] | 2013-04-01 | 2013-04-01
GI | Rice County 230/115 kV transformer Ckt 1 | U | MIDW | MIDW |  |  | 1 | 530686 | RICECO 230.00 | 530623 | RICE 3 115.00 | 530687 |  | 1 | [15 empty] | BASECASE | BASE CASE | [8 empty] | Credit Flowgate |  |  | MIDW | Rice County 230/115 kV transformer Ckt 1 | Install 230/115 kV transformer at Rice County. | [13 empty] | 2011-12-27 | [39 empty] | 2012-10-01 | 2012-10-01
2007-AG3 | RIVER ROAD - SAWYER 115KV CKT 1 | U | MKEC | MKEC |  |  | 0 | 539649 | SAWYER 3 115.00 | 539651 | RVROAD 115.00 | 0 |  | 1 | [15 empty] | BASECASE | BASE CASE | [8 empty] | Credit Flowgate |  |  | MKEC | RIVER ROAD - SAWYER 115KV CKT 1 | Rebuild line | [53 empty] | 2009-12-01 | 2013-06-01
2019-AG2 | SAWYER 2 69.0 | S | AEPW |  |  |  |  | 510920 | SAWYER 2 | [5 empty] | 25LP | [9 empty] | 0.89984 | 1.0041 | 0.92 | 1.05 | CATEGORYB | NONSINGLE | 87311 | 0 | 0 |  | 0 |  | 0 | [5 empty] | AEPW | Valliant 130 MVAR Capacitance | Add new 130 MVAR cap bank at Valliant 345kV | [12 empty] | 7500000 | 2020-03-04 | [39 empty] | 2022-04-01 | 2022-12-01
GI | Shidler 138 kV | U |  |  |  |  | 0 | 301369 |  | 510403 |  |  |  | 1 | [15 empty] | BASECASE | BASE CASE | [8 empty] | Credit Flowgate |  |  | AEPW | Shidler 138 kV | [14 empty] | 2011-07-28 | [39 empty] | 2014-02-08 | 2014-02-08
GI | Spearville 345/115 kV Transfomer CKT 1 | U | MKEC | MKEC |  |  | 1 | 539759 |  | 531469 |  | 539960 |  | 1 | [15 empty] | BASECASE | BASE CASE | [8 empty] | Credit Flowgate |  |  | MKEC | Spearville 345/115 kV Transformer CKT 1 | Spearville Substation - Add 345/115kV autotransformer and 345kV and 115kV terminal positions for autotransformer. Needed as Network Upgrade for Gray Co but cost shared with Ford Co. - Update! Ford Co withdrawn, sole cost to Gray Co. | [53 empty] | 2015-05-01 | 2015-05-01
GI | SPSSPPTIES | U |  |  |  |  | 0 | 525832 | TUCO | 511456 | OKLAUNION | 0 |  | 1 | [15 empty] | BASECASE | BASE CASE | [8 empty] | Credit Flowgate |  |  | SPS | Power System Stabilizers in SPS | Install Power System Stabilizers (PSS) at Tolk (Units: 1,2) and Jones (Units: 1,2,3). Costs allocated to ASGI-2011-004, Lubbock, Quay Co, & Denver City. | [53 empty] | 2014-11-30 | 2014-11-30
GI | STLN-DEMARCO - WHEELER 230 kV CKT 1 | U | SPS | SPS |  |  | 0 | 523779 | STLN-DEMARC6 230.0 | 523777 | WHEELER 6230.00 | 0 |  | 1 | [15 empty] | BASECASE | BASE CASE | [8 empty] | Credit Flowgate |  |  | SPS | DEMARCO - WHEELER 230KV CKT 1 | Replace terminal equipment. | [53 empty] | 2020-12-07 | 2020-12-07
2005-AG2 | STRAIGHT ROAD TAP - EXPLORER TAP 138KV CKT 1 | U | OKGE | OKGE |  |  | 0 | 515944 | STRRDTP4 138.00 | 515153 | COLEMNT4 138 | 0 |  | 1 | [15 empty] | BASECASE | BASE CASE | [8 empty] | Credit Flowgate |  |  | OKGE | STRAIGHT ROAD TAP - EXPLORER TAP 138KV CKT 1 | Upgrade terminal equipment. | [53 empty] | 2006-06-01 | 2006-06-01
2005-AG2 | SUB 110 - ORONOGO JCT. - SUB 167 - RIVERTON 161KV CKT 1 | U | EMDE | EMDE |  |  | 0 | 547469 | RIV167 5 161 | 547467 | ORO110 5 161 | 0 |  | 1 | [15 empty] | BASECASE | BASE CASE | [8 empty] | Credit Flowgate |  |  | EMDE | SUB 110 - ORONOGO JCT. - SUB 452 - RIVERTON 161KV CKT 1 | Reconductor Oronogo 59467 to Riverton 59469 with Bundled 556 ACSR | [53 empty] | 2011-06-01 | 2011-06-01
GI | SUGAR HILL - TURK 138KV CKT 1 | U | AEPW | AEPW | SARK | TEXARK | 0 | 507454 | HEMPSTD4 138.00 | 508080 | SUGARHL4 138.00 | 0 |  | 1 | [15 empty] | BASECASE | BASE CASE | [8 empty] | Credit Flowgate |  |  | AEPW | SUGAR HILL - TURK 138KV CKT 1 | Build new 24 mile Turk - Sugar Hill 138 kV line and add Sugar Hill 138 kV terminal. | [13 empty] | 2007-10-01 | [39 empty] | 2010-12-16 | 2010-12-16
GI | Sunnyside to tap on Pooleville - Ratliff 138kV Ckt 1 | U |  |  |  |  | 0 | 515561 |  | 515135 |  |  |  | 1 | [15 empty] | BASECASE | BASE CASE | [8 empty] | Credit Flowgate |  |  | OKGE | Carter County - Sunnyside 138kV Ckt 1 | Rebuild 0.75 mi of 138kV Transmission Line DBL CKT | [53 empty] | 2014-06-01 | 2014-06-01
GI | SWEETWATER - STLN-DEMARCO 230 kV CKT 1 | U | AEPW | SPS |  |  | 0 | 511541 | SWEETWT6 230.00 | 523779 | STLN-DEMARC6 230.0 | 0 |  | 1 | [15 empty] | BASECASE | BASE CASE | [8 empty] | Credit Flowgate |  |  | AEPW | SWEETWATER - DEMARCO 230KV CKT 1 | Rebuild ~5 miles of 230kV and replace terminal equipment to achieve 1150 amps (458 MVA). | [53 empty] | 2020-12-07 | 2020-12-07
GI | TATONGA - MATTHEWSON 345KV CKT 1 | U | OKGE | OKGE |  |  | 0 | 515407 | TATONGA7 345.00 | 515497 | MATHWSON7 345.00 | 0 |  | 1 | [15 empty] | BASECASE | BASE CASE | [8 empty] | Credit Flowgate |  |  | OKGE | Woodward EHV 138kV Phase Shifting Transformer circuit #1 | Install one (1) 138 kV phase shifting transformer along with upgrading relay, protective, and metering equipment, and all associated and miscellaneous materials. | [53 empty] | 2017-08-02 | 2017-08-02
NA | TATONGA - WOODWARD 345KV CKT 1 | U | OKGE | OKGE | ENID | ENID | 0 | 515407 |  | 515375 |  |  |  | 1 | [15 empty] | BASECASE | BASE CASE | [8 empty] | Credit Flowgate |  |  | OKGE | TATONGA - WOODWARD 345KV CKT 1 | Build 345 kV line | [53 empty] | 2010-01-01 | 2010-01-01
GI | TOLK EAST - PLANT X 230KV CKT 1 | U | SPS | SPS |  |  | 0 | 525524 | TOLK_EAST 6230.00 | 525481 | PLANT_X 6230.00 | 0 |  | 2 | [15 empty] | BASECASE | BASE CASE | [8 empty] | Credit Flowgate |  |  | SPS | Plant X - Tolk 230kV rebuild circuit #2 | Rebuild Plant X – Tolk 230kV transmission circuit #2 which is approximately 10 miles in length. The existing 795 MCM ACSR conductor will be replaced with 995 MCM ACCS conductor along with upgrading associated disconnect switches, structural steel, foundat | [53 empty] | 2017-12-31 | 2017-12-31
GI | TOLK WEST - PLANT X 230KV CKT 1 | U | SPS | SPS |  |  | 0 | 525531 | TOLK_WEST 6230.00 | 525481 | PLANT_X 6230.00 | 0 |  | 1 | [15 empty] | BASECASE | BASE CASE | [8 empty] | Credit Flowgate |  |  | SPS | Plant X - Tolk 230kV rebuild circuit #1 | Rebuild Plant X – Tolk 230kV transmission circuit #1 which is approximately 10 miles in length. The existing 795 MCM ACSR conductor will be replaced with 995 MCM ACCS conductor along with upgrading associated disconnect switches, structural steel, foundat | [53 empty] | 2017-12-31 | 2017-12-31
GI | TUCO INTERCHANGE 345/230KV TRANSFORMER CKT 1 | U | SPS | SPS |  |  | 1 | 525832 | TUCO_INT 7345.00 | 525830 | TUCO_INT 6230.00 | 525824 | TUCO_TR 113.200 | 1 | [15 empty] | BASECASE | BASE CASE | [8 empty] | Credit Flowgate |  |  | SPS | TUCO Interchange 345/230kV CKT 1 Replacement | The existing 345/230kV 560/560MVA autotransformer at Tuco Substation will be replaced with a new transformer unit to match the other transformer at this site. The new transformer can be installed at Tuco Substation by removing the existing transformer fro | [53 empty] | 2018-06-01 | 2018-06-01
2019-AG2 | TUPELO 4 - STNWLSW4 - 1 | S | WFEC | SWPA |  |  | 0 | 521071 | STNWLSW4 | 505600 | TUPELO 4 | 0 |  | 1 | 22LP | 145 | 169 | 0 |  | 66.3295 | 100.4 | [7 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 | [5 empty] | WFEC | Tupelo - Stonewall 138 kV Rebuild and Terminal Equipment Upgrades | Upgrade Switch #31 and #33 at Tupelo Switch, upgrade 1.2 miles of 477 conductor from Tupelo - Stonewall 138 kV | [12 empty] | 700000 | 2020-03-09 | [39 empty] | 2022-04-01 | 2022-06-01
2019-AG2 | TUPELO 4 - STNWLSW4 - 1 | S | WFEC | SWPA |  |  | 0 | 521071 | STNWLSW4 | 505600 | TUPELO 4 | 0 |  | 1 | 25LP | 145 | 169 | 0 |  | 66.8549 | 101.5 | [7 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 | [5 empty] | WFEC | Tupelo - Stonewall 138 kV Rebuild and Terminal Equipment Upgrades | Upgrade Switch #31 and #33 at Tupelo Switch, upgrade 1.2 miles of 477 conductor from Tupelo - Stonewall 138 kV | [12 empty] | 700000 | 2020-03-09 | [39 empty] | 2022-04-01 | 2022-06-01
GI | TURK 138/115KV TRANSFORMER CKT 1 | U | AEPW |  | SARK |  | 1 | 507454 | HEMPSTD4 138.00 | 507456 | HEMPSTD3 115.00 | 507458 | HEMP1 1 13.800 | 1 | [15 empty] | BASECASE | BASE CASE | [8 empty] | Credit Flowgate |  |  | AEPW | TURK 138/115KV TRANSFORMER CKT 1 | Build Turk 138-115 kV station and relocate autotransformer (and spare) from Patterson to this new Turk station | [13 empty] | 2007-10-01 | [39 empty] | 2011-12-01 | 2011-12-01
GI | Twin Church - Dixon County 230kV Line Upgrade | U | NPPD | NPPD |  |  | 0 | 640560 | WAKEFIELD 4 | 640386 | TWIN CH4 |  |  | 1 | [15 empty] | BASECASE | BASE CASE | [8 empty] | Credit Flowgate |  |  | NPPD | Twin Church - Dixon County 230kV Line Upgrade | Increase clearances to accommodate 320MVA facility rating | [53 empty] | 2015-10-24 | 2015-10-24
2019-AG2 | VALIANT4 138.0 | S | AEPW |  |  |  |  | 510918 | VALIANT4 | [5 empty] | 22LP | [9 empty] | 0.89674 | 1.0161 | 0.92 | 1.05 | CATEGORYB | NONSINGLE | 84206 | 0 | 0 |  | 0 |  | 0 | [5 empty] | AEPW | Valliant 130 MVAR Capacitance | Add new 130 MVAR cap bank at Valliant 345kV | [12 empty] | 7500000 | 2020-03-04 | [39 empty] | 2022-04-01 | 2022-12-01
2019-AG2 | VALIANT7 345.0 | S | AEPW |  |  |  |  | 510911 | VALIANT7 | [5 empty] | 22LP | [9 empty] | 0.88047 | 1.0013 | 0.92 | 1.05 | CATEGORYB | NONSINGLE | 84206 | 0 | 0 |  | 0 |  | 0 | [5 empty] | AEPW | Valliant 130 MVAR Capacitance | Add new 130 MVAR cap bank at Valliant 345kV | [12 empty] | 7500000 | 2020-03-04 | [39 empty] | 2022-04-01 | 2022-12-01
2019-AG2 | VALIANT7 345.0 | S | AEPW |  |  |  |  | 510911 | VALIANT7 | [5 empty] | 25LP | [9 empty] | 0.88626 | 0.99872 | 0.92 | 1.05 | CATEGORYB | NONSINGLE | 84206 | 0 | 0 |  | 0 |  | 0 | [5 empty] | AEPW | Valliant 130 MVAR Capacitance | Add new 130 MVAR cap bank at Valliant 345kV | [12 empty] | 7500000 | 2020-03-04 | [39 empty] | 2022-04-01 | 2022-12-01
2019-AG2 | VALLANT4 138.0 | S | WFEC |  |  |  |  | 521079 | VALLANT4 | [5 empty] | 25LP | [9 empty] | 0.89533 | 1.0026 | 0.9 | 1.05 | CATEGORYB | NONSINGLE | 87311 | 0 | 0 |  | 0 |  | 0 | [5 empty] | AEPW | Valliant 130 MVAR Capacitance | Add new 130 MVAR cap bank at Valliant 345kV | [12 empty] | 7500000 | 2020-03-04 | [39 empty] | 2022-04-01 | 2022-12-01
2019-AG2 | V-WEYCO4 138.0 | S | AEPW |  |  |  |  | 510866 | V-WEYCO4 | [5 empty] | 22LP | [9 empty] | 0.89304 | 1.0133 | 0.92 | 1.05 | CATEGORYB | NONSINGLE | 87311 | 0 | 0 |  | 0 |  | 0 | [5 empty] | AEPW | Valliant 130 MVAR Capacitance | Add new 130 MVAR cap bank at Valliant 345kV | [12 empty] | 7500000 | 2020-03-04 | [39 empty] | 2022-04-01 | 2022-12-01
2019-AG2 | V-WEYCO4 138.0 | S | AEPW |  |  |  |  | 510866 | V-WEYCO4 | [5 empty] | 25LP | [9 empty] | 0.89895 | 1.0062 | 0.92 | 1.05 | CATEGORYB | NONSINGLE | 84206 | 0 | 0 |  | 0 |  | 0 | [5 empty] | AEPW | Valliant 130 MVAR Capacitance | Add new 130 MVAR cap bank at Valliant 345kV | [12 empty] | 7500000 | 2020-03-04 | [39 empty] | 2022-04-01 | 2022-12-01
2019-AG2 | WAVERLY7 - LACYGNE7 - 1 | S | WERE | KCPL |  |  | 0 | 532799 | WAVERLY7 | 542981 | LACYGNE7 | 0 |  | 1 | 25LP | 1141 | 1195 | 0 |  | 80.961 | 101.3 | [7 empty] | CATEGORYB | SINGLE | NEOSHO 7 - G17-009-TAP - 1 | 0 | 532793 | NEOSHO 7 | 588544 | G17-009-TAP | 0 |  | 1 |  |  |  | WERE | LaCygne 345 kV Terminal Equipment Upgrades | Replace 2 switches, 1 breaker, and 2 breaker panels at LaCygne 345 kV substation | [12 empty] | 800000 | 2020-03-04 | [39 empty] | 2025-04-01 | 2025-04-01
2019-AG2 | WEBBTAP4 - SHIDLER4 - 1 | S | AEPW | AEPW |  |  | 0 | 510376 | WEBBTAP4 | 510403 | SHIDLER4 | 0 |  | 1 | 22LP | 179 | 200 | 0 | 89.7 | 64.2532 | 108.8 | [7 empty] | CATEGORYB | NONSINGLE | 89547 | 0 | 0 |  | 0 |  | 0 | [5 empty] | AEPW | Shidler - Webb Tap 138 kV Rebuild | Rebuild 3 miles of 138 kV line from Shidler - Webb Tap | [12 empty] | 5000000 | 2020-03-05 | [39 empty] | 2022-04-01 | 2022-12-01
2019-AG2 | WEBBTAP4 - SHIDLER4 - 1 | S | AEPW | AEPW |  |  | 0 | 510376 | WEBBTAP4 | 510403 | SHIDLER4 | 0 |  | 1 | 25LP | 179 | 200 | 0 | 90.7 | 64.5507 | 110.9 | [7 empty] | CATEGORYB | NONSINGLE | 89547 | 0 | 0 |  | 0 |  | 0 | [5 empty] | AEPW | Shidler - Webb Tap 138 kV Rebuild | Rebuild 3 miles of 138 kV line from Shidler - Webb Tap | [12 empty] | 5000000 | 2020-03-05 | [39 empty] | 2022-04-01 | 2022-12-01
2019-AG2 | WSBNKTP4 138.0 | S | WFEC |  |  |  |  | 521098 | WSBNKTP4 | [5 empty] | 22LP | [9 empty] | 0.94493 | 1.0059 | 0.95 | 1.05 | CATEGORYA | BASECASE | BASE CASE | 0 | 521077 | UNGER 4 138.00 | 521098 | WSBNKTP4 138.00 | 0 |  | 1 |  |  |  | AEPW | Valliant 130 MVAR Capacitance | Add new 130 MVAR cap bank at Valliant 345kV | [12 empty] | 7500000 | 2020-03-04 | [39 empty] | 2022-04-01 | 2022-12-01
2019-AG2 | WSBNKTP4 138.0 | S | WFEC |  |  |  |  | 521098 | WSBNKTP4 | [5 empty] | 25LP | [9 empty] | 0.93998 | 1.0043 | 0.95 | 1.05 | CATEGORYA | BASECASE | BASE CASE | 0 | 521077 | UNGER 4 138.00 | 521098 | WSBNKTP4 138.00 | 0 |  | 1 |  |  |  | AEPW | Valliant 130 MVAR Capacitance | Add new 130 MVAR cap bank at Valliant 345kV | [12 empty] | 7500000 | 2020-03-04 | [39 empty] | 2022-04-01 | 2022-12-01
2019-AG2 | ERCOTE DC TIE | S | AEPW | ERCOTE |  |  | 0 | 508359 | WELSH 7 | 599892 | EASTDC 7 | 0 |  |  | 20SP | 600 | 600 | 0 | 50 |  | 141.6667 | [7 empty] | CATEGORYA | BASECASE | BASE CASE | [11 empty] | AEPW | ERCOT East DC Tie Upgrade | Add additional 250 MW of capacity at Welsh 345kV DC Tie | [12 empty] | 100000000 | 2020-03-04 | [39 empty] | 2020-06-01 | 2024-06-01
2019-AG2 | MILES CITY DC TIE | S | WAPA | WBDC-WECC |  |  | 0 | 652411 | MI CTYE4 | 652402 | MI CTYW4 | 0 |  |  | 21SP | 200 | 200 | 0 | 70 |  | 122.5 | [7 empty] | CATEGORYA | BASECASE | BASE CASE | [11 empty] | WAPA | Miles City DC Tie Upgrade | Upgrade Miles City DC Tie to achieve additional 45 MW of East to West capacity | [12 empty] | 120000000 | 2020-03-04 | [39 empty] | 2021-06-01 | 2024-12-01

## tblAllFacilityLog<100%
STUDYDES | FacilityName | FacilityUpgradeCode | ModelArea1 | ModelArea2 | FZONENAME | TZONENAME | MONTFLAG | MONTFB | MONTFNAME | MONTTB1 | MONTTNAME1 | MONTTB2 | MONTTNAME2 | MONTCKT | Case | RATEA | RATEB | RATEC | Assessment Loading | BaseCaseLoading | TransferCaseLoading | NameOfBusWithMonitoredVoltage | Assessment Voltage | BaseCaseVoltage | TransferCaseVoltage | VINIT | VMIN | VMAX | CATEGORY | CONTTYPE | CONTNAME | CONTXFMRFLAG | CONTFB | CONTFNAME | CONTTB1 | CONTTNAME1 | CONTTB2 | CONTTNAME2 | CONTCKT | TransmissionProviderCommentsNotes | RequiredRateB | TransmissionOwnerComments | OwnerDesignation | UpgradeName | UpgradeComponentWithinFacility | NewSummerA | NewSummerB | NewOtherA | NewOtherB | DistToConstruct | TotalLead | ConstructionLeadOnly | NewOrConstructWhileEnergized | NewR | NewX | NewB | CommentsRegardingUpgradeRequirements | NewCost | EffDate | NetPlantDate | ReusableEx_GrossValue | ReusableEx_NetValue | Reusable_EndofDepr | SalvageValue | NewCostWhileExpediting | EffDateExpedited | StartDeprExpedited | EndDeprExpedited | NetPlantDateExpedited | ReusableEx_GrossExpedited | ReusableEx_NetExpedited | Reusable_EndofDeprExpedited | SalvageValueExpedited | Generation 1 Owner & Unit (Name) | Generation 1 Redispatch Cost ($) | Generation 1 Redispatch Date (M/D/Y) | Generation 2 Owner & Unit (Name) | Generation 2 Redispatch Cost ($) | Generation 2 Redispatch Date (M/D/Y) | Generation 3 Owner & Unit (Name) | Generation 3 Redispatch Cost ($) | Generation 3 Redispatch Date (M/D/Y) | ActualCompletion | ActualNewCost | ActualNetPlantDate | ActualReusableEx_GrossValue | ActualReusableEx_NetValue | ActualReusable_EndofDepr | ActualSalvageValue | Actual_NewCostWhileExpediting | Actual_StartDeprExp | Actual_EndDeprExp | Actual_NetPlantDateExpedited | ActualReusableEx_GrossExpedited | ActualReusableEx_NetExpedited | ActualReusable_EndofDeprExpedited | Actual_SalvageValueExpedited | SPPReliabilityDate | DUN | EOC | EarliestDate
2019-AG2 | 52DELTP4 - 36LEWIS4 - 1 | E | AEPW | AEPW |  |  | 0 | 509800 | 36LEWIS4 | 509776 | 52DELTP4 | 0 |  | 1 | 21SP | 278 | 278 | 0 | 102.1 | 50.8703 | 99.8 | [7 empty] | CATEGORYB | NONSINGLE | 84123 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | 52DELTP4 - 36LEWIS4 - 1 | E | AEPW | AEPW |  |  | 0 | 509800 | 36LEWIS4 | 509776 | 52DELTP4 | 0 |  | 1 | 25SP | 278 | 278 | 0 | 122.6 | 51.584 | 96.5 | [7 empty] | CATEGORYB | NONSINGLE | 87995 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | 5EVERTON RD - 5ST JOE - 1 | E | EES-EAI | EES-EAI |  |  | 0 | 338108 | 5ST JOE | 338107 | 5EVERTON RD | 0 |  | 1 | 20SP | 223 | 223 | 0 | 97.5 | 74.4068 | 99.1 | [7 empty] | CATEGORYB | NONSINGLE | 104720 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | 5EVERTON RD - 5ST JOE - 1 | E | EES-EAI | EES-EAI |  |  | 0 | 338108 | 5ST JOE | 338107 | 5EVERTON RD | 0 |  | 1 | 20SP | 223 | 223 | 0 | 95.4 | 74.4068 | 96.5 | [7 empty] | CATEGORYB | NONSINGLE | 104731 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | 5EVERTON RD - 5ST JOE - 1 | E | EES-EAI | EES-EAI |  |  | 0 | 338108 | 5ST JOE | 338107 | 5EVERTON RD | 0 |  | 1 | 21SP | 223 | 223 | 0 | 99.5 | 72.4339 | 98.5 | [7 empty] | CATEGORYB | NONSINGLE | 92673 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | 5EVERTON RD - 5ST JOE - 1 | E | EES-EAI | EES-EAI |  |  | 0 | 338108 | 5ST JOE | 338107 | 5EVERTON RD | 0 |  | 1 | 21SP | 223 | 223 | 0 | 98 | 72.4339 | 96.9 | [7 empty] | CATEGORYB | NONSINGLE | 92667 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | 5EVERTON RD - 5ST JOE - 1 | E | EES-EAI | EES-EAI |  |  | 0 | 338108 | 5ST JOE | 338107 | 5EVERTON RD | 0 |  | 1 | 21SP | 223 | 223 | 0 | 97.2 | 72.4339 | 96.3 | [7 empty] | CATEGORYB | NONSINGLE | 92674 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | 5EVERTON RD - 5ST JOE - 1 | E | EES-EAI | EES-EAI |  |  | 0 | 338108 | 5ST JOE | 338107 | 5EVERTON RD | 0 |  | 1 | 22SP | 223 | 223 | 0 |  | 73.9361 | 96.3 | [7 empty] | CATEGORYB | NONSINGLE | 104727 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | 5HARRISON.E! - 5EVERTON RD - 1 | E | EES-EAI | EES-EAI |  |  | 0 | 338107 | 5EVERTON RD | 338104 | 5HARRISON.E! | 0 |  | 1 | 20SP | 223 | 223 | 0 | 96.7 | 72.1658 | 98.4 | [7 empty] | CATEGORYB | NONSINGLE | 92667 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | 5HARRISON.E! - 5EVERTON RD - 1 | E | EES-EAI | EES-EAI |  |  | 0 | 338107 | 5EVERTON RD | 338104 | 5HARRISON.E! | 0 |  | 1 | 20SP | 223 | 223 | 0 | 96 | 72.1658 | 97.7 | [7 empty] | CATEGORYB | NONSINGLE | 92674 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | 5HARRISON.E! - 5EVERTON RD - 1 | E | EES-EAI | EES-EAI |  |  | 0 | 338107 | 5EVERTON RD | 338104 | 5HARRISON.E! | 0 |  | 1 | 21SP | 223 | 223 | 0 | 96.9 | 70.1659 | 95.9 | [7 empty] | CATEGORYB | NONSINGLE | 92673 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | 5MOOREFIELD - 5ISES% - 1 | E | EES-EAI | EES-EAI |  |  | 0 | 338142 | 5ISES% | 338138 | 5MOOREFIELD | 0 |  | 1 | 20SP | 310 | 310 | 0 | 97.6 | 83.2629 | 98.3 | [7 empty] | CATEGORYB | NONSINGLE | 64055 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | 5MOOREFIELD - 5ISES% - 1 | E | EES-EAI | EES-EAI |  |  | 0 | 338142 | 5ISES% | 338138 | 5MOOREFIELD | 0 |  | 1 | 21SP | 310 | 310 | 0 | 98.3 | 82.0831 | 97.8 | [7 empty] | CATEGORYB | NONSINGLE | 92673 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | 5MOOREFIELD - 5ISES% - 1 | E | EES-EAI | EES-EAI |  |  | 0 | 338142 | 5ISES% | 338138 | 5MOOREFIELD | 0 |  | 1 | 21SP | 310 | 310 | 0 | 97 | 82.0831 | 96.4 | [7 empty] | CATEGORYB | NONSINGLE | 92667 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | 5MT HOME - 5SOUTHLAND# - 1 | E | EES-EAI | EES-EAI |  |  | 0 | 338814 | 5SOUTHLAND# | 338125 | 5MT HOME | 0 |  | 1 | 20SP | 162 | 162 | 0 | 98.3 | 72.6544 | 99.9 | [7 empty] | CATEGORYB | SINGLE | 5HARRISON.E! - 5EVERTON RD - 1 | 0 | 338104 | 5HARRISON.E! | 338107 | 5EVERTON RD | 0 |  | 1 | Transfer Loading < 100%
2019-AG2 | 5MT HOME - 5SOUTHLAND# - 1 | E | EES-EAI | EES-EAI |  |  | 0 | 338814 | 5SOUTHLAND# | 338125 | 5MT HOME | 0 |  | 1 | 21SP | 162 | 162 | 0 | 97.1 | 70.9136 | 96 | [7 empty] | CATEGORYB | SINGLE | 5ST JOE - 5HILLTOP% - 1 | 0 | 338108 | 5ST JOE | 338110 | 5HILLTOP% | 0 |  | 1 | Transfer Loading < 100%
2019-AG2 | 5ST JOE - 5HILLTOP% - 1 | E | EES-EAI | EES-EAI |  |  | 0 | 338110 | 5HILLTOP% | 338108 | 5ST JOE | 0 |  | 1 | 20SP | 223 | 223 | 0 | 98.1 | 74.9645 | 99.7 | [7 empty] | CATEGORYB | NONSINGLE | 92340 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | 5ST JOE - 5HILLTOP% - 1 | E | EES-EAI | EES-EAI |  |  | 0 | 338110 | 5HILLTOP% | 338108 | 5ST JOE | 0 |  | 1 | 20SP | 223 | 223 | 0 | 96 | 74.9645 | 97.1 | [7 empty] | CATEGORYB | NONSINGLE | 104731 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | 5ST JOE - 5HILLTOP% - 1 | E | EES-EAI | EES-EAI |  |  | 0 | 338110 | 5HILLTOP% | 338108 | 5ST JOE | 0 |  | 1 | 21SP | 223 | 223 | 0 | 100.2 | 73.0108 | 99.1 | [7 empty] | CATEGORYB | NONSINGLE | 92673 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | 5ST JOE - 5HILLTOP% - 1 | E | EES-EAI | EES-EAI |  |  | 0 | 338110 | 5HILLTOP% | 338108 | 5ST JOE | 0 |  | 1 | 21SP | 223 | 223 | 0 | 98.7 | 73.0108 | 97.5 | [7 empty] | CATEGORYB | NONSINGLE | 92667 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | 5ST JOE - 5HILLTOP% - 1 | E | EES-EAI | EES-EAI |  |  | 0 | 338110 | 5HILLTOP% | 338108 | 5ST JOE | 0 |  | 1 | 21SP | 223 | 223 | 0 | 97.8 | 73.0108 | 96.9 | [7 empty] | CATEGORYB | NONSINGLE | 92674 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | 5ST JOE - 5HILLTOP% - 1 | E | EES-EAI | EES-EAI |  |  | 0 | 338110 | 5HILLTOP% | 338108 | 5ST JOE | 0 |  | 1 | 22SP | 223 | 223 | 0 |  | 74.5082 | 96.9 | [7 empty] | CATEGORYB | NONSINGLE | 104727 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | 5WASHBRN - 2WASHBRN - 1 | E | AECI | AECI |  |  | 0 | 300129 | 5WASHBRN | 300763 | 2WASHBRN | 0 |  | 1 | 22SP | 56 | 56 | 0 | 97.9 | 73.9304 | 97.3 | [7 empty] | CATEGORYB | SINGLE | NEO184 5 - 2NEOSAC - 1 | 0 | 547471 | NEO184 5 | 300748 | 2NEOSAC | 0 |  | 1 | Transfer Loading < 100%
2019-AG2 | 5WASHBRN - 2WASHBRN - 1 | E | AECI | AECI |  |  | 0 | 300129 | 5WASHBRN | 300763 | 2WASHBRN | 0 |  | 1 | 25SP | 56 | 56 | 0 | 99.1 | 75.2008 | 98.5 | [7 empty] | CATEGORYB | SINGLE | NEO184 5 - 2NEOSAC - 1 | 0 | 547471 | NEO184 5 | 300748 | 2NEOSAC | 0 |  | 1 | Transfer Loading < 100%
2019-AG2 | 5WASHBRN - 2WASHBRN - 1 | E | AECI | AECI |  |  | 0 | 300129 | 5WASHBRN | 300763 | 2WASHBRN | 0 |  | 1 | 30SP | 56 | 56 | 0 | 94.2 | 81.1294 | 95.2 | [7 empty] | CATEGORYB | SINGLE | MON383 5 - MON383 2 - 1 | 1 | 547480 | MON383 5 | 547591 | MON383 2 | 547712 | MON383 1 | 1 | Transfer Loading < 100%
2019-AG2 | 7HUBEN - 5HUBEN - 1 | E | AECI | AECI |  |  | 0 | 300042 | 7HUBEN | 300088 | 5HUBEN | 0 |  | 1 | 25SP | 392 | 392 | 0 | 92.6 | 67.6036 | 96.6 | [7 empty] | CATEGORYB | NONSINGLE | 80775 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | 7HUBEN - 5HUBEN - 1 | E | AECI | AECI |  |  | 0 | 300042 | 7HUBEN | 300088 | 5HUBEN | 0 |  | 1 | 25WP | 446 | 446 | 0 | 95.1 | 70.5536 | 98.3 | [7 empty] | CATEGORYB | NONSINGLE | 80792 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | 7HUBEN - 5HUBEN - 1 | E | AECI | AECI |  |  | 0 | 300042 | 7HUBEN | 300088 | 5HUBEN | 0 |  | 1 | 30SP | 392 | 392 | 0 | 95.2 | 68.4017 | 99.8 | [7 empty] | CATEGORYB | NONSINGLE | 80775 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | 7HUBEN - 5HUBEN - 1 | E | AECI | AECI |  |  | 0 | 300042 | 7HUBEN | 300088 | 5HUBEN | 0 |  | 1 | 30WP | 446 | 446 | 0 | 92.5 | 67.6943 | 96.3 | [7 empty] | CATEGORYB | NONSINGLE | 80792 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | 7MCCREDIE - 7MONTGMRY - 1 | E | AMMO | AMMO |  |  | 0 | 345230 | 7MONTGMRY | 345088 | 7MCCREDIE | 0 |  | 1 | 30SP | 998 | 1102 | 0 | 99.8 | 44.7883 | 96.9 | [7 empty] | CATEGORYB | NONSINGLE | 104728 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | AFTON 2 - FAIRTAP2 - 1 | E | GRDA | GRDA |  |  | 0 | 512633 | AFTON 2 | 512708 | FAIRTAP2 | 0 |  | 1 | 20SP | 72 | 72 | 0 | 91.5 | 25.9646 | 95.2 | [7 empty] | CATEGORYB | NONSINGLE | 81781 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | AFTON 2 - FAIRTAP2 - 1 | E | GRDA | GRDA |  |  | 0 | 512633 | AFTON 2 | 512708 | FAIRTAP2 | 0 |  | 1 | 25WP | 72 | 72 | 0 | 94.2 | 28.2433 | 95.6 | [7 empty] | CATEGORYB | NONSINGLE | 81781 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | AINSWND7 - CALAMS 7 - 1 | E | NPPD | NPPD |  |  | 0 | 640096 | CALAMS 7 | 640050 | AINSWND7 | 0 |  | 1 | 25SP | 120 | 120 | 0 |  | 71.1595 | 95.8 | [7 empty] | CATEGORYB | NONSINGLE | 105818 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | AINSWND7 - CALAMS 7 - 1 | E | NPPD | NPPD |  |  | 0 | 640096 | CALAMS 7 | 640050 | AINSWND7 | 0 |  | 1 | 30SP | 120 | 120 | 0 | 92.8 | 73.0316 | 98.5 | [7 empty] | CATEGORYB | NONSINGLE | 105818 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | ARBUCKL4 - MILLCKT4 - 1 | E | OKGE | OKGE |  |  | 0 | 515117 | ARBUCKL4 | 515121 | MILLCKT4 | 0 |  | 1 | 22LP | 191 | 191 | 0 |  | 3.6207 | 98.3 | [7 empty] | CATEGORYB | NONSINGLE | 87626 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | ARBUCKL4 - MILLCKT4 - 1 | E | OKGE | OKGE |  |  | 0 | 515117 | ARBUCKL4 | 515121 | MILLCKT4 | 0 |  | 1 | 25LP | 191 | 191 | 0 |  | 3.984 | 96.3 | [7 empty] | CATEGORYB | NONSINGLE | 84226 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | ARCHIE 5 - S.HARP 5 - 1 | E | KCPL | KCPL |  |  | 0 | 541341 | S.HARP 5 | 541207 | ARCHIE 5 | 0 |  | 1 | 22SP | 228 | 234 | 0 | 81.3 | 50.354 | 97.3 | [7 empty] | CATEGORYB | NONSINGLE | 104507 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | ASB349 5 - CJ 366 5 - 1 | E | EMDE | EMDE |  |  | 0 | 547476 | ASB349 5 | 547477 | CJ 366 5 | 0 |  | 1 | 21WP | 223 | 223 | 0 |  | 39.9869 | 99.6 | [7 empty] | CATEGORYB | SINGLE | ASB349 5 - PUR421 5 - 1 | 0 | 547476 | ASB349 5 | 547491 | PUR421 5 | 0 |  | 1 | Transfer Loading < 100%
2019-AG2 | ASB349 5 - CJ 366 5 - 1 | E | EMDE | EMDE |  |  | 0 | 547476 | ASB349 5 | 547477 | CJ 366 5 | 0 |  | 1 | 21WP | 223 | 223 | 0 | 77.3 | 39.9869 | 99.5 | [7 empty] | CATEGORYB | NONSINGLE | 103734 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | ASB349 5 - CJ 366 5 - 1 | E | EMDE | EMDE |  |  | 0 | 547476 | ASB349 5 | 547477 | CJ 366 5 | 0 |  | 1 | 21WP | 223 | 223 | 0 | 77.2 | 39.9869 | 99.4 | [7 empty] | CATEGORYB | NONSINGLE | 3672 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | ASB349 5 - CJ 366 5 - 1 | E | EMDE | EMDE |  |  | 0 | 547476 | ASB349 5 | 547477 | CJ 366 5 | 0 |  | 1 | 22WP | 223 | 223 | 0 |  | 39.7107 | 99.3 | [7 empty] | CATEGORYB | SINGLE | ASB349 5 - PUR421 5 - 1 | 0 | 547476 | ASB349 5 | 547491 | PUR421 5 | 0 |  | 1 | Transfer Loading < 100%
2019-AG2 | ASB349 5 - CJ 366 5 - 1 | E | EMDE | EMDE |  |  | 0 | 547476 | ASB349 5 | 547477 | CJ 366 5 | 0 |  | 1 | 22WP | 223 | 223 | 0 | 76.9 | 39.7107 | 99.2 | [7 empty] | CATEGORYB | NONSINGLE | 103734 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | ASB349 5 - CJ 366 5 - 1 | E | EMDE | EMDE |  |  | 0 | 547476 | ASB349 5 | 547477 | CJ 366 5 | 0 |  | 1 | 22WP | 223 | 223 | 0 | 76.8 | 39.7107 | 99.1 | [7 empty] | CATEGORYB | NONSINGLE | 3672 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | ASB349 5 - CJ 366 5 - 1 | E | EMDE | EMDE |  |  | 0 | 547476 | ASB349 5 | 547477 | CJ 366 5 | 0 |  | 1 | 25WP | 223 | 223 | 0 |  | 37.3766 | 95.4 | [7 empty] | CATEGORYB | SINGLE | ASB349 5 - PUR421 5 - 1 | 0 | 547476 | ASB349 5 | 547491 | PUR421 5 | 0 |  | 1 | Transfer Loading < 100%
2019-AG2 | ASB349 5 - CJ 366 5 - 1 | E | EMDE | EMDE |  |  | 0 | 547476 | ASB349 5 | 547477 | CJ 366 5 | 0 |  | 1 | 25WP | 223 | 223 | 0 | 74 | 37.3766 | 95.3 | [7 empty] | CATEGORYB | NONSINGLE | 103734 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | ASB349 5 - CJ 366 5 - 1 | E | EMDE | EMDE |  |  | 0 | 547476 | ASB349 5 | 547477 | CJ 366 5 | 0 |  | 1 | 25WP | 223 | 223 | 0 | 73.9 | 37.3766 | 95.2 | [7 empty] | CATEGORYB | NONSINGLE | 3672 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | ASB349 5 - PUR421 5 - 1 | E | EMDE | EMDE |  |  | 0 | 547476 | ASB349 5 | 547491 | PUR421 5 | 0 |  | 1 | 21WP | 223 | 223 | 0 | 78.5 | 52.1792 | 99.4 | [7 empty] | CATEGORYB | NONSINGLE | 3671 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | ASB349 5 - PUR421 5 - 1 | E | EMDE | EMDE |  |  | 0 | 547476 | ASB349 5 | 547491 | PUR421 5 | 0 |  | 1 | 21WP | 223 | 223 | 0 |  | 52.1792 | 99.3 | [7 empty] | CATEGORYB | SINGLE | ASB349 5 - CJ 366 5 - 1 | 0 | 547476 | ASB349 5 | 547477 | CJ 366 5 | 0 |  | 1 | Transfer Loading < 100%
2019-AG2 | ASB349 5 - PUR421 5 - 1 | E | EMDE | EMDE |  |  | 0 | 547476 | ASB349 5 | 547491 | PUR421 5 | 0 |  | 1 | 21WP | 223 | 223 | 0 |  | 52.1792 | 95.4 | [7 empty] | CATEGORYB | SINGLE | CJ 366 5 - FIR417 5 - 1 | 0 | 547477 | CJ 366 5 | 547490 | FIR417 5 | 0 |  | 1 | Transfer Loading < 100%
2019-AG2 | ASB349 5 - PUR421 5 - 1 | E | EMDE | EMDE |  |  | 0 | 547476 | ASB349 5 | 547491 | PUR421 5 | 0 |  | 1 | 22WP | 223 | 223 | 0 | 78.1 | 52.1633 | 99.2 | [7 empty] | CATEGORYB | NONSINGLE | 3671 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | ASB349 5 - PUR421 5 - 1 | E | EMDE | EMDE |  |  | 0 | 547476 | ASB349 5 | 547491 | PUR421 5 | 0 |  | 1 | 22WP | 223 | 223 | 0 |  | 52.1633 | 99 | [7 empty] | CATEGORYB | SINGLE | ASB349 5 - CJ 366 5 - 1 | 0 | 547476 | ASB349 5 | 547477 | CJ 366 5 | 0 |  | 1 | Transfer Loading < 100%
2019-AG2 | ASB349 5 - PUR421 5 - 1 | E | EMDE | EMDE |  |  | 0 | 547476 | ASB349 5 | 547491 | PUR421 5 | 0 |  | 1 | 22WP | 223 | 223 | 0 |  | 52.1633 | 95.1 | [7 empty] | CATEGORYB | SINGLE | CJ 366 5 - FIR417 5 - 1 | 0 | 547477 | CJ 366 5 | 547490 | FIR417 5 | 0 |  | 1 | Transfer Loading < 100%
2019-AG2 | ASB349 5 - PUR421 5 - 1 | E | EMDE | EMDE |  |  | 0 | 547476 | ASB349 5 | 547491 | PUR421 5 | 0 |  | 1 | 25WP | 223 | 223 | 0 | 75.9 | 51.3254 | 96 | [7 empty] | CATEGORYB | NONSINGLE | 3671 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | ASB349 5 - PUR421 5 - 1 | E | EMDE | EMDE |  |  | 0 | 547476 | ASB349 5 | 547491 | PUR421 5 | 0 |  | 1 | 25WP | 223 | 223 | 0 |  | 51.3254 | 95.9 | [7 empty] | CATEGORYB | SINGLE | ASB349 5 - CJ 366 5 - 1 | 0 | 547476 | ASB349 5 | 547477 | CJ 366 5 | 0 |  | 1 | Transfer Loading < 100%
2019-AG2 | ASHDWN_W 4 - PATTERS4 - 1 | E | AEPW | AEPW |  |  | 0 | 504124 | ASHDWN_W 4 | 507431 | PATTERS4 | 0 |  | 1 | 25LP | 347 | 347 | 0 |  | 14.1681 | 96 | [7 empty] | CATEGORYB | NONSINGLE | 84131 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | ATOKA--4 - LANE 4 - 1 | E | AEPW | WFEC |  |  | 0 | 510887 | ATOKA--4 | 520968 | LANE 4 | 0 |  | 1 | 22LP | 282 | 287 | 0 |  | 18.2445 | 95.8 | [7 empty] | CATEGORYB | NONSINGLE | 81723 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | BEATRCE7 - HARBINE7 - 1 | E | NPPD | NPPD |  |  | 0 | 640208 | HARBINE7 | 640076 | BEATRCE7 | 0 |  | 1 | 25LP | 99 | 99 | 0 | 90.9 | 55.3785 | 97.1 | [7 empty] | CATEGORYB | NONSINGLE | 85491 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | BEAVER 5 - BVR #1 1 - 1 | E | SWPA | SWPA |  |  | 0 | 505482 | BVR #1 1 | 505480 | BEAVER 5 | 0 |  | 1 | 20SP | 68 | 68 | 0 | 99.2 | 52.58 | 99.9 | [7 empty] | CATEGORYB | SINGLE | STOCKTN5 - STK #1 1 - 1 | 0 | 505498 | STOCKTN5 | 505500 | STK #1 1 | 0 |  | 1 | Transfer Loading < 100%
2019-AG2 | BEAVER 5 - BVR #1 1 - 1 | E | SWPA | SWPA |  |  | 0 | 505482 | BVR #1 1 | 505480 | BEAVER 5 | 0 |  | 1 | 20SP | 68 | 68 | 0 | 96.6 | 52.58 | 98.6 | [7 empty] | CATEGORYB | SINGLE | TENKIL 5 - TEN1&2 1 - 1 | 0 | 505566 | TENKIL 5 | 505568 | TEN1&2 1 | 0 |  | 1 | Transfer Loading < 100%
2019-AG2 | BEAVER 5 - BVR #1 1 - 1 | E | SWPA | SWPA |  |  | 0 | 505482 | BVR #1 1 | 505480 | BEAVER 5 | 0 |  | 1 | 20SP | 68 | 68 | 0 | 96.8 | 52.58 | 97.5 | [7 empty] | CATEGORYB | NONSINGLE | 44308 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | BEAVER 5 - BVR #1 1 - 1 | E | SWPA | SWPA |  |  | 0 | 505482 | BVR #1 1 | 505480 | BEAVER 5 | 0 |  | 1 | 20WP | 68 | 68 | 0 | 98 | 51.7098 | 99 | [7 empty] | CATEGORYB | SINGLE | STOCKTN5 - STK #1 1 - 1 | 0 | 505498 | STOCKTN5 | 505500 | STK #1 1 | 0 |  | 1 | Transfer Loading < 100%
2019-AG2 | BEAVER 5 - BVR #1 1 - 1 | E | SWPA | SWPA |  |  | 0 | 505482 | BVR #1 1 | 505480 | BEAVER 5 | 0 |  | 1 | 20WP | 68 | 68 | 0 | 97 | 51.7098 | 97.9 | [7 empty] | CATEGORYB | SINGLE | GORE 5 - TENKIL 5 - 1 | 0 | 505552 | GORE 5 | 505566 | TENKIL 5 | 0 |  | 1 | Transfer Loading < 100%
2019-AG2 | BEAVER 5 - BVR #1 1 - 1 | E | SWPA | SWPA |  |  | 0 | 505482 | BVR #1 1 | 505480 | BEAVER 5 | 0 |  | 1 | 21LP | 68 | 68 | 0 | 108.7 | 52.2732 | 95.9 | [7 empty] | CATEGORYB | NONSINGLE | 85219 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | BEAVER 5 - BVR #1 1 - 1 | E | SWPA | SWPA |  |  | 0 | 505482 | BVR #1 1 | 505480 | BEAVER 5 | 0 |  | 1 | 21SP | 68 | 68 | 0 | 99.1 | 52.239 | 99.7 | [7 empty] | CATEGORYB | NONSINGLE | 85222 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | BEAVER 5 - BVR #1 1 - 1 | E | SWPA | SWPA |  |  | 0 | 505482 | BVR #1 1 | 505480 | BEAVER 5 | 0 |  | 1 | 21SP | 68 | 68 | 0 | 99 | 52.239 | 99.6 | [7 empty] | CATEGORYB | SINGLE | STOCKTN5 - STK #1 1 - 1 | 0 | 505498 | STOCKTN5 | 505500 | STK #1 1 | 0 |  | 1 | Transfer Loading < 100%
2019-AG2 | BEAVER 5 - BVR #1 1 - 1 | E | SWPA | SWPA |  |  | 0 | 505482 | BVR #1 1 | 505480 | BEAVER 5 | 0 |  | 1 | 21SP | 68 | 68 | 0 | 96.5 | 52.239 | 97.3 | [7 empty] | CATEGORYB | NONSINGLE | 44308 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | BEAVER 5 - BVR #1 1 - 1 | E | SWPA | SWPA |  |  | 0 | 505482 | BVR #1 1 | 505480 | BEAVER 5 | 0 |  | 1 | 21WP | 68 | 68 | 0 | 97.2 | 52.9257 | 98.5 | [7 empty] | CATEGORYB | SINGLE | GREERSF5 - GF #1 1 - 1 | 0 | 505422 | GREERSF5 | 505424 | GF #1 1 | 0 |  | 1 | Transfer Loading < 100%
2019-AG2 | BEAVER 5 - BVR #1 1 - 1 | E | SWPA | SWPA |  |  | 0 | 505482 | BVR #1 1 | 505480 | BEAVER 5 | 0 |  | 1 | 21WP | 68 | 68 | 0 | 94 | 52.9257 | 95.4 | [7 empty] | CATEGORYB | NONSINGLE | 32026 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | BEAVER 5 - BVR #1 1 - 1 | E | SWPA | SWPA |  |  | 0 | 505482 | BVR #1 1 | 505480 | BEAVER 5 | 0 |  | 1 | 22LP | 68 | 68 | 0 | 110.9 | 53.583 | 98.5 | [7 empty] | CATEGORYB | NONSINGLE | 85219 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | BEAVER 5 - BVR #1 1 - 1 | E | SWPA | SWPA |  |  | 0 | 505482 | BVR #1 1 | 505480 | BEAVER 5 | 0 |  | 1 | 22SP | 68 | 68 | 0 | 97.7 | 55.4322 | 98.7 | [7 empty] | CATEGORYB | NONSINGLE | 32026 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | BEAVER 5 - BVR #1 1 - 1 | E | SWPA | SWPA |  |  | 0 | 505482 | BVR #1 1 | 505480 | BEAVER 5 | 0 |  | 1 | 25WP | 68 | 68 | 0 | 97.9 | 60.3187 | 99 | [7 empty] | CATEGORYB | NONSINGLE | 32029 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | BEAVER 5 - BVR #1 1 - 1 | E | SWPA | SWPA |  |  | 0 | 505482 | BVR #1 1 | 505480 | BEAVER 5 | 0 |  | 1 | 25WP | 68 | 68 | 0 | 97.2 | 60.3187 | 98.3 | [7 empty] | CATEGORYB | SINGLE | EUFAULA4 - EUF #2 1 - 1 | 0 | 505574 | EUFAULA4 | 505578 | EUF #2 1 | 0 |  | 1 | Transfer Loading < 100%
2019-AG2 | BEAVER 5 - BVR #1 1 - 1 | E | SWPA | SWPA |  |  | 0 | 505482 | BVR #1 1 | 505480 | BEAVER 5 | 0 |  | 1 | 30SP | 68 | 68 | 0 | 97.4 | 67.6375 | 97.8 | [7 empty] | CATEGORYB | SINGLE | FT GIB 5 - FTG3&4 1 - 1 | 0 | 505560 | FT GIB 5 | 505564 | FTG3&4 1 | 0 |  | 1 | Transfer Loading < 100%
2019-AG2 | BEAVER 5 - BVR #1 1 - 1 | E | SWPA | SWPA |  |  | 0 | 505482 | BVR #1 1 | 505480 | BEAVER 5 | 0 |  | 1 | 30WP | 68 | 68 | 0 | 97 | 65.2082 | 98.3 | [7 empty] | CATEGORYB | NONSINGLE | 81799 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | BEAVER 5 - BVR #1 1 - 1 | E | SWPA | SWPA |  |  | 0 | 505482 | BVR #1 1 | 505480 | BEAVER 5 | 0 |  | 1 | 30WP | 68 | 68 | 0 | 124.7 | 65.2082 | 97 | [7 empty] | CATEGORYB | SINGLE | CENTRATAP4 - CENTRAHOMA4 - 1 | 0 | 505665 | CENTRATAP4 | 505666 | CENTRAHOMA4 | 0 |  | 1 | Transfer Loading < 100%
2019-AG2 | BELFELD4 - DICKINSN-BE4 - 1 | E | WAPA | WAPA |  |  | 0 | 659124 | DICKINSN-BE4 | 652425 | BELFELD4 | 0 |  | 1 | 30LP | 263 | 263 | 0 | 92.8 | 27.8648 | 99.8 | [7 empty] | CATEGORYB | NONSINGLE | 93775 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | BELFELD4 - DICKINSN-BE4 - 1 | E | WAPA | WAPA |  |  | 0 | 659124 | DICKINSN-BE4 | 652425 | BELFELD4 | 0 |  | 1 | 30LP | 263 | 263 | 0 | 92.8 | 27.8648 | 99.8 | [7 empty] | CATEGORYB | NONSINGLE | 93775 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | BENNGTN4 - DURANTP4 - 1 | E | WFEC | WFEC |  |  | 0 | 520884 | DURANTP4 | 520826 | BENNGTN4 | 0 |  | 1 | 22LP | 287 | 287 | 0 |  | 14.0528 | 97.5 | [7 empty] | CATEGORYB | NONSINGLE | 81723 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | BISMARK4 - CAMPBELL 4 - 1 | E | WAPA | WAPA |  |  | 0 | 652499 | CAMPBELL 4 | 652426 | BISMARK4 | 0 |  | 1 | 30LP | 240 | 264 | 0 | 90.6 | 17.0972 | 97.7 | [7 empty] | CATEGORYB | NONSINGLE | 105814 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | BISMARK4 - CAMPBELL 4 - 1 | E | WAPA | WAPA |  |  | 0 | 652499 | CAMPBELL 4 | 652426 | BISMARK4 | 0 |  | 1 | 30LP | 240 | 264 | 0 | 90.6 | 17.0972 | 97.7 | [7 empty] | CATEGORYB | NONSINGLE | 105814 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | BRKN BW4 - BETHEL 4 - 1 | E | AEPW | SWPA |  |  | 0 | 510928 | BETHEL 4 | 505614 | BRKN BW4 | 0 |  | 1 | 22LP | 191 | 191 | 0 |  | 45.8792 | 97.5 | [7 empty] | CATEGORYB | NONSINGLE | 84223 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | BRKN BW4 - BETHEL 4 - 1 | E | AEPW | SWPA |  |  | 0 | 510928 | BETHEL 4 | 505614 | BRKN BW4 | 0 |  | 1 | 25LP | 191 | 191 | 0 |  | 45.4803 | 96.9 | [7 empty] | CATEGORYB | NONSINGLE | 84223 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | BROOKLINE 5 - BRKLTX1 - 1 | E | SPRM | SPRM |  |  | 1 | 549984 | BROOKLINE 7 | 549969 | BROOKLINE 5 | 549988 |  | 1 | 25WP | 400 | 400 | 0 |  | 55.0233 | 95.8 | [7 empty] | CATEGORYB | SINGLE | BROOKLINE 5 - BROOKLINE 7 - 2 | 1 | 549969 | BROOKLINE 5 | 549984 | BROOKLINE 7 | 549989 | BRKLNE XF2 1 | 2 | Transfer Loading < 100%
2019-AG2 | BROOKLINE 5 - BRKLTX1 - 1 | E | SPRM | SPRM |  |  | 1 | 549984 | BROOKLINE 7 | 549969 | BROOKLINE 5 | 549988 |  | 1 | 30WP | 400 | 400 | 0 | 88.1 | 54.5193 | 96 | [7 empty] | CATEGORYB | SINGLE | BROOKLINE 5 - BROOKLINE 7 - 2 | 1 | 549969 | BROOKLINE 5 | 549984 | BROOKLINE 7 | 549989 | BRKLNE XF2 1 | 2 | Transfer Loading < 100%
2019-AG2 | BROOKLINE 5 - BRKLTX2 - 2 | E | SPRM | SPRM |  |  | 1 | 549984 | BROOKLINE 7 | 549969 | BROOKLINE 5 | 549989 |  | 2 | 25WP | 400 | 400 | 0 | 89.2 | 54.5496 | 95.6 | [7 empty] | CATEGORYB | SINGLE | BROOKLINE 5 - BROOKLINE 7 - 1 | 1 | 549969 | BROOKLINE 5 | 549984 | BROOKLINE 7 | 549988 | BRKLNE XF1 1 | 1 | Transfer Loading < 100%
2019-AG2 | BROOKLINE 5 - BRKLTX2 - 2 | E | SPRM | SPRM |  |  | 1 | 549984 | BROOKLINE 7 | 549969 | BROOKLINE 5 | 549989 |  | 2 | 30WP | 400 | 400 | 0 |  | 54.05 | 95.7 | [7 empty] | CATEGORYB | SINGLE | BROOKLINE 5 - BROOKLINE 7 - 1 | 1 | 549969 | BROOKLINE 5 | 549984 | BROOKLINE 7 | 549988 | BRKLNE XF1 1 | 1 | Transfer Loading < 100%
2019-AG2 | BROOKLINE 7 - BRKLTX1 - 1 | E | SPRM | SPRM |  |  | 1 | 549984 | BROOKLINE 7 | 549969 | BROOKLINE 5 | 549988 |  | 1 | 25WP | 400 | 400 | 0 | 89.5 | 55.0233 | 96.2 | [7 empty] | CATEGORYB | SINGLE | BROOKLINE 5 - BROOKLINE 7 - 2 | 1 | 549969 | BROOKLINE 5 | 549984 | BROOKLINE 7 | 549989 | BRKLNE XF2 1 | 2 | Transfer Loading < 100%
2019-AG2 | BROOKLINE 7 - BRKLTX1 - 1 | E | SPRM | SPRM |  |  | 1 | 549984 | BROOKLINE 7 | 549969 | BROOKLINE 5 | 549988 |  | 1 | 30WP | 400 | 400 | 0 | 88.1 | 54.5193 | 96.3 | [7 empty] | CATEGORYB | SINGLE | BROOKLINE 5 - BROOKLINE 7 - 2 | 1 | 549969 | BROOKLINE 5 | 549984 | BROOKLINE 7 | 549989 | BRKLNE XF2 1 | 2 | Transfer Loading < 100%
2019-AG2 | BROOKLINE 7 - BRKLTX2 - 2 | E | SPRM | SPRM |  |  | 1 | 549984 | BROOKLINE 7 | 549969 | BROOKLINE 5 | 549989 |  | 2 | 25WP | 400 | 400 | 0 | 88.7 | 54.5496 | 95.9 | [7 empty] | CATEGORYB | SINGLE | BROOKLINE 5 - BROOKLINE 7 - 1 | 1 | 549969 | BROOKLINE 5 | 549984 | BROOKLINE 7 | 549988 | BRKLNE XF1 1 | 1 | Transfer Loading < 100%
2019-AG2 | BROOKLINE 7 - BRKLTX2 - 2 | E | SPRM | SPRM |  |  | 1 | 549984 | BROOKLINE 7 | 549969 | BROOKLINE 5 | 549989 |  | 2 | 30WP | 400 | 400 | 0 | 87.9 | 54.05 | 96 | [7 empty] | CATEGORYB | SINGLE | BROOKLINE 5 - BROOKLINE 7 - 1 | 1 | 549969 | BROOKLINE 5 | 549984 | BROOKLINE 7 | 549988 | BRKLNE XF1 1 | 1 | Transfer Loading < 100%
2019-AG2 | BUTLER 4 - ALTOONA4 - 1 | E | WERE | WERE |  |  | 0 | 532987 | BUTLER 4 | 533001 | ALTOONA4 | 0 |  | 1 | 21LP | 87 | 101 | 0 | 95.5 | 60.6964 | 95.6 | [7 empty] | CATEGORYB | NONSINGLE | 94117 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | CALAMS 7 - THEDFRD7 - 1 | E | NPPD | NPPD |  |  | 0 | 640381 | THEDFRD7 | 640096 | CALAMS 7 | 0 |  | 1 | 25SP | 120 | 120 | 0 |  | 71.6488 | 96.4 | [7 empty] | CATEGORYB | NONSINGLE | 105818 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | CALAMS 7 - THEDFRD7 - 1 | E | NPPD | NPPD |  |  | 0 | 640381 | THEDFRD7 | 640096 | CALAMS 7 | 0 |  | 1 | 30SP | 120 | 120 | 0 | 93.4 | 73.4657 | 99.1 | [7 empty] | CATEGORYB | NONSINGLE | 105818 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | CALAWAY7 - MAXWELS7 - 1 | E | NPPD | NPPD |  |  | 0 | 640267 | MAXWELS7 | 640098 | CALAWAY7 | 0 |  | 1 | 25SP | 140 | 140 | 0 | 93.7 | 65.4028 | 96.4 | [7 empty] | CATEGORYB | NONSINGLE | 85496 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | CALAWAY7 - MAXWELS7 - 1 | E | NPPD | NPPD |  |  | 0 | 640267 | MAXWELS7 | 640098 | CALAWAY7 | 0 |  | 1 | 30SP | 140 | 140 | 0 | 94.4 | 64.545 | 97 | [7 empty] | CATEGORYB | NONSINGLE | 85496 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | CARTHAG5 - ATL109 5 - 1 | E | EMDE | SWPA |  |  | 0 | 547466 | ATL109 5 | 505488 | CARTHAG5 | 0 |  | 1 | 30WP | 222 | 222 | 0 | 89.3 | 47.3516 | 96.8 | [7 empty] | CATEGORYB | NONSINGLE | 87087 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | CIMARON4 - CIMARON1 - 1 | E | OKGE | OKGE |  |  | 1 | 514901 | CIMARON7 | 514898 | CIMARON4 | 515714 |  | 1 | 21SP | 478 | 478 | 0 | 99.4 | 97.2 | 97.2 | [7 empty] | CATEGORYB | NONSINGLE | 80888 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | CIMARON4 - CIMARON1 - 1 | E | OKGE | OKGE |  |  | 1 | 514901 | CIMARON7 | 514898 | CIMARON4 | 515714 |  | 1 | 22LP | 478 | 478 | 0 | 86.8 | 97.2 | 97.2 | [7 empty] | CATEGORYB | NONSINGLE | 81738 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | CIMARON4 - CIMARON1 - 1 | E | OKGE | OKGE |  |  | 1 | 514901 | CIMARON7 | 514898 | CIMARON4 | 515714 |  | 1 | 22SP | 478 | 478 | 0 | 91.8 | 97.5 | 97.5 | [7 empty] | CATEGORYB | NONSINGLE | 92680 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | CIMARON4 - CIMARON1 - 1 | E | OKGE | OKGE |  |  | 1 | 514901 | CIMARON7 | 514898 | CIMARON4 | 515714 |  | 1 | 22SP | 478 | 478 | 0 | 91.7 | 97.2 | 97.2 | [7 empty] | CATEGORYB | NONSINGLE | 92693 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | CIMARON4 - CIMARON1 - 1 | E | OKGE | OKGE |  |  | 1 | 514901 | CIMARON7 | 514898 | CIMARON4 | 515714 |  | 1 | 22WP | 478 | 478 | 0 |  | 97.3 | 97.3 | [7 empty] | CATEGORYB | NONSINGLE | 80888 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | CIMARON4 - CIMARON1 - 1 | E | OKGE | OKGE |  |  | 1 | 514901 | CIMARON7 | 514898 | CIMARON4 | 515714 |  | 1 | 25LP | 478 | 478 | 0 | 88.8 | 99.4 | 99.4 | [7 empty] | CATEGORYB | NONSINGLE | 81738 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | CIMARON4 - CIMARON1 - 1 | E | OKGE | OKGE |  |  | 1 | 514901 | CIMARON7 | 514898 | CIMARON4 | 515714 |  | 1 | 25SP | 478 | 478 | 0 | 96.2 | 98.1 | 98.1 | [7 empty] | CATEGORYB | NONSINGLE | 92680 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | CIMARON4 - CIMARON1 - 1 | E | OKGE | OKGE |  |  | 1 | 514901 | CIMARON7 | 514898 | CIMARON4 | 515714 |  | 1 | 25SP | 478 | 478 | 0 | 92.4 | 97.6 | 97.6 | [7 empty] | CATEGORYB | NONSINGLE | 92693 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | CIMARON4 - CIMARON1 - 1 | E | OKGE | OKGE |  |  | 1 | 514901 | CIMARON7 | 514898 | CIMARON4 | 515714 |  | 1 | 30SP | 478 | 478 | 0 | 89.1 | 98.1 | 98.1 | [7 empty] | CATEGORYB | NONSINGLE | 81733 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | CIMARON4 - CIMARON1 - 1 | E | OKGE | OKGE |  |  | 1 | 514901 | CIMARON7 | 514898 | CIMARON4 | 515714 |  | 1 | 30SP | 478 | 478 | 0 | 95.4 | 95.2 | 95.2 | [7 empty] | CATEGORYB | NONSINGLE | 92670 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | CIMARON4 - CIMARON2 - 1 | E | OKGE | OKGE |  |  | 1 | 514901 | CIMARON7 | 514898 | CIMARON4 | 515715 |  | 1 | 25SP | 478 | 478 | 0 | 88 | 95.4 | 95.4 | [7 empty] | CATEGORYB | NONSINGLE | 91055 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | CIMARON4 - CIMARON2 - 1 | E | OKGE | OKGE |  |  | 1 | 514901 | CIMARON7 | 514898 | CIMARON4 | 515715 |  | 1 | 30SP | 478 | 478 | 0 |  | 98.4 | 98.4 | [7 empty] | CATEGORYB | NONSINGLE | 91055 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | CIMARON4 - CIMARON2 - 1 | E | OKGE | OKGE |  |  | 1 | 514901 | CIMARON7 | 514898 | CIMARON4 | 515715 |  | 1 | 30SP | 478 | 478 | 0 | 94.3 | 97.2 | 97.2 | [7 empty] | CATEGORYB | NONSINGLE | 92685 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | CIMARON7 - CIMARON1 - 1 | E | OKGE | OKGE |  |  | 1 | 514901 | CIMARON7 | 514898 | CIMARON4 | 515714 |  | 1 | 21LP | 478 | 478 | 0 |  | 95.3 | 95.3 | [7 empty] | CATEGORYB | NONSINGLE | 80888 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | CIMARON7 - CIMARON1 - 1 | E | OKGE | OKGE |  |  | 1 | 514901 | CIMARON7 | 514898 | CIMARON4 | 515714 |  | 1 | 22SP | 478 | 478 | 0 | 84.2 | 96.9 | 96.9 | [7 empty] | CATEGORYB | NONSINGLE | 81733 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | CIMARON7 - CIMARON1 - 1 | E | OKGE | OKGE |  |  | 1 | 514901 | CIMARON7 | 514898 | CIMARON4 | 515714 |  | 1 | 25SP | 478 | 478 | 0 | 85 | 97.4 | 97.4 | [7 empty] | CATEGORYB | NONSINGLE | 81733 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | CIMARON7 - CIMARON1 - 1 | E | OKGE | OKGE |  |  | 1 | 514901 | CIMARON7 | 514898 | CIMARON4 | 515714 |  | 1 | 30LP | 478 | 478 | 0 | 84.7 | 97.2 | 97.2 | [7 empty] | CATEGORYB | NONSINGLE | 81738 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | CIMARON7 - CIMARON1 - 1 | E | OKGE | OKGE |  |  | 1 | 514901 | CIMARON7 | 514898 | CIMARON4 | 515714 |  | 1 | 30SP | 478 | 478 | 0 | 95.4 | 98.8 | 98.8 | [7 empty] | CATEGORYB | NONSINGLE | 92670 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | CIMARON7 - CIMARON1 - 1 | E | OKGE | OKGE |  |  | 1 | 514901 | CIMARON7 | 514898 | CIMARON4 | 515714 |  | 1 | 30SP | 478 | 478 | 0 | 90.6 | 96.5 | 96.5 | [7 empty] | CATEGORYB | NONSINGLE | 92678 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | CIMARON7 - CIMARON1 - 1 | E | OKGE | OKGE |  |  | 1 | 514901 | CIMARON7 | 514898 | CIMARON4 | 515714 |  | 1 | 30WP | 478 | 478 | 0 | 80 | 97 | 97 | [7 empty] | CATEGORYB | NONSINGLE | 92685 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | CIMARON7 - CIMARON2 - 1 | E | OKGE | OKGE |  |  | 1 | 514901 | CIMARON7 | 514898 | CIMARON4 | 515715 |  | 1 | 22SP | 478 | 478 | 0 | 91.1 | 98.6 | 98.6 | [7 empty] | CATEGORYB | SINGLE | CIMARON4 - CIMARON7 - 1 | 1 | 514898 | CIMARON4 | 514901 | CIMARON7 | 515714 | CIMARO11 | 1 | Transfer Loading < 100%
2019-AG2 | CIMARON7 - CIMARON2 - 1 | E | OKGE | OKGE |  |  | 1 | 514901 | CIMARON7 | 514898 | CIMARON4 | 515715 |  | 1 | 22SP | 478 | 478 | 0 | 89 | 96.3 | 96.3 | [7 empty] | CATEGORYB | NONSINGLE | 92685 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | CIMARON7 - CIMARON2 - 1 | E | OKGE | OKGE |  |  | 1 | 514901 | CIMARON7 | 514898 | CIMARON4 | 515715 |  | 1 | 25SP | 478 | 478 | 0 |  | 99.7 | 99.7 | [7 empty] | CATEGORYB | SINGLE | CIMARON4 - CIMARON7 - 1 | 1 | 514898 | CIMARON4 | 514901 | CIMARON7 | 515714 | CIMARO11 | 1 | Transfer Loading < 100%
2019-AG2 | CIMARON7 - CIMARON2 - 1 | E | OKGE | OKGE |  |  | 1 | 514901 | CIMARON7 | 514898 | CIMARON4 | 515715 |  | 1 | 25SP | 478 | 478 | 0 | 86.1 | 96.5 | 96.5 | [7 empty] | CATEGORYB | NONSINGLE | 92685 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | CIMARON7 - CIMARON2 - 1 | E | OKGE | OKGE |  |  | 1 | 514901 | CIMARON7 | 514898 | CIMARON4 | 515715 |  | 1 | 30SP | 478 | 478 | 0 | 80.4 | 95.7 | 95.7 | [7 empty] | CATEGORYB | NONSINGLE | 81738 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | CIMARON7 - DRAPER 7 - 1 | E | OKGE | OKGE |  |  | 0 | 514901 | CIMARON7 | 514934 | DRAPER 7 | 0 |  | 1 | 22LP | 1195 | 1195 | 0 | 68.1 | 45.4474 | 95.7 | [7 empty] | CATEGORYB | NONSINGLE | 81738 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | CIMARON7 - DRAPER 7 - 1 | E | OKGE | OKGE |  |  | 0 | 514901 | CIMARON7 | 514934 | DRAPER 7 | 0 |  | 1 | 25LP | 1195 | 1195 | 0 | 68.2 | 46.9049 | 96.2 | [7 empty] | CATEGORYB | NONSINGLE | 81738 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | CIRCLVL3 - GOFF 3 - 1 | E | WERE | WERE |  |  | 0 | 533152 | CIRCLVL3 | 533331 | GOFF 3 | 0 |  | 1 | 21SP | 92 | 92 | 0 | 94.9 | 58.7982 | 98.4 | [7 empty] | CATEGORYB | NONSINGLE | 8295 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | CIRCLVL3 - GOFF 3 - 1 | E | WERE | WERE |  |  | 0 | 533152 | CIRCLVL3 | 533331 | GOFF 3 | 0 |  | 1 | 21SP | 92 | 92 | 0 |  | 58.7982 | 98.1 | [7 empty] | CATEGORYB | SINGLE | HOYT 7 - STRANGR7 - 1 | 0 | 532765 | HOYT 7 | 532772 | STRANGR7 | 0 |  | 1 | Transfer Loading < 100%
2019-AG2 | CIRCLVL3 - GOFF 3 - 1 | E | WERE | WERE |  |  | 0 | 533152 | CIRCLVL3 | 533331 | GOFF 3 | 0 |  | 1 | 22SP | 92 | 92 | 0 | 89.4 | 56.63 | 98.3 | [7 empty] | CATEGORYB | NONSINGLE | 8295 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | CIRCLVL3 - GOFF 3 - 1 | E | WERE | WERE |  |  | 0 | 533152 | CIRCLVL3 | 533331 | GOFF 3 | 0 |  | 1 | 22SP | 92 | 92 | 0 |  | 56.63 | 98.1 | [7 empty] | CATEGORYB | SINGLE | HOYT 7 - STRANGR7 - 1 | 0 | 532765 | HOYT 7 | 532772 | STRANGR7 | 0 |  | 1 | Transfer Loading < 100%
2019-AG2 | CIRCLVL3 - GOFF 3 - 1 | E | WERE | WERE |  |  | 0 | 533152 | CIRCLVL3 | 533331 | GOFF 3 | 0 |  | 1 | 25SP | 92 | 92 | 0 | 95.3 | 68.0261 | 99.6 | [7 empty] | CATEGORYB | NONSINGLE | 84839 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | CIRCLVL3 - GOFF 3 - 1 | E | WERE | WERE |  |  | 0 | 533152 | CIRCLVL3 | 533331 | GOFF 3 | 0 |  | 1 | 30SP | 92 | 92 | 0 |  | 66.8645 | 98.8 | [7 empty] | CATEGORYB | NONSINGLE | 84839 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | CLEOCOR2 - CLEOSW 2 - 1 | E | OKGE | WFEC |  |  | 0 | 514777 | CLEOCOR2 | 520855 | CLEOSW 2 | 0 |  | 1 | 21LP | 36 | 36 | 0 |  | 7.7665e-12 | 98.5 | [7 empty] | CATEGORYB | NONSINGLE | 90930 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | CLEOCOR2 - CLEOSW 2 - 1 | E | OKGE | WFEC |  |  | 0 | 514777 | CLEOCOR2 | 520855 | CLEOSW 2 | 0 |  | 1 | 21SP | 36 | 36 | 0 |  | 7.7399e-13 | 98.6 | [7 empty] | CATEGORYB | SINGLE | FAIRVEW2 - RNGWODJ2 - 1 | 0 | 520909 | FAIRVEW2 | 521039 | RNGWODJ2 | 0 |  | 1 | Transfer Loading < 100%
2019-AG2 | CLEOCOR2 - CLEOSW 2 - 1 | E | OKGE | WFEC |  |  | 0 | 514777 | CLEOCOR2 | 520855 | CLEOSW 2 | 0 |  | 1 | 22LP | 36 | 36 | 0 |  | 4.0934e-12 | 99.5 | [7 empty] | CATEGORYB | SINGLE | NASH 2 - RNGWOOD2 - 1 | 0 | 521008 | NASH 2 | 521040 | RNGWOOD2 | 0 |  | 1 | Transfer Loading < 100%
2019-AG2 | CLEOCOR2 - CLEOSW 2 - 1 | E | OKGE | WFEC |  |  | 0 | 514777 | CLEOCOR2 | 520855 | CLEOSW 2 | 0 |  | 1 | 22LP | 36 | 36 | 0 |  | 4.0934e-12 | 97.5 | [7 empty] | CATEGORYB | NONSINGLE | 94252 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | CLEOCOR2 - CLEOSW 2 - 1 | E | OKGE | WFEC |  |  | 0 | 514777 | CLEOCOR2 | 520855 | CLEOSW 2 | 0 |  | 1 | 22LP | 36 | 36 | 0 |  | 4.0934e-12 | 96.7 | [7 empty] | CATEGORYB | SINGLE | FAIRVEW2 - OKEENE 2 - 1 | 0 | 520909 | FAIRVEW2 | 521015 | OKEENE 2 | 0 |  | 1 | Transfer Loading < 100%
2019-AG2 | CLEOCOR2 - CLEOSW 2 - 1 | E | OKGE | WFEC |  |  | 0 | 514777 | CLEOCOR2 | 520855 | CLEOSW 2 | 0 |  | 1 | 22SP | 48 | 48 | 0 |  | 2.1396e-12 | 99.8 | [7 empty] | CATEGORYB | NONSINGLE | 94482 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | CLEOCOR2 - CLEOSW 2 - 1 | E | OKGE | WFEC |  |  | 0 | 514777 | CLEOCOR2 | 520855 | CLEOSW 2 | 0 |  | 1 | 22WP | 48 | 48 | 0 |  | 3.6114e-13 | 98.7 | [7 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | CLEOCOR2 - CLEOSW 2 - 1 | E | OKGE | WFEC |  |  | 0 | 514777 | CLEOCOR2 | 520855 | CLEOSW 2 | 0 |  | 1 | 22WP | 48 | 48 | 0 |  | 3.6114e-13 | 96.9 | [7 empty] | CATEGORYB | NONSINGLE | 7797 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | CLEOCOR2 - CLEOSW 2 - 1 | E | OKGE | WFEC |  |  | 0 | 514777 | CLEOCOR2 | 520855 | CLEOSW 2 | 0 |  | 1 | 25LP | 48 | 48 | 0 |  | 1.7831e-11 | 95.7 | [7 empty] | CATEGORYB | NONSINGLE | 94265 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | CLEOCOR2 - CLEOSW 2 - 1 | E | OKGE | WFEC |  |  | 0 | 514777 | CLEOCOR2 | 520855 | CLEOSW 2 | 0 |  | 1 | 25SP | 48 | 48 | 0 |  | 4.5636e-13 | 99.7 | [7 empty] | CATEGORYB | NONSINGLE | 94482 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | CLEOCOR2 - CLEOSW 2 - 1 | E | OKGE | WFEC |  |  | 0 | 514777 | CLEOCOR2 | 520855 | CLEOSW 2 | 0 |  | 1 | 25WP | 48 | 48 | 0 |  | 4.3352e-13 | 99.9 | [7 empty] | CATEGORYB | NONSINGLE | 81356 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | CLEOCOR2 - CLEOSW 2 - 1 | E | OKGE | WFEC |  |  | 0 | 514777 | CLEOCOR2 | 520855 | CLEOSW 2 | 0 |  | 1 | 25WP | 48 | 48 | 0 |  | 4.3352e-13 | 97.7 | [7 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | CLEOCOR2 - CLEOSW 2 - 1 | E | OKGE | WFEC |  |  | 0 | 514777 | CLEOCOR2 | 520855 | CLEOSW 2 | 0 |  | 1 | 30SP | 48 | 48 | 0 |  | 2.5487e-13 | 99.9 | [7 empty] | CATEGORYB | NONSINGLE | 92687 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | CLEOCOR2 - CLEOSW 2 - 1 | E | OKGE | WFEC |  |  | 0 | 514777 | CLEOCOR2 | 520855 | CLEOSW 2 | 0 |  | 1 | 30SP | 48 | 48 | 0 |  | 2.5487e-13 | 99.8 | [7 empty] | CATEGORYB | NONSINGLE | 81305 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | CLEOCOR2 - CLEOSW 2 - 1 | E | OKGE | WFEC |  |  | 0 | 514777 | CLEOCOR2 | 520855 | CLEOSW 2 | 0 |  | 1 | 30WP | 48 | 48 | 0 |  | 3.2448e-12 | 98.7 | [7 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | CLEOCOR2 - CLEOSW 2 - 1 | E | OKGE | WFEC |  |  | 0 | 514777 | CLEOCOR2 | 520855 | CLEOSW 2 | 0 |  | 1 | 30WP | 48 | 48 | 0 |  | 3.2448e-12 | 96.8 | [7 empty] | CATEGORYB | NONSINGLE | 7797 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | CLEOCOR2 - CLEOSW 2 - 1 | E | OKGE | WFEC |  |  | 0 | 514777 | CLEOCOR2 | 520855 | CLEOSW 2 | 0 |  | 1 | 30WP | 48 | 48 | 0 |  | 3.2448e-12 | 96.7 | [7 empty] | CATEGORYB | NONSINGLE | 81737 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | CLEOCOR4 - CLEOPLT4 - 1 | E | OKGE | OKGE |  |  | 0 | 514778 | CLEOCOR4 | 515562 | CLEOPLT4 | 0 |  | 1 | 21LP | 191 | 191 | 0 |  | 24.199 | 96.6 | [7 empty] | CATEGORYB | NONSINGLE | 81729 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | CLEOCOR4 - CLEOPLT4 - 1 | E | OKGE | OKGE |  |  | 0 | 514778 | CLEOCOR4 | 515562 | CLEOPLT4 | 0 |  | 1 | 22LP | 191 | 191 | 0 |  | 32.9138 | 99.3 | [7 empty] | CATEGORYB | NONSINGLE | 81743 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | CLEOCOR4 - CLEOPLT4 - 1 | E | OKGE | OKGE |  |  | 0 | 514778 | CLEOCOR4 | 515562 | CLEOPLT4 | 0 |  | 1 | 22LP | 191 | 191 | 0 |  | 32.9138 | 96.7 | [7 empty] | CATEGORYB | NONSINGLE | 81729 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | CLEOSW 2 - RNGWODJ2 - 1 | E | WFEC | WFEC |  |  | 0 | 520855 | CLEOSW 2 | 521039 | RNGWODJ2 | 0 |  | 1 | 21LP | 58 | 68 | 0 |  | 17.3153 | 99.5 | [7 empty] | CATEGORYB | SINGLE | MENOTAP4 - IMO 4 - 1 | 0 | 514789 | MENOTAP4 | 514790 | IMO 4 | 0 |  | 1 | Transfer Loading < 100%
2019-AG2 | CLEOSW 2 - RNGWODJ2 - 1 | E | WFEC | WFEC |  |  | 0 | 520855 | CLEOSW 2 | 521039 | RNGWODJ2 | 0 |  | 1 | 22LP | 58 | 68 | 0 |  | 17.4946 | 97.7 | [7 empty] | CATEGORYB | NONSINGLE | 90675 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | CLEOSW 2 - RNGWODJ2 - 1 | E | WFEC | WFEC |  |  | 0 | 520855 | CLEOSW 2 | 521039 | RNGWODJ2 | 0 |  | 1 | 22LP | 58 | 68 | 0 |  | 17.4946 | 97.4 | [7 empty] | CATEGORYB | SINGLE | MENOTAP4 - CLEOPLT4 - 1 | 0 | 514789 | MENOTAP4 | 515562 | CLEOPLT4 | 0 |  | 1 | Transfer Loading < 100%
2019-AG2 | CRAIG 5 - LENEXA 5 - 2 | E | KCPL | KCPL |  |  | 0 | 542978 | CRAIG 5 | 543038 | LENEXA 5 | 0 |  | 2 | 21SP | 293 | 334 | 0 |  | 54.0465 | 96.6 | [7 empty] | CATEGORYB | SINGLE | CRAIG 5 - LENEXA 5 - 1 | 0 | 542978 | CRAIG 5 | 543038 | LENEXA 5 | 0 |  | 1 | Transfer Loading < 100%
2019-AG2 | CRAIG 5 - LENEXA 5 - 2 | E | KCPL | KCPL |  |  | 0 | 542978 | CRAIG 5 | 543038 | LENEXA 5 | 0 |  | 2 | 22SP | 293 | 334 | 0 |  | 54.5213 | 97.5 | [7 empty] | CATEGORYB | SINGLE | CRAIG 5 - LENEXA 5 - 1 | 0 | 542978 | CRAIG 5 | 543038 | LENEXA 5 | 0 |  | 1 | Transfer Loading < 100%
2019-AG2 | CRAIG 5 - LENEXA 5 - 2 | E | KCPL | KCPL |  |  | 0 | 542978 | CRAIG 5 | 543038 | LENEXA 5 | 0 |  | 2 | 25SP | 293 | 334 | 0 |  | 53.1849 | 97.5 | [7 empty] | CATEGORYB | SINGLE | CRAIG 5 - LENEXA 5 - 1 | 0 | 542978 | CRAIG 5 | 543038 | LENEXA 5 | 0 |  | 1 | Transfer Loading < 100%
2019-AG2 | CRAIG 5 - LENEXA 5 - 2 | E | KCPL | KCPL |  |  | 0 | 542978 | CRAIG 5 | 543038 | LENEXA 5 | 0 |  | 2 | 30SP | 293 | 334 | 0 |  | 51.527 | 96.3 | [7 empty] | CATEGORYB | SINGLE | CRAIG 5 - LENEXA 5 - 1 | 0 | 542978 | CRAIG 5 | 543038 | LENEXA 5 | 0 |  | 1 | Transfer Loading < 100%
2019-AG2 | CRAIG 7 - CRAIG11 - 11 | E | KCPL | KCPL |  |  | 1 | 542977 | CRAIG 7 | 542978 | CRAIG 5 | 543641 |  | 11 | 21SP | 550 | 605 | 0 | 89.1 | 54.7279 | 95.7 | [7 empty] | CATEGORYB | NONSINGLE | 84723 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | CRAIG 7 - CRAIG11 - 11 | E | KCPL | KCPL |  |  | 1 | 542977 | CRAIG 7 | 542978 | CRAIG 5 | 543641 |  | 11 | 22SP | 550 | 605 | 0 | 89.6 | 55.2043 | 96.7 | [7 empty] | CATEGORYB | NONSINGLE | 84723 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | CRAIG 7 - CRAIG11 - 11 | E | KCPL | KCPL |  |  | 1 | 542977 | CRAIG 7 | 542978 | CRAIG 5 | 543641 |  | 11 | 25SP | 550 | 605 | 0 | 87.4 | 53.8502 | 95.5 | [7 empty] | CATEGORYB | NONSINGLE | 84723 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | DARWIN 4 - LANE 4 - 1 | E | WFEC | WFEC |  |  | 0 | 520968 | LANE 4 | 520874 | DARWIN 4 | 0 |  | 1 | 22LP | 287 | 287 | 0 |  | 15.5275 | 95 | [7 empty] | CATEGORYB | NONSINGLE | 81723 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | DIANA 4 - DIANA 3 - 3 | E | AEPW | AEPW |  |  | 1 | 508832 | DIANA 7 | 508831 | DIANA 4 | 508845 |  | 3 | 21WP | 430 | 473 | 0 | 96.6 | 98.3 | 98.3 | [7 empty] | CATEGORYB | NONSINGLE | 87284 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | DIANA 4 - DIANA 3 - 3 | E | AEPW | AEPW |  |  | 1 | 508832 | DIANA 7 | 508831 | DIANA 4 | 508845 |  | 3 | 25SP | 430 | 473 | 0 |  | 96.6 | 96.6 | [7 empty] | CATEGORYB | NONSINGLE | 87284 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | DIANA 7 - DIANA 3 - 3 | E | AEPW | AEPW |  |  | 1 | 508832 | DIANA 7 | 508831 | DIANA 4 | 508845 |  | 3 | 20WP | 430 | 473 | 0 | 102.7 | 96.7 | 96.7 | [7 empty] | CATEGORYB | NONSINGLE | 87284 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | DIANA 7 - DIANA 3 - 3 | E | AEPW | AEPW |  |  | 1 | 508832 | DIANA 7 | 508831 | DIANA 4 | 508845 |  | 3 | 25SP | 430 | 473 | 0 |  | 98.7 | 98.7 | [7 empty] | CATEGORYB | NONSINGLE | 84179 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | DIXGREENRVR7 - WSTMD1 7 - 1 | E | MDU | MDU |  |  | 0 | 661021 | WSTMD1 7 | 661020 | DIXGREENRVR7 | 0 |  | 1 | 25SP | 102 | 102 | 0 | 95.1 | 22.387 | 97.4 | [7 empty] | CATEGORYB | NONSINGLE | 70907 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | DIXGREENRVR7 - WSTMD1 7 - 1 | E | MDU | MDU |  |  | 0 | 661021 | WSTMD1 7 | 661020 | DIXGREENRVR7 | 0 |  | 1 | 25SP | 102 | 102 | 0 | 95.1 | 22.387 | 97.4 | [7 empty] | CATEGORYB | NONSINGLE | 70907 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | DURANTP4 - SCLMNJC4 - 1 | E | WFEC | WFEC |  |  | 0 | 521049 | SCLMNJC4 | 520884 | DURANTP4 | 0 |  | 1 | 22LP | 287 | 287 | 0 |  | 15.0343 | 98.2 | [7 empty] | CATEGORYB | NONSINGLE | 81723 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | DVISION4 - HAYMAKR4 - 1 | E | OKGE | OKGE |  |  | 0 | 514863 | HAYMAKR4 | 514853 | DVISION4 | 0 |  | 1 | 22LP | 268 | 308 | 0 | 80.5 | 29.9196 | 99.9 | [7 empty] | CATEGORYB | NONSINGLE | 81738 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | DVISION4 - HAYMAKR4 - 1 | E | OKGE | OKGE |  |  | 0 | 514863 | HAYMAKR4 | 514853 | DVISION4 | 0 |  | 1 | 30LP | 268 | 308 | 0 | 78.9 | 28.9705 | 97 | [7 empty] | CATEGORYB | NONSINGLE | 81726 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | DVISION4 - MUSTANG4 - 1 | E | OKGE | OKGE |  |  | 0 | 514853 | DVISION4 | 514861 | MUSTANG4 | 0 |  | 1 | 30LP | 268 | 308 | 0 | 79.3 | 33.3542 | 97.3 | [7 empty] | CATEGORYB | NONSINGLE | 81726 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | EAGLCHF2 - RNGWODJ2 - 1 | E | WFEC | WFEC |  |  | 0 | 521039 | RNGWODJ2 | 520890 | EAGLCHF2 | 0 |  | 1 | 21LP | 29 | 29 | 0 |  | 21.5754 | 97.9 | [7 empty] | CATEGORYB | NONSINGLE | 90675 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | EAGLCHF2 - RNGWODJ2 - 1 | E | WFEC | WFEC |  |  | 0 | 521039 | RNGWODJ2 | 520890 | EAGLCHF2 | 0 |  | 1 | 21LP | 29 | 29 | 0 |  | 21.5754 | 97.6 | [7 empty] | CATEGORYB | SINGLE | MENOTAP4 - CLEOPLT4 - 1 | 0 | 514789 | MENOTAP4 | 515562 | CLEOPLT4 | 0 |  | 1 | Transfer Loading < 100%
2019-AG2 | EAGLCHF2 - RNGWODJ2 - 1 | E | WFEC | WFEC |  |  | 0 | 521039 | RNGWODJ2 | 520890 | EAGLCHF2 | 0 |  | 1 | 21WP | 29 | 29 | 0 |  | 15.9232 | 98.7 | [7 empty] | CATEGORYB | SINGLE | CLEOCOR4 - CLEOPLT4 - 1 | 0 | 514778 | CLEOCOR4 | 515562 | CLEOPLT4 | 0 |  | 1 | Transfer Loading < 100%
2019-AG2 | EAGLCHF2 - RNGWODJ2 - 1 | E | WFEC | WFEC |  |  | 0 | 521039 | RNGWODJ2 | 520890 | EAGLCHF2 | 0 |  | 1 | 21WP | 29 | 29 | 0 |  | 15.9232 | 98.2 | [7 empty] | CATEGORYB | SINGLE | MENOTAP4 - CLEOPLT4 - 1 | 0 | 514789 | MENOTAP4 | 515562 | CLEOPLT4 | 0 |  | 1 | Transfer Loading < 100%
2019-AG2 | EAGLCHF2 - RNGWODJ2 - 1 | E | WFEC | WFEC |  |  | 0 | 521039 | RNGWODJ2 | 520890 | EAGLCHF2 | 0 |  | 1 | 22WP | 29 | 29 | 0 |  | 14.4025 | 96.6 | [7 empty] | CATEGORYB | SINGLE | CLEOCOR4 - CLEOPLT4 - 1 | 0 | 514778 | CLEOCOR4 | 515562 | CLEOPLT4 | 0 |  | 1 | Transfer Loading < 100%
2019-AG2 | EAGLCHF2 - RNGWODJ2 - 1 | E | WFEC | WFEC |  |  | 0 | 521039 | RNGWODJ2 | 520890 | EAGLCHF2 | 0 |  | 1 | 22WP | 29 | 29 | 0 |  | 14.4025 | 96.1 | [7 empty] | CATEGORYB | SINGLE | MENOTAP4 - CLEOPLT4 - 1 | 0 | 514789 | MENOTAP4 | 515562 | CLEOPLT4 | 0 |  | 1 | Transfer Loading < 100%
2019-AG2 | EAGLCHF2 - RNGWODJ2 - 1 | E | WFEC | WFEC |  |  | 0 | 521039 | RNGWODJ2 | 520890 | EAGLCHF2 | 0 |  | 1 | 30LP | 29 | 29 | 0 |  | 16.2421 | 98.2 | [7 empty] | CATEGORYB | NONSINGLE | 90675 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | EAGLCHF2 - RNGWODJ2 - 1 | E | WFEC | WFEC |  |  | 0 | 521039 | RNGWODJ2 | 520890 | EAGLCHF2 | 0 |  | 1 | 30LP | 29 | 29 | 0 |  | 16.2421 | 97.9 | [7 empty] | CATEGORYB | SINGLE | MENOTAP4 - CLEOPLT4 - 1 | 0 | 514789 | MENOTAP4 | 515562 | CLEOPLT4 | 0 |  | 1 | Transfer Loading < 100%
2019-AG2 | EARLSBORO 4 - MAUD 4 - 1 | E | OKGE | AEPW |  |  | 0 | 515055 | MAUD 4 | 510948 | EARLSBORO 4 | 0 |  | 1 | 25LP | 143 | 143 | 0 | 74.9 | 51.541 | 96.6 | [7 empty] | CATEGORYB | NONSINGLE | 81740 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | ESTGEN4 - ESTGAS1 - 1 | E | AEPW | AEPW |  |  | 0 | 506749 | ESTGAS1 | 508583 | ESTGEN4 | 0 |  | 1 | 20SP | 210 | 210 | 0 | 73.9 | 64.3002 | 97 | [7 empty] | CATEGORYB | NONSINGLE | 6420 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | ESTGEN4 - ESTGAS1 - 1 | E | AEPW | AEPW |  |  | 0 | 506749 | ESTGAS1 | 508583 | ESTGEN4 | 0 |  | 1 | 21SP | 210 | 210 | 0 | 72.6 | 64.3029 | 97.3 | [7 empty] | CATEGORYB | NONSINGLE | 84117 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | ESTGEN4 - ESTGAS2 - 1 | E | AEPW | AEPW |  |  | 0 | 506750 | ESTGAS2 | 508583 | ESTGEN4 | 0 |  | 1 | 20SP | 210 | 210 | 0 | 73.9 | 64.3002 | 97 | [7 empty] | CATEGORYB | NONSINGLE | 5749 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | ESTGEN4 - ESTGAS2 - 1 | E | AEPW | AEPW |  |  | 0 | 506750 | ESTGAS2 | 508583 | ESTGEN4 | 0 |  | 1 | 21SP | 210 | 210 | 0 | 72.6 | 64.3029 | 97.3 | [7 empty] | CATEGORYB | NONSINGLE | 84117 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | FAIRNEO2 - FAIRTAP2 - 1 | E | GRDA | GRDA |  |  | 0 | 512708 | FAIRTAP2 | 512691 | FAIRNEO2 | 0 |  | 1 | 21SP | 72 | 72 | 0 | 94.3 | 19.93 | 96.1 | [7 empty] | CATEGORYB | NONSINGLE | 81781 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | FAIRNEO2 - FAIRTAP2 - 1 | E | GRDA | GRDA |  |  | 0 | 512708 | FAIRTAP2 | 512691 | FAIRNEO2 | 0 |  | 1 | 22SP | 72 | 72 | 0 | 93.8 | 19.5266 | 95.5 | [7 empty] | CATEGORYB | NONSINGLE | 81781 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | FAIRNEO2 - FAIRTAP2 - 1 | E | GRDA | GRDA |  |  | 0 | 512708 | FAIRTAP2 | 512691 | FAIRNEO2 | 0 |  | 1 | 25SP | 72 | 72 | 0 | 94 | 18.7566 | 95.9 | [7 empty] | CATEGORYB | NONSINGLE | 81781 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | FAIRNEO2 - FAIRTAP2 - 1 | E | GRDA | GRDA |  |  | 0 | 512708 | FAIRTAP2 | 512691 | FAIRNEO2 | 0 |  | 1 | 30SP | 72 | 72 | 0 | 94.4 | 17.7001 | 97.1 | [7 empty] | CATEGORYB | NONSINGLE | 81781 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | FAIRVEW2 - RNGWODJ2 - 1 | E | WFEC | WFEC |  |  | 0 | 521039 | RNGWODJ2 | 520909 | FAIRVEW2 | 0 |  | 1 | 21LP | 37 | 42 | 0 |  | 14.5413 | 95.1 | [7 empty] | CATEGORYB | SINGLE | CLEOCOR4 - CLEOPLT4 - 1 | 0 | 514778 | CLEOCOR4 | 515562 | CLEOPLT4 | 0 |  | 1 | Transfer Loading < 100%
2019-AG2 | FAIRVEW2 - RNGWODJ2 - 1 | E | WFEC | WFEC |  |  | 0 | 521039 | RNGWODJ2 | 520909 | FAIRVEW2 | 0 |  | 1 | 30SP | 37 | 42 | 0 |  | 33.3862 | 95.1 | [7 empty] | CATEGORYB | SINGLE | CLEOCOR4 - CLEOPLT4 - 1 | 0 | 514778 | CLEOCOR4 | 515562 | CLEOPLT4 | 0 |  | 1 | Transfer Loading < 100%
2019-AG2 | FTSMITH8 - 8ANO% - 1 | E | EES-EAI | OKGE |  |  | 0 | 337909 | 8ANO% | 515305 | FTSMITH8 | 0 |  | 1 | 21SP | 1299 | 1299 | 0 | 98.5 | 3.7062e-14 | 95.3 | [7 empty] | CATEGORYB | NONSINGLE | 92673 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | FTSMITH8 - 8ANO% - 1 | E | EES-EAI | OKGE |  |  | 0 | 337909 | 8ANO% | 515305 | FTSMITH8 | 0 |  | 1 | 30SP | 1299 | 1299 | 0 | 103.5 | 1.4611e-13 | 97.3 | [7 empty] | CATEGORYB | NONSINGLE | 92673 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | Kingfisher - KingfisherXFMR1 - 1 | E | WFEC | WFEC |  |  | 0 | 587941 | KingfisherXFMR1 | 587940 | Kingfisher | 0 |  | 1 | 21WP | 300 | 300 | 0 |  | 0.0035088 | 95.5 | [7 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | Kingfisher - KingfisherXFMR1 - 2 | E | WFEC | WFEC |  |  | 0 | 587941 | KingfisherXFMR2 | 587940 | Kingfisher | 0 |  | 1 | 22LP | 300 | 300 | 0 |  | 0.0035088 | 95.3 | [7 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | Kingfisher - KingfisherXFMR1 - 3 | E | WFEC | WFEC |  |  | 0 | 587941 | KingfisherXFMR3 | 587940 | Kingfisher | 0 |  | 1 | 22SP | 300 | 300 | 0 |  | 0.0035088 | 95.2 | [7 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | Kingfisher - KingfisherXFMR1 - 4 | E | WFEC | WFEC |  |  | 0 | 587941 | KingfisherXFMR4 | 587940 | Kingfisher | 0 |  | 1 | 22WP | 300 | 300 | 0 |  | 0.0035088 | 95.7 | [7 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | Kingfisher - KingfisherXFMR1 - 5 | E | WFEC | WFEC |  |  | 0 | 587941 | KingfisherXFMR5 | 587940 | Kingfisher | 0 |  | 1 | 22WP | 300 | 300 | 0 |  | 0.0035088 | 95.3 | [7 empty] | CATEGORYB | NONSINGLE | 92695 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | Kingfisher - KingfisherXFMR1 - 6 | E | WFEC | WFEC |  |  | 0 | 587941 | KingfisherXFMR6 | 587940 | Kingfisher | 0 |  | 1 | 25LP | 300 | 300 | 0 |  | 0.0035088 | 95.5 | [7 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | Kingfisher - KingfisherXFMR1 - 7 | E | WFEC | WFEC |  |  | 0 | 587941 | KingfisherXFMR7 | 587940 | Kingfisher | 0 |  | 1 | 25SP | 300 | 300 | 0 |  | 0.0035088 | 95.3 | [7 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | Kingfisher - KingfisherXFMR1 - 8 | E | WFEC | WFEC |  |  | 0 | 587941 | KingfisherXFMR8 | 587940 | Kingfisher | 0 |  | 1 | 25WP | 300 | 300 | 0 |  | 0.0035088 | 95.6 | [7 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | Kingfisher - KingfisherXFMR1 - 9 | E | WFEC | WFEC |  |  | 0 | 587941 | KingfisherXFMR9 | 587940 | Kingfisher | 0 |  | 1 | 30LP | 300 | 300 | 0 |  | 0.017544 | 95.8 | [7 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | Kingfisher - KingfisherXFMR1 - 10 | E | WFEC | WFEC |  |  | 0 | 587941 | KingfisherXFMR10 | 587940 | Kingfisher | 0 |  | 1 | 30LP | 300 | 300 | 0 |  | 0.017544 | 95.4 | [7 empty] | CATEGORYB | NONSINGLE | 81732 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | Kingfisher - KingfisherXFMR1 - 11 | E | WFEC | WFEC |  |  | 0 | 587941 | KingfisherXFMR11 | 587940 | Kingfisher | 0 |  | 1 | 30LP | 300 | 300 | 0 |  | 0.017544 | 95.3 | [7 empty] | CATEGORYB | NONSINGLE | 81743 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | Kingfisher - KingfisherXFMR1 - 12 | E | WFEC | WFEC |  |  | 0 | 587941 | KingfisherXFMR12 | 587940 | Kingfisher | 0 |  | 1 | 30SP | 300 | 300 | 0 |  | 0.0035088 | 95.3 | [7 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | Kingfisher - KingfisherXFMR1 - 13 | E | WFEC | WFEC |  |  | 0 | 587941 | KingfisherXFMR13 | 587940 | Kingfisher | 0 |  | 1 | 30WP | 300 | 300 | 0 |  | 0.0035088 | 95.4 | [7 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | GENTLMN3 - GGS T1 - 1 | E | NPPD | NPPD |  |  | 1 | 640184 | GENTLMN4 | 640183 | GENTLMN3 | 640185 |  | 1 | 20WP | 336 | 336 | 0 | 97.8 | 29.3256 | 95.7 | [7 empty] | CATEGORYB | NONSINGLE | 85242 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | GENTLMN3 - GGS T1 - 1 | E | NPPD | NPPD |  |  | 1 | 640184 | GENTLMN4 | 640183 | GENTLMN3 | 640185 |  | 1 | 21WP | 336 | 336 | 0 | 102.7 | 30.9453 | 99.2 | [7 empty] | CATEGORYB | NONSINGLE | 85242 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | GENTLMN4 - GENTLM1G - 1 | E | NPPD | NPPD |  |  | 0 | 640010 | GENTLM1G | 640184 | GENTLMN4 | 0 |  | 1 | 25SP | 710 | 710 | 0 | 95.9 | 93.7766 | 96.4 | [7 empty] | CATEGORYB | NONSINGLE | 85487 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | GENTLMN4 - GENTLM1G - 1 | E | NPPD | NPPD |  |  | 0 | 640010 | GENTLM1G | 640184 | GENTLMN4 | 0 |  | 1 | 25SP | 710 | 710 | 0 | 95.6 | 93.7766 | 96.1 | [7 empty] | CATEGORYB | NONSINGLE | 85470 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | GENTLMN4 - GENTLM1G - 1 | E | NPPD | NPPD |  |  | 0 | 640010 | GENTLM1G | 640184 | GENTLMN4 | 0 |  | 1 | 25SP | 710 | 710 | 0 | 95 | 93.7766 | 95.5 | [7 empty] | CATEGORYB | NONSINGLE | 85244 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | GENTLMN4 - GENTLM1G - 1 | E | NPPD | NPPD |  |  | 0 | 640010 | GENTLM1G | 640184 | GENTLMN4 | 0 |  | 1 | 30SP | 710 | 710 | 0 | 95.7 | 93.7757 | 96.4 | [7 empty] | CATEGORYB | NONSINGLE | 85487 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | GENTLMN4 - GENTLM1G - 1 | E | NPPD | NPPD |  |  | 0 | 640010 | GENTLM1G | 640184 | GENTLMN4 | 0 |  | 1 | 30SP | 710 | 710 | 0 | 95.5 | 93.7757 | 96 | [7 empty] | CATEGORYB | NONSINGLE | 85470 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | GENTLMN4 - GGS T1 - 1 | E | NPPD | NPPD |  |  | 1 | 640184 | GENTLMN4 | 640183 | GENTLMN3 | 640185 |  | 1 | 20WP | 336 | 336 | 0 | 97.6 | 29.3256 | 95.4 | [7 empty] | CATEGORYB | NONSINGLE | 85242 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | GENTLMN4 - GGS T1 - 1 | E | NPPD | NPPD |  |  | 1 | 640184 | GENTLMN4 | 640183 | GENTLMN3 | 640185 |  | 1 | 21WP | 336 | 336 | 0 | 102.4 | 30.9453 | 99 | [7 empty] | CATEGORYB | NONSINGLE | 85242 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | GRAND W5 - CROSTWN5 - 1 | E | KCPL | KCPL |  |  | 0 | 542988 | GRAND W5 | 542990 | CROSTWN5 | 0 |  | 1 | 20WP | 257 | 257 | 0 | 98.9 | 12.9675 | 98.8 | [7 empty] | CATEGORYB | NONSINGLE | 104659 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | GRAND W5 - CROSTWN5 - 1 | E | KCPL | KCPL |  |  | 0 | 542988 | GRAND W5 | 542990 | CROSTWN5 | 0 |  | 1 | 30WP | 257 | 257 | 0 | 96.1 | 10.7622 | 95.9 | [7 empty] | CATEGORYB | NONSINGLE | 104658 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | GRDA1 5 - GRDAUTO1 - 1 | E | GRDA | GRDA |  |  | 1 | 512650 | GRDA1 7 | 512656 | GRDA1 5 | 512821 |  | 1 | 30SP | 448 | 478 | 0 | 100.5 | 95.2 | 95.2 | [7 empty] | CATEGORYB | NONSINGLE | 81921 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | GRDA1 5 - GRDAUTO2 - 2 | E | GRDA | GRDA |  |  | 1 | 512650 | GRDA1 7 | 512656 | GRDA1 5 | 512826 |  | 2 | 30SP | 448 | 478 | 0 | 101 | 95.7 | 95.7 | [7 empty] | CATEGORYB | NONSINGLE | 82048 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | GRDA1 7 - GRDAUTO1 - 1 | E | GRDA | GRDA |  |  | 1 | 512650 | GRDA1 7 | 512656 | GRDA1 5 | 512821 |  | 1 | 30SP | 448 | 478 | 0 | 101.7 | 96.3 | 96.3 | [7 empty] | CATEGORYB | NONSINGLE | 81921 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | GRDA1 7 - GRDAUTO2 - 2 | E | GRDA | GRDA |  |  | 1 | 512650 | GRDA1 7 | 512656 | GRDA1 5 | 512826 |  | 2 | 30SP | 448 | 478 | 0 | 102.2 | 96.8 | 96.8 | [7 empty] | CATEGORYB | NONSINGLE | 81863 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | GREC TAP7 - GRECCTG_1 - 1 | E | GRDA | GRDA |  |  | 0 | 512614 | GRECCTG_1 | 512865 | GREC TAP7 | 0 |  | 1 | 20SP | 450 | 450 | 0 | 90.4 | 71.8512 | 98 | [7 empty] | CATEGORYB | NONSINGLE | 103759 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | GREC TAP7 - GRECCTG_1 - 1 | E | GRDA | GRDA |  |  | 0 | 512614 | GRECCTG_1 | 512865 | GREC TAP7 | 0 |  | 1 | 22WP | 450 | 450 | 0 | 90.6 | 71.852 | 96.2 | [7 empty] | CATEGORYB | NONSINGLE | 103759 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | GREC TAP7 - GRECCTG_1 - 1 | E | GRDA | GRDA |  |  | 0 | 512614 | GRECCTG_1 | 512865 | GREC TAP7 | 0 |  | 1 | 25WP | 450 | 450 | 0 | 90.6 | 71.8491 | 99.1 | [7 empty] | CATEGORYB | NONSINGLE | 103759 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | GRNWD 5 - LEESUM 5 - 1 | E | KCPL | KCPL |  |  | 0 | 541218 | GRNWD 5 | 541233 | LEESUM 5 | 0 |  | 1 | 20SP | 446 | 446 | 0 | 96.5 | 72.5227 | 98.4 | [7 empty] | CATEGORYB | SINGLE | LKWINBG5 - HOOKRD 5 - 1 | 0 | 541243 | LKWINBG5 | 541249 | HOOKRD 5 | 0 |  | 1 | Transfer Loading < 100%
2019-AG2 | GRNWD 5 - LEESUM 5 - 1 | E | KCPL | KCPL |  |  | 0 | 541218 | GRNWD 5 | 541233 | LEESUM 5 | 0 |  | 1 | 20SP | 446 | 446 | 0 | 93.3 | 72.5227 | 95.5 | [7 empty] | CATEGORYB | NONSINGLE | 84390 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | HAYMAKR4 - CIMARON4 - 1 | E | OKGE | OKGE |  |  | 0 | 514898 | CIMARON4 | 514863 | HAYMAKR4 | 0 |  | 1 | 22SP | 268 | 308 | 0 | 73.8 | 43.4439 | 96.6 | [7 empty] | CATEGORYB | NONSINGLE | 81726 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | HAYMAKR4 - CIMARON4 - 1 | E | OKGE | OKGE |  |  | 0 | 514898 | CIMARON4 | 514863 | HAYMAKR4 | 0 |  | 1 | 25SP | 268 | 308 | 0 | 80.8 | 40.0138 | 98.9 | [7 empty] | CATEGORYB | NONSINGLE | 81738 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | HAYMAKR4 - CIMARON4 - 1 | E | OKGE | OKGE |  |  | 0 | 514898 | CIMARON4 | 514863 | HAYMAKR4 | 0 |  | 1 | 30LP | 268 | 308 | 0 | 81.5 | 32.1177 | 99.7 | [7 empty] | CATEGORYB | NONSINGLE | 81726 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | HOYT 7 - JEC N 7 - 1 | E | WERE | WERE |  |  | 0 | 532766 | JEC N 7 | 532765 | HOYT 7 | 0 |  | 1 | 20SP | 1036 | 1076 | 0 | 98.8 | 68.7433 | 98 | [7 empty] | CATEGORYB | NONSINGLE | 104458 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | HOYT 7 - JEC N 7 - 1 | E | WERE | WERE |  |  | 0 | 532766 | JEC N 7 | 532765 | HOYT 7 | 0 |  | 1 | 21SP | 1036 | 1076 | 0 | 91.4 | 72.0297 | 96.5 | [7 empty] | CATEGORYB | NONSINGLE | 104720 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | HOYT 7 - JEC N 7 - 1 | E | WERE | WERE |  |  | 0 | 532766 | JEC N 7 | 532765 | HOYT 7 | 0 |  | 1 | 22SP | 1036 | 1076 | 0 |  | 70.7444 | 95.4 | [7 empty] | CATEGORYB | NONSINGLE | 104727 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | HOYT 7 - JEC N 7 - 1 | E | WERE | WERE |  |  | 0 | 532766 | JEC N 7 | 532765 | HOYT 7 | 0 |  | 1 | 25SP | 1036 | 1076 | 0 | 90.1 | 71.9468 | 98.2 | [7 empty] | CATEGORYB | NONSINGLE | 104720 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | HOYT 7 - JEC N 7 - 1 | E | WERE | WERE |  |  | 0 | 532766 | JEC N 7 | 532765 | HOYT 7 | 0 |  | 1 | 30SP | 1036 | 1076 | 0 | 90.2 | 71.5208 | 99.2 | [7 empty] | CATEGORYB | NONSINGLE | 104728 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | HOYT 7 - JEC N 7 - 1 | E | WERE | WERE |  |  | 0 | 532766 | JEC N 7 | 532765 | HOYT 7 | 0 |  | 1 | 30SP | 1036 | 1076 | 0 | 89.4 | 71.5208 | 98.2 | [7 empty] | CATEGORYB | NONSINGLE | 92477 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | HSNVL 5 - 2SHARSNV - 1 | E | KCPL | AECI |  |  | 0 | 541239 | HSNVL 5 | 300709 | 2SHARSNV | 0 |  | 1 | 20WP | 64 | 64 | 0 | 105.8 | 76.672 | 97.9 | [7 empty] | CATEGORYB | SINGLE | ARCHIE 5 - ADRIAN 5 - 1 | 0 | 541207 | ARCHIE 5 | 541240 | ADRIAN 5 | 0 |  | 1 | Transfer Loading < 100%
2019-AG2 | HSNVL 5 - 2SHARSNV - 1 | E | KCPL | AECI |  |  | 0 | 541239 | HSNVL 5 | 300709 | 2SHARSNV | 0 |  | 1 | 21WP | 64 | 64 | 0 | 101.3 | 72.3574 | 96.4 | [7 empty] | CATEGORYB | SINGLE | ARCHIE 5 - ADRIAN 5 - 1 | 0 | 541207 | ARCHIE 5 | 541240 | ADRIAN 5 | 0 |  | 1 | Transfer Loading < 100%
2019-AG2 | HSNVL 5 - 2SHARSNV - 1 | E | KCPL | AECI |  |  | 0 | 541239 | HSNVL 5 | 300709 | 2SHARSNV | 0 |  | 1 | 22WP | 64 | 64 | 0 | 99.5 | 70.437 | 95.7 | [7 empty] | CATEGORYB | SINGLE | ARCHIE 5 - ADRIAN 5 - 1 | 0 | 541207 | ARCHIE 5 | 541240 | ADRIAN 5 | 0 |  | 1 | Transfer Loading < 100%
2019-AG2 | IPC-DOM4 - REDSPRG4 - 1 | E | AEPW | AEPW |  |  | 0 | 508075 | REDSPRG4 | 508060 | IPC-DOM4 | 0 |  | 1 | 22LP | 263 | 263 | 0 | 84.3 | 38.0156 | 96.3 | [7 empty] | CATEGORYB | NONSINGLE | 84111 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | IPC-DOM4 - REDSPRG4 - 1 | E | AEPW | AEPW |  |  | 0 | 508075 | REDSPRG4 | 508060 | IPC-DOM4 | 0 |  | 1 | 25LP | 263 | 263 | 0 | 88.4 | 38.9199 | 98.1 | [7 empty] | CATEGORYB | NONSINGLE | 84111 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | JARBALO3 - EFAIRMNT3 - 1 | E | WERE | WERE |  |  | 0 | 533244 | JARBALO3 | 533246 | EFAIRMNT3 | 0 |  | 1 | 21SP | 179 | 179 | 0 | 99.1 | 12.7273 | 99.1 | [7 empty] | CATEGORYB | NONSINGLE | 8657 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | JARBALO3 - EFAIRMNT3 - 1 | E | WERE | WERE |  |  | 0 | 533244 | JARBALO3 | 533246 | EFAIRMNT3 | 0 |  | 1 | 22SP | 179 | 179 | 0 | 96.6 | 12.6306 | 97.1 | [7 empty] | CATEGORYB | NONSINGLE | 8657 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | JARBALO3 - EFAIRMNT3 - 1 | E | WERE | WERE |  |  | 0 | 533244 | JARBALO3 | 533246 | EFAIRMNT3 | 0 |  | 1 | 25SP | 179 | 179 | 0 | 98.8 | 13.2266 | 98.8 | [7 empty] | CATEGORYB | NONSINGLE | 8657 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | JOP145 5 - STL439 5 - 1 | E | EMDE | EMDE |  |  | 0 | 547498 | STL439 5 | 547470 | JOP145 5 | 0 |  | 1 | 21SP | 290 | 290 | 0 | 95.8 | 45.0774 | 95.5 | [7 empty] | CATEGORYB | NONSINGLE | 87087 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | JOP145 5 - STL439 5 - 1 | E | EMDE | EMDE |  |  | 0 | 547498 | STL439 5 | 547470 | JOP145 5 | 0 |  | 1 | 22SP | 290 | 290 | 0 | 96.4 | 45.4951 | 96.8 | [7 empty] | CATEGORYB | NONSINGLE | 87087 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | JOP145 5 - STL439 5 - 1 | E | EMDE | EMDE |  |  | 0 | 547498 | STL439 5 | 547470 | JOP145 5 | 0 |  | 1 | 25SP | 290 | 290 | 0 | 98.3 | 47.3605 | 98.8 | [7 empty] | CATEGORYB | NONSINGLE | 87087 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | KELLY 3 - GOFF 3 - 1 | E | WERE | WERE |  |  | 0 | 533331 | GOFF 3 | 533217 | KELLY 3 | 0 |  | 1 | 21SP | 86 | 92 | 0 | 93.1 | 59.2479 | 96.6 | [7 empty] | CATEGORYB | NONSINGLE | 8585 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | KELLY 3 - GOFF 3 - 1 | E | WERE | WERE |  |  | 0 | 533331 | GOFF 3 | 533217 | KELLY 3 | 0 |  | 1 | 22SP | 86 | 92 | 0 | 87.6 | 56.7926 | 96.5 | [7 empty] | CATEGORYB | NONSINGLE | 8585 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | KELLY 3 - GOFF 3 - 1 | E | WERE | WERE |  |  | 0 | 533331 | GOFF 3 | 533217 | KELLY 3 | 0 |  | 1 | 25SP | 86 | 92 | 0 | 91.7 | 68.885 | 96 | [7 empty] | CATEGORYB | NONSINGLE | 84741 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | KELLY 3 - GOFF 3 - 1 | E | WERE | WERE |  |  | 0 | 533331 | GOFF 3 | 533217 | KELLY 3 | 0 |  | 1 | 30SP | 86 | 92 | 0 | 89.5 | 67.4389 | 95.1 | [7 empty] | CATEGORYB | NONSINGLE | 84741 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | L GROVE3 - KERR GR3 - 1 | E | GRDA | AEPW |  |  | 0 | 512634 | KERR GR3 | 510423 | L GROVE3 | 0 |  | 1 | 22SP | 140 | 140 | 0 | 74.4 | 70.6362 | 96.9 | [7 empty] | CATEGORYB | NONSINGLE | 81789 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | L GROVE3 - KERR GR3 - 1 | E | GRDA | AEPW |  |  | 0 | 512634 | KERR GR3 | 510423 | L GROVE3 | 0 |  | 1 | 22SP | 140 | 140 | 0 | 92.6 | 70.6362 | 96.1 | [7 empty] | CATEGORYB | NONSINGLE | 104003 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | L GROVE3 - KERR GR3 - 1 | E | GRDA | AEPW |  |  | 0 | 512634 | KERR GR3 | 510423 | L GROVE3 | 0 |  | 1 | 22SP | 140 | 140 | 0 |  | 70.6362 | 95.9 | [7 empty] | CATEGORYB | SINGLE | INOLATP4 - ROCKPT-4 - 1 | 0 | 509752 | INOLATP4 | 510437 | ROCKPT-4 | 0 |  | 1 | Transfer Loading < 100%
2019-AG2 | L GROVE3 - KERR GR3 - 1 | E | GRDA | AEPW |  |  | 0 | 512634 | KERR GR3 | 510423 | L GROVE3 | 0 |  | 1 | 25SP | 140 | 140 | 0 | 75 | 70.7994 | 97.3 | [7 empty] | CATEGORYB | NONSINGLE | 81789 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | L GROVE3 - KERR GR3 - 1 | E | GRDA | AEPW |  |  | 0 | 512634 | KERR GR3 | 510423 | L GROVE3 | 0 |  | 1 | 25SP | 140 | 140 | 0 | 92.6 | 70.7994 | 96.3 | [7 empty] | CATEGORYB | NONSINGLE | 104003 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | L GROVE3 - KERR GR3 - 1 | E | GRDA | AEPW |  |  | 0 | 512634 | KERR GR3 | 510423 | L GROVE3 | 0 |  | 1 | 25SP | 140 | 140 | 0 |  | 70.7994 | 96.1 | [7 empty] | CATEGORYB | SINGLE | INOLATP4 - ROCKPT-4 - 1 | 0 | 509752 | INOLATP4 | 510437 | ROCKPT-4 | 0 |  | 1 | Transfer Loading < 100%
2019-AG2 | L GROVE3 - KERR GR3 - 1 | E | GRDA | AEPW |  |  | 0 | 512634 | KERR GR3 | 510423 | L GROVE3 | 0 |  | 1 | 30SP | 140 | 140 | 0 | 77.1 | 72.7185 | 98 | [7 empty] | CATEGORYB | NONSINGLE | 81789 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | L GROVE3 - KERR GR3 - 1 | E | GRDA | AEPW |  |  | 0 | 512634 | KERR GR3 | 510423 | L GROVE3 | 0 |  | 1 | 30SP | 140 | 140 | 0 | 93.9 | 72.7185 | 97.9 | [7 empty] | CATEGORYB | NONSINGLE | 104003 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | L GROVE3 - KERR GR3 - 1 | E | GRDA | AEPW |  |  | 0 | 512634 | KERR GR3 | 510423 | L GROVE3 | 0 |  | 1 | 30SP | 140 | 140 | 0 |  | 72.7185 | 97.4 | [7 empty] | CATEGORYB | SINGLE | INOLATP4 - ROCKPT-4 - 1 | 0 | 509752 | INOLATP4 | 510437 | ROCKPT-4 | 0 |  | 1 | Transfer Loading < 100%
2019-AG2 | LONGWD 4 - LONGWOOD - 1 | E | AEPW | AEPW |  |  | 1 | 508809 | LONGWD 7 | 508808 | LONGWD 4 | 508819 |  | 1 | 21WP | 504.7 | 526.6 | 0 | 87.2 | 98.9 | 98.9 | [7 empty] | CATEGORYB | NONSINGLE | 84108 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | LONGWD 4 - OAKPH 4 - 1 | E | AEPW | AEPW |  |  | 0 | 508808 | LONGWD 4 | 508816 | OAKPH 4 | 0 |  | 1 | 25WP | 234 | 234 | 0 | 89.8 | 44.0709 | 96.7 | [7 empty] | CATEGORYB | NONSINGLE | 84108 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | LSSOUTH4 - DIANA 4 - 1 | E | AEPW | AEPW |  |  | 0 | 508831 | DIANA 4 | 508297 | LSSOUTH4 | 0 |  | 1 | 22WP | 287 | 316 | 0 |  | 37.079 | 95.1 | [7 empty] | CATEGORYB | NONSINGLE | 104728 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | LSSOUTH4 - DIANA 4 - 1 | E | AEPW | AEPW |  |  | 0 | 508831 | DIANA 4 | 508297 | LSSOUTH4 | 0 |  | 1 | 25SP | 245 | 287 | 0 |  | 41.4832 | 99.8 | [7 empty] | CATEGORYB | NONSINGLE | 104727 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | LULA 4 - STNWLSW4 - 1 | E | OKGE | WFEC |  |  | 0 | 515192 | LULA 4 | 521071 | STNWLSW4 | 0 |  | 1 | 22LP | 200 | 234 | 0 |  | 30.6453 | 98.6 | [7 empty] | CATEGORYB | NONSINGLE | 81723 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | MARMTNE5 - MARMTNW5 - Z1 | E | WERE | WERE |  |  | 0 | 532934 | MARMTNE5 | 532935 | MARMTNW5 | 0 |  | Z1 | 30LP | 160 | 189 | 0 |  | 39.0993 | 95.3 | [7 empty] | CATEGORYB | SINGLE | FRANKLIN5 - G17-005-TAP - 1 | 0 | 532938 | FRANKLIN5 | 588504 | G17-005-TAP | 0 |  | 1 | Transfer Loading < 100%
2019-AG2 | MARTCTY5 - STHTOWN5 - 1 | E | KCPL | KCPL |  |  | 0 | 541210 | MARTCTY5 | 542993 | STHTOWN5 | 0 |  | 1 | 20SP | 232 | 259 | 0 | 94.6 | 65.4274 | 95.5 | [7 empty] | CATEGORYB | NONSINGLE | 92340 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | MARTCTY5 - STHTOWN5 - 1 | E | KCPL | KCPL |  |  | 0 | 541210 | MARTCTY5 | 542993 | STHTOWN5 | 0 |  | 1 | 21SP | 232 | 259 | 0 | 97.2 | 69.8599 | 97.7 | [7 empty] | CATEGORYB | NONSINGLE | 92340 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | MARTCTY5 - STHTOWN5 - 1 | E | KCPL | KCPL |  |  | 0 | 541210 | MARTCTY5 | 542993 | STHTOWN5 | 0 |  | 1 | 21SP | 232 | 259 | 0 | 96.1 | 69.8599 | 96.6 | [7 empty] | CATEGORYB | NONSINGLE | 84358 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | MARTCTY5 - STHTOWN5 - 1 | E | KCPL | KCPL |  |  | 0 | 541210 | MARTCTY5 | 542993 | STHTOWN5 | 0 |  | 1 | 22SP | 232 | 259 | 0 | 90.9 | 65.2468 | 95.3 | [7 empty] | CATEGORYB | NONSINGLE | 84358 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | MARTCTY5 - STHTOWN5 - 1 | E | KCPL | KCPL |  |  | 0 | 541210 | MARTCTY5 | 542993 | STHTOWN5 | 0 |  | 1 | 25SP | 232 | 259 | 0 | 102.5 | 66.7405 | 97.5 | [7 empty] | CATEGORYB | NONSINGLE | 104180 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | MARTCTY5 - STHTOWN5 - 1 | E | KCPL | KCPL |  |  | 0 | 541210 | MARTCTY5 | 542993 | STHTOWN5 | 0 |  | 1 | 30SP | 232 | 259 | 0 | 94.6 | 58.1154 | 96.4 | [7 empty] | CATEGORYB | NONSINGLE | 104180 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | MIDLADN3 - MIDJ TX-1 - 1 | E | WERE | WERE |  |  | 1 | 532855 | MIDLAND6 | 533252 | MIDLADN3 | 532884 |  | 1 | 25SP | 280 | 308 | 0 | 92.4 | 52.9496 | 96.6 | [7 empty] | CATEGORYB | NONSINGLE | 4650 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | MIDLAND6 - MIDJ TX-1 - 1 | E | WERE | WERE |  |  | 1 | 532855 | MIDLAND6 | 533252 | MIDLADN3 | 532884 |  | 1 | 25SP | 280 | 308 | 0 | 92.4 | 52.9496 | 97.4 | [7 empty] | CATEGORYB | NONSINGLE | 4650 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | MIDLAND6 - MIDJ TX-1 - 1 | E | WERE | WERE |  |  | 1 | 532855 | MIDLAND6 | 533252 | MIDLADN3 | 532884 |  | 1 | 30SP | 280 | 308 | 0 | 90 | 51.1623 | 95.8 | [7 empty] | CATEGORYB | NONSINGLE | 4650 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | MIDWEST4 - FRNKLNS4 - 1 | E | OKGE | WFEC |  |  | 0 | 514946 | MIDWEST4 | 520917 | FRNKLNS4 | 0 |  | 1 | 22SP | 268 | 287 | 0 | 92.5 | 77.6673 | 95.7 | [7 empty] | CATEGORYB | NONSINGLE | 94256 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | MIDWEST4 - FRNKLNS4 - 1 | E | OKGE | WFEC |  |  | 0 | 514946 | MIDWEST4 | 520917 | FRNKLNS4 | 0 |  | 1 | 22SP | 268 | 287 | 0 | 88.5 | 77.6673 | 95.5 | [7 empty] | CATEGORYB | NONSINGLE | 92686 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | MIDWEST4 - FRNKLNS4 - 1 | E | OKGE | WFEC |  |  | 0 | 514946 | MIDWEST4 | 520917 | FRNKLNS4 | 0 |  | 1 | 22WP | 287 | 287 | 0 |  | 68.5066 | 99.8 | [7 empty] | CATEGORYB | SINGLE | CANADN-4 - CEDARLN4 - 1 | 0 | 514947 | CANADN-4 | 514948 | CEDARLN4 | 0 |  | 1 | Transfer Loading < 100%
2019-AG2 | MIDWEST4 - FRNKLNS4 - 1 | E | OKGE | WFEC |  |  | 0 | 514946 | MIDWEST4 | 520917 | FRNKLNS4 | 0 |  | 1 | 22WP | 287 | 287 | 0 | 75.4 | 68.5066 | 95.2 | [7 empty] | CATEGORYB | NONSINGLE | 92626 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | MIDWEST4 - FRNKLNS4 - 1 | E | OKGE | WFEC |  |  | 0 | 514946 | MIDWEST4 | 520917 | FRNKLNS4 | 0 |  | 1 | 25SP | 268 | 287 | 0 | 94.5 | 84.6876 | 97.4 | [7 empty] | CATEGORYB | NONSINGLE | 94256 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | MIDWEST4 - FRNKLNS4 - 1 | E | OKGE | WFEC |  |  | 0 | 514946 | MIDWEST4 | 520917 | FRNKLNS4 | 0 |  | 1 | 25SP | 268 | 287 | 0 | 87.1 | 84.6876 | 97.3 | [7 empty] | CATEGORYB | NONSINGLE | 92626 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | MIDWEST4 - FRNKLNS4 - 1 | E | OKGE | WFEC |  |  | 0 | 514946 | MIDWEST4 | 520917 | FRNKLNS4 | 0 |  | 1 | 25SP | 268 | 287 | 0 | 95.6 | 84.6876 | 97.1 | [7 empty] | CATEGORYB | SINGLE | MIDWEST4 - HOLLYWD4 - 1 | 0 | 514946 | MIDWEST4 | 514953 | HOLLYWD4 | 0 |  | 1 | Transfer Loading < 100%
2019-AG2 | MIDWEST4 - FRNKLNS4 - 1 | E | OKGE | WFEC |  |  | 0 | 514946 | MIDWEST4 | 520917 | FRNKLNS4 | 0 |  | 1 | 25WP | 287 | 287 | 0 |  | 66.7593 | 95.1 | [7 empty] | CATEGORYB | SINGLE | CANADN-4 - CEDARLN4 - 1 | 0 | 514947 | CANADN-4 | 514948 | CEDARLN4 | 0 |  | 1 | Transfer Loading < 100%
2019-AG2 | MIDWEST4 - FRNKLNS4 - 1 | E | OKGE | WFEC |  |  | 0 | 514946 | MIDWEST4 | 520917 | FRNKLNS4 | 0 |  | 1 | 30SP | 268 | 287 | 0 | 93.3 | 75.215 | 95.8 | [7 empty] | CATEGORYB | NONSINGLE | 94256 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | MOONLT 5 - BNSF 5 - 1 | E | KCPL | KCPL |  |  | 0 | 543132 | BNSF 5 | 543044 | MOONLT 5 | 0 |  | 1 | 22SP | 293 | 334 | 0 | 91.2 | 75.9313 | 95.6 | [7 empty] | CATEGORYB | NONSINGLE | 84667 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | MOONLT 5 - BNSF 5 - 1 | E | KCPL | KCPL |  |  | 0 | 543132 | BNSF 5 | 543044 | MOONLT 5 | 0 |  | 1 | 25SP | 293 | 334 | 0 | 90.6 | 75.615 | 95.5 | [7 empty] | CATEGORYB | NONSINGLE | 84667 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | MOONLT 5 - BNSF 5 - 1 | E | KCPL | KCPL |  |  | 0 | 543132 | BNSF 5 | 543044 | MOONLT 5 | 0 |  | 1 | 30SP | 293 | 334 | 0 | 94.4 | 74.4849 | 99 | [7 empty] | CATEGORYB | NONSINGLE | 84358 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | NASHUA-5 - SHOLCRK5 - 1 | E | KCPL | KCPL |  |  | 0 | 543028 | NASHUA-5 | 543029 | SHOLCRK5 | 0 |  | 1 | 21SP | 293 | 334 | 0 |  | 50.8065 | 96.2 | [7 empty] | CATEGORYB | NONSINGLE | 104180 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | NASHUA-5 - SHOLCRK5 - 1 | E | KCPL | KCPL |  |  | 0 | 543028 | NASHUA-5 | 543029 | SHOLCRK5 | 0 |  | 1 | 22SP | 293 | 334 | 0 |  | 52.5225 | 95.2 | [7 empty] | CATEGORYB | NONSINGLE | 104180 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | NEOSHO 4 - NSES TX-4 - 1 | E | WERE | WERE |  |  | 1 | 533021 | NEOSHO 4 | 532937 | NEOSHO 5 | 532958 |  | 1 | 30LP | 112 | 123.2 | 0 | 95.3 | 97 | 97 | [7 empty] | CATEGORYB | NONSINGLE | 4638 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | NEOSHO 5 - NSES TX-4 - 1 | E | WERE | WERE |  |  | 1 | 533021 | NEOSHO 4 | 532937 | NEOSHO 5 | 532958 |  | 1 | 30LP | 112 | 123.2 | 0 | 97.5 | 99.3 | 99.3 | [7 empty] | CATEGORYB | SINGLE | NEOSHO 5 - NEOSHOS4 - 1 | 1 | 532937 | NEOSHO 5 | 533020 | NEOSHOS4 | 532959 | NEOSH5 1 | 1 | Transfer Loading < 100%
2019-AG2 | NIXA 2 - NX ESPY2 - 1 | E | SWPA | SWPA |  |  | 0 | 505501 | NIXA 2 | 505543 | NX ESPY2 | 0 |  | 1 | 21SP | 72 | 72 | 0 | 95.2 | 29.5139 | 96.7 | [7 empty] | CATEGORYB | SINGLE | JRPS 69B-2 2 - JAMES RIVER5 - 1 | 1 | 549903 | JRPS 69B-2 2 | 549961 | JAMES RIVER5 | 549945 | JRPS XF2 1 | 1 | Transfer Loading < 100%
2019-AG2 | NIXA 2 - NX ESPY2 - 1 | E | SWPA | SWPA |  |  | 0 | 505501 | NIXA 2 | 505543 | NX ESPY2 | 0 |  | 1 | 22SP | 72 | 72 | 0 | 96.7 | 30.3474 | 97.8 | [7 empty] | CATEGORYB | SINGLE | JRPS 69B-2 2 - JAMES RIVER5 - 1 | 1 | 549903 | JRPS 69B-2 2 | 549961 | JAMES RIVER5 | 549945 | JRPS XF2 1 | 1 | Transfer Loading < 100%
2019-AG2 | NORFORK5 - 5SOUTHLAND# - 1 | E | SWPA | EES-EAI |  |  | 0 | 505448 | NORFORK5 | 338814 | 5SOUTHLAND# | 0 |  | 1 | 21SP | 162 | 162 | 0 | 100.7 | 75.6324 | 99.6 | [7 empty] | CATEGORYB | NONSINGLE | 64027 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | NORTHST3 - SALINA 3 - 1 | E | WERE | WERE |  |  | 0 | 533370 | NORTHST3 | 533376 | SALINA 3 | 0 |  | 1 | 20SP | 68 | 68 | 0 |  | 50.7362 | 97.1 | [7 empty] | CATEGORYB | SINGLE | NORTHST3 - SALINA 3 - 2 | 0 | 533370 | NORTHST3 | 533376 | SALINA 3 | 0 |  | 2 | Transfer Loading < 100%
2019-AG2 | NORTHST3 - SALINA 3 - 1 | E | WERE | WERE |  |  | 0 | 533370 | NORTHST3 | 533376 | SALINA 3 | 0 |  | 1 | 21SP | 68 | 68 | 0 | 97.4 | 51.4648 | 96.6 | [7 empty] | CATEGORYB | SINGLE | NORTHST3 - SALINA 3 - 2 | 0 | 533370 | NORTHST3 | 533376 | SALINA 3 | 0 |  | 2 | Transfer Loading < 100%
2019-AG2 | NORTHST3 - SALINA 3 - 1 | E | WERE | WERE |  |  | 0 | 533370 | NORTHST3 | 533376 | SALINA 3 | 0 |  | 1 | 22SP | 68 | 68 | 0 | 96.9 | 52.4432 | 95.3 | [7 empty] | CATEGORYB | SINGLE | NORTHST3 - SALINA 3 - 2 | 0 | 533370 | NORTHST3 | 533376 | SALINA 3 | 0 |  | 2 | Transfer Loading < 100%
2019-AG2 | NORTHST3 - SALINA 3 - 2 | E | WERE | WERE |  |  | 0 | 533370 | NORTHST3 | 533376 | SALINA 3 | 0 |  | 2 | 20SP | 68 | 68 | 0 |  | 50.7362 | 97.1 | [7 empty] | CATEGORYB | SINGLE | NORTHST3 - SALINA 3 - 1 | 0 | 533370 | NORTHST3 | 533376 | SALINA 3 | 0 |  | 1 | Transfer Loading < 100%
2019-AG2 | NORTHST3 - SALINA 3 - 2 | E | WERE | WERE |  |  | 0 | 533370 | NORTHST3 | 533376 | SALINA 3 | 0 |  | 2 | 21SP | 68 | 68 | 0 | 97.4 | 51.4648 | 96.6 | [7 empty] | CATEGORYB | SINGLE | NORTHST3 - SALINA 3 - 1 | 0 | 533370 | NORTHST3 | 533376 | SALINA 3 | 0 |  | 1 | Transfer Loading < 100%
2019-AG2 | NORTHST3 - SALINA 3 - 2 | E | WERE | WERE |  |  | 0 | 533370 | NORTHST3 | 533376 | SALINA 3 | 0 |  | 2 | 22SP | 68 | 68 | 0 | 96.9 | 52.4432 | 95.3 | [7 empty] | CATEGORYB | SINGLE | NORTHST3 - SALINA 3 - 1 | 0 | 533370 | NORTHST3 | 533376 | SALINA 3 | 0 |  | 1 | Transfer Loading < 100%
2019-AG2 | NORTWST7 - MATHWSN7 - 1 | E | OKGE | OKGE |  |  | 0 | 515497 | MATHWSN7 | 514880 | NORTWST7 | 0 |  | 1 | 30LP | 1793 | 1793 | 0 | 65.6 | 35.5299 | 96.7 | [7 empty] | CATEGORYB | NONSINGLE | 104895 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | OAHE 4 - OAHE2-3G - 1 | E | WAPA | WAPA |  |  | 0 | 652556 | OAHE2-3G | 652519 | OAHE 4 | 0 |  | 1 | 30SP | 206 | 254 | 0 |  | 92.3741 | 96.9 | [7 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | OAHE 4 - OAHE2-3G - 1 | E | WAPA | WAPA |  |  | 0 | 652556 | OAHE2-3G | 652519 | OAHE 4 | 0 |  | 1 | 30SP | 206 | 254 | 0 |  | 92.3741 | 96.9 | [7 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | OAHE 4 - OAHE4-5G - 1 | E | WAPA | WAPA |  |  | 0 | 652557 | OAHE4-5G | 652519 | OAHE 4 | 0 |  | 1 | 30SP | 206 | 254 | 0 |  | 92.3073 | 96.8 | [7 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | OAHE 4 - OAHE4-5G - 1 | E | WAPA | WAPA |  |  | 0 | 652557 | OAHE4-5G | 652519 | OAHE 4 | 0 |  | 1 | 30SP | 206 | 254 | 0 |  | 92.3073 | 96.8 | [7 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | OAHE 4 - OAHE6-7G - 1 | E | WAPA | WAPA |  |  | 0 | 652558 | OAHE6-7G | 652519 | OAHE 4 | 0 |  | 1 | 30SP | 206 | 254 | 0 |  | 92.4834 | 97 | [7 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | OAHE 4 - OAHE6-7G - 1 | E | WAPA | WAPA |  |  | 0 | 652558 | OAHE6-7G | 652519 | OAHE 4 | 0 |  | 1 | 30SP | 206 | 254 | 0 |  | 92.4834 | 97 | [7 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | OAHE 7 - OAHE 1G - 1 | E | WAPA | WAPA |  |  | 0 | 652559 | OAHE 1G | 652520 | OAHE 7 | 0 |  | 1 | 21WP | 103 | 129 | 0 | 98 | 83.0894 | 99.7 | [7 empty] | CATEGORYB | NONSINGLE | 105845 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | OAHE 7 - OAHE 1G - 1 | E | WAPA | WAPA |  |  | 0 | 652559 | OAHE 1G | 652520 | OAHE 7 | 0 |  | 1 | 21WP | 103 | 129 | 0 | 98 | 83.0894 | 99.7 | [7 empty] | CATEGORYB | NONSINGLE | 105845 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | OAHE 7 - OAHE 1G - 1 | E | WAPA | WAPA |  |  | 0 | 652559 | OAHE 1G | 652520 | OAHE 7 | 0 |  | 1 | 21WP | 103 | 129 | 0 | 94.8 | 83.0894 | 96.9 | [7 empty] | CATEGORYB | NONSINGLE | 105873 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | OAHE 7 - OAHE 1G - 1 | E | WAPA | WAPA |  |  | 0 | 652559 | OAHE 1G | 652520 | OAHE 7 | 0 |  | 1 | 21WP | 103 | 129 | 0 | 94.8 | 83.0894 | 96.9 | [7 empty] | CATEGORYB | NONSINGLE | 105873 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | OAHE 7 - OAHE 1G - 1 | E | WAPA | WAPA |  |  | 0 | 652559 | OAHE 1G | 652520 | OAHE 7 | 0 |  | 1 | 22WP | 103 | 129 | 0 | 98.3 | 83.3341 | 99.9 | [7 empty] | CATEGORYB | NONSINGLE | 105845 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | OAHE 7 - OAHE 1G - 1 | E | WAPA | WAPA |  |  | 0 | 652559 | OAHE 1G | 652520 | OAHE 7 | 0 |  | 1 | 22WP | 103 | 129 | 0 | 98.3 | 83.3341 | 99.9 | [7 empty] | CATEGORYB | NONSINGLE | 105845 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | OAHE 7 - OAHE 1G - 1 | E | WAPA | WAPA |  |  | 0 | 652559 | OAHE 1G | 652520 | OAHE 7 | 0 |  | 1 | 22WP | 103 | 129 | 0 | 92.5 | 83.3341 | 97.8 | [7 empty] | CATEGORYB | NONSINGLE | 106529 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | OAHE 7 - OAHE 1G - 1 | E | WAPA | WAPA |  |  | 0 | 652559 | OAHE 1G | 652520 | OAHE 7 | 0 |  | 1 | 22WP | 103 | 129 | 0 | 92.5 | 83.3341 | 97.8 | [7 empty] | CATEGORYB | NONSINGLE | 106529 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | OAHE 7 - OAHE 1G - 1 | E | WAPA | WAPA |  |  | 0 | 652559 | OAHE 1G | 652520 | OAHE 7 | 0 |  | 1 | 25SP | 103 | 129 | 0 | 95 | 80.2359 | 97.1 | [7 empty] | CATEGORYB | NONSINGLE | 105873 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | OAHE 7 - OAHE 1G - 1 | E | WAPA | WAPA |  |  | 0 | 652559 | OAHE 1G | 652520 | OAHE 7 | 0 |  | 1 | 25SP | 103 | 129 | 0 | 95 | 80.2359 | 97.1 | [7 empty] | CATEGORYB | NONSINGLE | 105873 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | OAHE 7 - OAHE 1G - 1 | E | WAPA | WAPA |  |  | 0 | 652559 | OAHE 1G | 652520 | OAHE 7 | 0 |  | 1 | 30LP | 103 | 129 | 0 | 94.6 | 77.5378 | 98 | [7 empty] | CATEGORYB | NONSINGLE | 7028 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | OAHE 7 - OAHE 1G - 1 | E | WAPA | WAPA |  |  | 0 | 652559 | OAHE 1G | 652520 | OAHE 7 | 0 |  | 1 | 30LP | 103 | 129 | 0 | 94.6 | 77.5378 | 98 | [7 empty] | CATEGORYB | NONSINGLE | 7028 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | OAHE 7 - OAHE 1G - 1 | E | WAPA | WAPA |  |  | 0 | 652559 | OAHE 1G | 652520 | OAHE 7 | 0 |  | 1 | 30LP | 103 | 129 | 0 | 91.7 | 77.5378 | 95.2 | [7 empty] | CATEGORYB | NONSINGLE | 105852 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | OAHE 7 - OAHE 1G - 1 | E | WAPA | WAPA |  |  | 0 | 652559 | OAHE 1G | 652520 | OAHE 7 | 0 |  | 1 | 30LP | 103 | 129 | 0 | 91.7 | 77.5378 | 95.2 | [7 empty] | CATEGORYB | NONSINGLE | 105852 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | ORO110 5 - OAK432 5 - 1 | E | EMDE | EMDE |  |  | 0 | 547467 | ORO110 5 | 547494 | OAK432 5 | 0 |  | 1 | 30WP | 335 | 335 | 0 | 90 | 53.4778 | 96.1 | [7 empty] | CATEGORYB | NONSINGLE | 87087 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | PARKLN 4 - LKKONWA4 - 1 | E | OKGE | OKGE |  |  | 0 | 515977 | LKKONWA4 | 515178 | PARKLN 4 | 0 |  | 1 | 21WP | 379 | 382 | 0 | 79.6 | 48.2505 | 96.7 | [7 empty] | CATEGORYB | NONSINGLE | 92675 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | PARKLN 4 - LKKONWA4 - 1 | E | OKGE | OKGE |  |  | 0 | 515977 | LKKONWA4 | 515178 | PARKLN 4 | 0 |  | 1 | 21WP | 379 | 382 | 0 | 77.6 | 48.2505 | 95.9 | [7 empty] | CATEGORYB | NONSINGLE | 92695 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | PARKLN 4 - LKKONWA4 - 1 | E | OKGE | OKGE |  |  | 0 | 515977 | LKKONWA4 | 515178 | PARKLN 4 | 0 |  | 1 | 22WP | 379 | 382 | 0 | 78.1 | 48.6298 | 98.8 | [7 empty] | CATEGORYB | NONSINGLE | 92695 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | PARKLN 4 - LKKONWA4 - 1 | E | OKGE | OKGE |  |  | 0 | 515977 | LKKONWA4 | 515178 | PARKLN 4 | 0 |  | 1 | 22WP | 379 | 382 | 0 | 80.1 | 48.6298 | 97.8 | [7 empty] | CATEGORYB | NONSINGLE | 92675 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | PARKLN 4 - LKKONWA4 - 1 | E | OKGE | OKGE |  |  | 0 | 515977 | LKKONWA4 | 515178 | PARKLN 4 | 0 |  | 1 | 25SP | 379 | 382 | 0 | 78.8 | 49.9156 | 99.7 | [7 empty] | CATEGORYB | NONSINGLE | 92666 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | PARKLN 4 - LKKONWA4 - 1 | E | OKGE | OKGE |  |  | 0 | 515977 | LKKONWA4 | 515178 | PARKLN 4 | 0 |  | 1 | 25SP | 379 | 382 | 0 | 79.5 | 49.9156 | 96.4 | [7 empty] | CATEGORYB | NONSINGLE | 81737 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | PARKLN 4 - LKKONWA4 - 1 | E | OKGE | OKGE |  |  | 0 | 515977 | LKKONWA4 | 515178 | PARKLN 4 | 0 |  | 1 | 25WP | 379 | 382 | 0 | 78.9 | 47.3346 | 97.3 | [7 empty] | CATEGORYB | NONSINGLE | 92675 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | PENTAGN3 - MUND 3 - 1 | E | WERE | WERE |  |  | 0 | 533261 | PENTAGN3 | 533282 | MUND 3 | 0 |  | 1 | 21SP | 173 | 206 | 0 | 94.4 | 75.4517 | 98.4 | [7 empty] | CATEGORYB | NONSINGLE | 84667 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | PHILL 5 - DOGWDCT1 - 1 | E | KCPL | KCPL |  |  | 0 | 541163 | DOGWDCT1 | 541225 | PHILL 5 | 0 |  | 1 | 21WP | 211 | 232.1 | 0 | 76.7 | 80.554 | 99.9 | [7 empty] | CATEGORYB | NONSINGLE | 104725 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | PHILL 5 - DOGWDCT1 - 1 | E | KCPL | KCPL |  |  | 0 | 541163 | DOGWDCT1 | 541225 | PHILL 5 | 0 |  | 1 | 21WP | 211 | 232.1 | 0 | 76.7 | 80.554 | 99.9 | [7 empty] | CATEGORYB | NONSINGLE | 104725 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | PHILL 5 - DOGWDCT1 - 1 | E | KCPL | KCPL |  |  | 0 | 541163 | DOGWDCT1 | 541225 | PHILL 5 | 0 |  | 1 | 21WP | 211 | 232.1 | 0 | 76.7 | 80.554 | 99.9 | [7 empty] | CATEGORYB | NONSINGLE | 104725 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | PHILL 5 - LKWINBG5 - 1 | E | KCPL | KCPL |  |  | 0 | 541225 | PHILL 5 | 541243 | LKWINBG5 | 0 |  | 1 | 20SP | 466 | 501 | 0 |  | 24.0865 | 96.2 | [7 empty] | CATEGORYB | SINGLE | GRNWD 5 - LEESUM 5 - 1 | 0 | 541218 | GRNWD 5 | 541233 | LEESUM 5 | 0 |  | 1 | Transfer Loading < 100%
2019-AG2 | PHILL 5 - LKWINBG5 - 1 | E | KCPL | KCPL |  |  | 0 | 541225 | PHILL 5 | 541243 | LKWINBG5 | 0 |  | 1 | 21SP | 466 | 501 | 0 | 82.8 | 25.3086 | 99.9 | [7 empty] | CATEGORYB | NONSINGLE | 84328 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | PHILL 5 - LKWINBG5 - 1 | E | KCPL | KCPL |  |  | 0 | 541225 | PHILL 5 | 541243 | LKWINBG5 | 0 |  | 1 | 22SP | 466 | 501 | 0 | 76.1 | 22.3187 | 99 | [7 empty] | CATEGORYB | NONSINGLE | 84328 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | PITTSB-7 - SEMINOL7 - 1 | E | OKGE | AEPW |  |  | 0 | 515045 | SEMINOL7 | 510907 | PITTSB-7 | 0 |  | 1 | 22LP | 956 | 956 | 0 |  | 50.6739 | 98.2 | [7 empty] | CATEGORYB | NONSINGLE | 105010 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | PITTSB-7 - SEMINOL7 - 1 | E | OKGE | AEPW |  |  | 0 | 515045 | SEMINOL7 | 510907 | PITTSB-7 | 0 |  | 1 | 22LP | 956 | 956 | 0 |  | 50.6739 | 97.3 | [7 empty] | CATEGORYB | NONSINGLE | 81741 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | PITTSB-7 - SEMINOL7 - 1 | E | OKGE | AEPW |  |  | 0 | 515045 | SEMINOL7 | 510907 | PITTSB-7 | 0 |  | 1 | 25LP | 956 | 956 | 0 |  | 49.9925 | 99.5 | [7 empty] | CATEGORYB | NONSINGLE | 105010 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | PITTSB-7 - SEMINOL7 - 1 | E | OKGE | AEPW |  |  | 0 | 515045 | SEMINOL7 | 510907 | PITTSB-7 | 0 |  | 1 | 25LP | 956 | 956 | 0 |  | 49.9925 | 98.2 | [7 empty] | CATEGORYB | NONSINGLE | 81741 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | PITTSB-7 - VALIANT7 - 1 | E | AEPW | AEPW |  |  | 0 | 510907 | PITTSB-7 | 510911 | VALIANT7 | 0 |  | 1 | 22LP | 1022 | 1143 | 0 |  | 49.1803 | 98.6 | [7 empty] | CATEGORYB | NONSINGLE | 81237 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | PRY-JCT2 - PRY-JCT1 - 1 | E | AEPW | AEPW |  |  | 1 | 510407 | PRY-JCT3 | 510400 | PRY-JCT2 | 510371 |  | 1 | 20SP | 75 | 75 | 0 |  | 96.1 | 96.1 | [7 empty] | CATEGORYB | SINGLE | MAID 2 - AMERCAST S2 - 1 | 0 | 512626 | MAID 2 | 512681 | AMERCAST S2 | 0 |  | 1 | Transfer Loading < 100%
2019-AG2 | PRY-JCT2 - PRY-JCT1 - 1 | E | AEPW | AEPW |  |  | 1 | 510407 | PRY-JCT3 | 510400 | PRY-JCT2 | 510371 |  | 1 | 20WP | 75 | 75 | 0 | 75.1 | 99.8 | 99.8 | [7 empty] | CATEGORYB | NONSINGLE | 81951 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | PRY-JCT2 - PRY-JCT1 - 1 | E | AEPW | AEPW |  |  | 1 | 510407 | PRY-JCT3 | 510400 | PRY-JCT2 | 510371 |  | 1 | 20WP | 75 | 75 | 0 |  | 97.4 | 97.4 | [7 empty] | CATEGORYB | SINGLE | INOLATP4 - CATOOSA4 - 1 | 0 | 509752 | INOLATP4 | 509790 | CATOOSA4 | 0 |  | 1 | Transfer Loading < 100%
2019-AG2 | PRY-JCT3 - PRY-JCT1 - 1 | E | AEPW | AEPW |  |  | 1 | 510407 | PRY-JCT3 | 510400 | PRY-JCT2 | 510371 |  | 1 | 20SP | 75 | 75 | 0 |  | 95.4 | 95.4 | [7 empty] | CATEGORYB | SINGLE | MAID 2 - AMERCAST S2 - 1 | 0 | 512626 | MAID 2 | 512681 | AMERCAST S2 | 0 |  | 1 | Transfer Loading < 100%
2019-AG2 | PRY-JCT3 - PRY-JCT1 - 1 | E | AEPW | AEPW |  |  | 1 | 510407 | PRY-JCT3 | 510400 | PRY-JCT2 | 510371 |  | 1 | 20WP | 75 | 75 | 0 | 74.3 | 98.5 | 98.5 | [7 empty] | CATEGORYB | NONSINGLE | 81951 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | PRY-JCT3 - PRY-JCT1 - 1 | E | AEPW | AEPW |  |  | 1 | 510407 | PRY-JCT3 | 510400 | PRY-JCT2 | 510371 |  | 1 | 20WP | 75 | 75 | 0 |  | 97.4 | 97.4 | [7 empty] | CATEGORYB | SINGLE | INOLATP4 - CATOOSA4 - 1 | 0 | 509752 | INOLATP4 | 509790 | CATOOSA4 | 0 |  | 1 | Transfer Loading < 100%
2019-AG2 | QUARRY 5 - MOONLT 5 - 1 | E | KCPL | KCPL |  |  | 0 | 543044 | MOONLT 5 | 543037 | QUARRY 5 | 0 |  | 1 | 21SP | 293 | 334 | 0 | 95.9 | 61.8324 | 99.1 | [7 empty] | CATEGORYB | NONSINGLE | 104255 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | QUARRY 5 - MOONLT 5 - 1 | E | KCPL | KCPL |  |  | 0 | 543044 | MOONLT 5 | 543037 | QUARRY 5 | 0 |  | 1 | 22SP | 293 | 334 | 0 |  | 61.4441 | 99.9 | [7 empty] | CATEGORYB | NONSINGLE | 84829 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | QUARRY 5 - MOONLT 5 - 1 | E | KCPL | KCPL |  |  | 0 | 543044 | MOONLT 5 | 543037 | QUARRY 5 | 0 |  | 1 | 30SP | 293 | 334 | 0 | 91.3 | 59.6712 | 99.5 | [7 empty] | CATEGORYB | NONSINGLE | 104255 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | ROCKCRK2 - VALLEY22 - 1 | E | WERE | WERE |  |  | 0 | 533458 | ROCKCRK2 | 533483 | VALLEY22 | 0 |  | 1 | 30SP | 35 | 41 | 0 | 96.3 | 39.7763 | 97.6 | [7 empty] | CATEGORYB | NONSINGLE | 94118 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | S BROWN4 - SCLMNJC4 - 1 | E | SWPA | WFEC |  |  | 0 | 505602 | S BROWN4 | 521049 | SCLMNJC4 | 0 |  | 1 | 22LP | 287 | 287 | 0 |  | 16.4454 | 99.7 | [7 empty] | CATEGORYB | NONSINGLE | 81723 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | S3456 3 - CBLUFFS3 - 1 | E | MEC | OPPD |  |  | 0 | 635000 | CBLUFFS3 | 645456 | S3456 3 | 0 |  | 1 | 21WP | 956 | 956 | 0 | 97 | 88.5518 | 95.8 | [7 empty] | CATEGORYB | NONSINGLE | 82313 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | SEMINOL4 - LKKONWA4 - 1 | E | OKGE | OKGE |  |  | 0 | 515044 | SEMINOL4 | 515977 | LKKONWA4 | 0 |  | 1 | 21SP | 379 | 382 | 0 | 93.3 | 39.0247 | 95.9 | [7 empty] | CATEGORYB | NONSINGLE | 81747 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | SEMINOL4 - LKKONWA4 - 1 | E | OKGE | OKGE |  |  | 0 | 515044 | SEMINOL4 | 515977 | LKKONWA4 | 0 |  | 1 | 21WP | 379 | 382 | 0 | 81.3 | 26.2637 | 98.4 | [7 empty] | CATEGORYB | NONSINGLE | 92675 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | SEMINOL4 - LKKONWA4 - 1 | E | OKGE | OKGE |  |  | 0 | 515044 | SEMINOL4 | 515977 | LKKONWA4 | 0 |  | 1 | 21WP | 379 | 382 | 0 | 79.3 | 26.2637 | 97.7 | [7 empty] | CATEGORYB | NONSINGLE | 92695 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | SEMINOL4 - LKKONWA4 - 1 | E | OKGE | OKGE |  |  | 0 | 515044 | SEMINOL4 | 515977 | LKKONWA4 | 0 |  | 1 | 21WP | 379 | 382 | 0 | 79.6 | 26.2637 | 95.3 | [7 empty] | CATEGORYB | NONSINGLE | 92672 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | SEMINOL4 - LKKONWA4 - 1 | E | OKGE | OKGE |  |  | 0 | 515044 | SEMINOL4 | 515977 | LKKONWA4 | 0 |  | 1 | 22WP | 379 | 382 | 0 | 81.8 | 26.7361 | 99.5 | [7 empty] | CATEGORYB | NONSINGLE | 92675 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | SEMINOL4 - LKKONWA4 - 1 | E | OKGE | OKGE |  |  | 0 | 515044 | SEMINOL4 | 515977 | LKKONWA4 | 0 |  | 1 | 22WP | 379 | 382 | 0 | 80.1 | 26.7361 | 96.4 | [7 empty] | CATEGORYB | NONSINGLE | 92672 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | SEMINOL4 - LKKONWA4 - 1 | E | OKGE | OKGE |  |  | 0 | 515044 | SEMINOL4 | 515977 | LKKONWA4 | 0 |  | 1 | 25SP | 379 | 382 | 0 | 81.1 | 36.4565 | 98.1 | [7 empty] | CATEGORYB | NONSINGLE | 81737 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | SEMINOL4 - LKKONWA4 - 1 | E | OKGE | OKGE |  |  | 0 | 515044 | SEMINOL4 | 515977 | LKKONWA4 | 0 |  | 1 | 25SP | 379 | 382 | 0 | 80 | 36.4565 | 95.1 | [7 empty] | CATEGORYB | NONSINGLE | 81747 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | SEMINOL4 - LKKONWA4 - 1 | E | OKGE | OKGE |  |  | 0 | 515044 | SEMINOL4 | 515977 | LKKONWA4 | 0 |  | 1 | 25WP | 379 | 382 | 0 | 80.6 | 27.3867 | 99 | [7 empty] | CATEGORYB | NONSINGLE | 92675 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | SEMINOL4 - LKKONWA4 - 1 | E | OKGE | OKGE |  |  | 0 | 515044 | SEMINOL4 | 515977 | LKKONWA4 | 0 |  | 1 | 25WP | 379 | 382 | 0 | 78.7 | 27.3867 | 95.2 | [7 empty] | CATEGORYB | NONSINGLE | 92672 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | SHELDON7 - MOORE T1 - 1 | E | NPPD | NPPD |  |  | 1 | 640277 | MOORE 3 | 640278 | SHELDON7 | 640280 |  | 1 | 20WP | 336 | 336 | 0 | 97.4 | 97.8 | 97.8 | [7 empty] | CATEGORYB | NONSINGLE | 104860 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | SHELDON7 - MOORE T1 - 1 | E | NPPD | NPPD |  |  | 1 | 640277 | MOORE 3 | 640278 | SHELDON7 | 640280 |  | 1 | 21WP | 336 | 336 | 0 | 95.7 | 95.5 | 95.5 | [7 empty] | CATEGORYB | NONSINGLE | 104860 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | SHELDON7 - MOORE T1 - 1 | E | NPPD | NPPD |  |  | 1 | 640277 | MOORE 3 | 640278 | SHELDON7 | 640280 |  | 1 | 22WP | 336 | 336 | 0 | 96.5 | 96.4 | 96.4 | [7 empty] | CATEGORYB | NONSINGLE | 104860 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | SHELDON7 - MOORE T1 - 1 | E | NPPD | NPPD |  |  | 1 | 640277 | MOORE 3 | 640278 | SHELDON7 | 640280 |  | 1 | 25WP | 336 | 336 | 0 | 95.1 | 95.5 | 95.5 | [7 empty] | CATEGORYB | NONSINGLE | 104860 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | SHELDON7 - MOORE T1 - 1 | E | NPPD | NPPD |  |  | 1 | 640277 | MOORE 3 | 640278 | SHELDON7 | 640280 |  | 1 | 30WP | 336 | 336 | 0 | 95.7 | 95.9 | 95.9 | [7 empty] | CATEGORYB | NONSINGLE | 104860 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | SHWNMSN5 - CEDRCRK5 - 1 | E | KCPL | KCPL |  |  | 0 | 543049 | CEDRCRK5 | 543031 | SHWNMSN5 | 0 |  | 1 | 30WP | 334 | 334 | 0 | 91.2 | 21.002 | 99.5 | [7 empty] | CATEGORYB | NONSINGLE | 92329 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | SIOUXCY2 - SC2 KU1B - 1 | E | WAPA | WAPA |  |  | 1 | 652564 | SIOUXCY3 | 652552 | SIOUXCY2 | 652305 |  | 1 | 21SP | 250 | 250 | 0 | 96 | 61.3033 | 96.6 | [7 empty] | CATEGORYB | SINGLE | SIOUXCY2 - SIOUXCY3 - 1 | 1 | 652552 | SIOUXCY2 | 652564 | SIOUXCY3 | 652304 | SIOUXC19 | 1 | Transfer Loading < 100%
2019-AG2 | SIOUXCY2 - SC2 KU1B - 1 | E | WAPA | WAPA |  |  | 1 | 652564 | SIOUXCY3 | 652552 | SIOUXCY2 | 652305 |  | 1 | 22SP | 250 | 250 | 0 | 95.2 | 60.7761 | 95.3 | [7 empty] | CATEGORYB | SINGLE | SIOUXCY2 - SIOUXCY3 - 1 | 1 | 652552 | SIOUXCY2 | 652564 | SIOUXCY3 | 652304 | SIOUXC19 | 1 | Transfer Loading < 100%
2019-AG2 | SIOUXCY3 - SC2 KU1B - 1 | E | WAPA | WAPA |  |  | 1 | 652564 | SIOUXCY3 | 652552 | SIOUXCY2 | 652305 |  | 1 | 21SP | 250 | 250 | 0 | 96.2 | 61.3033 | 96.8 | [7 empty] | CATEGORYB | SINGLE | SIOUXCY2 - SIOUXCY3 - 1 | 1 | 652552 | SIOUXCY2 | 652564 | SIOUXCY3 | 652304 | SIOUXC19 | 1 | Transfer Loading < 100%
2019-AG2 | SIOUXCY3 - SC2 KU1B - 1 | E | WAPA | WAPA |  |  | 1 | 652564 | SIOUXCY3 | 652552 | SIOUXCY2 | 652305 |  | 1 | 22SP | 250 | 250 | 0 | 95.4 | 60.7761 | 95.5 | [7 empty] | CATEGORYB | SINGLE | SIOUXCY2 - SIOUXCY3 - 1 | 1 | 652552 | SIOUXCY2 | 652564 | SIOUXCY3 | 652304 | SIOUXC19 | 1 | Transfer Loading < 100%
2019-AG2 | SMOKYHL6 - SUMMIT 6 - 1 | E | MIDW | WERE |  |  | 0 | 530592 | SMOKYHL6 | 532873 | SUMMIT 6 | 0 |  | 1 | 25LP | 330 | 350 | 0 | 93.3 | 74.8533 | 97.2 | [7 empty] | CATEGORYB | NONSINGLE | 8615 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | SOUTHRD4 - ROMNOSE4 - 1 | E | OKGE | OKGE |  |  | 0 | 514822 | SOUTHRD4 | 514823 | ROMNOSE4 | 0 |  | 1 | 25LP | 133 | 153 | 0 | 95.2 | 64.6971 | 97.4 | [7 empty] | CATEGORYB | NONSINGLE | 81729 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | SOUTHRD4 - ROMNOSE4 - 1 | E | OKGE | OKGE |  |  | 0 | 514822 | SOUTHRD4 | 514823 | ROMNOSE4 | 0 |  | 1 | 30LP | 133 | 153 | 0 | 103.7 | 65.7696 | 99 | [7 empty] | CATEGORYB | NONSINGLE | 81736 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | STILWEL5 - REDEL 5 - 1 | E | KCPL | KCPL |  |  | 0 | 542969 | STILWEL5 | 543053 | REDEL 5 | 0 |  | 1 | 25SP | 293 | 334 | 0 | 74 | 53.1585 | 95.1 | [7 empty] | CATEGORYB | NONSINGLE | 104652 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | STILWEL5 - REDEL 5 - 1 | E | KCPL | KCPL |  |  | 0 | 542969 | STILWEL5 | 543053 | REDEL 5 | 0 |  | 1 | 30SP | 293 | 334 | 0 | 78 | 50.6076 | 96.3 | [7 empty] | CATEGORYB | NONSINGLE | 104177 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | STILWEL5 - STILWELL22 - 22 | E | KCPL | KCPL |  |  | 1 | 542968 | STILWEL7 | 542969 | STILWEL5 | 543648 |  | 22 | 20SP | 550 | 605 | 0 | 96.3 | 53.8519 | 95.4 | [7 empty] | CATEGORYB | NONSINGLE | 84785 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | STILWEL5 - STILWELL22 - 22 | E | KCPL | KCPL |  |  | 1 | 542968 | STILWEL7 | 542969 | STILWEL5 | 543648 |  | 22 | 20WP | 550 | 605 | 0 |  | 51.4887 | 96.7 | [7 empty] | CATEGORYB | NONSINGLE | 84785 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | STILWEL5 - STILWELL22 - 22 | E | KCPL | KCPL |  |  | 1 | 542968 | STILWEL7 | 542969 | STILWEL5 | 543648 |  | 22 | 25WP | 550 | 605 | 0 | 91 | 48.0566 | 98.7 | [7 empty] | CATEGORYB | NONSINGLE | 104250 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | STILWEL5 - STILWELL22 - 22 | E | KCPL | KCPL |  |  | 1 | 542968 | STILWEL7 | 542969 | STILWEL5 | 543648 |  | 22 | 30WP | 550 | 605 | 0 | 87.2 | 46.3839 | 96.9 | [7 empty] | CATEGORYB | NONSINGLE | 104250 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | STILWEL7 - STILWELL22 - 22 | E | KCPL | KCPL |  |  | 1 | 542968 | STILWEL7 | 542969 | STILWEL5 | 543648 |  | 22 | 20SP | 550 | 605 | 0 | 97.8 | 53.8519 | 96.9 | [7 empty] | CATEGORYB | NONSINGLE | 84785 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | STILWEL7 - STILWELL22 - 22 | E | KCPL | KCPL |  |  | 1 | 542968 | STILWEL7 | 542969 | STILWEL5 | 543648 |  | 22 | 20WP | 550 | 605 | 0 |  | 51.4887 | 97.9 | [7 empty] | CATEGORYB | NONSINGLE | 84785 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | STILWEL7 - STILWELL22 - 22 | E | KCPL | KCPL |  |  | 1 | 542968 | STILWEL7 | 542969 | STILWEL5 | 543648 |  | 22 | 25WP | 550 | 605 | 0 | 91 | 48.0566 | 99.8 | [7 empty] | CATEGORYB | NONSINGLE | 84680 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | STILWEL7 - STILWELL22 - 22 | E | KCPL | KCPL |  |  | 1 | 542968 | STILWEL7 | 542969 | STILWEL5 | 543648 |  | 22 | 30WP | 550 | 605 | 0 | 87.2 | 46.3839 | 98 | [7 empty] | CATEGORYB | NONSINGLE | 84680 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | SWEET W3 - GR ISLD3 - 1 | E | NPPD | NPPD |  |  | 0 | 640374 | SWEET W3 | 653571 | GR ISLD3 | 0 |  | 1 | 20WP | 717 | 717 | 0 | 95.6 | 57.4994 | 98.4 | [7 empty] | CATEGORYB | NONSINGLE | 85473 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | T.S.E.-4 - 21STTAP4 - 1 | E | AEPW | AEPW |  |  | 0 | 509811 | T.S.E.-4 | 509828 | 21STTAP4 | 0 |  | 1 | 20SP | 212 | 212 | 0 | 101.4 | 28.1128 | 99.4 | [7 empty] | CATEGORYB | SINGLE | BA.N-ST4 - ONETA--4 - 1 | 0 | 509786 | BA.N-ST4 | 509806 | ONETA--4 | 0 |  | 1 | Transfer Loading < 100%
2019-AG2 | TUPELO 4 - ALLENGT4 - 1 | E | SWPA | AEPW |  |  | 0 | 505600 | TUPELO 4 | 510881 | ALLENGT4 | 0 |  | 1 | 22LP | 189 | 189 | 0 |  | 20.9834 | 95.6 | [7 empty] | CATEGORYB | NONSINGLE | 81723 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | TUPELO 4 - STNWLSW4 - 1 | E | WFEC | SWPA |  |  | 0 | 521071 | STNWLSW4 | 505600 | TUPELO 4 | 0 |  | 1 | 22LP | 145 | 169 | 0 | 66.2 | 66.3295 | 99.8 | [7 empty] | CATEGORYB | NONSINGLE | 84206 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | TUPELO 4 - STNWLSW4 - 1 | E | WFEC | SWPA |  |  | 0 | 521071 | STNWLSW4 | 505600 | TUPELO 4 | 0 |  | 1 | 25LP | 145 | 169 | 0 | 66.3 | 66.8549 | 99.6 | [7 empty] | CATEGORYB | NONSINGLE | 92677 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | TUPELO 4 - STNWLSW4 - 1 | E | WFEC | SWPA |  |  | 0 | 521071 | STNWLSW4 | 505600 | TUPELO 4 | 0 |  | 1 | 25LP | 145 | 169 | 0 | 65.7 | 66.8549 | 98.5 | [7 empty] | CATEGORYB | NONSINGLE | 81383 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | TUPELO 4 - STNWLSW4 - 1 | E | WFEC | SWPA |  |  | 0 | 521071 | STNWLSW4 | 505600 | TUPELO 4 | 0 |  | 1 | 30LP | 145 | 169 | 0 | 75.5 | 55.0468 | 95.6 | [7 empty] | CATEGORYB | NONSINGLE | 92669 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | TURNER_RD5 - BELTONS5 - 1 | E | KCPL | KCPL |  |  | 0 | 541340 | BELTONS5 | 541259 | TURNER_RD5 | 0 |  | 1 | 21SP | 233 | 265 | 0 | 96.2 | 64.796 | 95.6 | [7 empty] | CATEGORYB | NONSINGLE | 84363 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | TURNER_RD5 - BELTONS5 - 1 | E | KCPL | KCPL |  |  | 0 | 541340 | BELTONS5 | 541259 | TURNER_RD5 | 0 |  | 1 | 22SP | 233 | 265 | 0 | 94.8 | 64.1533 | 97.6 | [7 empty] | CATEGORYB | NONSINGLE | 84363 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | TURNER_RD5 - BELTONS5 - 1 | E | KCPL | KCPL |  |  | 0 | 541340 | BELTONS5 | 541259 | TURNER_RD5 | 0 |  | 1 | 25SP | 233 | 265 | 0 | 95.2 | 64.6247 | 98.9 | [7 empty] | CATEGORYB | NONSINGLE | 84363 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | VALIANT4 - HUGO PP4 - 1 | E | WFEC | AEPW |  |  | 0 | 520948 | HUGO PP4 | 510918 | VALIANT4 | 0 |  | 1 | 25LP | 287 | 287 | 0 |  | 18.9059 | 96.5 | [7 empty] | CATEGORYB | SINGLE | HUGO 7 - VALIANT7 - 1 | 0 | 521157 | HUGO 7 | 510911 | VALIANT7 | 0 |  | 1 | Transfer Loading < 100%
2019-AG2 | WAVERLY7 - LACYGNE7 - 1 | E | WERE | KCPL |  |  | 0 | 532799 | WAVERLY7 | 542981 | LACYGNE7 | 0 |  | 1 | 25LP | 1141 | 1195 | 0 |  | 80.961 | 99.4 | [7 empty] | CATEGORYB | SINGLE | CANEYRV7 - G17-009-TAP - 1 | 0 | 532780 | CANEYRV7 | 588544 | G17-009-TAP | 0 |  | 1 | Transfer Loading < 100%
2019-AG2 | WAVERLY7 - LACYGNE7 - 1 | E | WERE | KCPL |  |  | 0 | 532799 | WAVERLY7 | 542981 | LACYGNE7 | 0 |  | 1 | 25LP | 1141 | 1195 | 0 | 85.3 | 80.961 | 97 | [7 empty] | CATEGORYB | NONSINGLE | 104260 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | WEAVER 4 - ROSEHIL4 - 1 | E | WERE | WERE |  |  | 0 | 533062 | ROSEHIL4 | 532991 | WEAVER 4 | 0 |  | 1 | 20SP | 382 | 382 | 0 | 97.1 | 51.1932 | 96.9 | [7 empty] | CATEGORYB | NONSINGLE | 8599 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | WEAVER 4 - ROSEHIL4 - 1 | E | WERE | WERE |  |  | 0 | 533062 | ROSEHIL4 | 532991 | WEAVER 4 | 0 |  | 1 | 21SP | 382 | 382 | 0 | 103.2 | 52.18 | 99.9 | [7 empty] | CATEGORYB | NONSINGLE | 7819 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | WEAVER 4 - ROSEHIL4 - 1 | E | WERE | WERE |  |  | 0 | 533062 | ROSEHIL4 | 532991 | WEAVER 4 | 0 |  | 1 | 22SP | 382 | 382 | 0 | 102.8 | 51.0049 | 97.4 | [7 empty] | CATEGORYB | NONSINGLE | 7819 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | WEAVER 4 - ROSEHIL4 - 1 | E | WERE | WERE |  |  | 0 | 533062 | ROSEHIL4 | 532991 | WEAVER 4 | 0 |  | 1 | 25SP | 382 | 382 | 0 | 105.2 | 51.9612 | 99.7 | [7 empty] | CATEGORYB | NONSINGLE | 7819 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | WEAVER 4 - ROSEHIL4 - 1 | E | WERE | WERE |  |  | 0 | 533062 | ROSEHIL4 | 532991 | WEAVER 4 | 0 |  | 1 | 30SP | 382 | 382 | 0 | 103.5 | 50.8897 | 98.2 | [7 empty] | CATEGORYB | NONSINGLE | 7819 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | WEBBTAP4 - OSAGE 4 - 1 | E | OKGE | AEPW |  |  | 0 | 514743 | OSAGE 4 | 510376 | WEBBTAP4 | 0 |  | 1 | 22LP | 152 | 172 | 0 | 83.7 | 83.4257 | 98.6 | [7 empty] | CATEGORYB | NONSINGLE | 84126 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | WEBBTAP4 - OSAGE 4 - 1 | E | OKGE | AEPW |  |  | 0 | 514743 | OSAGE 4 | 510376 | WEBBTAP4 | 0 |  | 1 | 22LP | 152 | 172 | 0 |  | 83.4257 | 98.2 | [7 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | WEBBTAP4 - OSAGE 4 - 1 | E | OKGE | AEPW |  |  | 0 | 514743 | OSAGE 4 | 510376 | WEBBTAP4 | 0 |  | 1 | 22LP | 152 | 172 | 0 | 82.1 | 83.4257 | 97.4 | [7 empty] | CATEGORYB | NONSINGLE | 84244 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | WEBBTAP4 - OSAGE 4 - 1 | E | OKGE | AEPW |  |  | 0 | 514743 | OSAGE 4 | 510376 | WEBBTAP4 | 0 |  | 1 | 25LP | 152 | 172 | 0 |  | 83.9163 | 99.8 | [7 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | WEBBTAP4 - OSAGE 4 - 1 | E | OKGE | AEPW |  |  | 0 | 514743 | OSAGE 4 | 510376 | WEBBTAP4 | 0 |  | 1 | 25LP | 152 | 172 | 0 | 82.8 | 83.9163 | 99.2 | [7 empty] | CATEGORYB | NONSINGLE | 84244 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | WEBBTAP4 - OSAGE 4 - 1 | E | OKGE | AEPW |  |  | 0 | 514743 | OSAGE 4 | 510376 | WEBBTAP4 | 0 |  | 1 | 25LP | 152 | 172 | 0 |  | 83.9163 | 98.9 | [7 empty] | CATEGORYB | SINGLE | NEOSHO 7 - G17-009-TAP - 1 | 0 | 532793 | NEOSHO 7 | 588544 | G17-009-TAP | 0 |  | 1 | Transfer Loading < 100%
2019-AG2 | WEBBTAP4 - SHIDLER4 - 1 | E | AEPW | AEPW |  |  | 0 | 510376 | WEBBTAP4 | 510403 | SHIDLER4 | 0 |  | 1 | 30LP | 179 | 200 | 0 | 83.1 | 55.0379 | 97.6 | [7 empty] | CATEGORYB | NONSINGLE | 81740 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | WGARDNR5 - BNSF 5 - 1 | E | KCPL | KCPL |  |  | 0 | 542966 | WGARDNR5 | 543132 | BNSF 5 | 0 |  | 1 | 21SP | 293 | 334 | 0 | 95.4 | 73.0879 | 98 | [7 empty] | CATEGORYB | NONSINGLE | 84667 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | WGARDNR5 - BNSF 5 - 1 | E | KCPL | KCPL |  |  | 0 | 542966 | WGARDNR5 | 543132 | BNSF 5 | 0 |  | 1 | 21SP | 293 | 334 | 0 | 95.4 | 73.0879 | 97.9 | [7 empty] | CATEGORYB | NONSINGLE | 84353 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | WGARDNR5 - BNSF 5 - 1 | E | KCPL | KCPL |  |  | 0 | 542966 | WGARDNR5 | 543132 | BNSF 5 | 0 |  | 1 | 22SP | 293 | 334 | 0 | 94.5 | 72.4498 | 98.9 | [7 empty] | CATEGORYB | NONSINGLE | 84667 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | WGARDNR5 - BNSF 5 - 1 | E | KCPL | KCPL |  |  | 0 | 542966 | WGARDNR5 | 543132 | BNSF 5 | 0 |  | 1 | 22SP | 293 | 334 | 0 | 90.6 | 72.4498 | 96.1 | [7 empty] | CATEGORYB | NONSINGLE | 84357 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | WGARDNR5 - BNSF 5 - 1 | E | KCPL | KCPL |  |  | 0 | 542966 | WGARDNR5 | 543132 | BNSF 5 | 0 |  | 1 | 25SP | 293 | 334 | 0 | 93.9 | 72.2315 | 98.8 | [7 empty] | CATEGORYB | NONSINGLE | 84667 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | WGARDNR5 - BNSF 5 - 1 | E | KCPL | KCPL |  |  | 0 | 542966 | WGARDNR5 | 543132 | BNSF 5 | 0 |  | 1 | 25SP | 293 | 334 | 0 | 90 | 72.2315 | 96.8 | [7 empty] | CATEGORYB | NONSINGLE | 84357 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | WGARDNR5 - BNSF 5 - 1 | E | KCPL | KCPL |  |  | 0 | 542966 | WGARDNR5 | 543132 | BNSF 5 | 0 |  | 1 | 30SP | 293 | 334 | 0 | 92 | 72.2148 | 97.8 | [7 empty] | CATEGORYB | NONSINGLE | 84667 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | WGARDNR5 - BNSF 5 - 1 | E | KCPL | KCPL |  |  | 0 | 542966 | WGARDNR5 | 543132 | BNSF 5 | 0 |  | 1 | 30SP | 293 | 334 | 0 | 88.3 | 72.2148 | 95.1 | [7 empty] | CATEGORYB | NONSINGLE | 84357 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | WICHITA7 - WICH TX-12 - 1 | E | WERE | WERE |  |  | 1 | 532796 | WICHITA7 | 533040 | EVANS N4 | 532830 |  | 1 | 22SP | 400 | 430 | 0 | 87.9 | 65.1397 | 95.7 | [7 empty] | CATEGORYB | SINGLE | WICHITA7 - EVANS N4 - 1 | 1 | 532796 | WICHITA7 | 533040 | EVANS N4 | 532829 | WICH11 1 | 1 | Transfer Loading < 100%
2019-AG2 | WICHITA7 - WICH TX-12 - 1 | E | WERE | WERE |  |  | 1 | 532796 | WICHITA7 | 533040 | EVANS N4 | 532830 |  | 1 | 25SP | 400 | 430 | 0 | 85.9 | 66.7801 | 96.6 | [7 empty] | CATEGORYB | SINGLE | WICHITA7 - EVANS N4 - 1 | 1 | 532796 | WICHITA7 | 533040 | EVANS N4 | 532829 | WICH11 1 | 1 | Transfer Loading < 100%
2019-AG2 | WILKES 4 - WILKE2-1 - 1 | E | AEPW | AEPW |  |  | 0 | 508840 | WILKES 4 | 509408 | WILKE2-1 | 0 |  | 1 | 21SP | 196 | 196 | 0 | 122.2 | 70.8657 | 98.1 | [7 empty] | CATEGORYB | NONSINGLE | 92340 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | WILKES 4 - WILKE2-1 - 1 | E | AEPW | AEPW |  |  | 0 | 508840 | WILKES 4 | 509408 | WILKE2-1 | 0 |  | 1 | 21WP | 196 | 196 | 0 |  | 59.7122 | 96.9 | [7 empty] | CATEGORYB | NONSINGLE | 83956 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | WILKES 4 - WILKE2-1 - 1 | E | AEPW | AEPW |  |  | 0 | 508840 | WILKES 4 | 509408 | WILKE2-1 | 0 |  | 1 | 22WP | 196 | 196 | 0 |  | 62.5205 | 99.3 | [7 empty] | CATEGORYB | NONSINGLE | 104894 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | WILKES 4 - WILKE2-1 - 1 | E | AEPW | AEPW |  |  | 0 | 508840 | WILKES 4 | 509408 | WILKE2-1 | 0 |  | 1 | 22WP | 196 | 196 | 0 |  | 62.5205 | 99.1 | [7 empty] | CATEGORYB | NONSINGLE | 30731 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | WILKES 4 - WILKE2-1 - 1 | E | AEPW | AEPW |  |  | 0 | 508840 | WILKES 4 | 509408 | WILKE2-1 | 0 |  | 1 | 25SP | 196 | 196 | 0 |  | 76.8515 | 99.1 | [7 empty] | CATEGORYB | NONSINGLE | 104738 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | WILKES 4 - WILKE2-1 - 1 | E | AEPW | AEPW |  |  | 0 | 508840 | WILKES 4 | 509408 | WILKE2-1 | 0 |  | 1 | 25SP | 196 | 196 | 0 |  | 76.8515 | 96.7 | [7 empty] | CATEGORYB | NONSINGLE | 81750 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | WILKES 4 - WILKE2-1 - 1 | E | AEPW | AEPW |  |  | 0 | 508840 | WILKES 4 | 509408 | WILKE2-1 | 0 |  | 1 | 25WP | 196 | 196 | 0 |  | 75.8262 | 96.3 | [7 empty] | CATEGORYB | NONSINGLE | 92673 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | WILKES 4 - WILKE2-1 - 1 | E | AEPW | AEPW |  |  | 0 | 508840 | WILKES 4 | 509408 | WILKE2-1 | 0 |  | 1 | 30SP | 196 | 196 | 0 |  | 78.2491 | 99.5 | [7 empty] | CATEGORYB | NONSINGLE | 63068 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | WILKES 4 - WILKE2-1 - 1 | E | AEPW | AEPW |  |  | 0 | 508840 | WILKES 4 | 509408 | WILKE2-1 | 0 |  | 1 | 30SP | 196 | 196 | 0 |  | 78.2491 | 99.3 | [7 empty] | CATEGORYB | NONSINGLE | 63106 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | WILKES 4 - WILKE2-1 - 1 | E | AEPW | AEPW |  |  | 0 | 508840 | WILKES 4 | 509408 | WILKE2-1 | 0 |  | 1 | 30WP | 196 | 196 | 0 |  | 75.738 | 95.9 | [7 empty] | CATEGORYB | NONSINGLE | 104738 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | WILKES 4 - WILKE2-1 - 2 | E | AEPW | AEPW |  |  | 0 | 508840 | WILKES 4 | 509408 | WILKE2-1 | 0 |  | 2 | 21SP | 196 | 196 | 0 | 123.3 | 70.8652 | 99 | [7 empty] | CATEGORYB | NONSINGLE | 104720 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | WILKES 4 - WILKE2-1 - 2 | E | AEPW | AEPW |  |  | 0 | 508840 | WILKES 4 | 509408 | WILKE2-1 | 0 |  | 2 | 21SP | 196 | 196 | 0 | 118 | 70.8652 | 95 | [7 empty] | CATEGORYB | NONSINGLE | 104731 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | WILKES 4 - WILKE2-1 - 2 | E | AEPW | AEPW |  |  | 0 | 508840 | WILKES 4 | 509408 | WILKE2-1 | 0 |  | 2 | 21WP | 196 | 196 | 0 |  | 59.7118 | 97.8 | [7 empty] | CATEGORYB | NONSINGLE | 83956 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | WILKES 4 - WILKE2-1 - 2 | E | AEPW | AEPW |  |  | 0 | 508840 | WILKES 4 | 509408 | WILKE2-1 | 0 |  | 2 | 22WP | 196 | 196 | 0 |  | 62.52 | 97.5 | [7 empty] | CATEGORYB | NONSINGLE | 63068 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | WILKES 4 - WILKE2-1 - 2 | E | AEPW | AEPW |  |  | 0 | 508840 | WILKES 4 | 509408 | WILKE2-1 | 0 |  | 2 | 25SP | 196 | 196 | 0 |  | 76.851 | 97.6 | [7 empty] | CATEGORYB | NONSINGLE | 81750 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | WILKES 4 - WILKE2-1 - 2 | E | AEPW | AEPW |  |  | 0 | 508840 | WILKES 4 | 509408 | WILKE2-1 | 0 |  | 2 | 25WP | 196 | 196 | 0 |  | 75.8257 | 97.2 | [7 empty] | CATEGORYB | NONSINGLE | 92673 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | WILKES 4 - WILKE2-1 - 2 | E | AEPW | AEPW |  |  | 0 | 508840 | WILKES 4 | 509408 | WILKE2-1 | 0 |  | 2 | 30WP | 196 | 196 | 0 |  | 75.7375 | 96.8 | [7 empty] | CATEGORYB | NONSINGLE | 104738 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | WILKES 4 - WILKES - 1 | E | AEPW | AEPW |  |  | 1 | 508841 | WILKES 7 | 508840 | WILKES 4 | 508826 |  | 1 | 22SP | 471 | 525 | 0 | 65.8 | 98.3 | 98.3 | [7 empty] | CATEGORYB | NONSINGLE | 81750 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | WILKES 4 - WILKES - 1 | E | AEPW | AEPW |  |  | 1 | 508841 | WILKES 7 | 508840 | WILKES 4 | 508826 |  | 1 | 22SP | 471 | 525 | 0 | 65.9 | 98.2 | 98.2 | [7 empty] | CATEGORYB | NONSINGLE | 84364 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | WILKES 4 - WILKES - 1 | E | AEPW | AEPW |  |  | 1 | 508841 | WILKES 7 | 508840 | WILKES 4 | 508826 |  | 1 | 22SP | 471 | 525 | 0 | 65.8 | 97.8 | 97.8 | [7 empty] | CATEGORYB | NONSINGLE | 84355 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | WILKES 4 - WILKES - 1 | E | AEPW | AEPW |  |  | 1 | 508841 | WILKES 7 | 508840 | WILKES 4 | 508826 |  | 1 | 22WP | 525 | 597 | 0 | 66.4 | 97.5 | 97.5 | [7 empty] | CATEGORYB | NONSINGLE | 92340 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | WILKES 4 - WILKES - 1 | E | AEPW | AEPW |  |  | 1 | 508841 | WILKES 7 | 508840 | WILKES 4 | 508826 |  | 1 | 22WP | 525 | 597 | 0 | 65.2 | 96.3 | 96.3 | [7 empty] | CATEGORYB | NONSINGLE | 92674 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | WILKES 4 - WILKES - 1 | E | AEPW | AEPW |  |  | 1 | 508841 | WILKES 7 | 508840 | WILKES 4 | 508826 |  | 1 | 25SP | 471 | 525 | 0 |  | 98.2 | 98.2 | [7 empty] | CATEGORYB | NONSINGLE | 92348 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | WILKES 4 - WILKES - 1 | E | AEPW | AEPW |  |  | 1 | 508841 | WILKES 7 | 508840 | WILKES 4 | 508826 |  | 1 | 30SP | 471 | 525 | 0 |  | 99.9 | 99.9 | [7 empty] | CATEGORYB | NONSINGLE | 92342 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | WILKES 4 - WILKES - 1 | E | AEPW | AEPW |  |  | 1 | 508841 | WILKES 7 | 508840 | WILKES 4 | 508826 |  | 1 | 30SP | 471 | 525 | 0 |  | 98.5 | 98.5 | [7 empty] | CATEGORYB | NONSINGLE | 92476 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | WILKES 7 - WILKES - 1 | E | AEPW | AEPW |  |  | 1 | 508841 | WILKES 7 | 508840 | WILKES 4 | 508826 |  | 1 | 22SP | 471 | 525 | 0 | 65.8 | 98.2 | 98.2 | [7 empty] | CATEGORYB | NONSINGLE | 81750 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | WILKES 7 - WILKES - 1 | E | AEPW | AEPW |  |  | 1 | 508841 | WILKES 7 | 508840 | WILKES 4 | 508826 |  | 1 | 22SP | 471 | 525 | 0 | 65.9 | 98.1 | 98.1 | [7 empty] | CATEGORYB | NONSINGLE | 84364 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | WILKES 7 - WILKES - 1 | E | AEPW | AEPW |  |  | 1 | 508841 | WILKES 7 | 508840 | WILKES 4 | 508826 |  | 1 | 22SP | 471 | 525 | 0 | 65.8 | 97.7 | 97.7 | [7 empty] | CATEGORYB | NONSINGLE | 84355 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | WILKES 7 - WILKES - 1 | E | AEPW | AEPW |  |  | 1 | 508841 | WILKES 7 | 508840 | WILKES 4 | 508826 |  | 1 | 22WP | 525 | 597 | 0 | 66.2 | 97.3 | 97.3 | [7 empty] | CATEGORYB | NONSINGLE | 92340 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | WILKES 7 - WILKES - 1 | E | AEPW | AEPW |  |  | 1 | 508841 | WILKES 7 | 508840 | WILKES 4 | 508826 |  | 1 | 22WP | 525 | 597 | 0 | 65 | 96.1 | 96.1 | [7 empty] | CATEGORYB | NONSINGLE | 92674 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | WILKES 7 - WILKES - 1 | E | AEPW | AEPW |  |  | 1 | 508841 | WILKES 7 | 508840 | WILKES 4 | 508826 |  | 1 | 25SP | 471 | 525 | 0 |  | 98.1 | 98.1 | [7 empty] | CATEGORYB | NONSINGLE | 92348 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | WILKES 7 - WILKES - 1 | E | AEPW | AEPW |  |  | 1 | 508841 | WILKES 7 | 508840 | WILKES 4 | 508826 |  | 1 | 30SP | 471 | 525 | 0 |  | 99.8 | 99.8 | [7 empty] | CATEGORYB | NONSINGLE | 92342 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | WILKES 7 - WILKES - 1 | E | AEPW | AEPW |  |  | 1 | 508841 | WILKES 7 | 508840 | WILKES 4 | 508826 |  | 1 | 30SP | 471 | 525 | 0 |  | 98.4 | 98.4 | [7 empty] | CATEGORYB | NONSINGLE | 92476 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | WILLISTON27 - WILISTN7 - Z1 | E | WAPA | WAPA |  |  | 0 | 652421 | WILISTN7 | 652391 | WILLISTON27 | 0 |  | Z1 | 21SP | 201 | 201 | 0 | 97.6 | 51.997 | 97.3 | [7 empty] | CATEGORYB | NONSINGLE | 86753 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | WILLISTON27 - WILISTN7 - Z1 | E | WAPA | WAPA |  |  | 0 | 652421 | WILISTN7 | 652391 | WILLISTON27 | 0 |  | Z1 | 21SP | 201 | 201 | 0 | 95.4 | 51.997 | 95.1 | [7 empty] | CATEGORYB | SINGLE | STATELIN-MW7 - MONT -MW7 - 1 | 0 | 655924 | STATELIN-MW7 | 655940 | MONT -MW7 | 0 |  | 1 | Transfer Loading < 100%
2019-AG2 | WILLISTON27 - WILISTN7 - Z1 | E | WAPA | WAPA |  |  | 0 | 652421 | WILISTN7 | 652391 | WILLISTON27 | 0 |  | Z1 | 25SP | 201 | 201 | 0 | 96.8 | 51.3725 | 96.4 | [7 empty] | CATEGORYB | NONSINGLE | 86753 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | WOODWRD4 - WINDFRM4 - 1 | E | OKGE | OKGE |  |  | 0 | 515785 | WINDFRM4 | 514785 | WOODWRD4 | 0 |  | 1 | 22LP | 133 | 153 | 0 | 80.2 | 72.7598 | 97.3 | [7 empty] | CATEGORYB | SINGLE | CENT 4 - CENT 21 - 1 | 1 | 515363 | CENT 4 | 515365 | CENT 21 | 515364 | CENT 11 | 1 | Transfer Loading < 100%
2019-AG2 | WOODWRD4 - WINDFRM4 - 1 | E | OKGE | OKGE |  |  | 0 | 515785 | WINDFRM4 | 514785 | WOODWRD4 | 0 |  | 1 | 22LP | 133 | 153 | 0 | 80.1 | 72.7598 | 97.2 | [7 empty] | CATEGORYB | NONSINGLE | 90884 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | WOODWRD4 - WWDPST 4 - 1 | E | OKGE | OKGE |  |  | 0 | 514785 | WOODWRD4 | 515425 | WWDPST 4 | 0 |  | 1 | 22LP | 286 | 286 | 0 | 88.9 | 0 | 98.7 | [7 empty] | CATEGORYB | NONSINGLE | 106928 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | WSTELEC5 - LNGVW 5 - 1 | E | KCPL | KCPL |  |  | 0 | 541224 | LNGVW 5 | 541222 | WSTELEC5 | 0 |  | 1 | 20SP | 228 | 259 | 0 | 95.1 | 45.8248 | 96 | [7 empty] | CATEGORYB | SINGLE | GRNWD 5 - LEESUM 5 - 1 | 0 | 541218 | GRNWD 5 | 541233 | LEESUM 5 | 0 |  | 1 | Transfer Loading < 100%
2019-AG2 | WSTELEC5 - LNGVW 5 - 1 | E | KCPL | KCPL |  |  | 0 | 541224 | LNGVW 5 | 541222 | WSTELEC5 | 0 |  | 1 | 22SP | 228 | 259 | 0 | 95.4 | 44.5792 | 95.3 | [7 empty] | CATEGORYB | SINGLE | GRNWD 5 - LEESUM 5 - 1 | 0 | 541218 | GRNWD 5 | 541233 | LEESUM 5 | 0 |  | 1 | Transfer Loading < 100%
2019-AG2 | WSTELEC5 - LNGVW 5 - 1 | E | KCPL | KCPL |  |  | 0 | 541224 | LNGVW 5 | 541222 | WSTELEC5 | 0 |  | 1 | 25SP | 228 | 259 | 0 |  | 44.2763 | 96.1 | [7 empty] | CATEGORYB | NONSINGLE | 84328 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%
2019-AG2 | WWRDEHV4 - WWDPST 4 - 1 | E | OKGE | OKGE |  |  | 0 | 515425 | WWDPST 4 | 515376 | WWRDEHV4 | 0 |  | 1 | 22LP | 287 | 287 | 0 | 88.7 | 72.3458 | 98.9 | [7 empty] | CATEGORYB | NONSINGLE | 106928 | 0 | 0 |  | 0 |  | 0 |  |  | Transfer Loading < 100%